## Instructions
Distribution Network Service Provider
Annual Reporting RIN Template
This template is to be used by United Energy to fulfil its reporting obligations to the AER.
INSTRUCTIONS
Complete the Business & other details worksheet before entering data or values in any other worksheets. The Business & other details worksheet is linked to other worksheets within the workbook and automatically generates certain column headings and conditional formatting.
Identifying CONFIDENTIAL INFORMATION: Please use the macro at the top of each worksheet to identify confidential information.
-Do this by selecting the cell or cells that contain confidential information and then run the Mark selection as CONFIDENTIAL macro. This will format the cells a specific colour that is identified by the AER's database which in turn marks that information as confidential. -To reverse this, select the cell or cells and run the Return selection to NON-CONFIDENTIAL macro
UNITS OF MEASURE All amounts are to be unrounded and reported in nominal terms on a one for one basis: that is 1000 is to be entered as '1000'.
COLOUR CODING OF INPUT / NON-INPUT CELLS:
Yellow = Input cell (mandatory)
Darker yellow = input cell (mandatory)
Orange = input cell (if data available)
Grey = Not applicable/No inputs required
Leave coloured cells blank if no information exists. PLEASE DO NOT ENTER TEXT into cells that are to contain numeric data.
WORKSHEET NAVIGATION Many tables in the worksheets have been "grouped" to allow for easy navigation. To ungroup or group data use the outline symbols in the left margin of excel (for Row groupings) or above the columns (for column groupings).
RETURNING COMPLETED RESPONSES Please return four (4) files to the AER: 1. A confidential version which must contain a complete set of all responses with confidential information marked using the Mark selected cells CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. 2. An actual and an estimate version with confidential information marked using the Mark selected cells CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. 3. A public version with confidential information either removed completely or aggregated in some form together with writtten consent to disclose the public version of the response. Use the drop down box on the Business and other details worksheet to identify the file as either confidential ('consolidated') or public.
SUBMITTING AMENDED DATA TO THE AER If an NSP wishes to correct data previously submitted to the AER it should resubmit that data using the original completed submission as the starting point. Please make any necessary changes to the data. Data that is not being amended should be left unchanged. NSPs must identify the reason for the amendments in the Amendment Reason box on the Business and other details worksheet. NSPs may provide further details regarding any amendments in the Amendments worksheet. .
NSP may use Amended Data macro to highlight cells that contain amended data. NB: if data is also CONFIDENTIAL, re-apply the Confidentiality macro after applying the Amended macro
Please resubmit two (2) files - a confidential version and a public version of the amended submission to the AER
Contents
Instructions

## Contents
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
CONTENTS
| 1. Business details | 2. Expenditure
| 4. Alternative control services | 5. Network information | 6. Service & quality
Business & other details
2.1 Expenditure summary & reconciliation
2.3 Augex project data
2.5 Connections
2.2 Repex
2.7 Vegetation management
2.8 Maintenance
2.9 Emergency response
2.10 Overheads
2.6 Non-network
4.3 Ancillary services - Fee-based services
4.4 Ancillary services - Quoted services
4.1 Public lighting
4.2 Metering
5.4 Maximum demand & utilisation - Spatial
5.2 Asset age profile
5.3 Maximum demand - network level
6.3 Sustained interruptions
2.11 Labour
2.12 Input tables
2.3 (b) Augex data
2.1 Expenditure summary & reconciliation
2.3 (a) Augex project data
2.5 Connections
2.2 Repex
2.7 Vegetation management
2.8 Maintenance
2.9 Emergency response
2.6 Non-network
2.3 (b) Augex data

## Business & other details
CATEGORY ANALYSIS
United Energy
2019
BUSINESS & OTHER DETAILS
Instructions
Complete the following business details regulatory template before entering data or values in any other regulatory template. This regulatory template is linked to other cells within the spreadsheet and automatically generates column headings and conditional formatting to distinguish business specific input and non-input cells.
SUBMISSION PARTICULARS INPUT SHEETS
ENTITY DETAILS
Short name | United Energy |  |  | Select business name from drop down list first
ACN / ABN | 70064651029
Business address | Address 1 |  | Level 3
|  | Address 2 | 6 Nexus Court
| Suburb |  | MULGRAVE
|  | State | Vic | p/code | 3149
Postal address | Address 1 |  | PO Box 449
Address 2
| Suburb |  | MOUNT WAVERLEY
|  | State | VIC | p/code | 3170
Contact name/s
Contact phone/s
Contact email address/s
REGULATORY CONTROL PERIODS
Commencing regulatory year | 2019 | CRY
Last completed regulatory year | 2019 | dms_FinalYear
Source | Reporting |  | Please select the correct submission type from the dropdown list.
Data quality (actual, estimate, consolidated) | Consolidated
Confidentiality Status (public, confidential) | Public
Amended RIN submission - amendment reason | 20200804 - #11429997 - Augex classification change 05/08/2025 - #30,482,533 - correction 2.2 Repex Overhead conductors and underground cables
Submission Date | 2020-08-04 | dms_SubmissionDate | Please enter date this file submitted to AER (dd/mm/yyyy)
Contents
Instructions

## 2.1 Expenditure summary
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.1 EXPENDITURE SUMMARY & RECONCILIATION
There are SIX tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.1.1 - STANDARD CONTROL SERVICES CAPEX
EXPENDITURE ($0's)
2019
Replacement expenditure | 62647907
Connections | 45825830
Augmentation Expenditure | 21746928
Non-network | 22277640
Capitalised network overheads | 20137682
Capitalised corporate overheads
Metering
Public Lighting
Other Capons
balancing item
capcons (included in the above) | 36703402
TOTAL GROSS CAPEX (including capcons) | 172635987
2.1.2 - STANDARD CONTROL SERVICES OPEX
EXPENDITURE ($0's)
2019
Vegetation management | 17039258
Maintenance | 17407665
Emergency response | 9311803
Non-network | 0
Network overheads | 14657071
Corporate overheads | 53863801
Metering
Public Lighting
balancing item
TOTAL OPEX | 112279598
2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX
EXPENDITURE ($0's)
2019
Connections
Capitalised network overheads | 1926363
Capitalised corporate overheads
Metering | 7708999
Public lighting | 2147326
Fee and quoted
Non-network
balancing item
TOTAL CAPEX | 11782688
2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX
EXPENDITURE ($0's)
2019
Connections | 4851149
Network overheads | 53662
Corporate overheads | 8306669
Metering | 0
Public lighting | 3010194
Fee and quoted | 3361022
Non-network
balancing item
TOTAL OPEX | 19582696
2.1.5 - DUAL FUNCTION ASSETS CAPEX
EXPENDITURE ($0's)
2019
Replacement expenditure
Connections
Augmentation Expenditure
Non-network
Capitalised network overheads
Capitalised corporate overheads
balancing item
capcons (included in the above)
TOTAL GROSS CAPEX (including capcons) | 0
2.1.6 - DUAL FUNCTION ASSETS OPEX
EXPENDITURE ($0's)
2019
Vegetation management
Maintenance
Emergency response
Non-network
Network overheads
Corporate overheads
balancing item
TOTAL OPEX | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.2 Repex
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.2 REPEX
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY
|  |  | EXPENDITURE ($0's) | ASSET REPLACEMENTS (0's) | ASSET FAILURES (0's)
ASSET GROUP | ASSET CATEGORY |  | 2019 | 2019 | 2019
POLES BY: HIGHEST OPERATING VOLTAGE ; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole |  | 916972 | 1013 | 0
| ˂ = 1 kV; Wood |  | 3520689 | 474 | 0
| > 1 kV & < = 11 kV; Wood |  | 1663016 | 150 | 0
| ˃ 11 kV & < = 22 kV; Wood |  | 3880370 | 349 | 2
| > 22 kV & < = 66 kV; Wood |  | 811788 | 44 | 0
| > 66 kV & < = 132 kV; Wood |  | 0 | 0 | 0
| > 132 kV; Wood |  | 0 | 0 | 0
| ˂ = 1 kV; Concrete |  | 0 | 0 | 0
| > 1 kV & < = 11 kV; Concrete |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Concrete |  | 0 | 0 | 0
| > 22 kV & < = 66 kV; Concrete |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; Concrete |  | 0 | 0 | 0
| > 132 kV; Concrete |  | 0 | 0 | 0
| ˂ = 1 kV; Steel |  | 0 | 0 | 1
| > 1 kV & < = 11 kV; Steel |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Steel |  | 0 | 0 | 0
| > 22 kV & < = 66 kV; Steel |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; Steel |  | 0 | 0 | 0
| > 132 kV; Steel |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
POLE TOP STRUCTURES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 9765493 | 4009 | 30
| > 1 kV & < = 11 kV |  | 908415 | 307 | 1
| ˃ 11 kV & < = 22 kV |  | 3413992 | 1160 | 4
| > 22 kV & < = 66 kV |  | 348604 | 108 | 0
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 65053 | 47 | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV |  | 253693 | 2.354 | 0.95
| > 1 kV & < = 11 kV |  | 75726 | 0.559 | 0.1
| ˃ 11 kV & < = 22 kV ; SWER |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Single-Phase |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Multiple-Phase |  | 1520534 | 8.877 | 0.65
| > 22 kV & < = 66 kV |  | 0 | 0 | 0
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 1050030 | 1526 | 0
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 970451 | 1.765 | 1.62
| > 1 kV & < = 11 kV |  | 2847970 | 0.325 | 0.1
| > 11 kV & < = 22 kV |  | 3478700 | 4.792 | 0.2
| > 22 kV & < = 33 kV |  | 0 | 0 | 0
| > 33 kV & < = 66 kV |  | 0 | 0 | 0
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 2185316 | 452 | 0
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type |  | 3420259 | 5140 | 1121
| ˂ = 11 kV ; Commercial & Industrial ; Simple Type |  | 294464 | 443 | 97
| ˂ = 11 kV ; Residential ; Complex Type |  | 260173 | 391 | 85
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type |  | 63914 | 96 | 21
| ˂ = 11 kV ; Subdivision ; Complex Type |  | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Subdivision |  | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Subdivision |  | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Subdivision |  | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Subdivision |  | 0 | 0 | 0
| > 132 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 132 kV ; Subdivision |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 85523 | 13 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 39472 | 6 | 1
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 906507 | 72 | 6
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 1109107 | 18 | 1
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 161295 | 3 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 304687 | 13 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA |  | 449792 | 15 | 1
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA |  | 135004 | 3 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA |  | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA |  | 0 | 0 | 0
| Other |  | 1890822 | 57 | 0
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION | ˂ = 11 kV ; FUSE |  | 392051 | 467 | 0
| ˂ = 11 kV ; Switch |  | 2178826 | 908 | 139
| ˂ = 11 kV ; Circuit Breaker |  | 1692826 | 0 | 0
| > 11 kV & < = 22 kV ; Switch |  | 3921830 | 327 | 6
| > 11 kV & < = 22 kV ; Circuit Breaker |  | 1094071 | 5 | 0
| > 22 kV & < = 33 kV ; Switch |  | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Circuit Breaker |  | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Switch |  | 21286 | 5 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker |  | 4833 | 1 | 0
| > 66 kV & < = 132 kV ; Switch |  | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Circuit Breaker |  | 0 | 0 | 0
| > 132 kV ; Switch |  | 0 | 0 | 0
| > 132 kV ; Circuit Breaker |  | 0 | 0 | 0
| Other |  | 652160 | 112 | 4
PUBLIC LIGHTING BY: ASSET TYPE ; LIGHTING OBLIGATION | Luminaires ; Major Road |  | 643076 | 850 | 0
| Luminaires ; Minor Road |  | 390499 | 926 | 0
| Brackets ; Major Road |  | 643076 | 850 | 0
| Brackets ; Minor Road |  | 390499 | 926 | 0
| Lamps ; Major Road |  | 0 | 0 | 0
| Lamps ; Minor Road |  | 0 | 0 | 0
| Poles / Columns ; Major Road |  | 870981 | 149 | 0
| Poles / Columns ; Minor Road |  | 242770 | 92 | 0
| Other |  | 0 | 0 | 0
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices |  | 3700236 | 220 | 2
| Local Network Wiring Assets |  | 586288 | 12 | 0
| Communications Network Assets |  | 297506 | 11 | 0
| Master Station Assets |  | 0 | 0 | 0
| Communications Site Infrastructure |  | 0 | 0- | 0
| Communications Linear Assets |  | 143086 | 3 | 0
| AFLC |  | 0 | 0 | 0
| Other |  | 22847 | 10 | 0
OTHER BY: DNSP DEFINED | Buildings |  | 442580 | 7 | 0
| Civil |  | 264450 | 1 | 0
| Capacitor Banks - Large |  | 0 | 0 | 0
| Fences |  | 329877 | 32 | 0
| CTs and VTs |  | 105323 | 16 | 0
| NERs |  | 0 | 0 | 0
| Bunding/Noise |  | 0 | 0 | 0
0
2.2.2 - SELECTED ASSET CHARACTERISTICS
|  |  | ASSET VOLUMES CURRENTLY IN COMMISSION | ASSET REPLACEMENTS (0's)
ASSET GROUP | METRIC | UNITS | 2019 | 2019
TOTAL POLES BY: FEEDER TYPE | Total CBD poles | Number | 0 | 0
| Total urban poles | Number | 175337 | 927
| Total rural long poles | Number | 0 | 0
| Total rural short poles | Number | 29094 | 90
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH BY FEEDER TYPE | Conductors CBD | KM | 0 | 0
| Conductors urban | KM | 8066 | 8.208
| Conductors rural long | KM | 0 | 0
| Conductors rural short | KM | 1968 | 4
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH MATERIAL TYPE | OH conductor LV ABC | KM | 469 | 1
| OH conductor steel | KM | 311 | 0
| OH conductor ACSR | KM | 2807 | 2
| OH conductor AAAC | KM | 0 | 0
| OH conductor AAC | KM | 4840 | 4
| OH conductor HDBC | KM | 1607 | 3.879
| Other | KM | 0 | 2
UNDERGROUND CABLES BY: CABLE LENGTH BY FEEDER TYPE | Cable CBD | KM | 0 | 0
| Cable urban | KM | 2894 | 6.536
| Cable rural long | KM | 0 | 0
| Cable rural short | KM | 480 | 0.346
TRANSFORMERS BY: TOTAL MVA | Total MVA replaced | MVA | 8610.952 | 52
| Total MVA disposed of | MVA | 0 | 27.3
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.3(a) Augex
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.3 AUGEX PROJECT DATA
There are TWO tables on this worksheet - each has been 'grouped' for easy navigation. Both ROWS and COLUMNS have been grouped. See the Instructions sheet on how to group or ungroup tables.
2.3.1 - AUGEX ASSET DATA - SUBTRANSMISSION SUBSTATIONS, SWITCHING STATIONS AND ZONE SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE ($0's) | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
SUBSTATION ID | SUBSTATION TYPE (drop down) | PROJECT ID | PROJECT TYPE (drop down) | PROJECT TRIGGER (drop down) | VOLTAGE (KV) | SUBSTATION RATING NORMAL CYCLIC (MVA) |  | SUBSTATION RATING N-1 EMERGENCY (MVA) |  | TRANSFORMERS |  |  | SWITCHGEAR |  | CAPACITORS |  |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | PRE | POST | PRE | POST | UNITS ADDED | MVA ADDED | EXPENDITURE ($0's) | UNITS ADDED | EXPENDITURE ($0's) | MVAR ADDED | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's) | VOLUME | EXPENDITURE ($0's) | EXPENDITURE ($0's) |  |  |  | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's)
|  | Non material projects - [actual] | [21 empty] | 2616124 | 2018, 2019
AUG232_1 | AUG232_2 | AUG232_3 | AUG232_4 | AUG232_5 | AUG232_6 | ED_AUG232_00001 | ED_AUG232_00002 | ED_AUG232_00003 | ED_AUG232_00004 | ED_AUG232_00005 | ED_AUG232_00006 | ED_AUG232_00007 | ED_AUG232_00008 | ED_AUG232_00009 | ED_AUG232_00010 | ED_AUG232_00011 | ED_AUG232_00012 | ED_AUG232_00013 | ED_AUG232_00014 | ED_AUG232_00015 | ED_AUG232_00016 | ED_AUG232_00017 | ED_AUG232_00018 | ED_AUG232_00019 | ED_AUG232_00020 | ED_AUG232_00021
2.3.2 - AUGEX ASSET DATA - SUBTRANSMISSION LINES
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE ($0's) | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
LINE ID | PROJECT ID | PROJECT TYPE | PROJECT TRIGGER |  | VOLTAGE (KV) | ROUTE LINE LENGTH ADDED |  |  |  | POLES/TOWERS (INCLUDING STRUCTURES, AND CIVIL WORKS) |  |  | OVERHEAD LINES |  |  | UNDERGROUND CABLES |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | KM ADDED |  |  |  | POLES/TOWERS ADDED | POLES/TOWERS UPGRADED | EXPENDITURE ($0's) | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE ($0's) | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE ($0's) | EXPENDITURE ($0's) | VOLUME | EXPENDITURE ($0's) | EXPENDITURE ($0's) |  |  |  | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's)
New line on new route - single circuit
New line on new route - dual circuit
New line on new route - other
Line rebuild over existing route - single circuit
Line rebuild over existing route - dual circuit
Reconductor - Single circuit
Reconductor - Dual circuit
Reconductor - Other
Line upgrade - raising/retensoring
Line upgrade - voltage upgrade
Line upgrade - capacity
String spare circuit
Other
Non material projects - [actual]
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.3(b) Augex
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.3 AUGEX DATA
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON AN AS INCURRED BASIS.
DESCRIPTOR METRICS
PROJECT TYPE |  | UNITS ADDED (0's) | UNITS UPGRADED (0's)
| UNITS | 2019 | 2019
HV Feeder Augmentations - Overhead Lines | Circuit line length in km | 0.253 | 0.263
HV Feeder Augmentations - Underground Cables | Circuit line length in km | 0.955 | 0.473
LV Feeder Augmentations - Overhead Lines | Circuit line length in km | 0.162 | 0
LV Feeder Augmentations - Underground Cables | Circuit line length in km | 0.82 | 0
Distribution Substation Augmentations - Pole Mounted | Number | 15 | 61
Distribution Substation Augmentations - Ground Mounted | Number | 0 | 0
Distribution Substation Augmentations - Indoor | Number | 0 | 0
COST METRICS
TOTAL DIRECT EXPENDITURE - Project Type |  | EXPENDITURE ($0's)
2019
HV Feeder Augmentations - Overhead Lines |  | 0
HV Feeder Augmentations - Underground Cables |  | 696209
HV Feeder Non-Material Projects |  | 627856
LV Feeder Augmentations - Overhead Lines |  | 0
LV Feeder Augmentations - Underground Cables |  | 0
LV Feeder Non-Material Projects |  | 568805
Distribution Substation Augmentations - Pole Mounted |  | 4796541
Distribution Substation Augmentations - Ground Mounted |  | 0
Distribution Substation Augmentations - Indoor |  | 0
2.3.4 - AUGEX DATA - TOTAL EXPENDITURE
AUGMENTATION CAPEX (As incurred) |  | EXPENDITURE ($0's)
2019
Subtransmission Substations, Switching Stations, Zone Substations |  | 2133002
Subtransmission Lines |  | 26229
HV Feeders |  | 1324065
HV Feeders - Land Purchases and Easements |  | 0
Distribution Substations |  | 4796541
Distribution Substations - Land Purchases And Easements |  | 0
LV Feeders |  | 568805
LV Feeders - Land Purchases And Easements |  | 0
Other Assets |  | 12898287
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.5 Connections
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.5 CONNECTIONS
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.5.1 - DESCRIPTOR METRICS
<<<GROUP-ROW>>>
VOLUMES AND EXPENDITURE
CONNECTION SUBCATEGORY | DESCRIPTOR METRIC | UNITS | 2019
RESIDENTIAL | Underground connections | 0's | 7849
| Overhead connections | 0's | 220
| Distribution substation installed | MVA added | 0
| Distribution substations installed | 0's | 0
| Distribution substation installed | total spend $0s | 0
| Augmentation HV | net circuit km added | 0
| Augmentation HV | total spend $0s | 0
| Augmentation LV | net circuit km added | 0.03
| Augmentation LV | total spend $0s | 12416818
| Mean days to connect residential customer with LV single phase connection | 0's | 7
| Volume of GSL breaches for residential customers | 0's | 138
| Volume of customer complaints relating to connection services | 0's | 233
| GSL payments | $0s | 30170
COMMERCIAL/INDUSTRIAL | Underground connections | 0's | 1551
| Overhead connections | 0's | 1470
| Distribution substation installed | MVA added | 75.58
| Distribution substations installed | 0's | 120
| Distribution substation installed | total spend $0s | 10147339
| Augmentation HV | net circuit km added | 19.15
| Augmentation HV | total spend $0s | 14067520
| Augmentation LV | net circuit km added | 38
| Augmentation LV | total spend $0s | 3059157
SUBDIVISION | Underground connections | 0's | 1409
| Overhead connections | 0's | 17
| Distribution substation installed | MVA added | 1.41
| Distribution substations installed | 0's | 12
| Distribution substation installed | total spend $0s | 653693
| Augmentation HV | net circuit km added | 8.7
| Augmentation HV | total spend $0s | 2366379
| Augmentation LV | net circuit km added | 37.49
| Augmentation LV | total spend $0s | 3114924
| Cost per lot ($) | $0s | 4302
EMBEDDED GENERATION | Underground connections | 0's | 4654
| Overhead connections | 0's | 5386
| Distribution substation installed | MVA added | 0
| Distribution substations installed | 0's | 0
| Distribution substation installed | total spend $0s | 0
| Augmentation HV | net circuit km added | 0
| Augmentation HV | total spend $0s | 0
| Augmentation LV | net circuit km added | 0
| Augmentation LV | total spend $0s | 0
2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION
|  | EXPENDITURE ($0's) | VOLUMES (0's)
CONNECTION SUBCATEGORY | CONNECTION CLASSIFICATION | 2019 | 2019
RESIDENTIAL | Simple connection LV | 12416818 | 8069
| Complex connection LV | 0 | 0
| Complex connection HV | 0 | 0
COMMERCIAL/INDUSTRIAL | Simple connection LV | 3977353 | 884
| Complex connection HV (customer connected at LV, minor HV works) | 11445857 | 1030
| Complex connection HV (customer connected at LV, upstream asset works) | 1088383 | 2
| Complex connection HV (customer connected at HV) | 10762423 | 1105
| Complex connection sub-transmission | 0 | 0
SUBDIVISION | Complex connection LV | 3157644 | 1094
| Complex connection HV (no upstream asset works) | 2438742 | 332
| Complex connection HV (with upstream asset works) | 538610 | 0
EMBEDDED GENERATION | Simple connection LV | 0 | 0
| Complex connection HV (small capacity) | 0 | 0
| Complex connection HV (large capacity) | 0 | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.6 Non-network
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.6 NON NETWORK EXPENDITURE
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.6.1 - NON-NETWORK EXPENDITURE
EXPENDITURE ($0's)
SERVICE SUBCATEGORY | ASSET CATEGORY |  |  | 2019
OPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 0
| Recurrent expenditure |  |  | 25056338
| Non-recurrent expenditure |  |  | 1197141
MOTOR VEHICLES | Car |  |  | 387570
| Light commercial vehicle |  |  | 1848220
| Elevated work platform (LCV) |  |  | 0
| Elevated work platform (HCV) |  |  | 3739384
| Heavy commercial vehicle |  |  | 1121086
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 4807063
OTHER | Other expenditure
OTHER - DNSP nominated
CAPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 204561
| Recurrent expenditure |  |  | 6676159
| Non-recurrent expenditure |  |  | 10399741
MOTOR VEHICLES | Car |  |  | 0
| Light commercial vehicle |  |  | 0
| Elevated work platform (LCV) |  |  | 0
| Elevated work platform (HCV) |  |  | 1817827
| Heavy commercial vehicle |  |  | 0
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 3179351.83
OTHER | Other expenditure
OTHER - DNSP nominated
2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE
VOLUMES (0's)
NON-NETWORK CATEGORY | DESCRIPTOR METRIC |  |  | 2019
IT & COMMUNICATIONS | Employee numbers |  |  | 221
| User numbers |  |  | 747
| Number of devices |  |  | 495
2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES
VOLUMES / %
NON-NETWORK CATEGORY | ASSET CATEGORY | DESCRIPTOR METRIC | UNITS | 2019
MOTOR VEHICLES | CAR | Average kilometres travelled | 0's | 21779
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 27
|  | Number in fleet | 0's | 43
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 100%
| LIGHT COMMERCIAL VEHICLE | Average kilometres travelled | 0's | 23893
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 101
|  | Number in fleet | 0's | 122
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 100%
| ELEVATED WORK PLATFORM (LCV) | Average kilometres travelled | 0's | 0
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 0
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 0%
| ELEVATED WORK PLATFORM (HCV) | Average kilometres travelled | 0's | 18220
|  | Number purchased | 0's | 5
|  | Number leased | 0's | 33
|  | Number in fleet | 0's | 77
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 100%
| HEAVY COMMERCIAL VEHICLE | Average kilometres travelled | 0's | 7724
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 22
|  | Number in fleet | 0's | 50
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 100%
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.7 Vegetation management
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.7 VEGETATION MANAGEMENT
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
Please enter a description for each Zone in table 2.7.1 - Urban and CBD. The zone description will then autopopulate in tables 2.7.1 - Rural and 2.7.2.
` | 2.7.1 - DESCRIPTOR METRICS BY ZONE
URBAN AND CBD
2019
| ZONES | ASSET | UNITS
| ZONE 1 | Route line length within zone | km | 5348.02
|  | Number of maintenance spans | 0's | 40568
|  | Total length of maintenance spans | km | 1351
|  | Length of vegetation corridors | km | 1
|  | Average number of trees per maintenance span | 0's | 3.31
|  | Average frequency of cutting cycle | years | 2.75
| ZONE 2 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 3 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 4 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 5 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 6 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 7 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 8 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 9 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 10 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 11 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
RURAL
2019
| ZONES | ASSET | UNITS
| ZONE 1 | Route line length within zone | km | 1508.42
|  | Number of maintenance spans | 0's | 11017
|  | Total length of maintenance spans | km | 568
|  | Length of vegetation corridors | km | 1
|  | Average number of trees per maintenance span | 0's | 9.81
|  | Average frequency of cutting cycle | years | 2.22
| ZONE 2 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 3 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 4 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 5 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 6 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 7 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 8 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 9 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 10 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 11 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
2.7.2 - EXPENDITURE METRICS BY ZONE
EXPENDITURE ($0's)
| ZONES | SERVICE SUBCATEGORY |  | 2019
| ZONE 1 | Tree trimming (excluding hazard trees) |  | 15096525.55
|  | Hazard tree cutting |  | 3805.45
|  | Ground clearance |  | 0
|  | Vegetation corridor clearance |  | 11416.47
|  | Inspection |  | 2077830
|  | Audit |  | 0
|  | Contractor liaison expenditure |  | -150319.47
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 2 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 3 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 4 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 5 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 6 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 7 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 8 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 9 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 10 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 11 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 12 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 13 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 14 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 15 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 16 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 17 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 18 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS
VOLUMES (0's)
| DESCRIPTOR METRIC |  |  | 2019
| Number of fire starts caused by vegetation grow-ins (NSP responsibility) |  |  | 0
| Number of fire starts caused by vegetation blow-ins and fall-ins (NSP responsibility) |  |  | 1
| Number of fire starts caused by vegetation grow-ins (other party responsibility) |  |  | 0
| Number of fire starts caused by vegetation blow-ins and fall-ins (other party responsibility) |  |  | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.8 Maintenance
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.8 MAINTENANCE
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
|  |  |  | ASSET QUANTITY (0's) |  | AVERAGE AGE OF ASSET GROUP | INSPECTION CYCLE (YEARS) | MAINTENANCE CYCLE (YEARS)
|  |  |  | AT YEAR END | INSPECTED / MAINTAINED
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2019 | 2019 | 2019
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 216103 | 34693 | 32.81 | 5 | 3
| Service lines | Number of customers | Number | 697594 | 205 | 14.92 | 5 | 0
Pole inspection and treatment | All poles | Number of poles | Number | 216103 | 25795 | 32.81 | 5 | 0
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 10034 | 1307 | 41.56 | 5 | 0
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 3370 | 2489 | 22.52 | 5 | 0
| 33 KV and above | Length (KM) | KM | 4 | 0 | 11.02 | 2 | 0
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 0 | 0 | 0 | 0 | 0
| Non-CBD | Length (KM) | KM | 3374 | 2489 | 22.3 | 5 | 0
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 13856 | 264 | 20.06 | 1 | 0
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 96380 | 180 | 23.79 | 10 | 0
| Distribution substation - other equipment | Earth mat | Number | 3809 | 327 | 16.48 | 5 | 5
| Distribution substation - property | Number of distribution substation properties maintained | Number | 13856 | 4382 | 20.06 | 1 | 1
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 114 | 340 | 34.49 | 1 | 2
| Transformers - distribution | Number of distribution transformers within zone substation | Number | 76 | 0 | 15.84 | 4 | 0
| Transformers - HV | Number of HV transformers | Number | 0 | 0 | 0 | 0 | 0
| Zone substation - other equipment |  | Number | 1991 | 599 | 19.84 | 1 | 10
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 52 | 1275 | 47.98 | 0 | 0
Public lighting maintenance | Minor roads | Number of public lights maintained | Number | 93293 | 17189 | 6.42 | 4 | 4
| Major roads | Number of public lights maintained | Number | 28375 | 5417 | 19.06 | 0 | 0
SCADA & network control maintenance | SCADA & network control | Number of systems | Number | 318 | 120 | 11.78 | 3 | 3
Protection systems maintenance | Protection systems | Number of systems | Number | 2634 | 1177 | 12.99 | 3 | 0
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets |  | Number | 0 | 0 | 0 | 0 | 0
Various assets | includes rates, electricity, communications equip, metering | Various | Number | 0 | 0 | 0 | 0 | 0
Ground clearance - access tracks | Access tracks | Number | Number | 0 | 0 | 0 | 0 | 0
Other |  |  |  | 0 | 0 | 0
2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
EXPENDITURE ($0'S)
|  |  |  | ROUTINE MAINTENANCE | NON-ROUTINE MAINTENANCE
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2019 | 2019
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 1941619 | 406391
| Service lines | Number of customers | Number | 0 | 93876
Pole inspection and treatment | All poles | Number of poles | Number | 1251005 | 71112
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 236304 | 327637
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 209740 | 378735
| 33 KV and above | Length (KM) | KM | 0 | 0
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 0 | 0
| Non-CBD | Length (KM) | KM | 209740 | 378735
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 74374 | 84370
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 130824 | 51410
| Distribution substation - other equipment | Earth mat | Number | 196181 | 21025
| Distribution substation - property | Number of distribution substation properties maintained | Number | 359670 | 321795
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 1187641 | 84762
| Transformers - distribution | Number of distribution transformers within zone substation | Number | 0 | 0
| Transformers - HV | Number of HV transformers | Number | 0 | 0
| Zone substation - other equipment |  | Number | 806619 | 474665
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 849282 | 28295
Public lighting maintenance | Minor roads | Number of public lights maintained | Number | 508902 | 1188410
| Major roads | Number of public lights maintained | Number | 119592 | 1229193
SCADA & network control maintenance | SCADA & network control | Number of systems | Number | 68480 | 829793
Protection systems maintenance | Protection systems | Number of systems | Number | 663414 | 1191891
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets |  | Number | 0 | 0
Various assets | includes rates, electricity, communications equip, metering | Various | Number | 0 | 0
Ground clearance - access tracks | Access tracks | Number | Number | 0 | 0
Other | Other Maintenance |  |  | 2485086 | 2218416
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.9 Emergency Response
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.9 EMERGENCY RESPONSE
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX)
EXPENDITURE ($0's)
2019
(A) TOTAL EMERGENCY RESPONSE EXPENDITURE
Total Expenditure | 10104184.2
(B) MAJOR EVENTS O&M EXPENDITURE
N/A | 0
(C) MAJOR EVENT DAYS O&M EXPENDITURE
N/A | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.10 Overheads
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.10 OVERHEADS
Please note. This worksheet 2.10 Overheads is the original worksheet. We have also included a different version of the Overheads template (worksheet 2.10A Overheads) which collects the information in a different way. United Energy is not obliged to complete worksheet 2.10A. However, the AER would prefer to collect Overheads information as presented in the revised worksheet 2.10A Overheads. If United Energy is prepared to complete worksheet 2.10A in lieu of the original worksheet 2.10 Overheads, please indicate that choice by selecting from the drop down list at the right. United Energy is only required to complete one version of the Overheads worksheet in order to comply with the Category Analysis RIN. |  | Choose Response drop down selection
Worksheet 2.10A
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
Instructions Please enter a description for each expenditure category as currently reported under United Energy's annual RIN.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2019
NETWORK OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED NETWORK OVERHEADS
Standard Control Services
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2019
CORPORATE OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED CORPORATE OVERHEADS
Standard Control Services
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.10(A) Overheads
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.10(A) OVERHEADS
This worksheet may be completed on a voluntary basis. Please see worksheet 2.10 for an explanation of Overheads reporting options.
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2019
OPEX
Standard Control Services | Total | 14657071
Alternative Control Services | Total | 53662
CAPEX
Standard Control Services | Total | 20137682
Alternative Control Services | Total | 1926363
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total | 182009
Unregulated Services | Total | 0
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2019
OPEX
Standard Control Services | Total | 53863801
Alternative Control Services | Total | 8306669
CAPEX
Standard Control Services | Total
Alternative Control Services | Total
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total
Unregulated Services | Total
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.11 Labour
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.11 LABOUR
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.11.1 - COST METRICS PER ANNUM
|  | ASL (0's) | TOTAL LABOUR EXPENDITURE ($0's) | AVERAGE PRODUCTIVE WORK HOURS PER ASL (0's) | STAND-DOWN OCCURENCES PER ASL (0's)
|  | 2019 | 2019 | 2019 | 2019
INTERNAL LABOUR EXPENDITURE
CORPORATE OVERHEADS | Executive manager | 2 | 82847 | 494
| Senior manager | 1 | 52184 | 494
| Manager | 4.9 | 208933 | 493
| Professional | 69.1 | 1976068 | 493
| Semi professional | 0 | 0 | 0
| Support staff | 1 | 13420 | 494
| Intern, junior staff, apprentice | 0 | 0 | 0
NETWORK OVERHEADS | Executive manager | 1.8 | 249228 | 494
| Senior manager | 7.3 | 603227 | 491
| Manager | 22.6 | 1365250 | 491
| Professional | 84.5 | 3733790 | 492
| Semi professional | 0 | 0 | 0
| Support staff | 4.2 | 103242 | 494
| Intern, junior staff, apprentice | 0 | 0 | 0
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker
Skilled non electical worker
Apprentice
Unskilled worker
2.11.2 - DESCRIPTOR METRICS
|  | ORDINARY TIME (0's) |  | OVERTIME (0's)
|  | PER ASL | HOURLY RATE PER ASL | PER ASL | HOURLY RATE PER ASL
|  | 2019 | 2019 | 2019 | 2019
AVERAGE PRODUCTIVE WORK HOURS PER ASL
CORPORATE OVERHEADS | Executive manager | 494 | 86
| Senior manager | 494 | 108
| Manager | 493 | 87
| Professional | 493 | 58
| Semi professional | 0 | 0
| Support staff | 494 | 28
| Intern, junior staff, apprentice | 0 | 0
NETWORK OVERHEADS | Executive manager | 494 | 277
| Senior manager | 491 | 168
| Manager | 491 | 123
| Professional | 492 | 90
| Semi professional | 0 | 0
| Support staff | 494 | 50
| Intern, junior staff, apprentice | 0 | 0
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker
Skilled non electical worker
Apprentice
Unskilled worker
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.12 Input tables
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
2.12 INPUT TABLES
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.12.1 - INPUT TABLES
|  | DIRECT MATERIAL EXPENDITURE | DIRECT LABOUR EXPENDITURE | CONTRACT EXPENDITURE | OTHER EXPENDITURE | RELATED PARTY CONTRACT EXPENDITURE | RELATED PARTY CONTRACT MARGIN EXPENDITURE
EXPENDITURE ($0's)
|  | 2019 | 2019 | 2019 | 2019 | 2019 | 2019
VEGETATION MANAGEMENT | ZONE 1 | 0 | 17039258 | 0
ZONE 2
ZONE 3
ZONE 4
ZONE 5
ZONE 6
ZONE 7
ZONE 8
ZONE 9
ZONE 10
ZONE 11
ZONE 12
ZONE 13
ZONE 14
ZONE 15
ZONE 16
ZONE 17
ZONE 18
ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | 913325 | 930195 | 98098
| Pole inspection and treatment | 588465 | 599334 | 63206
| Overhead asset inspection | 111156 | 113209 | 11939
| Network underground cable maintenance | 98660 | 100483 | 10597
| Distribution substation equipment & property maintenance | 357993 | 364605 | 38451
| Zone substation equipment maintenance | 938087 | 955415 | 100758
| Zone substation property maintenance | 399497 | 406876 | 42909
| Public lighting maintenance | 5306 | 569165 | 54022
| Scada & network control maintenance | 32213 | 32808 | 3460
| Protection systems maintenance | 312066 | 317830 | 33518
| Subtransmission asset maintenance - for dnsps with dual function assets | 0 | 0 | 0
| Other | 1168969 | 1190561 | 125557
NON-ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | -1383 | 453403 | 48247
| Pole inspection and treatment | -197 | 64450 | 6858
| Overhead asset inspection | -906 | 296945 | 31598
| Network underground cable maintenance | -1047 | 343256 | 36526
| Distribution substation equipment & property maintenance | -1323 | 433766 | 46157
| Zone substation equipment maintenance | -1546 | 507021 | 53952
| Zone substation property maintenance | -78 | 25644 | 2729
| Public lighting maintenance | 25719 | 2758551 | 261827
| SCADA & network control maintenance | -2294 | 752060 | 80027
| Protection systems maintenance | -3294 | 1080237 | 114949
| Subtransmission asset maintenance - for DNSP with dual function assets | 0 | 0 | 0
| Other | -6132 | 2010599 | 213949
OVERHEADS | Network overheads | 280924 | 23402454 | 13091400
| Corporate overheads | 39 | 9904749 | 52265683
AUGMENTATION | Subtransmission substations, switching stations, zone substations | 855306 | 1136575 | 141121
| Subtransmission lines | 10517 | 13976 | 1735
| HV feeders | 530932.9256 | 705531.1912 | 87601.0031
| Distribution substations | 1923350.6338 | 2555848.0144 | 317342.2418
| LV feeders | 228083.4214 | 303089.0726 | 37632.506
| Other assets | 5172045.5561 | 6872882.2156 | 853358.9783
CONNECTIONS | Simple and complex customer connections | 5596819 | 26738556 | 13490455
EMERGENCY RESPONSE | Major storms | 1638269 | 7627898 | 838017
Major event days
PUBLIC LIGHTING | All public lighting services | 1125312 | 4663011 | 8683451
METERING | All metering services | 3118917 | 6007373 | 9309008
FEE-BASED SERVICES | All fee-based services | 6415 | 2378894 | 463406
QUOTED SERVICES | All quoted services | 4196 | 1556217 | 303149
REPLACEMENT | Poles | 2696348 | 7166121 | 930367
| Pole top structures | 3622889 | 9628601 | 1250067
| Overhead conductors | 724496 | 1925502 | 249985
| Underground cables | 2368974 | 6296055 | 817407
| Service lines | 1009006 | 2681649 | 348154
| Transformers | 1269676 | 3374435 | 438098
| Switchgear | 2487754 | 6611737 | 858392
| Public lighting | 1113587 | 1796581 | 270733
| SCADA network control and protection systems | 1186672 | 3153834 | 409457
| Other | 285361 | 758407 | 98463
NON-NETWORK EXPENDITURE | IT and communications | 10836062 | 23768581 | 8929298
| Motor vehicles | 8654557 | 0 | 259530
| Buildings and property | 4226635 | 0 | 3759779
Other
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.1 Public lighting
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
4.1 PUBLIC LIGHTING
There are THREE tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
4.1.1 - DESCRIPTOR METRICS OVER YEAR
VOLUME (0's)
| LIGHT TYPE |  | 2019
POPULATION OF LIGHTS | Flourescent 2x20W |  | 40
| Flourescent 3x20W |  | 3
| Mercury Vapour 50W |  | 11
| Mercury Vapour 80W |  | 7367
| Mercury Vapour 125W |  | 509
| Mercury Vapour 250W |  | 65
| Mercury Vapour 400W |  | 6
| Mercury Vapour 700W |  | 3
| Sodium HP 70W |  | 267
| Sodium HP 100W |  | 975
| Sodium HP 150W |  | 22599
| Sodium HP 250W |  | 10096
| Sodium HP 400W |  | 301
| Metal Halide 70W |  | 9
| Metal Halide 100W |  | 95
| Metal Halide 150W |  | 34
| Metal Halide 250W |  | 121
| Metal Halide 400W |  | 118
| T5 Fluorescent 2x14W |  | 33083
| T5 Fluorescent 2x24W |  | 360
| Compact Fluorescent 32W |  | 1651
| Compact Fluorescent 42W |  | 745
| LED |  | 43256
4.1.2 - DESCRIPTOR METRICS ANNUALLY
VOLUMES & EXPENDITURE
SERVICE/SERVICE QUALITY | DESCRIPTOR METRIC | UNITS | 2019
LIGHT INSTALLATION | Major road light installation | 0's | 11133
| Minor road light installation | 0's | 1008
| Number of poles installed | 0's | 0
| Total cost | $0s | 9314255
LIGHT REPLACEMENT | Major road light replacement | 0's | 850
| Minor road light replacement | 0's | 926
| Number of poles replaced | 0's | 241
| Total cost | $0s | 2147326
LIGHT MAINTENANCE | Major road light maintenance | 0's | 5397
| Minor road light maintenance | 0's | 16740
| Number of poles installed | 0's | 364
| Total cost | $0s | 3010194
QUALITY OF SUPPLY | Mean days to rectify/replace public lighting assets | days | 2
| GSO breaches | 0's | 25
| GSL payments | $0s | 625
| Customer complaints | 0's | 5
4.1.3 - COST METRICS
AVERAGE UNIT COST ($)
ACTIVITY TYPE | LIGHT TYPE |  | 2019
LIGHT INSTALLATION | New Light Major Road (CNJ) |  | 1439.66
| Pb.Light CapProj - Major Scheme (CLJ) |  | 729.85
| New Light Minor Road (CNM) |  | 376.56
| New Light Watchman (CNW) |  | 1471.07
| New Sustainable Light (CNG) |  | 618.14
| New Sustainable Lantern & Bracket (CNS) |  | 2584.88
| Pb.Light CapProj - Minor Scheme (CLN) |  | 907.23
LIGHT REPLACEMENT | SINGLE MAJOR RD REPL (RLJ) |  | 682.15
| POLE REPLACE P/L (RPA) |  | 6357.52
| SINGLE MINOR RD REPL (RLM) |  | 441.18
| SINGLE SUSTAINABLE LANTERN REPL (RLG) |  | 414.06
| Single Sustainable Lantern Replacement (RLS) |  | 1472.8
| Pole Reinforcememt (RRP) |  | 516.06
| POLE REPLACE P/L (RPB) |  | 2640.78
LIGHT MAINTENANCE | MAJOR ROAD PATROLS (MLP) |  | 21032.27
| PL Luminaires (MLF) |  | 230.27
| PL Poles (MLR) |  | 198.55
| MINOR LAMP BULK (MRB) |  | 54.51
| PL Luminaires (MRF) |  | 213.7
| PL Poles (MRR) |  | 220.86
| Bulk Change Sustainable Lantern - Minor Rd (MRS) |  | 41.92
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.2 Metering
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
4.2 METERING
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
4.2.1 - METERING DESCRIPTOR METRIC
VOLUMES (0's)
Asset Category | Asset Subcategory | 2019
Meter Type 4 | Single phase meter population | 576153
| Multi phase meter population | 103670
| Current transformer connected meter population | 3627
| Direct connect meter population | 679823
Meter Type 5 | Single phase meter population | 255
| Multi phase meter population | 388
| Current transformer connected meter population | 100
| Direct connect meter population | 543
Meter Type 6 | Single phase meter population | 12867
| Multi phase meter population | 6165
| Current transformer connected meter population | 75
| Direct connect meter population | 19106
4.2.2 - COST METRICS
|  | VOLUMES (0's) | EXPENDITURE ($0's)
Service Subcategory | Meter Type | 2019 | 2019
Meter purchase | Meter Type 4 | 14682 | 5326805
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter testing | Meter Type 4 | 933 | 208297
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter investigation | Meter Type 4 | 363 | 98794.92
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Scheduled meter reading | Meter Type 4 | 249111108 | 0
| Meter Type 5 | 3870 | 45887
| Meter Type 6 | 86640 | 412873
Special meter reading | Meter Type 4 | 0 | 0
| Meter Type 5 | 214 | 1154
| Meter Type 6 | 1899 | 34037
New meter installation | Meter Type 4 | 12340 | 3412366.04
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter replacement | Meter Type 4 | 9141 | 2954966.89
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter maintenance | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Remote meter reading | Meter Type 4 | 249111108 | 0
Remote meter re-configuration | Meter Type 4 | 9963 | 0
Other metering | Meter Type 4 |  | 1969284.25
| Meter Type 5 |  | 0
| Meter Type 6 |  | 0
| Meter Type 7 |  | 0
IT infrastructure capex | Meter Type 4 |  | 50422.73
IT infrastructure opex | Meter Type 4 |  | 2668403
Communications infrastructure capex | Meter Type 4 |  | 196354.8
Communications infrastructure opex | Meter Type 4 |  | 1055652
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.3 Fee-based services
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
4.3 ANCILLARY SERVICES - FEE BASED SERVICES
4.3.1 - COST METRICS FOR FEE-BASED SERVICES
|  | EXPENDITURE ($0's) |  | VOLUMES (0's)
SERVICE | SERVICE SUBCATEGORY | 2019 |  | 2019
Common Fee-Based Services | Energisation |  | ED_FEE431_00001
| De-energisation |  | ED_FEE431_00002
| Re-energisation |  | ED_FEE431_00003
Miscellaneous Fee-Based Services | Connection Services | 1037552 | ED_FEE431_00004 | 137663
| Metering Services | 0 | ED_FEE431_00005 | 0
| Ancillary Services | 1811162 | ED_FEE431_00006 | 7429
ED_FEE431_00007
ED_FEE431_00008
ED_FEE431_00009
ED_FEE431_00010
ED_FEE431_00011
ED_FEE431_00012
ED_FEE431_00013
ED_FEE431_00014
ED_FEE431_00015
ED_FEE431_00016
ED_FEE431_00017
ED_FEE431_00018
ED_FEE431_00019
ED_FEE431_00020
ED_FEE431_00021
ED_FEE431_00022
ED_FEE431_00023
ED_FEE431_00024
ED_FEE431_00025
ED_FEE431_00026
ED_FEE431_00027
ED_FEE431_00028
ED_FEE431_00029
ED_FEE431_00030
ED_FEE431_00031
ED_FEE431_00032
ED_FEE431_00033
ED_FEE431_00034
ED_FEE431_00035
ED_FEE431_00036
ED_FEE431_00037
ED_FEE431_00038
ED_FEE431_00039
ED_FEE431_00040
ED_FEE431_00041
ED_FEE431_00042
ED_FEE431_00043
ED_FEE431_00044
ED_FEE431_00045
ED_FEE431_00046
ED_FEE431_00047
ED_FEE431_00048
ED_FEE431_00049
ED_FEE431_00050
ED_FEE431_00051
ED_FEE431_00052
ED_FEE431_00053
ED_FEE431_00054
ED_FEE431_00055
ED_FEE431_00056
ED_FEE431_00057
ED_FEE431_00058
ED_FEE431_00059
ED_FEE431_00060
ED_FEE431_00061
ED_FEE431_00062
ED_FEE431_00063
ED_FEE431_00064
ED_FEE431_00065
ED_FEE431_00066
ED_FEE431_00067
ED_FEE431_00068
ED_FEE431_00069
ED_FEE431_00070
ED_FEE431_00071
ED_FEE431_00072
ED_FEE431_00073
ED_FEE431_00074
ED_FEE431_00075
ED_FEE431_00076
ED_FEE431_00077
ED_FEE431_00078
ED_FEE431_00079
ED_FEE431_00080
ED_FEE431_00081
ED_FEE431_00082
ED_FEE431_00083
ED_FEE431_00084
ED_FEE431_00085
ED_FEE431_00086
ED_FEE431_00087
ED_FEE431_00088
ED_FEE431_00089
ED_FEE431_00090
ED_FEE431_00091
ED_FEE431_00092
ED_FEE431_00093
ED_FEE431_00094
ED_FEE431_00095
ED_FEE431_00096
ED_FEE431_00097
ED_FEE431_00098
ED_FEE431_00099
ED_FEE431_00100
ED_FEE431_00101
ED_FEE431_00102
ED_FEE431_00103
ED_FEE431_00104
ED_FEE431_00105
ED_FEE431_00106
ED_FEE431_00107
ED_FEE431_00108
ED_FEE431_00109
ED_FEE431_00110
ED_FEE431_00111
ED_FEE431_00112
ED_FEE431_00113
ED_FEE431_00114
ED_FEE431_00115
ED_FEE431_00116
ED_FEE431_00117
ED_FEE431_00118
ED_FEE431_00119
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00164
ED_FEE431_00165
ED_FEE431_00166
ED_FEE431_00167
ED_FEE431_00168
ED_FEE431_00169
ED_FEE431_00170
ED_FEE431_00171
ED_FEE431_00172
ED_FEE431_00173
ED_FEE431_00174
ED_FEE431_00175
ED_FEE431_00176
ED_FEE431_00177
ED_FEE431_00178
ED_FEE431_00179
ED_FEE431_00180
ED_FEE431_00181
ED_FEE431_00182
ED_FEE431_00183
ED_FEE431_00184
ED_FEE431_00185
ED_FEE431_00186
ED_FEE431_00187
ED_FEE431_00188
ED_FEE431_00189
ED_FEE431_00190
ED_FEE431_00191
ED_FEE431_00192
ED_FEE431_00193
ED_FEE431_00194
ED_FEE431_00195
ED_FEE431_00196
ED_FEE431_00197
ED_FEE431_00198
ED_FEE431_00199
ED_FEE431_00200
ED_FEE431_00201
ED_FEE431_00202
ED_FEE431_00203
ED_FEE431_00204
ED_FEE431_00205
ED_FEE431_00206
ED_FEE431_00207
ED_FEE431_00208
ED_FEE431_00209
ED_FEE431_00210
ED_FEE431_00211
ED_FEE431_00212
ED_FEE431_00213
ED_FEE431_00214
ED_FEE431_00215
ED_FEE431_00216
ED_FEE431_00217
ED_FEE431_00218
ED_FEE431_00219
ED_FEE431_00220
ED_FEE431_00221
ED_FEE431_00222
ED_FEE431_00223
ED_FEE431_00224
ED_FEE431_00225
ED_FEE431_00226
ED_FEE431_00227
ED_FEE431_00228
ED_FEE431_00229
ED_FEE431_00230
ED_FEE431_00231
ED_FEE431_00232
ED_FEE431_00233
ED_FEE431_00234
ED_FEE431_00235
ED_FEE431_00236
ED_FEE431_00237
ED_FEE431_00238
ED_FEE431_00239
ED_FEE431_00240
ED_FEE431_00241
ED_FEE431_00242
ED_FEE431_00243
ED_FEE431_00244
ED_FEE431_00245
ED_FEE431_00246
ED_FEE431_00247
ED_FEE431_00248
ED_FEE431_00249
ED_FEE431_00250
ED_FEE431_00251
ED_FEE431_00252
ED_FEE431_00253
ED_FEE431_00254
ED_FEE431_00255
ED_FEE431_00256
ED_FEE431_00257
ED_FEE431_00258
ED_FEE431_00259
ED_FEE431_00260
ED_FEE431_00261
ED_FEE431_00262
ED_FEE431_00263
ED_FEE431_00264
ED_FEE431_00265
ED_FEE431_00266
ED_FEE431_00267
ED_FEE431_00268
ED_FEE431_00269
ED_FEE431_00270
ED_FEE431_00271
ED_FEE431_00272
ED_FEE431_00273
ED_FEE431_00274
ED_FEE431_00275
ED_FEE431_00276
ED_FEE431_00277
ED_FEE431_00278
ED_FEE431_00279
ED_FEE431_00280
ED_FEE431_00281
ED_FEE431_00282
ED_FEE431_00283
ED_FEE431_00284
ED_FEE431_00285
ED_FEE431_00286
ED_FEE431_00287
ED_FEE431_00288
ED_FEE431_00289
ED_FEE431_00290
ED_FEE431_00291
ED_FEE431_00292
ED_FEE431_00293
ED_FEE431_00294
ED_FEE431_00295
ED_FEE431_00296
ED_FEE431_00297
ED_FEE431_00298
ED_FEE431_00299
ED_FEE431_00300
ED_FEE431_00301
ED_FEE431_00302
ED_FEE431_00303
ED_FEE431_00304
ED_FEE431_00305
ED_FEE431_00306
ED_FEE431_00307
ED_FEE431_00308
ED_FEE431_00309
ED_FEE431_00310
ED_FEE431_00311
ED_FEE431_00312
ED_FEE431_00313
ED_FEE431_00314
ED_FEE431_00315
ED_FEE431_00316
ED_FEE431_00317
ED_FEE431_00318
ED_FEE431_00319
ED_FEE431_00320
ED_FEE431_00321
ED_FEE431_00322
ED_FEE431_00323
ED_FEE431_00324
ED_FEE431_00325
ED_FEE431_00326
ED_FEE431_00327
ED_FEE431_00328
ED_FEE431_00329
ED_FEE431_00330
ED_FEE431_00331
ED_FEE431_00332
ED_FEE431_00333
ED_FEE431_00334
ED_FEE431_00335
ED_FEE431_00336
ED_FEE431_00337
ED_FEE431_00338
ED_FEE431_00339
ED_FEE431_00340
ED_FEE431_00341
ED_FEE431_00342
ED_FEE431_00343
ED_FEE431_00344
ED_FEE431_00345
ED_FEE431_00346
ED_FEE431_00347
ED_FEE431_00348
ED_FEE431_00349
ED_FEE431_00350
ED_FEE431_00351
ED_FEE431_00352
ED_FEE431_00353
ED_FEE431_00354
ED_FEE431_00355
ED_FEE431_00356
ED_FEE431_00357
ED_FEE431_00358
ED_FEE431_00359
ED_FEE431_00360
ED_FEE431_00361
ED_FEE431_00362
ED_FEE431_00363
ED_FEE431_00364
ED_FEE431_00365
ED_FEE431_00366
ED_FEE431_00367
ED_FEE431_00368
ED_FEE431_00369
ED_FEE431_00370
ED_FEE431_00371
ED_FEE431_00372
ED_FEE431_00373
ED_FEE431_00374
ED_FEE431_00375
ED_FEE431_00376
ED_FEE431_00377
ED_FEE431_00378
ED_FEE431_00379
ED_FEE431_00380
ED_FEE431_00381
ED_FEE431_00382
ED_FEE431_00383
ED_FEE431_00384
ED_FEE431_00385
ED_FEE431_00386
ED_FEE431_00387
ED_FEE431_00388
ED_FEE431_00389
ED_FEE431_00390
ED_FEE431_00391
ED_FEE431_00392
ED_FEE431_00393
ED_FEE431_00394
ED_FEE431_00395
ED_FEE431_00396
ED_FEE431_00397
ED_FEE431_00398
ED_FEE431_00399
ED_FEE431_00400
ED_FEE431_00401
ED_FEE431_00402
ED_FEE431_00403
ED_FEE431_00404
ED_FEE431_00405
ED_FEE431_00406
ED_FEE431_00407
ED_FEE431_00408
ED_FEE431_00409
ED_FEE431_00410
ED_FEE431_00411
ED_FEE431_00412
ED_FEE431_00413
ED_FEE431_00414
ED_FEE431_00415
ED_FEE431_00416
ED_FEE431_00417
ED_FEE431_00418
ED_FEE431_00419
ED_FEE431_00420
ED_FEE431_00421
ED_FEE431_00422
ED_FEE431_00423
ED_FEE431_00424
ED_FEE431_00425
ED_FEE431_00426
ED_FEE431_00427
ED_FEE431_00428
ED_FEE431_00429
ED_FEE431_00430
ED_FEE431_00431
ED_FEE431_00432
ED_FEE431_00433
ED_FEE431_00434
ED_FEE431_00435
ED_FEE431_00436
ED_FEE431_00437
ED_FEE431_00438
ED_FEE431_00439
ED_FEE431_00440
ED_FEE431_00441
ED_FEE431_00442
ED_FEE431_00443
ED_FEE431_00444
ED_FEE431_00445
ED_FEE431_00446
ED_FEE431_00447
ED_FEE431_00448
ED_FEE431_00449
ED_FEE431_00450
ED_FEE431_00451
ED_FEE431_00452
ED_FEE431_00453
ED_FEE431_00454
ED_FEE431_00455
ED_FEE431_00456
ED_FEE431_00457
ED_FEE431_00458
ED_FEE431_00459
ED_FEE431_00460
ED_FEE431_00461
ED_FEE431_00462
ED_FEE431_00463
ED_FEE431_00464
ED_FEE431_00465
ED_FEE431_00466
ED_FEE431_00467
ED_FEE431_00468
ED_FEE431_00469
ED_FEE431_00470
ED_FEE431_00471
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.4 Quoted services
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
4.4 ANCILLARY SERVICES - QUOTED SERVICES
4.4.1 - COST METRICS FOR QUOTED SERVICES
|  | EXPENDITURE ($0's) |  | VOLUMES (0's)
SERVICE | SERVICE SUBCATEGORY | 2019 |  | 2019
Quoted Services | Connection Services | 7717 | ED_QUO441_00001 | 55
| Metering Services | 0 | ED_QUO441_00002 | 0
| Ancillary Network Services | 1855846 | ED_QUO441_00003 | 680
ED_QUO441_00004
ED_QUO441_00005
ED_QUO441_00006
ED_QUO441_00007
ED_QUO441_00008
ED_QUO441_00009
ED_QUO441_00010
ED_QUO441_00011
ED_QUO441_00012
ED_QUO441_00013
ED_QUO441_00014
ED_QUO441_00015
ED_QUO441_00016
ED_QUO441_00017
ED_QUO441_00018
ED_QUO441_00019
ED_QUO441_00020
ED_QUO441_00021
ED_QUO441_00022
ED_QUO441_00023
ED_QUO441_00024
ED_QUO441_00025
ED_QUO441_00026
ED_QUO441_00027
ED_QUO441_00028
ED_QUO441_00029
ED_QUO441_00030
ED_QUO441_00031
ED_QUO441_00032
ED_QUO441_00033
ED_QUO441_00034
ED_QUO441_00035
ED_QUO441_00036
ED_QUO441_00037
ED_QUO441_00038
ED_QUO441_00039
ED_QUO441_00040
ED_QUO441_00041
ED_QUO441_00042
ED_QUO441_00043
ED_QUO441_00044
ED_QUO441_00045
ED_QUO441_00046
ED_QUO441_00047
ED_QUO441_00048
ED_QUO441_00049
ED_QUO441_00050
ED_QUO441_00051
ED_QUO441_00052
ED_QUO441_00053
ED_QUO441_00054
ED_QUO441_00055
ED_QUO441_00056
ED_QUO441_00057
ED_QUO441_00058
ED_QUO441_00059
ED_QUO441_00060
ED_QUO441_00061
ED_QUO441_00062
ED_QUO441_00063
ED_QUO441_00064
ED_QUO441_00065
ED_QUO441_00066
ED_QUO441_00067
ED_QUO441_00068
ED_QUO441_00069
ED_QUO441_00070
ED_QUO441_00071
ED_QUO441_00072
ED_QUO441_00073
ED_QUO441_00074
ED_QUO441_00075
ED_QUO441_00076
ED_QUO441_00077
ED_QUO441_00078
ED_QUO441_00079
ED_QUO441_00080
ED_QUO441_00081
ED_QUO441_00082
ED_QUO441_00083
ED_QUO441_00084
ED_QUO441_00085
ED_QUO441_00086
ED_QUO441_00087
ED_QUO441_00088
ED_QUO441_00089
ED_QUO441_00090
ED_QUO441_00091
ED_QUO441_00092
ED_QUO441_00093
ED_QUO441_00094
ED_QUO441_00095
ED_QUO441_00096
ED_QUO441_00097
ED_QUO441_00098
ED_QUO441_00099
ED_QUO441_00100
ED_QUO441_00101
ED_QUO441_00102
ED_QUO441_00103
ED_QUO441_00104
ED_QUO441_00105
ED_QUO441_00106
ED_QUO441_00107
ED_QUO441_00108
ED_QUO441_00109
ED_QUO441_00110
ED_QUO441_00111
ED_QUO441_00112
ED_QUO441_00113
ED_QUO441_00114
ED_QUO441_00115
ED_QUO441_00116
ED_QUO441_00117
ED_QUO441_00118
ED_QUO441_00119
ED_QUO441_00120
ED_QUO441_00121
ED_QUO441_00122
ED_QUO441_00123
ED_QUO441_00124
ED_QUO441_00125
ED_QUO441_00126
ED_QUO441_00127
ED_QUO441_00128
ED_QUO441_00129
ED_QUO441_00130
ED_QUO441_00131
ED_QUO441_00132
ED_QUO441_00133
ED_QUO441_00134
ED_QUO441_00135
ED_QUO441_00136
ED_QUO441_00137
ED_QUO441_00138
ED_QUO441_00139
ED_QUO441_00140
ED_QUO441_00141
ED_QUO441_00142
ED_QUO441_00143
ED_QUO441_00144
ED_QUO441_00145
ED_QUO441_00146
ED_QUO441_00147
ED_QUO441_00148
ED_QUO441_00149
ED_QUO441_00150
ED_QUO441_00151
ED_QUO441_00152
ED_QUO441_00153
ED_QUO441_00154
ED_QUO441_00155
ED_QUO441_00156
ED_QUO441_00157
ED_QUO441_00158
ED_QUO441_00159
ED_QUO441_00160
ED_QUO441_00161
ED_QUO441_00162
ED_QUO441_00163
ED_QUO441_00164
ED_QUO441_00165
ED_QUO441_00166
ED_QUO441_00167
ED_QUO441_00168
ED_QUO441_00169
ED_QUO441_00170
ED_QUO441_00171
ED_QUO441_00172
ED_QUO441_00173
ED_QUO441_00174
ED_QUO441_00175
ED_QUO441_00176
ED_QUO441_00177
ED_QUO441_00178
ED_QUO441_00179
ED_QUO441_00180
ED_QUO441_00181
ED_QUO441_00182
ED_QUO441_00183
ED_QUO441_00184
ED_QUO441_00185
ED_QUO441_00186
ED_QUO441_00187
ED_QUO441_00188
ED_QUO441_00189
ED_QUO441_00190
ED_QUO441_00191
ED_QUO441_00192
ED_QUO441_00193
ED_QUO441_00194
ED_QUO441_00195
ED_QUO441_00196
ED_QUO441_00197
ED_QUO441_00198
ED_QUO441_00199
ED_QUO441_00200
ED_QUO441_00201
ED_QUO441_00202
ED_QUO441_00203
ED_QUO441_00204
ED_QUO441_00205
ED_QUO441_00206
ED_QUO441_00207
ED_QUO441_00208
ED_QUO441_00209
ED_QUO441_00210
ED_QUO441_00211
ED_QUO441_00212
ED_QUO441_00213
ED_QUO441_00214
ED_QUO441_00215
ED_QUO441_00216
ED_QUO441_00217
ED_QUO441_00218
ED_QUO441_00219
ED_QUO441_00220
ED_QUO441_00221
ED_QUO441_00222
ED_QUO441_00223
ED_QUO441_00224
ED_QUO441_00225
ED_QUO441_00226
ED_QUO441_00227
ED_QUO441_00228
ED_QUO441_00229
ED_QUO441_00230
ED_QUO441_00231
ED_QUO441_00232
ED_QUO441_00233
ED_QUO441_00234
ED_QUO441_00235
ED_QUO441_00236
ED_QUO441_00237
ED_QUO441_00238
ED_QUO441_00239
ED_QUO441_00240
ED_QUO441_00241
ED_QUO441_00242
ED_QUO441_00243
ED_QUO441_00244
ED_QUO441_00245
ED_QUO441_00246
ED_QUO441_00247
ED_QUO441_00248
ED_QUO441_00249
ED_QUO441_00250
ED_QUO441_00251
ED_QUO441_00252
ED_QUO441_00253
ED_QUO441_00254
ED_QUO441_00255
ED_QUO441_00256
ED_QUO441_00257
ED_QUO441_00258
ED_QUO441_00259
ED_QUO441_00260
ED_QUO441_00261
ED_QUO441_00262
ED_QUO441_00263
ED_QUO441_00264
ED_QUO441_00265
ED_QUO441_00266
ED_QUO441_00267
ED_QUO441_00268
ED_QUO441_00269
ED_QUO441_00270
ED_QUO441_00271
ED_QUO441_00272
ED_QUO441_00273
ED_QUO441_00274
ED_QUO441_00275
ED_QUO441_00276
ED_QUO441_00277
ED_QUO441_00278
ED_QUO441_00279
ED_QUO441_00280
ED_QUO441_00281
ED_QUO441_00282
ED_QUO441_00283
ED_QUO441_00284
ED_QUO441_00285
ED_QUO441_00286
ED_QUO441_00287
ED_QUO441_00288
ED_QUO441_00289
ED_QUO441_00290
ED_QUO441_00291
ED_QUO441_00292
ED_QUO441_00293
ED_QUO441_00294
ED_QUO441_00295
ED_QUO441_00296
ED_QUO441_00297
ED_QUO441_00298
ED_QUO441_00299
ED_QUO441_00300
ED_QUO441_00301
ED_QUO441_00302
ED_QUO441_00303
ED_QUO441_00304
ED_QUO441_00305
ED_QUO441_00306
ED_QUO441_00307
ED_QUO441_00308
ED_QUO441_00309
ED_QUO441_00310
ED_QUO441_00311
ED_QUO441_00312
ED_QUO441_00313
ED_QUO441_00314
ED_QUO441_00315
ED_QUO441_00316
ED_QUO441_00317
ED_QUO441_00318
ED_QUO441_00319
ED_QUO441_00320
ED_QUO441_00321
ED_QUO441_00322
ED_QUO441_00323
ED_QUO441_00324
ED_QUO441_00325
ED_QUO441_00326
ED_QUO441_00327
ED_QUO441_00328
ED_QUO441_00329
ED_QUO441_00330
ED_QUO441_00331
ED_QUO441_00332
ED_QUO441_00333
ED_QUO441_00334
ED_QUO441_00335
ED_QUO441_00336
ED_QUO441_00337
ED_QUO441_00338
ED_QUO441_00339
ED_QUO441_00340
ED_QUO441_00341
ED_QUO441_00342
ED_QUO441_00343
ED_QUO441_00344
ED_QUO441_00345
ED_QUO441_00346
ED_QUO441_00347
ED_QUO441_00348
ED_QUO441_00349
ED_QUO441_00350
ED_QUO441_00351
ED_QUO441_00352
ED_QUO441_00353
ED_QUO441_00354
ED_QUO441_00355
ED_QUO441_00356
ED_QUO441_00357
ED_QUO441_00358
ED_QUO441_00359
ED_QUO441_00360
ED_QUO441_00361
ED_QUO441_00362
ED_QUO441_00363
ED_QUO441_00364
ED_QUO441_00365
ED_QUO441_00366
ED_QUO441_00367
ED_QUO441_00368
ED_QUO441_00369
ED_QUO441_00370
ED_QUO441_00371
ED_QUO441_00372
ED_QUO441_00373
ED_QUO441_00374
ED_QUO441_00375
ED_QUO441_00376
ED_QUO441_00377
ED_QUO441_00378
ED_QUO441_00379
ED_QUO441_00380
ED_QUO441_00381
ED_QUO441_00382
ED_QUO441_00383
ED_QUO441_00384
ED_QUO441_00385
ED_QUO441_00386
ED_QUO441_00387
ED_QUO441_00388
ED_QUO441_00389
ED_QUO441_00390
ED_QUO441_00391
ED_QUO441_00392
ED_QUO441_00393
ED_QUO441_00394
ED_QUO441_00395
ED_QUO441_00396
ED_QUO441_00397
ED_QUO441_00398
ED_QUO441_00399
ED_QUO441_00400
ED_QUO441_00401
ED_QUO441_00402
ED_QUO441_00403
ED_QUO441_00404
ED_QUO441_00405
ED_QUO441_00406
ED_QUO441_00407
ED_QUO441_00408
ED_QUO441_00409
ED_QUO441_00410
ED_QUO441_00411
ED_QUO441_00412
ED_QUO441_00413
ED_QUO441_00414
ED_QUO441_00415
ED_QUO441_00416
ED_QUO441_00417
ED_QUO441_00418
ED_QUO441_00419
ED_QUO441_00420
ED_QUO441_00421
ED_QUO441_00422
ED_QUO441_00423
ED_QUO441_00424
ED_QUO441_00425
ED_QUO441_00426
ED_QUO441_00427
ED_QUO441_00428
ED_QUO441_00429
ED_QUO441_00430
ED_QUO441_00431
ED_QUO441_00432
ED_QUO441_00433
ED_QUO441_00434
ED_QUO441_00435
ED_QUO441_00436
ED_QUO441_00437
ED_QUO441_00438
ED_QUO441_00439
ED_QUO441_00440
ED_QUO441_00441
ED_QUO441_00442
ED_QUO441_00443
ED_QUO441_00444
ED_QUO441_00445
ED_QUO441_00446
ED_QUO441_00447
ED_QUO441_00448
ED_QUO441_00449
ED_QUO441_00450
ED_QUO441_00451
ED_QUO441_00452
ED_QUO441_00453
ED_QUO441_00454
ED_QUO441_00455
ED_QUO441_00456
ED_QUO441_00457
ED_QUO441_00458
ED_QUO441_00459
ED_QUO441_00460
ED_QUO441_00461
ED_QUO441_00462
ED_QUO441_00463
ED_QUO441_00464
ED_QUO441_00465
ED_QUO441_00466
ED_QUO441_00467
ED_QUO441_00468
ED_QUO441_00469
ED_QUO441_00470
ED_QUO441_00471
ED_QUO441_00472
ED_QUO441_00473
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.2 Asset Age Profile
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
5.2 ASSET AGE PROFILE
There is ONE table on this worksheet. Both the ROWS and COLUMNS have been 'grouped' for easy navigation. See the Instructions sheet on how to group or ungroup data.
5.2.1 - ASSET AGE PROFILE
|  | ECONOMIC LIFE (YEARS) |  | INSTALLED ASSETS -˃ QUANTITY CURRENTLY IN COMMISSION BY YEAR
ASSET GROUP | ASSET CATEGORY | MEAN | STANDARD DEVIATION | 2019 | 2018 | 2017 | 2016 | 2015 | 2014 | 2013 | 2012 | 2011 | 2010 | 2009 | 2008 | 2007 | 2006 | 2005 | 2004 | 2003 | 2002 | 2001 | 2000 | 1999 | 1998 | 1997 | 1996 | 1995 | 1994 | 1993 | 1992 | 1991 | 1990 | 1989 | 1988 | 1987 | 1986 | 1985 | 1984 | 1983 | 1982 | 1981 | 1980 | 1979 | 1978 | 1977 | 1976 | 1975 | 1974 | 1973 | 1972 | 1971 | 1970 | 1969 | 1968 | 1967 | 1966 | 1965 | 1964 | 1963 | 1962 | 1961 | 1960 | 1959 | 1958 | 1957 | 1956 | 1955 | 1954 | 1953 | 1952 | 1951 | 1950 | 1949 | 1948 | 1947 | 1946 | 1945 | 1944 | 1943 | 1942 | 1941 | 1940 | 1939 | 1938 | 1937 | 1936 | 1935 | 1934 | 1933 | 1932 | 1931 | 1930 | 1929 | 1928 | 1927 | 1926 | 1925 | 1924 | 1923 | 1922 | 1921 | 1920 | 1919 | 1918 | 1917 | 1916 | 1915 | 1914 | 1913 | 1912 | 1911
POLES BY: HIGHEST OPERATING VOLTAGE ; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole | 20 | 4.47 | 890 | 1410 | 1024 | 637 | 1018 | 868 | 770 | 307 | 399 | 285 | 310 | 482 | 545 | 419 | 475 | 630 | 383 | 405 | 414 | 499 | 526 | 745 | 613 | 289 | 200 | 232 | 626 | 703 | 533 | 1032 | 508 | 3 | 20 | 307 | 1 | 1 | 1 | 2 | 1 | 3 | 4 | 3 | 4 | 2 | 10 | 10 | 4 | 7 | 4 | 11 | 6 | 1 | 9 | 5 | 5 | 8 | 3 | 5 | 7 | 13 | 3 | 3 | 4 | 3 | 1 | 4 | 0 | 2 | 1 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Wood | 60 | 7.75 | 522 | 484 | 500 | 486 | 546 | 394 | 418 | 402 | 278 | 454 | 432 | 307 | 273 | 269 | 304 | 575 | 865 | 370 | 462 | 320 | 479 | 264 | 576 | 45 | 22 | 21 | 70 | 81 | 81 | 144 | 412 | 583 | 511 | 1127 | 808 | 1042 | 1090 | 1376 | 1433 | 1711 | 1138 | 1151 | 805 | 1213 | 1548 | 1470 | 1879 | 2309 | 1877 | 1988 | 2165 | 2276 | 2262 | 1403 | 1890 | 1566 | 1177 | 1180 | 1015 | 1079 | 922 | 693 | 508 | 246 | 192 | 240 | 145 | 118 | 89 | 506 | 130 | 121 | 145 | 107 | 41 | 22 | 54 | 112 | 308 | 356 | 367 | 427 | 389 | 264 | 426 | 373 | 260 | 77 | 24 | 33 | 36 | 38 | 36 | 2 | 0 | 3 | 1 | 11 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 0
| > 1 kV & < = 11 kV; Wood | 60 | 7.75 | 198 | 171 | 172 | 297 | 299 | 234 | 265 | 311 | 185 | 259 | 260 | 170 | 185 | 186 | 123 | 130 | 141 | 135 | 175 | 122 | 170 | 110 | 125 | 89 | 83 | 173 | 191 | 87 | 218 | 370 | 198 | 256 | 232 | 430 | 293 | 258 | 203 | 327 | 273 | 261 | 241 | 204 | 159 | 159 | 185 | 215 | 262 | 290 | 187 | 280 | 352 | 452 | 341 | 336 | 400 | 294 | 200 | 229 | 211 | 129 | 126 | 114 | 34 | 22 | 30 | 41 | 40 | 10 | 16 | 100 | 10 | 11 | 7 | 7 | 6 | 7 | 10 | 51 | 62 | 81 | 63 | 132 | 47 | 41 | 65 | 82 | 54 | 20 | 4 | 18 | 13 | 9 | 3 | 1 | 0 | 1 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Wood | 60 | 7.75 | 497 | 355 | 439 | 603 | 645 | 489 | 491 | 422 | 463 | 630 | 737 | 522 | 503 | 485 | 496 | 397 | 483 | 380 | 530 | 470 | 446 | 239 | 323 | 137 | 110 | 147 | 285 | 245 | 324 | 456 | 509 | 702 | 517 | 1032 | 1031 | 819 | 986 | 789 | 935 | 890 | 532 | 691 | 933 | 1110 | 887 | 1052 | 912 | 932 | 1052 | 951 | 1278 | 941 | 1008 | 977 | 1204 | 917 | 599 | 418 | 433 | 409 | 368 | 344 | 233 | 105 | 62 | 69 | 68 | 137 | 40 | 263 | 81 | 71 | 36 | 22 | 16 | 20 | 14 | 49 | 38 | 227 | 57 | 169 | 205 | 41 | 110 | 29 | 30 | 17 | 2 | 5 | 19 | 6 | 22 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; Wood | 60 | 7.75 | 51 | 116 | 100 | 62 | 96 | 190 | 72 | 171 | 86 | 127 | 161 | 76 | 156 | 105 | 160 | 106 | 107 | 156 | 192 | 210 | 65 | 78 | 47 | 58 | 73 | 26 | 82 | 32 | 62 | 115 | 67 | 81 | 43 | 144 | 95 | 211 | 356 | 242 | 196 | 88 | 56 | 77 | 126 | 309 | 112 | 64 | 53 | 85 | 88 | 180 | 367 | 299 | 298 | 207 | 438 | 236 | 213 | 38 | 89 | 23 | 16 | 12 | 31 | 57 | 36 | 31 | 16 | 35 | 6 | 7 | 23 | 3 | 3 | 1 | 0 | 2 | 2 | 6 | 6 | 4 | 2 | 3 | 8 | 2 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Concrete | 70 | 8.37 | 3 | 2 | 3 | 3 | 2 | 5 | 7 | 7 | 5 | 12 | 10 | 4 | 3 | 4 | 1 | 2 | 4 | 6 | 7 | 11 | 71 | 38 | 154 | 131 | 357 | 730 | 1212 | 1074 | 766 | 995 | 1139 | 1528 | 1093 | 956 | 1099 | 578 | 199 | 106 | 179 | 375 | 14 | 457 | 511 | 180 | 106 | 16 | 461 | 256 | 9 | 4 | 3 | 2 | 2 | 1 | 0 | 5 | 2 | 4 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; Concrete | 70 | 8.37 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 3 | 26 | 9 | 10 | 23 | 33 | 30 | 20 | 14 | 42 | 25 | 72 | 37 | 33 | 40 | 34 | 22 | 18 | 30 | 40 | 2 | 34 | 7 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Concrete | 70 | 8.37 | 1 | 0 | 0 | 2 | 3 | 1 | 2 | 1 | 3 | 6 | 2 | 2 | 0 | 2 | 4 | 2 | 3 | 1 | 3 | 1 | 29 | 35 | 71 | 76 | 239 | 297 | 401 | 577 | 358 | 719 | 892 | 889 | 780 | 581 | 821 | 439 | 114 | 117 | 235 | 198 | 5 | 319 | 281 | 80 | 34 | 2 | 7 | 19 | 2 | 2 | 0 | 1 | 1 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; Concrete | 70 | 8.37 | 0 | 1 | 6 | 0 | 1 | 3 | 1 | 2 | 1 | 15 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 1 | 0 | 0 | 2 | 10 | 10 | 69 | 71 | 81 | 52 | 45 | 51 | 65 | 52 | 30 | 20 | 58 | 208 | 51 | 30 | 79 | 17 | 0 | 26 | 14 | 1 | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; Steel | 40 | 6.32 | 9 | 7 | 5 | 8 | 17 | 8 | 14 | 54 | 13 | 11 | 9 | 3 | 32 | 1 | 5 | 3 | 1 | 17 | 2 | 7 | 7 | 6 | 2 | 5 | 3 | 2 | 1 | 3 | 4 | 9 | 4 | 10 | 5 | 12 | 8 | 10 | 7 | 5 | 8 | 14 | 4 | 7 | 7 | 3 | 12 | 4 | 8 | 12 | 2 | 8 | 0 | 4 | 1 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; Steel | 40 | 6.32 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Steel | 40 | 6.32 | 1 | 1 | 0 | 0 | 3 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; Steel | 40 | 6.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; Steel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; Steel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV | 53.33 | 7.3 | 2597 | 7056 | 4495 | 9339 | 13988 | 20846 | 27491 | 22420 | 18886 | 19371 | 20174 | 15946 | 25124 | 32322 | 15626 | 9101 | 11731 | 17993 | 13167 | 32596 | 13877 | 17233 | 48147 | 108235 | 68891 | 20259 | 32652 | 31418 | 39328 | 62986 | 69806 | 111234 | 97678 | 129971 | 148910 | 146717 | 153573 | 151861 | 165742 | 173762 | 156756 | 151177 | 143394 | 142930 | 122996 | 105109 | 108862 | 125082 | 112999 | 474799 | 140018 | 136913 | 140871 | 108296 | 151063 | 124909 | 95610 | 86911 | 85490 | 83836 | 72364 | 64399 | 47219 | 26109 | 19635 | 26593 | 20079 | 19241 | 12566 | 60597 | 16620 | 14772 | 12410 | 12137 | 4675 | 2451 | 4959 | 15603 | 22963 | 32388 | 32769 | 47388 | 38733 | 27443 | 40552 | 40174 | 28746 | 9971 | 2574 | 4585 | 6307 | 4500 | 5603 | 634 | 229 | 106 | 159 | 1921 | 131 | 630 | 173 | 177 | 196 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | 51.67 | 7.19 | 1209 | 976 | 1148 | 4763 | 2566 | 1294 | 2649 | 9144 | 3663 | 5996 | 5216 | 3500 | 2169 | 939 | 875 | 2119 | 319 | 958 | 862 | 1565 | 3725 | 3223 | 250 | 378 | 950 | 1578 | 1617 | 1028 | 3134 | 7079 | 5416 | 16531 | 12567 | 19575 | 20416 | 18601 | 14942 | 19853 | 25298 | 24985 | 31938 | 33484 | 30928 | 31105 | 13887 | 19839 | 16470 | 9315 | 9427 | 55297 | 7009 | 8784 | 8184 | 4977 | 5758 | 9317 | 8505 | 6643 | 6163 | 5903 | 4043 | 3724 | 520 | 1626 | 1528 | 1854 | 1406 | 203 | 1865 | 12518 | 424 | 696 | 337 | 1971 | 293 | 248 | 522 | 3074 | 3408 | 3283 | 3872 | 7990 | 4971 | 3431 | 7380 | 5621 | 3015 | 1730 | 209 | 610 | 1237 | 287 | 704 | 448 | 0 | 193 | 0 | 742 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; SWER | 60 | 7.75 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 105 | 775 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1785 | 843 | 2759 | 2950 | 0 | 3723 | 4572 | 11210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 324 | 1683 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Single-Phase | 60 | 7.75 | 1477 | 0 | 0 | 281 | 0 | 0 | 1146 | 38 | 1072 | 0 | 125 | 729 | 456 | 371 | 181 | 0 | 0 | 138 | 201 | 2166 | 1240 | 1989 | 594 | 475 | 3302 | 3031 | 2499 | 2499 | 4641 | 7115 | 12101 | 18343 | 10984 | 22981 | 9820 | 7244 | 16695 | 12563 | 14726 | 8741 | 7989 | 5215 | 8990 | 4329 | 1899 | 3242 | 619 | 1674 | 2490 | 18688 | 515 | 0 | 0 | 0 | 1380 | 734 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 627 | 1472 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 17 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Multiple-Phase | 47.5 | 6.89 | 9103 | 11132 | 34124 | 35212 | 17999 | 7407 | 15165 | 9879 | 21135 | 15377 | 32620 | 18886 | 7781 | 6854 | 10074 | 2869 | 3800 | 5921 | 8845 | 18966 | 10134 | 30560 | 11110 | 13184 | 15226 | 21408 | 34598 | 28095 | 43350 | 59403 | 69857 | 87807 | 79902 | 142310 | 131945 | 160413 | 161836 | 146137 | 129046 | 97779 | 101328 | 91176 | 69187 | 57183 | 43140 | 28504 | 17359 | 17952 | 8507 | 298746 | 10455 | 11948 | 12620 | 7552 | 7741 | 8538 | 5821 | 5985 | 10445 | 5932 | 6393 | 7590 | 1597 | 8161 | 3057 | 2571 | 1705 | 4786 | 1707 | 20062 | 2211 | 3537 | 2115 | 1413 | 193 | 0 | 391 | 345 | 221 | 2019 | 975 | 3132 | 2142 | 1675 | 7103 | 4443 | 891 | 975 | 234 | 896 | 788 | 0 | 1097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31
| > 22 kV & < = 66 kV | 60 | 7.75 | 0 | 5349 | 2321 | 0 | 533 | 43074 | 0 | 4297 | 4970 | 5983 | 9636 | 0 | 4578 | 1497 | 2198 | 0 | 232 | 0 | 0 | 6756 | 14547 | 189 | 0 | 0 | 0 | 407 | 0 | 787 | 484 | 3029 | 6192 | 7563 | 10292 | 15580 | 11590 | 19726 | 36392 | 29208 | 23302 | 35936 | 20851 | 30377 | 28978 | 14193 | 12046 | 11498 | 17091 | 48634 | 2244 | 35017 | 3374 | 8521 | 6381 | 577 | 149 | 3751 | 8112 | 1693 | 1178 | 0 | 528 | 0 | 5257 | 176 | 0 | 0 | 0 | 0 | 0 | 4690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1219 | 0 | 135 | 0 | 0 | 0 | 0 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV | 70 | 8.37 | 30875 | 36487 | 32659 | 40114 | 33470 | 36792 | 41180 | 49850 | 68682 | 52510 | 58842 | 71195 | 68563 | 68282 | 67539 | 69233 | 76941 | 87265 | 59632 | 99890 | 107771 | 130214 | 58651 | 37277 | 69199 | 68324 | 40181 | 30935 | 38274 | 71458 | 66744 | 55725 | 71552 | 67500 | 53324 | 67569 | 65039 | 42323 | 30511 | 35904 | 27662 | 42442 | 58906 | 56468 | 31987 | 44497 | 21531 | 14138 | 12716 | 2658 | 801 | 579 | 1804 | 660 | 428 | 418 | 86 | 519 | 250 | 540 | 91 | 100 | 0 | 0 | 110 | 205 | 9 | 0 | 0 | 315 | 137 | 49 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | 55 | 7.42 | 5246 | 3026 | 7893 | 10359 | 13230 | 7810 | 9422 | 8774 | 8059 | 8897 | 7724 | 4718 | 4645 | 8610 | 18233 | 2600 | 3302 | 2716 | 2889 | 2003 | 2599 | 1535 | 2431 | 1296 | 104 | 540 | 1522 | 882 | 909 | 875 | 1599 | 1806 | 907 | 300 | 4391 | 3647 | 1513 | 1483 | 2340 | 889 | 666 | 732 | 454 | 307 | 1051 | 488 | 1500 | 1028 | 1377 | 213 | 4133 | 3245 | 2822 | 1436 | 2370 | 2467 | 2165 | 5544 | 3510 | 3987 | 3568 | 4856 | 0 | 162 | 1275 | 0 | 0 | 0 | 61 | 376 | 521 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 324 | 1038 | 25 | 0 | 0 | 52 | 0 | 823 | 1569 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV | 55 | 7.42 | 16035 | 21003 | 22078 | 28933 | 32501 | 33138 | 24403 | 31744 | 23332 | 28564 | 26498 | 28969 | 30641 | 38612 | 49646 | 30030 | 24927 | 28199 | 26534 | 23319 | 27804 | 13325 | 10804 | 5668 | 4284 | 3641 | 1377 | 3830 | 2411 | 4672 | 10272 | 10739 | 9611 | 9658 | 4958 | 3578 | 17996 | 2373 | 3068 | 5777 | 4167 | 15670 | 14123 | 23628 | 18700 | 4446 | 10865 | 9863 | 9853 | 6120 | 5291 | 3951 | 3058 | 8300 | 5566 | 5252 | 5101 | 2973 | 2748 | 6782 | 5221 | 339 | 2530 | 2771 | 1042 | 50 | 0 | 141 | 152 | 1921 | 3797 | 1784 | 1727 | 294 | 2768 | 144 | 0 | 0 | 333 | 404 | 308 | 0 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV | 40 | 6.32 | 175 | 0 | 110 | 214 | 0 | 0 | 0 | 362 | 0 | 345 | 753 | 263 | 158 | 0 | 0 | 0 | 742 | 0 | 343 | 0 | 33 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 4530 | 5422 | 5147 | 5207 | 5836 | 4797 | 4200 | 4293 | 4835 | 4536 | 4567 | 4656 | 4287 | 4530 | 4245 | 4628 | 4003 | 4547 | 3856 | 5015 | 4866 | 4912 | 3070 | 2499 | 3291 | 2908 | 2172 | 1788 | 1523 | 2738 | 2558 | 2492 | 2037 | 2289 | 1493 | 1511 | 1687 | 799 | 675 | 696 | 710 | 1177 | 1200 | 1526 | 808 | 1036 | 528 | 316 | 331 | 147 | 55 | 93 | 69 | 83 | 77 | 57 | 63 | 55 | 49 | 67 | 63 | 30 | 6 | 14 | 12 | 3 | 2 | 2 | 2 | 9 | 6 | 0 | 0 | 1 | 3 | 3 | 0 | 0 | 8 | 9 | 0 | 1 | 2 | 1 | 0 | 5 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type | 40 | 6.32 | 7360 | 7267 | 5005 | 3361 | 8698 | 34274 | 37818 | 36854 | 22445 | 18103 | 7197 | 6924 | 5063 | 4490 | 2578 | 3718 | 3494 | 1174 | 1015 | 907 | 966 | 886 | 3102 | 579 | 668 | 902 | 1976 | 1389 | 1230 | 2096 | 1912 | 2325 | 1828 | 2711 | 2353 | 1527 | 1310 | 1260 | 1326 | 1523 | 971 | 1598 | 1562 | 1216 | 1383 | 1268 | 1946 | 1946 | 1515 | 1889 | 2057 | 1899 | 1806 | 1295 | 1968 | 1674 | 1095 | 1065 | 976 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Commercial & Industrial ; Simple Type | 40 | 6.32 | 634 | 630 | 392 | 355 | 520 | 1697 | 2065 | 1537 | 995 | 751 | 488 | 434 | 391 | 334 | 241 | 306 | 324 | 172 | 464 | 609 | 341 | 172 | 1761 | 247 | 192 | 158 | 275 | 184 | 186 | 324 | 388 | 424 | 287 | 361 | 279 | 234 | 183 | 242 | 228 | 249 | 137 | 203 | 288 | 209 | 134 | 209 | 193 | 243 | 169 | 484 | 224 | 180 | 210 | 181 | 197 | 152 | 110 | 84 | 118 | 105 | 51 | 50 | 38 | 17 | 28 | 19 | 18 | 9 | 10 | 48 | 11 | (179) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Residential ; Complex Type | 40 | 6.32 | 560 | 558 | 355 | 323 | 383 | 1230 | 1532 | 2405 | 1022 | 700 | 309 | 334 | 367 | 302 | 190 | 325 | 397 | 145 | 128 | 181 | 133 | 117 | 3865 | 274 | 53 | 105 | 108 | 139 | 131 | 157 | 154 | 187 | 196 | 236 | 200 | 175 | 156 | 205 | 160 | 202 | 92 | 140 | 91 | 122 | 121 | 117 | 120 | 129 | 89 | 331 | 124 | 117 | 131 | 138 | 151 | 168 | 104 | 150 | 87 | 96 | (107) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type | 40 | 6.32 | 138 | 139 | 87 | 59 | 78 | 153 | 247 | 191 | 145 | 132 | 82 | 64 | 91 | 52 | 56 | 53 | 68 | 67 | 106 | 208 | 141 | 98 | 938 | 74 | 44 | 30 | 50 | 46 | 40 | 76 | 61 | 70 | 57 | 88 | 69 | 57 | 38 | 57 | 66 | 65 | 29 | 39 | 48 | 59 | 26 | 40 | 34 | 35 | 45 | 242 | 17 | 37 | 27 | 32 | 31 | 30 | 22 | 16 | 38 | (18) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Subdivision ; Complex Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 50 | 7.07 | 18 | 26 | 31 | 16 | 18 | 18 | 22 | 34 | 27 | 27 | 26 | 17 | 2 | 28 | 17 | 16 | 16 | 19 | 22 | 31 | 14 | 13 | 12 | 16 | 20 | 12 | 16 | 16 | 18 | 57 | 59 | 67 | 64 | 71 | 85 | 51 | 29 | 32 | 29 | 26 | 29 | 22 | 16 | 19 | 6 | 1 | 5 | 10 | 10 | 7 | 4 | 4 | 1 | 2 | 4 | 1 | 2 | 1 | 5 | 1 | 3 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 50 | 7.07 | 0 | 0 | 1 | 9 | 1 | 1 | 1 | 2 | 2 | 0 | 0 | 2 | 1 | 0 | 3 | 1 | 0 | 2 | 0 | 3 | 1 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 50 | 7.07 | 9 | 9 | 10 | 6 | 10 | 6 | 10 | 3 | 7 | 4 | 8 | 3 | 0 | 13 | 11 | 3 | 7 | 9 | 18 | 22 | 27 | 16 | 8 | 14 | 22 | 26 | 12 | 6 | 12 | 32 | 36 | 16 | 17 | 30 | 21 | 21 | 8 | 7 | 13 | 10 | 11 | 5 | 11 | 12 | 5 | 5 | 5 | 3 | 6 | 6 | 3 | 8 | 2 | 2 | 1 | 2 | 3 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 50 | 7.07 | 201 | 194 | 164 | 231 | 284 | 258 | 288 | 305 | 211 | 229 | 617 | 291 | 264 | 258 | 109 | 187 | 190 | 188 | 201 | 114 | 92 | 58 | 43 | 34 | 45 | 53 | 62 | 57 | 70 | 138 | 130 | 154 | 130 | 131 | 106 | 69 | 69 | 79 | 75 | 67 | 77 | 96 | 117 | 116 | 57 | 47 | 60 | 45 | 48 | 65 | 18 | 37 | 48 | 30 | 24 | 27 | 16 | 16 | 12 | 22 | 7 | 5 | 2 | 4 | 4 | 2 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 50 | 7.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 50 | 7.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 50 | 7.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 50 | 7.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 50 | 7.07 | 57 | 70 | 68 | 74 | 61 | 61 | 63 | 67 | 57 | 55 | 98 | 56 | 65 | 66 | 60 | 48 | 58 | 65 | 40 | 46 | 35 | 27 | 33 | 19 | 22 | 25 | 16 | 25 | 22 | 37 | 38 | 41 | 29 | 30 | 20 | 20 | 10 | 13 | 9 | 7 | 16 | 35 | 15 | 11 | 8 | 5 | 4 | 0 | 1 | 5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 50 | 7.07 | 26 | 42 | 26 | 50 | 26 | 21 | 31 | 41 | 36 | 30 | 26 | 43 | 38 | 37 | 29 | 30 | 11 | 12 | 17 | 13 | 4 | 9 | 2 | 1 | 4 | 7 | 1 | 3 | 3 | 6 | 2 | 1 | 5 | 0 | 2 | 2 | 0 | 3 | 0 | 0 | 1 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 50 | 7.07 | 13 | 13 | 15 | 9 | 9 | 6 | 8 | 11 | 7 | 10 | 4 | 1 | 3 | 0 | 0 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 0 | 4 | 1 | 2 | 5 | 1 | 5 | 4 | 2 | 6 | 3 | 6 | 8 | 10 | 1 | 1 | 5 | 2 | 1 | 2 | 3 | 6 | 6 | 8 | 6 | 3 | 2 | 2 | 1 | 8 | 2 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase | 50 | 7.07 | 4 | 6 | 8 | 10 | 19 | 9 | 5 | 17 | 7 | 11 | 14 | 15 | 12 | 17 | 4 | 4 | 5 | 6 | 5 | 2 | 1 | 17 | 0 | 1 | 7 | 6 | 3 | 0 | 7 | 9 | 7 | 6 | 12 | 5 | 3 | 2 | 3 | 2 | 0 | 7 | 3 | 3 | 1 | 1 | 6 | 2 | 1 | 3 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA | 50.83 | 7.13 | 31 | 19 | 29 | 23 | 22 | 14 | 22 | 27 | 13 | 17 | 22 | 18 | 15 | 13 | 20 | 14 | 17 | 15 | 20 | 22 | 26 | 28 | 18 | 10 | 25 | 50 | 24 | 34 | 40 | 85 | 79 | 71 | 57 | 46 | 27 | 41 | 24 | 32 | 32 | 25 | 36 | 29 | 28 | 19 | 16 | 14 | 16 | 10 | 6 | 16 | 6 | 5 | 7 | 6 | 6 | 5 | 8 | 6 | 3 | 2 | 2 | 0 | 1 | 2 | 1 | 0 | 0 | 1 | 3 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA | 55 | 7.42 | 1 | 1 | 3 | 3 | 0 | 2 | 2 | 4 | 3 | 2 | 4 | 1 | 3 | 2 | 3 | 2 | 2 | 2 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 0 | 4 | 0 | 2 | 0 | 0 | 3 | 2 | 0 | 0 | 2 | 0 | 1 | 8 | 1 | 9 | 3 | 3 | 3 | 10 | 3 | 4 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION | ˂ = 11 kV ; Fuse | 30 | 5.48 | 28 | 27 | 45 | 56 | 46 | 80 | 64 | 101 | 81 | 89 | 96 | 73 | 70 | 47 | 39 | 39 | 49 | 61 | 35 | 22 | 26 | 32 | 15 | 46 | 16 | 26 | 29 | 15 | 17 | 43 | 26 | 62 | 43 | 40 | 42 | 30 | 14 | 15 | 17 | 38 | 6 | 21 | 13 | 7 | 11 | 11 | 15 | 18 | 11 | 16 | 17 | 13 | 23 | 17 | 34 | 15 | 9 | 16 | 13 | 7 | 12 | 4 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Switch | 35 | 5.92 | 858 | 791 | 979 | 1448 | 1439 | 1714 | 1654 | 1686 | 1396 | 1543 | 2517 | 1359 | 1259 | 1362 | 1287 | 3979 | 1751 | 5643 | 4728 | 2167 | 767 | 668 | 528 | 1229 | 763 | 732 | 959 | 1039 | 789 | 1518 | 1472 | 1492 | 1333 | 1569 | 1369 | 1124 | 641 | 956 | 681 | 857 | 446 | 651 | 531 | 517 | 490 | 565 | 696 | 647 | 586 | 1115 | 723 | 664 | 685 | 501 | 706 | 605 | 383 | 336 | 315 | 373 | 269 | 207 | 146 | 59 | 46 | 71 | 34 | 52 | 25 | 201 | 36 | 25 | 27 | 23 | 14 | 5 | 11 | 40 | 76 | 103 | 59 | 127 | 98 | 57 | 79 | 83 | 50 | 18 | 4 | 9 | 14 | 4 | 17 | 1 | 0 | 0 | 0 | 4 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Circuit Breaker | 44.98 | 6.71 | 5 | 0 | 38 | 18 | 21 | 12 | 38 | 26 | 6 | 7 | 17 | 6 | 17 | 25 | 12 | 24 | 0 | 4 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 15 | 0 | 0 | 0 | 32 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Switch | 34 | 5.83 | 483 | 449 | 334 | 660 | 521 | 623 | 659 | 504 | 635 | 649 | 720 | 528 | 448 | 445 | 497 | 447 | 462 | 451 | 455 | 532 | 261 | 217 | 175 | 612 | 1048 | 272 | 169 | 209 | 161 | 356 | 426 | 471 | 347 | 402 | 489 | 344 | 205 | 189 | 242 | 215 | 82 | 212 | 217 | 219 | 123 | 153 | 146 | 161 | 183 | 191 | 161 | 127 | 128 | 119 | 140 | 81 | 84 | 62 | 55 | 56 | 39 | 31 | 20 | 13 | 7 | 3 | 5 | 11 | 4 | 50 | 3 | 5 | 5 | 1 | 3 | 1 | 2 | 1 | 1 | 18 | 2 | 13 | 6 | 1 | 3 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Circuit Breaker | 44.99 | 6.71 | 20 | 6 | 22 | 15 | 20 | 32 | 50 | 39 | 2 | 6 | 36 | 11 | 26 | 40 | 52 | 12 | 15 | 20 | 19 | 5 | 12 | 5 | 1 | 4 | 8 | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 2 | 15 | 3 | 0 | 16 | 8 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 16 | 1 | 4 | 32 | 9 | 0 | 17 | 9 | 13 | 0 | 0 | 0 | 0 | 7 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Circuit Breaker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Switch | 45 | 6.71 | 1 | 2 | 9 | 2 | 4 | 19 | 9 | 20 | 2 | 2 | 6 | 2 | 8 | 7 | 18 | 12 | 3 | 6 | 2 | 0 | 5 | 0 | 0 | 52 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker | 45 | 6.71 | 1 | 0 | 4 | 0 | 1 | 7 | 5 | 8 | 0 | 7 | 8 | 2 | 6 | 2 | 5 | 4 | 5 | 4 | 3 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 3 | 4 | 3 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Circuit Breaker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Circuit Breaker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 96 | 16 | 42 | 41 | 47 | 102 | 85 | 69 | 3 | 55 | 65 | 1 | 58 | 38 | 423 | 64 | 80 | 167 | 369 | 738 | 974 | 393 | 0 | 35 | 0 | 0 | 1 | 93 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PUBLIC LIGHTING BY: ASSET TYPE ; LIGHTING OBLIGATION | Luminaires ; Major Road | 20 | 4.47 | 2520 | 2513 | 1327 | 563 | 2046 | 410 | 160 | 172 | 204 | 484 | 204 | 203 | 148 | 194 | 570 | 581 | 243 | 366 | 1416 | 336 | 363 | 131 | 342 | 1389 | 2542 | 127 | 1830 | 1027 | 38 | 133 | 33 | 33 | 154 | 136 | 248 | 217 | 230 | 238 | 254 | 232 | 223 | 231 | 229 | 239 | 214 | 206 | 234 | 251 | 298 | 373 | 270 | 326 | 326 | 307 | 279 | 0 | 0 | 0 | 0 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Luminaires ; Minor Road | 20 | 4.47 | 17026 | 17823 | 12025 | 9863 | 11570 | 1439 | 234 | 293 | 500 | 6455 | 873 | 411 | 340 | 335 | 599 | 948 | 551 | 700 | 1124 | 491 | 614 | 235 | 375 | 802 | 1812 | 127 | 847 | 521 | 61 | 164 | 60 | 53 | 127 | 108 | 174 | 152 | 178 | 158 | 163 | 153 | 156 | 167 | 166 | 152 | 155 | 144 | 176 | 143 | 225 | 250 | 202 | 221 | 230 | 203 | 216 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brackets ; Major Road | 20 | 4.47 | 2520 | 2513 | 1327 | 563 | 2046 | 410 | 160 | 172 | 204 | 484 | 204 | 203 | 148 | 194 | 570 | 581 | 243 | 366 | 1416 | 336 | 363 | 131 | 342 | 1389 | 2542 | 127 | 1830 | 1027 | 38 | 133 | 33 | 33 | 154 | 136 | 248 | 217 | 230 | 238 | 254 | 232 | 223 | 231 | 229 | 239 | 214 | 206 | 234 | 251 | 298 | 373 | 270 | 326 | 326 | 307 | 279 | 0 | 0 | 0 | 0 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brackets ; Minor Road | 20 | 4.47 | 17026 | 17823 | 12025 | 9863 | 11570 | 1439 | 234 | 293 | 500 | 6455 | 873 | 411 | 340 | 335 | 599 | 948 | 551 | 700 | 1124 | 491 | 614 | 235 | 375 | 802 | 1812 | 127 | 847 | 521 | 61 | 164 | 60 | 53 | 127 | 108 | 174 | 152 | 178 | 158 | 163 | 153 | 156 | 167 | 166 | 152 | 155 | 144 | 176 | 143 | 225 | 250 | 202 | 221 | 230 | 203 | 216 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lamps ; Major Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lamps ; Minor Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poles / Columns ; Major Road | 50 | 7.07 | 94 | 99 | 88 | 255 | 139 | 164 | 166 | 201 | 225 | 276 | 194 | 157 | 277 | 164 | 148 | 208 | 188 | 267 | 301 | 379 | 236 | 165 | 121 | 210 | 132 | 140 | 107 | 170 | 139 | 168 | 180 | 210 | 104 | 212 | 153 | 149 | 142 | 84 | 169 | 206 | 31 | 74 | 91 | 57 | 12 | 36 | 60 | 96 | 48 | 47 | 24 | 19 | 36 | 30 | 47 | 23 | 30 | 22 | 22 | 6 | 5 | 9 | 1 | 2 | 2 | 0 | 2 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poles / Columns ; Minor Road | 50 | 7.07 | 411 | 461 | 554 | 468 | 327 | 567 | 430 | 387 | 569 | 1056 | 1076 | 882 | 994 | 642 | 913 | 1124 | 1237 | 1212 | 568 | 1811 | 1780 | 737 | 602 | 470 | 302 | 838 | 687 | 384 | 302 | 687 | 986 | 1041 | 417 | 542 | 661 | 289 | 47 | 73 | 95 | 115 | 34 | 73 | 77 | 54 | 44 | 29 | 52 | 47 | 48 | 39 | 28 | 23 | 44 | 22 | 18 | 36 | 14 | 7 | 45 | 5 | 5 | 6 | 1 | 6 | 1 | 8 | 1 | 0 | 0 | 9 | 0 | 1 | 2 | 1 | 0 | 1 | 0 | 0 | 1 | 6 | 2 | 1 | 2 | 2 | 2 | 1 | 10 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices | 25 | 5 | 86 | 144 | 165 | 56 | 90 | 182 | 237 | 104 | 31 | 120 | 124 | 125 | 280 | 94 | 76 | 79 | 9 | 66 | 86 | 9 | 50 | 39 | 15 | 3 | 49 | 4 | 54 | 7 | 0 | 1 | 15 | 2 | 5 | 32 | 0 | 0 | 0 | 7 | 0 | 10 | 0 | 0 | 1 | 15 | 0 | 0 | 45 | 11 | 0 | 21 | 0 | 0 | 1 | 0 | 80 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Local Network Wiring Assets | 25 | 5 | 16 | 4 | 20 | 19 | 8 | 40 | 18 | 21 | 11 | 6 | 22 | 8 | 15 | 11 | 10 | 9 | 1 | 9 | 7 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 7 | 4 | 2 | 0 | 8 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Network Assets | 33.33 | 5.77 | 3 | 103 | 22 | 8 | 5 | 27 | 22 | 4 | 2 | 6 | 3 | 5 | 9 | 4 | 18 | 12 | 3 | 0 | 0 | 1 | 2 | 14 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 4 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 0 | 11 | 0 | 1 | 1 | 1 | 5 | 0 | 2 | 0 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Master Station Assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Site Infrastructure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Linear Assets | 0 | 0 | 1424 | 1559 | 10720 | 313 | 2279 | 5076 | 22742 | 3847 | 3808 | 34918 | 47394 | 45847 | 23383 | 69053 | 61430 | 71201 | 0 | 0 | 2900 | 0 | 0 | 75961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AFLC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BY: DNSP DEFINED | Buildings | 50 | 7.07 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 5 | 0 | 0 | 3 | 1 | 2 | 1 | 2 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 6 | 3 | 2 | 0 | 5 | 3 | 2 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Civil | 45 | 6.71 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 6 | 3 | 3 | 0 | 7 | 3 | 2 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacitor Banks - Large | 45 | 6.71 | 0 | 0 | 0 | 7 | 0 | 10 | 0 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 3 | 0 | 1 | 0 | 0 | 10 | 0 | 0 | 3 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fences | 45 | 6.71 | 1 | 1 | 0 | 0 | 2 | 1 | 6 | 4 | 2 | 1 | 2 | 1 | 4 | 2 | 6 | 2 | 1 | 1 | 1 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTs and VTs | 50 | 7.07 | 12 | 27 | 6 | 14 | 5 | 35 | 26 | 59 | 36 | 17 | 16 | 3 | 15 | 4 | 15 | 7 | 10 | 12 | 6 | 3 | 23 | 3 | 0 | 65 | 0 | 0 | 11 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NER's | 45 | 6.71 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 3 | 4 | 1 | 6 | 0 | 2 | 2 | 0 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.3 MD - Network level
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
5.3 MAXIMUM DEMAND AT NETWORK LEVEL
5.3.1 - RAW AND WEATHER CORRECTED COINCIDENT MD AT NETWORK LEVEL (Summed at transmission connection point)
| UNIT | 2019
Raw network coincident MD | MW | 2019
Date MD occurred |  | 25/01/2019
Half hour time period MD occurred |  | 11:00:00
Winter/summer peaking |  | Summer
Embedded generation | MW | 11
Weather corrected (10% POE) network coincident MD | MW | 2228
Weather corrected (50% POE) network coincident MD | MW | 2042
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.4 MD & utilisation-Spatial
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
5.4 MAXIMUM DEMAND AND UTILISATION AT SPATIAL LEVEL
There is ONE table on this worksheet. It has two sub-tables based on the Network Level. Each sub-table has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup data.
5.4.1 NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2019
SUBTRANSMISSION SUBSTATION | <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2019
ZONE SUBSTATION | BOX HILL | Substation Rating | MVA | Non-Coincident | 107.7
|  |  |  | Coincident | 107.7
|  | Raw Adjusted MD | MW | Non-Coincident | 49.38
|  |  |  | Coincident | 45.013
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.395
|  |  |  | Coincident | 47.952
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 49.813
|  |  |  | Coincident | 45.408
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 49.828
|  |  |  | Coincident | 48.372
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 48.99
|  |  |  | Coincident | 44.657
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 49.005
|  |  |  | Coincident | 47.573
| BEAUMARIS | Substation Rating | MVA | Non-Coincident | 61.6
|  |  |  | Coincident | 61.6
|  | Raw Adjusted MD | MW | Non-Coincident | 29.528
|  |  |  | Coincident | 25.248
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.886
|  |  |  | Coincident | 25.8
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 11:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.89
|  |  |  | Coincident | 25.557
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.252
|  |  |  | Coincident | 26.116
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.204
|  |  |  | Coincident | 24.97
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.558
|  |  |  | Coincident | 25.516
| BENTLEIGH | Substation Rating | MVA | Non-Coincident | 61
|  |  |  | Coincident | 61
|  | Raw Adjusted MD | MW | Non-Coincident | 29.387
|  |  |  | Coincident | 26.549
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.563
|  |  |  | Coincident | 26.732
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.691
|  |  |  | Coincident | 26.823
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 29.868
|  |  |  | Coincident | 27.008
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.107
|  |  |  | Coincident | 26.296
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.281
|  |  |  | Coincident | 26.477
| BULLEEN | Substation Rating | MVA | Non-Coincident | 59
|  |  |  | Coincident | 59
|  | Raw Adjusted MD | MW | Non-Coincident | 30.449
|  |  |  | Coincident | 25.239
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.69
|  |  |  | Coincident | 25.508
|  | Date MD occurred |  | Non-Coincident | 1/24/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 31.113
|  |  |  | Coincident | 25.79
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.36
|  |  |  | Coincident | 26.065
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.403
|  |  |  | Coincident | 25.2
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.643
|  |  |  | Coincident | 25.469
| BURWOOD | Substation Rating | MVA | Non-Coincident | 37.8
|  |  |  | Coincident | 37.8
|  | Raw Adjusted MD | MW | Non-Coincident | 23.225
|  |  |  | Coincident | 20.682
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.263
|  |  |  | Coincident | 20.813
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.494
|  |  |  | Coincident | 20.921
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.532
|  |  |  | Coincident | 21.054
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.983
|  |  |  | Coincident | 20.467
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.021
|  |  |  | Coincident | 20.597
| CLARINDA | Substation Rating | MVA | Non-Coincident | 59.2
|  |  |  | Coincident | 59.2
|  | Raw Adjusted MD | MW | Non-Coincident | 34.288
|  |  |  | Coincident | 32.287
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.419
|  |  |  | Coincident | 32.565
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.619
|  |  |  | Coincident | 32.598
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.75
|  |  |  | Coincident | 32.879
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.984
|  |  |  | Coincident | 32
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.113
|  |  |  | Coincident | 32.276
| CAULFIELD | Substation Rating | MVA | Non-Coincident | 82.6
|  |  |  | Coincident | 82.6
|  | Raw Adjusted MD | MW | Non-Coincident | 49.8
|  |  |  | Coincident | 46.065
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.925
|  |  |  | Coincident | 46.268
|  | Date MD occurred |  | Non-Coincident | 3/1/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 50.217
|  |  |  | Coincident | 46.451
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.343
|  |  |  | Coincident | 46.656
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 49.707
|  |  |  | Coincident | 45.98
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 49.832
|  |  |  | Coincident | 46.182
| CHELTENHAM | Substation Rating | MVA | Non-Coincident | 60.9
|  |  |  | Coincident | 60.9
|  | Raw Adjusted MD | MW | Non-Coincident | 23.787
|  |  |  | Coincident | 23.409
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.983
|  |  |  | Coincident | 23.439
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 11:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.107
|  |  |  | Coincident | 25.692
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.323
|  |  |  | Coincident | 25.726
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.01
|  |  |  | Coincident | 24.613
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.217
|  |  |  | Coincident | 24.644
| CARRUM | Substation Rating | MVA | Non-Coincident | 110.3
|  |  |  | Coincident | 110.3
|  | Raw Adjusted MD | MW | Non-Coincident | 72.433
|  |  |  | Coincident | 64.714
|  | Raw Adjusted MD | MVA | Non-Coincident | 72.541
|  |  |  | Coincident | 64.749
|  | Date MD occurred |  | Non-Coincident | 2/28/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 84.544
|  |  |  | Coincident | 75.533
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 84.669
|  |  |  | Coincident | 75.574
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 79.382
|  |  |  | Coincident | 70.922
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 79.5
|  |  |  | Coincident | 70.96
| DONCASTER | Substation Rating | MVA | Non-Coincident | 108.6
|  |  |  | Coincident | 108.6
|  | Raw Adjusted MD | MW | Non-Coincident | 86.962
|  |  |  | Coincident | 77.3
|  | Raw Adjusted MD | MVA | Non-Coincident | 87.478
|  |  |  | Coincident | 77.806
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 90.446
|  |  |  | Coincident | 80.396
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 90.982
|  |  |  | Coincident | 80.923
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 85.628
|  |  |  | Coincident | 76.114
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 86.136
|  |  |  | Coincident | 76.613
| DROMANA | Substation Rating | MVA | Non-Coincident | 89.6
|  |  |  | Coincident | 89.6
|  | Raw Adjusted MD | MW | Non-Coincident | 35.416
|  |  |  | Coincident | 31.62
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.472
|  |  |  | Coincident | 31.632
|  | Date MD occurred |  | Non-Coincident | 3/2/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 45.638
|  |  |  | Coincident | 40.746
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 45.71
|  |  |  | Coincident | 40.762
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 42.443
|  |  |  | Coincident | 37.894
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.51
|  |  |  | Coincident | 37.908
| DANDENONG | Substation Rating | MVA | Non-Coincident | 126.2
|  |  |  | Coincident | 126.2
|  | Raw Adjusted MD | MW | Non-Coincident | 79.141
|  |  |  | Coincident | 75.379
|  | Raw Adjusted MD | MVA | Non-Coincident | 79.481
|  |  |  | Coincident | 76.178
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 11:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.411
|  |  |  | Coincident | 0.891
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 83.025
|  |  |  | Coincident | 79.078
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 83.381
|  |  |  | Coincident | 79.917
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 75.555
|  |  |  | Coincident | 71.964
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 75.88
|  |  |  | Coincident | 72.727
| DANDENONG SOUTH | Substation Rating | MVA | Non-Coincident | 144.8
|  |  |  | Coincident | 144.8
|  | Raw Adjusted MD | MW | Non-Coincident | 60.058
|  |  |  | Coincident | 47.575
|  | Raw Adjusted MD | MVA | Non-Coincident | 60.764
|  |  |  | Coincident | 47.578
|  | Date MD occurred |  | Non-Coincident | 12/7/2018
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 10:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 62.743
|  |  |  | Coincident | 49.701
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 63.48
|  |  |  | Coincident | 49.705
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 61.599
|  |  |  | Coincident | 48.795
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 62.322
|  |  |  | Coincident | 48.799
| DANDENONG VALLEY | Substation Rating | MVA | Non-Coincident | 131.1
|  |  |  | Coincident | 131.1
|  | Raw Adjusted MD | MW | Non-Coincident | 72.821
|  |  |  | Coincident | 68.391
|  | Raw Adjusted MD | MVA | Non-Coincident | 74.873
|  |  |  | Coincident | 71.696
|  | Date MD occurred |  | Non-Coincident | 1/30/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 76.428
|  |  |  | Coincident | 71.778
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 78.581
|  |  |  | Coincident | 75.247
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 74.89
|  |  |  | Coincident | 70.334
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 77.001
|  |  |  | Coincident | 73.734
| EAST BURWOOD | Substation Rating | MVA | Non-Coincident | 100.9
|  |  |  | Coincident | 100.9
|  | Raw Adjusted MD | MW | Non-Coincident | 59.985
|  |  |  | Coincident | 52.978
|  | Raw Adjusted MD | MVA | Non-Coincident | 61.133
|  |  |  | Coincident | 53.438
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 60.596
|  |  |  | Coincident | 53.519
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 61.756
|  |  |  | Coincident | 53.983
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 59.434
|  |  |  | Coincident | 52.492
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 60.572
|  |  |  | Coincident | 52.948
| ELSTERNWICK | Substation Rating | MVA | Non-Coincident | 66.1
|  |  |  | Coincident | 66.1
|  | Raw Adjusted MD | MW | Non-Coincident | 34.698
|  |  |  | Coincident | 32.087
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.068
|  |  |  | Coincident | 32.137
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 11:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.553
|  |  |  | Coincident | 31.954
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.922
|  |  |  | Coincident | 32.003
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.498
|  |  |  | Coincident | 30.978
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.855
|  |  |  | Coincident | 31.026
| EAST MALVERN | Substation Rating | MVA | Non-Coincident | 62.4
|  |  |  | Coincident | 62.4
|  | Raw Adjusted MD | MW | Non-Coincident | 34.755
|  |  |  | Coincident | 31.555
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.84
|  |  |  | Coincident | 31.812
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 12:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.581
|  |  |  | Coincident | 32.304
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.691
|  |  |  | Coincident | 32.567
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.013
|  |  |  | Coincident | 30.881
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 35.075
|  |  |  | Coincident | 31.132
| ELWOOD | Substation Rating | MVA | Non-Coincident | 56.8
|  |  |  | Coincident | 56.8
|  | Raw Adjusted MD | MW | Non-Coincident | 22.026
|  |  |  | Coincident | 20.431
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.037
|  |  |  | Coincident | 20.442
|  | Date MD occurred |  | Non-Coincident | 1/24/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.502
|  |  |  | Coincident | 22.728
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.514
|  |  |  | Coincident | 22.74
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.655
|  |  |  | Coincident | 21.014
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.666
|  |  |  | Coincident | 21.026
| FRANKSTON SOUTH | Substation Rating | MVA | Non-Coincident | 92
|  |  |  | Coincident | 92
|  | Raw Adjusted MD | MW | Non-Coincident | 63.938
|  |  |  | Coincident | 56.436
|  | Raw Adjusted MD | MVA | Non-Coincident | 67.172
|  |  |  | Coincident | 56.923
|  | Date MD occurred |  | Non-Coincident | 3/1/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 72.037
|  |  |  | Coincident | 63.585
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 75.682
|  |  |  | Coincident | 64.134
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 62.482
|  |  |  | Coincident | 55.151
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 65.643
|  |  |  | Coincident | 55.627
| FRANKSTON | Substation Rating | MVA | Non-Coincident | 90.4
|  |  |  | Coincident | 90.4
|  | Raw Adjusted MD | MW | Non-Coincident | 54.868
|  |  |  | Coincident | 48.166
|  | Raw Adjusted MD | MVA | Non-Coincident | 54.918
|  |  |  | Coincident | 48.365
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 12:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 56.173
|  |  |  | Coincident | 49.311
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 56.224
|  |  |  | Coincident | 49.515
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 48.32
|  |  |  | Coincident | 42.418
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 48.364
|  |  |  | Coincident | 42.593
| GLEN WAVERLEY | Substation Rating | MVA | Non-Coincident | 103.2
|  |  |  | Coincident | 103.2
|  | Raw Adjusted MD | MW | Non-Coincident | 70.849
|  |  |  | Coincident | 62.739
|  | Raw Adjusted MD | MVA | Non-Coincident | 71.933
|  |  |  | Coincident | 62.966
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 72.014
|  |  |  | Coincident | 63.771
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 73.115
|  |  |  | Coincident | 64.001
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 69.774
|  |  |  | Coincident | 61.787
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 70.841
|  |  |  | Coincident | 62.011
| HASTINGS | Substation Rating | MVA | Non-Coincident | 77.7
|  |  |  | Coincident | 77.7
|  | Raw Adjusted MD | MW | Non-Coincident | 42.978
|  |  |  | Coincident | 41.85
|  | Raw Adjusted MD | MVA | Non-Coincident | 45.563
|  |  |  | Coincident | 42.72
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 47.428
|  |  |  | Coincident | 46.183
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.281
|  |  |  | Coincident | 47.143
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 42.211
|  |  |  | Coincident | 41.103
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.751
|  |  |  | Coincident | 41.958
| HEATHERTON | Substation Rating | MVA | Non-Coincident | 92.1
|  |  |  | Coincident | 92.1
|  | Raw Adjusted MD | MW | Non-Coincident | 45.924
|  |  |  | Coincident | 44.27
|  | Raw Adjusted MD | MVA | Non-Coincident | 47.982
|  |  |  | Coincident | 44.278
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 11:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 47.291
|  |  |  | Coincident | 45.587
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 49.409
|  |  |  | Coincident | 45.596
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.663
|  |  |  | Coincident | 43.054
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.664
|  |  |  | Coincident | 43.062
| GARDINER | Substation Rating | MVA | Non-Coincident | 73.2
|  |  |  | Coincident | 73.2
|  | Raw Adjusted MD | MW | Non-Coincident | 42.718
|  |  |  | Coincident | 39.349
|  | Raw Adjusted MD | MVA | Non-Coincident | 42.888
|  |  |  | Coincident | 39.403
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 12:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 42.745
|  |  |  | Coincident | 39.374
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 42.915
|  |  |  | Coincident | 39.428
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 42.693
|  |  |  | Coincident | 39.326
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.863
|  |  |  | Coincident | 39.381
| KEYSBOROUGH | Substation Rating | MVA | Non-Coincident | 45.8
|  |  |  | Coincident | 45.8
|  | Raw Adjusted MD | MW | Non-Coincident | 32.234
|  |  |  | Coincident | 28.683
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.339
|  |  |  | Coincident | 28.966
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 12:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.515
|  |  |  | Coincident | 30.712
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.627
|  |  |  | Coincident | 31.016
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.73
|  |  |  | Coincident | 28.234
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.833
|  |  |  | Coincident | 28.513
| LYNDALE | Substation Rating | MVA | Non-Coincident | 100.2
|  |  |  | Coincident | 100.2
|  | Raw Adjusted MD | MW | Non-Coincident | 54.686
|  |  |  | Coincident | 45.974
|  | Raw Adjusted MD | MVA | Non-Coincident | 56.341
|  |  |  | Coincident | 46.012
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 55.41
|  |  |  | Coincident | 46.583
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 57.088
|  |  |  | Coincident | 46.622
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 54.034
|  |  |  | Coincident | 45.426
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 55.67
|  |  |  | Coincident | 45.464
| LANGWARRIN | Substation Rating | MVA | Non-Coincident | 90
|  |  |  | Coincident | 90
|  | Raw Adjusted MD | MW | Non-Coincident | 43.051
|  |  |  | Coincident | 36.645
|  | Raw Adjusted MD | MVA | Non-Coincident | 43.767
|  |  |  | Coincident | 37.543
|  | Date MD occurred |  | Non-Coincident | 3/1/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 46.161
|  |  |  | Coincident | 39.292
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 46.929
|  |  |  | Coincident | 40.254
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.782
|  |  |  | Coincident | 37.267
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.51
|  |  |  | Coincident | 38.18
| MENTONE | Substation Rating | MVA | Non-Coincident | 79
|  |  |  | Coincident | 79
|  | Raw Adjusted MD | MW | Non-Coincident | 37.843
|  |  |  | Coincident | 34.786
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.289
|  |  |  | Coincident | 35.408
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 12:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 40.047
|  |  |  | Coincident | 36.812
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.519
|  |  |  | Coincident | 37.471
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 35.86
|  |  |  | Coincident | 32.963
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.283
|  |  |  | Coincident | 33.553
| MORDIALLOC | Substation Rating | MVA | Non-Coincident | 82.3
|  |  |  | Coincident | 82.3
|  | Raw Adjusted MD | MW | Non-Coincident | 57.229
|  |  |  | Coincident | 56.093
|  | Raw Adjusted MD | MVA | Non-Coincident | 57.781
|  |  |  | Coincident | 56.676
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 11:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 58.86
|  |  |  | Coincident | 57.692
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 59.427
|  |  |  | Coincident | 58.291
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 57.454
|  |  |  | Coincident | 56.314
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 58.008
|  |  |  | Coincident | 56.899
| MULGRAVE | Substation Rating | MVA | Non-Coincident | 111.6
|  |  |  | Coincident | 111.6
|  | Raw Adjusted MD | MW | Non-Coincident | 78.178
|  |  |  | Coincident | 70.976
|  | Raw Adjusted MD | MVA | Non-Coincident | 78.279
|  |  |  | Coincident | 71.273
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 79.34
|  |  |  | Coincident | 72.03
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 79.442
|  |  |  | Coincident | 72.332
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 77.134
|  |  |  | Coincident | 70.027
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 77.233
|  |  |  | Coincident | 70.321
| MOORABBIN | Substation Rating | MVA | Non-Coincident | 78.7
|  |  |  | Coincident | 78.7
|  | Raw Adjusted MD | MW | Non-Coincident | 50.774
|  |  |  | Coincident | 47.598
|  | Raw Adjusted MD | MVA | Non-Coincident | 50.879
|  |  |  | Coincident | 47.674
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 51.484
|  |  |  | Coincident | 48.263
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 51.59
|  |  |  | Coincident | 48.34
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 50.119
|  |  |  | Coincident | 46.984
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 50.223
|  |  |  | Coincident | 47.059
| MORNINGTON | Substation Rating | MVA | Non-Coincident | 90.4
|  |  |  | Coincident | 90.4
|  | Raw Adjusted MD | MW | Non-Coincident | 60.59
|  |  |  | Coincident | 51.591
|  | Raw Adjusted MD | MVA | Non-Coincident | 60.668
|  |  |  | Coincident | 51.611
|  | Date MD occurred |  | Non-Coincident | 3/1/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 66.334
|  |  |  | Coincident | 56.482
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 66.419
|  |  |  | Coincident | 56.503
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 59.485
|  |  |  | Coincident | 50.65
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 59.562
|  |  |  | Coincident | 50.669
| NORTH BRIGHTON | Substation Rating | MVA | Non-Coincident | 90.4
|  |  |  | Coincident | 90.4
|  | Raw Adjusted MD | MW | Non-Coincident | 44.878
|  |  |  | Coincident | 41.17
|  | Raw Adjusted MD | MVA | Non-Coincident | 45.733
|  |  |  | Coincident | 42
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 46.188
|  |  |  | Coincident | 42.372
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 47.068
|  |  |  | Coincident | 43.225
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.669
|  |  |  | Coincident | 40.061
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.501
|  |  |  | Coincident | 40.868
| NOTTING HILL | Substation Rating | MVA | Non-Coincident | 109.6
|  |  |  | Coincident | 109.6
|  | Raw Adjusted MD | MW | Non-Coincident | 43.091
|  |  |  | Coincident | 41.252
|  | Raw Adjusted MD | MVA | Non-Coincident | 44.683
|  |  |  | Coincident | 41.287
|  | Date MD occurred |  | Non-Coincident | 1/15/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 48.489
|  |  |  | Coincident | 46.42
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.281
|  |  |  | Coincident | 46.459
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 46.781
|  |  |  | Coincident | 44.785
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 48.51
|  |  |  | Coincident | 44.823
| NOBLE PARK | Substation Rating | MVA | Non-Coincident | 105.9
|  |  |  | Coincident | 105.9
|  | Raw Adjusted MD | MW | Non-Coincident | 58.868
|  |  |  | Coincident | 50.581
|  | Raw Adjusted MD | MVA | Non-Coincident | 58.87
|  |  |  | Coincident | 51.937
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 59.979
|  |  |  | Coincident | 51.536
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 59.981
|  |  |  | Coincident | 52.917
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 57.843
|  |  |  | Coincident | 49.7
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 57.844
|  |  |  | Coincident | 51.033
| NUNAWADING | Substation Rating | MVA | Non-Coincident | 132.4
|  |  |  | Coincident | 132.4
|  | Raw Adjusted MD | MW | Non-Coincident | 65.252
|  |  |  | Coincident | 57.251
|  | Raw Adjusted MD | MVA | Non-Coincident | 66.463
|  |  |  | Coincident | 57.34
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 66.155
|  |  |  | Coincident | 58.043
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 67.383
|  |  |  | Coincident | 58.134
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 64.439
|  |  |  | Coincident | 56.538
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 65.636
|  |  |  | Coincident | 56.626
| OAKLEIGH | Substation Rating | MVA | Non-Coincident | 85.7
|  |  |  | Coincident | 85.7
|  | Raw Adjusted MD | MW | Non-Coincident | 41.692
|  |  |  | Coincident | 39.042
|  | Raw Adjusted MD | MVA | Non-Coincident | 41.692
|  |  |  | Coincident | 39.135
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 42.138
|  |  |  | Coincident | 39.46
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 42.138
|  |  |  | Coincident | 39.554
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.28
|  |  |  | Coincident | 38.657
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 41.281
|  |  |  | Coincident | 38.749
| OAKLEIGH EAST | Substation Rating | MVA | Non-Coincident | 62.3
|  |  |  | Coincident | 62.3
|  | Raw Adjusted MD | MW | Non-Coincident | 13.457
|  |  |  | Coincident | 12.72
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.88
|  |  |  | Coincident | 13.384
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.342
|  |  |  | Coincident | 14.502
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.964
|  |  |  | Coincident | 15.259
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.101
|  |  |  | Coincident | 14.275
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.698
|  |  |  | Coincident | 15.019
| ORMOND | Substation Rating | MVA | Non-Coincident | 64.2
|  |  |  | Coincident | 64.2
|  | Raw Adjusted MD | MW | Non-Coincident | 34.767
|  |  |  | Coincident | 30.265
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.059
|  |  |  | Coincident | 30.487
|  | Date MD occurred |  | Non-Coincident | 3/1/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.33
|  |  |  | Coincident | 32.496
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.864
|  |  |  | Coincident | 32.734
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.811
|  |  |  | Coincident | 30.303
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 38.107
|  |  |  | Coincident | 30.526
| ROSEBUD | Substation Rating | MVA | Non-Coincident | 91.2
|  |  |  | Coincident | 91.2
|  | Raw Adjusted MD | MW | Non-Coincident | 37.403
|  |  |  | Coincident | 32.588
|  | Raw Adjusted MD | MVA | Non-Coincident | 37.492
|  |  |  | Coincident | 32.626
|  | Date MD occurred |  | Non-Coincident | 1/24/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 45.541
|  |  |  | Coincident | 39.679
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 45.649
|  |  |  | Coincident | 39.725
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 40.532
|  |  |  | Coincident | 35.314
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 40.628
|  |  |  | Coincident | 35.355
| SURREY HILLS | Substation Rating | MVA | Non-Coincident | 22.2
|  |  |  | Coincident | 22.2
|  | Raw Adjusted MD | MW | Non-Coincident | 6.792
|  |  |  | Coincident | 5.77
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.969
|  |  |  | Coincident | 5.968
|  | Date MD occurred |  | Non-Coincident | 1/24/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.893
|  |  |  | Coincident | 6.705
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.099
|  |  |  | Coincident | 6.936
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.279
|  |  |  | Coincident | 6.184
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.469
|  |  |  | Coincident | 6.397
| SANDRINGHAM | Substation Rating | MVA | Non-Coincident | 72.1
|  |  |  | Coincident | 72.1
|  | Raw Adjusted MD | MW | Non-Coincident | 29.824
|  |  |  | Coincident | 27.616
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.876
|  |  |  | Coincident | 28.011
|  | Date MD occurred |  | Non-Coincident | 1/24/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.956
|  |  |  | Coincident | 30.516
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 33.014
|  |  |  | Coincident | 30.953
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.407
|  |  |  | Coincident | 28.155
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.46
|  |  |  | Coincident | 28.558
| SPRINGVALE | Substation Rating | MVA | Non-Coincident | 80
|  |  |  | Coincident | 80
|  | Raw Adjusted MD | MW | Non-Coincident | 45.605
|  |  |  | Coincident | 44.877
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.795
|  |  |  | Coincident | 46.198
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 11:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 51.471
|  |  |  | Coincident | 50.649
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 56.2
|  |  |  | Coincident | 52.14
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 49.067
|  |  |  | Coincident | 48.284
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 53.575
|  |  |  | Coincident | 49.705
| SPRINGVALE WEST | Substation Rating | MVA | Non-Coincident | 80
|  |  |  | Coincident | 80
|  | Raw Adjusted MD | MW | Non-Coincident | 51.424
|  |  |  | Coincident | 50.687
|  | Raw Adjusted MD | MVA | Non-Coincident | 51.986
|  |  |  | Coincident | 50.742
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 11:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 52.803
|  |  |  | Coincident | 52.046
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 53.379
|  |  |  | Coincident | 52.102
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 50.152
|  |  |  | Coincident | 49.433
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 50.699
|  |  |  | Coincident | 49.486
| SPRINGVALE SOUTH | Substation Rating | MVA | Non-Coincident | 79.9
|  |  |  | Coincident | 79.9
|  | Raw Adjusted MD | MW | Non-Coincident | 40.459
|  |  |  | Coincident | 36.006
|  | Raw Adjusted MD | MVA | Non-Coincident | 42.733
|  |  |  | Coincident | 36.154
|  | Date MD occurred |  | Non-Coincident | 1/25/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 8.869
|  |  |  | Coincident | 10.797
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 43.162
|  |  |  | Coincident | 38.412
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 45.589
|  |  |  | Coincident | 38.569
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 38.925
|  |  |  | Coincident | 34.641
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 41.113
|  |  |  | Coincident | 34.783
| SORRENTO | Substation Rating | MVA | Non-Coincident | 72
|  |  |  | Coincident | 72
|  | Raw Adjusted MD | MW | Non-Coincident | 34.294
|  |  |  | Coincident | 30.435
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.235
|  |  |  | Coincident | 30.879
|  | Date MD occurred |  | Non-Coincident | 1/4/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.5
|  |  |  | Coincident | 0.5
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 46.116
|  |  |  | Coincident | 40.927
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 46.036
|  |  |  | Coincident | 41.524
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.751
|  |  |  | Coincident | 39.716
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.674
|  |  |  | Coincident | 40.295
| WEST DONCASTER | Substation Rating | MVA | Non-Coincident | 93.7
|  |  |  | Coincident | 93.7
|  | Raw Adjusted MD | MW | Non-Coincident | 49.847
|  |  |  | Coincident | 44.907
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.851
|  |  |  | Coincident | 44.938
|  | Date MD occurred |  | Non-Coincident | 3/1/2019
|  |  |  | Coincident | 1/25/2019
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 11:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 53.06
|  |  |  | Coincident | 47.801
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 53.064
|  |  |  | Coincident | 47.834
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 49.137
|  |  |  | Coincident | 44.267
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 49.141
|  |  |  | Coincident | 44.298
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 6.3 Sustained interruptions
REGULATORY REPORTING STATEMENT
United Energy
CATEGORY ANALYSIS 2019
6.3 SUSTAINED INTERRUPTIONS TO SUPPLY
6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY (for 2019)
There is ONE table on this worksheet. It has been grouped into five subgroups of 10000 rows each for navigation purposes. See the Instructions sheet on how to group and ungroup data.
Definitions:
Feeder classification definitions (column E) |  |  |  |  | Average duration of sustained customer interruption (column I) |  | Effect on unplanned SAIDI (column J) |  | Effect on unplanned SAIFI (column K)
CBD feeder: a feeder supplying predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. Urban feeder: a feeder, that is not a CBD feeder, with actual maximum demand over the reporting period per total feeder route length greater than 0.3 MVA/km. Short rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length less than 200 km. Long rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length greater than 200 km. |  |  |  |  | The average duration of an interruption experienced by an affected customer. |  | The sum of the duration of each unplanned sustained customer interruption (in minutes) divided by the total number of distribution customers. Unplanned SAIDI excludes momentary interruptions (one minute or less). |  | The total number of unplanned sustained customer interruptions divided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions.
Date of event | Time of interruption | Asset ID | Feeder classification | Reason for interruption | Detailed reason for interruption | Number of customers affected by the interruption | Average duration of sustained customer interruption | Effect on unplanned SAIDI | Effect on unplanned SAIFI | MED
(DD/MM/YYYY) | (HH:MM) | (eg. feeder ID) | (drop down) | (select from options in drop-down box) | (select from options in column 'O' that correspond with reason in column 'F') |  | (minutes)
01/01/2019 | 02:07 | EL8 | Urban | Animal | Animal impact | 67 | 93 | 0.0098443 | 0.010585 | No
01/01/2019 | 04:23 | FTN13 | Urban | Third Party | Vehicle Impact | 44 | 343 | 0.023931 | 0.0069768 | No
01/01/2019 | 04:23 | FTN25 | Urban | Third Party | Vehicle Impact | 11 | 343 | 0.0060964 | 0.0017774 | No
01/01/2019 | 04:34 | FSH11 | Urban | Asset Failure | LV | 1 | 74.6 | 0.00011783 | 0.00015799 | No
01/01/2019 | 10:26 | LD2 | Urban | Asset Failure | LV | 1 | 184 | 0.0002907 | 0.00015799 | No
01/01/2019 | 10:26 | FSH32 | Rural Short | Asset Failure | LV | 1 | 98.1 | 0.0016495 | 0.0016815 | No
01/01/2019 | 11:12 | BR1 | Urban | Asset Failure | LV | 1 | 137.2 | 0.00021679 | 0.00015799 | No
01/01/2019 | 12:03 | M13 | Urban | Asset Failure | LV | 1 | 138.2 | 0.00021834 | 0.00015799 | No
01/01/2019 | 20:55 | MTN31 | Urban | Asset Failure | LV | 1 | 75 | 0.00011849 | 0.00015799 | No
02/01/2019 | 11:16 | EL8 | Urban | Asset Failure | LV | 1 | 67.8 | 0.00010704 | 0.00015799 | No
02/01/2019 | 14:41 | LWN35 | Urban | Overloads |  | 1 | 64 | 0.00010111 | 0.00015799 | No
03/01/2019 | 03:16 | MTN32 | Rural Short | Animal | Animal impact | 1,959 | 56.4 | 1.8572 | 3.294 | No
03/01/2019 | 09:34 | WD36 | Urban | Planned |  | 1 | 39.4 | 6.2301e-05 | 0.00015799 | No
03/01/2019 | 11:03 | MTN23 | Urban | Asset Failure | LV | 30 | 87 | 0.0040823 | 0.0046923 | No
03/01/2019 | 20:08 | BW33 | Urban | Overloads |  | 1 | 62 | 9.7954e-05 | 0.00015799 | No
03/01/2019 | 22:06 | EB31 | Urban | Asset Failure | LV | 11 | 115 | 0.0019786 | 0.0017205 | No
04/01/2019 | 06:14 | RBD21 | Rural Short | Asset Failure | LV | 4 | 165.4 | 0.010098 | 0.0061038 | No
04/01/2019 | 09:53 | BC11 | Urban | Unknown | Unknown | 1 | 171.6 | 0.00027114 | 0.00015799 | No
04/01/2019 | 12:25 | OAK21 | Urban | Asset Failure | LV | 1 | 62 | 9.798e-05 | 0.00015799 | No
04/01/2019 | 12:26 | DC10 | Urban | Asset Failure | LV | 1 | 153.3 | 0.00024212 | 0.00015799 | No
04/01/2019 | 14:32 | STO13 | Urban | Overloads |  | 38 | 155.1 | 0.0092205 | 0.0059436 | No
04/01/2019 | 14:45 | STO21 | Rural Short | Unknown | Unknown | 1 | 104.7 | 0.0017611 | 0.0016815 | No
04/01/2019 | 15:30 | KBH32 | Urban | Unknown | Unknown | 26 | 120 | 0.00488 | 0.0040667 | No
04/01/2019 | 15:56 | DN2 | Urban | Third Party | Other | 72 | 24.8 | 0.0028201 | 0.011375 | No
04/01/2019 | 15:56 | DN2 | Urban | Third Party | Other | 72 | 7.8 | 0.00088348 | 0.011375 | No
04/01/2019 | 16:04 | DN2 | Urban | Third Party | Other | 7 | 787.3 | 0.0087064 | 0 | No
04/01/2019 | 16:31 | BU10 | Urban | Weather |  | 19 | 54 | 0.0016611 | 0.0030761 | No
04/01/2019 | 16:59 | DMA15 | Rural Short | Vegetation | Grow-in - NSP responsibility | 45 | 91.9 | 0.069563 | 0.075667 | No
04/01/2019 | 17:28 | K8 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 127.4 | 0.00020131 | 0.00015799 | No
04/01/2019 | 18:47 | FTN14 | Urban | Asset Failure | LV | 1 | 157.9 | 0.00024949 | 0.00015799 | No
04/01/2019 | 20:06 | SH22 | Urban | Vegetation | Grow-in - Other responsible party | 17 | 24 | 0.0006446 | 0.0026858 | No
04/01/2019 | 21:32 | EB33 | Urban | Vegetation | Grow-in - Other responsible party | 97 | 149 | 0.022834 | 0.015325 | No
04/01/2019 | 21:37 | EB33 | Urban | Unknown | Unknown | 1 | 52 | 8.2181e-05 | 0.00015799 | No
05/01/2019 | 00:08 | HGS33 | Rural Short | Third Party | Vehicle Impact | 66 | 98 | 0.10876 | 0.11098 | No
05/01/2019 | 01:12 | CRM35 | Urban | Asset Failure | LV | 15 | 18 | 0.00041292 | 0.002294 | No
05/01/2019 | 01:54 | FTN14 | Urban | Weather |  | 1 | 140.2 | 0.00022145 | 0.00015799 | No
05/01/2019 | 07:53 | MGE22 | Urban | Animal | Other | 5 | 206.3 | 0.0016294 | 0.00078995 | No
05/01/2019 | 09:24 | MTN24 | Rural Short | Unknown | Unknown | 7 | 485.6 | 0.057151 | 0.01177 | No
05/01/2019 | 12:43 | BH21 | Urban | Asset Failure | LV | 166 | 340 | 0.089169 | 0.026226 | No
06/01/2019 | 10:10 | BH34 | Urban | Asset Failure | LV | 1 | 110 | 0.00017379 | 0.00015799 | No
06/01/2019 | 14:57 | FSH34 | Urban | Asset Failure | LV | 1 | 70 | 0.00011059 | 0.00015799 | No
06/01/2019 | 19:42 | RBD23 | Urban | Vegetation | Grow-in - NSP responsibility | 112 | 28 | 0.0049546 | 0.017695 | No
06/01/2019 | 23:12 | NW31 | Urban | Asset Failure | LV | 1 | 132 | 0.00020855 | 0.00015799 | No
07/01/2019 | 02:16 | SR12 | Urban | Animal | Animal impact | 273 | 56.9 | 0.024543 | 0.043131 | No
07/01/2019 | 04:36 | CRM22 | Urban | Overloads |  | 1 | 203.5 | 0.00032143 | 0.00015799 | No
07/01/2019 | 06:05 | MTN32 | Rural Short | Unknown | Unknown | 4 | 69.2 | 0.0046521 | 0.006726 | No
07/01/2019 | 07:53 | CRM22 | Urban | Overloads |  | 1 | 16.2 | 2.5621e-05 | 0.00015799 | No
07/01/2019 | 08:25 | DN7 | Urban | Weather |  | 8 | 80 | 0.00095931 | 0.0011991 | No
07/01/2019 | 09:00 | OR32 | Urban | Overloads |  | 4 | 109.1 | 0.00068268 | 0.00062564 | No
07/01/2019 | 09:44 | FSH12 | Rural Short | Asset Failure | LV | 1 | 236 | 0.0039675 | 0.0016815 | No
07/01/2019 | 09:58 | GW12 | Urban | Asset Failure | LV | 2 | 167 | 0.00061212 | 0.00036654 | No
07/01/2019 | 10:00 | HGS31 | Rural Short | Weather |  | 4 | 134.8 | 0.0090644 | 0.006726 | No
07/01/2019 | 11:14 | OR25 | Urban | Asset Failure | LV | 1 | 156 | 0.00024646 | 0.00015799 | No
07/01/2019 | 11:35 | MTN34 | Urban | Asset Failure | LV | 1 | 159.7 | 0.00025228 | 0.00015799 | No
07/01/2019 | 13:06 | OR22 | Urban | Overloads |  | 1 | 143.9 | 0.00011363 | 7.8995e-05 | No
07/01/2019 | 14:00 | LWN35 | Urban | Overloads |  | 1 | 179.1 | 0.00028293 | 0.00015799 | No
07/01/2019 | 21:17 | NB22 | Urban | Asset Failure | LV | 1 | 111.4 | 0.000176 | 0.00015799 | No
08/01/2019 | 09:43 | NP12 | Urban | Asset Failure | LV | 1 | 122 | 0.00019275 | 0.00015799 | No
08/01/2019 | 12:00 | FSH13 | Urban | Unknown | Unknown | 1 | 124.3 | 0.00019635 | 0.00015799 | No
08/01/2019 | 19:21 | SVW55 | Urban | Asset Failure | LV | 1 | 59 | 9.3214e-05 | 0.00015799 | No
08/01/2019 | 21:50 | SVW45 | Urban | Other | XXX | 2 | 10 | 3.1598e-05 | 0.00031598 | No
08/01/2019 | 22:55 | NP24 | Urban | Animal | Animal impact | 63 | 125 | 0.012442 | 0.0099534 | No
08/01/2019 | 22:55 | NP24 | Urban | Asset Failure | Distribution substation | 23 | 329.7 | 0.01186 | 0.0035974 | No
09/01/2019 | 06:02 | LD2 | Urban | Asset Failure | LV | 1 | 104 | 0.00016431 | 0.00015799 | No
09/01/2019 | 06:35 | MC7 | Urban | Asset Failure | LV | 1 | 78.7 | 0.00012426 | 0.00015799 | No
09/01/2019 | 08:14 | EM8 | Urban | Asset Failure | LV | 1 | 48 | 7.5835e-05 | 0.00015799 | No
09/01/2019 | 09:17 | SV32 | Urban | Unknown | Unknown | 1 | 415.8 | 0.00065687 | 0.00015799 | No
09/01/2019 | 09:27 | SV14 | Urban |  | Zone substation | 25 | 44.2 | 0.0017438 | 0.0039497 | No
09/01/2019 | 09:27 | SV22 | Urban |  | Zone substation | 37 | 44.7 | 0.002614 | 0.0058456 | No
09/01/2019 | 09:27 | SV21 | Urban |  | Zone substation | 47 | 44.9 | 0.0033365 | 0.0074255 | No
09/01/2019 | 09:27 | SV20 | Urban |  | Zone substation | 98 | 45.3 | 0.0070138 | 0.015483 | No
09/01/2019 | 09:27 | SV23 | Urban |  | Zone substation | 186 | 44.4 | 0.013043 | 0.029386 | No
09/01/2019 | 09:50 | SV16 | Urban | Animal | Other | 153 | 139.9 | 0.033825 | 0.024172 | No
09/01/2019 | 09:58 | BH31 | Urban | Asset Failure | LV | 1 | 151.6 | 0.00023949 | 0.00015799 | No
09/01/2019 | 12:24 | OAK33 | Urban | Unknown | Unknown | 1 | 20 | 3.1598e-05 | 0.00015799 | No
09/01/2019 | 14:00 | STO13 | Urban | Animal | Animal impact | 2 | 309.2 | 0.00097685 | 0.00031598 | No
09/01/2019 | 21:47 | RBD23 | Urban | Asset Failure | LV | 1 | 58 | 9.1634e-05 | 0.00015799 | No
10/01/2019 | 01:01 | OR24 | Urban | Animal | Animal impact | 2,004 | 88.3 | 0.27956 | 0.31661 | No
10/01/2019 | 08:05 | RWT34 | Urban | Weather |  | 1 | 110 | 0.00017379 | 0.00015799 | No
10/01/2019 | 08:58 | NW11 | Urban | Unknown | Unknown | 1 | 101.5 | 0.00016031 | 0.00015799 | No
10/01/2019 | 09:37 | GW12 | Urban | Asset Failure | LV | 4 | 138 | 0.00091571 | 0.00066356 | No
10/01/2019 | 10:50 | OR24 | Urban | Asset Failure | LV | 1 | 59.9 | 9.4636e-05 | 0.00015799 | No
10/01/2019 | 11:00 | DMA23 | Rural Short | Animal | Animal impact | 1 | 119.9 | 0.0020167 | 0.0016815 | No
10/01/2019 | 11:42 | EB21 | Urban | Third Party | Other | 1 | 108 | 0.00017063 | 0.00015799 | No
10/01/2019 | 11:53 | SV16 | Urban | Third Party | Vehicle Impact | 1 | 231.4 | 0.00036559 | 0.00015799 | No
10/01/2019 | 12:19 | MC1 | Urban | Overloads |  | 1 | 96 | 0.00015167 | 0.00015799 | No
10/01/2019 | 12:43 | DN22 | Urban | Third Party | Other | 1 | 172.4 | 0.00027235 | 0.00015799 | No
10/01/2019 | 14:38 | LD7 | Urban | Unknown | Unknown | 1 | 81.2 | 0.00012821 | 0.00015799 | No
10/01/2019 | 16:02 | BW34 | Urban | Asset Failure | LV | 1 | 117.8 | 0.00018603 | 0.00015799 | No
10/01/2019 | 17:48 | DMA21 | Urban | Third Party | Other | 1 | 132 | 0.00020855 | 0.00015799 | No
10/01/2019 | 21:21 | LD7 | Urban | Asset Failure | LV | 1 | 68.3 | 0.00010793 | 0.00015799 | No
10/01/2019 | 21:58 | LD2 | Urban | Asset Failure | LV | 78 | 557 | 0.06864 | 0.012323 | No
10/01/2019 | 22:55 | STO21 | Rural Short | Animal | Animal impact | 5 | 385 | 0.032369 | 0.0084075 | No
11/01/2019 | 06:42 | BT15 | Urban | Asset Failure | LV | 1 | 117.3 | 0.00018535 | 0.00015799 | No
11/01/2019 | 08:05 | FSH12 | Rural Short | Asset Failure | LV | 8 | 145 | 0.01931 | 0.013317 | No
11/01/2019 | 08:44 | K13 | Urban | Third Party | Other | 1 | 41 | 6.4776e-05 | 0.00015799 | No
11/01/2019 | 08:52 | CFD13 | Urban | Other | XXX | 1 | 117 | 0.0001849 | 0.00015799 | No
11/01/2019 | 10:00 | LD4 | Urban | Planned |  | 1 | 47.7 | 7.5414e-05 | 0.00015799 | No
11/01/2019 | 10:17 | CDA22 | Urban | Asset Failure | LV | 1 | 102.2 | 0.00016152 | 0.00015799 | No
11/01/2019 | 15:18 | OR24 | Urban | Asset Failure | LV | 18 | 227 | 0.0065093 | 0.0028675 | No
11/01/2019 | 19:31 | RBD12 | Rural Short | Asset Failure | LV | 1 | 357 | 0.0060029 | 0.0016815 | No
11/01/2019 | 21:02 | RBD13 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 178.6 | 0.00028222 | 0.00015799 | No
12/01/2019 | 03:07 | SS23 | Urban | Asset Failure | LV | 1 | 272 | 0.00042973 | 0.00015799 | No
12/01/2019 | 06:37 | MR15 | Urban | Asset Failure | LV | 1 | 142.3 | 0.00022474 | 0.00015799 | No
12/01/2019 | 07:36 | MTN32 | Rural Short | Unknown | Unknown | 1 | 52.1 | 0.00087662 | 0.0016815 | No
12/01/2019 | 10:12 | DC2 | Urban | Unknown | Unknown | 57 | 408 | 0.036742 | 0.0090054 | No
12/01/2019 | 11:26 | DC3 | Urban | Asset Failure | HV | 57 | 125.6 | 0.011311 | 0 | No
12/01/2019 | 11:26 | DC3 | Urban | Asset Failure | HV | 89 | 34 | 0.0047808 | 0 | No
12/01/2019 | 11:45 | LWN21 | Rural Short | Unknown | Unknown | 3 | 155 | 0.0086008 | 0.0055489 | No
12/01/2019 | 14:19 | NW13 | Urban | Vegetation | Grow-in - NSP responsibility | 256 | 111 | 0.044909 | 0.040445 | No
12/01/2019 | 14:23 | NW13 | Urban | Asset Failure | LV | 11 | 727 | 0.012634 | 0.0017379 | No
12/01/2019 | 14:52 | FSH22 | Urban | Third Party | Vehicle Impact | 1 | 117.3 | 0.00018535 | 0.00015799 | No
12/01/2019 | 18:28 | CRM12 | Urban | Unknown | Unknown | 1 | 227 | 0.00035864 | 0.00015799 | No
12/01/2019 | 18:52 | NW13 | Urban | Asset Failure | LV | 12 | 217.6 | 0.0041248 | 0.0018959 | No
13/01/2019 | 03:10 | MTN32 | Rural Short | Animal | Other | 1 | 120 | 0.0020178 | 0.0016815 | No
13/01/2019 | 04:00 | MTN32 | Rural Short | Animal | Other | 1 | 81.7 | 0.0013738 | 0.0016815 | No
13/01/2019 | 09:31 | LWN21 | Rural Short | Animal | Animal impact | 3 | 164 | 0.0082729 | 0.0050445 | No
13/01/2019 | 15:57 | EL13 | Urban | Overloads |  | 29 | 78 | 0.0036329 | 0.0046575 | No
13/01/2019 | 18:14 | CDA23 | Urban | Weather |  | 1 | 138 | 0.00021803 | 0.00015799 | No
14/01/2019 | 02:41 | HGS23 | Rural Short | Animal | Other | 59 | 123 | 0.12285 | 0.099881 | No
14/01/2019 | 02:59 | SS22 | Urban | Unknown | Unknown | 1 | 105.5 | 0.00016668 | 0.00015799 | No
14/01/2019 | 11:06 | BT2 | Urban | Other | XXX | 1 | 160.1 | 0.00025289 | 0.00015799 | No
14/01/2019 | 11:59 | SS21 | Urban | Overloads |  | 6 | 76 | 0.00067361 | 0.00088632 | No
14/01/2019 | 13:00 | NP16 | Urban | Overloads |  | 24 | 169.2 | 0.0063515 | 0.0037538 | No
14/01/2019 | 13:39 | SR23 | Urban | Third Party | Other | 1 | 140.2 | 0.0002215 | 0.00015799 | No
14/01/2019 | 16:45 | HGS22 | Rural Short | Asset Failure | LV | 1 | 102 | 0.0017148 | 0.0016815 | No
14/01/2019 | 17:18 | STO21 | Rural Short | Weather |  | 1 | 72 | 0.0012107 | 0.0016815 | No
14/01/2019 | 17:20 | MTN32 | Rural Short | Asset Failure | LV | 1 | 99.5 | 0.0016725 | 0.0016815 | No
14/01/2019 | 18:01 | LWN35 | Urban | Third Party | Other | 1 | 63.3 | 0.00010003 | 0.00015799 | No
14/01/2019 | 18:17 | CFD13 | Urban | Weather |  | 1 | 87.7 | 0.00013858 | 0.00015799 | No
14/01/2019 | 18:30 | MR15 | Urban | Overloads |  | 54 | 60 | 0.005099 | 0.0084983 | No
14/01/2019 | 18:33 | CRM14 | Urban | Asset Failure | LV | 30 | 107 | 0.0050765 | 0.0047444 | No
14/01/2019 | 18:39 | K2 | Urban | Overloads |  | 17 | 131 | 0.0035515 | 0.0027111 | No
14/01/2019 | 20:12 | LD4 | Urban | Weather |  | 1 | 93 | 0.00014693 | 0.00015799 | No
14/01/2019 | 21:11 | LD6 | Urban | Asset Failure | LV | 296 | 249 | 0.11644 | 0.046765 | No
14/01/2019 | 21:32 | MC6 | Urban | Weather |  | 1 | 101 | 0.00015957 | 0.00015799 | No
15/01/2019 | 01:12 | STO14 | Rural Short | Unknown | Unknown | 136 | 73 | 0.16694 | 0.22868 | No
15/01/2019 | 06:40 | DMA23 | Rural Short | Animal | Other | 20 | 238.6 | 0.080224 | 0.03363 | No
15/01/2019 | 08:35 | STO14 | Rural Short | Asset Failure | HV | 59 | 147 | 0.14584 | 0.099208 | No
15/01/2019 | 08:51 | LWN21 | Rural Short | Unknown | Unknown | 1 | 95.3 | 0.0016025 | 0.0016815 | No
15/01/2019 | 11:15 | WD16 | Urban | Asset Failure | LV | 31 | 160 | 0.0079248 | 0.004953 | No
15/01/2019 | 11:40 | RBD21 | Rural Short | Asset Failure | LV | 1 | 169.1 | 0.002844 | 0.0016815 | No
15/01/2019 | 13:08 | M31 | Urban | Overloads |  | 25 | 119 | 0.0047152 | 0.0039624 | No
15/01/2019 | 13:54 | GW2 | Urban | Asset Failure | LV | 1 | 108.4 | 0.00017131 | 0.00015799 | No
16/01/2019 | 01:25 | FSH21 | Rural Short | Weather |  | 1 | 149.9 | 0.00252 | 0.0016815 | No
16/01/2019 | 03:23 | FSH11 | Urban | Asset Failure | LV | 61 | 72 | 0.0069071 | 0.0095931 | No
16/01/2019 | 07:07 | EW14 | Urban | Asset Failure | LV | 1 | 136.6 | 0.00021587 | 0.00015799 | No
16/01/2019 | 08:41 | BR6 | Urban | Overloads |  | 1 | 158.4 | 0.0002502 | 0.00015799 | No
16/01/2019 | 14:28 | BC23 | Urban | Unknown | Unknown | 1 | 123.1 | 0.00019454 | 0.00015799 | No
16/01/2019 | 14:39 | HGS22 | Rural Short | Unknown | Unknown | 1 | 230 | 0.0038666 | 0.0016815 | No
16/01/2019 | 15:26 | EW2 | Urban | Unknown | Unknown | 1 | 90.8 | 0.00014351 | 0.00015799 | No
16/01/2019 | 15:36 | EB21 | Urban | Asset Failure | LV | 1 | 204 | 0.0003223 | 0.00015799 | No
16/01/2019 | 16:33 | DC3 | Urban | Third Party | Vehicle Impact | 73 | 477 | 0.055014 | 0.011533 | No
16/01/2019 | 20:26 | SR24 | Urban | Asset Failure | LV | 1 | 63.2 | 9.9797e-05 | 0.00015799 | No
17/01/2019 | 00:33 | HGS22 | Rural Short | Animal | Animal impact | 2 | 82 | 0.0027576 | 0.003363 | No
17/01/2019 | 09:56 | EL5 | Urban | Planned |  | 1 | 35.1 | 5.5375e-05 | 0.00015799 | No
17/01/2019 | 11:25 | FTN12 | Urban | Asset Failure | LV | 1 | 50 | 7.8995e-05 | 0.00015799 | No
17/01/2019 | 19:32 | RWT23 | Urban | Asset Failure | LV | 1 | 97 | 0.00015325 | 0.00015799 | No
17/01/2019 | 20:09 | MC2 | Urban | Asset Failure | HV | 1,130 | 76.7 | 0.1369 | 0.17853 | No
17/01/2019 | 20:48 | OR35 | Urban | Overloads |  | 1 | 238 | 0.00037602 | 0.00015799 | No
17/01/2019 | 20:57 | FSH31 | Urban | Asset Failure | LV | 1 | 62 | 9.7954e-05 | 0.00015799 | No
17/01/2019 | 21:06 | DN11 | Urban | Asset Failure | HV | 2,717 | 47.1 | 0.20214 | 0.42926 | No
17/01/2019 | 21:17 | HGS23 | Rural Short | Asset Failure | LV | 4 | 135 | 0.0090801 | 0.006726 | No
17/01/2019 | 21:21 | EL11 | Urban | Overloads |  | 8 | 233.1 | 0.0027948 | 0.0011991 | No
17/01/2019 | 21:40 | NW13 | Urban | Asset Failure | LV | 1 | 50.8 | 8.0285e-05 | 0.00015799 | No
17/01/2019 | 21:44 | MR14 | Urban | Asset Failure | LV | 1 | 228.3 | 0.00036074 | 0.00015799 | No
17/01/2019 | 22:26 | BR6 | Urban | Asset Failure | LV | 42 | 214 | 0.0142 | 0.0066356 | No
18/01/2019 | 03:03 | FSH13 | Urban | Asset Failure | LV | 1 | 86.9 | 0.00013727 | 0.00015799 | No
18/01/2019 | 06:56 | CRM35 | Urban | Asset Failure | LV | 1 | 94 | 0.00014851 | 0.00015799 | No
18/01/2019 | 10:02 | HGS22 | Rural Short | Weather |  | 4 | 253 | 0.017017 | 0.006726 | No
18/01/2019 | 10:07 | HGS23 | Rural Short | Weather |  | 6 | 313 | 0.031578 | 0.010089 | No
18/01/2019 | 10:46 | HGS22 | Rural Short | Weather |  | 1 | 128 | 0.0021526 | 0.0016815 | No
18/01/2019 | 11:52 | HGS23 | Rural Short | Weather |  | 1 | 126.5 | 0.0021274 | 0.0016815 | No
18/01/2019 | 12:44 | DC6 | Urban | Asset Failure | LV | 1 | 115.7 | 0.00018277 | 0.00015799 | No
18/01/2019 | 14:12 | CRM21 | Urban | Asset Failure | LV | 1 | 188 | 0.00029702 | 0.00015799 | No
18/01/2019 | 15:36 | HGS23 | Rural Short | Weather |  | 1 | 350.5 | 0.0058931 | 0.0016815 | No
18/01/2019 | 18:12 | CDA24 | Urban | Asset Failure | LV | 1 | 232.4 | 0.00036709 | 0.00015799 | No
18/01/2019 | 18:29 | RD4 | Urban | Asset Failure | LV | 1 | 150.8 | 0.00023822 | 0.00015799 | No
19/01/2019 | 09:52 | K2 | Urban | Asset Failure | LV | 1 | 93.9 | 0.0001484 | 0.00015799 | No
19/01/2019 | 10:52 | SS24 | Urban | Asset Failure | LV | 1 | 97.4 | 0.00015386 | 0.00015799 | No
19/01/2019 | 11:34 | FTN14 | Urban | Asset Failure | LV | 1 | 81 | 0.00012797 | 0.00015799 | No
19/01/2019 | 13:58 | NP11 | Urban | Third Party | Other | 181 | 27.5 | 0.0078639 | 0.028596 | No
19/01/2019 | 16:36 | M35 | Urban | Unknown | Unknown | 1 | 106 | 0.00016747 | 0.00015799 | No
19/01/2019 | 18:33 | FSH21 | Rural Short | Asset Failure | LV | 1 | 67 | 0.0011266 | 0.0016815 | No
20/01/2019 | 00:42 | NW21 | Urban | Animal | Animal impact | 3,036 | 51.6 | 0.24753 | 0.47966 | No
20/01/2019 | 06:17 | BH12 | Urban | Third Party | Other | 1 | 118 | 0.00018643 | 0.00015799 | No
20/01/2019 | 09:24 | NO7 | Urban | Planned |  | 1 | 123.5 | 0.00019509 | 0.00015799 | No
20/01/2019 | 09:28 | BW23 | Urban | Asset Failure | LV | 1 | 82 | 0.00012955 | 0.00015799 | No
20/01/2019 | 13:58 | GW1 | Urban | Asset Failure | LV | 1 | 91.1 | 0.00014395 | 0.00015799 | No
20/01/2019 | 16:31 | BH23 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 78.4 | 0.00012381 | 0.00015799 | No
20/01/2019 | 20:47 | CRM21 | Urban | Asset Failure | LV | 1 | 84.2 | 0.000133 | 0.00015799 | No
20/01/2019 | 23:17 | CRM21 | Urban | Asset Failure | LV | 1 | 237.5 | 0.00037515 | 0.00015799 | No
20/01/2019 | 23:35 | KBH32 | Urban | Asset Failure | LV | 35 | 130 | 0.0071885 | 0.0055296 | No
21/01/2019 | 06:07 | HGS33 | Rural Short | Animal | Other | 1 | 132.5 | 0.0022285 | 0.0016815 | No
21/01/2019 | 07:52 | LWN35 | Urban | Asset Failure | LV | 1 | 112.6 | 0.00017782 | 0.00015799 | No
21/01/2019 | 13:01 | CRM35 | Urban | Asset Failure | Distribution substation | 2 | 358.5 | 0.0011327 | 0.00031598 | No
21/01/2019 | 15:19 | CRM34 | Urban | Other | XXX | 1 | 145.8 | 0.00023027 | 0.00015799 | No
21/01/2019 | 15:38 | NB33 | Urban | Other | XXX | 1 | 106.3 | 0.00016789 | 0.00015799 | No
21/01/2019 | 15:51 | DVY14 | Urban | Other | XXX | 1 | 188.2 | 0.00029739 | 0.00015799 | No
21/01/2019 | 16:07 | NO32 | Urban | Other | XXX | 1 | 60.4 | 9.5478e-05 | 0.00015799 | No
21/01/2019 | 16:36 | GW6 | Urban | Other | XXX | 1 | 116.3 | 0.00018377 | 0.00015799 | No
21/01/2019 | 19:28 | EB22 | Urban | Asset Failure | LV | 1 | 92 | 0.00014535 | 0.00015799 | No
22/01/2019 | 07:15 | DC2 | Urban | Asset Failure | HV | 1,765 | 87 | 0.24264 | 0.27885 | No
22/01/2019 | 09:19 | SS13 | Urban | Third Party | Other | 15 | 191 | 0.0043816 | 0.002294 | No
22/01/2019 | 11:01 | NO32 | Urban | Asset Failure | LV | 1 | 216.3 | 0.00034178 | 0.00015799 | No
22/01/2019 | 17:42 | CM13 | Urban | Asset Failure | LV | 1 | 192.3 | 0.00030387 | 0.00015799 | No
22/01/2019 | 19:54 | CRM22 | Urban | Asset Failure | LV | 1 | 119 | 0.00018801 | 0.00015799 | No
22/01/2019 | 20:21 | FSH13 | Urban | Asset Failure | LV | 1 | 166 | 0.00026226 | 0.00015799 | No
22/01/2019 | 21:18 | EL10 | Urban | Asset Failure | LV | 2 | 56.5 | 0.00017848 | 0.00031598 | No
22/01/2019 | 22:22 | GW4 | Urban | Asset Failure | LV | 1 | 67 | 0.00010577 | 0.00015799 | No
23/01/2019 | 07:05 | DVY13 | Urban | Other | XXX | 2 | 15 | 4.7397e-05 | 0.00031598 | No
23/01/2019 | 09:50 | FSH11 | Urban | Asset Failure | LV | 13 | 219.7 | 0.0045123 | 0.0020539 | No
23/01/2019 | 10:10 | MTN32 | Rural Short | Vegetation | Grow-in - NSP responsibility | 12 | 90 | 0.017979 | 0.019976 | No
23/01/2019 | 14:07 | HT1 | Urban | Asset Failure | LV | 90 | 93 | 0.013224 | 0.014219 | No
23/01/2019 | 14:50 | HT11 | Urban | Asset Failure | LV | 1 | 83.4 | 0.00013176 | 0.00015799 | No
23/01/2019 | 15:08 | MTN32 | Rural Short | Unknown | Unknown | 1 | 102.7 | 0.0017272 | 0.0016815 | No
23/01/2019 | 20:30 | WD36 | Urban | Vegetation | Grow-in - Other responsible party | 9 | 275.3 | 0.0039141 | 0.0014219 | No
24/01/2019 | 06:10 | HGS33 | Rural Short | Unknown | Unknown | 53 | 90 | 0.080207 | 0.089119 | No
24/01/2019 | 07:29 | RBD24 | Urban | Weather |  | 13 | 163 | 0.0033993 | 0.0020855 | No
24/01/2019 | 07:57 | LWN35 | Urban | Asset Failure | LV | 1 | 57 | 9.0054e-05 | 0.00015799 | No
24/01/2019 | 08:30 | HGS23 | Rural Short | Vegetation | Grow-in - NSP responsibility | 5 | 57.5 | 0.0048329 | 0.0084075 | No
24/01/2019 | 09:51 | K8 | Urban | Animal | Other | 1,223 | 39.2 | 0.075836 | 0.19322 | No
24/01/2019 | 10:50 | SS11 | Urban | Weather |  | 1 | 130 | 0.00020539 | 0.00015799 | No
24/01/2019 | 11:11 | FTN14 | Urban | Weather |  | 2 | 91.3 | 0.00028844 | 0.00031598 | No
24/01/2019 | 14:46 | EL5 | Urban | Overloads |  | 52 | 89 | 0.0073118 | 0.0082155 | No
24/01/2019 | 15:22 | LD7 | Urban | Unknown | Unknown | 1 | 127.5 | 0.00020146 | 0.00015799 | No
24/01/2019 | 15:33 | HGS23 | Rural Short | Unknown | Unknown | 1 | 147.6 | 0.0024813 | 0.0016815 | No
24/01/2019 | 15:37 | RWT34 | Urban | Asset Failure | LV | 1 | 91 | 0.00014377 | 0.00015799 | No
24/01/2019 | 16:12 | MC6 | Urban | Asset Failure | Distribution substation | 56 | 153 | 0.013481 | 0.0088111 | No
24/01/2019 | 16:36 | BW33 | Urban | Asset Failure | LV | 2 | 54 | 0.00014077 | 0.00026068 | No
24/01/2019 | 17:08 | MR31 | Urban | Overloads |  | 56 | 122 | 0.010794 | 0.0088474 | No
24/01/2019 | 17:08 | GW8 | Urban | Weather |  | 1 | 56 | 8.8474e-05 | 0.00015799 | No
24/01/2019 | 17:29 | SV20 | Urban | Asset Failure | HV | 1 | 2,820.5 | 0.004456 | 0.00015799 | No
24/01/2019 | 17:30 | MR31 | Urban | Asset Failure | LV | 94 | 640.2 | 0.095074 | 0.014851 | No
24/01/2019 | 17:41 | EM8 | Urban | Overloads |  | 21 | 64 | 0.0021689 | 0.0033889 | No
24/01/2019 | 17:43 | MTN22 | Rural Short | Asset Failure | LV | 34 | 111 | 0.063441 | 0.057154 | No
24/01/2019 | 17:50 | HGS31 | Rural Short | Other | XXX | 1 | 99.5 | 0.0016722 | 0.0016815 | No
24/01/2019 | 17:56 | MTN31 | Urban | Overloads |  | 25 | 164 | 0.0065838 | 0.0040145 | No
24/01/2019 | 18:04 | HGS21 | Rural Short | Overloads |  | 45 | 121 | 0.090642 | 0.07491 | No
24/01/2019 | 18:06 | MTN34 | Urban | Overloads |  | 93 | 214 | 0.031443 | 0.014693 | No
24/01/2019 | 18:10 | RWT34 | Urban | Overloads |  | 24 | 170 | 0.0064702 | 0.003806 | No
24/01/2019 | 18:17 | NW11 | Urban | Overloads |  | 1 | 341.9 | 0.00054011 | 0.00015799 | No
24/01/2019 | 18:30 | MR31 | Urban | Overloads |  | 21 | 100 | 0.0032814 | 0.0032814 | No
24/01/2019 | 18:30 | GW1 | Urban | Overloads |  | 1 | 359.2 | 0.00056753 | 0.00015799 | No
24/01/2019 | 18:35 | K2 | Urban | Overloads |  | 59 | 85 | 0.0078883 | 0.0092803 | No
24/01/2019 | 18:41 | MTN31 | Urban | Overloads |  | 20 | 164 | 0.0053013 | 0.0032325 | No
24/01/2019 | 18:44 | HGS22 | Rural Short | Overloads |  | 17 | 96 | 0.0277 | 0.028854 | No
24/01/2019 | 18:44 | NP23 | Urban | Overloads |  | 19 | 136 | 0.0040416 | 0.0029718 | No
24/01/2019 | 18:46 | MTN35 | Rural Short | Unknown | Unknown | 1 | 178.7 | 0.0030051 | 0.0016815 | No
24/01/2019 | 18:53 | MR12 | Urban | Asset Failure | LV | 1 | 369 | 0.00058298 | 0.00015799 | No
24/01/2019 | 19:00 | MGE12 | Urban | Overloads |  | 25 | 90 | 0.0036131 | 0.0040145 | No
24/01/2019 | 19:06 | LWN24 | Urban | Overloads |  | 36 | 174 | 0.009979 | 0.005735 | No
24/01/2019 | 19:06 | SS13 | Urban | Unknown | Unknown | 37 | 74 | 0.0042825 | 0.0057872 | No
24/01/2019 | 19:06 | NP33 | Urban | Overloads |  | 17 | 74 | 0.0019676 | 0.002659 | No
24/01/2019 | 19:09 | BH11 | Urban | Asset Failure | LV | 93 | 231 | 0.033941 | 0.014693 | No
24/01/2019 | 19:09 | EL9 | Urban | Overloads |  | 11 | 96 | 0.0016016 | 0.0016684 | No
24/01/2019 | 19:10 | RWT35 | Urban | Overloads |  | 18 | 140 | 0.0040145 | 0.0028675 | No
24/01/2019 | 19:11 | DC1 | Urban | Overloads |  | 32 | 135 | 0.0068252 | 0.0050557 | No
24/01/2019 | 19:14 | DMA14 | Urban | Overloads |  | 10 | 61 | 0.0009541 | 0.0015641 | No
24/01/2019 | 19:18 | OR35 | Urban | Asset Failure | LV | 50 | 132.6 | 0.010504 | 0.0079248 | No
24/01/2019 | 19:18 | NP12 | Urban | Asset Failure | LV | 2 | 252 | 0.00074053 | 0.00029386 | No
24/01/2019 | 19:29 | RWT35 | Urban | Overloads |  | 1 | 180.7 | 0.00028551 | 0.00015799 | No
24/01/2019 | 19:36 | NB35 | Urban | Asset Failure | LV | 1 | 393.9 | 0.00062237 | 0.00015799 | No
24/01/2019 | 19:39 | BU2 | Urban | Asset Failure | LV | 34 | 291 | 0.015632 | 0.0053717 | No
24/01/2019 | 19:40 | EM8 | Urban | Overloads |  | 1 | 124.3 | 0.0001963 | 0.00015799 | No
24/01/2019 | 19:46 | LD6 | Urban | Overloads |  | 15 | 119 | 0.0027919 | 0.0023461 | No
24/01/2019 | 19:46 | LD6 | Urban | Overloads |  | 11 | 119 | 0.0021094 | 0.0017726 | No
24/01/2019 | 19:46 | OR35 | Urban | Asset Failure | LV | 1 | 108.9 | 0.00017208 | 0.00015799 | No
24/01/2019 | 20:18 | RWT23 | Urban | Overloads |  | 21 | 82 | 0.0026934 | 0.0032846 | No
24/01/2019 | 20:31 | LD7 | Urban | Overloads |  | 1 | 224 | 0.0003539 | 0.00015799 | No
24/01/2019 | 20:31 | OR35 | Urban | Overloads |  | 20 | 49 | 0.0015584 | 0.0031803 | No
24/01/2019 | 20:39 | CDA23 | Urban | Asset Failure | LV | 1 | 193 | 0.00030497 | 0.00015799 | No
24/01/2019 | 20:55 | K2 | Urban | Overloads |  | 17 | 84.6 | 0.0022945 | 0.0027111 | No
24/01/2019 | 21:08 | CFD24 | Urban | Overloads |  | 21 | 63 | 0.002135 | 0.0033889 | No
24/01/2019 | 21:16 | MGE12 | Urban | Overloads |  | 25 | 108 | 0.0043357 | 0.0040145 | No
24/01/2019 | 21:30 | MTN35 | Rural Short | Unknown | Unknown | 1 | 15 | 0.00025222 | 0.0016815 | No
24/01/2019 | 21:30 | RBD21 | Rural Short | Animal | Animal impact | 560 | 77.7 | 0.73157 | 0.94164 | No
24/01/2019 | 21:31 | EL9 | Urban | Overloads |  | 22 | 89 | 0.0030625 | 0.003441 | No
24/01/2019 | 21:33 | MGE12 | Urban | Overloads |  | 13 | 115 | 0.0022784 | 0.0019812 | No
24/01/2019 | 22:05 | DMA24 | Rural Short | Asset Failure | LV | 1 | 174.4 | 0.0029325 | 0.0016815 | No
24/01/2019 | 22:10 | DMA24 | Rural Short | Asset Failure | LV | 1 | 169.2 | 0.0028448 | 0.0016815 | No
24/01/2019 | 22:43 | FSH22 | Urban | Overloads |  | 1 | 121.4 | 0.00019172 | 0.00015799 | No
24/01/2019 | 23:07 | BU10 | Urban | Vegetation | Grow-in - NSP responsibility | 1,810 | 44.7 | 0.12796 | 0.28596 | No
24/01/2019 | 23:28 | MR32 | Urban | Asset Failure | LV | 1 | 127 | 0.00020065 | 0.00015799 | No
25/01/2019 | 00:08 | MGE12 | Urban | Overloads |  | 13 | 67 | 0.0013274 | 0.0019812 | No
25/01/2019 | 02:10 | BU10 | Urban | Vegetation | Grow-in - NSP responsibility | 45 | 512 | 0.036401 | 0.0071095 | No
25/01/2019 | 06:29 | RBD12 | Rural Short | Asset Failure | LV | 2 | 150.6 | 0.0050652 | 0.003363 | No
25/01/2019 | 08:15 | MR22 | Urban | Overloads |  | 111 | 73 | 0.012802 | 0.017537 | No
25/01/2019 | 09:44 | NP14 | Urban | Overloads |  | 1 | 24.8 | 3.9208e-05 | 0.00015799 | No
25/01/2019 | 09:51 | DMA23 | Rural Short | Asset Failure | HV | 27 | 648.6 | 0.29444 | 0.0454 | No
25/01/2019 | 10:13 | DC4 | Urban | Overloads |  | 21 | 164 | 0.0053868 | 0.0032846 | No
25/01/2019 | 10:22 | DC8 | Urban | Vegetation | Grow-in - NSP responsibility | 33 | 178 | 0.0092803 | 0.0052137 | No
25/01/2019 | 10:27 | MGE34 | Urban | Vegetation | Grow-in - Other responsible party | 422 | 33 | 0.021979 | 0.066672 | No
25/01/2019 | 10:28 | GW8 | Urban | Vegetation | Grow-in - NSP responsibility | 35 | 330 | 0.018237 | 0.0055265 | No
25/01/2019 | 10:45 | NP14 | Urban | Overloads |  | 1 | 38.1 | 6.0115e-05 | 0.00015799 | No
25/01/2019 | 11:01 | RWT35 | Urban | Weather |  | 31 | 209 | 0.010352 | 0.004953 | No
25/01/2019 | 11:05 | MC7 | Urban | Overloads |  | 1 | 114.1 | 0.00018021 | 0.00015799 | No
25/01/2019 | 11:21 | NB23 | Urban | Overloads |  | 34 | 158 | 0.0084023 | 0.0053179 | No
25/01/2019 | 11:23 | NB24 | Urban | Overloads |  | 13 | 246 | 0.005002 | 0.0020333 | No
25/01/2019 | 11:27 | MR31 | Urban | Asset Failure | LV | 1 | 269.9 | 0.00042641 | 0.00015799 | No
25/01/2019 | 11:38 | SS13 | Urban | Overloads |  | 18 | 127 | 0.0036417 | 0.0028675 | No
25/01/2019 | 11:54 | AR7 | Urban | Overloads |  | 110 | 66 | 0.01147 | 0.017379 | No
25/01/2019 | 12:10 | OR32 | Urban | Overloads |  | 1 | 230.5 | 0.00036422 | 0.00015799 | No
25/01/2019 | 12:10 | FSH33 | Urban | Unknown | Unknown | 1 | 66.3 | 0.00010475 | 0.00015799 | No
25/01/2019 | 12:23 | BU4 | Urban | Asset Failure | LV | 109 | 297 | 0.051146 | 0.017221 | No
25/01/2019 | 12:59 | MR13 | Urban | Overloads |  | 55 | 121 | 0.010598 | 0.008759 | No
25/01/2019 | 13:21 | M22 | Urban | Overloads |  | 59 | 164 | 0.015391 | 0.0093846 | No
25/01/2019 | 13:30 | K3 | Urban | Overloads |  | 27 | 166 | 0.0070811 | 0.0042657 | No
25/01/2019 | 13:39 | STO13 | Urban | Other | XXX | 1 | 184.9 | 0.0002921 | 0.00015799 | No
25/01/2019 | 13:42 | BW22 | Urban | Unknown | Unknown | 50 | 152 | 0.012007 | 0.0078995 | No
25/01/2019 | 14:03 | MGE12 | Urban | Overloads |  | 25 | 162 | 0.0064191 | 0.0039624 | No
25/01/2019 | 14:20 | FSH33 | Urban | Overloads |  | 16 | 190 | 0.0048539 | 0.0025547 | No
25/01/2019 | 14:23 | CFD25 | Urban | Unknown | Unknown | 73 | 102 | 0.011764 | 0.011533 | No
25/01/2019 | 14:28 | MR11 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 61.7 | 9.7427e-05 | 0.00015799 | No
25/01/2019 | 14:43 | AR7 | Urban | Overloads |  | 36 | 121.4 | 0.0069633 | 0.005735 | No
25/01/2019 | 15:03 | BR6 | Urban | Unknown | Unknown | 1 | 111.5 | 0.00017608 | 0.00015799 | No
25/01/2019 | 15:05 | K2 | Urban | Overloads |  | 8 | 122.8 | 0.0014725 | 0.0011991 | No
25/01/2019 | 15:55 | MC2 | Urban | Asset Failure | LV | 25 | 214 | 0.0084795 | 0.0039624 | No
25/01/2019 | 16:53 | OAK32 | Urban | Vegetation | Grow-in - NSP responsibility | 48 | 12 | 0.00091002 | 0.0075835 | No
25/01/2019 | 16:57 | NW21 | Urban | Asset Failure | LV | 1 | 64 | 0.00010111 | 0.00015799 | No
25/01/2019 | 17:15 | K12 | Urban | Overloads |  | 141 | 90 | 0.019989 | 0.02221 | No
25/01/2019 | 17:15 | K10 | Urban | Overloads |  | 140 | 165 | 0.036496 | 0.022119 | No
25/01/2019 | 17:59 | MTN22 | Rural Short | Overloads |  | 25 | 46 | 0.019144 | 0.041617 | No
25/01/2019 | 18:42 | LD2 | Urban | Weather |  | 1 | 33 | 5.2137e-05 | 0.00015799 | No
25/01/2019 | 18:46 | OAK22 | Urban | Weather |  | 1 | 140 | 0.00022119 | 0.00015799 | No
25/01/2019 | 19:17 | K12 | Urban | Overloads |  | 141 | 87.1 | 0.019352 | 0.02221 | No
25/01/2019 | 19:39 | FSH11 | Urban | Asset Failure | LV | 1 | 81 | 0.00012797 | 0.00015799 | No
25/01/2019 | 23:06 | SH22 | Urban | Overloads |  | 35 | 53.3 | 0.0029725 | 0.0055786 | No
26/01/2019 | 01:04 | GW1 | Urban | Animal | Other | 115 | 62 | 0.011265 | 0.018169 | No
26/01/2019 | 02:10 | DC8 | Urban | Animal | Other | 70 | 73 | 0.0080733 | 0.011059 | No
26/01/2019 | 06:40 | STO13 | Urban | Unknown | Unknown | 1 | 639.5 | 0.0010104 | 0.00015799 | No
26/01/2019 | 10:00 | FSH34 | Urban | Unknown | Unknown | 1 | 11 | 1.7379e-05 | 0.00015799 | No
26/01/2019 | 10:44 | HT11 | Urban | Asset Failure | HV | 49 | 508.6 | 0.039376 | 0.0077415 | No
26/01/2019 | 11:00 | EW8 | Urban | Asset Failure | LV | 1 | 419.6 | 0.00066285 | 0.00015799 | No
26/01/2019 | 19:16 | BH31 | Urban | Asset Failure | Distribution substation | 54 | 97 | 0.0083445 | 0.0086025 | No
26/01/2019 | 19:45 | WD14 | Urban | Asset Failure | Distribution substation | 50 | 150 | 0.011809 | 0.0078726 | No
27/01/2019 | 08:06 | DMA23 | Rural Short | Asset Failure | LV | 1 | 123.4 | 0.0020744 | 0.0016815 | No
27/01/2019 | 08:57 | STO14 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 184 | 0.0030939 | 0.0016815 | No
27/01/2019 | 09:47 | CRM24 | Urban | Asset Failure | LV | 2 | 147.4 | 0.00044702 | 0.00030334 | No
27/01/2019 | 11:10 | FSH34 | Urban | Vegetation | Grow-in - Other responsible party | 96 | 80 | 0.012134 | 0.015167 | No
27/01/2019 | 12:19 | LWN34 | Urban | Asset Failure | LV | 11 | 101 | 0.0017904 | 0.0017726 | No
27/01/2019 | 15:39 | DN22 | Urban | Third Party | Vehicle Impact | 1,221 | 236.3 | 0.45576 | 0.19291 | No
27/01/2019 | 15:39 | DN22 | Urban |  | HV | 3,628 | 23.3 | 0.13336 | 0.57319 | No
27/01/2019 | 18:06 | MGE24 | Urban | Vegetation | Grow-in - NSP responsibility | 30 | 194 | 0.0093054 | 0.0047966 | No
27/01/2019 | 18:07 | DN22 | Urban | Unknown | Unknown | 57 | 453 | 0.040795 | 0.0090054 | No
27/01/2019 | 21:08 | LD4 | Urban | Asset Failure | LV | 1 | 66.7 | 0.00010535 | 0.00015799 | No
27/01/2019 | 22:20 | BH31 | Urban | Third Party | Other | 10 | 170 | 0.0025515 | 0.0015009 | No
28/01/2019 | 07:50 | RBD12 | Rural Short | Asset Failure | LV | 2 | 119.9 | 0.0040311 | 0.003363 | No
28/01/2019 | 09:38 | DVY22 | Urban | Asset Failure | LV | 6 | 81.8 | 0.00076797 | 0.00093846 | No
28/01/2019 | 10:28 | EB11 | Urban | Asset Failure | LV | 1 | 61.7 | 9.7401e-05 | 0.00015799 | No
28/01/2019 | 14:04 | STO22 | Urban | Asset Failure | LV | 1 | 120.8 | 0.0001908 | 0.00015799 | No
28/01/2019 | 14:22 | KBH34 | Urban | Asset Failure | LV | 1 | 68 | 0.00010743 | 0.00015799 | No
28/01/2019 | 15:21 | BW21 | Urban | Asset Failure | LV | 1 | 103.4 | 0.00016333 | 0.00015799 | No
28/01/2019 | 17:46 | OAK32 | Urban | Third Party | Other | 10 | 94 | 0.0015193 | 0.0016162 | No
28/01/2019 | 18:45 | CFD16 | Urban | Asset Failure | LV | 1 | 89 | 0.00014061 | 0.00015799 | No
28/01/2019 | 19:38 | STO23 | Urban | Asset Failure | LV | 1 | 112 | 0.00017695 | 0.00015799 | No
29/01/2019 | 10:28 | CFD24 | Urban | Asset Failure | LV | 1 | 152 | 0.00024017 | 0.00015799 | No
29/01/2019 | 10:51 | LD7 | Urban | Animal | Other | 1,615 | 67.1 | 0.17116 | 0.25515 | No
29/01/2019 | 10:58 | NO2 | Urban | Asset Failure | LV | 1 | 150.6 | 0.00023798 | 0.00015799 | No
29/01/2019 | 12:05 | FSH31 | Urban | Asset Failure | LV | 1 | 95.7 | 0.00015117 | 0.00015799 | No
29/01/2019 | 12:30 | MC10 | Urban | Unknown | Unknown | 1 | 210.3 | 0.00022264 | 0.00010585 | No
29/01/2019 | 12:37 | EL5 | Urban | Overloads |  | 17 | 71 | 0.0019249 | 0.0027111 | No
29/01/2019 | 14:36 | EL5 | Urban | Overloads |  | 17 | 69 | 0.0018707 | 0.0027111 | No
29/01/2019 | 15:00 | DN10 | Urban | Unknown | Unknown | 29 | 27 | 0.0012371 | 0.0045817 | No
29/01/2019 | 16:48 | WD34 | Urban | Asset Failure | LV | 1 | 232 | 0.00036654 | 0.00015799 | No
29/01/2019 | 17:05 | DC6 | Urban | Third Party | Other | 1 | 114.8 | 0.00018137 | 0.00015799 | No
29/01/2019 | 17:19 | DC6 | Urban | Third Party | Other | 1 | 100.3 | 0.00015852 | 0.00015799 | No
29/01/2019 | 17:40 | DN21 | Urban | Asset Failure | LV | 1 | 215 | 0.00033968 | 0.00015799 | No
29/01/2019 | 18:11 | LWN24 | Urban | Asset Failure | LV | 28 | 174 | 0.0077577 | 0.0044585 | No
29/01/2019 | 19:42 | CRM22 | Urban | Third Party | Other | 1 | 137.7 | 0.00021753 | 0.00015799 | No
29/01/2019 | 19:53 | BW33 | Urban | Asset Failure | LV | 1 | 157 | 0.00024804 | 0.00015799 | No
29/01/2019 | 19:57 | M34 | Urban | Asset Failure | LV | 1 | 138 | 0.00021803 | 0.00015799 | No
30/01/2019 | 04:58 | HGS31 | Rural Short | Animal | Other | 1 | 117 | 0.0019673 | 0.0016815 | No
30/01/2019 | 07:50 | NB25 | Urban | Overloads |  | 13 | 280 | 0.0058393 | 0.0020855 | No
30/01/2019 | 09:59 | MR21 | Urban | Asset Failure | Distribution substation | 36 | 588 | 0.033722 | 0.005735 | No
30/01/2019 | 10:46 | STO21 | Rural Short | Asset Failure | HV | 324 | 94.3 | 0.51384 | 0.5448 | No
30/01/2019 | 11:26 | EL5 | Urban | Overloads |  | 17 | 334 | 0.0090537 | 0.0027111 | No
30/01/2019 | 11:47 | NW23 | Urban | Unknown | Unknown | 1 | 132.7 | 0.00020968 | 0.00015799 | No
30/01/2019 | 13:20 | HT1 | Urban | Overloads |  | 18 | 115 | 0.0033576 | 0.0029197 | No
30/01/2019 | 13:27 | DN6 | Urban | Asset Failure | LV | 1 | 172.6 | 0.00027264 | 0.00015799 | No
30/01/2019 | 13:27 | STO21 | Rural Short | Asset Failure | LV | 1 | 122.2 | 0.0020553 | 0.0016815 | No
30/01/2019 | 13:28 | LD6 | Urban | Unknown | Unknown | 1 | 341.8 | 0.00054004 | 0.00015799 | No
30/01/2019 | 13:48 | CFD12 | Urban | Overloads |  | 18 | 182 | 0.005124 | 0.0028154 | No
30/01/2019 | 14:46 | NB24 | Urban | Overloads |  | 13 | 379 | 0.0077063 | 0.0020333 | No
30/01/2019 | 16:23 | CDA23 | Urban | Asset Failure | LV | 1 | 125.8 | 0.00019867 | 0.00015799 | No
30/01/2019 | 16:50 | MC7 | Urban | Overloads |  | 3 | 354.4 | 0.001478 | 0.00041709 | No
30/01/2019 | 16:55 | DC2 | Urban | Weather |  | 187 | 13.1 | 0.0038752 | 0.029544 | No
30/01/2019 | 16:55 | DC1 | Urban | Weather |  | 1,074 | 99.1 | 0.16809 | 0.16968 | No
30/01/2019 | 16:58 | NW13 | Urban | Weather |  | 3,213 | 116.1 | 0.58953 | 0.50762 | No
30/01/2019 | 17:04 | NB35 | Urban | Unknown | Unknown | 1 | 655.4 | 0.0010354 | 0.00015799 | No
30/01/2019 | 17:05 | RWT12 | Urban |  |  | 232 | 254.2 | 0.093167 | 0.036654 | No
30/01/2019 | 17:25 | LWN21 | Rural Short |  |  | 3,107 | 66.7 | 3.4858 | 5.2244 | No
30/01/2019 | 17:25 | MGE12 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1,129 | 152.3 | 0.2716 | 0.17837 | No
30/01/2019 | 17:26 | CRM35 | Urban | Asset Failure | Distribution substation | 46 | 304 | 0.021872 | 0.0071949 | No
30/01/2019 | 17:26 | LWN32 | Rural Short | Weather |  | 1,312 | 157.5 | 3.4736 | 2.2061 | No
30/01/2019 | 17:26 | LWN23 | Urban | Weather |  | 1,841 | 191.7 | 0.55749 | 0.29086 | No
30/01/2019 | 17:27 | CRM33 | Urban |  |  | 311 | 145.1 | 0.071286 | 0.049135 | No
30/01/2019 | 17:27 | FTN13 | Urban | Weather |  | 16 | 63 | 0.0015766 | 0.0025026 | No
30/01/2019 | 17:27 | DVY34 | Urban |  |  | 721 | 80.2 | 0.091363 | 0.11391 | No
30/01/2019 | 17:28 | DVY24 | Rural Short |  |  | 319 | 97.8 | 0.52478 | 0.5364 | No
30/01/2019 | 17:29 | CRM35 | Urban |  |  | 17 | 571 | 0.015336 | 0.0026858 | No
30/01/2019 | 17:35 | CRM33 | Urban | Weather |  | 209 | 225.7 | 0.074526 | 0.03302 | No
30/01/2019 | 17:43 | BU4 | Urban | Vegetation | Grow-in - NSP responsibility | 10 | 377 | 0.0060932 | 0.0016162 | No
30/01/2019 | 17:54 | NO5 | Urban | Weather |  | 184 | 193.9 | 0.056354 | 0.02907 | No
30/01/2019 | 18:32 | NW13 | Urban | Vegetation | Grow-in - Other responsible party | 45 | 982.9 | 0.069881 | 0.0071095 | No
30/01/2019 | 18:40 | EB22 | Urban | Asset Failure | LV | 1 | 257 | 0.00040603 | 0.00015799 | No
30/01/2019 | 19:00 | CRM33 | Urban | Vegetation | Grow-in - Other responsible party | 311 | 20 | 0.009827 | 0.049135 | No
30/01/2019 | 19:40 | LWN21 | Rural Short | Weather |  | 1 | 794.4 | 0.013358 | 0.0016815 | No
30/01/2019 | 19:51 | DC1 | Urban | Vegetation | Grow-in - Other responsible party | 15 | 828.1 | 0.019624 | 0.0023698 | No
30/01/2019 | 20:19 | NB35 | Urban | Asset Failure | LV | 1 | 1,120.3 | 0.0017699 | 0.00015799 | No
30/01/2019 | 20:24 | LWN23 | Urban | Weather |  | 697 | 1.3 | 0.0014315 | 0.11012 | No
30/01/2019 | 20:24 | LWN32 | Rural Short | Weather |  | 908 | 1.3 | 0.019848 | 1.5268 | No
30/01/2019 | 20:41 | LWN24 | Urban | Weather |  | 36 | 239 | 0.013707 | 0.005735 | No
30/01/2019 | 20:52 | AR3 | Urban | Asset Failure | LV | 1 | 87.2 | 0.00013779 | 0.00015799 | No
30/01/2019 | 21:03 | LWN21 | Rural Short | Vegetation | Grow-in - Other responsible party | 2 | 1,092.0 | 0.030297 | 0.0027745 | No
30/01/2019 | 21:09 | LWN21 | Rural Short |  |  | 6 | 447 | 0.045099 | 0.010089 | No
30/01/2019 | 21:13 | DMA21 | Urban | Weather |  | 1 | 796.1 | 0.0012578 | 0.00015799 | No
30/01/2019 | 21:17 | NW22 | Urban | Weather |  | 1 | 101.3 | 0.00016004 | 0.00015799 | No
30/01/2019 | 21:37 | CDA23 | Urban | Weather |  | 214 | 250 | 0.084525 | 0.03381 | No
30/01/2019 | 23:16 | CDA23 | Urban | Third Party | Other | 1 | 89 | 0.00014061 | 0.00015799 | No
31/01/2019 | 01:22 | DMA15 | Rural Short | Weather |  | 32 | 458 | 0.24644 | 0.053808 | No
31/01/2019 | 03:03 | NW13 | Urban | Weather |  | 47 | 22.7 | 0.0016819 | 0.0074255 | No
31/01/2019 | 04:59 | BT5 | Urban | Weather |  | 1 | 681 | 0.0010758 | 0.00015799 | No
31/01/2019 | 06:27 | AR7 | Urban | Asset Failure | LV | 36 | 167 | 0.0095775 | 0.005735 | No
31/01/2019 | 07:17 | DC5 | Urban | Asset Failure | LV | 1 | 507.9 | 0.00080235 | 0.00015799 | No
31/01/2019 | 07:21 | LWN21 | Rural Short | Weather |  | 9 | 269.9 | 0.040838 | 0.015133 | No
31/01/2019 | 07:50 | DMA24 | Rural Short | Weather |  | 1 | 249 | 0.0041866 | 0.0016815 | No
31/01/2019 | 08:34 | LWN21 | Rural Short | Weather |  | 3 | 4.3 | 0.00021859 | 0.0050445 | No
31/01/2019 | 09:23 | NP36 | Urban | Asset Failure | LV | 1 | 148.7 | 0.00023493 | 0.00015799 | No
31/01/2019 | 09:32 | NW33 | Urban | Third Party | Other | 1 | 430 | 0.00067938 | 0.00015799 | No
31/01/2019 | 10:24 | CM25 | Urban | Asset Failure | LV | 1 | 155.2 | 0.00024512 | 0.00015799 | No
31/01/2019 | 11:05 | NP36 | Urban | Asset Failure | LV | 1 | 46.9 | 7.4071e-05 | 0.00015799 | No
31/01/2019 | 12:30 | OR33 | Urban | Asset Failure | LV | 1 | 434.2 | 0.00068602 | 0.00015799 | No
31/01/2019 | 13:06 | GW7 | Urban | Third Party | Other | 1 | 229.7 | 0.00036285 | 0.00015799 | No
31/01/2019 | 13:46 | LWN21 | Rural Short | Weather |  | 18 | 63.5 | 0.019204 | 0.030267 | No
31/01/2019 | 14:15 | GW8 | Urban | Other | XXX | 1 | 274.7 | 0.00043392 | 0.00015799 | No
31/01/2019 | 15:14 | WD23 | Urban | Asset Failure | LV | 1 | 164.9 | 0.0002605 | 0.00015799 | No
31/01/2019 | 15:34 | DC1 | Urban | Overloads |  | 1 | 220.2 | 0.00034782 | 0.00015799 | No
31/01/2019 | 15:45 | EM9 | Urban | Weather |  | 1 | 254.8 | 0.00040261 | 0.00015799 | No
31/01/2019 | 16:21 | LWN24 | Urban | Asset Failure | LV | 1 | 119 | 0.00018801 | 0.00015799 | No
31/01/2019 | 16:22 | EW2 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 207.3 | 0.00032757 | 0.00015799 | No
31/01/2019 | 16:37 | EW2 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 192.9 | 0.00030471 | 0.00015799 | No
31/01/2019 | 16:55 | CDA23 | Urban | Weather |  | 1 | 63.8 | 0.00010074 | 0.00015799 | No
31/01/2019 | 18:00 | NB35 | Urban | Overloads |  | 1 | 89.8 | 0.00014182 | 0.00015799 | No
31/01/2019 | 18:15 | EW2 | Urban | Asset Failure | LV | 1 | 94.3 | 0.00014891 | 0 | No
31/01/2019 | 18:32 | EW2 | Urban | Asset Failure | LV | 1 | 77.2 | 0.00012197 | 0.00015799 | No
31/01/2019 | 19:15 | WD36 | Urban | Vegetation | Grow-in - NSP responsibility | 17 | 88 | 0.0023858 | 0.0027111 | No
31/01/2019 | 21:11 | DC1 | Urban | Asset Failure | LV | 15 | 78.4 | 0.0017968 | 0.0022909 | No
31/01/2019 | 22:37 | MTN31 | Urban | Third Party | Vehicle Impact | 62 | 293 | 0.0287 | 0.0097954 | No
31/01/2019 | 23:07 | STO21 | Rural Short | Asset Failure | HV | 153 | 190.8 | 0.49078 | 0.25727 | No
01/02/2019 | 06:01 | SV32 | Urban | Asset Failure | HV | 369 | 362.8 | 0.21152 | 0.058298 | No
01/02/2019 | 07:49 | DC3 | Urban | Asset Failure | LV | 1 | 204.2 | 0.00032254 | 0.00015799 | No
01/02/2019 | 08:44 | MTN24 | Rural Short | Asset Failure | LV | 1 | 85.2 | 0.0014318 | 0.0016815 | No
01/02/2019 | 10:34 | FTN14 | Urban | Third Party | Other | 1 | 163.9 | 0.00025892 | 0.00015799 | No
01/02/2019 | 12:28 | EB11 | Urban | Planned |  | 28 | 32 | 0.0014014 | 0.0043795 | No
01/02/2019 | 13:33 | DC2 | Urban | Third Party | Vehicle Impact | 29 | 147 | 0.0067351 | 0.0045817 | No
01/02/2019 | 13:39 | HT2 | Urban | Asset Failure | LV | 1 | 170.2 | 0.00026887 | 0.00015799 | No
01/02/2019 | 15:42 | MGE23 | Urban | Asset Failure | LV | 23 | 462.7 | 0.016448 | 0.0035548 | No
01/02/2019 | 16:29 | EL9 | Urban | Overloads |  | 4 | 75.1 | 0.00050878 | 0.00067778 | No
01/02/2019 | 18:44 | EB31 | Urban | Asset Failure | LV | 1 | 426 | 0.00067304 | 0.00015799 | No
02/02/2019 | 06:39 | MGE23 | Urban | Asset Failure | LV | 1 | 110.1 | 0.00017397 | 0.00015799 | No
02/02/2019 | 08:40 | CRM33 | Urban | Asset Failure | LV | 1 | 79.9 | 0.00012618 | 0.00015799 | No
02/02/2019 | 10:56 | EW8 | Urban | Other | XXX | 1 | 123.6 | 0.0001952 | 0.00015799 | No
02/02/2019 | 15:06 | EM8 | Urban | Unknown | Unknown | 10 | 54 | 0.00084461 | 0.0015641 | No
02/02/2019 | 15:50 | HT8 | Urban | Asset Failure | LV | 1 | 85 | 0.00013427 | 0.00015799 | No
02/02/2019 | 16:28 | WD36 | Urban | Overloads |  | 21 | 57 | 0.0019019 | 0.0033367 | No
02/02/2019 | 16:39 | DC10 | Urban | Overloads |  | 1 | 109 | 0.00017221 | 0.00015799 | No
02/02/2019 | 19:12 | GW10 | Urban | Overloads |  | 1 | 45 | 7.1095e-05 | 0.00015799 | No
02/02/2019 | 19:56 | DMA14 | Urban | Weather |  | 1 | 404 | 0.00063828 | 0.00015799 | No
02/02/2019 | 20:28 | BH22 | Urban | Overloads |  | 1 | 116 | 0.00018327 | 0.00015799 | No
02/02/2019 | 20:59 | NP23 | Urban | Overloads |  | 19 | 41 | 0.0012184 | 0.0029718 | No
02/02/2019 | 21:14 | DMA14 | Urban | Asset Failure | LV | 1 | 376 | 0.00059404 | 0.00015799 | No
02/02/2019 | 23:30 | BU10 | Urban | Overloads |  | 1 | 201 | 0.00031756 | 0.00015799 | No
03/02/2019 | 00:27 | NW13 | Urban | Weather |  | 1 | 99.9 | 0.00015775 | 0.00015799 | No
03/02/2019 | 11:26 | FTN24 | Urban | Overloads |  | 5 | 49 | 0.00040875 | 0.00083419 | No
03/02/2019 | 12:24 | DC1 | Urban | Asset Failure | LV | 11 | 178.4 | 0.0029767 | 0.0016684 | No
03/02/2019 | 14:45 | CFD14 | Urban | Asset Failure | LV | 35 | 165 | 0.0091187 | 0.0055265 | No
03/02/2019 | 15:14 | MR32 | Urban | Overloads |  | 15 | 256 | 0.0058727 | 0.002294 | No
03/02/2019 | 15:34 | CFD22 | Urban | Asset Failure | LV | 1 | 378.5 | 0.00059796 | 0.00015799 | No
03/02/2019 | 15:45 | K12 | Urban | Overloads |  | 426 | 65 | 0.043747 | 0.067304 | No
03/02/2019 | 15:57 | FTN24 | Urban | Asset Failure | LV | 5 | 48 | 0.00040041 | 0.00083419 | No
03/02/2019 | 16:12 | K7 | Urban | Weather |  | 58 | 64 | 0.0058646 | 0.0091634 | No
03/02/2019 | 16:43 | NW33 | Urban | Asset Failure | LV | 31 | 92 | 0.0045088 | 0.0049008 | No
03/02/2019 | 17:03 | CDA24 | Urban | Overloads |  | 19 | 177 | 0.0053523 | 0.0030239 | No
03/02/2019 | 17:26 | EM5 | Urban | Overloads |  | 22 | 57 | 0.0020208 | 0.0035453 | No
03/02/2019 | 17:28 | EM8 | Urban | Overloads |  | 10 | 62 | 0.00096974 | 0.0015641 | No
03/02/2019 | 18:12 | K13 | Urban | Overloads |  | 1 | 62 | 9.7954e-05 | 0.00015799 | No
03/02/2019 | 18:30 | CRM22 | Urban | Asset Failure | HV | 4,223 | 26.6 | 0.1773 | 0.66719 | No
03/02/2019 | 18:41 | K12 | Urban | Overloads |  | 141 | 64 | 0.014215 | 0.02221 | No
03/02/2019 | 18:45 | CRM12 | Urban | Asset Failure | LV | 1,002 | 1.9 | 0.0030078 | 0.15831 | No
03/02/2019 | 18:45 | CRM22 | Urban | Asset Failure | LV | 2,253 | 1.9 | 0.0067631 | 0.35595 | No
03/02/2019 | 19:28 | CRM22 | Urban | Asset Failure | HV | 155 | 1.2 | 0.00028162 | 0 | No
03/02/2019 | 19:45 | FTN24 | Urban | Asset Failure | LV | 16 | 409 | 0.010339 | 0.0025278 | No
03/02/2019 | 20:10 | GW2 | Urban | Unknown | Unknown | 1 | 94.1 | 0.0001487 | 0.00015799 | No
03/02/2019 | 20:32 | DC4 | Urban | Asset Failure | LV | 2 | 132.3 | 0.00043487 | 0.00032862 | No
03/02/2019 | 21:06 | OR32 | Urban | Asset Failure | LV | 1 | 116.3 | 0.00018379 | 0.00015799 | No
04/02/2019 | 00:09 | BU10 | Urban | Vegetation | Grow-in - Other responsible party | 1,811 | 34.8 | 0.099452 | 0.28612 | No
04/02/2019 | 00:09 | BU2 | Urban | Vegetation | Grow-in - Other responsible party | 681 | 83.3 | 0.08957 | 0.10759 | No
04/02/2019 | 03:54 | FSH13 | Urban | Weather |  | 19 | 103.5 | 0.0031054 | 0.0030018 | No
04/02/2019 | 07:03 | NP34 | Urban | Asset Failure | LV | 1 | 416.9 | 0.00065869 | 0.00015799 | No
04/02/2019 | 08:14 | NB34 | Urban | Asset Failure | LV | 1 | 61.3 | 9.6795e-05 | 0.00015799 | No
04/02/2019 | 08:29 | BH21 | Urban | Asset Failure | HV | 2,370 | 46.9 | 0.17559 | 0.37444 | No
04/02/2019 | 08:41 | BH21 | Urban | Asset Failure | LV | 1 | 378.6 | 0.00059815 | 0.00015799 | No
04/02/2019 | 12:19 | STO21 | Rural Short | Asset Failure | LV | 1 | 56 | 0.00094164 | 0.0016815 | No
04/02/2019 | 14:04 | SS13 | Urban | Asset Failure | LV | 1 | 15.3 | 2.4146e-05 | 0.00015799 | No
04/02/2019 | 14:25 | CFD26 | Urban | Asset Failure | LV | 1 | 165 | 0.00026068 | 0.00015799 | No
04/02/2019 | 14:42 | BH21 | Urban | Unknown | Unknown | 18 | 25 | 0.00072991 | 0.0029197 | No
04/02/2019 | 17:05 | M35 | Urban | Asset Failure | LV | 1 | 99.5 | 0.00015723 | 0.00015799 | No
05/02/2019 | 03:39 | DMA23 | Rural Short | Animal | Other | 123 | 62.8 | 0.12999 | 0.20682 | No
05/02/2019 | 08:48 | FSH31 | Urban | Third Party | Other | 2 | 192 | 0.00060668 | 0.00031598 | No
05/02/2019 | 11:24 | EB32 | Urban | Asset Failure | LV | 1 | 87.2 | 0.00013777 | 0.00015799 | No
05/02/2019 | 14:09 | FTN25 | Urban | Third Party | Other | 2 | 80.9 | 0.00025547 | 0.00031598 | No
05/02/2019 | 17:19 | LWN23 | Urban | Asset Failure | LV | 1 | 310 | 0.00048982 | 0.00015799 | No
05/02/2019 | 18:00 | DMA15 | Rural Short | Animal | Animal impact | 2 | 109.2 | 0.0036735 | 0.003363 | No
05/02/2019 | 21:20 | NW11 | Urban | Asset Failure | LV | 1 | 63.5 | 0.00010035 | 0.00015799 | No
05/02/2019 | 22:17 | FSH22 | Urban | Vegetation | Grow-in - NSP responsibility | 2,709 | 16.6 | 0.071259 | 0.42799 | No
06/02/2019 | 07:41 | STO21 | Rural Short | Asset Failure | LV | 1 | 93.4 | 0.0015705 | 0.0016815 | No
06/02/2019 | 08:19 | DC3 | Urban | Asset Failure | LV | 1 | 74.8 | 0.00011812 | 0.00015799 | No
06/02/2019 | 08:47 | EL8 | Urban | Asset Failure | LV | 1 | 133 | 0.00021013 | 0.00015799 | No
06/02/2019 | 11:09 | LWN35 | Urban | Asset Failure | LV | 1 | 110.3 | 0.00017426 | 0.00015799 | No
06/02/2019 | 12:06 | SS22 | Urban | Overloads |  | 3 | 68.3 | 0.00035601 | 0.00052137 | No
06/02/2019 | 12:18 | DC7 | Urban | Asset Failure | HV | 1,470 | 112.5 | 0.26133 | 0.23225 | No
06/02/2019 | 12:55 | DC7 | Urban | Asset Failure | LV | 56 | 1,201.3 | 0.10648 | 0.0088632 | No
06/02/2019 | 12:59 | CRM21 | Urban | Overloads |  | 1 | 90.4 | 0.00014287 | 0.00015799 | No
06/02/2019 | 13:33 | DC7 | Urban | Asset Failure | LV | 9 | 137 | 0.0019043 | 0.0013903 | No
06/02/2019 | 13:40 | MC1 | Urban | Asset Failure | LV | 4 | 60 | 0.00040667 | 0.00067778 | No
06/02/2019 | 13:52 | OR24 | Urban | Asset Failure | LV | 1 | 67.3 | 0.0001063 | 0.00015799 | No
06/02/2019 | 17:50 | DC7 | Urban | Overloads |  | 42 | 70 | 0.0046681 | 0.0066735 | No
06/02/2019 | 17:58 | MR31 | Urban | Overloads |  | 88 | 81.8 | 0.011375 | 0.013903 | No
06/02/2019 | 18:38 | M35 | Urban | Asset Failure | LV | 1 | 195.6 | 0.00030903 | 0.00015799 | No
06/02/2019 | 19:17 | K6 | Urban | Asset Failure | LV | 17 | 312.5 | 0.0086361 | 0.0027632 | No
06/02/2019 | 19:33 | NW31 | Urban | Weather |  | 2,368 | 32.3 | 0.12096 | 0.37412 | No
06/02/2019 | 19:33 | NW31 | Urban | Weather |  | 1,366 | 50 | 0.10794 | 0.21581 | No
06/02/2019 | 20:01 | MGE23 | Urban | Vegetation | Grow-in - NSP responsibility | 882 | 74.5 | 0.10381 | 0.13935 | No
06/02/2019 | 21:13 | KBH32 | Urban | Third Party | Other | 1 | 102.7 | 0.00016228 | 0.00015799 | No
06/02/2019 | 21:31 | DN10 | Urban | Asset Failure | HV | 192 | 458.7 | 0.13914 | 0.030334 | No
06/02/2019 | 22:05 | STO21 | Rural Short | Asset Failure | HV | 41 | 365 | 0.25164 | 0.068941 | No
06/02/2019 | 22:19 | NW33 | Urban | Asset Failure | LV | 1 | 51 | 8.0522e-05 | 0.00015799 | No
07/02/2019 | 05:09 | CFD24 | Urban | Asset Failure | LV | 1 | 166.6 | 0.00026321 | 0.00015799 | No
07/02/2019 | 06:36 | LWN33 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 110.7 | 0.00017495 | 0.00015799 | No
07/02/2019 | 06:44 | EB14 | Urban | Asset Failure | LV | 1 | 149.8 | 0.00023664 | 0.00015799 | No
07/02/2019 | 06:51 | EM5 | Urban | Unknown | Unknown | 25 | 188.5 | 0.0073721 | 0.0039102 | No
07/02/2019 | 10:15 | MC10 | Urban | Unknown | Unknown | 1 | 65.6 | 0.00010367 | 0.00015799 | No
07/02/2019 | 11:08 | K13 | Urban | Asset Failure | LV | 20 | 71.3 | 0.002267 | 0.0031803 | No
07/02/2019 | 12:32 | FTN11 | Urban | Asset Failure | LV | 1 | 226.6 | 0.00035806 | 0.00015799 | No
07/02/2019 | 12:45 | NW21 | Urban | Unknown | Unknown | 1 | 434.3 | 0.00068607 | 0.00015799 | No
07/02/2019 | 17:22 | M35 | Urban | Overloads |  | 1 | 67.6 | 0.00010683 | 0.00015799 | No
07/02/2019 | 17:26 | M35 | Urban | Overloads |  | 125 | 68.3 | 0.013495 | 0.019749 | No
07/02/2019 | 17:32 | DC7 | Urban | Asset Failure | LV | 22 | 87 | 0.0030402 | 0.0034932 | No
07/02/2019 | 18:53 | LWN21 | Rural Short | Asset Failure | LV | 1 | 56.3 | 0.00094724 | 0.0016815 | No
07/02/2019 | 22:39 | CRM21 | Urban | Unknown | Unknown | 4 | 560.7 | 0.0035435 | 0.00063196 | No
07/02/2019 | 23:00 | DMA15 | Rural Short | Asset Failure | LV | 1 | 109.9 | 0.0018477 | 0.0016815 | No
08/02/2019 | 08:02 | FTN21 | Urban | Weather |  | 1 | 92.7 | 0.00014638 | 0.00015799 | No
08/02/2019 | 08:31 | FSH22 | Urban | Asset Failure | LV | 1 | 252.3 | 0.00039866 | 0.00015799 | No
08/02/2019 | 11:46 | GW8 | Urban | Asset Failure | HV | 34 | 259.7 | 0.013952 | 0.0053717 | No
08/02/2019 | 11:58 | CDA23 | Urban | Asset Failure | LV | 1 | 341.5 | 0.00053953 | 0.00015799 | No
08/02/2019 | 13:40 | SS12 | Urban | Asset Failure | LV | 1 | 299.6 | 0.00047331 | 0.00015799 | No
08/02/2019 | 16:35 | EM8 | Urban | Third Party | Vehicle Impact | 20 | 415 | 0.012785 | 0.0030808 | No
08/02/2019 | 18:00 | OE4 | Urban | Asset Failure | LV | 1 | 164.6 | 0.00026008 | 0.00015799 | No
08/02/2019 | 18:53 | EW8 | Urban | Asset Failure | LV | 1 | 156.9 | 0.00024794 | 0.00015799 | No
08/02/2019 | 20:23 | BT10 | Urban | Asset Failure | LV | 1 | 162 | 0.00025592 | 0.00015799 | No
08/02/2019 | 21:32 | CDA23 | Urban | Vegetation | Grow-in - NSP responsibility | 126 | 7.4 | 0.0014698 | 0.019907 | No
08/02/2019 | 22:21 | STO23 | Urban | Asset Failure | LV | 1 | 173.6 | 0.0002743 | 0.00015799 | No
08/02/2019 | 23:04 | FTN14 | Urban | Third Party | Other | 1 | 115.7 | 0.00018279 | 0.00015799 | No
09/02/2019 | 09:30 | MGE14 | Urban | Third Party | Vehicle Impact | 32 | 35 | 0.0017518 | 0.0050051 | No
09/02/2019 | 09:32 | RBD24 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1,529 | 41.5 | 0.10013 | 0.24157 | No
09/02/2019 | 10:02 | EB22 | Urban | Asset Failure | LV | 1 | 207.2 | 0.0003273 | 0.00015799 | No
09/02/2019 | 10:39 | MTN21 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 48 | 92.5 | 0.0070148 | 0.0075835 | No
09/02/2019 | 11:47 | STO21 | Rural Short | Asset Failure | LV | 6 | 28 | 0.0027496 | 0.0098199 | No
09/02/2019 | 12:09 | M35 | Urban | Asset Failure | LV | 1 | 171 | 0.00027016 | 0.00015799 | No
09/02/2019 | 12:21 | HGS31 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 233.9 | 0.0039336 | 0.0016815 | No
09/02/2019 | 17:04 | WD34 | Urban | Overloads |  | 15 | 56 | 0.001343 | 0.0023983 | No
09/02/2019 | 18:03 | GW12 | Urban | Asset Failure | LV | 1 | 72 | 0.00011375 | 0.00015799 | No
09/02/2019 | 18:33 | M25 | Urban | Asset Failure | LV | 1 | 191.4 | 0.00030234 | 0.00015799 | No
09/02/2019 | 19:03 | M25 | Urban | Asset Failure | LV | 1 | 161 | 0.00025442 | 0.00015799 | No
09/02/2019 | 19:29 | BU13 | Urban | Asset Failure | LV | 1 | 76 | 0.00012007 | 0.00015799 | No
09/02/2019 | 19:37 | NP23 | Urban | Asset Failure | LV | 1 | 163 | 0.00025752 | 0.00015799 | No
09/02/2019 | 19:39 | NP36 | Urban | Asset Failure | LV | 1 | 111 | 0.00017537 | 0.00015799 | No
09/02/2019 | 22:13 | RBD14 | Urban | Asset Failure | LV | 1 | 101.6 | 0.00016054 | 0.00015799 | No
10/02/2019 | 01:22 | STO21 | Rural Short | Asset Failure | LV | 29 | 83 | 0.040069 | 0.048276 | No
10/02/2019 | 02:16 | HT13 | Urban | Animal | Animal impact | 299 | 64.5 | 0.030456 | 0.047239 | No
10/02/2019 | 03:28 | HT13 | Urban | Asset Failure | HV | 185 | 7.1 | 0.0020606 | 0.029228 | No
10/02/2019 | 08:20 | OAK22 | Urban |  | Networ Error | 42 | 100 | 0.0066356 | 0.0066356 | No
10/02/2019 | 08:49 | DN13 | Urban | Asset Failure | LV | 50 | 401 | 0.031677 | 0.0078995 | No
10/02/2019 | 09:02 | CRM35 | Urban | Unknown | Unknown | 7 | 58 | 0.00066526 | 0.001147 | No
10/02/2019 | 09:25 | LD32 | Urban | Planned |  | 1 | 6.5 | 1.0269e-05 | 0.00015799 | No
10/02/2019 | 09:38 | EL7 | Urban | Overloads |  | 1 | 192.2 | 0.00030368 | 0.00015799 | No
10/02/2019 | 10:15 | FTN14 | Urban | Weather |  | 1 | 286 | 0.00045185 | 0.00015799 | No
10/02/2019 | 12:47 | FTN11 | Urban | Planned |  | 1 | 10 | 1.5773e-05 | 0.00015799 | No
10/02/2019 | 13:30 | HT13 | Urban | Overloads |  | 1 | 119.2 | 6.2156e-05 | 5.2137e-05 | No
10/02/2019 | 14:22 | MR31 | Urban | Third Party | Other | 1 | 117.9 | 0.0001863 | 0.00015799 | No
10/02/2019 | 15:06 | BH11 | Urban | Overloads |  | 1 | 181 | 0.00028596 | 0.00015799 | No
11/02/2019 | 01:22 | CRM35 | Urban | Asset Failure | HV | 1 | 522.1 | 0.00082481 | 0.00015799 | No
11/02/2019 | 06:47 | FSH12 | Rural Short | Unknown | Unknown | 1 | 133 | 0.0022364 | 0.0016815 | No
11/02/2019 | 10:45 | LD3 | Urban | Asset Failure | LV | 1 | 315 | 0.00049761 | 0.00015799 | No
11/02/2019 | 11:01 | SS22 | Urban | Overloads |  | 7 | 91.2 | 0.0010459 | 0.001147 | No
11/02/2019 | 11:39 | SS12 | Urban | Unknown | Unknown | 9 | 53.2 | 0.00075693 | 0.0014219 | No
11/02/2019 | 11:48 | DVY31 | Urban | Asset Failure | LV | 1 | 312.6 | 0.0004939 | 0.00015799 | No
11/02/2019 | 11:53 | DVY31 | Urban | Third Party | Vehicle Impact | 257 | 44.6 | 0.018097 | 0.040603 | No
11/02/2019 | 11:53 | DVY31 | Urban | Third Party | Vehicle Impact | 15 | 246.1 | 0.0058322 | 0.0023698 | No
12/02/2019 | 01:41 | DMA24 | Rural Short | Animal | Animal impact | 3 | 91 | 0.0045905 | 0.0050445 | No
12/02/2019 | 03:51 | NP34 | Urban | Animal | Animal impact | 1,881 | 36.1 | 0.10735 | 0.29718 | No
12/02/2019 | 06:39 | BU1 | Urban | Asset Failure | LV | 1 | 141.9 | 0.00022411 | 0.00015799 | No
12/02/2019 | 07:05 | HT8 | Urban | Overloads |  | 1 | 113.1 | 0.00017861 | 0.00015799 | No
12/02/2019 | 09:19 | HGS23 | Rural Short | Vegetation | Grow-in - NSP responsibility | 866 | 101.7 | 1.4808 | 1.4562 | No
12/02/2019 | 09:20 | MTN32 | Rural Short | Asset Failure | LV | 1 | 182.7 | 0.0030715 | 0.0016815 | No
12/02/2019 | 11:13 | FSH34 | Urban | Asset Failure | HV | 2,880 | 25 | 0.11368 | 0.45501 | No
12/02/2019 | 12:54 | FSH31 | Urban | Other | XXX | 1 | 110.4 | 0.00017434 | 0.00015799 | No
12/02/2019 | 14:10 | GW1 | Urban | Vegetation | Grow-in - Other responsible party | 2 | 20.7 | 7.5485e-05 | 0.00036496 | No
12/02/2019 | 16:56 | DC7 | Urban | Asset Failure | LV | 1 | 74 | 0.00011691 | 0.00015799 | No
12/02/2019 | 18:13 | NP36 | Urban | Vegetation | Grow-in - NSP responsibility | 15 | 27 | 0.00063346 | 0.0023461 | No
12/02/2019 | 20:33 | GW12 | Urban | Asset Failure | HV | 22 | 403 | 0.013689 | 0.0033968 | No
13/02/2019 | 05:57 | NB36 | Urban | Asset Failure | LV | 1 | 169.7 | 0.00026814 | 0.00015799 | No
13/02/2019 | 09:19 | SS22 | Urban | Asset Failure | LV | 1 | 119 | 0.00018801 | 0.00015799 | No
13/02/2019 | 10:17 | HT8 | Urban | Asset Failure | LV | 1 | 162.9 | 0.00025729 | 0.00015799 | No
13/02/2019 | 10:32 | BR10 | Urban | Vegetation | Grow-in - NSP responsibility | 3 | 87.6 | 0.00041512 | 0.00047397 | No
13/02/2019 | 10:34 | BR15 | Urban | Asset Failure | LV | 1 | 296 | 0.00046765 | 0.00015799 | No
13/02/2019 | 11:00 | MTN35 | Rural Short | Unknown | Unknown | 1,367 | 32.7 | 0.75227 | 2.2986 | No
13/02/2019 | 11:00 | MTN22 | Rural Short | Unknown | Unknown | 3,231 | 24.4 | 1.3263 | 5.4329 | No
13/02/2019 | 11:28 | FSH33 | Urban | Network Business | Networ Error | 1,893 | 33 | 0.098645 | 0.29907 | No
13/02/2019 | 11:28 | MTN22 | Rural Short | Network Business | Networ Error | 1,180 | 63.9 | 1.267 | 0 | No
13/02/2019 | 14:04 | EM5 | Urban | Asset Failure | LV | 1 | 92.4 | 0.00014593 | 0.00015799 | No
14/02/2019 | 08:39 | STO23 | Urban | Asset Failure | LV | 1 | 130.4 | 0.00020599 | 0.00015799 | No
14/02/2019 | 09:05 | HGS32 | Urban | Asset Failure | LV | 1 | 620 | 0.00097946 | 0.00015799 | No
14/02/2019 | 10:27 | LWN33 | Urban | Overloads |  | 1 | 182.2 | 0.00028788 | 0.00015799 | No
14/02/2019 | 10:35 | STO22 | Urban | Asset Failure | LV | 5 | 75 | 0.00057587 | 0.00076783 | No
14/02/2019 | 12:50 | HT8 | Urban | Asset Failure | LV | 1 | 189.4 | 0.00029915 | 0.00015799 | No
14/02/2019 | 13:11 | RBD12 | Rural Short | Asset Failure | LV | 1 | 424 | 0.0071295 | 0.0016815 | No
14/02/2019 | 13:54 | FSH33 | Urban | Asset Failure | LV | 1 | 125.7 | 0.00019859 | 0.00015799 | No
14/02/2019 | 17:04 | RBD21 | Rural Short | Asset Failure | LV | 1 | 116.4 | 0.001957 | 0.0016815 | No
14/02/2019 | 17:31 | EL12 | Urban | Asset Failure | LV | 1 | 118.8 | 0.00018761 | 0.00015799 | No
14/02/2019 | 22:49 | K13 | Urban | Asset Failure | LV | 1 | 130.6 | 0.00020628 | 0.00015799 | No
15/02/2019 | 13:26 | HGS33 | Rural Short | Asset Failure | HV | 2 | 64 | 0.0021523 | 0.003363 | No
15/02/2019 | 15:58 | STO14 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 311.4 | 0.0052367 | 0.0016815 | No
15/02/2019 | 17:03 | STO22 | Urban | Asset Failure | LV | 1 | 306.3 | 0.00048384 | 0.00015799 | No
15/02/2019 | 17:21 | BT10 | Urban | Unknown | Unknown | 1 | 49.2 | 7.7705e-05 | 0.00015799 | No
15/02/2019 | 23:50 | MC2 | Urban | Asset Failure | Distribution substation | 34 | 70 | 0.0037955 | 0.0054222 | No
16/02/2019 | 06:54 | HGS23 | Rural Short | Asset Failure | LV | 1 | 80.2 | 0.0013483 | 0.0016815 | No
16/02/2019 | 11:01 | DMA23 | Rural Short | Unknown | Unknown | 1 | 449 | 0.0075499 | 0.0016815 | No
16/02/2019 | 11:50 | CFD16 | Urban | Asset Failure | LV | 1 | 69.7 | 0.00011014 | 0.00015799 | No
16/02/2019 | 13:30 | KBH34 | Urban | Asset Failure | LV | 2 | 135.9 | 0.00042947 | 0.00031598 | No
16/02/2019 | 13:41 | SS11 | Urban | Third Party | Vehicle Impact | 1 | 63.6 | 0.00010051 | 0.00015799 | No
16/02/2019 | 14:29 | DMA14 | Urban | Asset Failure | LV | 1 | 148 | 0.00023383 | 0.00015799 | No
16/02/2019 | 16:49 | NP12 | Urban | Asset Failure | LV | 20 | 31 | 0.00096974 | 0.0031282 | No
16/02/2019 | 21:15 | MGE21 | Urban | Asset Failure | LV | 34 | 845 | 0.04539 | 0.0053717 | No
16/02/2019 | 22:53 | FSH32 | Rural Short | Animal | Animal impact | 1 | 167 | 0.0028081 | 0.0016815 | No
17/02/2019 | 01:40 | FSH33 | Urban | Third Party | Vehicle Impact | 49 | 520 | 0.040256 | 0.0077415 | No
17/02/2019 | 03:40 | FSH33 | Urban | Third Party | Vehicle Impact | 272 | 399.3 | 0.17158 | 0.042973 | No
17/02/2019 | 05:45 | RBD21 | Rural Short | Animal | Other | 88 | 195 | 0.28854 | 0.14797 | No
17/02/2019 | 09:47 | HGS21 | Rural Short | Unknown | Unknown | 8 | 73 | 0.0098199 | 0.013452 | No
17/02/2019 | 10:53 | FSH33 | Urban | Asset Failure | LV | 13 | 46.2 | 0.00093872 | 0.0020333 | No
17/02/2019 | 17:51 | RWT23 | Urban | Asset Failure | LV | 1 | 77 | 0.00012165 | 0.00015799 | No
17/02/2019 | 23:55 | STO23 | Urban | Unknown | Unknown | 151 | 110 | 0.026242 | 0.023856 | No
18/02/2019 | 00:22 | K2 | Urban | Animal | Animal impact | 90 | 88 | 0.012513 | 0.014219 | No
18/02/2019 | 07:13 | MGE34 | Urban | Vegetation | Grow-in - Other responsible party | 203 | 1.7 | 0.00055058 | 0.032072 | No
18/02/2019 | 07:22 | EL8 | Urban | Third Party | Vehicle Impact | 15 | 108 | 0.0024775 | 0.002294 | No
18/02/2019 | 10:13 | FSH13 | Urban | Asset Failure | LV | 1 | 161.5 | 0.00025513 | 0.00015799 | No
18/02/2019 | 16:40 | WD14 | Urban | Unknown | Unknown | 1 | 60.7 | 9.59e-05 | 0.00015799 | No
18/02/2019 | 17:53 | STO22 | Urban | Vegetation | Grow-in - NSP responsibility | 57 | 667 | 0.060066 | 0.0090054 | No
19/02/2019 | 00:29 | MGE12 | Urban | Animal | Other | 75 | 22.2 | 0.0026246 | 0.011849 | No
19/02/2019 | 01:55 | M33 | Urban | Vegetation | Grow-in - Other responsible party | 829 | 78.2 | 0.10236 | 0.13097 | No
19/02/2019 | 14:27 | RWT12 | Urban | Unknown | Unknown | 1 | 263 | 0.00027424 | 0.00010427 | No
19/02/2019 | 16:03 | RBD13 | Urban | Asset Failure | LV | 1 | 177 | 0.00027964 | 0.00015799 | No
19/02/2019 | 17:07 | RWT24 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 80 | 0.00012642 | 0.00015799 | No
20/02/2019 | 03:33 | BR15 | Urban | Vegetation | Grow-in - NSP responsibility | 673 | 93.3 | 0.099203 | 0.10633 | No
20/02/2019 | 07:49 | FSH34 | Urban | Third Party | Dig-in | 1,732 | 31.6 | 0.086392 | 0.27364 | No
20/02/2019 | 11:04 | CFD25 | Urban | Asset Failure | LV | 1 | 221 | 0.00034916 | 0.00015799 | No
20/02/2019 | 14:34 | HGS31 | Rural Short | Unknown | Unknown | 1 | 327.8 | 0.0055114 | 0.0016815 | No
20/02/2019 | 22:31 | DMA13 | Rural Short | Unknown | Unknown | 221 | 119 | 0.44222 | 0.37161 | No
20/02/2019 | 23:14 | STO14 | Rural Short | Unknown | Unknown | 77 | 159.8 | 0.20694 | 0.12947 | No
21/02/2019 | 07:40 | OR32 | Urban | Asset Failure | LV | 1 | 92.1 | 0.00014543 | 0.00015799 | No
21/02/2019 | 08:12 | FTN14 | Urban | Asset Failure | LV | 1 | 32.4 | 5.1136e-05 | 0.00015799 | No
21/02/2019 | 11:11 | MGE23 | Urban | Asset Failure | LV | 25 | 35 | 0.0013686 | 0.0039102 | No
21/02/2019 | 16:53 | NP16 | Urban | Asset Failure | LV | 1 | 100.7 | 0.0001591 | 0.00015799 | No
21/02/2019 | 21:24 | DC2 | Urban |  | Other | 19 | 35.2 | 0.0010451 | 0.0029718 | No
21/02/2019 | 22:47 | HGS33 | Rural Short | Animal | Animal impact | 4 | 88 | 0.0059189 | 0.006726 | No
22/02/2019 | 05:12 | RBD14 | Urban | Asset Failure | LV | 5 | 188 | 0.0015683 | 0.00083419 | No
22/02/2019 | 05:43 | CDA11 | Urban | Asset Failure | LV | 1 | 79.9 | 0.00012618 | 0.00015799 | No
22/02/2019 | 09:40 | NO6 | Urban | Asset Failure | LV | 31 | 182.7 | 0.0088297 | 0.0048329 | No
22/02/2019 | 21:21 | MR31 | Urban | Animal | Animal impact | 1,108 | 49.3 | 0.086301 | 0.17505 | No
22/02/2019 | 21:53 | FTN14 | Urban | Third Party | Other | 12 | 97 | 0.0017792 | 0.0018343 | No
23/02/2019 | 02:52 | STO14 | Rural Short | Animal | Other | 8 | 113 | 0.015201 | 0.013452 | No
23/02/2019 | 08:29 | NB25 | Urban | Asset Failure | LV | 1 | 176.2 | 0.00027838 | 0.00015799 | No
23/02/2019 | 10:09 | NB22 | Urban | Asset Failure | LV | 1 | 150.2 | 0.00023735 | 0.00015799 | No
23/02/2019 | 13:33 | MGE22 | Urban | Asset Failure | LV | 11 | 132 | 0.0022023 | 0.0016684 | No
23/02/2019 | 15:54 | CRM21 | Urban | Vegetation | Grow-in - NSP responsibility | 1,834 | 66.1 | 0.19143 | 0.28975 | No
23/02/2019 | 23:44 | RWT23 | Urban | Asset Failure | LV | 1 | 137 | 0.00021645 | 0.00015799 | No
23/02/2019 | 23:46 | RBD12 | Rural Short | Unknown | Unknown | 80 | 76 | 0.10223 | 0.13452 | No
24/02/2019 | 07:31 | FSH31 | Urban | Asset Failure | LV | 1 | 179 | 0.0002828 | 0.00015799 | No
24/02/2019 | 10:11 | OR35 | Urban | Asset Failure | LV | 1 | 194 | 0.0003065 | 0.00015799 | No
24/02/2019 | 12:07 | MTN32 | Rural Short | Asset Failure | LV | 1 | 83 | 0.0013956 | 0.0016815 | No
24/02/2019 | 12:44 | LWN21 | Rural Short | Asset Failure | LV | 1 | 145.4 | 0.002444 | 0.0016815 | No
24/02/2019 | 14:14 | EB22 | Urban | Asset Failure | LV | 1 | 91 | 0.00014377 | 0.00015799 | No
24/02/2019 | 14:56 | OR23 | Urban | Asset Failure | LV | 1 | 169 | 0.000267 | 0.00015799 | No
24/02/2019 | 15:08 | OAK33 | Urban | Asset Failure | LV | 1 | 81.5 | 0.00012881 | 0.00015799 | No
24/02/2019 | 15:50 | MR31 | Urban | Asset Failure | LV | 21 | 295.9 | 0.0097192 | 0.0032846 | No
24/02/2019 | 15:52 | LWN21 | Rural Short | Asset Failure | LV | 1 | 88 | 0.0014797 | 0.0016815 | No
24/02/2019 | 15:54 | FTN23 | Urban | Asset Failure | LV | 1 | 111 | 0.00017537 | 0.00015799 | No
24/02/2019 | 17:50 | MR31 | Urban | Asset Failure | LV | 29 | 174.6 | 0.0080115 | 0.004588 | No
24/02/2019 | 22:08 | CRM12 | Urban | Unknown | Unknown | 1 | 181 | 0.00028596 | 0.00015799 | No
24/02/2019 | 22:24 | RBD24 | Urban | Vegetation | Grow-in - Other responsible party | 293 | 20.1 | 0.0092814 | 0.046291 | No
25/02/2019 | 03:52 | HGS33 | Rural Short | Animal | Animal impact | 3 | 83 | 0.0041869 | 0.0050445 | No
25/02/2019 | 05:48 | KBH34 | Urban | Third Party | Vehicle Impact | 473 | 105.2 | 0.078643 | 0.074729 | No
25/02/2019 | 06:40 | DSH32 | Urban | Animal | Animal impact | 1 | 219.6 | 0.00034687 | 0.00015799 | No
25/02/2019 | 07:55 | LWN24 | Urban | Overloads |  | 20 | 94 | 0.0029405 | 0.0031282 | No
25/02/2019 | 09:40 | DN10 | Urban | Asset Failure | LV | 1 | 248 | 0.00039182 | 0.00015799 | No
25/02/2019 | 10:45 | EL5 | Urban | Overloads |  | 1 | 144.6 | 0.00022851 | 0.00015799 | No
25/02/2019 | 11:19 | STO14 | Rural Short | Asset Failure | LV | 1 | 268.4 | 0.0045137 | 0.0016815 | No
25/02/2019 | 13:19 | RBD21 | Rural Short | Asset Failure | LV | 1 | 230.4 | 0.0038744 | 0.0016815 | No
25/02/2019 | 13:43 | BW23 | Urban | Asset Failure | LV | 7 | 107 | 0.0012273 | 0.001147 | No
25/02/2019 | 15:08 | OAK21 | Urban | Asset Failure | LV | 1 | 136 | 0.00021487 | 0.00015799 | No
25/02/2019 | 15:10 | EW14 | Urban | Third Party | Vehicle Impact | 3 | 440 | 0.002155 | 0.00048977 | No
25/02/2019 | 17:09 | STO13 | Urban | Unknown | Unknown | 108 | 96 | 0.01638 | 0.017063 | No
25/02/2019 | 18:00 | STO21 | Rural Short | Asset Failure | LV | 1 | 180 | 0.0030267 | 0.0016815 | No
25/02/2019 | 18:53 | MR11 | Urban | Overloads |  | 13 | 82 | 0.0016673 | 0.0020333 | No
25/02/2019 | 20:05 | FTN24 | Urban | Asset Failure | LV | 26 | 45 | 0.00183 | 0.0040667 | No
25/02/2019 | 20:34 | BW33 | Urban | Overloads |  | 37 | 106 | 0.0061897 | 0.0058393 | No
25/02/2019 | 20:53 | MGE23 | Urban | Asset Failure | LV | 1 | 139.6 | 0.0002205 | 0.00015799 | No
25/02/2019 | 22:00 | DN10 | Urban | Unknown | Unknown | 1 | 90 | 0.00014219 | 0.00015799 | No
26/02/2019 | 00:54 | NP36 | Urban | Third Party | Other | 1 | 139.4 | 0.00022024 | 0.00015799 | No
26/02/2019 | 08:11 | DMA14 | Urban | Asset Failure | LV | 1 | 133.7 | 0.00021123 | 0.00015799 | No
26/02/2019 | 15:22 | CDA23 | Urban | Asset Failure | LV | 4 | 68 | 0.00038676 | 0.00056876 | No
26/02/2019 | 15:51 | K4 | Urban | Unknown | Unknown | 5 | 30 | 0.00025594 | 0.00085315 | No
26/02/2019 | 16:00 | KBH31 | Urban | Asset Failure | LV | 1 | 89.8 | 0.00014182 | 0.00015799 | No
26/02/2019 | 16:13 | CFD26 | Urban | Asset Failure | LV | 1 | 106.6 | 0.00016847 | 0.00015799 | No
26/02/2019 | 17:25 | CFD14 | Urban | Asset Failure | LV | 87 | 95 | 0.013058 | 0.013745 | No
26/02/2019 | 22:39 | FSH31 | Urban | Asset Failure | LV | 1 | 35.7 | 5.6323e-05 | 0.00015799 | No
26/02/2019 | 23:47 | LD2 | Urban | Unknown | Unknown | 6 | 118 | 0.0010459 | 0.00088632 | No
27/02/2019 | 04:42 | STO14 | Rural Short | Animal | Animal impact | 26 | 68 | 0.029729 | 0.043719 | No
27/02/2019 | 12:20 | MR22 | Urban | Asset Failure | LV | 1 | 74.6 | 0.00011786 | 0.00015799 | No
27/02/2019 | 14:40 | SV33 | Urban | Asset Failure | LV | 1 | 118.8 | 0.00018761 | 0.00015799 | No
27/02/2019 | 16:23 | EL5 | Urban | Third Party | Other | 1 | 81.3 | 0.00012842 | 0.00015799 | No
27/02/2019 | 16:35 | CFD26 | Urban | Asset Failure | LV | 1 | 119 | 0.00018801 | 0.00015799 | No
27/02/2019 | 18:15 | WD34 | Urban | Overloads |  | 15 | 60 | 0.001439 | 0.0023983 | No
27/02/2019 | 21:20 | FSH12 | Rural Short | Unknown | Unknown | 1 | 169.8 | 0.0028552 | 0.0016815 | No
27/02/2019 | 21:53 | HGS22 | Rural Short | Animal | Animal impact | 743 | 42.8 | 0.53492 | 1.2493 | No
28/02/2019 | 00:19 | DMA23 | Rural Short | Animal | Animal impact | 6 | 77.8 | 0.0078526 | 0.010089 | No
28/02/2019 | 00:21 | EB22 | Urban | Asset Failure | LV | 1 | 44 | 6.9516e-05 | 0.00015799 | No
28/02/2019 | 11:20 | DN11 | Urban | Overloads |  | 42 | 305 | 0.020239 | 0.0066356 | No
28/02/2019 | 12:07 | GW8 | Urban | Asset Failure | LV | 1 | 206.5 | 0.00032622 | 0.00015799 | No
28/02/2019 | 12:55 | CRM21 | Urban | Overloads |  | 1 | 44.2 | 6.9858e-05 | 0.00015799 | No
28/02/2019 | 13:40 | DMA15 | Rural Short | Asset Failure | Distribution substation | 1 | 350 | 0.0058852 | 0.0016815 | No
28/02/2019 | 17:44 | DN6 | Urban | Network Business | Networ Error | 1 | 180.6 | 0.00028525 | 0.00015799 | No
28/02/2019 | 18:44 | K13 | Urban | Overloads |  | 17 | 86 | 0.0022419 | 0.0026068 | No
28/02/2019 | 18:45 | MGE12 | Urban | Overloads |  | 77 | 73 | 0.0088806 | 0.012165 | No
28/02/2019 | 19:07 | GW3 | Urban | Asset Failure | LV | 27 | 68 | 0.0028717 | 0.0042231 | No
28/02/2019 | 19:35 | BT10 | Urban | Asset Failure | LV | 1 | 249.8 | 0.00039461 | 0.00015799 | No
28/02/2019 | 19:57 | EM8 | Urban | Overloads |  | 10 | 88 | 0.0013764 | 0.0015641 | No
28/02/2019 | 20:02 | CDA22 | Urban | Asset Failure | LV | 51 | 248.9 | 0.020111 | 0.0080812 | No
28/02/2019 | 20:13 | BU14 | Urban | Asset Failure | LV | 99 | 202 | 0.031595 | 0.015641 | No
28/02/2019 | 20:17 | K12 | Urban | Overloads |  | 141 | 33 | 0.0073294 | 0.02221 | No
28/02/2019 | 20:33 | BW21 | Urban | Unknown | Unknown | 41 | 77 | 0.004978 | 0.0064649 | No
28/02/2019 | 20:35 | EM3 | Urban | Asset Failure | LV | 1 | 154.6 | 0.0002443 | 0.00015799 | No
28/02/2019 | 20:37 | NO7 | Urban | Overloads |  | 1 | 83 | 0.00013113 | 0.00015799 | No
28/02/2019 | 22:47 | CDA23 | Urban | Asset Failure | LV | 1 | 133 | 0.00021013 | 0.00015799 | No
28/02/2019 | 23:08 | SS23 | Urban | Asset Failure | LV | 22 | 146.4 | 0.0050897 | 0.0034758 | No
01/03/2019 | 07:34 | STO21 | Rural Short | Asset Failure | LV | 1 | 113.2 | 0.0019037 | 0.0016815 | No
01/03/2019 | 07:57 | BT10 | Urban | Asset Failure | LV | 1 | 62 | 9.7954e-05 | 0.00015799 | No
01/03/2019 | 08:57 | M35 | Urban | Asset Failure | LV | 1 | 47 | 7.4255e-05 | 0.00015799 | No
01/03/2019 | 09:38 | NB36 | Urban | Asset Failure | LV | 1 | 420.1 | 0.00066374 | 0.00015799 | No
01/03/2019 | 10:29 | HGS33 | Rural Short | Asset Failure | Distribution substation | 5 | 61 | 0.0051285 | 0.0084075 | No
01/03/2019 | 11:14 | CFD25 | Urban | Asset Failure | HV | 87 | 297 | 0.040823 | 0.013745 | No
01/03/2019 | 11:21 | CFD24 | Urban | Asset Failure | HV | 43 | 289.2 | 0.019647 | 0.0067936 | No
01/03/2019 | 12:10 | NW14 | Urban | Asset Failure | LV | 1 | 130.8 | 0.00020665 | 0.00015799 | No
01/03/2019 | 12:46 | CRM21 | Urban | Overloads |  | 1 | 161.7 | 0.0002555 | 0.00015799 | No
01/03/2019 | 12:51 | DN22 | Urban | Other | XXX | 1 | 216.1 | 0.00034147 | 0.00015799 | No
01/03/2019 | 12:52 | HT6 | Urban | Unknown | Unknown | 1 | 211.8 | 0.00033465 | 0.00015799 | No
01/03/2019 | 12:52 | EB14 | Urban | Other | XXX | 1 | 127.6 | 0.00020162 | 0.00015799 | No
01/03/2019 | 14:11 | HGS31 | Rural Short | Asset Failure | LV | 1 | 274.2 | 0.0046107 | 0.0016815 | No
01/03/2019 | 14:15 | CFD14 | Urban | Overloads |  | 35 | 106 | 0.0059133 | 0.0055786 | No
01/03/2019 | 15:23 | MTN32 | Rural Short | Other | XXX | 1 | 231.8 | 0.003898 | 0.0016815 | No
01/03/2019 | 16:27 | EB14 | Urban | Overloads |  | 23 | 63 | 0.0022664 | 0.0035974 | No
01/03/2019 | 17:17 | K12 | Urban | Overloads |  | 285 | 92.9 | 0.041869 | 0.045093 | No
01/03/2019 | 17:21 | EL9 | Urban | Overloads |  | 65 | 204 | 0.021059 | 0.010323 | No
01/03/2019 | 17:22 | K2 | Urban | Overloads |  | 18 | 108 | 0.0031532 | 0.0029197 | No
01/03/2019 | 17:34 | CFD14 | Urban | Overloads |  | 35 | 165.1 | 0.0092122 | 0.0055786 | No
01/03/2019 | 17:36 | FTN13 | Urban | Overloads |  | 15 | 99 | 0.0022711 | 0.002294 | No
01/03/2019 | 17:39 | SS13 | Urban | Unknown | Unknown | 55 | 66 | 0.005735 | 0.0086894 | No
01/03/2019 | 17:46 | LWN32 | Rural Short | Overloads |  | 13 | 114 | 0.024038 | 0.021086 | No
01/03/2019 | 17:50 | EM8 | Urban | Overloads |  | 24 | 115 | 0.0043169 | 0.0037538 | No
01/03/2019 | 18:12 | MTN22 | Rural Short | Overloads |  | 19 | 128 | 0.040485 | 0.031629 | No
01/03/2019 | 18:13 | CRM35 | Urban | Overloads |  | 35 | 182 | 0.010058 | 0.0055265 | No
01/03/2019 | 18:16 | BC23 | Urban | Overloads |  | 30 | 244 | 0.011576 | 0.0047444 | No
01/03/2019 | 18:22 | BU14 | Urban | Vegetation | Grow-in - NSP responsibility | 29 | 197 | 0.0091754 | 0.0046575 | No
01/03/2019 | 18:27 | NB22 | Urban | Overloads |  | 30 | 73 | 0.0034254 | 0.0046923 | No
01/03/2019 | 18:32 | EL6 | Urban | Overloads |  | 22 | 173 | 0.0061334 | 0.0035453 | No
01/03/2019 | 18:44 | BT14 | Urban | Overloads |  | 137 | 71 | 0.015368 | 0.021645 | No
01/03/2019 | 18:44 | EW2 | Urban | Overloads |  | 9 | 216 | 0.0030406 | 0.0014077 | No
01/03/2019 | 18:53 | EM5 | Urban | Overloads |  | 151 | 112 | 0.026711 | 0.023856 | No
01/03/2019 | 18:55 | MR32 | Urban | Overloads |  | 15 | 95 | 0.0021793 | 0.002294 | No
01/03/2019 | 19:02 | RBD12 | Rural Short | Overloads |  | 27 | 108 | 0.049141 | 0.045501 | No
01/03/2019 | 19:03 | MTN22 | Rural Short | Overloads |  | 68 | 161.6 | 0.18472 | 0.11431 | No
01/03/2019 | 19:06 | LWN35 | Urban | Asset Failure | LV | 25 | 85 | 0.0033237 | 0.0039102 | No
01/03/2019 | 19:08 | K12 | Urban | Overloads |  | 285 | 102 | 0.045995 | 0.045093 | No
01/03/2019 | 19:08 | FTN11 | Urban | Asset Failure | LV | 1 | 236.4 | 0.00037354 | 0.00015799 | No
01/03/2019 | 19:11 | DMA24 | Rural Short | Overloads |  | 33 | 154 | 0.085453 | 0.055489 | No
01/03/2019 | 19:39 | OR35 | Urban | Overloads |  | 20 | 69 | 0.0021944 | 0.0031803 | No
01/03/2019 | 19:53 | MGE12 | Urban | Overloads |  | 25 | 26.9 | 0.0010792 | 0.0040145 | No
01/03/2019 | 20:04 | RBD13 | Urban | Overloads |  | 44 | 91 | 0.0063575 | 0.0069863 | No
01/03/2019 | 20:22 | MC3 | Urban | Overloads |  | 33 | 128 | 0.0066068 | 0.0051615 | No
01/03/2019 | 20:25 | DSH34 | Urban | Asset Failure | LV | 1 | 135 | 0.00021329 | 0.00015799 | No
01/03/2019 | 20:35 | CDA22 | Urban | Asset Failure | LV | 1 | 69.9 | 0.00011038 | 0.00015799 | No
01/03/2019 | 20:40 | MTN34 | Urban | Asset Failure | LV | 31 | 140 | 0.0067882 | 0.0048487 | No
01/03/2019 | 21:19 | MR32 | Urban | Asset Failure | LV | 30 | 116 | 0.0054431 | 0.0046923 | No
01/03/2019 | 22:30 | K12 | Urban | Overloads |  | 256 | 241.6 | 0.097563 | 0.040382 | No
01/03/2019 | 23:33 | FSH13 | Urban | Asset Failure | LV | 32 | 77 | 0.0038929 | 0.0050557 | No
02/03/2019 | 01:19 | SR12 | Urban | Asset Failure | LV | 1 | 90.6 | 0.00014306 | 0.00015799 | No
02/03/2019 | 05:45 | CDA22 | Urban | Overloads |  | 1 | 267.2 | 0.00042212 | 0.00015799 | No
02/03/2019 | 08:35 | MC2 | Urban | Asset Failure | LV | 1 | 155.7 | 0.00024599 | 0.00015799 | No
02/03/2019 | 08:58 | RBD22 | Urban | Asset Failure | HV | 998 | 75.1 | 0.11847 | 0.15767 | No
02/03/2019 | 09:45 | MTN32 | Rural Short | Other | XXX | 1 | 131.1 | 0.0022047 | 0.0016815 | No
02/03/2019 | 11:46 | CFD12 | Urban | Overloads |  | 18 | 44 | 0.0012388 | 0.0028154 | No
02/03/2019 | 12:37 | BR9 | Urban | Asset Failure | LV | 1 | 139 | 0.00021961 | 0.00015799 | No
02/03/2019 | 13:21 | MTN32 | Rural Short | Other | XXX | 1 | 177.7 | 0.0029886 | 0.0016815 | No
02/03/2019 | 15:22 | DMA23 | Rural Short | Overloads |  | 3 | 82.2 | 0.0036468 | 0.0044391 | No
02/03/2019 | 15:55 | STO14 | Rural Short | Overloads |  | 8 | 105 | 0.013401 | 0.012763 | No
02/03/2019 | 16:08 | RBD22 | Urban | Asset Failure | LV | 19 | 52 | 0.0015438 | 0.0029718 | No
02/03/2019 | 16:17 | MR32 | Urban | Overloads |  | 15 | 172.2 | 0.0039495 | 0.002294 | No
02/03/2019 | 16:18 | NB32 | Urban | Overloads |  | 18 | 147 | 0.0041386 | 0.0028154 | No
02/03/2019 | 16:20 | MR13 | Urban | Animal | Other | 54 | 85 | 0.0072517 | 0.0085315 | No
02/03/2019 | 16:22 | SR11 | Urban | Overloads |  | 12 | 58 | 0.0010584 | 0.0018248 | No
02/03/2019 | 16:34 | MR22 | Urban | Asset Failure | LV | 26 | 266 | 0.010817 | 0.0040667 | No
02/03/2019 | 16:57 | DN10 | Urban | Unknown | Unknown | 1 | 93 | 0.00014693 | 0.00015799 | No
02/03/2019 | 17:02 | K12 | Urban | Overloads |  | 33 | 72.8 | 0.0038309 | 0.0052658 | No
02/03/2019 | 17:17 | OR34 | Urban | Overloads |  | 14 | 68 | 0.0015245 | 0.0022419 | No
02/03/2019 | 17:47 | DMA14 | Urban | Overloads |  | 17 | 53 | 0.0014369 | 0.0027111 | No
02/03/2019 | 17:53 | NW13 | Urban | Other | XXX | 1 | 178.2 | 0.00028148 | 0.00015799 | No
02/03/2019 | 17:59 | OR24 | Urban | Asset Failure | LV | 62 | 211 | 0.020792 | 0.0098538 | No
02/03/2019 | 18:04 | MGE12 | Urban | Overloads |  | 25 | 55.4 | 0.0022234 | 0.0040145 | No
02/03/2019 | 18:07 | SR20 | Urban | Overloads |  | 32 | 207 | 0.010469 | 0.0050573 | No
02/03/2019 | 18:08 | M35 | Urban | Asset Failure | HV | 213 | 319.3 | 0.10744 | 0.033652 | No
02/03/2019 | 18:08 | M22 | Urban | Asset Failure | LV | 38 | 292 | 0.017531 | 0.0060036 | No
02/03/2019 | 18:10 | BR1 | Urban | Weather |  | 27 | 165 | 0.0069681 | 0.0042231 | No
02/03/2019 | 18:19 | M35 | Urban | Asset Failure | HV | 455 | 251.3 | 0.18067 | 0.071885 | No
02/03/2019 | 18:30 | SR11 | Urban | Overloads |  | 35 | 204.5 | 0.01131 | 0.0055296 | No
02/03/2019 | 18:39 | EL7 | Urban | Overloads |  | 9 | 140.2 | 0.0019736 | 0.0014077 | No
02/03/2019 | 19:04 | OR35 | Urban | Unknown | Unknown | 1 | 205 | 0.00032391 | 0.00015799 | No
02/03/2019 | 19:06 | K12 | Urban | Overloads |  | 33 | 43.4 | 0.0022845 | 0.0052658 | No
02/03/2019 | 19:29 | STO14 | Rural Short | Overloads |  | 8 | 250.7 | 0.032 | 0.012763 | No
02/03/2019 | 19:41 | CDA24 | Urban | Overloads |  | 19 | 93.4 | 0.0028228 | 0.0030239 | No
02/03/2019 | 19:46 | CRM24 | Urban | Overloads |  | 12 | 59 | 0.0010766 | 0.0018248 | No
02/03/2019 | 19:48 | FSH33 | Urban | Asset Failure | LV | 1 | 217 | 0.00034284 | 0.00015799 | No
02/03/2019 | 19:56 | DMA14 | Urban | Overloads |  | 17 | 153.8 | 0.0041701 | 0.0027111 | No
02/03/2019 | 19:57 | BR9 | Urban | Overloads |  | 22 | 58 | 0.002026 | 0.0034932 | No
02/03/2019 | 20:51 | BH23 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 113.4 | 0.00017921 | 0.00015799 | No
02/03/2019 | 21:30 | RWT24 | Urban | Overloads |  | 25 | 58.1 | 0.0022712 | 0.0039102 | No
02/03/2019 | 22:13 | HGS23 | Rural Short | Animal | Other | 4 | 96.1 | 0.0064637 | 0.006726 | No
02/03/2019 | 23:43 | M35 | Urban | Asset Failure | LV | 1 | 82.4 | 0.0001301 | 0.00015799 | No
03/03/2019 | 08:29 | EM5 | Urban | Asset Failure | LV | 1 | 140.3 | 0.00022171 | 0.00015799 | No
03/03/2019 | 08:59 | KBH32 | Urban | Third Party | Vehicle Impact | 38 | 91 | 0.0054633 | 0.0060036 | No
03/03/2019 | 09:16 | DSH24 | Urban | Third Party | Vehicle Impact | 29 | 74 | 0.0033905 | 0.0045817 | No
03/03/2019 | 09:55 | NP11 | Urban | Asset Failure | LV | 1 | 231.3 | 0.00036548 | 0.00015799 | No
03/03/2019 | 10:00 | NB25 | Urban | Asset Failure | LV | 1 | 409.4 | 0.00064678 | 0.00015799 | No
03/03/2019 | 10:45 | BH21 | Urban | Asset Failure | LV | 55 | 124.8 | 0.010865 | 0.0087068 | No
03/03/2019 | 11:29 | NB25 | Urban | Asset Failure | LV | 1 | 135.5 | 0.00021413 | 0.00015799 | No
03/03/2019 | 13:22 | NP36 | Urban | Asset Failure | LV | 1 | 134 | 0.00021171 | 0.00015799 | No
03/03/2019 | 13:42 | MR32 | Urban | Overloads |  | 15 | 62.2 | 0.0014276 | 0.002294 | No
03/03/2019 | 15:22 | DN11 | Urban | Overloads |  | 39 | 42 | 0.0025839 | 0.0061521 | No
03/03/2019 | 15:44 | MR32 | Urban | Weather |  | 15 | 121 | 0.002775 | 0.002294 | No
03/03/2019 | 15:51 | MGE12 | Urban | Weather |  | 25 | 68.5 | 0.0027513 | 0.0040145 | No
03/03/2019 | 16:26 | CFD14 | Urban | Weather |  | 20 | 84 | 0.0026715 | 0.0031803 | No
03/03/2019 | 17:48 | MGE12 | Urban | Overloads |  | 25 | 221.8 | 0.0089029 | 0.0040145 | No
03/03/2019 | 18:09 | MR12 | Urban | Unknown | Unknown | 1 | 96 | 0.00015167 | 0.00015799 | No
03/03/2019 | 18:47 | EL8 | Urban | Overloads |  | 21 | 118 | 0.0039989 | 0.0033889 | No
03/03/2019 | 18:57 | BH31 | Urban | Asset Failure | LV | 32 | 153 | 0.0078174 | 0.0051094 | No
03/03/2019 | 19:17 | DC6 | Urban | Overloads |  | 8 | 222 | 0.002894 | 0.0013034 | No
03/03/2019 | 22:21 | BR15 | Urban | Vegetation | Grow-in - NSP responsibility | 11 | 40 | 0.00070906 | 0.0017726 | No
04/03/2019 | 06:58 | RBD21 | Rural Short | Animal | Other | 3 | 67 | 0.0033798 | 0.0050445 | No
04/03/2019 | 07:23 | DMA15 | Rural Short | Animal | Other | 1 | 373.1 | 0.0062734 | 0.0016815 | No
04/03/2019 | 09:22 | HT8 | Urban | Asset Failure | LV | 1 | 112.1 | 0.00017708 | 0.00015799 | No
04/03/2019 | 11:16 | FSH33 | Urban | Asset Failure | LV | 11 | 689 | 0.012214 | 0.0017726 | No
04/03/2019 | 11:32 | GW5 | Urban | Third Party | Other | 1 | 211.1 | 0.00033354 | 0.00015799 | No
04/03/2019 | 12:15 | RWT24 | Urban | Unknown | Unknown | 1 | 270.9 | 0.000428 | 0.00015799 | No
04/03/2019 | 12:29 | CDA22 | Urban | Asset Failure | LV | 1 | 105.3 | 0.00016639 | 0.00015799 | No
04/03/2019 | 12:30 | SVW53 | Urban | Third Party | Vehicle Impact | 1 | 152.5 | 0.00024091 | 0.00015799 | No
04/03/2019 | 13:26 | FSH34 | Urban | Asset Failure | LV | 1 | 138 | 0.00021808 | 0.00015799 | No
04/03/2019 | 15:44 | EB32 | Urban | Asset Failure | LV | 1 | 121 | 0.00019117 | 0.00015799 | No
04/03/2019 | 17:09 | EB24 | Urban | Unknown | Unknown | 1 | 96 | 0.00015167 | 0.00015799 | No
04/03/2019 | 18:51 | BW21 | Urban | Unknown | Unknown | 1 | 84 | 0.00013263 | 0.00015799 | No
04/03/2019 | 20:49 | MTN32 | Rural Short | Asset Failure | LV | 1 | 216 | 0.003632 | 0.0016815 | No
04/03/2019 | 20:57 | GW1 | Urban | Unknown | Unknown | 116 | 138 | 0.025291 | 0.018327 | No
04/03/2019 | 21:38 | NW13 | Urban | Overloads |  | 1 | 126.4 | 0.00019965 | 0.00015799 | No
04/03/2019 | 23:53 | NP33 | Urban | Animal | Other | 113 | 37 | 0.0066056 | 0.017853 | No
05/03/2019 | 00:14 | NW21 | Urban | Animal | Other | 1 | 50.1 | 7.9127e-05 | 0.00015799 | No
05/03/2019 | 01:03 | LWN32 | Rural Short | Animal | Animal impact | 1 | 402 | 0.0067588 | 0.0016815 | No
05/03/2019 | 01:04 | DMA21 | Urban | Asset Failure | HV | 3,034 | 70.9 | 0.33996 | 0.47934 | No
05/03/2019 | 08:03 | LWN35 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 116.2 | 0.00018353 | 0.00015799 | No
05/03/2019 | 11:33 | LD3 | Urban | Asset Failure | LV | 1 | 214.8 | 0.00033928 | 0.00015799 | No
05/03/2019 | 11:50 | EW1 | Urban | Asset Failure | LV | 1 | 189.6 | 0.0002995 | 0.00015799 | No
05/03/2019 | 14:02 | OAK22 | Urban | Third Party | Other | 1 | 57.2 | 9.0397e-05 | 0.00015799 | No
05/03/2019 | 16:20 | DC8 | Urban | Asset Failure | LV | 20 | 179 | 0.0056419 | 0.0031519 | No
05/03/2019 | 17:22 | FTN11 | Urban | Weather |  | 1 | 278 | 0.00043921 | 0.00015799 | No
05/03/2019 | 19:47 | MR31 | Urban | Asset Failure | LV | 1 | 163 | 0.00025752 | 0.00015799 | No
05/03/2019 | 20:07 | NP36 | Urban | Weather |  | 1 | 153 | 0.00024172 | 0.00015799 | No
05/03/2019 | 20:31 | RWT23 | Urban | Unknown | Unknown | 174 | 44 | 0.012096 | 0.02749 | No
05/03/2019 | 20:31 | RWT23 | Urban | Unknown | Unknown | 100 | 44 | 0.0069516 | 0.015799 | No
06/03/2019 | 00:13 | HGS23 | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 91 | 110.5 | 0.16914 | 0.15302 | No
06/03/2019 | 01:07 | AR7 | Urban | Asset Failure | HV | 234 | 72.8 | 0.026925 | 0.03697 | No
06/03/2019 | 01:16 | AR7 | Urban | Asset Failure | HV | 72 | 92 | 0.010465 | 0.011375 | No
06/03/2019 | 01:51 | BU14 | Urban | Vegetation | Grow-in - NSP responsibility | 1,678 | 96.7 | 0.2563 | 0.26511 | No
06/03/2019 | 01:59 | BU9 | Urban | Unknown | Unknown | 1 | 76.3 | 0.00012047 | 0.00015799 | No
06/03/2019 | 08:06 | STO13 | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 173.4 | 0.00054786 | 0.00031598 | No
06/03/2019 | 09:37 | MGE11 | Urban | Unknown | Unknown | 49 | 69 | 0.0053416 | 0.0077415 | No
06/03/2019 | 11:53 | CRM14 | Urban | Unknown | Unknown | 4,097 | 45.7 | 0.29601 | 0.64728 | No
06/03/2019 | 11:54 | NB25 | Urban | Asset Failure | LV | 13 | 146 | 0.0028925 | 0.0019812 | No
06/03/2019 | 12:06 | BC22 | Urban | Asset Failure | LV | 54 | 129 | 0.011097 | 0.0086025 | No
06/03/2019 | 12:11 | RWT24 | Urban | Vegetation | Grow-in - Other responsible party | 22 | 169 | 0.0059915 | 0.0035453 | No
06/03/2019 | 12:33 | CDA23 | Urban | Overloads |  | 1 | 208 | 0.00032862 | 0.00015799 | No
06/03/2019 | 12:46 | CRM22 | Urban | Asset Failure | LV | 1 | 184 | 0.0002907 | 0.00015799 | No
06/03/2019 | 13:21 | SH22 | Urban | Asset Failure | HV | 1,074 | 67.2 | 0.11398 | 0.16968 | No
06/03/2019 | 14:20 | SH22 | Urban | Asset Failure | HV | 200 | 23.3 | 0.0073729 | 0 | No
06/03/2019 | 14:36 | SH22 | Urban | Asset Failure | HV | 182 | 7.3 | 0.0020943 | 0 | No
06/03/2019 | 16:17 | EB22 | Urban | Third Party | Vehicle Impact | 265 | 88 | 0.036843 | 0.041867 | No
06/03/2019 | 16:25 | FTN14 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 244.2 | 0.00038581 | 0.00015799 | No
06/03/2019 | 18:33 | OR35 | Urban | Asset Failure | LV | 7 | 181 | 0.0019016 | 0.0010506 | No
06/03/2019 | 18:37 | FSH13 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 102.9 | 0.0001626 | 0.00015799 | No
06/03/2019 | 19:03 | FSH34 | Urban | Asset Failure | LV | 6 | 102 | 0.0010007 | 0.00098112 | No
06/03/2019 | 19:12 | FSH13 | Urban | Unknown | Unknown | 1 | 18 | 2.8438e-05 | 0.00015799 | No
06/03/2019 | 20:11 | FSH32 | Rural Short | Animal | Other | 37 | 94 | 0.058482 | 0.062215 | No
06/03/2019 | 20:42 | DMA15 | Rural Short | Asset Failure | LV | 1 | 97.6 | 0.0016417 | 0.0016815 | No
07/03/2019 | 07:59 | K13 | Urban | Asset Failure | LV | 1 | 35.6 | 5.6271e-05 | 0.00015799 | No
07/03/2019 | 08:10 | RWT23 | Urban | Asset Failure | LV | 48 | 98 | 0.0073575 | 0.0075077 | No
07/03/2019 | 08:39 | DC2 | Urban | Asset Failure | LV | 1 | 119 | 0.00018801 | 0.00015799 | No
07/03/2019 | 09:11 | DN25 | Urban | Third Party | Vehicle Impact | 30 | 606.8 | 0.028759 | 0.0047397 | No
07/03/2019 | 11:01 | MR22 | Urban | Overloads |  | 1 | 119 | 0.00018801 | 0.00015799 | No
07/03/2019 | 11:12 | LD4 | Urban | Asset Failure | LV | 1 | 190.9 | 0.00030166 | 0.00015799 | No
07/03/2019 | 11:57 | FTN13 | Urban | Unknown | Unknown | 70 | 18 | 0.0019907 | 0.011059 | No
07/03/2019 | 12:01 | FTN13 | Urban | Unknown | Unknown | 73 | 14 | 0.0016147 | 0.011533 | No
07/03/2019 | 13:27 | CRM34 | Urban | Asset Failure | LV | 1 | 92.7 | 0.00014651 | 0.00015799 | No
07/03/2019 | 14:18 | HT2 | Urban | Asset Failure | LV | 1 | 146.4 | 0.00023122 | 0.00015799 | No
07/03/2019 | 17:15 | DC1 | Urban | Weather |  | 1 | 104.9 | 0.00016573 | 0.00015799 | No
07/03/2019 | 17:22 | RWT23 | Urban | Asset Failure | LV | 60 | 246 | 0.023506 | 0.0095552 | No
07/03/2019 | 18:41 | DMA23 | Rural Short | Animal | Animal impact | 1 | 114 | 0.0012843 | 0.0011266 | No
07/03/2019 | 21:30 | HGS31 | Rural Short | Asset Failure | HV | 53 | 79.1 | 0.070478 | 0.089119 | No
08/03/2019 | 01:10 | HGS33 | Rural Short | Animal | Animal impact | 2 | 205 | 0.0068941 | 0.003363 | No
08/03/2019 | 10:50 | HGS33 | Rural Short | Animal | Animal impact | 1 | 154.7 | 0.0026015 | 0.0016815 | No
08/03/2019 | 12:18 | STO23 | Urban | Asset Failure | LV | 1 | 341.4 | 0.0005393 | 0.00015799 | No
08/03/2019 | 12:35 | EL5 | Urban | Asset Failure | LV | 1 | 294.3 | 0.00046494 | 0.00015799 | No
08/03/2019 | 14:30 | DMA14 | Urban | Asset Failure | LV | 1 | 59.3 | 9.3662e-05 | 0.00015799 | No
08/03/2019 | 16:15 | BR15 | Urban | Asset Failure | LV | 1 | 134.9 | 0.00021313 | 0.00015799 | No
08/03/2019 | 17:45 | CDA21 | Urban | Asset Failure | LV | 1 | 164.5 | 0.00025989 | 0.00015799 | No
08/03/2019 | 23:42 | NW14 | Urban | Vegetation | Grow-in - NSP responsibility | 999 | 48.1 | 0.075865 | 0.15783 | No
08/03/2019 | 23:58 | RWT34 | Urban | Unknown | Unknown | 11 | 227 | 0.003945 | 0.0017379 | No
09/03/2019 | 03:45 | RWT34 | Urban | Asset Failure | LV | 3 | 675 | 0.0035192 | 0 | No
09/03/2019 | 03:59 | LWN21 | Rural Short | Animal | Animal impact | 3 | 245 | 0.012359 | 0.0050445 | No
09/03/2019 | 05:50 | DC2 | Urban | Unknown | Unknown | 1 | 250 | 0.00039497 | 0.00015799 | No
09/03/2019 | 08:23 | STO23 | Urban | Asset Failure | LV | 1 | 101.4 | 0.0001602 | 0.00015799 | No
09/03/2019 | 14:56 | RBD21 | Rural Short | Overloads |  | 1 | 74.6 | 0.0012538 | 0.0016815 | No
09/03/2019 | 15:00 | RWT34 | Urban | Unknown | Unknown | 11 | 120 | 0.0020855 | 0.0017379 | No
09/03/2019 | 16:19 | NW31 | Urban | Vegetation | Grow-in - Other responsible party | 2,370 | 34.9 | 0.13074 | 0.37444 | No
09/03/2019 | 16:20 | RBD21 | Rural Short | Overloads |  | 1 | 44.1 | 0.0007407 | 0.0016815 | No
09/03/2019 | 17:26 | DC2 | Urban | Asset Failure | LV | 1 | 1,083.7 | 0.0017122 | 0.00015799 | No
09/03/2019 | 19:28 | EB23 | Urban |  | HV | 466 | 11.2 | 0.0082581 | 0.073623 | No
09/03/2019 | 21:19 | DC3 | Urban | Asset Failure | LV | 1 | 81 | 0.00012797 | 0.00015799 | No
10/03/2019 | 00:11 | BT15 | Urban | Animal | Animal impact | 1,771 | 63.6 | 0.17786 | 0.2798 | No
10/03/2019 | 02:33 | K2 | Urban | Third Party | Other | 1 | 86.3 | 0.00013629 | 0.00015799 | No
10/03/2019 | 11:32 | CRM33 | Urban | Asset Failure | LV | 1 | 74 | 0.00011691 | 0.00015799 | No
10/03/2019 | 14:49 | NW33 | Urban |  | Other | 898 | 33.4 | 0.047364 | 0.14187 | No
10/03/2019 | 16:29 | MR32 | Urban | Asset Failure | HV | 564 | 36.8 | 0.032828 | 0.089106 | No
10/03/2019 | 16:31 | DMA23 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 113.4 | 0.0019068 | 0.0016815 | No
10/03/2019 | 17:14 | MR32 | Urban | Asset Failure | LV | 39 | 166 | 0.010228 | 0 | No
10/03/2019 | 19:03 | NW21 | Urban | Asset Failure | LV | 1 | 132 | 0.00020855 | 0.00015799 | No
11/03/2019 | 04:49 | CRM13 | Urban | Animal | Animal impact | 711 | 76.4 | 0.085859 | 0.11233 | No
11/03/2019 | 09:39 | HGS22 | Rural Short | Asset Failure | LV | 1 | 170.6 | 0.0028689 | 0.0016815 | No
11/03/2019 | 12:55 | NW32 | Urban | Asset Failure | LV | 1 | 94.3 | 0.00014901 | 0.00015799 | No
12/03/2019 | 01:20 | KBH32 | Urban | Asset Failure | LV | 1 | 53 | 8.3735e-05 | 0.00015799 | No
12/03/2019 | 02:10 | CRM21 | Urban | Animal | Other | 3,280 | 25.4 | 0.13138 | 0.51821 | No
12/03/2019 | 03:52 | NP12 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 255 | 0.00040287 | 0.00015799 | No
12/03/2019 | 04:59 | HGS22 | Rural Short | Asset Failure | Distribution substation | 128 | 125.9 | 0.27087 | 0.21523 | No
12/03/2019 | 07:47 | DSH33 | Urban | Animal | Other | 2 | 62.8 | 0.00019854 | 0.00031598 | No
12/03/2019 | 09:39 | HGS23 | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 29 | 101 | 0.049251 | 0.048763 | No
12/03/2019 | 10:49 | HT8 | Urban | Unknown | Unknown | 1 | 131.4 | 0.00020752 | 0.00015799 | No
12/03/2019 | 11:34 | MC9 | Urban | Asset Failure | HV | 360 | 41 | 0.023347 | 0.056876 | No
12/03/2019 | 11:50 | MC6 | Urban | Asset Failure | LV | 1 | 189.1 | 0.00029876 | 0.00015799 | No
12/03/2019 | 15:31 | STO13 | Urban | Asset Failure | LV | 1 | 88.7 | 0.00014019 | 0.00015799 | No
12/03/2019 | 16:14 | GW2 | Urban | Asset Failure | HV | 36 | 51 | 0.0029007 | 0.0056876 | No
12/03/2019 | 17:27 | RBD23 | Urban | Asset Failure | LV | 1 | 123 | 0.00019433 | 0.00015799 | No
12/03/2019 | 17:42 | OAK33 | Urban | Asset Failure | LV | 1 | 138 | 0.00021803 | 0.00015799 | No
12/03/2019 | 18:38 | DC8 | Urban | Asset Failure | LV | 1 | 176 | 0.00027806 | 0.00015799 | No
12/03/2019 | 19:01 | MTN22 | Rural Short | Asset Failure | LV | 1 | 73.4 | 0.0012339 | 0.0016815 | No
12/03/2019 | 19:27 | NW32 | Urban | Asset Failure | LV | 1 | 193 | 0.00030484 | 0.00015799 | No
13/03/2019 | 05:27 | NW32 | Urban | Asset Failure | LV | 63 | 168 | 0.016817 | 0.01001 | No
13/03/2019 | 07:32 | FSH11 | Urban | Asset Failure | LV | 1 | 153.5 | 0.00024243 | 0.00015799 | No
13/03/2019 | 10:44 | NW22 | Urban | Asset Failure | LV | 1 | 63.1 | 9.9613e-05 | 0.00015799 | No
13/03/2019 | 16:14 | FSH13 | Urban | Asset Failure | LV | 1 | 60.7 | 9.5952e-05 | 0.00015799 | No
13/03/2019 | 17:45 | OE4 | Urban | Asset Failure | LV | 1 | 253.5 | 0.00040042 | 0.00015799 | No
14/03/2019 | 00:18 | BU14 | Urban | Asset Failure | LV | 1 | 86.3 | 0.00013632 | 0.00015799 | No
14/03/2019 | 03:23 | BU14 | Urban | Asset Failure | LV | 15 | 81.2 | 0.001862 | 0.002294 | No
14/03/2019 | 07:04 | CRM35 | Urban | Unknown | Unknown | 1 | 89.2 | 0.00014085 | 0.00015799 | No
14/03/2019 | 09:27 | NW31 | Urban | Third Party | Vehicle Impact | 2,372 | 22.1 | 0.082807 | 0.37475 | No
14/03/2019 | 09:27 | NW31 | Urban | Third Party | Vehicle Impact | 1,367 | 36.8 | 0.079406 | 0.21597 | No
14/03/2019 | 10:18 | SR23 | Urban | Asset Failure | LV | 1 | 101.3 | 0.00015997 | 0.00015799 | No
14/03/2019 | 11:46 | NW11 | Urban | Asset Failure | LV | 1 | 193.3 | 0.00030537 | 0.00015799 | No
14/03/2019 | 12:01 | FSH33 | Urban | Third Party | Dig-in | 11 | 132 | 0.0023402 | 0.0017726 | No
14/03/2019 | 15:09 | STO21 | Rural Short | Asset Failure | LV | 1 | 138 | 0.002321 | 0.0016815 | No
14/03/2019 | 15:49 | RD10 | Urban | Unknown | Unknown | 1 | 129.3 | 0.00020426 | 0.00015799 | No
14/03/2019 | 16:45 | GW7 | Urban | Network Business | Networ Error | 17 | 136.4 | 0.003663 | 0.0026858 | No
14/03/2019 | 19:25 | DN22 | Urban | Asset Failure | LV | 18 | 215 | 0.0061142 | 0.0028438 | No
14/03/2019 | 20:09 | FSH31 | Urban | Asset Failure | LV | 1 | 69.6 | 0.00010991 | 0.00015799 | No
14/03/2019 | 20:28 | CRM21 | Urban | Animal | Animal impact | 4,543 | 19.6 | 0.14052 | 0.71775 | No
14/03/2019 | 21:03 | FSH31 | Urban | Asset Failure | LV | 1 | 72.5 | 0.00011454 | 0.00015799 | No
14/03/2019 | 22:21 | MTN32 | Rural Short | Animal | Other | 4 | 59 | 0.0039661 | 0.006726 | No
15/03/2019 | 05:22 | LD33 | Urban | Asset Failure | LV | 1 | 158 | 0.00024968 | 0.00015799 | No
15/03/2019 | 12:06 | KBH33 | Urban | Third Party | Vehicle Impact | 1 | 273.1 | 0.0004315 | 0.00015799 | No
15/03/2019 | 16:10 | STO21 | Rural Short | Asset Failure | HV | 2 | 65 | 0.0021859 | 0.003363 | No
15/03/2019 | 19:52 | NB25 | Urban | Weather |  | 1 | 113.6 | 0.0001795 | 0.00015799 | No
16/03/2019 | 00:54 | DMA23 | Rural Short | Unknown | Unknown | 32 | 144 | 0.077492 | 0.053808 | No
16/03/2019 | 01:39 | SS24 | Urban | Third Party | Other | 110 | 102.1 | 0.017738 | 0.017379 | No
16/03/2019 | 05:30 | MC10 | Urban | Unknown | Unknown | 1 | 943.9 | 0.0014912 | 0.00015799 | No
16/03/2019 | 06:47 | HGS23 | Rural Short | Animal | Other | 1 | 179.5 | 0.0030188 | 0.0016815 | No
16/03/2019 | 13:15 | SS14 | Urban | Third Party | Other | 14 | 235.7 | 0.0052137 | 0.0022119 | No
16/03/2019 | 17:06 | STO13 | Urban | Unknown | Unknown | 103 | 328.8 | 0.053497 | 0.016273 | No
16/03/2019 | 18:07 | MGE24 | Urban | Asset Failure | LV | 1 | 80.2 | 0.00012668 | 0.00015799 | No
16/03/2019 | 21:25 | DMA23 | Rural Short | Asset Failure | Distribution substation | 1 | 659.5 | 0.011089 | 0.0016815 | No
16/03/2019 | 23:45 | CRM22 | Urban | Asset Failure | Distribution substation | 146 | 70 | 0.016135 | 0.023067 | No
17/03/2019 | 00:26 | BR15 | Urban | Asset Failure | LV | 1 | 154.7 | 0.00024436 | 0.00015799 | No
17/03/2019 | 00:54 | LWN21 | Rural Short | Third Party | Vehicle Impact | 439 | 122.6 | 0.90528 | 0.73817 | No
17/03/2019 | 12:41 | HGS33 | Rural Short | Overloads |  | 1 | 197.6 | 0.0033223 | 0.0016815 | No
17/03/2019 | 19:37 | LD7 | Urban | Third Party | Vehicle Impact | 11 | 112.5 | 0.0019554 | 0.0017379 | No
17/03/2019 | 21:04 | FSH23 | Rural Short | Third Party | Vehicle Impact | 1 | 55.5 | 0.00093267 | 0.0016815 | No
18/03/2019 | 06:50 | OR33 | Urban | Third Party | Vehicle Impact | 1 | 131.7 | 0.00020813 | 0.00015799 | No
18/03/2019 | 08:25 | BU14 | Urban | Unknown | Unknown | 1 | 184.9 | 0.00029207 | 0.00015799 | No
18/03/2019 | 09:17 | STO23 | Urban | Asset Failure | LV | 1 | 86.3 | 0.00013632 | 0.00015799 | No
18/03/2019 | 09:50 | BR15 | Urban | Asset Failure | LV | 1 | 189.3 | 0.00029913 | 0.00015799 | No
18/03/2019 | 12:26 | BH22 | Urban | Asset Failure | LV | 1 | 93.1 | 0.00014709 | 0.00015799 | No
18/03/2019 | 16:30 | MGE31 | Urban | Asset Failure | LV | 54 | 207 | 0.017662 | 0.0085315 | No
19/03/2019 | 06:37 | HGS22 | Rural Short | Asset Failure | LV | 8 | 97.7 | 0.012463 | 0.012763 | No
19/03/2019 | 09:44 | WD14 | Urban | Asset Failure | LV | 1 | 268.9 | 0.00042481 | 0.00015799 | No
19/03/2019 | 11:19 | NP11 | Urban | Asset Failure | LV | 1 | 151 | 0.00023859 | 0.00015799 | No
19/03/2019 | 13:23 | SS22 | Urban | Unknown | Unknown | 3 | 41.8 | 0.00017427 | 0.00041709 | No
19/03/2019 | 14:55 | DSH31 | Urban | Asset Failure | LV | 1 | 396.3 | 0.00062609 | 0.00015799 | No
19/03/2019 | 15:40 | STO21 | Rural Short | Asset Failure | LV | 1 | 94.9 | 0.0015957 | 0.0016815 | No
20/03/2019 | 00:55 | MR32 | Urban | Asset Failure | HV | 820 | 105.1 | 0.13616 | 0.12955 | No
20/03/2019 | 01:00 | MR32 | Urban | Animal | Other | 17 | 289 | 0.0077616 | 0 | No
20/03/2019 | 01:23 | MR32 | Urban | Unknown | Unknown | 1 | 286.3 | 0.00045238 | 0.00015799 | No
20/03/2019 | 08:47 | CM22 | Urban | Planned |  | 1 | 88 | 0.00013903 | 0.00015799 | No
20/03/2019 | 09:08 | CM22 | Urban | Planned |  | 1 | 66.2 | 0.00010464 | 0.00015799 | No
20/03/2019 | 09:22 | BT2 | Urban | Planned |  | 3 | 157.9 | 0.00074076 | 0.00046923 | No
20/03/2019 | 09:36 | CM22 | Urban | Planned |  | 1 | 39 | 6.1616e-05 | 0.00015799 | No
20/03/2019 | 09:42 | HGS22 | Rural Short | Asset Failure | LV | 1 | 188.2 | 0.003164 | 0.0016815 | No
20/03/2019 | 13:12 | K6 | Urban | Third Party | Dig-in | 1,907 | 21.6 | 0.065126 | 0.30129 | No
20/03/2019 | 14:40 | SV16 | Urban | Unknown | Unknown | 1 | 82.2 | 0.00012979 | 0.00015799 | No
20/03/2019 | 19:27 | MTN24 | Rural Short | Third Party | Other | 1 | 153 | 0.0025727 | 0.0016815 | No
21/03/2019 | 01:16 | MGE24 | Urban | Asset Failure | LV | 1 | 94 | 0.00014851 | 0.00015799 | No
21/03/2019 | 06:00 | SS24 | Urban | Asset Failure | HV | 6 | 917.9 | 0.0087011 | 0.00094794 | No
21/03/2019 | 08:20 | SR24 | Urban | Asset Failure | LV | 1 | 130 | 0.00020539 | 0.00015799 | No
21/03/2019 | 12:12 | DMA21 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 77.7 | 0.00012268 | 0.00015799 | No
21/03/2019 | 20:02 | SS13 | Urban | Unknown | Unknown | 1 | 147.1 | 0.00023232 | 0.00015799 | No
21/03/2019 | 21:41 | SS14 | Urban | Unknown | Unknown | 1 | 79 | 0.00012481 | 0.00015799 | No
22/03/2019 | 07:13 | SH34 | Urban | Asset Failure | LV | 1 | 32 | 5.0557e-05 | 0.00015799 | No
22/03/2019 | 08:08 | CRM22 | Urban | Planned |  | 9 | 22 | 0.00029683 | 0.0013492 | No
22/03/2019 | 10:01 | MGE33 | Urban | Vegetation | Grow-in - Other responsible party | 228 | 40.9 | 0.014733 | 0.036022 | No
22/03/2019 | 12:00 | STO14 | Rural Short | Asset Failure | LV | 2 | 284.9 | 0.0095806 | 0.003363 | No
22/03/2019 | 12:23 | BR6 | Urban | Network Business | Networ Error | 49 | 23 | 0.0017805 | 0.0077415 | No
22/03/2019 | 15:34 | DC2 | Urban | Asset Failure | LV | 1 | 86 | 0.00013587 | 0.00015799 | No
22/03/2019 | 16:16 | STO22 | Urban | Asset Failure | LV | 1 | 74 | 0.00011691 | 0.00015799 | No
22/03/2019 | 16:23 | GW12 | Urban | Asset Failure | HV | 101 | 97 | 0.015478 | 0.015957 | No
22/03/2019 | 18:00 | NW21 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 3,033 | 39.2 | 0.18799 | 0.47918 | No
22/03/2019 | 18:04 | NW32 | Urban | Overloads |  | 81 | 286 | 0.036681 | 0.012826 | No
22/03/2019 | 18:04 | NW32 | Urban | Overloads |  | 106 | 286 | 0.048014 | 0.016788 | No
22/03/2019 | 18:04 | NW32 | Urban | Overloads |  | 46 | 324 | 0.023311 | 0.0071949 | No
22/03/2019 | 18:07 | NW11 | Urban | Overloads |  | 88 | 283 | 0.039247 | 0.013868 | No
22/03/2019 | 18:22 | DC4 | Urban | Unknown | Unknown | 59 | 213 | 0.019855 | 0.0093214 | No
22/03/2019 | 20:22 | NW21 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 27 | 27.6 | 0.0011766 | 0.0042657 | No
22/03/2019 | 20:34 | EM3 | Urban | Asset Failure | LV | 1 | 89 | 0.00014061 | 0.00015799 | No
22/03/2019 | 22:55 | WD34 | Urban | Overloads |  | 15 | 50 | 0.0011991 | 0.0023983 | No
23/03/2019 | 05:58 | BU4 | Urban | Unknown | Unknown | 1 | 181.2 | 0.00028628 | 0.00015799 | No
23/03/2019 | 06:04 | BU4 | Urban | Unknown | Unknown | 1 | 115.3 | 0.00018211 | 0.00015799 | No
23/03/2019 | 09:39 | NW32 | Urban | Asset Failure | LV | 5 | 1 | 7.773e-06 | 0.00077731 | No
23/03/2019 | 11:27 | NW32 | Urban | Overloads |  | 1 | 144.7 | 0.00022859 | 0.00015799 | No
23/03/2019 | 15:51 | CFD13 | Urban | Asset Failure | LV | 1 | 188.4 | 0.00029765 | 0.00015799 | No
23/03/2019 | 20:08 | GW2 | Urban | Asset Failure | LV | 1 | 315.5 | 0.00049843 | 0.00015799 | No
23/03/2019 | 20:49 | CFD15 | Urban | Asset Failure | LV | 1 | 135.5 | 0.00021413 | 0.00015799 | No
23/03/2019 | 22:33 | DC2 | Urban | Asset Failure | LV | 1 | 100 | 0.00015799 | 0.00015799 | No
23/03/2019 | 23:10 | SV32 | Urban | Asset Failure | LV | 1 | 50 | 7.8995e-05 | 0.00015799 | No
24/03/2019 | 05:49 | HGS33 | Rural Short | Animal | Animal impact | 3 | 81.5 | 0.0041129 | 0.0050445 | No
24/03/2019 | 08:54 | MR15 | Urban | Asset Failure | LV | 1 | 141 | 0.00022277 | 0.00015799 | No
24/03/2019 | 12:31 | NP34 | Urban | Third Party | Other | 1 | 138.3 | 0.00021842 | 0.00015799 | No
24/03/2019 | 13:04 | CRM21 | Urban | Asset Failure | LV | 1 | 115.5 | 0.0001824 | 0.00015799 | No
24/03/2019 | 14:41 | BU9 | Urban | Vegetation | Grow-in - NSP responsibility | 44 | 85 | 0.0059088 | 0.0069516 | No
24/03/2019 | 15:53 | EM5 | Urban | Asset Failure | HV | 737 | 60.2 | 0.070137 | 0.11644 | No
24/03/2019 | 16:06 | MGE24 | Urban | Asset Failure | LV | 1 | 134 | 0.00021171 | 0.00015799 | No
24/03/2019 | 16:57 | DMA23 | Rural Short | Weather |  | 91 | 55 | 0.084196 | 0.15302 | No
24/03/2019 | 16:57 | EM7 | Urban | Vegetation | Grow-in - Other responsible party | 1,533 | 9.8 | 0.023695 | 0.2422 | No
24/03/2019 | 16:57 | EM5 | Urban | Vegetation | Grow-in - Other responsible party | 1,562 | 25.1 | 0.061946 | 0.24678 | No
25/03/2019 | 00:00 | BU4 | Urban | Asset Failure | LV | 1 | 211.5 | 0.00033415 | 0.00015799 | No
25/03/2019 | 02:04 | OAK35 | Urban | Asset Failure | HV | 34 | 111 | 0.0059625 | 0.0053717 | No
25/03/2019 | 02:33 | FSH12 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1,272 | 56.3 | 1.2044 | 2.1389 | No
25/03/2019 | 04:11 | FSH31 | Urban | Asset Failure | LV | 1 | 51.7 | 8.1681e-05 | 0.00015799 | No
25/03/2019 | 04:42 | LWN21 | Rural Short | Unknown | Unknown | 3 | 188 | 0.0094836 | 0.0050445 | No
25/03/2019 | 07:12 | STO14 | Rural Short | Asset Failure | Distribution substation | 2 | 178 | 0.0059861 | 0.003363 | No
25/03/2019 | 08:44 | DVY13 | Urban | Third Party | Other | 1 | 184.5 | 0.00029152 | 0.00015799 | No
25/03/2019 | 09:06 | CRM35 | Urban | Asset Failure | LV | 1 | 67.2 | 0.00010617 | 0.00015799 | No
25/03/2019 | 09:55 | BU4 | Urban | Asset Failure | LV | 1 | 125.8 | 0.0001988 | 0.00015799 | No
25/03/2019 | 10:05 | FTN21 | Urban | Asset Failure | LV | 5 | 160 | 0.0012209 | 0.00076309 | No
25/03/2019 | 10:09 | MTN31 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 140.9 | 0.00022256 | 0.00015799 | No
25/03/2019 | 11:16 | HGS31 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 492.6 | 0.0082836 | 0.0016815 | No
25/03/2019 | 12:22 | DMA21 | Urban | Overloads |  | 1 | 384.2 | 0.00060692 | 0.00015799 | No
25/03/2019 | 13:02 | RBD24 | Urban | Vegetation | Grow-in - NSP responsibility | 1,516 | 61.8 | 0.14795 | 0.23951 | No
25/03/2019 | 13:13 | DMA23 | Rural Short | Vegetation | Grow-in - NSP responsibility | 8 | 934.6 | 0.12572 | 0.013452 | No
25/03/2019 | 13:24 | STO13 | Urban | Vegetation | Grow-in - NSP responsibility | 261 | 170 | 0.070093 | 0.041235 | No
25/03/2019 | 13:27 | LWN24 | Urban | Third Party | Vehicle Impact | 1 | 146.6 | 0.00023153 | 0.00015799 | No
25/03/2019 | 13:30 | GW6 | Urban | Weather |  | 1,206 | 22.4 | 0.042704 | 0.19054 | No
25/03/2019 | 13:46 | RBD12 | Rural Short | Asset Failure | LV | 1 | 328.7 | 0.0055265 | 0.0016815 | No
25/03/2019 | 13:54 | MTN32 | Rural Short | Weather |  | 482 | 52.4 | 0.42469 | 0.81048 | No
25/03/2019 | 14:05 | STO13 | Urban | Vegetation | Grow-in - NSP responsibility | 1,558 | 37.1 | 0.091356 | 0.24615 | No
25/03/2019 | 14:10 | BU2 | Urban | Vegetation | Grow-in - NSP responsibility | 10 | 150 | 0.0024244 | 0.0016162 | No
25/03/2019 | 14:26 | BU13 | Urban | Weather |  | 12 | 215 | 0.0040354 | 0.0018769 | No
25/03/2019 | 14:28 | RBD24 | Urban | Asset Failure | Distribution substation | 101 | 46.7 | 0.0074492 | 0.015957 | No
25/03/2019 | 14:34 | BH23 | Urban | Asset Failure | LV | 53 | 390 | 0.032533 | 0.0083419 | No
25/03/2019 | 14:48 | HGS33 | Rural Short | Vegetation | Grow-in - NSP responsibility | 19 | 267 | 0.085302 | 0.031948 | No
25/03/2019 | 15:20 | FTN11 | Urban | Asset Failure | LV | 1 | 95.6 | 0.00015101 | 0.00015799 | No
25/03/2019 | 16:10 | STO13 | Urban | Unknown | Unknown | 41 | 1.3 | 8.4209e-05 | 0 | No
25/03/2019 | 16:11 | KBH34 | Urban | Asset Failure | LV | 1 | 469 | 0.00074097 | 0.00015799 | No
25/03/2019 | 17:27 | BU6 | Urban | Vegetation | Grow-in - NSP responsibility | 37 | 33 | 0.0019291 | 0.0058456 | No
25/03/2019 | 17:49 | DMA14 | Urban | Weather |  | 178 | 315.8 | 0.088815 | 0.028122 | No
25/03/2019 | 18:31 | BH12 | Urban | Asset Failure | LV | 45 | 149 | 0.010643 | 0.0071427 | No
25/03/2019 | 19:08 | K10 | Urban | Asset Failure | LV | 1 | 185.2 | 0.00029257 | 0.00015799 | No
25/03/2019 | 19:14 | DMA13 | Rural Short | Asset Failure | LV | 1 | 45 | 0.00075667 | 0.0016815 | No
25/03/2019 | 20:58 | MR15 | Urban | Asset Failure | LV | 22 | 132 | 0.0046798 | 0.0035453 | No
25/03/2019 | 21:30 | HGS22 | Rural Short | Vegetation | Grow-in - NSP responsibility | 8 | 60 | 0.0080712 | 0.013452 | No
25/03/2019 | 22:09 | DMA24 | Rural Short | Asset Failure | HV | 1,735 | 70.9 | 2.0673 | 2.9174 | No
25/03/2019 | 22:09 | DMA14 | Urban | Asset Failure | HV | 3,120 | 30.3 | 0.14915 | 0.49293 | No
25/03/2019 | 22:40 | BW22 | Urban | Asset Failure | LV | 1 | 109.3 | 0.0001726 | 0.00015799 | No
25/03/2019 | 22:57 | MTN32 | Rural Short | Vegetation | Grow-in - NSP responsibility | 21 | 38.4 | 0.013571 | 0.035311 | No
26/03/2019 | 00:09 | DMA24 | Rural Short | Asset Failure | HV | 147 | 4.4 | 0.010794 | 0 | No
26/03/2019 | 03:54 | CRM12 | Urban | Asset Failure | LV | 7 | 81 | 0.00092908 | 0.001147 | No
26/03/2019 | 07:04 | EB24 | Urban | Third Party | Other | 1 | 86 | 0.00013587 | 0.00015799 | No
26/03/2019 | 07:39 | FTN14 | Urban | Asset Failure | LV | 21 | 66 | 0.0022023 | 0.0033367 | No
26/03/2019 | 12:47 | NW22 | Urban | Asset Failure | LV | 1 | 340.4 | 0.0005378 | 0.00015799 | No
26/03/2019 | 12:54 | MTN31 | Urban | Other | XXX | 1 | 155.9 | 0.00024628 | 0.00015799 | No
26/03/2019 | 13:18 | GW11 | Urban | Asset Failure | LV | 1 | 186 | 0.00029386 | 0.00015799 | No
26/03/2019 | 13:36 | MTN24 | Rural Short | Weather |  | 1 | 44 | 0.00073986 | 0.0016815 | No
26/03/2019 | 14:03 | OR34 | Urban | Asset Failure | LV | 1 | 186.9 | 0.00029526 | 0.00015799 | No
26/03/2019 | 17:11 | CRM13 | Urban | Third Party | Other | 1 | 117 | 0.00018485 | 0.00015799 | No
26/03/2019 | 18:02 | SR13 | Urban | Unknown | Unknown | 1 | 180.3 | 0.0002848 | 0.00015799 | No
26/03/2019 | 22:03 | DMA23 | Rural Short | Animal | Animal impact | 2 | 82 | 0.0027576 | 0.003363 | No
27/03/2019 | 15:05 | CRM21 | Urban | Asset Failure | LV | 1 | 139.2 | 0.00021984 | 0.00015799 | No
27/03/2019 | 21:40 | MR24 | Urban | Asset Failure | LV | 52 | 270 | 0.022182 | 0.0082155 | No
27/03/2019 | 22:21 | BH22 | Urban | Animal | Animal impact | 698 | 127.3 | 0.14036 | 0.11028 | No
27/03/2019 | 22:24 | BH34 | Urban | Unknown | Unknown | 6 | 224 | 0.0021942 | 0.00097954 | No
27/03/2019 | 23:49 | MR15 | Urban | Asset Failure | LV | 4 | 21 | 0.00012939 | 0.00061616 | No
28/03/2019 | 00:39 | DC2 | Urban | Asset Failure | LV | 1 | 196 | 0.00030958 | 0.00015799 | No
28/03/2019 | 10:25 | DN24 | Urban | Unknown | Unknown | 1 | 464.4 | 0.00073368 | 0.00015799 | No
28/03/2019 | 12:00 | LWN32 | Rural Short | Asset Failure | LV | 1 | 299.2 | 0.0050305 | 0.0016815 | No
28/03/2019 | 12:45 | STO21 | Rural Short | Weather |  | 324 | 30.7 | 0.16732 | 0.5448 | No
28/03/2019 | 16:43 | FSH22 | Urban | Asset Failure | LV | 1 | 92 | 0.00014535 | 0.00015799 | No
28/03/2019 | 17:23 | BC23 | Urban | Asset Failure | LV | 1 | 321.9 | 0.00050862 | 0.00015799 | No
28/03/2019 | 19:07 | EM11 | Urban | Asset Failure | LV | 1 | 127.3 | 0.00020107 | 0.00015799 | No
29/03/2019 | 05:30 | BR1 | Urban | Asset Failure | LV | 21 | 269.6 | 0.0089948 | 0.0033367 | No
29/03/2019 | 07:57 | M32 | Urban | Asset Failure | LV | 1 | 213 | 0.00033652 | 0.00015799 | No
29/03/2019 | 10:10 | MTN34 | Urban | Network Business | Networ Error | 12 | 67 | 0.0012226 | 0.0018248 | No
29/03/2019 | 15:08 | DSH14 | Urban | Asset Failure | LV | 1 | 126.6 | 0.00020002 | 0.00015799 | No
29/03/2019 | 16:10 | MGE23 | Urban | Vegetation | Grow-in - NSP responsibility | 964 | 60.6 | 0.092292 | 0.1523 | No
29/03/2019 | 16:14 | OR23 | Urban | Asset Failure | LV | 1 | 615.4 | 0.0009723 | 0.00015799 | No
29/03/2019 | 16:30 | OR23 | Urban | Asset Failure | LV | 1 | 599.9 | 0.00094781 | 0.00015799 | No
29/03/2019 | 17:10 | FSH33 | Urban | Asset Failure | HV | 58 | 91.8 | 0.0084074 | 0.0091634 | No
29/03/2019 | 17:14 | OAK33 | Urban | Vegetation | Grow-in - NSP responsibility | 1,324 | 32 | 0.066972 | 0.20918 | No
29/03/2019 | 17:33 | FSH32 | Rural Short | Vegetation | Grow-in - NSP responsibility | 28 | 219.5 | 0.10332 | 0.047082 | No
29/03/2019 | 17:57 | CRM13 | Urban | Asset Failure | LV | 6 | 476.9 | 0.0044755 | 0.00093846 | No
29/03/2019 | 19:35 | RBD14 | Urban | Asset Failure | Distribution substation | 128 | 85 | 0.017189 | 0.020223 | No
29/03/2019 | 19:37 | RBD22 | Urban | Unknown | Unknown | 63 | 438 | 0.043596 | 0.0099534 | No
29/03/2019 | 20:51 | CDA11 | Urban | Asset Failure | LV | 1 | 283 | 0.00044711 | 0.00015799 | No
29/03/2019 | 22:41 | DC3 | Urban | Third Party | Vehicle Impact | 59 | 152 | 0.014169 | 0.0093214 | No
30/03/2019 | 02:25 | SV23 | Urban | Asset Failure | HV | 74 | 103.7 | 0.012122 | 0.011691 | No
30/03/2019 | 04:16 | STO13 | Urban | Asset Failure | LV | 3 | 599 | 0.002981 | 0.00049767 | No
30/03/2019 | 07:40 | NB35 | Urban | Asset Failure | HV | 746 | 94.9 | 0.11187 | 0.11786 | No
30/03/2019 | 09:37 | MR21 | Urban | Unknown | Unknown | 1 | 57.3 | 9.0581e-05 | 0.00015799 | No
30/03/2019 | 10:20 | CFD16 | Urban | Asset Failure | LV | 1 | 324.3 | 0.00051231 | 0.00015799 | No
30/03/2019 | 13:33 | KBH34 | Urban | Asset Failure | LV | 1 | 162 | 0.00025594 | 0.00015799 | No
30/03/2019 | 13:37 | M32 | Urban | Asset Failure | LV | 1 | 228 | 0.00036022 | 0.00015799 | No
30/03/2019 | 14:09 | STO14 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 77.4 | 0.0013018 | 0.0016815 | No
30/03/2019 | 14:39 | CFD16 | Urban | Asset Failure | LV | 1 | 65.5 | 0.00010343 | 0.00015799 | No
30/03/2019 | 16:23 | STO21 | Rural Short | Third Party | Other | 2 | 16 | 0.00053808 | 0.003363 | No
30/03/2019 | 20:57 | EW9 | Urban | Asset Failure | LV | 1 | 47.7 | 7.5335e-05 | 0.00015799 | No
31/03/2019 | 06:51 | STO13 | Urban | Asset Failure | LV | 1 | 113.4 | 0.00017911 | 0.00015799 | No
31/03/2019 | 07:23 | MR32 | Urban | Asset Failure | LV | 2 | 185 | 0.00058451 | 0.00031598 | No
31/03/2019 | 10:40 | FSH34 | Urban | Third Party | Vehicle Impact | 1 | 223.5 | 0.00035303 | 0.00015799 | No
31/03/2019 | 17:50 | CRM22 | Urban | Asset Failure | LV | 1 | 307 | 0.00048503 | 0.00015799 | No
31/03/2019 | 21:21 | SR13 | Urban | Asset Failure | LV | 1 | 102.4 | 0.00016181 | 0.00015799 | No
31/03/2019 | 22:10 | CDA11 | Urban | Third Party | Vehicle Impact | 75 | 335 | 0.039695 | 0.011849 | No
31/03/2019 | 23:00 | STO23 | Urban | Asset Failure | HV | 3 | 86.9 | 0.00041164 | 0.00047397 | No
01/04/2019 | 08:26 | EW8 | Urban | Asset Failure | LV | 1 | 79 | 0.00012481 | 0.00015799 | No
01/04/2019 | 08:40 | BU10 | Urban | Asset Failure | LV | 1 | 93.5 | 0.00014767 | 0.00015799 | No
01/04/2019 | 09:15 | FSH31 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 92 | 0.00014535 | 0.00015799 | No
01/04/2019 | 10:32 | LWN35 | Urban | Asset Failure | LV | 1 | 148 | 0.00023383 | 0.00015799 | No
01/04/2019 | 18:28 | K8 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 90.7 | 0.0001433 | 0.00015799 | No
01/04/2019 | 21:01 | NB26 | Urban | Asset Failure | LV | 1 | 103.9 | 0.0001642 | 0.00015799 | No
01/04/2019 | 21:39 | EB14 | Urban | Unknown | Unknown | 1 | 41 | 6.4776e-05 | 0.00015799 | No
01/04/2019 | 22:42 | NW21 | Urban | Asset Failure | LV | 1 | 45.3 | 7.1596e-05 | 0.00015799 | No
02/04/2019 | 08:23 | SV23 | Urban | Asset Failure | LV | 1 | 186.7 | 0.00029489 | 0.00015799 | No
02/04/2019 | 09:19 | CFD23 | Urban | Asset Failure | LV | 1 | 99 | 0.00015641 | 0.00015799 | No
02/04/2019 | 11:11 | DC5 | Urban | Unknown | Unknown | 1 | 75.7 | 0.00011955 | 0.00015799 | No
02/04/2019 | 14:21 | NB24 | Urban | Asset Failure | HV | 662 | 35.6 | 0.037236 | 0.10459 | No
02/04/2019 | 16:21 | KBH35 | Urban | Third Party | Other | 1 | 180.1 | 0.00028451 | 0.00015799 | No
02/04/2019 | 20:25 | DMA15 | Rural Short | Asset Failure | HV | 49 | 167 | 0.13761 | 0.082393 | No
02/04/2019 | 20:43 | FTN22 | Urban | Asset Failure | LV | 1 | 183 | 0.00028912 | 0.00015799 | No
02/04/2019 | 23:12 | NW22 | Urban | Asset Failure | LV | 1 | 112 | 0.00017695 | 0.00015799 | No
03/04/2019 | 02:58 | SV20 | Urban | Unknown | Unknown | 98 | 118.9 | 0.018416 | 0.015483 | No
03/04/2019 | 08:36 | SV23 | Urban | Asset Failure | LV | 1 | 73.2 | 0.00011562 | 0.00015799 | No
03/04/2019 | 12:28 | MTN32 | Rural Short | Asset Failure | LV | 1 | 181.7 | 0.003055 | 0.0016815 | No
04/04/2019 | 00:35 | NW13 | Urban | Unknown | Unknown | 1 | 3.3 | 5.214e-06 | 0.00015799 | No
04/04/2019 | 08:52 | MC2 | Urban | Asset Failure | LV | 1 | 157 | 0.00024804 | 0.00015799 | No
04/04/2019 | 09:22 | HGS33 | Rural Short | Asset Failure | LV | 7 | 83 | 0.0097695 | 0.01177 | No
04/04/2019 | 11:56 | OE4 | Urban | Unknown | Unknown | 1 | 61 | 9.6374e-05 | 0.00015799 | No
04/04/2019 | 12:51 | MTN22 | Rural Short | Third Party | Vehicle Impact | 37 | 124 | 0.077147 | 0.062215 | No
04/04/2019 | 14:08 | MGE34 | Urban | Asset Failure | LV | 1 | 51 | 8.0575e-05 | 0.00015799 | No
04/04/2019 | 16:39 | MTN22 | Rural Short | Asset Failure | LV | 1 | 125.1 | 0.0021038 | 0.0016815 | No
04/04/2019 | 18:34 | MTN24 | Rural Short | Network Business | Networ Error | 1 | 215.2 | 0.0036177 | 0.0016815 | No
04/04/2019 | 22:33 | FSH23 | Rural Short | Animal | Animal impact | 25 | 140 | 0.058852 | 0.042037 | No
05/04/2019 | 10:42 | CRM35 | Urban | Weather |  | 17 | 273 | 0.0073323 | 0.0026858 | No
05/04/2019 | 11:54 | LD32 | Urban | Asset Failure | LV | 10 | 59.7 | 0.00094267 | 0.0015799 | No
05/04/2019 | 16:55 | BW32 | Urban | Asset Failure | LV | 1 | 140 | 0.00022119 | 0.00015799 | No
05/04/2019 | 17:36 | FSH13 | Urban | Unknown | Unknown | 2 | 101 | 0.00031595 | 0.00031282 | No
05/04/2019 | 18:36 | CDA23 | Urban | Third Party | Vehicle Impact | 26 | 618 | 0.025386 | 0.0041077 | No
05/04/2019 | 18:47 | CDA23 | Urban | Third Party | Vehicle Impact | 166 | 606.8 | 0.15913 | 0.026226 | No
05/04/2019 | 19:06 | GW5 | Urban | Unknown | Unknown | 1 | 83.8 | 0.00013237 | 0.00015799 | No
06/04/2019 | 03:38 | DC1 | Urban | Asset Failure | HV | 39 | 301 | 0.018544 | 0.0061616 | No
06/04/2019 | 09:39 | FSH33 | Urban | Asset Failure | LV | 28 | 96 | 0.0042544 | 0.0044316 | No
06/04/2019 | 11:45 | BT15 | Urban | Overloads |  | 1 | 164.2 | 0.00025939 | 0.00015799 | No
06/04/2019 | 19:40 | LWN21 | Rural Short | Other | XXX | 1 | 109.9 | 0.0018485 | 0.0016815 | No
06/04/2019 | 19:59 | LWN21 | Rural Short | Other | XXX | 1 | 90.2 | 0.0015159 | 0.0016815 | No
07/04/2019 | 06:31 | CRM24 | Urban | Unknown | Unknown | 1 | 178.4 | 0.0002818 | 0.00015799 | No
07/04/2019 | 06:56 | EL14 | Urban | Asset Failure | LV | 1 | 109 | 0.00017221 | 0.00015799 | No
07/04/2019 | 08:04 | EB21 | Urban | Asset Failure | LV | 1 | 105.5 | 0.00016673 | 0.00015799 | No
07/04/2019 | 15:06 | MTN34 | Urban | Asset Failure | HV | 2,432 | 53 | 0.20352 | 0.38423 | No
07/04/2019 | 18:56 | MGE24 | Urban | Asset Failure | LV | 1 | 94.9 | 0.00014998 | 0.00015799 | No
07/04/2019 | 18:56 | NP14 | Urban | Asset Failure | LV | 1 | 245.4 | 0.00038771 | 0.00015799 | No
08/04/2019 | 09:06 | STO21 | Rural Short | Third Party | Vehicle Impact | 24 | 199 | 0.080609 | 0.040507 | No
08/04/2019 | 09:28 | DN11 | Urban | Asset Failure | LV | 1 | 104.2 | 0.00016463 | 0.00015799 | No
08/04/2019 | 11:29 | STO21 | Rural Short | Asset Failure | LV | 1 | 241 | 0.0040524 | 0.0016815 | No
08/04/2019 | 13:11 | LWN34 | Urban | Unknown | Unknown | 1 | 138.1 | 0.00021816 | 0.00015799 | No
08/04/2019 | 14:24 | DMA23 | Rural Short | Vegetation | Grow-in - Other responsible party | 8 | 256 | 0.034437 | 0.013452 | No
08/04/2019 | 15:26 | DN11 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 212.2 | 0.00033518 | 0.00015799 | No
08/04/2019 | 16:35 | NB36 | Urban | Asset Failure | LV | 13 | 144 | 0.0030031 | 0.0020855 | No
08/04/2019 | 16:55 | FSH12 | Rural Short | Asset Failure | LV | 1 | 66.8 | 0.0011235 | 0.0016815 | No
08/04/2019 | 17:40 | HT1 | Urban | Asset Failure | HV | 9 | 440 | 0.0059088 | 0.0013429 | No
08/04/2019 | 19:30 | DVY14 | Urban | Asset Failure | HV | 58 | 23.6 | 0.0021633 | 0.0091634 | No
08/04/2019 | 21:41 | SS22 | Urban | Third Party | Other | 4 | 214 | 0.001278 | 0.0005972 | No
09/04/2019 | 06:43 | GW12 | Urban | Asset Failure | LV | 1 | 129 | 0.00020381 | 0.00015799 | No
09/04/2019 | 08:49 | DMA14 | Urban | Asset Failure | LV | 2 | 176 | 0.00047549 | 0.00027016 | No
09/04/2019 | 08:50 | DN10 | Urban | Third Party | Other | 1 | 34 | 5.3769e-05 | 0.00015799 | No
09/04/2019 | 11:06 | MTN34 | Urban | Asset Failure | LV | 36 | 69 | 0.00387 | 0.0056086 | No
09/04/2019 | 15:06 | M22 | Urban | Third Party | Other | 1 | 99 | 0.00015641 | 0.00015799 | No
09/04/2019 | 15:12 | FSH33 | Urban | Asset Failure | HV | 44 | 78 | 0.0054222 | 0.0069516 | No
09/04/2019 | 15:14 | FSH31 | Urban | Unknown | Unknown | 1 | 158.5 | 0.00025036 | 0.00015799 | No
09/04/2019 | 17:49 | DMA15 | Rural Short | Unknown | Unknown | 1 | 208.9 | 0.0035124 | 0.0016815 | No
09/04/2019 | 18:25 | FTN11 | Urban | Asset Failure | LV | 1 | 144.6 | 0.0002284 | 0.00015799 | No
09/04/2019 | 18:49 | FTN11 | Urban | Asset Failure | LV | 1 | 120.3 | 0.00019003 | 0.00015799 | No
10/04/2019 | 06:24 | SV34 | Urban | Asset Failure | LV | 1 | 65.8 | 0.00010393 | 0.00015799 | No
10/04/2019 | 11:00 | SVW53 | Urban | Asset Failure | LV | 1 | 314.4 | 0.00049675 | 0.00015799 | No
10/04/2019 | 17:28 | CDA22 | Urban | Asset Failure | HV | 42 | 62 | 0.0041141 | 0.0066356 | No
11/04/2019 | 15:02 | NP12 | Urban | Third Party | Vehicle Impact | 38 | 88 | 0.0052832 | 0.0060036 | No
11/04/2019 | 15:12 | STO21 | Rural Short | Unknown | Unknown | 2 | 157.7 | 0.0053034 | 0.003363 | No
11/04/2019 | 16:59 | EW2 | Urban | Overloads |  | 1 | 179.7 | 0.00028396 | 0.00015799 | No
11/04/2019 | 19:51 | SS23 | Urban | Animal | Other | 55 | 57 | 0.004953 | 0.0086894 | No
12/04/2019 | 07:10 | MR22 | Urban | Asset Failure | LV | 1 | 95 | 0.00015009 | 0.00015799 | No
12/04/2019 | 08:20 | FSH12 | Rural Short | Third Party | Other | 1 | 52.5 | 0.00088194 | 0.0016815 | No
12/04/2019 | 09:28 | MR14 | Urban | Asset Failure | LV | 1 | 121.6 | 0.00019206 | 0.00015799 | No
12/04/2019 | 13:05 | BH22 | Urban | Asset Failure | LV | 1 | 160.4 | 0.00025347 | 0.00015799 | No
12/04/2019 | 14:18 | HGS22 | Rural Short | Asset Failure | LV | 1 | 377 | 0.0063392 | 0.0016815 | No
12/04/2019 | 14:42 | DVY22 | Urban | Asset Failure | LV | 1 | 261.1 | 0.00041243 | 0.00015799 | No
12/04/2019 | 16:08 | LD4 | Urban | Third Party | Other | 1 | 157 | 0.00024804 | 0.00015799 | No
12/04/2019 | 21:00 | DC8 | Urban | Asset Failure | LV | 1 | 75 | 0.00011849 | 0.00015799 | No
13/04/2019 | 06:21 | HGS33 | Rural Short | Unknown | Unknown | 6 | 219 | 0.022095 | 0.010089 | No
13/04/2019 | 08:58 | M22 | Urban | Unknown | Unknown | 1 | 89 | 0.00014061 | 0.00015799 | No
13/04/2019 | 11:34 | SVW53 | Urban | Asset Failure | LV | 1 | 141 | 0.00022282 | 0.00015799 | No
13/04/2019 | 12:43 | SV33 | Urban | Asset Failure | LV | 1 | 2,101.6 | 0.0033203 | 0.00015799 | No
13/04/2019 | 16:38 | BW35 | Urban | Asset Failure | LV | 1 | 67 | 0.00010585 | 0.00015799 | No
13/04/2019 | 18:51 | DC5 | Urban | Asset Failure | LV | 1 | 63.7 | 0.00010061 | 0.00015799 | No
13/04/2019 | 19:12 | CRM22 | Urban | Asset Failure | LV | 1 | 100 | 0.00015799 | 0.00015799 | No
14/04/2019 | 01:35 | RBD12 | Rural Short | Animal | Animal impact | 4 | 160 | 0.010762 | 0.006726 | No
14/04/2019 | 05:52 | RWT24 | Urban | Animal | Other | 78 | 88.7 | 0.010912 | 0.012304 | No
14/04/2019 | 10:52 | NB34 | Urban | Asset Failure | LV | 1 | 203 | 0.00032072 | 0.00015799 | No
14/04/2019 | 11:44 | EB31 | Urban | Asset Failure | LV | 1 | 44.8 | 7.0727e-05 | 0.00015799 | No
14/04/2019 | 11:54 | STO21 | Rural Short | Asset Failure | LV | 1 | 50 | 0.00084075 | 0.0016815 | No
14/04/2019 | 16:22 | FTN21 | Urban | Third Party | Vehicle Impact | 1 | 60.1 | 9.4873e-05 | 0.00015799 | No
14/04/2019 | 23:33 | DN10 | Urban | Third Party | Other | 92 | 72 | 0.010465 | 0.014535 | No
15/04/2019 | 07:05 | DSH34 | Urban | Third Party | Other | 1 | 55 | 8.6894e-05 | 0.00015799 | No
15/04/2019 | 07:06 | OAK22 | Urban |  | Networ Error | 1 | 163.6 | 0.00025839 | 0.00015799 | No
15/04/2019 | 07:57 | DSH32 | Urban | Third Party | Other | 1 | 62.7 | 9.9033e-05 | 0.00015799 | No
15/04/2019 | 08:43 | WD16 | Urban | Asset Failure | LV | 1 | 47 | 7.4255e-05 | 0.00015799 | No
15/04/2019 | 09:24 | HT2 | Urban | Third Party | Vehicle Impact | 593 | 36.8 | 0.034438 | 0.093688 | No
15/04/2019 | 09:39 | SS13 | Urban | Asset Failure | LV | 1 | 110.1 | 0.00017395 | 0.00015799 | No
15/04/2019 | 12:57 | HT7 | Urban | Animal | Other | 22 | 143 | 0.0049704 | 0.0034758 | No
15/04/2019 | 14:00 | OR24 | Urban | Asset Failure | LV | 1 | 75 | 0.00011849 | 0.00015799 | No
15/04/2019 | 15:19 | MTN23 | Urban | Overloads |  | 18 | 41 | 0.0011718 | 0.002858 | No
15/04/2019 | 15:34 | MC3 | Urban | Asset Failure | LV | 3 | 100.9 | 0.0004733 | 0.00046923 | No
15/04/2019 | 19:28 | RWT23 | Urban | Weather |  | 1 | 62 | 9.7954e-05 | 0.00015799 | No
15/04/2019 | 19:53 | NB25 | Urban | Asset Failure | LV | 22 | 112 | 0.0038539 | 0.003441 | No
15/04/2019 | 21:29 | MGE34 | Urban | Animal | Animal impact | 62 | 46 | 0.0045059 | 0.0097954 | No
16/04/2019 | 09:09 | SR13 | Urban | Unknown | Unknown | 1 | 2 | 3.16e-06 | 0.00015799 | No
16/04/2019 | 10:00 | BC12 | Urban | Asset Failure | LV | 1 | 149.8 | 0.00023664 | 0.00015799 | No
16/04/2019 | 13:39 | GW11 | Urban | Asset Failure | LV | 1 | 141 | 0.00022277 | 0.00015799 | No
16/04/2019 | 14:30 | MTN31 | Urban | Asset Failure | LV | 3 | 419.7 | 0.0022078 | 0.00052611 | No
16/04/2019 | 15:15 | MTN32 | Rural Short | Third Party | Vehicle Impact | 5 | 1,740.0 | 0.14629 | 0.0084075 | No
16/04/2019 | 16:35 | EW9 | Urban | Asset Failure | LV | 43 | 40 | 0.002725 | 0.0068125 | No
16/04/2019 | 17:41 | RBD11 | Urban | Asset Failure | LV | 1 | 128.4 | 0.00020281 | 0.00015799 | No
16/04/2019 | 17:46 | LD7 | Urban | Unknown | Unknown | 1 | 358 | 0.0005656 | 0.00015799 | No
16/04/2019 | 18:07 | M25 | Urban | Asset Failure | LV | 1 | 142 | 0.00022435 | 0.00015799 | No
16/04/2019 | 19:48 | EB21 | Urban | Asset Failure | LV | 1 | 104 | 0.00016431 | 0.00015799 | No
16/04/2019 | 20:25 | SV32 | Urban | Third Party | Vehicle Impact | 455 | 305.8 | 0.21981 | 0.071885 | No
16/04/2019 | 21:46 | MTN34 | Urban | Asset Failure | Distribution substation | 173 | 265.2 | 0.07249 | 0.027332 | No
16/04/2019 | 21:46 | MTN22 | Rural Short | Third Party | Vehicle Impact | 32 | 254 | 0.13454 | 0.052967 | No
17/04/2019 | 03:29 | MTN34 | Urban | Unknown | Unknown | 1 | 60.2 | 9.5031e-05 | 0.00015799 | No
17/04/2019 | 04:26 | DMA15 | Rural Short | Asset Failure | HV | 573 | 25.7 | 0.24762 | 0.96349 | No
17/04/2019 | 04:26 | DMA23 | Rural Short | Asset Failure | HV | 2,452 | 52.4 | 2.1586 | 4.123 | No
17/04/2019 | 07:18 | DN8 | Urban | Asset Failure | LV | 1 | 191.3 | 0.00030216 | 0.00015799 | No
17/04/2019 | 13:42 | CDA21 | Urban | Asset Failure | LV | 1 | 78 | 0.00012323 | 0.00015799 | No
17/04/2019 | 17:32 | CRM22 | Urban | Third Party | Vehicle Impact | 1 | 107.1 | 0.00016926 | 0.00015799 | No
17/04/2019 | 17:49 | HT11 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 120.9 | 0.00019104 | 0.00015799 | No
17/04/2019 | 18:34 | EB22 | Urban | Asset Failure | LV | 1 | 115.9 | 0.00018303 | 0.00015799 | No
17/04/2019 | 19:37 | EB22 | Urban | Unknown | Unknown | 1 | 52.7 | 8.3208e-05 | 0.00015799 | No
18/04/2019 | 00:19 | HT11 | Urban | Asset Failure | LV | 119 | 81 | 0.015229 | 0.018801 | No
18/04/2019 | 00:39 | HT3 | Urban | Asset Failure | LV | 423 | 104.9 | 0.070109 | 0 | No
18/04/2019 | 00:56 | DC12 | Urban | Animal | Other | 181 | 79 | 0.022591 | 0.028596 | No
18/04/2019 | 09:19 | OAK35 | Urban | Asset Failure | LV | 1 | 90.7 | 0.00014322 | 0.00015799 | No
18/04/2019 | 11:00 | EB32 | Urban | Asset Failure | LV | 1 | 75 | 0.00011849 | 0.00015799 | No
18/04/2019 | 12:38 | DVY21 | Urban | Asset Failure | LV | 1 | 371.7 | 0.0005872 | 0.00015799 | No
18/04/2019 | 17:31 | K12 | Urban | Asset Failure | LV | 1 | 118.9 | 0.00018785 | 0.00015799 | No
18/04/2019 | 18:04 | CM13 | Urban | Unknown | Unknown | 1 | 166 | 0.00026226 | 0.00015799 | No
18/04/2019 | 18:12 | MGE31 | Urban | Asset Failure | LV | 1 | 68 | 0.00010743 | 0.00015799 | No
18/04/2019 | 21:32 | NP16 | Urban | Asset Failure | LV | 1 | 131 | 0.00020697 | 0.00015799 | No
19/04/2019 | 00:22 | CDA23 | Urban | Asset Failure | LV | 1 | 48 | 7.5835e-05 | 0.00015799 | No
19/04/2019 | 08:39 | STO23 | Urban | Asset Failure | LV | 1 | 335.9 | 0.00053069 | 0.00015799 | No
19/04/2019 | 10:23 | STO22 | Urban | Overloads |  | 7 | 67 | 0.00076849 | 0.001147 | No
19/04/2019 | 10:59 | MTN23 | Urban | Unknown | Unknown | 18 | 130.8 | 0.0036816 | 0.0028154 | No
19/04/2019 | 18:43 | OAK26 | Urban | Asset Failure | LV | 1 | 157 | 0.00024804 | 0.00015799 | No
20/04/2019 | 05:50 | RWT35 | Urban | Unknown | Unknown | 99 | 85 | 0.013295 | 0.015641 | No
20/04/2019 | 06:00 | CDA23 | Urban | Asset Failure | LV | 1 | 149.3 | 0.00023583 | 0.00015799 | No
20/04/2019 | 08:37 | RWT35 | Urban | Unknown | Unknown | 28 | 97.6 | 0.0043761 | 0.0044838 | No
20/04/2019 | 11:32 | DC3 | Urban | Asset Failure | HV | 84 | 177.6 | 0.023565 | 0.013271 | No
20/04/2019 | 13:08 | CDA11 | Urban | Asset Failure | LV | 1 | 175.6 | 0.0002774 | 0.00015799 | No
20/04/2019 | 18:44 | NW21 | Urban | Asset Failure | LV | 1 | 86 | 0.00013587 | 0.00015799 | No
20/04/2019 | 21:00 | CRM12 | Urban | Asset Failure | Distribution substation | 149 | 4.9 | 0.0011535 | 0.02354 | No
21/04/2019 | 13:11 | DMA14 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 173.4 | 0.0002739 | 0.00015799 | No
21/04/2019 | 21:55 | DMA23 | Rural Short | Weather |  | 114 | 247.3 | 0.4741 | 0.19169 | No
21/04/2019 | 23:19 | DMA23 | Rural Short | Weather |  | 2 | 386.1 | 0.012986 | 0.003363 | No
22/04/2019 | 02:43 | HGS33 | Rural Short | Animal | Animal impact | 61 | 107 | 0.10975 | 0.10257 | No
22/04/2019 | 17:38 | K2 | Urban | Asset Failure | LV | 1 | 47 | 7.4255e-05 | 0.00015799 | No
22/04/2019 | 17:51 | DC2 | Urban | Asset Failure | LV | 1 | 78.6 | 0.00012421 | 0.00015799 | No
22/04/2019 | 18:20 | HGS23 | Rural Short | Animal | Other | 1 | 95 | 0.0015974 | 0.0016815 | No
22/04/2019 | 20:36 | EM6 | Urban | Unknown | Unknown | 38 | 149 | 0.0089454 | 0.0060036 | No
23/04/2019 | 08:24 | EW2 | Urban | Asset Failure | LV | 1 | 101 | 0.00015957 | 0.00015799 | No
23/04/2019 | 08:46 | GW2 | Urban | Asset Failure | LV | 1 | 83 | 0.00013116 | 0.00015799 | No
23/04/2019 | 12:58 | HGS31 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 256.2 | 0.0043083 | 0.0016815 | No
23/04/2019 | 14:30 | CDA11 | Urban | Asset Failure | LV | 1 | 239 | 0.00037765 | 0.00015799 | No
23/04/2019 | 17:08 | CRM22 | Urban | Third Party | Other | 1 | 142 | 0.00022427 | 0.00015799 | No
23/04/2019 | 18:35 | MR22 | Urban | Overloads |  | 27 | 55 | 0.0023227 | 0.0042231 | No
23/04/2019 | 18:44 | MR12 | Urban | Asset Failure | LV | 1 | 225.1 | 0.00035558 | 0.00015799 | No
24/04/2019 | 02:27 | SS13 | Urban | Third Party | Other | 13 | 113 | 0.0022387 | 0.0019812 | No
24/04/2019 | 06:36 | HT6 | Urban | Asset Failure | HV | 22 | 183.4 | 0.0063734 | 0.0034758 | No
24/04/2019 | 10:09 | HT6 | Urban | Asset Failure | LV | 1 | 290 | 0.0004582 | 0.00015799 | No
24/04/2019 | 10:34 | KBH31 | Urban | Asset Failure | LV | 1 | 186 | 0.00029386 | 0.00015799 | No
24/04/2019 | 14:16 | M13 | Urban | Asset Failure | LV | 1 | 129.4 | 0.00020447 | 0.00015799 | No
24/04/2019 | 16:51 | LWN21 | Rural Short | Asset Failure | HV | 6 | 108.5 | 0.010945 | 0.010089 | No
24/04/2019 | 17:11 | MGE34 | Urban | Asset Failure | LV | 20 | 74 | 0.0023149 | 0.0031282 | No
25/04/2019 | 20:08 | MTN32 | Rural Short | Asset Failure | LV | 1 | 218.4 | 0.0036727 | 0.0016815 | No
26/04/2019 | 07:28 | MC6 | Urban | Vegetation | Grow-in - Other responsible party | 2,546 | 39 | 0.15676 | 0.40224 | No
26/04/2019 | 07:33 | BU6 | Urban | Unknown | Unknown | 1 | 89 | 0.00014061 | 0.00015799 | No
26/04/2019 | 07:39 | STO23 | Urban | Asset Failure | HV | 1,083 | 73.6 | 0.12595 | 0.1711 | No
26/04/2019 | 09:36 | FSH34 | Urban | Asset Failure | LV | 1 | 300.1 | 0.00047408 | 0.00015799 | No
26/04/2019 | 13:02 | OR34 | Urban | Unknown | Unknown | 1 | 14.7 | 2.3277e-05 | 0.00015799 | No
26/04/2019 | 13:42 | BH23 | Urban | Asset Failure | LV | 10 | 93 | 0.0014546 | 0.0015641 | No
26/04/2019 | 13:47 | EB14 | Urban | Asset Failure | LV | 1 | 57.8 | 9.1345e-05 | 0.00015799 | No
26/04/2019 | 14:46 | RBD14 | Urban | Unknown | Unknown | 1 | 358.5 | 0.00056631 | 0.00015799 | No
26/04/2019 | 14:47 | OR24 | Urban | Asset Failure | HV | 24 | 11.8 | 0.00044679 | 0.0037918 | No
26/04/2019 | 15:15 | STO13 | Urban | Asset Failure | Distribution substation | 98 | 85 | 0.013161 | 0.015483 | No
26/04/2019 | 15:18 | FSH32 | Rural Short | Asset Failure | LV | 3 | 146.7 | 0.0073977 | 0.0050445 | No
26/04/2019 | 15:59 | RBD13 | Urban | Asset Failure | LV | 36 | 86 | 0.0048425 | 0.0056308 | No
26/04/2019 | 19:43 | HT1 | Urban | Asset Failure | LV | 18 | 111.7 | 0.0032603 | 0.0029197 | No
26/04/2019 | 20:23 | FSH31 | Urban | Asset Failure | LV | 1 | 118.8 | 0.00018769 | 0.00015799 | No
26/04/2019 | 20:49 | DMA15 | Rural Short | Asset Failure | LV | 3 | 71 | 0.0035816 | 0.0050445 | No
26/04/2019 | 21:34 | STO13 | Urban | Weather |  | 1 | 195.4 | 0.00030877 | 0.00015799 | No
26/04/2019 | 21:59 | FSH31 | Urban | Asset Failure | LV | 1 | 31 | 4.8977e-05 | 0.00015799 | No
27/04/2019 | 00:08 | FTN23 | Urban | Planned |  | 6 | 36.6 | 0.0003471 | 0.00094794 | No
27/04/2019 | 06:55 | FSH12 | Rural Short | Asset Failure | LV | 1 | 130 | 0.0021859 | 0.0016815 | No
27/04/2019 | 10:22 | SS13 | Urban | Asset Failure | LV | 1 | 90.3 | 0.00014264 | 0.00015799 | No
27/04/2019 | 12:20 | HGS23 | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 38 | 128.9 | 0.082386 | 0.063897 | No
27/04/2019 | 14:32 | HGS23 | Rural Short | Asset Failure | LV | 11 | 43 | 0.0079535 | 0.018496 | No
27/04/2019 | 14:56 | SS23 | Urban | Asset Failure | HV | 85 | 103.2 | 0.013854 | 0.013429 | No
27/04/2019 | 16:50 | RBD23 | Urban | Weather |  | 1 | 130 | 0.00020539 | 0.00015799 | No
27/04/2019 | 19:12 | FSH23 | Rural Short | Asset Failure | LV | 2 | 102.8 | 0.0028508 | 0.0027745 | No
27/04/2019 | 19:35 | NP24 | Urban | Asset Failure | LV | 1 | 215 | 0.00033968 | 0.00015799 | No
28/04/2019 | 02:48 | OAK26 | Urban | Asset Failure | LV | 1 | 355.5 | 0.00056158 | 0.00015799 | No
28/04/2019 | 07:23 | BR9 | Urban | Asset Failure | LV | 1 | 156.2 | 0.00024681 | 0.00015799 | No
28/04/2019 | 13:30 | NW33 | Urban | Unknown | Unknown | 1 | 70 | 0.00011059 | 0.00015799 | No
28/04/2019 | 14:58 | LD32 | Urban | Asset Failure | LV | 1 | 72 | 0.00011375 | 0.00015799 | No
28/04/2019 | 18:12 | DN22 | Urban | Asset Failure | LV | 1 | 314 | 0.00049609 | 0.00015799 | No
29/04/2019 | 02:14 | NO4 | Urban | Unknown | Unknown | 1 | 133 | 0.00021005 | 0.00015799 | No
29/04/2019 | 07:12 | DSH32 | Urban | Animal | Animal impact | 2 | 87.4 | 0.00027617 | 0.00031598 | No
29/04/2019 | 09:10 | MTN22 | Rural Short | Asset Failure | LV | 14 | 65 | 0.015509 | 0.02386 | No
29/04/2019 | 09:50 | DMA23 | Rural Short | Weather |  | 3 | 234.7 | 0.011839 | 0.0050445 | No
29/04/2019 | 10:23 | EW12 | Urban | Asset Failure | LV | 1 | 67 | 0.00010585 | 0.00015799 | No
29/04/2019 | 11:31 | EB24 | Urban | Asset Failure | LV | 1 | 119 | 0.00018793 | 0.00015799 | No
30/04/2019 | 00:38 | LD4 | Urban | Third Party | Other | 1 | 197 | 0.00031124 | 0.00015799 | No
30/04/2019 | 05:21 | GW8 | Urban | Animal | Animal impact | 89 | 128.3 | 0.018043 | 0.014061 | No
30/04/2019 | 07:42 | HT3 | Urban | Asset Failure | LV | 1 | 137.7 | 0.00021761 | 0.00015799 | No
30/04/2019 | 07:49 | LWN21 | Rural Short | Overloads |  | 7 | 161 | 0.01895 | 0.01177 | No
30/04/2019 | 09:06 | DN25 | Urban | Asset Failure | LV | 1 | 144 | 0.0002275 | 0.00015799 | No
30/04/2019 | 11:45 | EB23 | Urban | Network Business | Networ Error | 4 | 35 | 0.00019907 | 0.00056876 | No
30/04/2019 | 13:43 | FSH31 | Urban | Asset Failure | LV | 9 | 137 | 0.0020238 | 0.0014772 | No
30/04/2019 | 14:00 | LD2 | Urban | Network Business | Networ Error | 10 | 119.6 | 0.0019198 | 0.0016052 | No
01/05/2019 | 02:56 | RBD21 | Rural Short | Asset Failure | LV | 4 | 179 | 0.010923 | 0.0061038 | No
01/05/2019 | 07:21 | DN4 | Urban | Asset Failure | LV | 2 | 118.4 | 0.00043211 | 0.00036496 | No
01/05/2019 | 10:44 | RWT24 | Urban | Asset Failure | LV | 16 | 66 | 0.0017101 | 0.002591 | No
01/05/2019 | 11:26 | MGE23 | Urban | Asset Failure | HV | 40 | 279 | 0.017632 | 0.0063196 | No
01/05/2019 | 11:42 | DMA24 | Rural Short | Asset Failure | LV | 1 | 118 | 0.0019842 | 0.0016815 | No
01/05/2019 | 12:50 | EM10 | Urban | Asset Failure | LV | 1 | 59.8 | 9.4452e-05 | 0.00015799 | No
01/05/2019 | 14:47 | LD33 | Urban | Asset Failure | LV | 11 | 43 | 0.00076088 | 0.0017695 | No
01/05/2019 | 15:20 | SR20 | Urban | Asset Failure | LV | 1 | 162.1 | 0.00025605 | 0.00015799 | No
01/05/2019 | 17:22 | K8 | Urban | Asset Failure | LV | 1 | 268.6 | 0.00042436 | 0.00015799 | No
01/05/2019 | 17:45 | CRM21 | Urban | Asset Failure | LV | 21 | 195 | 0.0064697 | 0.0033178 | No
02/05/2019 | 03:08 | FTN14 | Urban | Asset Failure | LV | 1 | 196.8 | 0.00031085 | 0.00015799 | No
02/05/2019 | 08:11 | CM13 | Urban | Asset Failure | LV | 1 | 94 | 0.00014851 | 0.00015799 | No
02/05/2019 | 10:14 | NB35 | Urban | Asset Failure | LV | 1 | 146 | 0.00023066 | 0.00015799 | No
02/05/2019 | 10:53 | K2 | Urban | Planned |  | 1 | 154.9 | 0.00024478 | 0.00015799 | No
02/05/2019 | 15:09 | LWN35 | Urban | Unknown | Unknown | 1 | 252.9 | 0.00039953 | 0.00015799 | No
02/05/2019 | 15:33 | BR15 | Urban | Asset Failure | LV | 1 | 267 | 0.00042183 | 0.00015799 | No
02/05/2019 | 18:14 | BH34 | Urban | Asset Failure | LV | 1 | 192.8 | 0.00030452 | 0.00015799 | No
03/05/2019 | 05:12 | MTN23 | Urban | Asset Failure | LV | 13 | 633 | 0.012541 | 0.0019812 | No
03/05/2019 | 07:17 | CRM34 | Urban | Asset Failure | LV | 1 | 345 | 0.00054512 | 0.00015799 | No
03/05/2019 | 07:50 | FTN24 | Urban | Asset Failure | Distribution substation | 40 | 130 | 0.0081333 | 0.0062564 | No
03/05/2019 | 16:32 | AR12 | Urban | Asset Failure | LV | 1 | 117.2 | 0.00018509 | 0.00015799 | No
03/05/2019 | 17:07 | RBD21 | Rural Short | Third Party | Dig-in | 1 | 187.4 | 0.0031517 | 0.0016815 | No
03/05/2019 | 19:43 | FTN24 | Urban | Asset Failure | LV | 1 | 52 | 8.2128e-05 | 0.00015799 | No
03/05/2019 | 19:47 | HGS33 | Rural Short | Animal | Other | 22 | 88 | 0.032554 | 0.036993 | No
04/05/2019 | 05:20 | FSH21 | Rural Short | Unknown | Unknown | 20 | 100 | 0.03363 | 0.03363 | No
04/05/2019 | 07:39 | NB24 | Urban | Overloads |  | 1 | 231 | 0.00036496 | 0.00015799 | No
04/05/2019 | 09:23 | OR33 | Urban | Overloads |  | 1 | 142 | 0.00022435 | 0.00015799 | No
04/05/2019 | 12:09 | SR15 | Urban | Asset Failure | LV | 117 | 141 | 0.026064 | 0.018485 | No
04/05/2019 | 14:14 | DC7 | Urban | Asset Failure | LV | 1 | 123.2 | 0.00019462 | 0.00015799 | No
04/05/2019 | 19:12 | HGS22 | Rural Short | Asset Failure | LV | 4 | 182.9 | 0.010763 | 0.0058852 | No
04/05/2019 | 22:19 | M31 | Urban | Asset Failure | LV | 1 | 116 | 0.00018327 | 0.00015799 | No
05/05/2019 | 07:57 | FSH13 | Urban | Asset Failure | LV | 1 | 150.2 | 0.0002373 | 0.00015799 | No
05/05/2019 | 08:37 | BU13 | Urban | Asset Failure | LV | 1 | 68.2 | 0.00010778 | 0.00015799 | No
05/05/2019 | 10:15 | DC8 | Urban | Weather |  | 1 | 107 | 0.00016905 | 0.00015799 | No
05/05/2019 | 13:42 | RWT34 | Urban | Asset Failure | HV | 70 | 28 | 0.0030966 | 0.011059 | No
05/05/2019 | 17:45 | FSH13 | Urban | Overloads |  | 1 | 90 | 0.00014219 | 0.00015799 | No
05/05/2019 | 18:50 | MR32 | Urban | Asset Failure | LV | 1 | 93.9 | 4.893e-05 | 5.2137e-05 | No
06/05/2019 | 01:54 | BR4 | Urban | Asset Failure | LV | 1 | 90.6 | 0.00014306 | 0.00015799 | No
06/05/2019 | 10:12 | EB32 | Urban | Unknown | Unknown | 1 | 187.3 | 2.0716e-05 | 1.1059e-05 | No
06/05/2019 | 14:00 | GW5 | Urban | Asset Failure | LV | 86 | 55 | 0.0074729 | 0.013587 | No
06/05/2019 | 19:00 | DC10 | Urban | Overloads |  | 9 | 80 | 0.0010844 | 0.0013556 | No
06/05/2019 | 19:00 | DC10 | Urban | Overloads |  | 13 | 80 | 0.001585 | 0.0019812 | No
06/05/2019 | 19:00 | DC10 | Urban | Overloads |  | 11 | 80 | 0.0014181 | 0.0017726 | No
06/05/2019 | 19:29 | CDA23 | Urban | Asset Failure | LV | 1 | 66 | 0.00010427 | 0.00015799 | No
07/05/2019 | 09:21 | GW7 | Urban | Planned |  | 1 | 69 | 0.00010901 | 0.00015799 | No
07/05/2019 | 10:57 | OR24 | Urban | Asset Failure | LV | 1 | 93 | 0.00014693 | 0.00015799 | No
07/05/2019 | 11:18 | FSH31 | Urban | Asset Failure | LV | 1 | 126.5 | 0.00019978 | 0.00015799 | No
07/05/2019 | 13:57 | EW2 | Urban | Third Party | Vehicle Impact | 1 | 122.1 | 0.00019288 | 0.00015799 | No
07/05/2019 | 15:43 | SS12 | Urban | Asset Failure | LV | 1 | 92.7 | 0.00014651 | 0.00015799 | No
07/05/2019 | 20:04 | DN11 | Urban | Asset Failure | LV | 33 | 86 | 0.0045286 | 0.0052658 | No
07/05/2019 | 21:41 | EM5 | Urban | Vegetation | Grow-in - Other responsible party | 34 | 490.3 | 0.026335 | 0.0053717 | No
07/05/2019 | 21:47 | SV16 | Urban | Asset Failure | LV | 13 | 118 | 0.0024236 | 0.0020539 | No
07/05/2019 | 21:49 | OAK26 | Urban | Asset Failure | LV | 1 | 105.6 | 0.00016678 | 0.00015799 | No
07/05/2019 | 21:50 | EM5 | Urban | Vegetation | Grow-in - Other responsible party | 1,525 | 35 | 0.084307 | 0.24093 | No
07/05/2019 | 21:56 | FSH34 | Urban |  |  | 2,884 | 35.5 | 0.16182 | 0.45564 | No
07/05/2019 | 22:23 | BH22 | Urban | Overloads |  | 1 | 132 | 0.00024191 | 0.00018327 | No
08/05/2019 | 00:56 | RWT34 | Urban | Asset Failure | LV | 1 | 93 | 0.00014693 | 0.00015799 | No
08/05/2019 | 05:27 | MGE12 | Urban | Asset Failure | LV | 39 | 302.2 | 0.01862 | 0.0061616 | No
08/05/2019 | 10:12 | GW7 | Urban | Asset Failure | LV | 1 | 138 | 0.00021803 | 0.00015799 | No
08/05/2019 | 12:30 | NW32 | Urban | Asset Failure | LV | 1 | 15 | 2.3698e-05 | 0.00015799 | No
08/05/2019 | 14:36 | EM5 | Urban | Asset Failure | LV | 1 | 233 | 0.00036817 | 0.00015799 | No
08/05/2019 | 15:03 | BW22 | Urban | Overloads |  | 1 | 206.6 | 0.00032641 | 0.00015799 | No
08/05/2019 | 16:14 | K12 | Urban | Asset Failure | LV | 1 | 221.5 | 0.00034992 | 0.00015799 | No
08/05/2019 | 18:03 | NW23 | Urban | Asset Failure | HV | 2 | 267 | 0.00084367 | 0.00031598 | No
08/05/2019 | 19:21 | CDA22 | Urban | Asset Failure | LV | 1 | 126 | 0.00019907 | 0.00015799 | No
08/05/2019 | 20:42 | LWN21 | Rural Short | Animal | Animal impact | 1 | 138.6 | 0.00233 | 0.0016815 | No
08/05/2019 | 21:15 | LWN33 | Urban | Third Party | Vehicle Impact | 4 | 104 | 0.00065067 | 0.00062564 | No
09/05/2019 | 00:36 | FTN12 | Urban | Weather |  | 1 | 50.4 | 7.9574e-05 | 0.00015799 | No
09/05/2019 | 05:32 | FSH21 | Rural Short | Unknown | Unknown | 12 | 132.6 | 0.026746 | 0.020178 | No
09/05/2019 | 07:12 | FSH21 | Rural Short | Asset Failure | LV | 1 | 92.3 | 0.0015523 | 0.0016815 | No
09/05/2019 | 08:00 | DMA23 | Rural Short | Asset Failure | LV | 1 | 450 | 0.0075667 | 0.0016815 | No
09/05/2019 | 08:02 | STO13 | Urban | Asset Failure | LV | 1 | 237.1 | 0.00037462 | 0.00015799 | No
09/05/2019 | 09:17 | LD6 | Urban | Asset Failure | LV | 1 | 118 | 0.00018643 | 0.00015799 | No
09/05/2019 | 09:58 | MC3 | Urban | Third Party | Vehicle Impact | 1 | 82 | 0.00012955 | 0.00015799 | No
09/05/2019 | 12:38 | HGS22 | Rural Short | Third Party | Vehicle Impact | 46 | 331.1 | 0.25613 | 0.077349 | No
09/05/2019 | 15:13 | CDA24 | Urban | Asset Failure | LV | 1 | 135 | 0.00021329 | 0.00015799 | No
09/05/2019 | 15:51 | HGS22 | Rural Short | Unknown | Unknown | 1 | 119 | 0.002001 | 0.0016815 | No
09/05/2019 | 16:03 | NW33 | Urban | Asset Failure | LV | 1 | 116.1 | 0.00018343 | 0.00015799 | No
09/05/2019 | 16:35 | NW33 | Urban | Asset Failure | LV | 1 | 84 | 0.00013276 | 0.00015799 | No
09/05/2019 | 19:17 | FSH11 | Urban | Asset Failure | LV | 1 | 72 | 0.0001138 | 0.00015799 | No
09/05/2019 | 22:58 | EL6 | Urban | Asset Failure | HV | 810 | 47 | 0.060143 | 0.12797 | No
10/05/2019 | 03:21 | NW22 | Urban | Asset Failure | LV | 1 | 62 | 9.7954e-05 | 0.00015799 | No
10/05/2019 | 08:02 | STO13 | Urban | Asset Failure | LV | 204 | 178 | 0.057369 | 0.03223 | No
10/05/2019 | 08:47 | NB24 | Urban | Asset Failure | LV | 1 | 135 | 0.00021329 | 0.00015799 | No
10/05/2019 | 08:49 | BH22 | Urban | Unknown | Unknown | 1 | 247 | 0.00039024 | 0.00015799 | No
10/05/2019 | 09:53 | STO22 | Urban | Unknown | Unknown | 2 | 66.7 | 0.00021076 | 0.00031598 | No
10/05/2019 | 11:07 | RWT34 | Urban | Asset Failure | LV | 1 | 229 | 0.00036185 | 0.00015799 | No
10/05/2019 | 12:12 | STO14 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 318 | 0.0053471 | 0.0016815 | No
10/05/2019 | 12:39 | STO23 | Urban | Asset Failure | LV | 11 | 56.5 | 0.00098133 | 0.0017379 | No
10/05/2019 | 13:38 | CRM24 | Urban | Asset Failure | LV | 1 | 232 | 0.00036654 | 0.00015799 | No
10/05/2019 | 13:38 | MR15 | Urban | Asset Failure | LV | 1 | 127 | 0.00020065 | 0.00015799 | No
10/05/2019 | 15:19 | SV34 | Urban | Asset Failure | LV | 1 | 99 | 0.00015641 | 0.00015799 | No
10/05/2019 | 16:03 | OR35 | Urban | Unknown | Unknown | 1 | 120.2 | 0.00018985 | 0.00015799 | No
10/05/2019 | 17:52 | STO13 | Urban | Asset Failure | LV | 1 | 292.1 | 0.00046154 | 0.00015799 | No
10/05/2019 | 18:49 | STO14 | Rural Short | Asset Failure | LV | 1 | 295.4 | 0.0049674 | 0.0016815 | No
10/05/2019 | 21:18 | SS13 | Urban | Asset Failure | LV | 1 | 91.7 | 0.00014485 | 0.00015799 | No
11/05/2019 | 00:37 | BR1 | Urban | Asset Failure | LV | 1 | 117 | 0.00018485 | 0.00015799 | No
11/05/2019 | 00:41 | DC5 | Urban | Third Party | Vehicle Impact | 5 | 593.1 | 0.0046849 | 0.00078995 | No
11/05/2019 | 03:22 | FTN21 | Urban | Overloads |  | 35 | 62.8 | 0.0034725 | 0.0055265 | No
11/05/2019 | 06:59 | DN10 | Urban | Unknown | Unknown | 165 | 163.4 | 0.042604 | 0.026068 | No
11/05/2019 | 07:52 | LWN35 | Urban | Asset Failure | LV | 1 | 97.5 | 0.00015396 | 0.00015799 | No
11/05/2019 | 08:28 | FTN24 | Urban | Asset Failure | LV | 1 | 159.1 | 0.00025136 | 0.00015799 | No
11/05/2019 | 09:43 | STO14 | Rural Short | Asset Failure | LV | 1 | 133.6 | 0.002247 | 0.0016815 | No
11/05/2019 | 09:50 | CRM33 | Urban | Unknown | Unknown | 1 | 256.5 | 0.00040522 | 0.00015799 | No
11/05/2019 | 10:19 | EB22 | Urban | Asset Failure | LV | 1 | 100.3 | 0.00015844 | 0.00015799 | No
11/05/2019 | 11:53 | CRM24 | Urban | Unknown | Unknown | 1 | 186.7 | 0.00029489 | 0.00015799 | No
11/05/2019 | 13:16 | FTN24 | Urban | Unknown | Unknown | 1 | 96.7 | 0.00015272 | 0.00015799 | No
11/05/2019 | 14:21 | DVY34 | Urban | Animal | Animal nesting/burrowing, etc and other | 424 | 128.4 | 0.086035 | 0.066988 | No
11/05/2019 | 14:55 | FSH21 | Rural Short | Other | XXX | 1 | 19.2 | 0.00032313 | 0.0016815 | No
11/05/2019 | 14:57 | NP34 | Urban | Asset Failure | LV | 1 | 71.3 | 0.00011265 | 0.00015799 | No
11/05/2019 | 19:02 | EW1 | Urban | Overloads |  | 3 | 219.6 | 0.0010408 | 0.00047397 | No
12/05/2019 | 07:03 | FSH13 | Urban | Asset Failure | LV | 1 | 111.5 | 0.00017611 | 0.00015799 | No
12/05/2019 | 07:18 | BW32 | Urban | Animal | Other | 1 | 76 | 0.00012013 | 0.00015799 | No
12/05/2019 | 09:57 | GW1 | Urban | Asset Failure | LV | 2 | 72.5 | 0.0002576 | 0.00035548 | No
12/05/2019 | 11:25 | STO21 | Rural Short | Asset Failure | LV | 1 | 199.1 | 0.0033478 | 0.0016815 | No
12/05/2019 | 14:07 | STO13 | Urban | Asset Failure | Distribution substation | 1 | 188 | 0.00029702 | 0.00015799 | No
12/05/2019 | 16:15 | RBD11 | Urban | Asset Failure | LV | 1 | 144.8 | 0.00022874 | 0.00015799 | No
12/05/2019 | 19:16 | DC7 | Urban | Asset Failure | LV | 1 | 163.8 | 0.00025884 | 0.00015799 | No
12/05/2019 | 19:37 | DMA21 | Urban | Asset Failure | LV | 29 | 12.1 | 0.00055591 | 0.0045817 | No
13/05/2019 | 08:10 | MTN22 | Rural Short | Asset Failure | LV | 1 | 109.4 | 0.0018401 | 0.0016815 | No
13/05/2019 | 12:13 | MTN24 | Rural Short | Third Party | Vehicle Impact | 35 | 597.2 | 0.35144 | 0.058852 | No
13/05/2019 | 13:17 | STO21 | Rural Short | Asset Failure | LV | 50 | 102.1 | 0.085868 | 0.084075 | No
13/05/2019 | 15:29 | EB14 | Urban | Asset Failure | LV | 1 | 119 | 0.00018801 | 0.00015799 | No
14/05/2019 | 09:15 | RBD21 | Rural Short | Third Party | Dig-in | 2 | 59.1 | 0.0019864 | 0.003363 | No
14/05/2019 | 10:40 | DC10 | Urban | Third Party | Other | 1 | 136 | 0.00021487 | 0.00015799 | No
14/05/2019 | 12:10 | GW3 | Urban | Third Party | Vehicle Impact | 1 | 81.3 | 0.0001285 | 0.00015799 | No
14/05/2019 | 14:18 | DMA14 | Urban | Asset Failure | LV | 10 | 297 | 0.0047486 | 0.0015989 | No
14/05/2019 | 20:14 | SH34 | Urban | Asset Failure | LV | 1 | 76 | 0.00012007 | 0.00015799 | No
14/05/2019 | 23:15 | BT4 | Urban | Asset Failure | LV | 1 | 70 | 0.00011059 | 0.00015799 | No
15/05/2019 | 09:33 | NP12 | Urban | Asset Failure | HV | 71 | 17 | 0.0019069 | 0.011217 | No
15/05/2019 | 10:43 | SH22 | Urban | Vegetation | Grow-in - NSP responsibility | 253 | 56.7 | 0.022678 | 0.039971 | No
15/05/2019 | 13:47 | DMA15 | Rural Short | Animal | Animal impact | 30 | 78 | 0.039544 | 0.050697 | No
15/05/2019 | 13:59 | DMA15 | Rural Short | Animal | Other | 1 | 65.9 | 0.0011078 | 0.0016815 | No
15/05/2019 | 16:01 | DSH23 | Urban | Asset Failure | LV | 1 | 268.3 | 0.00042389 | 0.00015799 | No
15/05/2019 | 18:12 | MTN31 | Urban | Asset Failure | LV | 1 | 97.7 | 0.00015438 | 0.00015799 | No
15/05/2019 | 18:39 | MR12 | Urban | Asset Failure | LV | 1 | 76 | 0.00012007 | 0.00015799 | No
15/05/2019 | 22:59 | NW31 | Urban | Asset Failure | LV | 1 | 46 | 7.2675e-05 | 0.00015799 | No
15/05/2019 | 23:15 | NP12 | Urban | Asset Failure | LV | 43 | 70 | 0.0047444 | 0.0067778 | No
16/05/2019 | 04:11 | DMA23 | Rural Short | Animal | Animal impact | 23 | 204 | 0.078141 | 0.038304 | No
16/05/2019 | 11:16 | LD7 | Urban | Third Party | Other | 1 | 103.4 | 0.00016336 | 0.00015799 | No
16/05/2019 | 16:31 | MC2 | Urban | Asset Failure | LV | 1 | 89 | 0.00014061 | 0.00015799 | No
16/05/2019 | 19:08 | CFD24 | Urban | Asset Failure | LV | 1 | 101.8 | 0.00016078 | 0.00015799 | No
16/05/2019 | 20:25 | FSH21 | Rural Short | Asset Failure | LV | 1 | 144.8 | 0.0024354 | 0.0016815 | No
16/05/2019 | 20:46 | FSH21 | Rural Short | Asset Failure | LV | 1 | 142.3 | 0.0023928 | 0.0016815 | No
16/05/2019 | 23:17 | EW1 | Urban | Asset Failure | LV | 1 | 81.3 | 0.00012845 | 0.00015799 | No
17/05/2019 | 10:04 | NO4 | Urban | Asset Failure | LV | 2 | 65.6 | 0.00020511 | 0.00031282 | No
17/05/2019 | 13:08 | GW7 | Urban | Asset Failure | HV | 1,158 | 43.2 | 0.079092 | 0.18295 | No
17/05/2019 | 13:12 | GW12 | Urban | Asset Failure | LV | 69 | 68 | 0.0074129 | 0.010901 | No
17/05/2019 | 13:36 | DMA13 | Rural Short | Asset Failure | LV | 20 | 29 | 0.0096551 | 0.033294 | No
17/05/2019 | 13:42 | DMA13 | Rural Short | Asset Failure | LV | 14 | 23 | 0.0053603 | 0.023305 | No
17/05/2019 | 14:09 | NB35 | Urban | Asset Failure | LV | 1 | 205.8 | 0.00032506 | 0.00015799 | No
17/05/2019 | 17:54 | BR10 | Urban | Overloads |  | 1 | 46 | 7.2675e-05 | 0.00015799 | No
17/05/2019 | 18:38 | BU1 | Urban | Asset Failure | LV | 1 | 220 | 0.00034758 | 0.00015799 | No
17/05/2019 | 20:05 | EW2 | Urban | Asset Failure | LV | 1 | 88.5 | 0.00013987 | 0.00015799 | No
18/05/2019 | 08:43 | FTN12 | Urban | Overloads |  | 1 | 76.1 | 0.00012026 | 0.00015799 | No
18/05/2019 | 12:32 | NW11 | Urban | Asset Failure | LV | 1 | 117.8 | 0.00018606 | 0.00015799 | No
18/05/2019 | 12:36 | STO21 | Rural Short | Asset Failure | LV | 12 | 29 | 0.0057931 | 0.019976 | No
18/05/2019 | 13:24 | EW12 | Urban | Asset Failure | LV | 1 | 156 | 0.00024646 | 0.00015799 | No
18/05/2019 | 15:04 | EW1 | Urban | Third Party | Other | 1 | 146 | 0.00023066 | 0.00015799 | No
18/05/2019 | 19:05 | CRM12 | Urban | Asset Failure | LV | 36 | 85 | 0.0048305 | 0.0056829 | No
18/05/2019 | 21:19 | STO14 | Rural Short | Asset Failure | LV | 1 | 268.8 | 0.0045198 | 0.0016815 | No
19/05/2019 | 07:44 | RWT34 | Urban | Asset Failure | LV | 1 | 91 | 0.00014377 | 0.00015799 | No
19/05/2019 | 08:03 | RBD12 | Rural Short | Asset Failure | LV | 1 | 147 | 0.0024718 | 0.0016815 | No
19/05/2019 | 09:54 | EB24 | Urban | Asset Failure | LV | 1 | 111 | 0.00017537 | 0.00015799 | No
19/05/2019 | 12:31 | FTN25 | Urban | Asset Failure | LV | 1 | 104 | 0.00016431 | 0.00015799 | No
19/05/2019 | 14:10 | BT10 | Urban | Asset Failure | LV | 1 | 116.3 | 0.00018379 | 0.00015799 | No
19/05/2019 | 16:36 | RBD23 | Urban | Asset Failure | LV | 60 | 235.5 | 0.022324 | 0.0094794 | No
19/05/2019 | 20:32 | EM10 | Urban | Asset Failure | LV | 1 | 150 | 0.00023698 | 0.00015799 | No
19/05/2019 | 22:10 | DN10 | Urban | Asset Failure | LV | 51 | 65 | 0.0052189 | 0.008029 | No
20/05/2019 | 00:53 | KBH34 | Urban | Asset Failure | LV | 5 | 118 | 0.00092282 | 0.00078205 | No
20/05/2019 | 06:04 | HT2 | Urban | Animal | Animal impact | 3 | 140.2 | 0.00066451 | 0.00047397 | No
20/05/2019 | 06:33 | OE10 | Urban | Unknown | Unknown | 1 | 52 | 8.2155e-05 | 0.00015799 | No
20/05/2019 | 11:06 | RBD23 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 114 | 0.00018011 | 0.00015799 | No
20/05/2019 | 11:48 | DSH34 | Urban | Unknown | Unknown | 1 | 97.4 | 0.00015394 | 0.00015799 | No
20/05/2019 | 12:29 | NB23 | Urban | Asset Failure | LV | 1 | 66 | 0.00010427 | 0.00015799 | No
20/05/2019 | 13:28 | SVW53 | Urban | Asset Failure | LV | 2 | 116.8 | 0.00036896 | 0.00031598 | No
20/05/2019 | 14:52 | NW14 | Urban | Animal | Other | 15 | 63 | 0.0015109 | 0.0023983 | No
20/05/2019 | 15:37 | MR22 | Urban | Third Party | Vehicle Impact | 1 | 643 | 0.0010158 | 0.00015799 | No
20/05/2019 | 17:46 | STO14 | Rural Short | Asset Failure | Distribution substation | 48 | 518.9 | 0.41881 | 0.080712 | No
20/05/2019 | 18:53 | BU10 | Urban | Asset Failure | LV | 1 | 144.3 | 0.00022793 | 0.00015799 | No
20/05/2019 | 18:59 | LWN34 | Urban | Third Party | Vehicle Impact | 5 | 266 | 0.0019416 | 0.00072991 | No
20/05/2019 | 19:07 | LWN23 | Urban | Animal | Animal impact | 2,669 | 56.8 | 0.23961 | 0.42167 | No
20/05/2019 | 22:06 | DMA15 | Rural Short | Unknown | Unknown | 2 | 148.2 | 0.0049823 | 0.003363 | No
21/05/2019 | 02:02 | STO14 | Rural Short | Animal | Animal impact | 5 | 108 | 0.0090801 | 0.0084075 | No
21/05/2019 | 03:07 | STO23 | Urban | Asset Failure | LV | 11 | 23 | 0.00040771 | 0.0017726 | No
21/05/2019 | 08:55 | CRM24 | Urban | Asset Failure | LV | 37 | 331 | 0.019349 | 0.0058456 | No
21/05/2019 | 09:52 | K10 | Urban | Asset Failure | LV | 1 | 157.9 | 0.00024941 | 0.00015799 | No
21/05/2019 | 09:55 | GW8 | Urban | Asset Failure | LV | 1 | 79.2 | 0.0001251 | 0.00015799 | No
21/05/2019 | 11:21 | MC7 | Urban | Asset Failure | LV | 1 | 99 | 0.00015636 | 0.00015799 | No
21/05/2019 | 11:55 | DMA23 | Rural Short | Asset Failure | HV | 35 | 69.4 | 0.040863 | 0.058852 | No
21/05/2019 | 12:19 | HGS33 | Rural Short | Asset Failure | LV | 1 | 245.1 | 0.0041205 | 0.0016815 | No
21/05/2019 | 13:53 | BW33 | Urban | Unknown | Unknown | 1 | 82 | 0.00012955 | 0.00015799 | No
21/05/2019 | 16:50 | EW9 | Urban | Asset Failure | Distribution substation | 271 | 110 | 0.047097 | 0.042815 | No
21/05/2019 | 17:36 | FTN14 | Urban | Asset Failure | LV | 1 | 84 | 0.00013271 | 0.00015799 | No
21/05/2019 | 18:21 | BT2 | Urban | Third Party | Vehicle Impact | 1 | 174.1 | 0.00027498 | 0.00015799 | No
21/05/2019 | 18:35 | BH11 | Urban | Animal | Animal impact | 118 | 59 | 0.010999 | 0.018643 | No
21/05/2019 | 19:15 | NW22 | Urban | Asset Failure | LV | 1 | 195 | 0.00030808 | 0.00015799 | No
22/05/2019 | 00:20 | FSH13 | Urban | Animal | Animal impact | 54 | 91 | 0.0077636 | 0.0085315 | No
22/05/2019 | 08:41 | CM13 | Urban | Unknown | Unknown | 1 | 8.9 | 1.4035e-05 | 0.00015799 | No
22/05/2019 | 09:23 | CFD12 | Urban | Other | XXX | 1 | 75.4 | 0.00011912 | 0.00015799 | No
22/05/2019 | 10:09 | OR24 | Urban | Unknown | Unknown | 1 | 38 | 6.0036e-05 | 0.00015799 | No
22/05/2019 | 10:48 | HGS32 | Urban | Asset Failure | LV | 1 | 161.7 | 0.00025542 | 0.00015799 | No
22/05/2019 | 13:31 | CFD26 | Urban | Unknown | Unknown | 1 | 192.7 | 0.00030439 | 0.00015799 | No
22/05/2019 | 19:22 | RWT34 | Urban | Asset Failure | LV | 9 | 338 | 0.0049129 | 0.0014535 | No
23/05/2019 | 00:53 | RBD24 | Urban | Asset Failure | LV | 3 | 112 | 0.00050253 | 0.00044869 | No
23/05/2019 | 04:26 | BH11 | Urban | Animal | Animal impact | 118 | 229 | 0.042692 | 0.018643 | No
23/05/2019 | 04:39 | K13 | Urban | Asset Failure | HV | 1,036 | 95.5 | 0.15639 | 0.16368 | No
23/05/2019 | 07:13 | LWN21 | Rural Short | Animal | Other | 1 | 56.7 | 0.00095312 | 0.0016815 | No
23/05/2019 | 07:25 | HGS32 | Urban | Asset Failure | LV | 3 | 139.7 | 0.00066206 | 0.00047397 | No
23/05/2019 | 09:15 | FTN14 | Urban | Asset Failure | LV | 1 | 74.7 | 0.00011794 | 0.00015799 | No
23/05/2019 | 09:51 | NW22 | Urban | Asset Failure | LV | 1 | 88 | 0.00013903 | 0.00015799 | No
23/05/2019 | 11:33 | WD34 | Urban | Asset Failure | LV | 47 | 147 | 0.010916 | 0.0074255 | No
23/05/2019 | 16:57 | BR15 | Urban | Asset Failure | LV | 1 | 242.1 | 0.00038244 | 0.00015799 | No
23/05/2019 | 23:19 | WD16 | Urban | Asset Failure | Distribution substation | 47 | 81 | 0.0059545 | 0.0073513 | No
23/05/2019 | 23:50 | EM9 | Urban | Asset Failure | LV | 1 | 44 | 6.9516e-05 | 0.00015799 | No
24/05/2019 | 05:34 | CDA22 | Urban | Asset Failure | LV | 1 | 178.8 | 9.3212e-05 | 5.2137e-05 | No
24/05/2019 | 08:59 | DC3 | Urban | Animal | Other | 90 | 11.9 | 0.0016968 | 0.014219 | No
24/05/2019 | 08:59 | DC6 | Urban | Animal | Other | 1,945 | 33.4 | 0.10276 | 0.30729 | No
24/05/2019 | 08:59 | DC4 | Urban | Animal | Other | 3,424 | 21 | 0.11377 | 0.54096 | No
24/05/2019 | 08:59 | DC2 | Urban | Animal | Other | 3,957 | 20 | 0.12528 | 0.62517 | No
24/05/2019 | 13:28 | CDA22 | Urban | Asset Failure | LV | 1 | 454.8 | 0.00071856 | 0.00015799 | No
24/05/2019 | 15:55 | BU10 | Urban | Overloads |  | 10 | 65 | 0.0010475 | 0.0016115 | No
24/05/2019 | 17:29 | RBD21 | Rural Short | Asset Failure | HV | 1 | 141 | 0.0023709 | 0.0016815 | No
24/05/2019 | 20:21 | EM5 | Urban | Asset Failure | LV | 22 | 57 | 0.0019614 | 0.003441 | No
24/05/2019 | 21:26 | HGS23 | Rural Short | Animal | Other | 13 | 113.5 | 0.024799 | 0.021859 | No
24/05/2019 | 23:57 | DMA23 | Rural Short | Asset Failure | LV | 5 | 118 | 0.0091668 | 0.0077685 | No
25/05/2019 | 06:25 | MTN32 | Rural Short | Overloads |  | 2 | 124.1 | 0.004174 | 0.003363 | No
25/05/2019 | 07:46 | RWT24 | Urban | Asset Failure | LV | 1 | 118 | 0.00018643 | 0.00015799 | No
25/05/2019 | 13:15 | BT10 | Urban | Third Party | Other | 1 | 95 | 0.00015009 | 0.00015799 | No
25/05/2019 | 13:37 | NP16 | Urban | Overloads |  | 1 | 189.8 | 0.00029989 | 0.00015799 | No
25/05/2019 | 14:57 | HGS22 | Rural Short | Asset Failure | LV | 1 | 133 | 0.0020127 | 0.0015133 | No
25/05/2019 | 20:10 | BC12 | Urban | Asset Failure | LV | 1 | 349.8 | 0.00055262 | 0.00015799 | No
25/05/2019 | 21:06 | DC1 | Urban | Asset Failure | LV | 7 | 354 | 0.003915 | 0.0011059 | No
25/05/2019 | 21:06 | DC1 | Urban | Asset Failure | LV | 1 | 353.5 | 0.00055842 | 0.00015799 | No
25/05/2019 | 21:09 | DC1 | Urban | Asset Failure | LV | 1 | 350.4 | 0.00055365 | 0.00015799 | No
26/05/2019 | 11:19 | EM2 | Urban | Asset Failure | LV | 1 | 87.2 | 0.00013774 | 0.00015799 | No
26/05/2019 | 17:28 | FSH31 | Urban | Weather |  | 1 | 118 | 0.00018645 | 0.00015799 | No
26/05/2019 | 20:01 | STO21 | Rural Short | Weather |  | 1 | 79 | 0.0013284 | 0.0016815 | No
27/05/2019 | 00:39 | SS13 | Urban | Animal | Animal impact | 134 | 90.7 | 0.019209 | 0.021171 | No
27/05/2019 | 06:22 | BR6 | Urban | Overloads |  | 1 | 117.9 | 0.00018627 | 0.00015799 | No
27/05/2019 | 06:34 | SS14 | Urban | Asset Failure | HV | 2 | 175.8 | 0.00055533 | 0.00031598 | No
27/05/2019 | 07:03 | HT1 | Urban | Unknown | Unknown | 1 | 296.9 | 0.00062859 | 0.00021171 | No
27/05/2019 | 08:46 | BR15 | Urban | Asset Failure | LV | 1 | 136 | 0.00021487 | 0.00015799 | No
27/05/2019 | 09:49 | CDA24 | Urban | Asset Failure | LV | 1 | 193.9 | 0.00030626 | 0.00015799 | No
27/05/2019 | 10:44 | BW35 | Urban | Asset Failure | LV | 1 | 199 | 0.0003144 | 0.00015799 | No
27/05/2019 | 10:59 | STO14 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 105.5 | 0.0017731 | 0.0016815 | No
27/05/2019 | 12:41 | FTN21 | Urban | Weather |  | 22 | 100.1 | 0.0034439 | 0.003441 | No
27/05/2019 | 14:17 | STO23 | Urban | Unknown | Unknown | 1 | 162.7 | 0.00025705 | 0.00015799 | No
27/05/2019 | 15:07 | BH22 | Urban | Asset Failure | LV | 1 | 67.6 | 0.00010683 | 0.00015799 | No
27/05/2019 | 15:27 | CRM13 | Urban | Asset Failure | LV | 1 | 69.6 | 0.00010991 | 0.00015799 | No
27/05/2019 | 15:47 | LD4 | Urban | Asset Failure | LV | 1 | 112.8 | 0.00017824 | 0.00015799 | No
27/05/2019 | 16:53 | STO23 | Urban | Asset Failure | LV | 1 | 84 | 0.00013271 | 0.00015799 | No
27/05/2019 | 17:02 | STO13 | Urban | Asset Failure | LV | 23 | 491.5 | 0.018194 | 0.0037017 | No
27/05/2019 | 17:08 | NP36 | Urban | Asset Failure | LV | 1 | 56.1 | 8.8685e-05 | 0.00015799 | No
27/05/2019 | 17:31 | DMA14 | Urban | Asset Failure | LV | 1 | 253 | 0.00039971 | 0.00015799 | No
27/05/2019 | 19:24 | RBD13 | Urban | Asset Failure | LV | 1 | 119 | 0.00018801 | 0.00015799 | No
27/05/2019 | 19:25 | DMA14 | Urban | Unknown | Unknown | 1 | 174.8 | 0.00027614 | 0.00015799 | No
27/05/2019 | 20:30 | SS14 | Urban | Asset Failure | HV | 1 | 555 | 0.00087684 | 0.00015799 | No
27/05/2019 | 21:10 | OR33 | Urban | Asset Failure | LV | 1 | 110 | 0.00017379 | 0.00015799 | No
27/05/2019 | 21:55 | MTN24 | Rural Short | Asset Failure | HV | 30 | 125.9 | 0.063518 | 0.050445 | No
28/05/2019 | 08:19 | RBD14 | Urban | Asset Failure | LV | 1 | 145 | 0.00022908 | 0.00015799 | No
28/05/2019 | 09:24 | MTN22 | Rural Short | Asset Failure | LV | 1 | 515.2 | 0.0086636 | 0.0016815 | No
28/05/2019 | 10:31 | FSH32 | Rural Short | Overloads |  | 1 | 403.8 | 0.0067893 | 0.0016815 | No
28/05/2019 | 10:54 | CDA22 | Urban | Other | XXX | 1 | 96 | 0.00015159 | 0.00015799 | No
28/05/2019 | 10:58 | KBH31 | Urban | Overloads |  | 1 | 171.8 | 0.00027137 | 0.00015799 | No
28/05/2019 | 12:17 | STO21 | Rural Short | Asset Failure | LV | 1 | 178 | 0.0029931 | 0.0016815 | No
28/05/2019 | 12:24 | CRM35 | Urban | Asset Failure | LV | 1 | 285 | 0.00045027 | 0.00015799 | No
28/05/2019 | 12:59 | BW35 | Urban | Asset Failure | LV | 19 | 60.9 | 0.0018108 | 0.0029718 | No
28/05/2019 | 13:56 | STO23 | Urban | Asset Failure | LV | 6 | 129 | 0.0012779 | 0.0009906 | No
28/05/2019 | 15:49 | BU6 | Urban | Asset Failure | LV | 1 | 111 | 0.00017537 | 0.00015799 | No
28/05/2019 | 16:27 | STO21 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 92.5 | 0.0015557 | 0.0016815 | No
28/05/2019 | 20:07 | EB14 | Urban | Asset Failure | LV | 1 | 82.7 | 0.00013061 | 0.00015799 | No
28/05/2019 | 21:16 | FSH12 | Rural Short | Vegetation | Grow-in - NSP responsibility | 66 | 89 | 0.098771 | 0.11098 | No
28/05/2019 | 21:49 | CRM21 | Urban | Overloads |  | 15 | 86 | 0.0019729 | 0.002294 | No
29/05/2019 | 00:03 | FSH13 | Urban | Asset Failure | LV | 22 | 87 | 0.003039 | 0.0034932 | No
29/05/2019 | 09:34 | CRM14 | Urban | Asset Failure | LV | 1 | 86 | 0.00013587 | 0.00015799 | No
29/05/2019 | 09:56 | MC3 | Urban | Asset Failure | LV | 1 | 184 | 0.0002907 | 0.00015799 | No
29/05/2019 | 12:03 | FTN24 | Urban | Asset Failure | LV | 1 | 110 | 0.00017379 | 0.00015799 | No
29/05/2019 | 12:19 | EW1 | Urban | Asset Failure | LV | 1 | 175 | 0.00027651 | 0.00015799 | No
29/05/2019 | 12:24 | DMA23 | Rural Short | Asset Failure | LV | 1 | 127.7 | 0.0021464 | 0.0016815 | No
29/05/2019 | 12:51 | SVW54 | Urban | Asset Failure | LV | 8 | 84 | 0.001075 | 0.0012797 | No
29/05/2019 | 13:38 | BR6 | Urban | Asset Failure | LV | 1 | 207 | 0.00032704 | 0.00015799 | No
29/05/2019 | 16:00 | OR33 | Urban | Asset Failure | LV | 1 | 375 | 0.00059246 | 0.00015799 | No
29/05/2019 | 17:00 | DMA23 | Rural Short | Asset Failure | LV | 5 | 224.3 | 0.019911 | 0.0088783 | No
29/05/2019 | 17:11 | CFD26 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 255.2 | 0.00040314 | 0.00015799 | No
29/05/2019 | 17:36 | CFD26 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 230.3 | 0.00036377 | 0.00015799 | No
29/05/2019 | 17:56 | SR15 | Urban | Other | XXX | 132 | 243.1 | 0.050705 | 0.020855 | No
29/05/2019 | 18:00 | SVW53 | Urban | Asset Failure | LV | 1 | 152 | 0.00024015 | 0.00015799 | No
29/05/2019 | 19:48 | FTN12 | Urban | Unknown | Unknown | 181 | 146 | 0.04175 | 0.028596 | No
29/05/2019 | 20:10 | MTN34 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 118 | 0.00018648 | 0.00015799 | No
29/05/2019 | 23:07 | RWT34 | Urban | Asset Failure | LV | 1 | 43 | 6.7936e-05 | 0.00015799 | No
30/05/2019 | 06:17 | FSH31 | Urban | Asset Failure | LV | 1 | 82.8 | 0.00013084 | 0.00015799 | No
30/05/2019 | 06:37 | DN11 | Urban | Asset Failure | LV | 1 | 82.4 | 0.00013018 | 0.00015799 | No
30/05/2019 | 07:00 | BW32 | Urban | Asset Failure | LV | 1 | 58 | 9.1634e-05 | 0.00015799 | No
30/05/2019 | 07:33 | FTN12 | Urban | Asset Failure | LV | 1 | 102 | 0.00016115 | 0.00015799 | No
30/05/2019 | 08:16 | LD1 | Urban | Asset Failure | LV | 1 | 143.8 | 0.00022722 | 0.00015799 | No
30/05/2019 | 08:24 | CM13 | Urban | Asset Failure | LV | 1 | 456.1 | 0.00072064 | 0.00015799 | No
30/05/2019 | 08:34 | DC10 | Urban | Vegetation | Grow-in - NSP responsibility | 20 | 156 | 0.0048652 | 0.0031187 | No
30/05/2019 | 09:02 | BH22 | Urban | Overloads |  | 1 | 193 | 0.00030492 | 0.00015799 | No
30/05/2019 | 09:28 | DN24 | Urban | Unknown | Unknown | 1 | 601.2 | 0.00094984 | 0.00015799 | No
30/05/2019 | 09:46 | CDA23 | Urban | Asset Failure | LV | 1 | 449 | 0.00070937 | 0.00015799 | No
30/05/2019 | 09:55 | NW33 | Urban | Unknown | Unknown | 1 | 125 | 0.00019749 | 0.00015799 | No
30/05/2019 | 10:32 | DVY32 | Urban | Asset Failure | Distribution substation | 1 | 842.5 | 0.001331 | 0.00015799 | No
30/05/2019 | 13:08 | MGE12 | Urban | Asset Failure | LV | 1 | 159.8 | 0.00025249 | 0.00015799 | No
30/05/2019 | 13:27 | RBD21 | Rural Short | Third Party | Vehicle Impact | 13 | 512.8 | 0.1121 | 0.021859 | No
30/05/2019 | 13:51 | NP25 | Urban | Asset Failure | LV | 1 | 43 | 6.7936e-05 | 0.00015799 | No
30/05/2019 | 14:23 | FSH31 | Urban | Unknown | Unknown | 1 | 112 | 0.00017695 | 0.00015799 | No
30/05/2019 | 15:47 | NP36 | Urban | Asset Failure | LV | 1 | 131 | 0.00020697 | 0.00015799 | No
30/05/2019 | 15:54 | DMA14 | Urban | Asset Failure | LV | 1 | 116 | 0.00018327 | 0.00015799 | No
30/05/2019 | 17:43 | CFD26 | Urban | Asset Failure | LV | 1 | 179.2 | 0.00028304 | 0.00015799 | No
30/05/2019 | 17:52 | DC6 | Urban | Asset Failure | LV | 1 | 158 | 0.00024962 | 0.00015799 | No
30/05/2019 | 18:31 | HGS22 | Rural Short | Asset Failure | LV | 1 | 373.8 | 0.0062846 | 0.0016815 | No
30/05/2019 | 19:51 | FSH31 | Urban | Overloads |  | 22 | 124 | 0.0042669 | 0.003441 | No
30/05/2019 | 19:51 | FSH31 | Urban | Overloads |  | 15 | 124 | 0.0029092 | 0.0023461 | No
30/05/2019 | 21:34 | GW8 | Urban | Asset Failure | LV | 1 | 85.3 | 0.00013474 | 0.00015799 | No
31/05/2019 | 07:17 | CFD13 | Urban | Asset Failure | LV | 1 | 161 | 0.00025436 | 0.00015799 | No
31/05/2019 | 07:52 | MTN22 | Rural Short | Asset Failure | LV | 1 | 103 | 0.0017319 | 0.0016815 | No
31/05/2019 | 08:54 | HT1 | Urban | Asset Failure | LV | 1 | 264 | 0.00041709 | 0.00015799 | No
31/05/2019 | 09:01 | EM5 | Urban | Asset Failure | LV | 1 | 179 | 0.0002828 | 0.00015799 | No
31/05/2019 | 09:51 | HGS33 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 118.2 | 0.001987 | 0.0016815 | No
31/05/2019 | 11:07 | SVW54 | Urban | Asset Failure | LV | 1 | 321.2 | 0.00050746 | 0.00015799 | No
31/05/2019 | 15:08 | BT4 | Urban | Asset Failure | LV | 1 | 52 | 8.2155e-05 | 0.00015799 | No
31/05/2019 | 17:41 | STO23 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 123.8 | 0.00019557 | 0.00015799 | No
31/05/2019 | 18:43 | EB22 | Urban | Asset Failure | LV | 1 | 47 | 7.4255e-05 | 0.00015799 | No
31/05/2019 | 19:37 | CFD26 | Urban | Asset Failure | LV | 1 | 56 | 8.8474e-05 | 0.00015799 | No
31/05/2019 | 21:20 | LWN35 | Urban | Asset Failure | LV | 1 | 89.8 | 0.00014193 | 0.00015799 | No
31/05/2019 | 21:26 | LWN35 | Urban | Asset Failure | LV | 1 | 83.5 | 0.00013195 | 0.00015799 | No
31/05/2019 | 22:54 | RBD24 | Urban | Asset Failure | LV | 1 | 75.2 | 0.00011876 | 0.00015799 | No
01/06/2019 | 05:52 | FSH13 | Urban | Animal | Animal impact | 54 | 108 | 0.009214 | 0.0085315 | No
01/06/2019 | 07:57 | SS21 | Urban | Asset Failure | Distribution substation | 7 | 183 | 0.0020239 | 0.0011059 | No
01/06/2019 | 08:18 | DC7 | Urban | Asset Failure | LV | 1 | 72 | 0.00011375 | 0.00015799 | No
01/06/2019 | 09:06 | RBD12 | Rural Short | Third Party | Vehicle Impact | 1,051 | 93.3 | 1.648 | 1.7672 | No
01/06/2019 | 14:00 | DC8 | Urban | Asset Failure | Distribution substation | 20 | 109.1 | 0.0035266 | 0.0032325 | No
01/06/2019 | 14:16 | FSH33 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 153.4 | 0.0002423 | 0.00015799 | No
01/06/2019 | 14:36 | STO14 | Rural Short | Asset Failure | LV | 1 | 219 | 0.0036825 | 0.0016815 | No
01/06/2019 | 17:35 | SS12 | Urban | Asset Failure | LV | 53 | 85 | 0.0070906 | 0.0083419 | No
01/06/2019 | 18:59 | MTN34 | Urban | Overloads |  | 56 | 106 | 0.0094503 | 0.0089154 | No
01/06/2019 | 19:00 | FSH13 | Urban | Overloads |  | 1 | 172.7 | 0.00027285 | 0.00015799 | No
01/06/2019 | 19:32 | K8 | Urban | Overloads |  | 1 | 58 | 9.1634e-05 | 0.00015799 | No
01/06/2019 | 21:44 | CDA11 | Urban | Asset Failure | LV | 1 | 115.4 | 0.00018224 | 0.00015799 | No
01/06/2019 | 22:12 | BT4 | Urban | Overloads |  | 1 | 158 | 0.00024962 | 0.00015799 | No
02/06/2019 | 07:18 | NW32 | Urban | Asset Failure | LV | 1 | 101.5 | 0.00016039 | 0.00015799 | No
02/06/2019 | 09:05 | LWN24 | Urban | Unknown | Unknown | 1 | 119 | 0.00018801 | 0.00015799 | No
02/06/2019 | 09:18 | EW3 | Urban | Third Party | Vehicle Impact | 40 | 117 | 0.0073939 | 0.0063196 | No
02/06/2019 | 16:16 | OR34 | Urban | Asset Failure | LV | 1 | 104 | 0.00016431 | 0.00015799 | No
02/06/2019 | 16:57 | OAK21 | Urban | Asset Failure | LV | 1 | 122.7 | 0.00019383 | 0.00015799 | No
02/06/2019 | 22:18 | RBD24 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 92.7 | 0.00014643 | 0.00015799 | No
03/06/2019 | 07:21 | EW12 | Urban | Asset Failure | LV | 1 | 138.6 | 0.00021892 | 0.00015799 | No
03/06/2019 | 08:01 | DC2 | Urban | Asset Failure | LV | 1 | 134 | 0.00021171 | 0.00015799 | No
03/06/2019 | 08:28 | BT2 | Urban | Asset Failure | LV | 1 | 127 | 0.00020065 | 0.00015799 | No
03/06/2019 | 09:01 | SS21 | Urban | Asset Failure | LV | 7 | 118.6 | 0.0013118 | 0.0011059 | No
03/06/2019 | 10:39 | EL6 | Urban | Planned |  | 1 | 114.3 | 0.00018064 | 0.00015799 | No
03/06/2019 | 11:08 | MC2 | Urban | Asset Failure | LV | 20 | 81.5 | 0.0025904 | 0.0031803 | No
03/06/2019 | 12:00 | CDA11 | Urban | Asset Failure | LV | 1 | 65 | 0.00010269 | 0.00015799 | No
03/06/2019 | 13:50 | EB24 | Urban | Asset Failure | LV | 1 | 77.7 | 0.00012268 | 0.00015799 | No
03/06/2019 | 15:14 | OAK21 | Urban | Asset Failure | LV | 15 | 106 | 0.0024317 | 0.002294 | No
03/06/2019 | 15:29 | NO7 | Urban | Asset Failure | LV | 1 | 135.1 | 0.0002135 | 0.00015799 | No
03/06/2019 | 16:00 | CRM33 | Urban | Asset Failure | LV | 55 | 171.1 | 0.014866 | 0.0086894 | No
03/06/2019 | 16:54 | HGS31 | Rural Short | Asset Failure | LV | 1 | 141 | 0.0023709 | 0.0016815 | No
03/06/2019 | 16:54 | DN11 | Urban | Overloads |  | 1 | 170.4 | 0.00026919 | 0.00015799 | No
03/06/2019 | 17:00 | FSH33 | Urban | Weather |  | 1 | 109 | 0.00017221 | 0.00015799 | No
03/06/2019 | 23:41 | MR13 | Urban | Asset Failure | LV | 1 | 104 | 0.00016431 | 0.00015799 | No
04/06/2019 | 06:58 | CRM14 | Urban | Asset Failure | HV | 2,323 | 62.6 | 0.22961 | 0.36701 | No
04/06/2019 | 08:51 | CFD14 | Urban | Network Business | Networ Error | 17 | 25 | 0.00065171 | 0.0026068 | No
04/06/2019 | 10:25 | MC3 | Urban | Asset Failure | LV | 1 | 144.7 | 0.00022853 | 0.00015799 | No
04/06/2019 | 12:10 | FTN25 | Urban | Asset Failure | LV | 1 | 159.4 | 0.00025176 | 0.00015799 | No
04/06/2019 | 12:21 | EB32 | Urban | Asset Failure | LV | 10 | 114 | 0.0018155 | 0.0015925 | No
04/06/2019 | 12:41 | DMA14 | Urban | Unknown | Unknown | 55 | 100 | 0.0086894 | 0.0086894 | No
04/06/2019 | 14:06 | CDA22 | Urban | Asset Failure | LV | 27 | 94 | 0.0039697 | 0.0042231 | No
04/06/2019 | 16:13 | EB11 | Urban | Asset Failure | LV | 1 | 166.9 | 0.00026361 | 0.00015799 | No
04/06/2019 | 16:15 | DVY24 | Rural Short | Asset Failure | LV | 1 | 239.1 | 0.0040196 | 0.0016815 | No
04/06/2019 | 16:31 | CDA11 | Urban | Asset Failure | LV | 1 | 134 | 0.00021171 | 0.00015799 | No
04/06/2019 | 16:45 | M11 | Urban | Overloads |  | 1 | 55 | 8.6894e-05 | 0.00015799 | No
04/06/2019 | 18:02 | CRM14 | Urban | Asset Failure | LV | 28 | 133 | 0.005894 | 0.0044316 | No
04/06/2019 | 18:02 | CRM14 | Urban | Asset Failure | LV | 26 | 133 | 0.0054087 | 0.0040667 | No
04/06/2019 | 20:15 | FSH31 | Urban | Asset Failure | LV | 1 | 89.6 | 0.00014148 | 0.00015799 | No
04/06/2019 | 21:49 | RBD22 | Urban | Asset Failure | LV | 1 | 113 | 0.00017845 | 0.00015799 | No
05/06/2019 | 08:15 | STO21 | Rural Short | Asset Failure | LV | 1 | 240 | 0.0040356 | 0.0016815 | No
05/06/2019 | 10:46 | SS11 | Urban | Asset Failure | LV | 2 | 133.1 | 0.00042067 | 0.00031598 | No
05/06/2019 | 12:23 | CRM33 | Urban | Asset Failure | LV | 1 | 147 | 0.00023225 | 0.00015799 | No
05/06/2019 | 12:39 | DC6 | Urban | Asset Failure | LV | 1 | 101 | 0.00015957 | 0.00015799 | No
05/06/2019 | 12:56 | CRM12 | Urban | Asset Failure | LV | 1 | 110 | 0.00017379 | 0.00015799 | No
05/06/2019 | 13:09 | EL13 | Urban | Asset Failure | LV | 1 | 140.1 | 0.00022134 | 0.00015799 | No
05/06/2019 | 13:19 | RBD13 | Urban | Asset Failure | LV | 1 | 151 | 0.00023856 | 0.00015799 | No
05/06/2019 | 13:26 | OR35 | Urban | Asset Failure | LV | 1 | 78.2 | 0.00012357 | 0.00015799 | No
05/06/2019 | 13:30 | CRM34 | Urban | Asset Failure | LV | 34 | 15 | 0.00080575 | 0.0053717 | No
05/06/2019 | 14:15 | SVW53 | Urban | Third Party | Vehicle Impact | 28 | 75 | 0.0033178 | 0.0044237 | No
05/06/2019 | 17:08 | M12 | Urban | Asset Failure | LV | 1 | 97 | 0.0001533 | 0.00015799 | No
05/06/2019 | 18:25 | K12 | Urban | Asset Failure | LV | 1 | 86 | 0.00013587 | 0.00015799 | No
05/06/2019 | 18:34 | MGE33 | Urban | Asset Failure | LV | 6 | 86 | 0.00085191 | 0.0009906 | No
06/06/2019 | 07:04 | FSH12 | Rural Short | Asset Failure | LV | 1 | 146 | 0.002455 | 0.0016815 | No
06/06/2019 | 07:34 | STO21 | Rural Short | Asset Failure | HV | 2 | 836 | 0.028114 | 0.003363 | No
06/06/2019 | 16:24 | DMA14 | Urban | Asset Failure | LV | 1 | 231 | 0.00036496 | 0.00015799 | No
06/06/2019 | 16:52 | HGS21 | Rural Short | Asset Failure | HV | 492 | 125.3 | 1.0365 | 0.82729 | No
06/06/2019 | 18:13 | MC1 | Urban | Asset Failure | LV | 29 | 92 | 0.004221 | 0.004588 | No
07/06/2019 | 02:35 | NB23 | Urban | Asset Failure | LV | 1 | 54 | 8.5315e-05 | 0.00015799 | No
07/06/2019 | 07:59 | STO21 | Rural Short | Asset Failure | LV | 2 | 115.6 | 0.003887 | 0.003363 | No
07/06/2019 | 08:30 | CDA24 | Urban | Third Party | Other | 1 | 89 | 0.00014061 | 0.00015799 | No
07/06/2019 | 09:25 | LWN34 | Urban | Asset Failure | LV | 1 | 90 | 0.00014219 | 0.00015799 | No
07/06/2019 | 12:06 | DMA23 | Rural Short | Asset Failure | LV | 1 | 116 | 0.0019505 | 0.0016815 | No
07/06/2019 | 16:11 | MR14 | Urban | Asset Failure | LV | 1 | 109 | 0.00017221 | 0.00015799 | No
07/06/2019 | 17:42 | STO14 | Rural Short | Asset Failure | LV | 1 | 107.8 | 0.0018129 | 0.0016815 | No
07/06/2019 | 18:25 | FSH13 | Urban | Asset Failure | LV | 22 | 80 | 0.0027945 | 0.0034932 | No
07/06/2019 | 22:46 | DMA23 | Rural Short | Unknown | Unknown | 1 | 698.7 | 0.011749 | 0.0016815 | No
07/06/2019 | 23:14 | DMA23 | Rural Short | Asset Failure | LV | 17 | 91 | 0.025248 | 0.027745 | No
08/06/2019 | 00:11 | NP23 | Urban | Overloads |  | 1 | 86 | 0.00013587 | 0.00015799 | No
08/06/2019 | 02:02 | DMA23 | Rural Short | Asset Failure | LV | 1 | 45 | 0.00075667 | 0.0016815 | No
08/06/2019 | 02:02 | EM1 | Urban | Asset Failure | LV | 1 | 58 | 9.1634e-05 | 0.00015799 | No
08/06/2019 | 03:42 | DC3 | Urban | Overloads |  | 1 | 28 | 4.4237e-05 | 0.00015799 | No
08/06/2019 | 07:12 | MC3 | Urban | Third Party | Vehicle Impact | 90 | 290.7 | 0.04134 | 0.014219 | No
08/06/2019 | 08:41 | BW33 | Urban | Asset Failure | LV | 1 | 78.7 | 0.00012426 | 0.00015799 | No
08/06/2019 | 11:42 | DN10 | Urban | Asset Failure | LV | 1 | 166 | 0.00026226 | 0.00015799 | No
08/06/2019 | 15:33 | MC2 | Urban | Asset Failure | LV | 1 | 153.2 | 0.00024196 | 0.00015799 | No
08/06/2019 | 16:33 | SH34 | Urban | Asset Failure | LV | 1 | 172 | 0.00027174 | 0.00015799 | No
08/06/2019 | 16:52 | NW33 | Urban | Asset Failure | LV | 10 | 112.5 | 0.0018393 | 0.0016352 | No
08/06/2019 | 18:05 | MGE23 | Urban | Asset Failure | LV | 1 | 94.2 | 0.00014885 | 0.00015799 | No
08/06/2019 | 18:09 | STO21 | Rural Short | Asset Failure | LV | 1 | 140.9 | 0.0023695 | 0.0016815 | No
09/06/2019 | 11:53 | NP16 | Urban | Asset Failure | LV | 1 | 179.3 | 0.0002833 | 0.00015799 | No
09/06/2019 | 12:17 | STO23 | Urban | Asset Failure | LV | 1 | 164.2 | 0.00025947 | 0.00015799 | No
09/06/2019 | 13:01 | STO13 | Urban | Asset Failure | LV | 1 | 209 | 0.00033017 | 0.00015799 | No
09/06/2019 | 16:03 | BR6 | Urban | Asset Failure | LV | 1 | 155 | 0.00024488 | 0.00015799 | No
09/06/2019 | 22:53 | FTN21 | Urban | Asset Failure | LV | 32 | 351.5 | 0.017772 | 0.0050557 | No
10/06/2019 | 07:15 | HGS23 | Rural Short | Animal | Other | 1 | 45 | 0.00075667 | 0.0016815 | No
10/06/2019 | 09:25 | SVW53 | Urban | Asset Failure | LV | 1 | 110 | 0.00017376 | 0.00015799 | No
10/06/2019 | 10:34 | DMA14 | Urban | Asset Failure | LV | 1 | 100.7 | 0.0001591 | 0.00015799 | No
10/06/2019 | 10:48 | LWN21 | Rural Short | Asset Failure | LV | 1 | 387 | 0.0065065 | 0.0016815 | No
10/06/2019 | 20:24 | BH21 | Urban | Asset Failure | LV | 1 | 149 | 0.00023541 | 0.00015799 | No
11/06/2019 | 08:46 | SS12 | Urban | Asset Failure | LV | 1 | 131.1 | 0.00020718 | 0.00015799 | No
11/06/2019 | 09:19 | BH22 | Urban | Unknown | Unknown | 1 | 55.1 | 8.7026e-05 | 0.00015799 | No
11/06/2019 | 09:38 | MTN32 | Rural Short | Asset Failure | LV | 1 | 307 | 0.0051622 | 0.0016815 | No
11/06/2019 | 09:44 | LD7 | Urban | Asset Failure | LV | 1 | 121 | 0.00019117 | 0.00015799 | No
11/06/2019 | 09:53 | STO21 | Rural Short | Asset Failure | LV | 1 | 321.3 | 0.0054029 | 0.0016815 | No
11/06/2019 | 11:13 | RBD13 | Urban | Third Party | Vehicle Impact | 31 | 115 | 0.005576 | 0.0048487 | No
11/06/2019 | 18:07 | DSH23 | Urban | Asset Failure | LV | 1 | 67.8 | 0.00010714 | 0.00015799 | No
11/06/2019 | 18:14 | SV34 | Urban | Unknown | Unknown | 1 | 203.6 | 0.00032169 | 0.00015799 | No
11/06/2019 | 18:33 | EM2 | Urban | Asset Failure | LV | 1 | 154 | 0.0002433 | 0.00015799 | No
12/06/2019 | 08:56 | RWT24 | Urban | Asset Failure | LV | 1 | 138.5 | 0.00021876 | 0.00015799 | No
12/06/2019 | 11:49 | CDA11 | Urban | Asset Failure | LV | 1 | 110.3 | 0.00017432 | 0.00015799 | No
12/06/2019 | 12:31 | NP25 | Urban | Asset Failure | LV | 1 | 59 | 9.3214e-05 | 0.00015799 | No
12/06/2019 | 13:16 | MTN23 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 108.6 | 0.00017158 | 0.00015799 | No
12/06/2019 | 13:22 | OE10 | Urban | Asset Failure | HV | 286 | 70.6 | 0.031895 | 0.045185 | No
12/06/2019 | 16:16 | NP25 | Urban | Asset Failure | LV | 1 | 103.4 | 0.00016341 | 0.00015799 | No
12/06/2019 | 18:07 | HGS23 | Rural Short | Asset Failure | HV | 8 | 488 | 0.065645 | 0.013452 | No
12/06/2019 | 18:38 | OR33 | Urban | Third Party | Other | 1 | 132 | 0.00020855 | 0.00015799 | No
12/06/2019 | 20:33 | RWT24 | Urban | Asset Failure | LV | 1 | 146.1 | 0.00023082 | 0.00015799 | No
12/06/2019 | 20:52 | MTN22 | Rural Short | Asset Failure | LV | 1 | 102.9 | 0.00173 | 0.0016815 | No
12/06/2019 | 21:22 | DMA15 | Rural Short | Animal | Other | 94 | 80.6 | 0.12738 | 0.15806 | No
12/06/2019 | 22:19 | HT2 | Urban | Asset Failure | LV | 1 | 756.6 | 0.0011954 | 0.00015799 | No
12/06/2019 | 23:55 | RBD12 | Rural Short | Asset Failure | LV | 50 | 127.9 | 0.10785 | 0.084344 | No
13/06/2019 | 04:51 | MTN35 | Rural Short | Animal | Animal nesting/burrowing, etc and other | 3 | 188.6 | 0.0095156 | 0.0050445 | No
13/06/2019 | 08:01 | RWT23 | Urban | Third Party | Other | 1 | 104 | 0.00016431 | 0.00015799 | No
13/06/2019 | 08:01 | BH22 | Urban | Asset Failure | LV | 2 | 173 | 0.0005467 | 0.00031598 | No
13/06/2019 | 08:19 | MGE22 | Urban | Asset Failure | LV | 2 | 201 | 0.00052397 | 0.00026068 | No
14/06/2019 | 05:17 | CDA23 | Urban | Asset Failure | LV | 1 | 103 | 0.00016273 | 0.00015799 | No
14/06/2019 | 05:47 | LWN23 | Urban | Asset Failure | LV | 1 | 133 | 0.00021013 | 0.00015799 | No
14/06/2019 | 10:54 | STO23 | Urban | Asset Failure | LV | 96 | 116 | 0.017594 | 0.015167 | No
14/06/2019 | 12:04 | DN22 | Urban | Overloads |  | 10 | 246 | 0.0037194 | 0.001512 | No
14/06/2019 | 13:20 | EL5 | Urban | Asset Failure | LV | 19 | 477.5 | 0.014687 | 0.0030761 | No
14/06/2019 | 15:24 | CDA24 | Urban | Overloads |  | 1 | 157 | 0.00024804 | 0.00015799 | No
14/06/2019 | 16:10 | MGE21 | Urban | Unknown | Unknown | 11 | 1,190.0 | 0.021207 | 0.0017821 | No
14/06/2019 | 17:05 | RBD14 | Urban | Asset Failure | LV | 1 | 175 | 0.00027648 | 0.00015799 | No
14/06/2019 | 18:59 | GW3 | Urban | Asset Failure | LV | 1 | 178 | 0.00028122 | 0.00015799 | No
14/06/2019 | 19:09 | DMA24 | Rural Short | Overloads |  | 8 | 96 | 0.012785 | 0.013317 | No
14/06/2019 | 19:47 | DN10 | Urban | Asset Failure | LV | 1 | 279 | 0.00044079 | 0.00015799 | No
14/06/2019 | 23:08 | MR15 | Urban | Asset Failure | LV | 1 | 97 | 0.00015325 | 0.00015799 | No
14/06/2019 | 23:18 | DMA24 | Rural Short | Unknown | Unknown | 8 | 72 | 0.0095885 | 0.013317 | No
15/06/2019 | 09:08 | STO14 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 231.3 | 0.003889 | 0.0016815 | No
15/06/2019 | 09:10 | DMA24 | Rural Short | Asset Failure | LV | 1 | 469.2 | 0.0078896 | 0.0016815 | No
15/06/2019 | 12:11 | MR15 | Urban | Asset Failure | LV | 1 | 219 | 0.00034602 | 0.00015799 | No
15/06/2019 | 14:49 | NB36 | Urban | Asset Failure | LV | 1 | 84.2 | 0.00013305 | 0.00015799 | No
15/06/2019 | 17:19 | HGS31 | Rural Short | Asset Failure | LV | 23 | 96 | 0.036756 | 0.038288 | No
15/06/2019 | 17:53 | CRM14 | Urban | Asset Failure | LV | 1 | 152 | 0.00024015 | 0.00015799 | No
15/06/2019 | 18:31 | HGS23 | Rural Short | Asset Failure | LV | 2 | 253.1 | 0.0099594 | 0.0039347 | No
15/06/2019 | 18:37 | DMA23 | Rural Short | Unknown | Unknown | 2 | 148 | 0.0049772 | 0.003363 | No
15/06/2019 | 18:37 | MGE21 | Urban | Unknown | Unknown | 15 | 173 | 0.0039686 | 0.002294 | No
15/06/2019 | 18:57 | DN11 | Urban | Asset Failure | LV | 33 | 63 | 0.0033175 | 0.0052658 | No
16/06/2019 | 14:32 | CDA23 | Urban | Asset Failure | LV | 16 | 193 | 0.0049306 | 0.0025547 | No
16/06/2019 | 15:27 | MR24 | Urban | Third Party | Other | 1 | 77.8 | 0.00012289 | 0.00015799 | No
16/06/2019 | 15:28 | MR24 | Urban | Third Party | Other | 1 | 76.7 | 0.00012121 | 0.00015799 | No
16/06/2019 | 15:36 | CRM12 | Urban | Unknown | Unknown | 1 | 218.2 | 0.00034473 | 0.00015799 | No
16/06/2019 | 16:03 | CRM12 | Urban | Asset Failure | LV | 1 | 200 | 0.00031598 | 0.00015799 | No
16/06/2019 | 18:57 | EM1 | Urban | Asset Failure | LV | 4 | 112.5 | 0.00066632 | 0.00059246 | No
17/06/2019 | 07:54 | SVW53 | Urban | Unknown | Unknown | 24 | 96 | 0.0036401 | 0.0037918 | No
17/06/2019 | 07:54 | SVW53 | Urban | Unknown | Unknown | 1 | 96 | 0.00020021 | 0.00020855 | No
17/06/2019 | 08:33 | SVW53 | Urban | Unknown | Unknown | 2 | 56.5 | 0.00020531 | 0.00036338 | No
17/06/2019 | 09:23 | OE10 | Urban | Other | XXX | 1 | 397 | 0.00062717 | 0.00015799 | No
17/06/2019 | 09:29 | RBD14 | Urban | Asset Failure | LV | 1 | 190.3 | 0.0003006 | 0.00015799 | No
17/06/2019 | 09:53 | FSH31 | Urban | Asset Failure | LV | 2 | 178 | 0.00056244 | 0.00031598 | No
17/06/2019 | 09:57 | HGS23 | Rural Short | Asset Failure | LV | 1 | 326.3 | 0.0054867 | 0.0016815 | No
17/06/2019 | 11:55 | EM10 | Urban | Overloads |  | 1 | 155 | 0.00024488 | 0.00015799 | No
17/06/2019 | 12:54 | NW31 | Urban | Asset Failure | LV | 1 | 160.7 | 0.00025386 | 0.00015799 | No
17/06/2019 | 14:16 | GW6 | Urban | Overloads |  | 1 | 283.2 | 0.00044743 | 0.00015799 | No
17/06/2019 | 15:08 | CRM13 | Urban | Unknown | Unknown | 26 | 352 | 0.014682 | 0.0041709 | No
17/06/2019 | 15:25 | FTN21 | Urban | Asset Failure | LV | 1 | 634.1 | 0.0010018 | 0.00015799 | No
17/06/2019 | 16:59 | CRM33 | Urban | Unknown | Unknown | 24 | 120.6 | 0.0045265 | 0.0037538 | No
17/06/2019 | 21:56 | FSH22 | Urban | Asset Failure | LV | 1 | 94 | 0.00014851 | 0.00015799 | No
18/06/2019 | 00:13 | SVW53 | Urban | Asset Failure | LV | 4 | 57 | 0.00037823 | 0.00066356 | No
18/06/2019 | 13:23 | GW3 | Urban | Network Business | Networ Error | 2 | 7 | 2.2119e-05 | 0.00031598 | No
18/06/2019 | 14:18 | MR31 | Urban | Third Party | Vehicle Impact | 70 | 282 | 0.031187 | 0.011059 | No
18/06/2019 | 18:31 | CDA23 | Urban | Asset Failure | LV | 1 | 355.7 | 0.00056202 | 0.00015799 | No
18/06/2019 | 20:04 | MGE33 | Urban | Asset Failure | LV | 26 | 26 | 0.001068 | 0.0041077 | No
18/06/2019 | 21:09 | FSH12 | Rural Short | Asset Failure | LV | 1 | 70.3 | 0.0011824 | 0.0016815 | No
19/06/2019 | 02:28 | DC2 | Urban | Asset Failure | LV | 18 | 42 | 0.0011944 | 0.0028438 | No
19/06/2019 | 06:44 | MR32 | Urban | Asset Failure | LV | 1 | 119.2 | 0.0001883 | 0.00015799 | No
19/06/2019 | 08:09 | LWN24 | Urban | Third Party | Vehicle Impact | 66 | 496 | 0.05172 | 0.010427 | No
19/06/2019 | 08:51 | RBD21 | Rural Short | Asset Failure | LV | 1 | 550.9 | 0.0092639 | 0.0016815 | No
19/06/2019 | 11:34 | CRM33 | Urban | Third Party | Other | 1 | 129.9 | 0.00020528 | 0.00015799 | No
19/06/2019 | 11:49 | AR6 | Urban | Asset Failure | Distribution substation | 32 | 231 | 0.011679 | 0.0050557 | No
19/06/2019 | 11:49 | AR6 | Urban | Asset Failure | LV | 94 | 231 | 0.034306 | 0.014851 | No
19/06/2019 | 12:50 | STO23 | Urban | Asset Failure | LV | 1 | 399.4 | 0.00063096 | 0.00015799 | No
19/06/2019 | 13:46 | NB25 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 182.6 | 0.00028844 | 0.00015799 | No
19/06/2019 | 16:53 | NB33 | Urban | Asset Failure | LV | 1 | 36.5 | 5.7693e-05 | 0.00015799 | No
19/06/2019 | 18:00 | NO7 | Urban | Asset Failure | LV | 1 | 79.1 | 0.00012489 | 0.00015799 | No
19/06/2019 | 19:11 | SVW53 | Urban | Overloads |  | 1 | 54 | 8.5315e-05 | 0.00015799 | No
19/06/2019 | 22:20 | NO6 | Urban | Overloads |  | 1 | 150 | 0.00023698 | 0.00015799 | No
20/06/2019 | 08:32 | DMA12 | Urban | Asset Failure | LV | 1 | 168 | 0.00026542 | 0.00015799 | No
20/06/2019 | 08:39 | BH11 | Urban | Asset Failure | LV | 1 | 141 | 0.00022277 | 0.00015799 | No
20/06/2019 | 08:53 | BW32 | Urban | Asset Failure | LV | 1 | 56.1 | 8.8685e-05 | 0.00015799 | No
20/06/2019 | 09:08 | FSH21 | Rural Short | Asset Failure | LV | 1 | 231.3 | 0.0038896 | 0.0016815 | No
20/06/2019 | 10:28 | RBD24 | Urban | Asset Failure | LV | 1 | 107 | 0.00016905 | 0.00015799 | No
20/06/2019 | 14:23 | LD4 | Urban | Asset Failure | LV | 1 | 81.6 | 0.00012897 | 0.00015799 | No
20/06/2019 | 14:39 | BH23 | Urban | Asset Failure | LV | 1 | 141 | 0.00022277 | 0.00015799 | No
20/06/2019 | 15:30 | DC2 | Urban | Asset Failure | LV | 1 | 179.6 | 0.00028372 | 0.00015799 | No
20/06/2019 | 16:18 | FTN14 | Urban | Third Party | Other | 1 | 161 | 0.00025436 | 0.00015799 | No
20/06/2019 | 17:53 | LWN21 | Rural Short | Asset Failure | HV | 80 | 310.4 | 0.41755 | 0.13452 | No
20/06/2019 | 19:27 | MC2 | Urban | Asset Failure | LV | 26 | 88 | 0.0035787 | 0.0040667 | No
20/06/2019 | 20:50 | DMA15 | Rural Short | Animal | Animal impact | 1 | 380 | 0.0063897 | 0.0016815 | No
20/06/2019 | 22:05 | EL6 | Urban | Asset Failure | LV | 1 | 145 | 0.00022908 | 0.00015799 | No
21/06/2019 | 05:21 | BU14 | Urban | Overloads |  | 9 | 114 | 0.0015453 | 0.0013556 | No
21/06/2019 | 08:18 | CRM34 | Urban | Asset Failure | LV | 1 | 207 | 0.00032704 | 0.00015799 | No
21/06/2019 | 11:38 | FSH22 | Urban | Unknown | Unknown | 1 | 211.6 | 0.00033431 | 0.00015799 | No
21/06/2019 | 15:58 | NP23 | Urban | Asset Failure | LV | 6 | 77 | 0.00076276 | 0.0009906 | No
21/06/2019 | 15:59 | FSH21 | Rural Short | Third Party | Vehicle Impact | 476 | 53.6 | 0.42939 | 0.80039 | No
21/06/2019 | 16:21 | FSH12 | Rural Short | Unknown | Unknown | 1 | 50 | 0.00084046 | 0.0016815 | No
21/06/2019 | 17:45 | WD14 | Urban | Asset Failure | LV | 1 | 164 | 0.00025913 | 0.00015799 | No
21/06/2019 | 17:49 | NB35 | Urban | Asset Failure | LV | 1 | 100 | 0.00015799 | 0.00015799 | No
21/06/2019 | 18:08 | FSH21 | Rural Short | Unknown | Unknown | 3 | 251.2 | 0.012671 | 0.0050445 | No
21/06/2019 | 18:18 | BW35 | Urban | Overloads |  | 26 | 92 | 0.0038373 | 0.0041709 | No
21/06/2019 | 18:27 | DMA23 | Rural Short | Third Party | Vehicle Impact | 1 | 153.3 | 0.0025772 | 0.0016815 | No
21/06/2019 | 20:15 | EW14 | Urban | Asset Failure | LV | 1 | 100.6 | 0.00015894 | 0.00015799 | No
21/06/2019 | 20:52 | NB35 | Urban | Asset Failure | Distribution substation | 2 | 97.4 | 0.00035375 | 0.00036338 | No
22/06/2019 | 00:25 | DC2 | Urban | Asset Failure | LV | 35 | 55 | 0.0030396 | 0.0055265 | No
22/06/2019 | 10:29 | MTN24 | Rural Short | Asset Failure | LV | 1 | 130.9 | 0.0022011 | 0.0016815 | No
22/06/2019 | 14:13 | FTN14 | Urban | Asset Failure | LV | 4 | 56.7 | 0.00035821 | 0.00063196 | No
22/06/2019 | 14:13 | FTN14 | Urban | Asset Failure | LV | 9 | 56.7 | 0.00080598 | 0.0014219 | No
22/06/2019 | 15:26 | M32 | Urban | Asset Failure | LV | 1 | 101 | 0.00015957 | 0.00015799 | No
22/06/2019 | 17:58 | GW2 | Urban | Asset Failure | LV | 1 | 49 | 7.7415e-05 | 0.00015799 | No
22/06/2019 | 18:05 | MR22 | Urban | Asset Failure | HV | 654 | 41.6 | 0.042969 | 0.10333 | No
22/06/2019 | 18:05 | MR14 | Urban | Asset Failure | HV | 1,735 | 41.7 | 0.11428 | 0.27411 | No
22/06/2019 | 18:48 | DN6 | Urban | Asset Failure | LV | 1 | 162 | 0.00025594 | 0.00015799 | No
22/06/2019 | 19:06 | CRM22 | Urban | Asset Failure | LV | 1 | 164 | 0.0002591 | 0.00015799 | No
22/06/2019 | 19:53 | EB12 | Urban | Asset Failure | LV | 1 | 76.5 | 0.00012078 | 0.00015799 | No
22/06/2019 | 20:04 | RBD14 | Urban | Asset Failure | LV | 1 | 101 | 0.00015957 | 0.00015799 | No
22/06/2019 | 21:43 | DC2 | Urban | Asset Failure | LV | 53 | 796.3 | 0.066676 | 0.0083735 | No
23/06/2019 | 07:25 | DMA23 | Rural Short | Asset Failure | LV | 1 | 155 | 0.0026063 | 0.0016815 | No
23/06/2019 | 07:37 | DVY31 | Urban | Network Business | Networ Error | 6 | 6 | 5.6876e-05 | 0.00094794 | No
23/06/2019 | 08:15 | EL10 | Urban | Asset Failure | LV | 1 | 150 | 0.00023698 | 0.00015799 | No
23/06/2019 | 11:04 | CDA11 | Urban | Asset Failure | LV | 1 | 191 | 0.00030176 | 0.00015799 | No
23/06/2019 | 11:09 | FSH31 | Urban | Asset Failure | LV | 5 | 170.1 | 0.0013924 | 0.00081839 | No
23/06/2019 | 11:37 | FTN21 | Urban | Planned |  | 17 | 40 | 0.0010743 | 0.0026858 | No
23/06/2019 | 12:08 | EB23 | Urban | Asset Failure | LV | 1 | 64 | 0.00010111 | 0.00015799 | No
23/06/2019 | 12:30 | OE4 | Urban | Asset Failure | LV | 1 | 143 | 0.00022593 | 0.00015799 | No
23/06/2019 | 12:49 | RWT24 | Urban | Unknown | Unknown | 1 | 72 | 0.00011375 | 0.00015799 | No
23/06/2019 | 14:16 | CRM35 | Urban | Asset Failure | LV | 1 | 119 | 0.00018801 | 0.00015799 | No
23/06/2019 | 15:08 | CRM12 | Urban | Asset Failure | LV | 1 | 127 | 0.00020065 | 0.00015799 | No
23/06/2019 | 18:11 | CRM12 | Urban | Asset Failure | LV | 1 | 178.4 | 0.0002818 | 0.00015799 | No
23/06/2019 | 18:25 | CRM12 | Urban | Asset Failure | LV | 1 | 164.3 | 0.00025955 | 0.00015799 | No
23/06/2019 | 19:00 | CRM12 | Urban | Asset Failure | LV | 1 | 90 | 0.00014219 | 0.00015799 | No
23/06/2019 | 19:06 | BW35 | Urban | Asset Failure | LV | 1 | 54 | 8.5315e-05 | 0.00015799 | No
23/06/2019 | 19:38 | EL7 | Urban | Asset Failure | LV | 1 | 242 | 0.00038233 | 0.00015799 | No
23/06/2019 | 19:40 | SV32 | Urban | Overloads |  | 13 | 65 | 0.0013556 | 0.0020855 | No
23/06/2019 | 20:25 | NW14 | Urban | Asset Failure | LV | 1 | 34.2 | 5.398e-05 | 0.00015799 | No
23/06/2019 | 23:38 | FTN25 | Urban | Asset Failure | LV | 1 | 92 | 0.00014535 | 0.00015799 | No
24/06/2019 | 00:35 | DC5 | Urban | Asset Failure | LV | 1 | 130 | 0.00020539 | 0.00015799 | No
24/06/2019 | 05:11 | MTN22 | Rural Short | Asset Failure | LV | 4 | 153.5 | 0.010327 | 0.006726 | No
24/06/2019 | 08:13 | MR32 | Urban | Asset Failure | LV | 25 | 112 | 0.0043795 | 0.0039102 | No
24/06/2019 | 08:30 | MR22 | Urban | Asset Failure | LV | 1 | 155 | 0.00024488 | 0.00015799 | No
24/06/2019 | 09:10 | BT9 | Urban | Asset Failure | LV | 1 | 141.4 | 0.00022345 | 0.00015799 | No
24/06/2019 | 09:12 | RBD22 | Urban | Asset Failure | LV | 7 | 92.8 | 0.0010159 | 0.0010949 | No
24/06/2019 | 09:28 | HGS31 | Rural Short | Asset Failure | LV | 1 | 882 | 0.014831 | 0.0016815 | No
24/06/2019 | 09:34 | MTN22 | Rural Short | Overloads |  | 1 | 118 | 0.0019844 | 0.0016815 | No
24/06/2019 | 09:59 | MR24 | Urban | Overloads |  | 1 | 141 | 0.00022277 | 0.00015799 | No
24/06/2019 | 10:21 | FSH31 | Urban | Overloads |  | 7 | 243.8 | 0.0026687 | 0.0010949 | No
24/06/2019 | 10:28 | NO6 | Urban | Overloads |  | 1 | 242 | 0.00038233 | 0.00015799 | No
24/06/2019 | 11:03 | KBH33 | Urban | Asset Failure | LV | 1 | 744.6 | 0.0011764 | 0.00015799 | No
24/06/2019 | 11:22 | K8 | Urban | Asset Failure | LV | 1 | 62 | 9.7954e-05 | 0.00015799 | No
24/06/2019 | 11:34 | MR15 | Urban | Overloads |  | 1 | 141 | 0.00022277 | 0.00015799 | No
24/06/2019 | 12:15 | DN9 | Urban | Overloads |  | 5 | 114.5 | 0.00090462 | 0.00078995 | No
24/06/2019 | 12:50 | EM5 | Urban | Unknown | Unknown | 16 | 55 | 0.0013477 | 0.0024504 | No
24/06/2019 | 12:59 | SVW54 | Urban | Asset Failure | LV | 1 | 226 | 0.00035703 | 0.00015799 | No
24/06/2019 | 15:25 | KBH32 | Urban | Asset Failure | LV | 1 | 305 | 0.00048187 | 0.00015799 | No
24/06/2019 | 17:00 | RWT35 | Urban | Asset Failure | LV | 62 | 135 | 0.013224 | 0.0097954 | No
24/06/2019 | 17:46 | NW21 | Urban | Asset Failure | LV | 1 | 118.9 | 0.0001878 | 0.00015799 | No
24/06/2019 | 18:53 | SS13 | Urban | Asset Failure | LV | 2 | 171.9 | 0.00054312 | 0.00031598 | No
24/06/2019 | 19:01 | BH31 | Urban | Asset Failure | LV | 1 | 109 | 0.00017221 | 0.00015799 | No
24/06/2019 | 19:03 | DN21 | Urban | Asset Failure | LV | 14 | 72 | 0.0015391 | 0.0021376 | No
24/06/2019 | 19:51 | EM3 | Urban | Overloads |  | 1 | 99 | 0.00015641 | 0.00015799 | No
24/06/2019 | 20:46 | RWT24 | Urban | Asset Failure | LV | 1 | 72 | 0.00011375 | 0.00015799 | No
24/06/2019 | 21:08 | KBH34 | Urban | Asset Failure | LV | 32 | 662 | 0.033469 | 0.0050557 | No
25/06/2019 | 08:37 | FSH23 | Rural Short | Asset Failure | Distribution substation | 33 | 83 | 0.046056 | 0.055489 | No
25/06/2019 | 09:07 | FSH31 | Urban | Overloads |  | 7 | 98 | 0.0010219 | 0.0010427 | No
25/06/2019 | 09:36 | SR14 | Urban | Planned |  | 1 | 83.5 | 0.00013184 | 0.00015799 | No
25/06/2019 | 09:56 | DN9 | Urban | Overloads |  | 2 | 153.7 | 0.00036428 | 0.00023698 | No
25/06/2019 | 10:34 | MTN32 | Rural Short | Asset Failure | LV | 1 | 206 | 0.0034639 | 0.0016815 | No
25/06/2019 | 10:58 | BH31 | Urban | Unknown | Unknown | 1 | 77 | 0.00012165 | 0.00015799 | No
25/06/2019 | 14:33 | MTN22 | Rural Short | Overloads |  | 1 | 117 | 0.0019673 | 0.0016815 | No
25/06/2019 | 14:45 | BR15 | Urban | Asset Failure | LV | 1 | 162 | 0.00025594 | 0.00015799 | No
25/06/2019 | 15:32 | KBH32 | Urban | Overloads |  | 1 | 187.9 | 0.00029681 | 0.00015799 | No
25/06/2019 | 18:15 | EM1 | Urban | Asset Failure | LV | 1 | 84.2 | 0.00013305 | 0.00015799 | No
25/06/2019 | 18:50 | BC22 | Urban | Asset Failure | LV | 1 | 100 | 0.00015799 | 0.00015799 | No
25/06/2019 | 19:58 | LD2 | Urban | Asset Failure | LV | 21 | 12 | 0.00039415 | 0.0032846 | No
25/06/2019 | 20:33 | BH23 | Urban | Overloads |  | 56 | 87 | 0.0077564 | 0.0089154 | No
26/06/2019 | 00:02 | BW35 | Urban | Asset Failure | LV | 1 | 43 | 6.7936e-05 | 0.00015799 | No
26/06/2019 | 07:51 | LWN34 | Urban | Asset Failure | LV | 1 | 54 | 8.5315e-05 | 0.00015799 | No
26/06/2019 | 08:09 | HGS23 | Rural Short | Asset Failure | LV | 1 | 336 | 0.0056498 | 0.0016815 | No
26/06/2019 | 08:31 | SV16 | Urban | Asset Failure | LV | 1 | 145 | 0.00022908 | 0.00015799 | No
26/06/2019 | 09:07 | MTN23 | Urban | Overloads |  | 3 | 83 | 0.00034619 | 0.00041709 | No
26/06/2019 | 09:42 | GW8 | Urban | Asset Failure | LV | 1 | 92.1 | 0.00014543 | 0.00015799 | No
26/06/2019 | 10:45 | MC5 | Urban | Asset Failure | LV | 5 | 105 | 0.00082945 | 0.00078995 | No
26/06/2019 | 16:50 | MTN23 | Urban | Unknown | Unknown | 8 | 60 | 0.00071095 | 0.0011849 | No
27/06/2019 | 01:56 | MTN31 | Urban | Asset Failure | LV | 1 | 64 | 0.00010111 | 0.00015799 | No
27/06/2019 | 08:11 | HT9 | Urban | Asset Failure | LV | 1 | 199 | 0.00031432 | 0.00015799 | No
27/06/2019 | 08:32 | HGS22 | Rural Short | Asset Failure | LV | 1 | 718.3 | 0.012078 | 0.0016815 | No
27/06/2019 | 09:02 | EM10 | Urban | Asset Failure | LV | 1 | 162 | 0.00025594 | 0.00015799 | No
27/06/2019 | 09:22 | NB32 | Urban | Asset Failure | LV | 3 | 158 | 0.00084872 | 0.00053717 | No
27/06/2019 | 09:57 | LWN35 | Urban | Unknown | Unknown | 1 | 257.5 | 0.00040685 | 0.00015799 | No
27/06/2019 | 10:57 | EL5 | Urban | Overloads |  | 39 | 225.5 | 0.01387 | 0.0061521 | No
27/06/2019 | 11:11 | HGS23 | Rural Short | Asset Failure | LV | 1 | 79 | 0.0013284 | 0.0016815 | No
27/06/2019 | 12:36 | BC11 | Urban | Unknown | Unknown | 1 | 676.7 | 0.001069 | 0.00015799 | No
27/06/2019 | 12:42 | DC3 | Urban | Vegetation | Grow-in - NSP responsibility | 1,554 | 19.7 | 0.048253 | 0.24552 | No
27/06/2019 | 14:11 | MGE21 | Urban | Unknown | Unknown | 1 | 428.9 | 0.00067754 | 0.00015799 | No
27/06/2019 | 15:20 | LD5 | Urban | Unknown | Unknown | 1 | 93 | 0.00015428 | 0.00016589 | No
27/06/2019 | 17:51 | MGE34 | Urban | Asset Failure | Distribution substation | 69 | 482.6 | 0.05233 | 0.010844 | No
27/06/2019 | 18:19 | BH31 | Urban | Asset Failure | LV | 1 | 143.7 | 0.00022706 | 0.00015799 | No
27/06/2019 | 19:42 | STO21 | Rural Short | Asset Failure | LV | 1 | 173 | 0.002909 | 0.0016815 | No
27/06/2019 | 20:18 | BU13 | Urban | Asset Failure | LV | 1 | 87 | 0.00013745 | 0.00015799 | No
27/06/2019 | 22:08 | EL7 | Urban | Asset Failure | LV | 1 | 156 | 0.00024646 | 0.00015799 | No
28/06/2019 | 02:39 | MGE21 | Urban | Asset Failure | LV | 8 | 611 | 0.0074136 | 0.0012134 | No
28/06/2019 | 03:10 | LWN21 | Rural Short | Overloads |  | 4 | 253 | 0.017013 | 0.006726 | No
28/06/2019 | 09:42 | RWT35 | Urban | Asset Failure | LV | 1 | 72.8 | 0.00011502 | 0.00015799 | No
28/06/2019 | 11:36 | BT2 | Urban | Asset Failure | LV | 1 | 170 | 0.00026858 | 0.00015799 | No
28/06/2019 | 11:53 | MC2 | Urban | Asset Failure | LV | 1 | 292 | 0.00046133 | 0.00015799 | No
28/06/2019 | 12:12 | STO23 | Urban | Asset Failure | LV | 1 | 137.1 | 0.0002166 | 0.00015799 | No
28/06/2019 | 12:54 | FSH33 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 97.1 | 0.00015341 | 0.00015799 | No
28/06/2019 | 12:59 | HGS23 | Rural Short | Overloads |  | 1 | 185.6 | 0.0031206 | 0.0016815 | No
28/06/2019 | 13:07 | STO21 | Rural Short | Asset Failure | LV | 1 | 283 | 0.0047586 | 0.0016815 | No
28/06/2019 | 13:32 | SS11 | Urban | Asset Failure | LV | 1 | 98 | 0.00015483 | 0.00015799 | No
28/06/2019 | 14:43 | NW13 | Urban | Asset Failure | LV | 1 | 136.1 | 0.000215 | 0.00015799 | No
28/06/2019 | 16:53 | FSH31 | Urban | Asset Failure | LV | 1 | 82 | 0.00012955 | 0.00015799 | No
28/06/2019 | 17:51 | RWT35 | Urban | Asset Failure | LV | 1 | 218 | 0.00034444 | 0.00015799 | No
28/06/2019 | 21:44 | FTN14 | Urban | Asset Failure | LV | 1 | 85.4 | 0.0001349 | 0.00015799 | No
29/06/2019 | 08:06 | DMA21 | Urban | Overloads |  | 1 | 78.7 | 0.00012439 | 0.00015799 | No
29/06/2019 | 11:08 | OAK23 | Urban | Asset Failure | LV | 1 | 98 | 0.00015483 | 0.00015799 | No
29/06/2019 | 12:22 | NW13 | Urban | Unknown | Unknown | 13 | 118 | 0.0024236 | 0.0020539 | No
29/06/2019 | 12:23 | FTN13 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 105 | 0.00016589 | 0.00015799 | No
29/06/2019 | 13:18 | EL11 | Urban | Vegetation | Grow-in - Other responsible party | 2 | 161.9 | 0.00059086 | 0.00036496 | No
29/06/2019 | 13:24 | KBH32 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 216 | 0.00034118 | 0.00015799 | No
29/06/2019 | 14:02 | HT8 | Urban | Overloads |  | 1 | 283 | 0.00044711 | 0.00015799 | No
29/06/2019 | 15:14 | NW31 | Urban | Asset Failure | LV | 1 | 54 | 8.5315e-05 | 0.00015799 | No
29/06/2019 | 15:50 | OE5 | Urban | Asset Failure | LV | 1 | 118.4 | 0.00018701 | 0.00015799 | No
29/06/2019 | 16:55 | SVW55 | Urban | Asset Failure | LV | 1 | 95 | 0.00015009 | 0.00015799 | No
29/06/2019 | 17:15 | MTN21 | Urban | Vegetation | Grow-in - NSP responsibility | 2,607 | 41.6 | 0.17145 | 0.41188 | No
29/06/2019 | 17:29 | HGS33 | Rural Short | Vegetation | Grow-in - NSP responsibility | 55 | 118 | 0.10913 | 0.092482 | No
29/06/2019 | 17:39 | HGS33 | Rural Short | Asset Failure | LV | 25 | 141 | 0.059462 | 0.042172 | No
29/06/2019 | 18:09 | BU10 | Urban | Asset Failure | LV | 1 | 205.9 | 0.00032533 | 0.00015799 | No
29/06/2019 | 18:12 | BU10 | Urban | Asset Failure | LV | 1 | 182.7 | 0.00028857 | 0.00015799 | No
29/06/2019 | 18:25 | STO22 | Urban | Asset Failure | LV | 1 | 450 | 0.00071095 | 0.00015799 | No
29/06/2019 | 18:47 | FTN13 | Urban |  | Zone substation | 1,036 | 5.9 | 0.0096025 | 0.16368 | No
29/06/2019 | 18:47 | FTN14 | Urban |  | Zone substation | 2,105 | 5.9 | 0.019511 | 0.33257 | No
29/06/2019 | 18:47 | FTN11 | Urban |  | Zone substation | 2,372 | 5.9 | 0.021986 | 0.37475 | No
29/06/2019 | 18:47 | FTN12 | Urban |  | Zone substation | 2,660 | 5.9 | 0.024655 | 0.42025 | No
29/06/2019 | 18:55 | HGS31 | Rural Short | Asset Failure | HV | 244 | 398.5 | 1.635 | 0.41028 | No
29/06/2019 | 21:46 | MC1 | Urban | Asset Failure | LV | 30 | 104 | 0.0049342 | 0.0047444 | No
29/06/2019 | 22:36 | NP25 | Urban | Asset Failure | LV | 1 | 174.2 | 0.00027514 | 0.00015799 | No
30/06/2019 | 05:48 | FTN13 | Urban | Asset Failure | LV | 1 | 61.1 | 9.6532e-05 | 0.00015799 | No
30/06/2019 | 07:47 | BC22 | Urban | Asset Failure | LV | 1 | 48 | 7.5835e-05 | 0.00015799 | No
30/06/2019 | 10:01 | SV32 | Urban | Asset Failure | LV | 1 | 179 | 0.0002828 | 0.00015799 | No
30/06/2019 | 11:23 | MR31 | Urban | Asset Failure | LV | 1 | 108.3 | 0.00017102 | 0.00015799 | No
30/06/2019 | 11:47 | LD6 | Urban | Asset Failure | LV | 1 | 133 | 0.00021013 | 0.00015799 | No
30/06/2019 | 12:16 | RBD11 | Urban | Asset Failure | LV | 1 | 194 | 0.0003065 | 0.00015799 | No
30/06/2019 | 12:27 | CDA23 | Urban | Asset Failure | LV | 1 | 92.5 | 0.00014611 | 0.00015799 | No
30/06/2019 | 13:30 | MC6 | Urban | Asset Failure | LV | 1 | 120 | 0.00018954 | 0.00015799 | No
30/06/2019 | 14:09 | FSH32 | Rural Short | Overloads |  | 1 | 66 | 0.0011098 | 0.0016815 | No
30/06/2019 | 15:09 | CRM22 | Urban | Asset Failure | LV | 1 | 170.7 | 0.00026969 | 0.00015799 | No
30/06/2019 | 15:53 | OAK32 | Urban | Asset Failure | LV | 23 | 97 | 0.0035907 | 0.0037017 | No
30/06/2019 | 16:49 | MGE24 | Urban | Asset Failure | LV | 1 | 154 | 0.0002433 | 0.00015799 | No
30/06/2019 | 18:28 | SS23 | Urban | Overloads |  | 1 | 182 | 0.00028754 | 0.00015799 | No
30/06/2019 | 19:07 | LWN21 | Rural Short | Overloads |  | 1 | 62.2 | 0.0010456 | 0.0016815 | No
30/06/2019 | 21:42 | OAK26 | Urban | Vegetation | Grow-in - Other responsible party | 48 | 78 | 0.0059151 | 0.0075835 | No
01/07/2019 | 06:29 | RWT23 | Urban | Asset Failure | LV | 9 | 66 | 0.00089467 | 0.0013556 | No
01/07/2019 | 10:33 | EM6 | Urban | Asset Failure | Distribution substation | 70 | 72 | 0.0079229 | 0.011004 | No
01/07/2019 | 11:41 | HGS22 | Rural Short | Vegetation | Grow-in - NSP responsibility | 51 | 489 | 0.41935 | 0.085756 | No
01/07/2019 | 12:58 | KBH34 | Urban | Vegetation | Grow-in - NSP responsibility | 480 | 20.2 | 0.015282 | 0.075835 | No
01/07/2019 | 13:05 | HT3 | Urban | Asset Failure | LV | 1 | 399.3 | 0.00063088 | 0.00015799 | No
01/07/2019 | 13:25 | RBD13 | Urban | Asset Failure | LV | 1 | 154.2 | 0.00024357 | 0.00015799 | No
01/07/2019 | 13:40 | LD7 | Urban | Third Party | Other | 1 | 50 | 7.8995e-05 | 0.00015799 | No
01/07/2019 | 14:35 | NW23 | Urban | Third Party | Vehicle Impact | 85 | 235 | 0.031558 | 0.013429 | No
01/07/2019 | 14:58 | CDA23 | Urban | Asset Failure | LV | 1 | 52 | 8.2155e-05 | 0.00015799 | No
01/07/2019 | 15:54 | BW23 | Urban | Asset Failure | LV | 1 | 45.2 | 7.1385e-05 | 0.00015799 | No
01/07/2019 | 16:05 | NW21 | Urban | Third Party | Other | 1 | 78.5 | 0.00012407 | 0.00015799 | No
01/07/2019 | 16:36 | MR31 | Urban | Asset Failure | LV | 1 | 59 | 9.3214e-05 | 0.00015799 | No
01/07/2019 | 17:02 | SR14 | Urban | Overloads |  | 1 | 208 | 0.00032862 | 0.00015799 | No
01/07/2019 | 17:28 | CRM22 | Urban | Asset Failure | LV | 6 | 52 | 0.00050279 | 0.0009669 | No
01/07/2019 | 17:46 | SS14 | Urban | Asset Failure | LV | 1 | 268.7 | 0.00042444 | 0.00015799 | No
01/07/2019 | 18:19 | DVY31 | Urban | Overloads |  | 1 | 210.4 | 0.00033233 | 0.00015799 | No
01/07/2019 | 18:21 | EW2 | Urban | Unknown | Unknown | 1 | 308.1 | 0.00048679 | 0.00015799 | No
01/07/2019 | 18:25 | CFD26 | Urban | Overloads |  | 1 | 175 | 0.00027648 | 0.00015799 | No
01/07/2019 | 19:26 | RBD21 | Rural Short | Overloads |  | 1 | 64 | 0.0010762 | 0.0016815 | No
01/07/2019 | 20:01 | SR23 | Urban | Overloads |  | 1 | 159 | 0.0002512 | 0.00015799 | No
02/07/2019 | 08:51 | OE9 | Urban | Overloads |  | 20 | 107 | 0.003403 | 0.0031803 | No
02/07/2019 | 11:18 | CDA23 | Urban | Asset Failure | LV | 1 | 176 | 0.00027806 | 0.00015799 | No
02/07/2019 | 11:42 | MC4 | Urban | Third Party | Vehicle Impact | 1 | 137.6 | 0.00027171 | 0.00019749 | No
02/07/2019 | 12:54 | NP36 | Urban | Asset Failure | LV | 1 | 119 | 0.00018801 | 0.00015799 | No
02/07/2019 | 20:12 | M12 | Urban | Asset Failure | LV | 1 | 87.8 | 0.00013864 | 0.00015799 | No
02/07/2019 | 20:19 | M12 | Urban | Asset Failure | LV | 1 | 80 | 0.00012642 | 0.00015799 | No
02/07/2019 | 20:20 | M12 | Urban | Asset Failure | LV | 1 | 79.6 | 0.00012568 | 0.00015799 | No
02/07/2019 | 22:58 | EW8 | Urban | Asset Failure | LV | 5 | 92 | 0.0007064 | 0.00076783 | No
03/07/2019 | 01:00 | BH31 | Urban | Asset Failure | HV | 324 | 184.2 | 0.094308 | 0.051189 | No
03/07/2019 | 01:12 | BH31 | Urban | Asset Failure | HV | 456 | 47.7 | 0.034353 | 0.072043 | No
03/07/2019 | 05:10 | LWN21 | Rural Short | Overloads |  | 1 | 154.8 | 0.0026035 | 0.0016815 | No
03/07/2019 | 08:12 | MTN34 | Urban | Asset Failure | LV | 1 | 118 | 0.00018643 | 0.00015799 | No
03/07/2019 | 09:12 | FTN14 | Urban | Asset Failure | LV | 1 | 208 | 0.00032862 | 0.00015799 | No
03/07/2019 | 09:20 | MGE31 | Urban | Asset Failure | LV | 1 | 69.3 | 0.00010946 | 0.00015799 | No
03/07/2019 | 09:54 | LWN21 | Rural Short | Unknown | Unknown | 6 | 296 | 0.029863 | 0.010089 | No
03/07/2019 | 10:06 | STO21 | Rural Short | Asset Failure | LV | 1 | 188.6 | 0.0031719 | 0.0016815 | No
03/07/2019 | 14:48 | CFD22 | Urban | Asset Failure | LV | 1 | 127 | 0.00020065 | 0.00015799 | No
03/07/2019 | 15:24 | FTN22 | Urban | Overloads |  | 6 | 66 | 0.00058497 | 0.00088632 | No
03/07/2019 | 17:23 | RBD21 | Rural Short | Unknown | Unknown | 5 | 96 | 0.0079918 | 0.0083234 | No
03/07/2019 | 18:10 | HGS32 | Urban | Asset Failure | LV | 1 | 130 | 0.00020539 | 0.00015799 | No
03/07/2019 | 20:42 | STO13 | Urban | Asset Failure | LV | 1 | 93 | 0.00014693 | 0.00015799 | No
03/07/2019 | 20:46 | BT15 | Urban | Asset Failure | LV | 1 | 13.1 | 2.0723e-05 | 0.00015799 | No
03/07/2019 | 22:17 | OR32 | Urban | Asset Failure | LV | 1 | 72.5 | 0.00011452 | 0.00015799 | No
03/07/2019 | 23:25 | BR4 | Urban | Asset Failure | LV | 1 | 64.1 | 0.00010124 | 0.00015799 | No
04/07/2019 | 02:47 | OR33 | Urban | Asset Failure | LV | 1 | 32.4 | 5.1215e-05 | 0.00015799 | No
04/07/2019 | 06:53 | DN4 | Urban | Asset Failure | LV | 1 | 116.7 | 0.00018432 | 0.00015799 | No
04/07/2019 | 09:13 | SVW42 | Urban | Asset Failure | LV | 2 | 136.5 | 0.00043137 | 0.00031598 | No
04/07/2019 | 10:09 | CDA23 | Urban | Asset Failure | LV | 1 | 96 | 0.00015167 | 0.00015799 | No
04/07/2019 | 11:29 | FTN11 | Urban | Third Party | Other | 1 | 150.3 | 0.00023738 | 0.00015799 | No
04/07/2019 | 13:38 | LD7 | Urban | Unknown | Unknown | 1 | 112 | 0.00017695 | 0.00015799 | No
04/07/2019 | 14:35 | BT15 | Urban | Unknown | Unknown | 1 | 40.1 | 6.3328e-05 | 0.00015799 | No
04/07/2019 | 16:34 | LD5 | Urban | Asset Failure | LV | 12 | 101 | 0.001843 | 0.0018248 | No
04/07/2019 | 17:55 | BC11 | Urban | Asset Failure | LV | 1 | 228.8 | 0.00036148 | 0.00015799 | No
04/07/2019 | 21:27 | HT1 | Urban | Asset Failure | HV | 1 | 128.9 | 0.00020365 | 0.00015799 | No
05/07/2019 | 01:24 | BH23 | Urban | Third Party | Vehicle Impact | 45 | 446 | 0.031709 | 0.0071095 | No
05/07/2019 | 01:33 | HGS22 | Rural Short | Asset Failure | LV | 8 | 72 | 0.01017 | 0.014125 | No
05/07/2019 | 04:11 | MTN23 | Urban | Asset Failure | LV | 1 | 184 | 0.00029068 | 0.00015799 | No
05/07/2019 | 09:14 | FTN24 | Urban | Asset Failure | LV | 1 | 343 | 0.0005419 | 0.00015799 | No
05/07/2019 | 11:01 | STO13 | Urban | Asset Failure | LV | 1 | 99.8 | 0.00015773 | 0.00015799 | No
05/07/2019 | 11:11 | MC6 | Urban | Asset Failure | LV | 1 | 195.3 | 0.00030848 | 0.00015799 | No
05/07/2019 | 11:23 | MR33 | Urban | Asset Failure | LV | 20 | 97 | 0.0031355 | 0.0032325 | No
05/07/2019 | 13:47 | MTN32 | Rural Short | Asset Failure | Distribution substation | 1 | 208 | 0.0034967 | 0.0016815 | No
05/07/2019 | 16:07 | EW14 | Urban | Asset Failure | LV | 1 | 111 | 0.00017537 | 0.00015799 | No
05/07/2019 | 17:14 | FTN25 | Urban | Asset Failure | LV | 12 | 166 | 0.0030291 | 0.0018248 | No
05/07/2019 | 17:42 | SS12 | Urban | Third Party | Vehicle Impact | 23 | 212.4 | 0.0078523 | 0.003697 | No
05/07/2019 | 18:47 | RWT34 | Urban | Asset Failure | LV | 62 | 103 | 0.010089 | 0.0097954 | No
05/07/2019 | 20:23 | NP16 | Urban | Asset Failure | HV | 228 | 464 | 0.16714 | 0.036022 | No
05/07/2019 | 21:01 | STO13 | Urban | Asset Failure | LV | 1 | 109 | 0.00017221 | 0.00015799 | No
06/07/2019 | 08:09 | WD23 | Urban | Asset Failure | LV | 1 | 111 | 0.00017537 | 0.00015799 | No
06/07/2019 | 10:22 | RBD13 | Urban | Asset Failure | LV | 1 | 217.9 | 0.00034429 | 0.00015799 | No
06/07/2019 | 11:39 | WD36 | Urban | Overloads |  | 1 | 171 | 0.00027016 | 0.00015799 | No
06/07/2019 | 12:28 | DSH14 | Urban | Animal | Other | 10 | 168.4 | 0.0026605 | 0.0015799 | No
06/07/2019 | 13:10 | EM3 | Urban | Asset Failure | LV | 1 | 88 | 0.00013903 | 0.00015799 | No
06/07/2019 | 15:07 | FTN11 | Urban | Third Party | Other | 1 | 143.4 | 0.00022648 | 0.00015799 | No
06/07/2019 | 17:38 | DMA23 | Rural Short | Asset Failure | LV | 1 | 112 | 0.0018833 | 0.0016815 | No
06/07/2019 | 17:57 | MTN32 | Rural Short | Asset Failure | LV | 1 | 153 | 0.0025727 | 0.0016815 | No
07/07/2019 | 05:06 | DMA15 | Rural Short | Animal | Animal impact | 45 | 114 | 0.086261 | 0.075667 | No
07/07/2019 | 10:30 | WD26 | Urban | Animal | Other | 40 | 80.9 | 0.0051094 | 0.0063196 | No
07/07/2019 | 12:30 | DC10 | Urban | Unknown | Unknown | 13 | 510 | 0.010104 | 0.0019812 | No
07/07/2019 | 12:43 | DC10 | Urban | Asset Failure | Distribution substation | 90 | 27 | 0.0038392 | 0.014219 | No
07/07/2019 | 12:47 | STO13 | Urban | Asset Failure | LV | 1 | 233.5 | 0.00036893 | 0.00015799 | No
07/07/2019 | 12:53 | DC10 | Urban | Asset Failure | HV | 71 | 128 | 0.014358 | 0.011217 | No
07/07/2019 | 12:56 | DC10 | Urban | Asset Failure | HV | 201 | 42.1 | 0.013356 | 0.031756 | No
07/07/2019 | 16:53 | DN10 | Urban | Asset Failure | LV | 1 | 156 | 0.00024646 | 0.00015799 | No
07/07/2019 | 17:01 | HGS22 | Rural Short | Asset Failure | LV | 2 | 118.2 | 0.0045912 | 0.0038842 | No
07/07/2019 | 19:08 | LD3 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 111.9 | 0.00017676 | 0.00015799 | No
07/07/2019 | 19:15 | M34 | Urban | Asset Failure | LV | 1 | 286.7 | 0.00045293 | 0.00015799 | No
07/07/2019 | 22:18 | EW8 | Urban | Asset Failure | HV | 924 | 80.3 | 0.11715 | 0.14598 | No
07/07/2019 | 22:22 | EW8 | Urban | Asset Failure | HV | 711 | 75.2 | 0.084473 | 0 | No
08/07/2019 | 08:43 | MC1 | Urban | Overloads |  | 1 | 117 | 0.00018485 | 0.00015799 | No
08/07/2019 | 09:01 | NB25 | Urban | Overloads |  | 1 | 84 | 0.00013271 | 0.00015799 | No
08/07/2019 | 10:41 | NW21 | Urban | Asset Failure | LV | 1 | 115 | 0.00018169 | 0.00015799 | No
08/07/2019 | 13:39 | EW12 | Urban | Overloads |  | 1 | 151 | 0.00023856 | 0.00015799 | No
08/07/2019 | 13:57 | EW2 | Urban | Overloads |  | 1 | 212.8 | 0.00033612 | 0.00015799 | No
08/07/2019 | 14:21 | DN24 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 259 | 0.00040919 | 0.00015799 | No
08/07/2019 | 15:28 | DC8 | Urban | Asset Failure | LV | 1 | 63 | 9.9534e-05 | 0.00015799 | No
08/07/2019 | 16:26 | FSH33 | Urban | Asset Failure | HV | 212 | 74 | 0.024773 | 0.033494 | No
08/07/2019 | 16:38 | FSH13 | Urban | Asset Failure | LV | 37 | 42 | 0.0024744 | 0.0058914 | No
08/07/2019 | 17:09 | DN21 | Urban | Overloads |  | 1 | 181 | 0.00028596 | 0.00015799 | No
08/07/2019 | 20:04 | EW9 | Urban | Overloads |  | 27 | 146 | 0.0063179 | 0.0043273 | No
08/07/2019 | 20:04 | EW8 | Urban | Overloads |  | 34 | 116 | 0.0061688 | 0.0053179 | No
08/07/2019 | 20:04 | EW8 | Urban | Overloads |  | 26 | 116 | 0.0048383 | 0.0041709 | No
08/07/2019 | 20:11 | BC11 | Urban | Overloads |  | 34 | 118.3 | 0.0063519 | 0.0053701 | No
09/07/2019 | 00:13 | DC7 | Urban | Asset Failure | LV | 1 | 101 | 0.00015957 | 0.00015799 | No
09/07/2019 | 07:22 | OAK33 | Urban | Asset Failure | LV | 52 | 27 | 0.0022101 | 0.0081855 | No
09/07/2019 | 17:01 | RBD12 | Rural Short | Asset Failure | LV | 1 | 161.6 | 0.0027179 | 0.0016815 | No
09/07/2019 | 18:26 | OAK21 | Urban | Asset Failure | LV | 20 | 154 | 0.0048661 | 0.0031598 | No
09/07/2019 | 21:01 | MTN35 | Rural Short | Asset Failure | LV | 1 | 103.8 | 0.0017451 | 0.0016815 | No
09/07/2019 | 21:51 | NP23 | Urban | Asset Failure | Distribution substation | 100 | 28.9 | 0.0045633 | 0.015799 | No
10/07/2019 | 12:46 | FTN13 | Urban | Asset Failure | LV | 1 | 193.3 | 0.00030545 | 0.00015799 | No
10/07/2019 | 14:21 | MGE12 | Urban | Vegetation | Grow-in - Other responsible party | 1,093 | 15.7 | 0.027161 | 0.17268 | No
10/07/2019 | 15:06 | MTN32 | Rural Short | Asset Failure | HV | 1 | 188.9 | 0.0031755 | 0.0016815 | No
10/07/2019 | 15:50 | BW33 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 69 | 140 | 0.015262 | 0.010901 | No
10/07/2019 | 16:49 | DC10 | Urban | Asset Failure | LV | 25 | 51 | 0.0020208 | 0.0039624 | No
10/07/2019 | 17:50 | EM6 | Urban | Vegetation | Grow-in - Other responsible party | 37 | 85 | 0.0049688 | 0.0058456 | No
10/07/2019 | 17:53 | STO21 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 106 | 0.0017824 | 0.0016815 | No
10/07/2019 | 18:31 | SS12 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 178.4 | 0.00028185 | 0.00015799 | No
10/07/2019 | 18:52 | HT2 | Urban | Asset Failure | LV | 1 | 408 | 0.0006446 | 0.00015799 | No
10/07/2019 | 18:54 | CFD14 | Urban | Weather |  | 2 | 205.3 | 0.0006486 | 0.00031598 | No
10/07/2019 | 19:05 | HGS23 | Rural Short | Weather |  | 48 | 426.3 | 0.34403 | 0.080712 | No
10/07/2019 | 19:15 | RBD23 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 345 | 0.00054506 | 0.00015799 | No
10/07/2019 | 19:26 | CFD26 | Urban | Overloads |  | 36 | 124 | 0.0070879 | 0.0057161 | No
10/07/2019 | 19:53 | SR20 | Urban | Asset Failure | LV | 1 | 267 | 0.00042183 | 0.00015799 | No
10/07/2019 | 19:54 | RBD23 | Urban | Asset Failure | LV | 1 | 364.9 | 0.00057645 | 0.00015799 | No
10/07/2019 | 20:23 | AR4 | Urban | Third Party | Other | 18 | 62 | 0.0017632 | 0.0028438 | No
10/07/2019 | 20:27 | FSH33 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 767.6 | 0.0012127 | 0.00015799 | No
10/07/2019 | 20:46 | DMA24 | Rural Short | Overloads |  | 21 | 464 | 0.16221 | 0.034958 | No
10/07/2019 | 20:52 | LWN21 | Rural Short | Vegetation | Grow-in - Other responsible party | 1,793 | 103.1 | 3.1069 | 3.0149 | No
10/07/2019 | 20:57 | NP12 | Urban | Weather |  | 10 | 198 | 0.0032001 | 0.0016162 | No
10/07/2019 | 21:04 | MGE34 | Urban | Vegetation | Grow-in - NSP responsibility | 623 | 46 | 0.04531 | 0.098428 | No
10/07/2019 | 21:07 | HGS33 | Rural Short | Vegetation | Grow-in - NSP responsibility | 26 | 208 | 0.090935 | 0.043719 | No
10/07/2019 | 21:08 | FSH22 | Urban | Vegetation | Grow-in - Other responsible party | 60 | 801 | 0.07593 | 0.0094794 | No
10/07/2019 | 21:08 | FSH32 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 361.7 | 0.0060817 | 0.0016815 | No
10/07/2019 | 21:23 | HGS33 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 382 | 0.0064233 | 0.0016815 | No
10/07/2019 | 21:46 | RBD12 | Rural Short | Weather |  | 323 | 267.4 | 1.4524 | 0.54312 | No
10/07/2019 | 21:47 | DMA21 | Urban | Vegetation | Grow-in - Other responsible party | 1,009 | 115.5 | 0.18418 | 0.15941 | No
10/07/2019 | 21:55 | DMA15 | Rural Short | Weather |  | 2 | 365 | 0.014177 | 0.0038842 | No
10/07/2019 | 21:56 | DMA15 | Rural Short | Vegetation | Grow-in - Other responsible party | 108 | 1,076.0 | 1.954 | 0.1816 | No
10/07/2019 | 21:56 | DMA15 | Rural Short | Weather |  | 17 | 1,214.0 | 0.34703 | 0.028585 | No
10/07/2019 | 22:01 | DMA13 | Rural Short | Vegetation | Grow-in - Other responsible party | 496 | 127.1 | 1.0603 | 0.83402 | No
10/07/2019 | 22:15 | FSH21 | Rural Short | Weather |  | 687 | 154 | 1.7788 | 1.1552 | No
10/07/2019 | 22:15 | LWN21 | Rural Short | Weather |  | 12 | 215.5 | 0.04349 | 0.020178 | No
10/07/2019 | 22:17 | DN25 | Urban | Weather |  | 1,006 | 71.3 | 0.11335 | 0.15894 | No
10/07/2019 | 22:21 | FTN25 | Urban | Weather |  | 940 | 51.4 | 0.07631 | 0.14851 | No
10/07/2019 | 22:33 | OR23 | Urban | Asset Failure | LV | 1 | 226.7 | 0.00035816 | 0.00015799 | No
10/07/2019 | 22:36 | FSH31 | Urban | Unknown | Unknown | 13 | 361.7 | 0.0074282 | 0.0020539 | No
10/07/2019 | 23:08 | FTN23 | Urban | Asset Failure | LV | 1 | 156.5 | 0.00024725 | 0.00015799 | No
11/07/2019 | 03:45 | FSH33 | Urban | Vegetation | Grow-in - Other responsible party | 30 | 50 | 0.0023698 | 0.0047397 | No
11/07/2019 | 04:12 | RBD12 | Rural Short | Vegetation | Grow-in - NSP responsibility | 17 | 752.2 | 0.21501 | 0.028585 | No
11/07/2019 | 06:12 | CDA24 | Urban | Asset Failure | LV | 1 | 618 | 0.00097638 | 0.00015799 | No
11/07/2019 | 08:05 | HGS33 | Rural Short | Unknown | Unknown | 1 | 745 | 0.012527 | 0.0016815 | No
11/07/2019 | 08:26 | BW21 | Urban | Asset Failure | LV | 1 | 198.8 | 0.00031403 | 0.00015799 | No
11/07/2019 | 08:52 | LWN21 | Rural Short | Unknown | Unknown | 1 | 297.2 | 0.0049971 | 0.0016815 | No
11/07/2019 | 09:33 | DSH23 | Urban | Asset Failure | HV | 39 | 3.7 | 0.00023003 | 0.0061616 | No
11/07/2019 | 09:52 | DN10 | Urban | Asset Failure | LV | 1 | 157.5 | 0.00024878 | 0.00015799 | No
11/07/2019 | 11:32 | DMA15 | Rural Short | Asset Failure | LV | 1 | 42.2 | 0.00070959 | 0.0016815 | No
11/07/2019 | 11:57 | FSH31 | Urban | Overloads |  | 1 | 543 | 0.00085788 | 0.00015799 | No
11/07/2019 | 15:18 | MC6 | Urban | Asset Failure | LV | 1 | 227 | 0.00035858 | 0.00015799 | No
11/07/2019 | 15:30 | STO13 | Urban | Asset Failure | LV | 1 | 535 | 0.00084525 | 0.00015799 | No
11/07/2019 | 16:46 | CRM35 | Urban | Asset Failure | LV | 1 | 289 | 0.00045659 | 0.00015799 | No
11/07/2019 | 18:24 | NP24 | Urban | Asset Failure | LV | 1 | 64.2 | 0.00010138 | 0.00015799 | No
11/07/2019 | 18:40 | STO13 | Urban | Asset Failure | HV | 302 | 32.8 | 0.015658 | 0.047713 | No
11/07/2019 | 19:31 | FSH12 | Rural Short | Vegetation | Grow-in - NSP responsibility | 18 | 14 | 0.0042374 | 0.030267 | No
11/07/2019 | 20:08 | CRM24 | Urban | Asset Failure | LV | 18 | 117.6 | 0.0033727 | 0.0028675 | No
11/07/2019 | 20:26 | DMA21 | Urban | Asset Failure | LV | 2 | 139 | 0.00049192 | 0.0003539 | No
12/07/2019 | 07:17 | FSH13 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 234.9 | 0.00037107 | 0.00015799 | No
12/07/2019 | 08:09 | MGE23 | Urban | Vegetation | Grow-in - Other responsible party | 965 | 36.9 | 0.056283 | 0.15246 | No
12/07/2019 | 10:19 | CRM22 | Urban | Asset Failure | LV | 1 | 205.6 | 0.00032483 | 0.00015799 | No
12/07/2019 | 11:26 | LWN24 | Urban | Asset Failure | LV | 1 | 588.9 | 0.0009304 | 0.00015799 | No
12/07/2019 | 11:48 | BR15 | Urban | Asset Failure | LV | 1 | 280 | 0.00044237 | 0.00015799 | No
12/07/2019 | 11:55 | RBD13 | Urban | Asset Failure | LV | 1 | 428.4 | 0.00067678 | 0.00015799 | No
12/07/2019 | 13:47 | MGE34 | Urban | Asset Failure | HV | 550 | 2.6 | 0.0022882 | 0.086894 | No
12/07/2019 | 14:41 | SH22 | Urban | Asset Failure | LV | 1 | 78.6 | 0.0001241 | 0.00015799 | No
12/07/2019 | 14:43 | BC22 | Urban | Asset Failure | LV | 1 | 122 | 0.00019275 | 0.00015799 | No
12/07/2019 | 15:26 | DMA23 | Rural Short | Vegetation | Grow-in - NSP responsibility | 38 | 123.3 | 0.078753 | 0.063897 | No
12/07/2019 | 16:51 | MTN23 | Urban | Asset Failure | LV | 15 | 504 | 0.011944 | 0.0023698 | No
12/07/2019 | 18:58 | STO23 | Urban | Asset Failure | LV | 1 | 58 | 9.1634e-05 | 0.00015799 | No
12/07/2019 | 20:29 | NP33 | Urban | Asset Failure | LV | 1 | 81 | 0.00012797 | 0.00015799 | No
12/07/2019 | 23:22 | LD3 | Urban | Third Party | Vehicle Impact | 71 | 273 | 0.030623 | 0.011217 | No
13/07/2019 | 09:54 | FSH31 | Urban | Asset Failure | LV | 8 | 165.9 | 0.0020311 | 0.0012244 | No
13/07/2019 | 09:56 | MC1 | Urban | Asset Failure | LV | 7 | 293.5 | 0.003301 | 0.0011249 | No
13/07/2019 | 11:21 | STO13 | Urban | Asset Failure | LV | 39 | 219 | 0.013494 | 0.0061616 | No
13/07/2019 | 12:59 | EB22 | Urban | Weather |  | 2,001 | 65.5 | 0.20722 | 0.31614 | No
13/07/2019 | 13:01 | CFD15 | Urban | Vegetation | Grow-in - Other responsible party | 1,636 | 57.8 | 0.14944 | 0.25847 | No
13/07/2019 | 13:08 | WD15 | Urban | Vegetation | Grow-in - Other responsible party | 626 | 71 | 0.070237 | 0.098902 | No
13/07/2019 | 13:09 | WD23 | Urban | Vegetation | Grow-in - NSP responsibility | 508 | 71.3 | 0.057184 | 0.080259 | No
13/07/2019 | 13:09 | NW21 | Urban | Vegetation | Grow-in - NSP responsibility | 731 | 83.7 | 0.096608 | 0.11549 | No
13/07/2019 | 13:10 | DC2 | Urban | Weather |  | 901 | 295.2 | 0.42017 | 0.14235 | No
13/07/2019 | 13:20 | NW21 | Urban | Asset Failure | LV | 1 | 528.1 | 0.0008344 | 0.00015799 | No
13/07/2019 | 13:22 | K13 | Urban | Asset Failure | HV | 759 | 152.2 | 0.18245 | 0.11991 | No
13/07/2019 | 14:08 | CFD15 | Urban | Unknown | Unknown | 80 | 131.8 | 0.016663 | 0.012639 | No
13/07/2019 | 14:25 | SS12 | Urban | Weather |  | 272 | 50.9 | 0.021881 | 0.042973 | No
13/07/2019 | 14:51 | KBH32 | Urban | Vegetation | Grow-in - Other responsible party | 30 | 96 | 0.0046047 | 0.0047966 | No
13/07/2019 | 15:26 | NW22 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 353.9 | 0.00055918 | 0.00015799 | No
13/07/2019 | 15:34 | LWN21 | Rural Short | Asset Failure | LV | 4 | 205.8 | 0.013843 | 0.006726 | No
13/07/2019 | 15:52 | MC3 | Urban | Third Party | Other | 1 | 116.8 | 0.00018445 | 0.00015799 | No
13/07/2019 | 15:58 | DN22 | Urban | Asset Failure | LV | 1 | 122 | 0.00019275 | 0.00015799 | No
13/07/2019 | 16:00 | EB22 | Urban | Asset Failure | LV | 81 | 140.5 | 0.017974 | 0.012797 | No
13/07/2019 | 16:43 | RWT24 | Urban | Weather |  | 18 | 32 | 0.00091761 | 0.0028675 | No
13/07/2019 | 22:48 | EW8 | Urban | Asset Failure | LV | 1 | 71.2 | 0.00011244 | 0.00015799 | No
14/07/2019 | 02:35 | KBH32 | Urban | Asset Failure | LV | 1 | 75 | 0.00011849 | 0.00015799 | No
14/07/2019 | 10:47 | CRM22 | Urban | Asset Failure | LV | 1 | 92.6 | 0.0001463 | 0.00015799 | No
14/07/2019 | 13:42 | CRM35 | Urban | Asset Failure | LV | 1 | 213 | 0.00033652 | 0.00015799 | No
14/07/2019 | 13:54 | CRM22 | Urban | Asset Failure | LV | 25 | 106 | 0.0042001 | 0.0039624 | No
14/07/2019 | 14:42 | MTN23 | Urban | Asset Failure | LV | 1 | 228 | 0.00036022 | 0.00015799 | No
14/07/2019 | 15:13 | HT1 | Urban | Asset Failure | LV | 139 | 251 | 0.055121 | 0.021961 | No
14/07/2019 | 16:50 | STO21 | Rural Short | Asset Failure | LV | 1 | 55 | 0.00092482 | 0.0016815 | No
14/07/2019 | 17:20 | CRM14 | Urban | Asset Failure | LV | 1 | 90 | 0.00014219 | 0.00015799 | No
14/07/2019 | 17:48 | NP23 | Urban | Asset Failure | LV | 1 | 122 | 0.00019275 | 0.00015799 | No
14/07/2019 | 18:17 | CDA21 | Urban | Asset Failure | LV | 1 | 128 | 0.00020223 | 0.00015799 | No
14/07/2019 | 18:40 | CRM22 | Urban | Asset Failure | LV | 1 | 95 | 0.00015009 | 0.00015799 | No
14/07/2019 | 19:23 | LD5 | Urban | Third Party | Vehicle Impact | 1 | 109.2 | 0.00017253 | 0.00015799 | No
14/07/2019 | 20:28 | SS13 | Urban | Asset Failure | LV | 16 | 92 | 0.0023024 | 0.0025026 | No
14/07/2019 | 20:35 | SH32 | Urban | Unknown | Unknown | 1 | 102 | 0.00016115 | 0.00015799 | No
14/07/2019 | 22:04 | NW11 | Urban | Weather |  | 1,619 | 127.8 | 0.32687 | 0.25579 | No
14/07/2019 | 22:25 | STO21 | Rural Short | Weather |  | 21 | 220 | 0.077685 | 0.035311 | No
14/07/2019 | 22:40 | RWT23 | Urban | Vegetation | Grow-in - Other responsible party | 205 | 950 | 0.30769 | 0.032388 | No
15/07/2019 | 00:01 | BH23 | Urban | Overloads |  | 2 | 149 | 0.00052966 | 0.00035548 | No
15/07/2019 | 03:50 | HGS21 | Rural Short | Asset Failure | HV | 36 | 574.9 | 0.34801 | 0.060534 | No
15/07/2019 | 06:02 | MC1 | Urban | Asset Failure | LV | 1 | 118 | 0.00018643 | 0.00015799 | No
15/07/2019 | 07:03 | DN25 | Urban | Asset Failure | LV | 29 | 166.2 | 0.007614 | 0.0045817 | No
15/07/2019 | 07:29 | K4 | Urban | Asset Failure | LV | 1 | 91 | 0.00014374 | 0.00015799 | No
15/07/2019 | 08:49 | RBD23 | Urban | Asset Failure | LV | 1 | 130.8 | 0.00020662 | 0.00015799 | No
15/07/2019 | 08:54 | DN25 | Urban | Asset Failure | LV | 1 | 376 | 0.00059396 | 0.00015799 | No
15/07/2019 | 09:37 | RBD21 | Rural Short | Asset Failure | HV | 3 | 383 | 0.01932 | 0.0050445 | No
15/07/2019 | 09:40 | BH21 | Urban | Asset Failure | LV | 1 | 350.5 | 0.00055381 | 0.00015799 | No
15/07/2019 | 11:42 | BR9 | Urban | Vegetation | Grow-in - Other responsible party | 36 | 123 | 0.0069958 | 0.0056876 | No
15/07/2019 | 12:48 | GW5 | Urban | Third Party | Other | 19 | 242 | 0.0071917 | 0.0029718 | No
15/07/2019 | 14:56 | RWT23 | Urban | Network Business | Networ Error | 12 | 93.2 | 0.0016933 | 0.0018169 | No
15/07/2019 | 16:44 | CDA11 | Urban | Overloads |  | 1 | 116 | 0.00018327 | 0.00015799 | No
15/07/2019 | 17:04 | SV33 | Urban | Overloads |  | 1 | 371 | 0.00058614 | 0 | No
15/07/2019 | 17:15 | OR25 | Urban | Asset Failure | LV | 1 | 120 | 0.00018959 | 0.00015799 | No
15/07/2019 | 17:44 | RBD23 | Urban | Weather |  | 1 | 175.4 | 0.00027714 | 0.00015799 | No
15/07/2019 | 18:13 | DSH23 | Urban | Asset Failure | LV | 1 | 332 | 0.00052453 | 0.00015799 | No
15/07/2019 | 18:17 | HGS21 | Rural Short | Asset Failure | LV | 45 | 113 | 0.084649 | 0.07491 | No
15/07/2019 | 18:40 | KBH32 | Urban | Asset Failure | LV | 1 | 389.4 | 0.00061521 | 0.00015799 | No
15/07/2019 | 19:00 | RBD12 | Rural Short | Asset Failure | LV | 1 | 235.7 | 0.0039627 | 0.0016815 | No
15/07/2019 | 19:48 | M31 | Urban | Overloads |  | 1 | 157.3 | 0.00024844 | 0.00015799 | No
15/07/2019 | 19:53 | MR15 | Urban | Asset Failure | LV | 1 | 187 | 0.00029544 | 0.00015799 | No
15/07/2019 | 20:54 | BH21 | Urban | Third Party | Vehicle Impact | 21 | 201 | 0.0066021 | 0.0032846 | No
15/07/2019 | 23:02 | MTN22 | Rural Short | Overloads |  | 1 | 243 | 0.004086 | 0.0016815 | No
15/07/2019 | 23:49 | MTN32 | Rural Short | Vegetation | Grow-in - Other responsible party | 15 | 876 | 0.22095 | 0.025222 | No
16/07/2019 | 07:03 | FSH13 | Urban | Asset Failure | LV | 1 | 196.5 | 0.0003104 | 0.00015799 | No
16/07/2019 | 09:00 | DSH31 | Urban |  | Networ Error | 1 | 30 | 4.7397e-05 | 0.00015799 | No
16/07/2019 | 10:49 | EW9 | Urban | Asset Failure | LV | 38 | 81 | 0.0048988 | 0.0060479 | No
16/07/2019 | 11:12 | EW14 | Urban | Asset Failure | LV | 2 | 77.9 | 0.00024609 | 0.00031598 | No
16/07/2019 | 12:58 | DMA23 | Rural Short | Asset Failure | LV | 16 | 107 | 0.029093 | 0.02719 | No
16/07/2019 | 16:26 | SR24 | Urban | Asset Failure | LV | 1 | 274.9 | 0.00043431 | 0.00015799 | No
16/07/2019 | 18:22 | LD7 | Urban | Overloads |  | 1 | 87.7 | 0.00013853 | 0.00015799 | No
16/07/2019 | 18:34 | M31 | Urban | Asset Failure | LV | 1 | 76 | 0.00012007 | 0.00015799 | No
17/07/2019 | 07:55 | DMA13 | Rural Short | Asset Failure | LV | 1 | 110 | 0.0018488 | 0.0016815 | No
17/07/2019 | 09:16 | NB32 | Urban | Asset Failure | LV | 1 | 378 | 0.0005972 | 0.00015799 | No
17/07/2019 | 10:08 | BW35 | Urban | Asset Failure | LV | 1 | 217 | 0.00034284 | 0.00015799 | No
17/07/2019 | 10:15 | GW7 | Urban | Asset Failure | LV | 1 | 114.5 | 0.00018095 | 0.00015799 | No
17/07/2019 | 14:30 | SS22 | Urban | Asset Failure | LV | 2 | 209.2 | 0.00066092 | 0.00031598 | No
17/07/2019 | 15:19 | DC7 | Urban | Unknown | Unknown | 1 | 79 | 0.00012481 | 0.00015799 | No
17/07/2019 | 15:35 | OAK26 | Urban | Asset Failure | LV | 1 | 84.6 | 0.00013363 | 0.00015799 | No
17/07/2019 | 18:54 | SR15 | Urban | Asset Failure | LV | 1 | 51 | 8.0575e-05 | 0.00015799 | No
17/07/2019 | 19:23 | SVW41 | Urban | Asset Failure | LV | 1 | 125.6 | 0.00019836 | 0.00015799 | No
17/07/2019 | 20:35 | K13 | Urban | Asset Failure | LV | 1 | 55.3 | 8.7421e-05 | 0.00015799 | No
17/07/2019 | 22:08 | FTN11 | Urban | Third Party | Other | 1 | 46.3 | 7.3176e-05 | 0.00015799 | No
18/07/2019 | 08:05 | FSH31 | Urban | Overloads |  | 7 | 135 | 0.0014077 | 0.0010427 | No
18/07/2019 | 09:01 | MC6 | Urban | Overloads |  | 1 | 88.2 | 0.00013927 | 0.00015799 | No
18/07/2019 | 10:46 | MR33 | Urban | Overloads |  | 1 | 104 | 0.00016431 | 0.00015799 | No
18/07/2019 | 14:45 | LWN21 | Rural Short | Third Party | Other | 1 | 355 | 0.0059096 | 0.0016647 | No
18/07/2019 | 15:26 | NW13 | Urban | Asset Failure | LV | 1 | 160.7 | 0.00025392 | 0.00015799 | No
18/07/2019 | 15:54 | STO23 | Urban | Asset Failure | LV | 1 | 163 | 0.00025752 | 0.00015799 | No
18/07/2019 | 16:41 | OR24 | Urban | Asset Failure | LV | 1 | 138.4 | 0.00021863 | 0.00015799 | No
18/07/2019 | 18:33 | HGS33 | Rural Short | Asset Failure | LV | 1 | 46.5 | 0.00078217 | 0.0016815 | No
18/07/2019 | 19:44 | EW1 | Urban | Asset Failure | LV | 1 | 104 | 0.00016436 | 0.00015799 | No
18/07/2019 | 20:04 | NW31 | Urban | Third Party | Other | 1 | 75 | 0.00011849 | 0.00015799 | No
19/07/2019 | 03:52 | FSH34 | Urban | Animal | Animal impact | 23 | 33 | 0.0012226 | 0.0037049 | No
19/07/2019 | 08:39 | OAK26 | Urban | Asset Failure | LV | 1 | 69.1 | 0.00010917 | 0.00015799 | No
19/07/2019 | 09:53 | CRM13 | Urban | Asset Failure | LV | 1 | 366.3 | 0.00057874 | 0.00015799 | No
19/07/2019 | 11:38 | SVW45 | Urban | Animal | Animal impact | 2 | 156.9 | 0.00049572 | 0.00031598 | No
19/07/2019 | 13:13 | BC22 | Urban | Asset Failure | LV | 1 | 526 | 0.000831 | 0.00015799 | No
19/07/2019 | 18:10 | FSH12 | Rural Short | Overloads |  | 12 | 42 | 0.0084747 | 0.020178 | No
19/07/2019 | 18:15 | K7 | Urban | Vegetation | Grow-in - NSP responsibility | 30 | 180 | 0.0084461 | 0.0046923 | No
19/07/2019 | 19:12 | LWN21 | Rural Short | Asset Failure | LV | 1 | 118 | 0.0019842 | 0.0016815 | No
19/07/2019 | 21:58 | EM6 | Urban | Unknown | Unknown | 1 | 107 | 0.00016905 | 0.00015799 | No
19/07/2019 | 22:17 | OR24 | Urban | Unknown | Unknown | 1 | 112 | 0.00017695 | 0.00015799 | No
19/07/2019 | 22:34 | SVW55 | Urban | Asset Failure | LV | 1 | 98 | 0.00015483 | 0.00015799 | No
20/07/2019 | 01:01 | EW1 | Urban | Asset Failure | LV | 1 | 177.5 | 0.00028046 | 0.00015799 | No
20/07/2019 | 09:16 | STO21 | Rural Short | Asset Failure | LV | 1 | 118.5 | 0.0019928 | 0.0016815 | No
20/07/2019 | 11:36 | DMA23 | Rural Short | Asset Failure | LV | 1 | 173.3 | 0.0029132 | 0.0016815 | No
20/07/2019 | 16:14 | K6 | Urban | Unknown | Unknown | 1 | 81 | 0.00012797 | 0.00015799 | No
20/07/2019 | 19:33 | CDA11 | Urban | Asset Failure | LV | 1 | 141.3 | 0.00022324 | 0.00015799 | No
20/07/2019 | 20:09 | STO21 | Rural Short | Asset Failure | LV | 1 | 96 | 0.0016142 | 0.0016815 | No
20/07/2019 | 20:49 | MC2 | Urban | Unknown | Unknown | 2 | 76.6 | 0.00024204 | 0.00031598 | No
20/07/2019 | 21:23 | LWN33 | Urban | Asset Failure | LV | 1 | 112 | 0.00017695 | 0.00015799 | No
21/07/2019 | 00:34 | NW33 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 115.9 | 0.00018303 | 0.00015799 | No
21/07/2019 | 06:33 | BT10 | Urban | Asset Failure | LV | 23 | 161.6 | 0.005982 | 0.0037017 | No
21/07/2019 | 08:22 | HGS21 | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 22 | 128 | 0.047351 | 0.036993 | No
21/07/2019 | 13:26 | SVW54 | Urban | Asset Failure | LV | 18 | 302 | 0.0085883 | 0.0028438 | No
21/07/2019 | 13:39 | EW8 | Urban | Asset Failure | LV | 1 | 500.3 | 0.00079048 | 0.00015799 | No
21/07/2019 | 15:23 | SVW41 | Urban | Network Business | Networ Error | 64 | 37 | 0.0037412 | 0.010111 | No
21/07/2019 | 15:25 | EB31 | Urban | Asset Failure | LV | 1 | 79.7 | 0.00012589 | 0.00015799 | No
21/07/2019 | 21:28 | CRM13 | Urban | Asset Failure | LV | 13 | 152 | 0.0031699 | 0.0020855 | No
21/07/2019 | 22:42 | K4 | Urban | Asset Failure | LV | 1 | 93 | 0.00014693 | 0.00015799 | No
22/07/2019 | 08:11 | RBD21 | Rural Short | Unknown | Unknown | 19 | 13.2 | 0.0042118 | 0.031948 | No
22/07/2019 | 10:44 | DC7 | Urban | Asset Failure | LV | 1 | 120.6 | 0.00019046 | 0.00015799 | No
22/07/2019 | 11:02 | CRM13 | Urban | Asset Failure | LV | 40 | 633 | 0.040003 | 0.0063196 | No
22/07/2019 | 12:09 | FSH32 | Rural Short | Asset Failure | HV | 9 | 15.1 | 0.0022851 | 0.015133 | No
22/07/2019 | 12:41 | STO21 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 289.4 | 0.0048662 | 0.0016815 | No
22/07/2019 | 12:53 | OE5 | Urban | Asset Failure | LV | 1 | 114.1 | 0.00018027 | 0.00015799 | No
22/07/2019 | 16:19 | K8 | Urban | Asset Failure | LV | 1 | 370.8 | 0.00058575 | 0.00015799 | No
22/07/2019 | 17:42 | SH22 | Urban | Asset Failure | LV | 1 | 197.7 | 0.00031229 | 0.00015799 | No
22/07/2019 | 19:38 | NP33 | Urban | Third Party | Other | 1 | 137 | 0.00021645 | 0.00015799 | No
22/07/2019 | 19:46 | NW22 | Urban | Asset Failure | LV | 1 | 88 | 0.00013903 | 0.00015799 | No
22/07/2019 | 23:32 | SS22 | Urban | Asset Failure | LV | 1 | 42 | 6.6408e-05 | 0.00015799 | No
23/07/2019 | 00:48 | DC8 | Urban | Asset Failure | LV | 1 | 51.3 | 8.0996e-05 | 0.00015799 | No
23/07/2019 | 07:41 | FSH23 | Rural Short | Vegetation | Grow-in - Other responsible party | 24 | 334 | 0.13479 | 0.040356 | No
23/07/2019 | 10:01 | EL10 | Urban | Asset Failure | LV | 1 | 232.9 | 0.00036796 | 0.00015799 | No
23/07/2019 | 10:24 | MGE32 | Urban | Asset Failure | LV | 66 | 726 | 0.075702 | 0.010427 | No
23/07/2019 | 10:24 | MGE32 | Urban | Asset Failure | LV | 68 | 726 | 0.077996 | 0.010743 | No
23/07/2019 | 12:25 | SR15 | Urban | Third Party | Other | 1 | 389.8 | 0.00061576 | 0.00015799 | No
23/07/2019 | 12:25 | MTN22 | Rural Short | Unknown | Unknown | 2 | 94 | 0.0031618 | 0.003363 | No
23/07/2019 | 13:08 | BC11 | Urban | Asset Failure | LV | 1 | 116.5 | 0.00018411 | 0.00015799 | No
23/07/2019 | 13:48 | DMA24 | Rural Short | Asset Failure | LV | 1 | 201.7 | 0.0033919 | 0.0016815 | No
23/07/2019 | 16:24 | NB36 | Urban | Asset Failure | LV | 1 | 223 | 0.00035229 | 0.00015799 | No
23/07/2019 | 17:10 | FSH22 | Urban | Asset Failure | LV | 1 | 79.9 | 0.00012623 | 0.00015799 | No
23/07/2019 | 17:47 | RWT23 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 154.6 | 0.0002443 | 0.00015799 | No
23/07/2019 | 18:02 | BR1 | Urban | Asset Failure | LV | 32 | 148 | 0.0074847 | 0.0050573 | No
23/07/2019 | 19:10 | RWT12 | Urban | Vegetation | Grow-in - NSP responsibility | 30 | 80 | 0.0037412 | 0.0046765 | No
23/07/2019 | 19:36 | LD32 | Urban | Asset Failure | LV | 38 | 372 | 0.02211 | 0.0059436 | No
23/07/2019 | 19:56 | DC5 | Urban | Asset Failure | LV | 187 | 241.3 | 0.07128 | 0.029544 | No
24/07/2019 | 00:00 | DC5 | Urban | Asset Failure | HV | 504 | 75.9 | 0.060397 | 0.079627 | No
24/07/2019 | 08:27 | CFD14 | Urban | Asset Failure | LV | 1 | 119 | 0.00018796 | 0.00015799 | No
24/07/2019 | 09:59 | CRM22 | Urban | Asset Failure | LV | 21 | 106 | 0.0034817 | 0.0032846 | No
24/07/2019 | 10:27 | NB32 | Urban | Asset Failure | LV | 1 | 206 | 0.00032546 | 0.00015799 | No
24/07/2019 | 19:06 | DC10 | Urban | Asset Failure | LV | 1 | 172 | 0.00027177 | 0.00015799 | No
24/07/2019 | 20:28 | WD14 | Urban | Asset Failure | LV | 1 | 92 | 0.00014535 | 0.00015799 | No
24/07/2019 | 21:30 | K10 | Urban | Asset Failure | LV | 1 | 92 | 0.0001453 | 0.00015799 | No
24/07/2019 | 21:36 | EB22 | Urban | Asset Failure | LV | 1 | 174 | 0.0002749 | 0.00015799 | No
25/07/2019 | 07:28 | MTN21 | Urban | Asset Failure | LV | 1 | 369.8 | 0.00058417 | 0.00015799 | No
25/07/2019 | 12:25 | CRM34 | Urban | Overloads |  | 11 | 79.4 | 0.0013655 | 0.0017205 | No
25/07/2019 | 13:39 | SR20 | Urban | Asset Failure | LV | 1 | 465.8 | 0.00073594 | 0.00015799 | No
25/07/2019 | 15:43 | FSH34 | Urban | Vegetation | Grow-in - Other responsible party | 3 | 112 | 0.000499 | 0.00044553 | No
25/07/2019 | 19:29 | CRM12 | Urban | Asset Failure | LV | 1 | 80.7 | 0.00012747 | 0.00015799 | No
25/07/2019 | 19:32 | CRM12 | Urban | Asset Failure | LV | 1 | 77.6 | 0.00012257 | 0.00015799 | No
26/07/2019 | 07:26 | SV32 | Urban | Asset Failure | LV | 1 | 49 | 7.7415e-05 | 0.00015799 | No
26/07/2019 | 08:20 | LWN21 | Rural Short | Asset Failure | LV | 1 | 113 | 0.0019001 | 0.0016815 | No
26/07/2019 | 09:08 | CRM14 | Urban | Asset Failure | LV | 1 | 141.1 | 0.00026305 | 0.00018643 | No
26/07/2019 | 10:06 | NW13 | Urban | Asset Failure | LV | 1 | 84 | 0.00013271 | 0.00015799 | No
26/07/2019 | 13:22 | FTN21 | Urban | Unknown | Unknown | 9 | 322.2 | 0.0047031 | 0.0014598 | No
26/07/2019 | 20:32 | MR13 | Urban | Asset Failure | LV | 1 | 73 | 0.00011533 | 0.00015799 | No
27/07/2019 | 03:10 | M35 | Urban | Asset Failure | LV | 20 | 95 | 0.0030213 | 0.0031803 | No
27/07/2019 | 17:32 | NB26 | Urban | Asset Failure | LV | 1 | 118 | 0.00018643 | 0.00015799 | No
28/07/2019 | 03:01 | EM10 | Urban | Asset Failure | LV | 1 | 238.4 | 0.0003767 | 0.00015799 | No
28/07/2019 | 03:48 | GW3 | Urban | Asset Failure | LV | 1 | 222 | 0.00035074 | 0.00015799 | No
28/07/2019 | 06:09 | HGS33 | Rural Short | Unknown | Unknown | 3 | 85.4 | 0.0043097 | 0.0050445 | No
28/07/2019 | 07:37 | WD34 | Urban | Asset Failure | LV | 17 | 803 | 0.022189 | 0.0027632 | No
28/07/2019 | 10:38 | LD4 | Urban | Asset Failure | LV | 30 | 112 | 0.0052554 | 0.0046923 | No
28/07/2019 | 11:36 | GW8 | Urban | Asset Failure | LV | 1 | 112.2 | 0.00017726 | 0.00015799 | No
28/07/2019 | 11:47 | STO21 | Rural Short | Unknown | Unknown | 104 | 120.4 | 0.21049 | 0.17488 | No
28/07/2019 | 13:51 | NW31 | Urban | Asset Failure | LV | 1 | 133.3 | 0.00021055 | 0.00015799 | No
28/07/2019 | 15:04 | EL10 | Urban | Asset Failure | LV | 1 | 155.9 | 0.00024636 | 0.00015799 | No
28/07/2019 | 16:02 | LWN35 | Urban | Third Party | Vehicle Impact | 146 | 240 | 0.05536 | 0.023067 | No
28/07/2019 | 17:30 | CRM12 | Urban | Asset Failure | LV | 1 | 135 | 0.00021329 | 0.00015799 | No
28/07/2019 | 18:21 | BT14 | Urban | Overloads |  | 61 | 89.8 | 0.008656 | 0.0096374 | No
28/07/2019 | 20:01 | BT6 | Urban | Overloads |  | 17 | 24.7 | 0.00065677 | 0.002659 | No
28/07/2019 | 20:08 | BT14 | Urban | Overloads |  | 1 | 31.9 | 5.032e-05 | 0.00015799 | No
28/07/2019 | 21:05 | DMA15 | Rural Short | Unknown | Unknown | 1 | 85 | 0.0014293 | 0.0016815 | No
29/07/2019 | 10:29 | DMA24 | Rural Short | Asset Failure | LV | 15 | 118.2 | 0.029519 | 0.02497 | No
29/07/2019 | 19:18 | CRM35 | Urban | Asset Failure | LV | 109 | 62 | 0.010677 | 0.017221 | No
29/07/2019 | 19:36 | HGS22 | Rural Short | Asset Failure | Distribution substation | 5 | 69 | 0.0058011 | 0.0084075 | No
30/07/2019 | 07:58 | EW2 | Urban | Planned |  | 1 | 97 | 0.00015322 | 0.00015799 | No
30/07/2019 | 08:52 | FSH12 | Rural Short | Asset Failure | LV | 3 | 117.1 | 0.0059079 | 0.0050445 | No
30/07/2019 | 13:27 | NP16 | Urban | Third Party | Other | 1 | 154 | 0.0002433 | 0.00015799 | No
30/07/2019 | 18:56 | DC7 | Urban | Asset Failure | LV | 1 | 63.8 | 0.00010074 | 0.00015799 | No
30/07/2019 | 18:59 | MR11 | Urban | Asset Failure | LV | 1 | 119.5 | 0.00018875 | 0.00015799 | No
30/07/2019 | 20:11 | LWN21 | Rural Short | Asset Failure | HV | 2 | 93.9 | 0.0031584 | 0.003363 | No
31/07/2019 | 02:01 | MGE13 | Urban | Asset Failure | LV | 9 | 49 | 0.00071532 | 0.0014598 | No
31/07/2019 | 04:31 | HGS22 | Rural Short | Unknown | Unknown | 3 | 416.5 | 0.021009 | 0.0050445 | No
31/07/2019 | 06:51 | LD7 | Urban | Asset Failure | LV | 1 | 134.1 | 0.00021186 | 0.00015799 | No
31/07/2019 | 08:34 | STO14 | Rural Short | Overloads |  | 1 | 236 | 0.0026191 | 0.0011098 | No
31/07/2019 | 09:54 | LWN21 | Rural Short | Asset Failure | LV | 2 | 170.5 | 0.0057344 | 0.003363 | No
31/07/2019 | 09:58 | FTN23 | Urban | Asset Failure | LV | 1 | 391 | 0.00061777 | 0.00015799 | No
31/07/2019 | 10:29 | OAK23 | Urban | Asset Failure | LV | 1 | 61 | 9.6374e-05 | 0.00015799 | No
31/07/2019 | 11:17 | CFD26 | Urban | Asset Failure | LV | 106 | 118 | 0.019687 | 0.016684 | No
31/07/2019 | 12:34 | STO13 | Urban | Asset Failure | LV | 1 | 100.1 | 0.00015817 | 0.00015799 | No
31/07/2019 | 13:30 | OR24 | Urban | Asset Failure | LV | 17 | 15 | 0.00041449 | 0.0027632 | No
31/07/2019 | 14:24 | OR24 | Urban | Asset Failure | LV | 1 | 135.8 | 0.00021447 | 0.00015799 | No
31/07/2019 | 17:04 | M13 | Urban | Asset Failure | LV | 1 | 175.4 | 0.00027704 | 0.00015799 | No
31/07/2019 | 18:31 | LWN21 | Rural Short | Asset Failure | LV | 1 | 1,168.5 | 0.019648 | 0.0016815 | No
31/07/2019 | 18:53 | BT9 | Urban | Overloads |  | 1 | 96.4 | 0.00015228 | 0.00015799 | No
31/07/2019 | 20:01 | SK1 | Urban | Asset Failure | LV | 1 | 148.3 | 0.00023425 | 0.00015799 | No
31/07/2019 | 21:50 | NW13 | Urban | Asset Failure | LV | 14 | 210 | 0.0047776 | 0.0022751 | No
01/08/2019 | 08:59 | OE4 | Urban | Asset Failure | LV | 1 | 91 | 0.00014377 | 0.00015799 | No
01/08/2019 | 09:22 | BT2 | Urban | Network Business | Networ Error | 1 | 157.7 | 0.00024915 | 0.00015799 | No
01/08/2019 | 10:44 | EW14 | Urban | Overloads |  | 4 | 51 | 0.00031908 | 0.00062564 | No
01/08/2019 | 14:03 | OR34 | Urban | Asset Failure | LV | 5 | 127 | 0.00095107 | 0.00074887 | No
01/08/2019 | 17:43 | MTN35 | Rural Short | Asset Failure | LV | 1 | 73.1 | 0.0012295 | 0.0016815 | No
01/08/2019 | 18:54 | RWT12 | Urban | Unknown | Unknown | 572 | 61.9 | 0.055972 | 0.09037 | No
01/08/2019 | 19:21 | SR15 | Urban | Asset Failure | LV | 1 | 54 | 8.5315e-05 | 0.00015799 | No
01/08/2019 | 19:29 | DC10 | Urban | Network Business | Networ Error | 1 | 135.2 | 0.0002136 | 0.00015799 | No
02/08/2019 | 02:24 | EB31 | Urban | Asset Failure | HV | 33 | 216 | 0.011262 | 0.0052137 | No
02/08/2019 | 07:38 | OAK26 | Urban | Asset Failure | LV | 69 | 102 | 0.011061 | 0.010844 | No
02/08/2019 | 07:57 | NP25 | Urban | Asset Failure | LV | 1 | 92.5 | 0.00014614 | 0.00015799 | No
02/08/2019 | 09:12 | RBD12 | Rural Short | Network Business | Networ Error | 1 | 92.3 | 0.0015512 | 0.0016815 | No
02/08/2019 | 13:46 | STO23 | Urban | Asset Failure | LV | 1 | 243.9 | 0.00038529 | 0.00015799 | No
02/08/2019 | 14:38 | BU13 | Urban | Asset Failure | LV | 1 | 232 | 0.00036654 | 0.00015799 | No
02/08/2019 | 17:02 | STO14 | Rural Short | Asset Failure | LV | 1 | 103 | 0.0017319 | 0.0016815 | No
02/08/2019 | 18:07 | BW35 | Urban | Asset Failure | LV | 1 | 143 | 0.00022593 | 0.00015799 | No
02/08/2019 | 18:31 | FSH31 | Urban | Asset Failure | LV | 1 | 229 | 0.00036172 | 0.00015799 | No
02/08/2019 | 18:54 | CFD14 | Urban | Asset Failure | LV | 1 | 202.9 | 0.00032061 | 0.00015799 | No
03/08/2019 | 04:17 | KBH34 | Urban | Third Party | Vehicle Impact | 3 | 33 | 0.00015641 | 0.00047397 | No
03/08/2019 | 09:37 | SVW41 | Urban | Animal | Animal nesting/burrowing, etc and other | 1 | 94.1 | 0.0001487 | 0.00015799 | No
03/08/2019 | 16:01 | EM7 | Urban | Unknown | Unknown | 1 | 47 | 7.4255e-05 | 0.00015799 | No
03/08/2019 | 20:10 | BT4 | Urban | Asset Failure | LV | 1 | 50 | 7.8995e-05 | 0.00015799 | No
03/08/2019 | 20:50 | NW31 | Urban | Asset Failure | LV | 1 | 119.9 | 0.0001894 | 0.00015799 | No
04/08/2019 | 01:07 | EB24 | Urban | Asset Failure | LV | 1 | 43 | 6.7936e-05 | 0.00015799 | No
04/08/2019 | 06:03 | RBD23 | Urban | Asset Failure | LV | 1 | 102 | 0.00016112 | 0.00015799 | No
04/08/2019 | 15:05 | CRM35 | Urban | Unknown | Unknown | 1 | 159.6 | 0.00025218 | 0.00015799 | No
04/08/2019 | 17:32 | RBD14 | Urban | Third Party | Other | 1 | 87.5 | 0.00013827 | 0.00015799 | No
05/08/2019 | 00:21 | NW14 | Urban | Third Party | Vehicle Impact | 56 | 309 | 0.027339 | 0.0088474 | No
05/08/2019 | 00:21 | NW14 | Urban | Third Party | Vehicle Impact | 14 | 308.3 | 0.0068181 | 0.0022119 | No
05/08/2019 | 05:23 | DMA15 | Rural Short | Animal | Animal impact | 316 | 74 | 0.39311 | 0.53135 | No
05/08/2019 | 08:25 | HGS21 | Rural Short | Unknown | Unknown | 494 | 118 | 0.98018 | 0.83066 | No
05/08/2019 | 09:42 | MGE24 | Urban | Unknown | Unknown | 1 | 105.5 | 0.00016665 | 0.00015799 | No
05/08/2019 | 09:57 | CRM22 | Urban | Third Party | Vehicle Impact | 1 | 92.2 | 0.00014559 | 0.00015799 | No
05/08/2019 | 10:21 | BR10 | Urban | Asset Failure | LV | 1 | 480 | 0.00075835 | 0.00015799 | No
05/08/2019 | 15:05 | DC2 | Urban | Third Party | Vehicle Impact | 20 | 374.4 | 0.011829 | 0.0031598 | No
05/08/2019 | 19:38 | EW1 | Urban | Asset Failure | LV | 1 | 117 | 0.00018485 | 0.00015799 | No
05/08/2019 | 21:11 | DC5 | Urban | Asset Failure | LV | 1 | 63 | 9.9534e-05 | 0.00015799 | No
05/08/2019 | 23:05 | KBH33 | Urban | Asset Failure | HV | 1 | 165 | 0.00026068 | 0.00015799 | No
06/08/2019 | 04:57 | DMA21 | Urban | Weather |  | 5 | 138 | 0.0011512 | 0.00083419 | No
06/08/2019 | 09:40 | RWT12 | Urban | Asset Failure | LV | 2 | 37 | 0.00012276 | 0.00033178 | No
06/08/2019 | 09:42 | HGS23 | Rural Short | Overloads |  | 3 | 232.4 | 0.011605 | 0.004994 | No
06/08/2019 | 09:58 | MC10 | Urban | Asset Failure | HV | 417 | 2.3 | 0.0015153 | 0.065882 | No
06/08/2019 | 18:26 | OR35 | Urban | Asset Failure | LV | 27 | 51 | 0.0022069 | 0.0043273 | No
06/08/2019 | 20:03 | BH11 | Urban | Asset Failure | LV | 2 | 27 | 7.0384e-05 | 0.00026068 | No
06/08/2019 | 20:19 | MTN32 | Rural Short | Unknown | Unknown | 45 | 76 | 0.057507 | 0.075667 | No
07/08/2019 | 06:59 | FSH32 | Rural Short | Asset Failure | LV | 1 | 76 | 0.0012771 | 0.0016815 | No
07/08/2019 | 13:19 | NW13 | Urban | Asset Failure | LV | 1 | 51 | 8.0575e-05 | 0.00015799 | No
07/08/2019 | 20:12 | DC7 | Urban | Asset Failure | LV | 1 | 142.6 | 0.00022521 | 0.00015799 | No
07/08/2019 | 20:19 | FSH11 | Urban | Asset Failure | LV | 1 | 116 | 0.00018327 | 0.00015799 | No
07/08/2019 | 20:23 | CRM14 | Urban | Asset Failure | LV | 1 | 159.4 | 0.00025178 | 0.00015799 | No
07/08/2019 | 20:24 | HGS33 | Rural Short | Asset Failure | LV | 1 | 201 | 0.0033798 | 0.0016815 | No
07/08/2019 | 23:03 | KBH32 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 139.7 | 0.00022076 | 0.00015799 | No
08/08/2019 | 00:57 | NB35 | Urban | Asset Failure | HV | 1,510 | 10.8 | 0.025807 | 0.23856 | No
08/08/2019 | 02:13 | HGS22 | Rural Short | Animal | Animal nesting/burrowing, etc and other | 4 | 610 | 0.041028 | 0.006726 | No
08/08/2019 | 02:35 | OAK35 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 10 | 98 | 0.0015483 | 0.0015799 | No
08/08/2019 | 02:41 | MTN31 | Urban | Asset Failure | LV | 14 | 318 | 0.0067979 | 0.0021376 | No
08/08/2019 | 04:54 | CRM22 | Urban | Asset Failure | LV | 15 | 851 | 0.019966 | 0.0023461 | No
08/08/2019 | 07:20 | NB26 | Urban | Overloads |  | 6 | 80 | 0.00070906 | 0.00088632 | No
08/08/2019 | 08:03 | DN4 | Urban | Overloads |  | 1 | 191.9 | 0.00030321 | 0.00015799 | No
08/08/2019 | 08:48 | MR12 | Urban | Unknown | Unknown | 1 | 72 | 0.00011375 | 0.00015799 | No
08/08/2019 | 10:49 | MR15 | Urban | Other | XXX | 1 | 160.3 | 0.00025326 | 0.00015799 | No
08/08/2019 | 10:54 | MTN35 | Rural Short | Overloads |  | 1 | 155.9 | 0.0026209 | 0.0016815 | No
08/08/2019 | 13:21 | RWT34 | Urban | Asset Failure | LV | 1 | 358.3 | 0.000566 | 0.00015799 | No
08/08/2019 | 14:42 | NO7 | Urban | Planned |  | 69 | 163.8 | 0.017856 | 0.010901 | No
08/08/2019 | 17:16 | FTN12 | Urban | Third Party | Other | 1 | 118.3 | 0.00018688 | 0.00015799 | No
08/08/2019 | 18:06 | RBD13 | Urban | Asset Failure | LV | 13 | 49 | 0.0010219 | 0.0020855 | No
08/08/2019 | 20:07 | SVW54 | Urban | Asset Failure | LV | 1 | 128 | 0.00020223 | 0.00015799 | No
08/08/2019 | 21:12 | RWT24 | Urban | Asset Failure | LV | 1 | 93 | 0.00014693 | 0.00015799 | No
08/08/2019 | 22:31 | DMA24 | Rural Short | Vegetation | Grow-in - NSP responsibility | 60 | 299 | 0.30166 | 0.10089 | No
09/08/2019 | 03:04 | SR24 | Urban | Vegetation | Grow-in - Other responsible party | 1,630 | 49.7 | 0.12808 | 0.25752 | No
09/08/2019 | 04:29 | MTN22 | Rural Short | Weather |  | 413 | 116.9 | 0.81182 | 0.69446 | No
09/08/2019 | 05:41 | MC1 | Urban | Asset Failure | HV | 776 | 31.1 | 0.038169 | 0.1226 | No
09/08/2019 | 05:42 | MC1 | Urban | Asset Failure | HV | 1,485 | 63.4 | 0.14866 | 0.23461 | No
09/08/2019 | 05:42 | CRM12 | Urban | Asset Failure | HV | 1,528 | 22.8 | 0.055122 | 0.24141 | No
09/08/2019 | 05:42 | CRM22 | Urban | Asset Failure | HV | 2,281 | 22.8 | 0.082285 | 0.36037 | No
09/08/2019 | 06:44 | MC1 | Urban | Asset Failure | HV | 399 | 37.2 | 0.023419 | 0 | No
09/08/2019 | 06:58 | DC12 | Urban | Vegetation | Grow-in - Other responsible party | 72 | 179 | 0.020362 | 0.011375 | No
09/08/2019 | 07:03 | DC2 | Urban | Asset Failure | LV | 65 | 246.2 | 0.02528 | 0.010269 | No
09/08/2019 | 07:11 | MGE31 | Urban | Asset Failure | LV | 1 | 124 | 0.00019591 | 0.00015799 | No
09/08/2019 | 07:14 | FSH33 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 105.3 | 0.00016634 | 0.00015799 | No
09/08/2019 | 07:43 | RBD11 | Urban | Vegetation | Grow-in - Other responsible party | 137 | 312 | 0.067531 | 0.021645 | No
09/08/2019 | 07:59 | HGS33 | Rural Short | Asset Failure | LV | 1 | 386 | 0.0064906 | 0.0016815 | No
09/08/2019 | 08:04 | STO21 | Rural Short | Asset Failure | Distribution substation | 12 | 594.9 | 0.12004 | 0.020178 | No
09/08/2019 | 08:08 | RBD21 | Rural Short | Weather |  | 88 | 130 | 0.19236 | 0.14797 | No
09/08/2019 | 08:17 | DMA24 | Rural Short | Weather |  | 1,970 | 20.8 | 0.6891 | 3.3125 | No
09/08/2019 | 08:19 | DMA14 | Urban | Vegetation | Grow-in - Other responsible party | 4 | 401 | 0.0023061 | 0.00057508 | No
09/08/2019 | 08:40 | MTN32 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 417.8 | 0.007025 | 0.0016815 | No
09/08/2019 | 08:45 | FSH12 | Rural Short | Asset Failure | LV | 1 | 344.9 | 0.0057989 | 0.0016815 | No
09/08/2019 | 08:51 | MTN32 | Rural Short | Weather |  | 2,848 | 34.2 | 1.6398 | 4.7889 | No
09/08/2019 | 08:55 | MTN32 | Rural Short | Weather |  | 10 | 592.9 | 0.099687 | 0 | No
09/08/2019 | 08:56 | STO14 | Rural Short | Asset Failure | HV | 253 | 664 | 2.8248 | 0.42542 | No
09/08/2019 | 09:03 | EL10 | Urban | Asset Failure | LV | 1 | 499 | 0.00078837 | 0.00015799 | No
09/08/2019 | 09:03 | DMA24 | Rural Short |  | HV | 161 | 10.2 | 0.027704 | 0.27072 | No
09/08/2019 | 09:03 | MTN24 | Rural Short |  | HV | 2,950 | 13.2 | 0.65644 | 4.9604 | No
09/08/2019 | 09:04 | MTN32 | Rural Short | Weather |  | 658 | 25.9 | 0.28603 | 0 | No
09/08/2019 | 09:07 | MC1 | Urban | Asset Failure | LV | 1 | 635 | 0.0010032 | 0.00015799 | No
09/08/2019 | 09:17 | LWN33 | Urban | Unknown | Unknown | 1 | 547 | 0.00086421 | 0.00015799 | No
09/08/2019 | 09:30 | DMA24 | Rural Short | Weather |  | 69 | 82.9 | 0.096222 | 0.11602 | No
09/08/2019 | 10:06 | DC10 | Urban | Third Party | Other | 1 | 117.2 | 0.00018511 | 0.00015799 | No
09/08/2019 | 10:09 | STO23 | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 348.6 | 0.0011016 | 0.00031598 | No
09/08/2019 | 10:11 | MTN21 | Urban | Asset Failure | LV | 1 | 259 | 0.00040919 | 0.00015799 | No
09/08/2019 | 10:14 | NW14 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 105.8 | 0.00016721 | 0.00015799 | No
09/08/2019 | 10:16 | MTN31 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 207 | 0.00032704 | 0.00015799 | No
09/08/2019 | 10:41 | LWN21 | Rural Short | Weather |  | 1 | 1,312.0 | 0.022061 | 0.0016815 | No
09/08/2019 | 11:23 | MTN22 | Rural Short | Weather |  | 804 | 18 | 0.24358 | 1.3519 | No
09/08/2019 | 11:38 | DMA23 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 217 | 0.0036488 | 0.0016815 | No
09/08/2019 | 13:20 | HGS21 | Rural Short | Overloads |  | 33 | 15 | 0.0084066 | 0.056044 | No
09/08/2019 | 13:28 | BH23 | Urban | Asset Failure | LV | 10 | 52 | 0.00078622 | 0.001512 | No
09/08/2019 | 13:29 | BR9 | Urban | Asset Failure | LV | 1 | 185.9 | 0.00029362 | 0.00015799 | No
09/08/2019 | 13:55 | RBD13 | Urban | Weather |  | 1 | 115.3 | 6.0096e-05 | 5.2137e-05 | No
09/08/2019 | 14:03 | LWN21 | Rural Short |  | Other | 1 | 339 | 0.0057003 | 0.0016815 | No
09/08/2019 | 14:05 | MR12 | Urban | Vegetation | Grow-in - Other responsible party | 26 | 320 | 0.013347 | 0.0041709 | No
09/08/2019 | 14:46 | MTN32 | Rural Short | Asset Failure | Distribution substation | 1 | 123.6 | 0.0020786 | 0.0016815 | No
09/08/2019 | 16:16 | MC10 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 363.7 | 0.00057453 | 0.00015799 | No
09/08/2019 | 17:47 | MTN34 | Urban | Asset Failure | LV | 1 | 133 | 0.00021013 | 0.00015799 | No
09/08/2019 | 17:55 | RBD23 | Urban | Asset Failure | LV | 23 | 145 | 0.0053675 | 0.0037017 | No
09/08/2019 | 18:13 | CM22 | Urban | Overloads |  | 1 | 108 | 0.00017063 | 0.00015799 | No
09/08/2019 | 19:37 | MTN31 | Urban | Asset Failure | LV | 1 | 103 | 0.00016273 | 0.00015799 | No
09/08/2019 | 20:04 | MC1 | Urban | Overloads |  | 2 | 55.9 | 0.00017658 | 0.00031598 | No
09/08/2019 | 20:48 | STO21 | Rural Short | Asset Failure | LV | 1 | 332 | 0.0055826 | 0.0016815 | No
10/08/2019 | 08:45 | STO14 | Rural Short | Vegetation | Grow-in - Other responsible party | 46 | 10 | 0.0077349 | 0.077349 | No
10/08/2019 | 10:00 | EW12 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 155 | 0.00034284 | 0.00022119 | No
10/08/2019 | 10:27 | HGS33 | Rural Short | Asset Failure | LV | 3 | 258 | 0.013015 | 0.0050445 | No
10/08/2019 | 11:48 | CFD24 | Urban | Asset Failure | LV | 5 | 97 | 0.00074173 | 0.00076467 | No
10/08/2019 | 12:49 | DMA14 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 75.2 | 0.00011886 | 0.00015799 | No
10/08/2019 | 12:50 | MTN22 | Rural Short | Asset Failure | LV | 1 | 309.9 | 0.0052101 | 0.0016815 | No
10/08/2019 | 13:53 | STO14 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 96.2 | 0.0016179 | 0.0016815 | No
10/08/2019 | 14:24 | OAK26 | Urban | Asset Failure | LV | 1 | 95 | 0.00015009 | 0.00015799 | No
10/08/2019 | 14:44 | CFD24 | Urban | Asset Failure | LV | 1 | 141 | 0.00022274 | 0.00015799 | No
10/08/2019 | 16:35 | FTN11 | Urban | Asset Failure | LV | 1 | 125 | 0.00019749 | 0.00015799 | No
10/08/2019 | 17:11 | NO7 | Urban | Asset Failure | LV | 45 | 196.1 | 0.014006 | 0.0071427 | No
10/08/2019 | 17:57 | EB31 | Urban | Asset Failure | LV | 1 | 171.8 | 0.00027137 | 0.00015799 | No
10/08/2019 | 20:16 | RBD13 | Urban | Asset Failure | LV | 1 | 193 | 0.00030495 | 0.00015799 | No
11/08/2019 | 04:22 | DMA23 | Rural Short | Unknown | Unknown | 3 | 258 | 0.013015 | 0.0050445 | No
11/08/2019 | 09:15 | DN22 | Urban | Asset Failure | LV | 6 | 45 | 0.00041235 | 0.00091634 | No
11/08/2019 | 09:21 | STO21 | Rural Short | Asset Failure | LV | 86 | 179 | 0.25885 | 0.14461 | No
11/08/2019 | 10:43 | MGE32 | Urban | Overloads |  | 1 | 182 | 0.00028754 | 0.00015799 | No
11/08/2019 | 13:49 | LD7 | Urban | Unknown | Unknown | 1 | 110.1 | 0.00017389 | 0.00015799 | No
11/08/2019 | 13:51 | NP33 | Urban | Overloads |  | 1 | 139 | 0.00021961 | 0.00015799 | No
11/08/2019 | 15:08 | STO22 | Urban | Asset Failure | LV | 1 | 171.2 | 0.00027043 | 0.00015799 | No
11/08/2019 | 15:15 | EW8 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 149.7 | 0.00023643 | 0.00015799 | No
11/08/2019 | 15:46 | DMA14 | Urban | Overloads |  | 1 | 219 | 0.000346 | 0.00015799 | No
11/08/2019 | 16:49 | FSH22 | Urban | Asset Failure | LV | 1 | 160.2 | 0.00025305 | 0.00015799 | No
11/08/2019 | 17:08 | LD2 | Urban | Asset Failure | LV | 78 | 302 | 0.037216 | 0.012323 | No
11/08/2019 | 17:50 | DMA12 | Urban | Overloads |  | 1 | 175 | 0.00027648 | 0.00015799 | No
11/08/2019 | 18:24 | M13 | Urban | Overloads |  | 1 | 69 | 0.00010901 | 0.00015799 | No
11/08/2019 | 18:44 | CRM22 | Urban | Asset Failure | LV | 1 | 275.4 | 0.00043503 | 0.00015799 | No
11/08/2019 | 19:41 | HGS33 | Rural Short | Vegetation | Grow-in - NSP responsibility | 15 | 129 | 0.032537 | 0.025222 | No
11/08/2019 | 20:48 | FSH13 | Urban | Overloads |  | 1 | 146.1 | 0.00023088 | 0.00015799 | No
11/08/2019 | 21:04 | FSH21 | Rural Short | Asset Failure | LV | 15 | 56 | 0.014125 | 0.025222 | No
11/08/2019 | 22:41 | MTN34 | Urban | Asset Failure | LV | 1 | 93 | 0.00014698 | 0.00015799 | No
11/08/2019 | 23:36 | DC8 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 173.4 | 0.00027387 | 0.00015799 | No
12/08/2019 | 00:56 | MTN24 | Rural Short | Asset Failure | HV | 25 | 409 | 0.17193 | 0.042037 | No
12/08/2019 | 00:58 | FSH21 | Rural Short | Asset Failure | LV | 15 | 62 | 0.015638 | 0.025222 | No
12/08/2019 | 05:22 | FSH21 | Rural Short | Overloads |  | 15 | 278 | 0.070118 | 0.025222 | No
12/08/2019 | 09:09 | NW13 | Urban | Unknown | Unknown | 5 | 50.4 | 0.00042057 | 0.00083419 | No
12/08/2019 | 10:21 | GW8 | Urban | Asset Failure | LV | 1 | 263.3 | 0.00041591 | 0.00015799 | No
12/08/2019 | 10:31 | FTN23 | Urban | Asset Failure | Distribution substation | 1 | 29 | 4.5817e-05 | 0.00015799 | No
12/08/2019 | 11:52 | NW13 | Urban | Asset Failure | LV | 16 | 807.4 | 0.02041 | 0.0025278 | No
12/08/2019 | 12:05 | DMA23 | Rural Short | Asset Failure | LV | 1 | 114.9 | 0.0019326 | 0.0016815 | No
12/08/2019 | 13:10 | FTN11 | Urban | Asset Failure | LV | 1 | 270 | 0.00042657 | 0.00015799 | No
12/08/2019 | 13:14 | MTN22 | Rural Short | Vegetation | Grow-in - NSP responsibility | 9 | 179.7 | 0.026314 | 0.014646 | No
12/08/2019 | 16:58 | GW8 | Urban | Third Party | Other | 1 | 77 | 0.00012165 | 0.00015799 | No
13/08/2019 | 07:41 | OAK26 | Urban | Asset Failure | LV | 1 | 94 | 0.00014851 | 0.00015799 | No
13/08/2019 | 09:07 | SV16 | Urban | Asset Failure | LV | 1 | 79 | 0.00012481 | 0.00015799 | No
13/08/2019 | 09:40 | FSH32 | Rural Short | Asset Failure | Distribution substation | 1 | 152 | 0.0025303 | 0.0016647 | No
13/08/2019 | 10:00 | BH23 | Urban | Asset Failure | LV | 1 | 60 | 9.4794e-05 | 0.00015799 | No
13/08/2019 | 12:30 | MTN32 | Rural Short | Asset Failure | LV | 1 | 134.9 | 0.0022681 | 0.0016815 | No
13/08/2019 | 13:28 | FSH34 | Urban | Planned |  | 1 | 68.9 | 0.00010886 | 0.00015799 | No
13/08/2019 | 15:16 | OAK23 | Urban | Asset Failure | LV | 1 | 311.7 | 0.00049237 | 0.00015799 | No
13/08/2019 | 16:23 | DC8 | Urban | Unknown | Unknown | 1 | 29.7 | 4.6844e-05 | 0.00015799 | No
13/08/2019 | 18:41 | FTN13 | Urban | Asset Failure | LV | 1 | 175.4 | 0.00027706 | 0.00015799 | No
13/08/2019 | 19:29 | EM3 | Urban | Asset Failure | Distribution substation | 31 | 81 | 0.0039275 | 0.0048487 | No
14/08/2019 | 08:07 | LWN21 | Rural Short | Overloads |  | 1 | 107.3 | 0.00045092 | 0.00042037 | No
14/08/2019 | 09:28 | SR24 | Urban | Unknown | Unknown | 1 | 151.8 | 0.00023985 | 0.00015799 | No
14/08/2019 | 12:02 | NW14 | Urban | Asset Failure | LV | 1 | 132.5 | 0.00020928 | 0.00015799 | No
14/08/2019 | 14:25 | NP16 | Urban | Asset Failure | LV | 1 | 134.5 | 0.0002125 | 0.00015799 | No
14/08/2019 | 15:28 | CFD15 | Urban | Other | XXX | 1 | 91.2 | 0.00014406 | 0.00015799 | No
14/08/2019 | 16:53 | DN7 | Urban | Asset Failure | LV | 1 | 321.5 | 0.00050786 | 0.00015799 | No
14/08/2019 | 18:42 | BU6 | Urban | Animal | Other | 15 | 114 | 0.0026152 | 0.002294 | No
14/08/2019 | 22:29 | NP36 | Urban | Asset Failure | LV | 1 | 85 | 0.00013429 | 0.00015799 | No
15/08/2019 | 07:17 | MC4 | Urban | Asset Failure | LV | 1 | 112.8 | 0.00017813 | 0.00015799 | No
15/08/2019 | 13:05 | LWN35 | Urban | Asset Failure | LV | 1 | 99.9 | 0.00015775 | 0.00015799 | No
15/08/2019 | 13:27 | BH21 | Urban | Vegetation | Grow-in - NSP responsibility | 2,368 | 65.8 | 0.24623 | 0.37412 | No
15/08/2019 | 13:39 | CRM24 | Urban | Asset Failure | LV | 1 | 170.6 | 0.0002695 | 0.00015799 | No
15/08/2019 | 14:44 | HT8 | Urban | Asset Failure | LV | 2 | 180.9 | 0.00047158 | 0.00026068 | No
15/08/2019 | 14:48 | MTN21 | Urban | Asset Failure | HV | 87 | 101.9 | 0.014004 | 0.013745 | No
15/08/2019 | 16:37 | MTN22 | Rural Short | Asset Failure | LV | 1 | 282 | 0.0047421 | 0.0016815 | No
15/08/2019 | 17:12 | STO22 | Urban | Asset Failure | LV | 1 | 118 | 0.00018643 | 0.00015799 | No
15/08/2019 | 20:36 | HT11 | Urban | Asset Failure | LV | 1 | 58.1 | 9.1845e-05 | 0.00015799 | No
16/08/2019 | 04:45 | DC3 | Urban | Asset Failure | HV | 34 | 135 | 0.0072517 | 0.0053717 | No
16/08/2019 | 09:08 | CRM21 | Urban | Asset Failure | LV | 1 | 141.7 | 0.00022382 | 0.00015799 | No
16/08/2019 | 09:19 | RBD21 | Rural Short | Asset Failure | LV | 1 | 266.9 | 0.0044871 | 0.0016815 | No
16/08/2019 | 11:31 | EW14 | Urban | Asset Failure | LV | 12 | 1,216.9 | 0.023071 | 0.0018959 | No
16/08/2019 | 12:35 | MR21 | Urban | Asset Failure | LV | 1 | 338 | 0.00053401 | 0.00015799 | No
16/08/2019 | 14:16 | STO21 | Rural Short |  | Distribution substation | 2 | 74 | 0.0024886 | 0.003363 | No
16/08/2019 | 14:53 | NB32 | Urban | Asset Failure | HV | 615 | 51 | 0.049576 | 0.097164 | No
16/08/2019 | 15:23 | EB22 | Urban | Network Business | Networ Error | 14 | 46.3 | 0.0010372 | 0.0022419 | No
16/08/2019 | 15:25 | CRM21 | Urban | Asset Failure | LV | 1 | 119.3 | 0.00018848 | 0.00015799 | No
16/08/2019 | 18:38 | HGS21 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 106.2 | 0.001786 | 0.0016815 | No
17/08/2019 | 08:32 | DMA15 | Rural Short | Asset Failure | LV | 40 | 193 | 0.12981 | 0.06726 | No
17/08/2019 | 10:11 | EB32 | Urban | Overloads |  | 1 | 109 | 0.00017221 | 0.00015799 | No
17/08/2019 | 10:53 | DC3 | Urban | Overloads |  | 1 | 187 | 0.00029544 | 0.00015799 | No
17/08/2019 | 11:24 | DC4 | Urban | Asset Failure | LV | 1 | 96 | 0.00015167 | 0.00015799 | No
17/08/2019 | 14:30 | EM8 | Urban | Overloads |  | 1 | 105 | 0.00016589 | 0.00015799 | No
17/08/2019 | 20:02 | BH23 | Urban | Overloads |  | 1 | 58 | 9.1634e-05 | 0.00015799 | No
17/08/2019 | 20:06 | MTN32 | Rural Short | Overloads |  | 1 | 84 | 0.0014125 | 0.0016815 | No
17/08/2019 | 21:30 | DMA12 | Urban | Unknown | Unknown | 30 | 1,550.0 | 0.073467 | 0.0047397 | No
18/08/2019 | 08:04 | SR19 | Urban | Overloads |  | 1 | 131 | 0.00020697 | 0.00015799 | No
18/08/2019 | 09:36 | BU9 | Urban | Vegetation | Grow-in - Other responsible party | 24 | 404 | 0.015319 | 0.0037918 | No
18/08/2019 | 10:22 | LD33 | Urban | Vegetation | Grow-in - Other responsible party | 56 | 666.2 | 0.058945 | 0.0088474 | No
18/08/2019 | 11:15 | NW23 | Urban | Unknown | Unknown | 1 | 145 | 0.00022908 | 0.00015799 | No
18/08/2019 | 11:19 | BH23 | Urban | Asset Failure | LV | 1 | 186 | 0.00029386 | 0.00015799 | No
18/08/2019 | 13:30 | M25 | Urban | Unknown | Unknown | 1 | 90 | 0.00014219 | 0.00015799 | No
18/08/2019 | 14:53 | STO21 | Rural Short | Asset Failure | LV | 1 | 132 | 0.0022196 | 0.0016815 | No
18/08/2019 | 15:11 | FSH12 | Rural Short | Overloads |  | 1 | 259 | 0.0043551 | 0.0016815 | No
18/08/2019 | 16:05 | FTN12 | Urban | Asset Failure | HV | 33 | 534.4 | 0.028141 | 0.0052658 | No
18/08/2019 | 18:15 | LD2 | Urban | Unknown | Unknown | 38 | 267.2 | 0.016042 | 0.0060036 | No
18/08/2019 | 19:30 | LD2 | Urban | Unknown | Unknown | 11 | 221.1 | 0.0038431 | 0.0017379 | No
18/08/2019 | 21:22 | FTN21 | Urban | Asset Failure | LV | 1 | 167 | 0.00026384 | 0.00015799 | No
18/08/2019 | 22:13 | FSH21 | Rural Short | Unknown | Unknown | 15 | 192 | 0.048427 | 0.025222 | No
18/08/2019 | 23:17 | LD2 | Urban | Asset Failure | LV | 27 | 507.8 | 0.021659 | 0.0042657 | No
18/08/2019 | 23:30 | MTN32 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 97.4 | 0.0016369 | 0.0016815 | No
19/08/2019 | 04:44 | BR13 | Urban | Asset Failure | LV | 1 | 160.4 | 0.00025344 | 0.00015799 | No
19/08/2019 | 09:38 | LD6 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 174.3 | 0.00027543 | 0.00015799 | No
19/08/2019 | 09:55 | GW11 | Urban | Asset Failure | LV | 1 | 185 | 0.00029228 | 0.00015799 | No
19/08/2019 | 10:43 | HGS33 | Rural Short | Asset Failure | LV | 1 | 217.4 | 0.0036558 | 0.0016815 | No
19/08/2019 | 12:20 | LD7 | Urban | Asset Failure | LV | 1 | 59.7 | 9.4241e-05 | 0.00015799 | No
19/08/2019 | 13:42 | HGS21 | Rural Short | Asset Failure | LV | 1 | 288 | 0.0048427 | 0.0016815 | No
19/08/2019 | 14:45 | GW11 | Urban | Asset Failure | LV | 1 | 134 | 0.00021171 | 0.00015799 | No
19/08/2019 | 17:46 | MR15 | Urban | Asset Failure | LV | 1 | 58.2 | 9.1924e-05 | 0.00015799 | No
19/08/2019 | 19:23 | OR34 | Urban | Overloads |  | 1 | 42 | 6.6356e-05 | 0.00015799 | No
19/08/2019 | 23:15 | DMA14 | Urban | Unknown | Unknown | 1 | 85 | 0.00013429 | 0.00015799 | No
20/08/2019 | 08:06 | DMA14 | Urban | Vegetation | Grow-in - NSP responsibility | 17 | 363.9 | 0.0096764 | 0.002659 | No
20/08/2019 | 08:09 | DC3 | Urban | Unknown | Unknown | 16 | 101 | 0.0025802 | 0.0025547 | No
20/08/2019 | 08:31 | DVY34 | Urban | Asset Failure | LV | 1 | 114.3 | 0.0001805 | 0.00015799 | No
20/08/2019 | 10:16 | DC3 | Urban | Unknown | Unknown | 1 | 89 | 0.00014061 | 0.00015799 | No
20/08/2019 | 12:06 | MR24 | Urban | Asset Failure | LV | 1 | 109.5 | 0.00017295 | 0.00015799 | No
20/08/2019 | 12:31 | NB32 | Urban | Third Party | Vehicle Impact | 96 | 104 | 0.015774 | 0.015167 | No
20/08/2019 | 12:31 | DMA13 | Rural Short | Vegetation | Grow-in - NSP responsibility | 58 | 48.7 | 0.047528 | 0.097527 | No
20/08/2019 | 12:54 | NB22 | Urban | Third Party | Other | 1 | 143.4 | 0.00022648 | 0.00015799 | No
20/08/2019 | 14:08 | STO14 | Rural Short | Asset Failure | LV | 1 | 186.5 | 0.0031357 | 0.0016815 | No
20/08/2019 | 14:52 | DC3 | Urban | Asset Failure | LV | 1 | 144.4 | 0.00022806 | 0.00015799 | No
20/08/2019 | 15:30 | CRM21 | Urban | Asset Failure | LV | 1 | 329.7 | 0.00052092 | 0.00015799 | No
20/08/2019 | 16:46 | GW3 | Urban | Asset Failure | LV | 1 | 193.1 | 0.00030513 | 0.00015799 | No
20/08/2019 | 16:51 | HT1 | Urban | Asset Failure | LV | 1 | 338.2 | 0.00053429 | 0.00015799 | No
20/08/2019 | 17:29 | DC3 | Urban | Asset Failure | LV | 24 | 436 | 0.016532 | 0.0037918 | No
20/08/2019 | 18:55 | EB33 | Urban | Asset Failure | LV | 1 | 319 | 0.00050399 | 0.00015799 | No
20/08/2019 | 22:48 | DC8 | Urban | Asset Failure | HV | 737 | 2.8 | 0.0032991 | 0.11644 | No
20/08/2019 | 23:04 | DC8 | Urban | Asset Failure | HV | 265 | 12.1 | 0.005059 | 0.041867 | No
21/08/2019 | 07:22 | LWN23 | Urban | Asset Failure | LV | 2 | 128 | 0.00040445 | 0.00031598 | No
21/08/2019 | 08:11 | CRM22 | Urban | Asset Failure | LV | 1 | 154 | 0.0002433 | 0.00015799 | No
21/08/2019 | 08:14 | M23 | Urban | Asset Failure | LV | 1 | 145.8 | 0.00023032 | 0.00015799 | No
21/08/2019 | 11:00 | BU10 | Urban | Asset Failure | LV | 1 | 64.3 | 0.00010159 | 0.00015799 | No
21/08/2019 | 11:16 | MR14 | Urban | Asset Failure | LV | 1 | 58.8 | 9.2872e-05 | 0.00015799 | No
21/08/2019 | 15:43 | DC10 | Urban | Asset Failure | LV | 1 | 79.1 | 0.00012492 | 0.00015799 | No
21/08/2019 | 18:38 | CRM35 | Urban | Asset Failure | LV | 4 | 97 | 0.00065438 | 0.00067462 | No
21/08/2019 | 18:45 | EL10 | Urban | Asset Failure | LV | 1 | 103 | 0.00016273 | 0.00015799 | No
21/08/2019 | 19:33 | MGE12 | Urban | Asset Failure | LV | 1 | 80 | 0.00012639 | 0.00015799 | No
21/08/2019 | 19:44 | OR34 | Urban | Asset Failure | LV | 1 | 109 | 0.00017221 | 0.00015799 | No
21/08/2019 | 22:30 | MC1 | Urban | Asset Failure | LV | 42 | 115 | 0.0076309 | 0.0066356 | No
21/08/2019 | 22:47 | DMA15 | Rural Short | Vegetation | Grow-in - NSP responsibility | 109 | 883 | 1.6184 | 0.18328 | No
21/08/2019 | 22:50 | DMA23 | Rural Short | Vegetation | Grow-in - NSP responsibility | 31 | 1,230.0 | 0.64115 | 0.052126 | No
21/08/2019 | 23:17 | STO21 | Rural Short | Asset Failure | HV | 101 | 233 | 0.39571 | 0.16983 | No
22/08/2019 | 00:26 | FSH33 | Urban | Asset Failure | LV | 14 | 124 | 0.0028309 | 0.002283 | No
22/08/2019 | 00:40 | SS23 | Urban | Third Party | Vehicle Impact | 1,214 | 22.5 | 0.043082 | 0.1918 | No
22/08/2019 | 10:48 | RBD22 | Urban | Asset Failure | LV | 16 | 76.5 | 0.0019149 | 0.0025026 | No
22/08/2019 | 12:14 | LD7 | Urban | Asset Failure | LV | 12 | 91 | 0.0016606 | 0.0018248 | No
22/08/2019 | 14:45 | CRM35 | Urban | Asset Failure | LV | 1 | 165 | 0.00026068 | 0.00015799 | No
22/08/2019 | 18:59 | CRM22 | Urban | Asset Failure | LV | 1 | 125.5 | 0.0001982 | 0.00015799 | No
22/08/2019 | 20:10 | CRM22 | Urban | Asset Failure | LV | 1 | 64.1 | 0.00010122 | 0.00015799 | No
23/08/2019 | 13:20 | KBH35 | Urban | Asset Failure | LV | 2 | 115 | 0.00034521 | 0.00030018 | No
23/08/2019 | 13:28 | HGS22 | Rural Short | Unknown | Unknown | 2 | 226.9 | 0.00763 | 0.003363 | No
23/08/2019 | 21:27 | DN11 | Urban | Asset Failure | LV | 1 | 83 | 0.00013113 | 0.00015799 | No
24/08/2019 | 04:56 | DMA15 | Rural Short | Animal | Other | 1 | 243.8 | 0.0040995 | 0.0016815 | No
24/08/2019 | 08:57 | HGS22 | Rural Short | Asset Failure | LV | 1 | 102.5 | 0.0017241 | 0.0016815 | No
24/08/2019 | 14:43 | BT2 | Urban | Asset Failure | LV | 1 | 111.7 | 0.0001764 | 0.00015799 | No
24/08/2019 | 17:50 | BT9 | Urban | Asset Failure | LV | 1 | 190 | 0.00030018 | 0.00015799 | No
24/08/2019 | 18:11 | STO13 | Urban | Asset Failure | LV | 1 | 244 | 0.0003855 | 0.00015799 | No
25/08/2019 | 12:19 | MGE13 | Urban | Asset Failure | LV | 1 | 5,501.0 | 0.008691 | 0.00015799 | No
25/08/2019 | 16:43 | MTN32 | Rural Short | Asset Failure | LV | 1 | 77 | 0.0012945 | 0.0016815 | No
25/08/2019 | 17:11 | FSH31 | Urban | Overloads |  | 1 | 136 | 0.00021487 | 0.00015799 | No
25/08/2019 | 23:20 | NP16 | Urban | Overloads |  | 1 | 100 | 0.00015799 | 0.00015799 | No
26/08/2019 | 06:38 | NW31 | Urban | Asset Failure | LV | 1 | 32 | 5.0557e-05 | 0.00015799 | No
26/08/2019 | 07:09 | OAK23 | Urban | Asset Failure | LV | 1 | 84 | 0.00013271 | 0.00015799 | No
26/08/2019 | 07:11 | HGS32 | Urban | Asset Failure | LV | 1 | 78.7 | 0.00012428 | 0.00015799 | No
26/08/2019 | 09:02 | LD33 | Urban | Asset Failure | LV | 1 | 132.8 | 0.00020978 | 0.00015799 | No
26/08/2019 | 12:20 | SS12 | Urban | Asset Failure | LV | 4 | 369.3 | 0.0023339 | 0.00063196 | No
26/08/2019 | 13:19 | LD4 | Urban | Asset Failure | LV | 1 | 249 | 0.00039339 | 0.00015799 | No
26/08/2019 | 14:04 | NW31 | Urban | Unknown | Unknown | 1 | 85.4 | 0.00013492 | 0.00015799 | No
26/08/2019 | 14:40 | RBD12 | Rural Short | Asset Failure | LV | 1 | 50 | 0.00084075 | 0.0016815 | No
26/08/2019 | 17:20 | NW13 | Urban | Asset Failure | LV | 1 | 95 | 0.00015009 | 0.00015799 | No
26/08/2019 | 17:39 | SS12 | Urban | Asset Failure | LV | 1 | 200 | 0.00031598 | 0.00015799 | No
26/08/2019 | 18:04 | OE4 | Urban | Asset Failure | LV | 1 | 191 | 0.00030176 | 0.00015799 | No
26/08/2019 | 22:37 | NW33 | Urban | Asset Failure | LV | 1 | 219.7 | 0.0003471 | 0.00015799 | No
26/08/2019 | 23:19 | GW7 | Urban | Asset Failure | LV | 25 | 12.2 | 0.00049111 | 0.0040145 | No
27/08/2019 | 07:05 | STO21 | Rural Short | Unknown | Unknown | 2 | 9.1 | 0.00030547 | 0.003363 | No
27/08/2019 | 10:20 | DMA14 | Urban | Asset Failure | LV | 1 | 100 | 0.00015794 | 0.00015799 | No
27/08/2019 | 12:00 | NB35 | Urban | Third Party | Vehicle Impact | 30 | 75 | 0.0035548 | 0.0047397 | No
27/08/2019 | 12:44 | BU1 | Urban | Third Party | Other | 1 | 115.7 | 0.00018285 | 0.00015799 | No
27/08/2019 | 14:44 | BU9 | Urban | Asset Failure | LV | 1 | 64 | 0.00010111 | 0.00015799 | No
27/08/2019 | 20:45 | MGE21 | Urban | Asset Failure | LV | 15 | 150 | 0.0035192 | 0.0023461 | No
27/08/2019 | 20:52 | CDA11 | Urban | Asset Failure | LV | 1 | 157.7 | 0.0002491 | 0.00015799 | No
27/08/2019 | 23:22 | RBD13 | Urban | Asset Failure | LV | 1 | 81 | 0.00012797 | 0.00015799 | No
28/08/2019 | 00:17 | MR23 | Urban | Asset Failure | HV | 104 | 13.6 | 0.0022264 | 0.016431 | No
28/08/2019 | 00:31 | MR23 | Urban | Asset Failure | HV | 15 | 869 | 0.020594 | 0.0023698 | No
28/08/2019 | 00:53 | EB22 | Urban | Asset Failure | LV | 1 | 99 | 0.00015641 | 0.00015799 | No
28/08/2019 | 08:30 | CRM21 | Urban | Asset Failure | LV | 8 | 90 | 0.0010807 | 0.0012007 | No
28/08/2019 | 10:14 | RWT24 | Urban | Asset Failure | LV | 1 | 81 | 0.00012797 | 0.00015799 | No
28/08/2019 | 12:01 | STO13 | Urban | Third Party | Other | 1 | 81 | 0.00012797 | 0.00015799 | No
28/08/2019 | 12:01 | HT3 | Urban | Asset Failure | LV | 1 | 108.7 | 0.00017171 | 0.00015799 | No
28/08/2019 | 12:32 | CRM22 | Urban | Asset Failure | LV | 30 | 203 | 0.0096216 | 0.0047397 | No
28/08/2019 | 12:52 | K6 | Urban | Asset Failure | LV | 1 | 157.8 | 0.00024925 | 0.00015799 | No
28/08/2019 | 12:53 | EM7 | Urban | Asset Failure | LV | 1 | 110.4 | 0.00017437 | 0.00015799 | No
28/08/2019 | 17:02 | DC10 | Urban | Asset Failure | LV | 1 | 148 | 0.00023383 | 0.00015799 | No
28/08/2019 | 19:10 | LWN21 | Rural Short | Asset Failure | LV | 1 | 774 | 0.013015 | 0.0016815 | No
28/08/2019 | 19:14 | CRM33 | Urban | Asset Failure | LV | 2 | 116 | 0.00036654 | 0.00031598 | No
28/08/2019 | 22:30 | BT4 | Urban | Asset Failure | LV | 1 | 90 | 0.00014219 | 0.00015799 | No
28/08/2019 | 23:17 | RWT24 | Urban | Vegetation | Grow-in - Other responsible party | 30 | 169.2 | 0.0080172 | 0.0047397 | No
29/08/2019 | 00:12 | RBD13 | Urban | Asset Failure | LV | 1 | 48 | 7.5835e-05 | 0.00015799 | No
29/08/2019 | 00:45 | SS12 | Urban | Asset Failure | HV | 1 | 45 | 7.1095e-05 | 0.00015799 | No
29/08/2019 | 08:42 | SS13 | Urban | Unknown | Unknown | 1 | 77 | 0.00012165 | 0.00015799 | No
29/08/2019 | 09:20 | OAK23 | Urban | Overloads |  | 1 | 24.4 | 3.8523e-05 | 0.00015799 | No
29/08/2019 | 09:49 | RD10 | Urban | Asset Failure | LV | 1 | 61 | 9.6374e-05 | 0.00015799 | No
29/08/2019 | 11:54 | FTN14 | Urban | Asset Failure | LV | 1 | 485.4 | 0.00076683 | 0.00015799 | No
29/08/2019 | 17:36 | DC7 | Urban | Asset Failure | HV | 118 | 84 | 0.01566 | 0.018643 | No
29/08/2019 | 19:40 | MTN32 | Rural Short | Overloads |  | 1 | 110 | 0.0018496 | 0.0016815 | No
29/08/2019 | 20:13 | EB24 | Urban | Overloads |  | 1 | 16.3 | 2.5726e-05 | 0.00015799 | No
29/08/2019 | 20:38 | FTN11 | Urban | Overloads |  | 1 | 132 | 0.00020855 | 0.00015799 | No
29/08/2019 | 20:40 | BW22 | Urban | Asset Failure | LV | 56 | 400 | 0.03539 | 0.0088474 | No
29/08/2019 | 22:31 | DN22 | Urban | Overloads |  | 1 | 109 | 0.00017221 | 0.00015799 | No
29/08/2019 | 22:51 | EB32 | Urban | Asset Failure | LV | 1 | 159 | 0.0002512 | 0.00015799 | No
30/08/2019 | 08:43 | MTN32 | Rural Short | Other | XXX | 1 | 656.4 | 0.011038 | 0.0016815 | No
30/08/2019 | 09:44 | GW12 | Urban | Asset Failure | LV | 2 | 71 | 0.00022435 | 0.00031598 | No
30/08/2019 | 10:01 | LWN24 | Urban | Asset Failure | HV | 873 | 68.6 | 0.094587 | 0.13793 | No
30/08/2019 | 10:05 | FSH22 | Urban | Asset Failure | LV | 13 | 320 | 0.0065724 | 0.0020539 | No
30/08/2019 | 10:15 | EW3 | Urban | Third Party | Vehicle Impact | 62 | 322.4 | 0.031397 | 0.0097401 | No
30/08/2019 | 11:05 | LWN24 | Urban | Asset Failure | HV | 197 | 265.1 | 0.08252 | 0 | No
30/08/2019 | 11:11 | EL10 | Urban | Asset Failure | LV | 1 | 76.7 | 0.00012118 | 0.00015799 | No
30/08/2019 | 13:33 | STO14 | Rural Short | Asset Failure | LV | 1 | 156.9 | 0.0026383 | 0.0016815 | No
30/08/2019 | 14:49 | CFD11 | Urban | Overloads |  | 1 | 221 | 0.00034916 | 0.00015799 | No
30/08/2019 | 15:04 | SVW53 | Urban | Asset Failure | LV | 1 | 236 | 0.00037286 | 0.00015799 | No
30/08/2019 | 15:08 | DMA23 | Rural Short | Asset Failure | LV | 1 | 159 | 0.0026736 | 0.0016815 | No
30/08/2019 | 17:40 | MC7 | Urban | Asset Failure | LV | 1 | 325 | 0.00051347 | 0.00015799 | No
31/08/2019 | 06:46 | GW11 | Urban | Asset Failure | LV | 1 | 149 | 0.00023541 | 0.00015799 | No
31/08/2019 | 09:39 | FSH12 | Rural Short | Asset Failure | LV | 1 | 71 | 0.0011939 | 0.0016815 | No
31/08/2019 | 10:04 | DSH34 | Urban | Unknown | Unknown | 1 | 126 | 0.00019907 | 0.00015799 | No
31/08/2019 | 14:48 | NB25 | Urban | Third Party | Vehicle Impact | 61 | 57 | 0.0054933 | 0.0096374 | No
31/08/2019 | 15:29 | MC5 | Urban | Asset Failure | LV | 1 | 299.7 | 0.0004735 | 0.00015799 | No
31/08/2019 | 17:21 | LD4 | Urban | Asset Failure | LV | 1 | 83.2 | 0.00013137 | 0.00015799 | No
31/08/2019 | 17:41 | BH23 | Urban | Asset Failure | LV | 1 | 124 | 0.00019591 | 0.00015799 | No
31/08/2019 | 19:10 | EM9 | Urban | Overloads |  | 1 | 83.5 | 0.00013197 | 0.00015799 | No
31/08/2019 | 22:51 | FTN21 | Urban | Asset Failure | LV | 1 | 69 | 0.00010901 | 0.00015799 | No
31/08/2019 | 23:27 | STO14 | Rural Short | Asset Failure | LV | 1 | 168 | 0.0028249 | 0.0016815 | No
31/08/2019 | 23:47 | BR10 | Urban | Overloads |  | 1 | 70 | 0.00011059 | 0.00015799 | No
01/09/2019 | 08:04 | EM6 | Urban | Planned |  | 35 | 152 | 0.0084051 | 0.0055296 | No
01/09/2019 | 08:26 | CDA11 | Urban | Weather |  | 1 | 93.6 | 0.00014788 | 0.00015799 | No
01/09/2019 | 10:01 | BU9 | Urban | Asset Failure | LV | 22 | 134 | 0.0046808 | 0.0034932 | No
01/09/2019 | 10:03 | DN6 | Urban | Unknown | Unknown | 108 | 76.8 | 0.013096 | 0 | No
01/09/2019 | 10:05 | DN11 | Urban | Unknown | Unknown | 101 | 60 | 0.0095742 | 0.015957 | No
01/09/2019 | 10:51 | DN11 | Urban | Unknown | Unknown | 50 | 8.6 | 0.00068199 | 0.0078995 | No
01/09/2019 | 19:14 | EW12 | Urban | Overloads |  | 1 | 79 | 0.00012481 | 0.00015799 | No
01/09/2019 | 21:40 | FSH34 | Urban | Asset Failure | LV | 20 | 115 | 0.0036338 | 0.0031598 | No
02/09/2019 | 04:08 | RBD23 | Urban | Unknown | Unknown | 148 | 112 | 0.026188 | 0.023382 | No
02/09/2019 | 07:48 | FTN25 | Urban | Third Party | Other | 1 | 134.8 | 0.00021297 | 0.00015799 | No
02/09/2019 | 08:07 | HGS33 | Rural Short | Animal | Other | 6 | 210 | 0.021187 | 0.010089 | No
02/09/2019 | 08:25 | HGS33 | Rural Short | Unknown | Unknown | 1 | 130 | 0.0021859 | 0.0016815 | No
02/09/2019 | 08:39 | CFD16 | Urban | Asset Failure | LV | 1 | 101 | 0.00015957 | 0.00015799 | No
02/09/2019 | 12:08 | NW21 | Urban | Asset Failure | LV | 1 | 104.4 | 0.00016491 | 0.00015799 | No
02/09/2019 | 13:40 | LWN33 | Urban | Asset Failure | LV | 1 | 266.5 | 0.00042096 | 0.00015799 | No
03/09/2019 | 08:20 | RWT34 | Urban | Animal | Animal impact | 129 | 110 | 0.022419 | 0.020381 | No
03/09/2019 | 11:31 | FSH12 | Rural Short | Asset Failure | LV | 1 | 103.3 | 0.0017367 | 0.0016815 | No
03/09/2019 | 12:40 | DMA23 | Rural Short | Asset Failure | LV | 1 | 126.8 | 0.0021319 | 0.0016815 | No
03/09/2019 | 14:04 | MTN31 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 155.6 | 0.00024575 | 0.00015799 | No
03/09/2019 | 15:54 | CRM24 | Urban | Asset Failure | LV | 13 | 98 | 0.0019416 | 0.0019812 | No
03/09/2019 | 18:40 | CDA11 | Urban | Asset Failure | LV | 1 | 40 | 6.3196e-05 | 0.00015799 | No
03/09/2019 | 19:45 | DMA14 | Urban | Asset Failure | LV | 54 | 140 | 0.011944 | 0.0085315 | No
04/09/2019 | 09:30 | DC3 | Urban | Unknown | Unknown | 1 | 60 | 9.4794e-05 | 0.00015799 | No
04/09/2019 | 14:06 | BU14 | Urban | Asset Failure | LV | 1 | 164 | 0.0002591 | 0.00015799 | No
04/09/2019 | 15:55 | DMA21 | Urban | Asset Failure | HV | 48 | 95.8 | 0.0072637 | 0.0075835 | No
04/09/2019 | 16:27 | M12 | Urban | Asset Failure | HV | 763 | 34.8 | 0.041908 | 0.12055 | No
04/09/2019 | 16:53 | WD23 | Urban | Unknown | Unknown | 1 | 47 | 7.4176e-05 | 0.00015799 | No
04/09/2019 | 18:06 | STO21 | Rural Short | Asset Failure | LV | 1 | 174 | 0.0029258 | 0.0016815 | No
04/09/2019 | 19:42 | MTN35 | Rural Short | Asset Failure | LV | 1 | 147.7 | 0.0024838 | 0.0016815 | No
04/09/2019 | 20:43 | CRM22 | Urban | Asset Failure | LV | 1 | 136.7 | 0.00021603 | 0.00015799 | No
05/09/2019 | 07:55 | LD6 | Urban | Asset Failure | HV | 1,532 | 36.2 | 0.08751 | 0.24204 | No
05/09/2019 | 07:55 | LD33 | Urban | Asset Failure | HV | 2,332 | 9.4 | 0.034802 | 0.36843 | No
05/09/2019 | 10:31 | CRM34 | Urban | Asset Failure | HV | 207 | 1.1 | 0.0003652 | 0.032704 | No
05/09/2019 | 11:01 | NW32 | Urban | Asset Failure | LV | 1 | 43.6 | 6.8831e-05 | 0.00015799 | No
05/09/2019 | 13:00 | MC6 | Urban | Asset Failure | LV | 1 | 89 | 0.00014066 | 0.00015799 | No
05/09/2019 | 13:46 | NP11 | Urban | Asset Failure | LV | 10 | 178.3 | 0.0027893 | 0.0015641 | No
05/09/2019 | 14:14 | M23 | Urban | Third Party | Other | 1 | 196 | 0.00030966 | 0.00015799 | No
06/09/2019 | 01:10 | RWT24 | Urban | Asset Failure | LV | 1 | 80 | 0.00012639 | 0.00015799 | No
06/09/2019 | 10:41 | DN22 | Urban | Overloads |  | 1 | 219 | 0.000346 | 0.00015799 | No
06/09/2019 | 14:17 | HGS33 | Rural Short | Third Party | Other | 35 | 252.4 | 0.14855 | 0.058852 | No
06/09/2019 | 17:26 | MTN23 | Urban | Asset Failure | LV | 36 | 154 | 0.0086714 | 0.0056308 | No
07/09/2019 | 01:21 | OAK21 | Urban | Asset Failure | LV | 33 | 79 | 0.0041188 | 0.0052137 | No
07/09/2019 | 01:57 | NP12 | Urban | Third Party | Other | 1 | 112.4 | 0.00017758 | 0.00015799 | No
07/09/2019 | 07:55 | HGS22 | Rural Short | Unknown | Unknown | 3 | 155.1 | 0.007824 | 0.0050445 | No
07/09/2019 | 07:59 | DSH21 | Urban | Asset Failure | HV | 2 | 262.9 | 0.0008306 | 0.00031598 | No
07/09/2019 | 08:16 | DMA21 | Urban | Overloads |  | 1 | 383.1 | 0.00060526 | 0.00015799 | No
07/09/2019 | 09:32 | OE9 | Urban | Asset Failure | LV | 1 | 172.3 | 0.00027214 | 0.00015799 | No
07/09/2019 | 09:48 | RBD24 | Urban | Vegetation | Grow-in - Other responsible party | 8 | 156.7 | 0.0019601 | 0.0012513 | No
07/09/2019 | 10:06 | FSH11 | Urban | Third Party | Other | 1 | 53.8 | 8.4999e-05 | 0.00015799 | No
07/09/2019 | 14:25 | CRM14 | Urban | Asset Failure | LV | 1 | 65 | 0.00010269 | 0.00015799 | No
07/09/2019 | 14:47 | EM8 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 72.3 | 0.0001142 | 0.00015799 | No
07/09/2019 | 15:00 | STO14 | Rural Short | Asset Failure | LV | 1 | 39.9 | 0.00067092 | 0.0016815 | No
07/09/2019 | 16:11 | STO14 | Rural Short | Asset Failure | LV | 1 | 63.2 | 0.0010624 | 0.0016815 | No
07/09/2019 | 18:56 | DC12 | Urban | Asset Failure | LV | 1 | 188.4 | 0.00029765 | 0.00015799 | No
07/09/2019 | 22:11 | RBD13 | Urban | Asset Failure | Distribution substation | 137 | 149.8 | 0.032424 | 0.021645 | No
08/09/2019 | 08:14 | NW31 | Urban | Asset Failure | LV | 1 | 114.1 | 0.00018029 | 0.00015799 | No
08/09/2019 | 11:31 | SS11 | Urban | Asset Failure | LV | 1 | 54.8 | 8.6552e-05 | 0.00015799 | No
08/09/2019 | 12:35 | DC1 | Urban | Asset Failure | LV | 1 | 39.2 | 6.1879e-05 | 0.00015799 | No
08/09/2019 | 12:38 | NO7 | Urban | Third Party | Other | 1 | 51.9 | 8.2023e-05 | 0.00015799 | No
08/09/2019 | 13:16 | FSH12 | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 30 | 64 | 0.032285 | 0.050445 | No
08/09/2019 | 16:08 | CFD21 | Urban | Overloads |  | 1 | 187 | 0.00029544 | 0.00015799 | No
08/09/2019 | 16:50 | DN11 | Urban | Overloads |  | 1 | 69.6 | 0.00010988 | 0.00015799 | No
08/09/2019 | 17:33 | EW9 | Urban | Asset Failure | LV | 1 | 107 | 0.00016905 | 0.00015799 | No
08/09/2019 | 18:09 | DMA23 | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 3 | 231 | 0.011653 | 0.0050445 | No
08/09/2019 | 18:45 | CDA24 | Urban | Overloads |  | 29 | 149.6 | 0.0069409 | 0.0046402 | No
08/09/2019 | 18:53 | NP33 | Urban | Overloads |  | 1 | 86.5 | 0.00013666 | 0.00015799 | No
08/09/2019 | 19:35 | NP16 | Urban | Overloads |  | 1 | 255 | 0.00040287 | 0.00015799 | No
08/09/2019 | 20:02 | MR11 | Urban | Asset Failure | LV | 1 | 158 | 0.00024962 | 0.00015799 | No
08/09/2019 | 20:02 | FSH31 | Urban | Asset Failure | LV | 1 | 192.8 | 0.00030452 | 0.00015799 | No
08/09/2019 | 20:21 | EL8 | Urban | Third Party | Vehicle Impact | 36 | 294 | 0.016722 | 0.0056876 | No
08/09/2019 | 20:36 | DMA23 | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 31 | 1,313.0 | 0.68442 | 0.052126 | No
08/09/2019 | 20:59 | DN22 | Urban | Asset Failure | HV | 73 | 20.7 | 0.0023912 | 0.011533 | No
08/09/2019 | 21:02 | CRM22 | Urban | Overloads |  | 1 | 137 | 0.00021645 | 0.00015799 | No
09/09/2019 | 00:43 | KBH32 | Urban | Overloads |  | 1 | 63 | 9.9534e-05 | 0.00015799 | No
09/09/2019 | 03:12 | FSH13 | Urban | Vegetation | Grow-in - NSP responsibility | 83 | 284.9 | 0.03736 | 0.013113 | No
09/09/2019 | 05:37 | MR13 | Urban | Unknown | Unknown | 37 | 143 | 0.0083592 | 0.0058456 | No
09/09/2019 | 06:18 | MTN22 | Rural Short | Asset Failure | LV | 1 | 178 | 0.0029931 | 0.0016815 | No
09/09/2019 | 07:34 | M33 | Urban | Unknown | Unknown | 16 | 146 | 0.0036906 | 0.0025278 | No
09/09/2019 | 08:11 | CRM34 | Urban | Unknown | Unknown | 1 | 198.7 | 0.00031393 | 0.00015799 | No
09/09/2019 | 08:50 | MR12 | Urban | Unknown | Unknown | 1 | 101.5 | 0.00016041 | 0.00015799 | No
09/09/2019 | 09:17 | EM6 | Urban | Asset Failure | LV | 1 | 477.4 | 0.00075419 | 0.00015799 | No
09/09/2019 | 09:28 | DC1 | Urban | Asset Failure | LV | 1 | 251 | 0.0003965 | 0.00015799 | No
09/09/2019 | 09:31 | BR1 | Urban | Asset Failure | LV | 1 | 358 | 0.0005656 | 0.00015799 | No
09/09/2019 | 10:46 | EB22 | Urban | Third Party | Other | 1 | 103.5 | 0.00016352 | 0.00015799 | No
09/09/2019 | 10:53 | OAK23 | Urban | Asset Failure | LV | 1 | 216.3 | 0.00034168 | 0.00015799 | No
09/09/2019 | 11:09 | FTN11 | Urban | Unknown | Unknown | 1 | 541.9 | 0.00085607 | 0.00015799 | No
09/09/2019 | 14:00 | FTN25 | Urban | Third Party | Other | 1 | 123 | 0.00019433 | 0.00015799 | No
09/09/2019 | 17:28 | WD23 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 66.5 | 0.00010504 | 0.00015799 | No
09/09/2019 | 17:52 | OAK23 | Urban | Asset Failure | LV | 1 | 48.7 | 7.6941e-05 | 0.00015799 | No
09/09/2019 | 17:54 | EB12 | Urban | Asset Failure | LV | 1 | 175.2 | 0.00027683 | 0.00015799 | No
09/09/2019 | 20:10 | STO21 | Rural Short | Asset Failure | LV | 1 | 80 | 0.0013452 | 0.0016815 | No
09/09/2019 | 23:31 | EW14 | Urban | Overloads |  | 1 | 39 | 6.1616e-05 | 0.00015799 | No
09/09/2019 | 23:41 | BH31 | Urban | Asset Failure | LV | 1 | 694 | 0.0010964 | 0.00015799 | No
10/09/2019 | 05:34 | EB12 | Urban | Asset Failure | HV | 681 | 54.7 | 0.058878 | 0.10759 | No
10/09/2019 | 05:34 | EB12 | Urban |  | HV | 1,220 | 43 | 0.082914 | 0.19275 | No
10/09/2019 | 08:48 | DVY32 | Urban | Asset Failure | LV | 1 | 156.8 | 0.00024775 | 0.00015799 | No
10/09/2019 | 09:00 | BW22 | Urban | Asset Failure | LV | 1 | 165 | 0.00026068 | 0.00015799 | No
10/09/2019 | 09:20 | RD4 | Urban | Asset Failure | LV | 7 | 95 | 0.0010506 | 0.0011059 | No
10/09/2019 | 09:33 | SS23 | Urban | Third Party | Vehicle Impact | 27 | 287.5 | 0.012265 | 0.0042657 | No
10/09/2019 | 10:22 | CFD23 | Urban | Unknown | Unknown | 1 | 144.6 | 0.00022848 | 0.00015799 | No
10/09/2019 | 11:17 | EM1 | Urban | Asset Failure | LV | 1 | 296.4 | 0.00046831 | 0.00015799 | No
10/09/2019 | 12:31 | BH31 | Urban | Asset Failure | LV | 1 | 139 | 0.00021961 | 0.00015799 | No
10/09/2019 | 13:27 | EM5 | Urban | Asset Failure | LV | 1 | 109 | 0.00017221 | 0.00015799 | No
10/09/2019 | 16:48 | STO21 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 101.1 | 0.0017005 | 0.0016815 | No
10/09/2019 | 18:40 | M23 | Urban | Asset Failure | LV | 1 | 62.8 | 9.9165e-05 | 0.00015799 | No
10/09/2019 | 23:48 | BR13 | Urban | Asset Failure | LV | 8 | 42 | 0.00053085 | 0.0012639 | No
11/09/2019 | 07:09 | RBD21 | Rural Short | Animal | Animal impact | 1 | 65.3 | 0.0010975 | 0.0016815 | No
11/09/2019 | 08:51 | LD7 | Urban | Asset Failure | LV | 1 | 89 | 0.00014061 | 0.00015799 | No
11/09/2019 | 11:05 | NW23 | Urban | Asset Failure | LV | 1 | 129.9 | 0.00020518 | 0.00015799 | No
11/09/2019 | 12:51 | SVW42 | Urban | Asset Failure | LV | 1 | 278.9 | 0.00044061 | 0.00015799 | No
11/09/2019 | 14:46 | MTN21 | Urban | Third Party | Other | 25 | 93.9 | 0.0037095 | 0.0039497 | No
11/09/2019 | 14:52 | DMA21 | Urban | Vegetation | Grow-in - Other responsible party | 18 | 18 | 0.00052554 | 0.0029197 | No
11/09/2019 | 15:12 | CFD22 | Urban | Unknown | Unknown | 1 | 313 | 0.00049451 | 0.00015799 | No
11/09/2019 | 17:11 | NP12 | Urban | Third Party | Other | 1 | 173.4 | 0.00027398 | 0.00015799 | No
11/09/2019 | 17:22 | CFD11 | Urban | Asset Failure | LV | 1 | 68 | 0.00010743 | 0.00015799 | No
11/09/2019 | 19:38 | HT11 | Urban | Asset Failure | LV | 1 | 111 | 0.00017542 | 0.00015799 | No
11/09/2019 | 21:30 | BR4 | Urban | Asset Failure | LV | 5 | 45 | 0.00035548 | 0.00078995 | No
11/09/2019 | 22:07 | FSH33 | Urban | Asset Failure | LV | 1 | 88 | 0.00013903 | 0.00015799 | No
12/09/2019 | 04:06 | HGS33 | Rural Short | Animal | Animal impact | 9 | 186.4 | 0.028204 | 0.015133 | No
12/09/2019 | 08:19 | RBD12 | Rural Short | Planned |  | 1 | 18 | 0.00030267 | 0.0016815 | No
12/09/2019 | 09:27 | DC7 | Urban | Asset Failure | LV | 1 | 122.2 | 0.00019312 | 0.00015799 | No
12/09/2019 | 10:04 | MTN34 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 85.7 | 0.00013535 | 0.00015799 | No
12/09/2019 | 10:11 | DC10 | Urban | Asset Failure | LV | 1 | 93.4 | 0.00014754 | 0.00015799 | No
12/09/2019 | 10:25 | NB24 | Urban | Asset Failure | LV | 8 | 185 | 0.0023149 | 0.0012513 | No
12/09/2019 | 10:54 | DC2 | Urban | Third Party | Vehicle Impact | 20 | 81 | 0.0025338 | 0.0031282 | No
12/09/2019 | 17:24 | OR33 | Urban | Asset Failure | LV | 1 | 116 | 0.00018327 | 0.00015799 | No
12/09/2019 | 17:27 | NP12 | Urban | Third Party | Other | 1 | 92.7 | 0.00014651 | 0.00015799 | No
13/09/2019 | 03:34 | LD4 | Urban | Third Party | Vehicle Impact | 735 | 125.4 | 0.14559 | 0.11612 | No
13/09/2019 | 04:16 | LD4 | Urban | Third Party | Vehicle Impact | 30 | 214 | 0.010143 | 0.0047397 | No
13/09/2019 | 04:16 | LD4 | Urban | Third Party | Vehicle Impact | 17 | 204 | 0.0054243 | 0 | No
13/09/2019 | 12:36 | NP33 | Urban | Overloads |  | 1 | 368.6 | 0.00058232 | 0.00015799 | No
13/09/2019 | 13:39 | BW23 | Urban | Third Party | Vehicle Impact | 24 | 81 | 0.0030713 | 0.0037918 | No
13/09/2019 | 14:22 | EB31 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 217.9 | 0.00034429 | 0.00015799 | No
13/09/2019 | 14:41 | OAK21 | Urban | Asset Failure | LV | 1 | 434 | 0.00068568 | 0.00015799 | No
13/09/2019 | 15:15 | EB21 | Urban | Unknown | Unknown | 17 | 210 | 0.0056402 | 0.0026858 | No
13/09/2019 | 15:26 | EB11 | Urban | Third Party | Other | 121 | 236.4 | 0.045189 | 0.019117 | No
13/09/2019 | 15:30 | EB11 | Urban | Third Party | Other | 10 | 33 | 0.00052137 | 0.0015799 | No
13/09/2019 | 15:49 | EB11 | Urban | Unknown | Unknown | 29 | 176 | 0.0080638 | 0.0045817 | No
13/09/2019 | 18:02 | OE4 | Urban | Asset Failure | LV | 1 | 313 | 0.00049451 | 0.00015799 | No
13/09/2019 | 18:20 | DC6 | Urban | Third Party | Vehicle Impact | 1 | 189.9 | 0.00029994 | 0.00015799 | No
13/09/2019 | 19:52 | BR1 | Urban | Asset Failure | LV | 1 | 88 | 0.00013903 | 0.00015799 | No
14/09/2019 | 14:51 | DC6 | Urban | Asset Failure | LV | 1 | 443.8 | 0.00070119 | 0.00015799 | No
14/09/2019 | 15:56 | STO13 | Urban | Asset Failure | LV | 1 | 213.3 | 0.00033699 | 0.00015799 | No
14/09/2019 | 18:46 | HGS23 | Rural Short | Asset Failure | LV | 1 | 119 | 0.002001 | 0.0016815 | No
14/09/2019 | 21:07 | BU1 | Urban | Asset Failure | LV | 3 | 153 | 0.00072517 | 0.00047397 | No
15/09/2019 | 09:47 | CRM13 | Urban | Asset Failure | LV | 12 | 793 | 0.015034 | 0.0018959 | No
15/09/2019 | 18:58 | FTN24 | Urban | Overloads |  | 1 | 157 | 2.48e-06 | 1.5799e-06 | No
16/09/2019 | 06:53 | HT1 | Urban | Animal | Animal nesting/burrowing, etc and other | 2 | 181.9 | 0.00057461 | 0.00031598 | No
16/09/2019 | 08:50 | FSH31 | Urban | Asset Failure | LV | 17 | 100 | 0.0027632 | 0.0027632 | No
16/09/2019 | 09:46 | DC5 | Urban | Unknown | Unknown | 1 | 58.1 | 9.1713e-05 | 0.00015799 | No
16/09/2019 | 11:22 | STO22 | Urban | Overloads |  | 1 | 157.3 | 0.00024857 | 0.00015799 | No
16/09/2019 | 12:11 | DN22 | Urban | Overloads |  | 10 | 169 | 0.0025552 | 0.001512 | No
16/09/2019 | 13:19 | EL11 | Urban | Third Party | Other | 232 | 45.4 | 0.016655 | 0.036654 | No
16/09/2019 | 13:50 | HGS31 | Rural Short | Unknown | Unknown | 12 | 226.5 | 0.043996 | 0.019421 | No
16/09/2019 | 14:59 | RWT12 | Urban | Third Party | Vehicle Impact | 25 | 231 | 0.0091239 | 0.0039497 | No
16/09/2019 | 16:35 | CFD15 | Urban | Asset Failure | LV | 10 | 250.2 | 0.0039521 | 0.0015799 | No
16/09/2019 | 16:56 | CFD15 | Urban | Asset Failure | LV | 33 | 229.3 | 0.011955 | 0.0052137 | No
16/09/2019 | 17:01 | MTN24 | Rural Short | Asset Failure | LV | 1 | 169 | 0.0028417 | 0.0016815 | No
16/09/2019 | 18:17 | NW33 | Urban | Asset Failure | LV | 94 | 163.2 | 0.024229 | 0.014851 | No
16/09/2019 | 19:51 | FSH33 | Urban | Asset Failure | LV | 1 | 190.4 | 0.00030086 | 0.00015799 | No
17/09/2019 | 07:21 | GW3 | Urban | Asset Failure | LV | 1 | 98.1 | 0.00015496 | 0.00015799 | No
17/09/2019 | 08:14 | FSH13 | Urban | Planned |  | 1 | 28 | 4.4237e-05 | 0.00015799 | No
17/09/2019 | 11:07 | NW21 | Urban | Asset Failure | LV | 16 | 58 | 0.0014515 | 0.0025026 | No
17/09/2019 | 13:16 | NW11 | Urban | Asset Failure | LV | 1 | 135.8 | 0.00021447 | 0.00015799 | No
17/09/2019 | 14:34 | CFD14 | Urban | Asset Failure | LV | 1 | 176 | 0.00027806 | 0.00015799 | No
17/09/2019 | 17:48 | DN25 | Urban | Asset Failure | LV | 6 | 240 | 0.0023778 | 0.0009906 | No
17/09/2019 | 23:42 | DSH14 | Urban | Third Party | Vehicle Impact | 2 | 205 | 0.00064776 | 0.00031598 | No
18/09/2019 | 00:44 | NW14 | Urban | Third Party | Vehicle Impact | 2 | 182 | 0.00057508 | 0.00031598 | No
18/09/2019 | 01:14 | FTN13 | Urban | Asset Failure | LV | 21 | 91 | 0.0030192 | 0.0033178 | No
18/09/2019 | 06:50 | DC1 | Urban | Unknown | Unknown | 1 | 99.3 | 0.00015686 | 0.00015799 | No
18/09/2019 | 06:59 | DMA23 | Rural Short | Asset Failure | LV | 1 | 225.8 | 0.0037965 | 0.0016815 | No
18/09/2019 | 08:23 | HGS21 | Rural Short | Animal | Animal impact | 331 | 108.2 | 0.6019 | 0.55654 | No
18/09/2019 | 09:08 | NW31 | Urban | Asset Failure | LV | 1 | 96.3 | 0.00015212 | 0.00015799 | No
18/09/2019 | 15:23 | M13 | Urban | Third Party | Vehicle Impact | 12 | 412 | 0.007811 | 0.0018959 | No
18/09/2019 | 15:36 | CRM13 | Urban | Asset Failure | LV | 1 | 114 | 0.00018006 | 0.00015799 | No
18/09/2019 | 18:56 | HGS31 | Rural Short | Asset Failure | LV | 1 | 384 | 0.0064569 | 0.0016815 | No
18/09/2019 | 19:42 | EL11 | Urban | Overloads |  | 1 | 197.5 | 0.00031206 | 0.00015799 | No
19/09/2019 | 00:48 | EL12 | Urban | Third Party | Vehicle Impact | 56 | 192 | 0.016987 | 0.0088474 | No
19/09/2019 | 08:02 | HT8 | Urban | Asset Failure | LV | 1 | 132.9 | 0.00020997 | 0.00015799 | No
19/09/2019 | 10:15 | EL12 | Urban | Third Party | Other | 56 | 35 | 0.0030966 | 0.0088474 | No
19/09/2019 | 14:10 | HT2 | Urban | Third Party | Other | 2 | 140 | 0.00033178 | 0.00023698 | No
19/09/2019 | 16:02 | OAK32 | Urban | Asset Failure | LV | 23 | 99 | 0.0036628 | 0.0037017 | No
19/09/2019 | 17:31 | MGE31 | Urban | Third Party | Other | 7 | 89 | 0.0010208 | 0.001147 | No
19/09/2019 | 20:36 | OR35 | Urban | Animal | Animal impact | 51 | 64 | 0.0051487 | 0.0080448 | No
20/09/2019 | 03:09 | EW14 | Urban | Weather |  | 749 | 54.5 | 0.064492 | 0.11833 | No
20/09/2019 | 11:05 | OAK22 | Urban | Asset Failure | LV | 38 | 105 | 0.0063038 | 0.0060036 | No
20/09/2019 | 15:06 | MTN32 | Rural Short | Asset Failure | Distribution substation | 5 | 585.2 | 0.049199 | 0.0084075 | No
20/09/2019 | 17:22 | DC1 | Urban | Third Party | Other | 15 | 154 | 0.0036496 | 0.0023698 | No
20/09/2019 | 21:43 | BW21 | Urban | Unknown | Unknown | 865 | 27 | 0.036965 | 0.13666 | No
20/09/2019 | 23:39 | DN6 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 164 | 0.0002591 | 0.00015799 | No
21/09/2019 | 00:49 | HGS21 | Rural Short | Unknown | Unknown | 3 | 72.1 | 0.0036371 | 0.0050445 | No
21/09/2019 | 02:27 | LWN33 | Urban | Animal | Animal impact | 2,003 | 27 | 0.085451 | 0.31645 | No
21/09/2019 | 03:10 | BU14 | Urban | Vegetation | Grow-in - Other responsible party | 1,702 | 33.5 | 0.090187 | 0.2689 | No
21/09/2019 | 05:14 | BU14 | Urban | Asset Failure | LV | 19 | 466 | 0.013988 | 0.0030018 | No
21/09/2019 | 07:11 | DVY34 | Urban | Unknown | Unknown | 731 | 87.5 | 0.10101 | 0.11549 | No
21/09/2019 | 09:05 | BU14 | Urban | Asset Failure | HV | 25 | 147.2 | 0.0058147 | 0.0039497 | No
21/09/2019 | 11:48 | STO21 | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 422 | 0.0070959 | 0.0016815 | No
21/09/2019 | 12:07 | CDA24 | Urban | Asset Failure | LV | 2 | 183 | 0.00051174 | 0.00027964 | No
21/09/2019 | 12:07 | LD3 | Urban | Weather |  | 18 | 173 | 0.0049608 | 0.0028675 | No
21/09/2019 | 12:23 | MTN32 | Rural Short | Third Party | Vehicle Impact | 5 | 257 | 0.021607 | 0.0084075 | No
21/09/2019 | 13:07 | EM11 | Urban | Asset Failure | LV | 1 | 158 | 0.00024962 | 0.00015799 | No
21/09/2019 | 13:24 | SR15 | Urban | Asset Failure | LV | 1 | 301 | 0.00047555 | 0.00015799 | No
21/09/2019 | 15:56 | OE4 | Urban | Asset Failure | LV | 1 | 98.2 | 0.00015512 | 0.00015799 | No
21/09/2019 | 16:14 | RBD22 | Urban | Third Party | Vehicle Impact | 17 | 357.9 | 0.0096135 | 0.0026858 | No
21/09/2019 | 16:21 | DN22 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 414 | 0.00065408 | 0.00015799 | No
21/09/2019 | 16:31 | DMA21 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 134 | 0.00021171 | 0.00015799 | No
21/09/2019 | 16:35 | EM5 | Urban | Asset Failure | LV | 1 | 128.5 | 0.00020296 | 0.00015799 | No
21/09/2019 | 16:40 | DN7 | Urban | Asset Failure | LV | 1 | 320.5 | 0.00050638 | 0.00015799 | No
21/09/2019 | 18:10 | LD3 | Urban | Asset Failure | LV | 3 | 170 | 0.00080575 | 0.00047397 | No
21/09/2019 | 18:25 | STO21 | Rural Short | Asset Failure | LV | 52 | 75 | 0.066083 | 0.08811 | No
21/09/2019 | 20:54 | HGS23 | Rural Short | Animal | Animal impact | 2 | 106 | 0.0035648 | 0.003363 | No
22/09/2019 | 14:48 | BU14 | Urban | Asset Failure | LV | 1 | 71 | 0.00011223 | 0.00015799 | No
22/09/2019 | 14:57 | CRM14 | Urban | Network Business | Networ Error | 62 | 53 | 0.0051915 | 0.0097954 | No
22/09/2019 | 15:35 | FTN11 | Urban | Asset Failure | LV | 1 | 85 | 0.00013429 | 0.00015799 | No
22/09/2019 | 19:54 | CFD16 | Urban | Asset Failure | LV | 1 | 71 | 0.00011217 | 0.00015799 | No
22/09/2019 | 22:52 | BU1 | Urban | Unknown | Unknown | 54 | 58 | 0.0049482 | 0.0085315 | No
23/09/2019 | 00:22 | MTN21 | Urban | Asset Failure | HV | 87 | 110.8 | 0.015227 | 0.013745 | No
23/09/2019 | 04:19 | BU1 | Urban | Asset Failure | LV | 1 | 221 | 0.00034916 | 0.00015799 | No
23/09/2019 | 09:05 | LD2 | Urban | Asset Failure | LV | 19 | 40 | 0.0012007 | 0.0030018 | No
23/09/2019 | 09:27 | KBH31 | Urban | Overloads |  | 1 | 312.6 | 0.00049393 | 0.00015799 | No
23/09/2019 | 09:30 | DMA15 | Rural Short | Asset Failure | LV | 8 | 297.4 | 0.041259 | 0.013872 | No
23/09/2019 | 09:47 | DSH21 | Urban | Overloads |  | 13 | 258 | 0.005299 | 0.0020539 | No
23/09/2019 | 10:00 | MC2 | Urban | Overloads |  | 1 | 189.4 | 0.00029915 | 0.00015799 | No
23/09/2019 | 10:50 | SS12 | Urban | Animal | Animal nesting/burrowing, etc and other | 4 | 151.5 | 0.00095721 | 0.00063196 | No
23/09/2019 | 10:51 | NW11 | Urban | Unknown | Unknown | 1 | 23.3 | 3.6838e-05 | 0.00015799 | No
23/09/2019 | 14:25 | DMA24 | Rural Short | Asset Failure | LV | 1 | 214 | 0.0035984 | 0.0016815 | No
23/09/2019 | 23:17 | FSH21 | Rural Short | Asset Failure | HV | 17 | 96 | 0.0277 | 0.028854 | No
24/09/2019 | 06:09 | EL9 | Urban | Animal | Animal impact | 56 | 144 | 0.01274 | 0.0088474 | No
24/09/2019 | 07:01 | FTN11 | Urban | Asset Failure | LV | 1 | 134 | 0.00021171 | 0.00015799 | No
24/09/2019 | 09:36 | STO14 | Rural Short | Asset Failure | LV | 1 | 94 | 0.0015806 | 0.0016815 | No
24/09/2019 | 11:04 | CRM14 | Urban | Asset Failure | LV | 1 | 310.9 | 0.00049122 | 0.00015799 | No
24/09/2019 | 12:27 | DC3 | Urban | Unknown | Unknown | 1 | 137.5 | 0.00021721 | 0.00015799 | No
24/09/2019 | 17:19 | NP11 | Urban | Asset Failure | LV | 4 | 101 | 0.00063828 | 0.00063196 | No
24/09/2019 | 20:42 | BR10 | Urban | Third Party | Vehicle Impact | 41 | 158 | 0.010235 | 0.0064776 | No
24/09/2019 | 21:42 | NW22 | Urban | Asset Failure | LV | 1 | 117 | 0.00018488 | 0.00015799 | No
25/09/2019 | 00:55 | LWN24 | Urban | Third Party | Vehicle Impact | 16 | 110 | 0.0027806 | 0.0025278 | No
25/09/2019 | 07:02 | DC4 | Urban | Asset Failure | LV | 2 | 82.3 | 0.00026005 | 0.00031598 | No
25/09/2019 | 08:19 | MC7 | Urban | Third Party | Other | 1 | 143.7 | 0.00022698 | 0.00015799 | No
25/09/2019 | 09:44 | SR23 | Urban | Asset Failure | LV | 1 | 89.2 | 0.00014098 | 0.00015799 | No
25/09/2019 | 18:44 | CRM21 | Urban | Asset Failure | LV | 3 | 106 | 0.00050911 | 0.00048029 | No
25/09/2019 | 18:46 | HT3 | Urban | Third Party | Vehicle Impact | 1 | 193.4 | 0.00030547 | 0.00015799 | No
25/09/2019 | 19:00 | FTN12 | Urban | Asset Failure | LV | 1 | 160 | 0.00025278 | 0.00015799 | No
26/09/2019 | 00:59 | CDA11 | Urban | Asset Failure | LV | 1 | 26 | 4.1077e-05 | 0.00015799 | No
26/09/2019 | 01:44 | FSH31 | Urban | Asset Failure | LV | 1 | 51 | 8.0575e-05 | 0.00015799 | No
26/09/2019 | 04:38 | DMA13 | Rural Short | Asset Failure | LV | 4 | 201.2 | 0.01353 | 0 | No
26/09/2019 | 06:28 | SVW45 | Urban | Asset Failure | HV | 433 | 39.6 | 0.027067 | 0.06841 | No
26/09/2019 | 18:10 | BU2 | Urban | Asset Failure | LV | 1 | 79.4 | 0.00012544 | 0.00015799 | No
26/09/2019 | 19:41 | EL9 | Urban | Asset Failure | LV | 18 | 109 | 0.0030688 | 0.0028154 | No
26/09/2019 | 19:52 | MGE11 | Urban | Asset Failure | LV | 36 | 98 | 0.0055739 | 0.0056876 | No
27/09/2019 | 06:51 | DN6 | Urban | Third Party | Other | 43 | 291.7 | 0.019815 | 0.0067936 | No
27/09/2019 | 12:42 | DMA12 | Urban | Asset Failure | LV | 76 | 152.2 | 0.018275 | 0.012007 | No
27/09/2019 | 16:55 | DMA12 | Urban | Asset Failure | Distribution substation | 65 | 45.1 | 0.0046298 | 0.010269 | No
27/09/2019 | 16:58 | HGS22 | Rural Short | Asset Failure | LV | 1 | 270.4 | 0.0045468 | 0.0016815 | No
27/09/2019 | 17:07 | M35 | Urban | Asset Failure | LV | 1 | 243 | 0.00038392 | 0.00015799 | No
27/09/2019 | 17:44 | DMA12 | Urban | Asset Failure | LV | 1 | 17.9 | 2.8333e-05 | 0.00015799 | No
27/09/2019 | 17:44 | DMA12 | Urban | Asset Failure | LV | 1 | 17.9 | 2.8333e-05 | 0.00015799 | No
27/09/2019 | 17:48 | DC2 | Urban | Asset Failure | HV | 289 | 166 | 0.075777 | 0.045659 | No
27/09/2019 | 18:20 | DMA21 | Urban | Asset Failure | LV | 40 | 150 | 0.0094794 | 0.0063196 | No
28/09/2019 | 08:30 | K13 | Urban | Asset Failure | LV | 1 | 93.4 | 0.00014756 | 0.00015799 | No
28/09/2019 | 09:34 | DC1 | Urban | Overloads |  | 1 | 105.5 | 0.00016671 | 0.00015799 | No
28/09/2019 | 15:36 | RBD23 | Urban | Asset Failure | LV | 1 | 49 | 7.7415e-05 | 0.00015799 | No
28/09/2019 | 15:43 | OE10 | Urban | Asset Failure | LV | 1 | 108 | 0.00017063 | 0.00015799 | No
28/09/2019 | 19:00 | DMA14 | Urban | Animal | Animal impact | 1 | 109.1 | 0.00017242 | 0.00015799 | No
28/09/2019 | 21:21 | BR4 | Urban | Asset Failure | LV | 1 | 113.8 | 0.00017979 | 0.00015799 | No
28/09/2019 | 23:10 | NB22 | Urban | Unknown | Unknown | 1 | 85.4 | 0.00013498 | 0.00015799 | No
28/09/2019 | 23:17 | FSH11 | Urban | Asset Failure | LV | 1 | 68 | 0.00010743 | 0.00015799 | No
29/09/2019 | 07:36 | MTN32 | Rural Short | Asset Failure | LV | 1 | 98.6 | 0.0016582 | 0.0016815 | No
29/09/2019 | 08:26 | DC8 | Urban | Asset Failure | LV | 3 | 23 | 0.000108 | 0.00046923 | No
29/09/2019 | 18:31 | SR20 | Urban | Overloads |  | 1 | 179 | 0.0002828 | 0.00015799 | No
29/09/2019 | 22:06 | FSH33 | Urban | Unknown | Unknown | 1 | 33.7 | 5.3269e-05 | 0.00015799 | No
30/09/2019 | 00:39 | CDA11 | Urban | Asset Failure | LV | 1 | 161 | 0.00025436 | 0.00015799 | No
30/09/2019 | 07:11 | EL8 | Urban | Asset Failure | LV | 1 | 49 | 7.7415e-05 | 0.00015799 | No
30/09/2019 | 07:29 | BH21 | Urban | Asset Failure | LV | 1 | 66 | 0.00010427 | 0.00015799 | No
30/09/2019 | 14:04 | DC5 | Urban | Asset Failure | LV | 1 | 101 | 0.00015957 | 0.00015799 | No
30/09/2019 | 14:14 | M11 | Urban | Asset Failure | LV | 25 | 135.1 | 0.0053374 | 0.0039497 | No
30/09/2019 | 19:05 | MGE31 | Urban | Asset Failure | LV | 3 | 310 | 0.0014693 | 0.00047397 | No
30/09/2019 | 19:56 | LD33 | Urban | Asset Failure | LV | 11 | 109 | 0.0018909 | 0.0017347 | No
30/09/2019 | 22:10 | MC6 | Urban | Asset Failure | LV | 5 | 115 | 0.00082668 | 0.00071885 | No
01/10/2019 | 00:47 | KBH32 | Urban | Asset Failure | LV | 1 | 125 | 0.00019749 | 0.00015799 | No
01/10/2019 | 04:52 | MTN32 | Rural Short | Unknown | Unknown | 2 | 133 | 0.0044728 | 0.003363 | No
01/10/2019 | 20:50 | MR32 | Urban | Asset Failure | LV | 7 | 55 | 0.00057003 | 0.0010364 | No
02/10/2019 | 10:04 | NW11 | Urban | Asset Failure | LV | 4 | 478.1 | 0.0030215 | 0.00063196 | No
02/10/2019 | 11:43 | BH31 | Urban | Vegetation | Grow-in - Other responsible party | 57 | 182 | 0.01639 | 0.0090054 | No
02/10/2019 | 11:50 | EB24 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 136.3 | 0.00021534 | 0.00015799 | No
02/10/2019 | 14:22 | GW12 | Urban | Vegetation | Grow-in - NSP responsibility | 14 | 143 | 0.0031313 | 0.0021897 | No
02/10/2019 | 14:30 | BU14 | Urban | Asset Failure | LV | 1 | 267.4 | 0.00042252 | 0.00015799 | No
02/10/2019 | 15:05 | EB12 | Urban | Asset Failure | Distribution substation | 179 | 98.9 | 0.027969 | 0.02828 | No
02/10/2019 | 23:19 | BU9 | Urban | Asset Failure | LV | 6 | 123 | 0.0011854 | 0.00096374 | No
02/10/2019 | 23:24 | DC6 | Urban | Asset Failure | LV | 2 | 213 | 0.00067304 | 0.00031598 | No
03/10/2019 | 07:20 | FTN14 | Urban | Overloads |  | 1 | 89.2 | 0.00014093 | 0.00015799 | No
03/10/2019 | 07:30 | CFD16 | Urban | Asset Failure | LV | 1 | 74.6 | 0.00011778 | 0.00015799 | No
03/10/2019 | 08:19 | BH23 | Urban | Asset Failure | LV | 1 | 84 | 0.00013271 | 0.00015799 | No
03/10/2019 | 08:28 | STO22 | Urban | Unknown | Unknown | 1 | 126.7 | 0.00020023 | 0.00015799 | No
03/10/2019 | 09:41 | BR1 | Urban | Asset Failure | LV | 1 | 284 | 0.00044861 | 0.00015799 | No
03/10/2019 | 10:08 | MGE14 | Urban | Asset Failure | LV | 4 | 125.9 | 0.00079564 | 0.00063196 | No
03/10/2019 | 11:35 | FTN23 | Urban | Asset Failure | HV | 1 | 355.2 | 0.00056118 | 0.00015799 | No
03/10/2019 | 12:29 | SS21 | Urban | Network Business | Networ Error | 7 | 346 | 0.0038265 | 0.0011059 | No
03/10/2019 | 13:06 | DC2 | Urban | Asset Failure | HV | 34 | 503 | 0.027019 | 0.0053717 | No
03/10/2019 | 13:20 | MTN32 | Rural Short | Asset Failure | LV | 1 | 134.9 | 0.0022686 | 0.0016815 | No
03/10/2019 | 14:56 | CRM34 | Urban | Asset Failure | Distribution substation | 13 | 113.4 | 0.0023051 | 0.0020333 | No
04/10/2019 | 01:27 | DC2 | Urban | Third Party | Other | 1 | 92.1 | 0.00014546 | 0.00015799 | No
04/10/2019 | 08:44 | SS23 | Urban | Third Party | Vehicle Impact | 3,595 | 11.9 | 0.067422 | 0.56797 | No
04/10/2019 | 10:34 | MTN21 | Urban |  | HV | 2,648 | 3.6 | 0.014852 | 0.41836 | No
04/10/2019 | 10:34 | MTN34 | Urban |  | HV | 3,717 | 4 | 0.023304 | 0.58725 | No
04/10/2019 | 13:43 | BT14 | Urban | Asset Failure | LV | 1 | 196.1 | 0.00030974 | 0.00015799 | No
04/10/2019 | 14:03 | STO21 | Rural Short | Asset Failure | LV | 1 | 184 | 0.0025989 | 0.0014125 | No
04/10/2019 | 14:03 | MTN34 | Urban | Asset Failure | LV | 6 | 57 | 0.00056734 | 0.00099534 | No
04/10/2019 | 16:02 | DMA14 | Urban | Asset Failure | LV | 1 | 147.7 | 0.00023332 | 0.00015799 | No
04/10/2019 | 18:38 | FSH21 | Rural Short | Asset Failure | LV | 1 | 392 | 0.0065912 | 0.0016815 | No
04/10/2019 | 18:48 | RBD22 | Urban | Asset Failure | LV | 1 | 57 | 9.0054e-05 | 0.00015799 | No
04/10/2019 | 19:00 | MR12 | Urban | Asset Failure | LV | 1 | 140 | 0.00022119 | 0.00015799 | No
04/10/2019 | 19:15 | GW6 | Urban | Asset Failure | HV | 1,225 | 59.5 | 0.11516 | 0.19354 | No
04/10/2019 | 20:50 | GW6 | Urban | Asset Failure | HV | 1,091 | 3.6 | 0.006234 | 0 | No
04/10/2019 | 20:52 | HGS33 | Rural Short | Asset Failure | LV | 1 | 352 | 0.0059189 | 0.0016815 | No
04/10/2019 | 22:14 | EB24 | Urban | Asset Failure | LV | 1 | 46 | 7.2675e-05 | 0.00015799 | No
05/10/2019 | 18:33 | FSH31 | Urban | Asset Failure | LV | 1 | 131.6 | 0.00020792 | 0.00015799 | No
06/10/2019 | 14:14 | BU9 | Urban | Asset Failure | LV | 53 | 96 | 0.0080385 | 0.0083735 | No
06/10/2019 | 18:00 | EB23 | Urban | Vegetation | Grow-in - NSP responsibility | 30 | 85 | 0.0040771 | 0.0047966 | No
06/10/2019 | 18:54 | FTN25 | Urban | Asset Failure | LV | 1 | 163.3 | 0.00025797 | 0.00015799 | No
06/10/2019 | 19:05 | EL9 | Urban | Third Party | Vehicle Impact | 1 | 115 | 0.00018169 | 0.00015799 | No
06/10/2019 | 21:25 | CRM52 | Urban | Asset Failure | HV | 18 | 175.3 | 0.0049862 | 0.0028438 | No
07/10/2019 | 04:48 | NW31 | Urban | Asset Failure | LV | 2 | 292 | 0.00092266 | 0.00031598 | No
07/10/2019 | 04:48 | NW31 | Urban | Asset Failure | LV | 1 | 292 | 0.00046133 | 0.00015799 | No
07/10/2019 | 07:20 | OR35 | Urban | Asset Failure | LV | 1 | 110 | 0.00017379 | 0.00015799 | No
07/10/2019 | 10:16 | EL7 | Urban | Asset Failure | LV | 1 | 178.6 | 0.00028217 | 0.00015799 | No
07/10/2019 | 13:21 | RWT34 | Urban | Overloads |  | 1 | 64 | 0.00010111 | 0.00015799 | No
07/10/2019 | 14:49 | FSH13 | Urban | Overloads |  | 1 | 111.8 | 0.00017661 | 0.00015799 | No
07/10/2019 | 16:05 | MR15 | Urban | Third Party | Other | 1 | 114.2 | 0.00018042 | 0.00015799 | No
08/10/2019 | 05:10 | DMA15 | Rural Short | Asset Failure | Distribution substation | 6 | 125 | 0.012611 | 0.010089 | No
08/10/2019 | 07:11 | GW12 | Urban | Asset Failure | LV | 9 | 124 | 0.0016809 | 0.0013556 | No
08/10/2019 | 08:14 | STO21 | Rural Short | Asset Failure | LV | 1 | 316 | 0.0053135 | 0.0016815 | No
08/10/2019 | 08:38 | LWN21 | Rural Short | Asset Failure | LV | 1 | 306.1 | 0.0051465 | 0.0016815 | No
08/10/2019 | 13:02 | SV16 | Urban | Asset Failure | LV | 1 | 177.3 | 0.00028014 | 0.00015799 | No
08/10/2019 | 13:32 | EB24 | Urban | Asset Failure | LV | 2 | 103 | 0.00032546 | 0.00031598 | No
08/10/2019 | 16:02 | RBD22 | Urban | Asset Failure | LV | 7 | 106 | 0.0011606 | 0.0010949 | No
08/10/2019 | 17:16 | MR13 | Urban | Asset Failure | LV | 1 | 278.7 | 0.00044032 | 0.00015799 | No
08/10/2019 | 18:11 | FTN21 | Urban | Asset Failure | LV | 20 | 51 | 0.0016486 | 0.0032325 | No
08/10/2019 | 19:05 | M32 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 205 | 0.00032388 | 0.00015799 | No
08/10/2019 | 20:10 | EW8 | Urban | Vegetation | Grow-in - Other responsible party | 8 | 259 | 0.0032736 | 0.0012639 | No
08/10/2019 | 20:40 | GW4 | Urban | Asset Failure | LV | 1 | 60 | 9.4794e-05 | 0.00015799 | No
08/10/2019 | 22:12 | MR14 | Urban | Asset Failure | LV | 1 | 98 | 0.00015483 | 0.00015799 | No
09/10/2019 | 10:51 | MTN21 | Urban | Asset Failure | LV | 1 | 99 | 0.00015641 | 0.00015799 | No
09/10/2019 | 13:25 | CFD12 | Urban | Asset Failure | LV | 1 | 124.9 | 0.0001973 | 0.00015799 | No
09/10/2019 | 15:04 | CRM22 | Urban | Asset Failure | LV | 1 | 75.9 | 0.00011991 | 0.00015799 | No
09/10/2019 | 17:12 | CRM12 | Urban | Asset Failure | LV | 1 | 147.2 | 0.00023253 | 0.00015799 | No
09/10/2019 | 23:58 | RWT34 | Urban | Unknown | Unknown | 17 | 7 | 0.00018613 | 0.002659 | No
10/10/2019 | 12:40 | EB12 | Urban | Asset Failure | LV | 1 | 64.6 | 0.00010201 | 0.00015799 | No
11/10/2019 | 04:57 | LWN21 | Rural Short | Unknown | Unknown | 15 | 48 | 0.012107 | 0.025222 | No
11/10/2019 | 11:00 | FTN24 | Urban | Unknown | Unknown | 3 | 5 | 2.3698e-05 | 0.00047397 | No
11/10/2019 | 11:23 | OR34 | Urban | Asset Failure | LV | 1 | 73 | 0.00011533 | 0.00015799 | No
11/10/2019 | 12:34 | BU14 | Urban | Asset Failure | LV | 1 | 118.8 | 0.00018772 | 0.00015799 | No
11/10/2019 | 17:01 | DMA13 | Rural Short | Asset Failure | LV | 1 | 163.3 | 0.0027464 | 0.0016815 | No
11/10/2019 | 17:04 | STO13 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 301 | 0.00047555 | 0.00015799 | No
11/10/2019 | 18:22 | HGS22 | Rural Short | Asset Failure | LV | 34 | 1,388.0 | 0.79353 | 0.057171 | No
11/10/2019 | 18:55 | EM3 | Urban | Asset Failure | LV | 1 | 38.5 | 6.0852e-05 | 0.00015799 | No
12/10/2019 | 11:06 | LWN33 | Urban | Asset Failure | LV | 1 | 159 | 0.0002512 | 0.00015799 | No
12/10/2019 | 12:26 | FTN21 | Urban | Asset Failure | LV | 29 | 124 | 0.0056245 | 0.0045359 | No
12/10/2019 | 13:20 | FTN12 | Urban | Animal | Other | 1 | 87.5 | 0.00013829 | 0.00015799 | No
12/10/2019 | 15:59 | HGS22 | Rural Short | Asset Failure | HV | 2 | 73.8 | 0.0024813 | 0.003363 | No
13/10/2019 | 07:21 | BT14 | Urban | Asset Failure | LV | 1 | 328.8 | 0.0005195 | 0.00015799 | No
13/10/2019 | 07:49 | OR31 | Urban | Network Business | Networ Error | 2 | 1.9 | 5.951e-06 | 0.00031598 | No
13/10/2019 | 07:49 | OR22 | Urban | Network Business | Networ Error | 8 | 1.9 | 2.3803e-05 | 0.0012639 | No
13/10/2019 | 10:54 | DMA21 | Urban | Asset Failure | LV | 1 | 125.7 | 0.00019851 | 0.00015799 | No
13/10/2019 | 12:18 | NB24 | Urban | Third Party | Other | 1 | 146.9 | 0.00023214 | 0.00015799 | No
14/10/2019 | 15:23 | SVW53 | Urban | Asset Failure | LV | 1 | 67 | 0.00010585 | 0.00015799 | No
14/10/2019 | 20:52 | GW8 | Urban | Asset Failure | LV | 1 | 88.9 | 0.00014048 | 0.00015799 | No
15/10/2019 | 07:35 | HGS22 | Rural Short | Overloads |  | 2 | 85.8 | 0.0028838 | 0.003363 | No
15/10/2019 | 09:17 | NP16 | Urban | Third Party | Dig-in | 1 | 69.7 | 0.00011014 | 0.00015799 | No
15/10/2019 | 11:24 | EM8 | Urban | Asset Failure | LV | 1 | 55.2 | 8.7237e-05 | 0.00015799 | No
15/10/2019 | 12:28 | BU9 | Urban | Unknown | Unknown | 1 | 163.4 | 0.00025808 | 0 | No
15/10/2019 | 15:37 | CRM35 | Urban | Asset Failure | LV | 1 | 111.4 | 0.00017595 | 0.00015799 | No
15/10/2019 | 15:46 | STO21 | Rural Short | Asset Failure | LV | 1 | 94 | 0.0015806 | 0.0016815 | No
15/10/2019 | 17:23 | CDA22 | Urban | Asset Failure | LV | 1 | 206.8 | 0.00032675 | 0.00015799 | No
15/10/2019 | 17:38 | DN13 | Urban | Asset Failure | HV | 79 | 37 | 0.004618 | 0.012481 | No
15/10/2019 | 18:38 | FTN13 | Urban | Asset Failure | LV | 1 | 132 | 0.00020852 | 0.00015799 | No
15/10/2019 | 18:40 | FSH22 | Urban | Asset Failure | LV | 1 | 210.3 | 0.0003322 | 0.00015799 | No
16/10/2019 | 06:55 | MGE34 | Urban | Asset Failure | LV | 5 | 255 | 0.0018734 | 0.00073465 | No
16/10/2019 | 09:18 | DN7 | Urban | Asset Failure | LV | 1 | 301.7 | 0.00047663 | 0.00015799 | No
16/10/2019 | 10:46 | HGS21 | Rural Short | Asset Failure | LV | 1 | 189 | 0.003178 | 0.0016815 | No
16/10/2019 | 11:08 | DVY24 | Rural Short | Third Party | Other | 10 | 99 | 0.016647 | 0.016815 | No
16/10/2019 | 12:48 | BU2 | Urban | Overloads |  | 26 | 82 | 0.0033774 | 0.0041188 | No
16/10/2019 | 13:58 | NP33 | Urban | Unknown | Unknown | 1 | 264.3 | 0.00041762 | 0.00015799 | No
16/10/2019 | 14:20 | CDA22 | Urban | Asset Failure | LV | 74 | 104 | 0.012146 | 0.011679 | No
16/10/2019 | 14:46 | BU2 | Urban | Unknown | Unknown | 1 | 19.3 | 3.0413e-05 | 0.00015799 | No
16/10/2019 | 15:45 | OAK21 | Urban | Asset Failure | LV | 1 | 74.7 | 0.00011794 | 0.00015799 | No
16/10/2019 | 23:50 | CDA21 | Urban | Animal | Animal nesting/burrowing, etc and other | 654 | 53.2 | 0.05492 | 0.10333 | No
17/10/2019 | 03:47 | DMA23 | Rural Short | Weather |  | 10 | 224.3 | 0.037717 | 0.016815 | No
17/10/2019 | 03:57 | DMA15 | Rural Short | Weather |  | 31 | 160.2 | 0.083524 | 0.052126 | No
17/10/2019 | 04:02 | MTN32 | Rural Short | Weather |  | 2 | 306.9 | 0.01032 | 0.003363 | No
17/10/2019 | 10:14 | BW32 | Urban | Asset Failure | LV | 29 | 121 | 0.0056146 | 0.0046402 | No
17/10/2019 | 12:56 | RWT34 | Urban | Weather |  | 1,974 | 33.2 | 0.1036 | 0.31187 | No
17/10/2019 | 13:00 | RWT35 | Urban | Unknown | Unknown | 28 | 42 | 0.0018394 | 0.0043795 | No
17/10/2019 | 13:07 | RWT34 | Urban | Unknown | Unknown | 1 | 34.3 | 5.4243e-05 | 0.00015799 | No
17/10/2019 | 13:22 | CDA24 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 107.3 | 0.00016952 | 0.00015799 | No
17/10/2019 | 13:48 | RBD21 | Rural Short | Asset Failure | LV | 1 | 331.9 | 0.0055812 | 0.0016815 | No
17/10/2019 | 13:55 | FTN11 | Urban | Asset Failure | LV | 1 | 275.8 | 0.00043568 | 0.00015799 | No
17/10/2019 | 14:22 | DMA23 | Rural Short | Network Business | Networ Error | 32 | 178 | 0.095769 | 0.053808 | No
17/10/2019 | 18:18 | STO14 | Rural Short | Asset Failure | LV | 1 | 162 | 0.002724 | 0.0016815 | No
17/10/2019 | 18:45 | BH34 | Urban | Vegetation | Grow-in - Other responsible party | 1,167 | 28.5 | 0.052527 | 0.18437 | No
18/10/2019 | 06:17 | BW33 | Urban | Overloads |  | 1 | 38 | 6.0036e-05 | 0.00015799 | No
18/10/2019 | 07:36 | CRM11 | Urban | Unknown | Unknown | 1 | 143.9 | 0.00022735 | 0.00015799 | No
18/10/2019 | 08:26 | MR15 | Urban | Planned |  | 1 | 8 | 1.2639e-05 | 0.00015799 | No
18/10/2019 | 08:26 | MC1 | Urban | Asset Failure | LV | 1 | 118.3 | 0.00018695 | 0.00015799 | No
18/10/2019 | 10:58 | MTN32 | Rural Short | Weather |  | 1 | 182.2 | 0.0030634 | 0.0016815 | No
18/10/2019 | 13:27 | MR32 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 197.9 | 0.00031258 | 0.00015799 | No
18/10/2019 | 14:31 | DMA12 | Urban | Asset Failure | LV | 1 | 118.1 | 0.00018656 | 0.00015799 | No
18/10/2019 | 15:28 | FSH34 | Urban | Unknown | Unknown | 1 | 127 | 0.00020065 | 0.00015799 | No
18/10/2019 | 15:30 | MGE34 | Urban | Asset Failure | HV | 2,466 | 36.4 | 0.14201 | 0.3896 | No
18/10/2019 | 15:40 | MGE22 | Urban | Unknown | Unknown | 1 | 117.5 | 0.00018569 | 0.00015799 | No
18/10/2019 | 16:34 | MGE23 | Urban | Vegetation | Grow-in - Other responsible party | 34 | 26 | 0.0013966 | 0.0053717 | No
19/10/2019 | 00:03 | NP16 | Urban | Asset Failure | LV | 6 | 85 | 0.00080575 | 0.00094794 | No
19/10/2019 | 02:38 | RBD13 | Urban | Asset Failure | LV | 1 | 237 | 0.00037444 | 0.00015799 | No
19/10/2019 | 02:53 | NW14 | Urban | Third Party | Vehicle Impact | 44 | 67 | 0.0046575 | 0.0069516 | No
19/10/2019 | 07:30 | STO14 | Rural Short | Asset Failure | LV | 1 | 84.4 | 0.0014186 | 0.0016815 | No
19/10/2019 | 09:10 | MTN31 | Urban | Asset Failure | LV | 1 | 79.6 | 0.00012568 | 0.00015799 | No
19/10/2019 | 10:08 | CFD14 | Urban | Asset Failure | LV | 1 | 92 | 0.00014535 | 0.00015799 | No
19/10/2019 | 11:26 | GW12 | Urban | Asset Failure | LV | 1 | 163.1 | 0.00025766 | 0.00015799 | No
19/10/2019 | 12:06 | STO13 | Urban | Asset Failure | HV | 1 | 58.9 | 9.2977e-05 | 0.00015799 | No
19/10/2019 | 14:19 | DMA13 | Rural Short | Asset Failure | LV | 6 | 70.8 | 0.0071396 | 0.010089 | No
19/10/2019 | 16:51 | M33 | Urban | Vegetation | Grow-in - Other responsible party | 3 | 69 | 0.00032704 | 0.00047397 | No
19/10/2019 | 18:15 | MC2 | Urban | Third Party | Vehicle Impact | 2 | 635 | 0.0020065 | 0.00031598 | No
20/10/2019 | 01:45 | NB33 | Urban | Third Party | Other | 1 | 548 | 0.00086578 | 0.00015799 | No
20/10/2019 | 08:15 | HT3 | Urban | Network Business | Networ Error | 12 | 45 | 0.00085315 | 0.0018959 | No
20/10/2019 | 08:53 | BT10 | Urban | Asset Failure | LV | 1 | 167 | 0.00026384 | 0.00015799 | No
20/10/2019 | 09:45 | MC6 | Urban | Asset Failure | LV | 1 | 155 | 0.00024488 | 0.00015799 | No
20/10/2019 | 14:21 | FSH12 | Rural Short | Asset Failure | LV | 2 | 149 | 0.0057875 | 0.0038842 | No
20/10/2019 | 15:33 | FSH21 | Rural Short | Asset Failure | LV | 1 | 35 | 0.00058852 | 0.0016815 | No
20/10/2019 | 17:00 | FTN21 | Urban | Asset Failure | LV | 14 | 1,289.2 | 0.028514 | 0.0022119 | No
20/10/2019 | 21:13 | GW12 | Urban | Asset Failure | LV | 26 | 777 | 0.031917 | 0.0041077 | No
21/10/2019 | 07:50 | EB32 | Urban | Unknown | Unknown | 24 | 128 | 0.0048716 | 0.003806 | No
21/10/2019 | 12:16 | EW1 | Urban | Third Party | Dig-in | 1 | 653.9 | 0.0010331 | 0.00015799 | No
21/10/2019 | 17:32 | K7 | Urban | Third Party | Dig-in | 3 | 147.1 | 0.00069737 | 0.00047397 | No
22/10/2019 | 10:11 | OR24 | Urban | Asset Failure | LV | 2 | 169 | 0.00053401 | 0.00031598 | No
22/10/2019 | 15:25 | SR20 | Urban | Asset Failure | LV | 1 | 265 | 0.00041862 | 0.00015799 | No
22/10/2019 | 17:53 | MC1 | Urban | Asset Failure | LV | 81 | 97 | 0.012413 | 0.012797 | No
22/10/2019 | 18:09 | LWN32 | Rural Short | Weather |  | 1 | 145 | 0.0024387 | 0.0016815 | No
22/10/2019 | 18:26 | SR24 | Urban | Asset Failure | LV | 1 | 1,714.0 | 0.0010832 | 6.3196e-05 | No
22/10/2019 | 18:26 | SR24 | Urban | Asset Failure | LV | 5 | 1,714.0 | 0.01354 | 0.00078995 | No
22/10/2019 | 19:09 | M33 | Urban | Asset Failure | LV | 1 | 141 | 0.00014703 | 0.00010427 | No
22/10/2019 | 19:09 | M21 | Urban | Asset Failure | LV | 31 | 141 | 0.0069102 | 0.0049008 | No
22/10/2019 | 22:02 | HGS33 | Rural Short | Unknown | Unknown | 4 | 284 | 0.019102 | 0.006726 | No
22/10/2019 | 22:26 | BR15 | Urban | Asset Failure | LV | 1 | 91.9 | 0.00014517 | 0.00015799 | No
23/10/2019 | 07:59 | HT7 | Urban | Asset Failure | LV | 11 | 91 | 0.0015815 | 0.0017379 | No
23/10/2019 | 09:45 | FSH32 | Rural Short | Third Party | Vehicle Impact | 9 | 280 | 0.042374 | 0.015133 | No
23/10/2019 | 10:01 | LD5 | Urban | Animal | Animal impact | 7 | 238.2 | 0.0026338 | 0.0011059 | No
23/10/2019 | 10:31 | CM25 | Urban | Third Party | Other | 1 | 194 | 0.0003065 | 0.00015799 | No
23/10/2019 | 15:27 | RBD13 | Urban | Asset Failure | LV | 1 | 123 | 0.00019433 | 0.00015799 | No
23/10/2019 | 16:05 | EB14 | Urban | Asset Failure | LV | 1 | 264.6 | 0.00041807 | 0.00015799 | No
23/10/2019 | 17:02 | K4 | Urban | Asset Failure | LV | 1 | 222.7 | 0.0003519 | 0.00015799 | No
24/10/2019 | 09:14 | MGE21 | Urban | Overloads |  | 6 | 56 | 0.00052554 | 0.00093846 | No
24/10/2019 | 14:59 | GW5 | Urban | Vegetation | Grow-in - Other responsible party | 53 | 136 | 0.011388 | 0.0083735 | No
24/10/2019 | 17:58 | NP36 | Urban | Asset Failure | LV | 1 | 222 | 0.00035074 | 0.00015799 | No
24/10/2019 | 20:41 | M25 | Urban | Asset Failure | LV | 1 | 274 | 0.00043289 | 0.00015799 | No
24/10/2019 | 21:27 | NP25 | Urban | Unknown | Unknown | 71 | 143 | 0.016029 | 0.011209 | No
24/10/2019 | 21:28 | FSH13 | Urban | Unknown | Unknown | 49 | 146.9 | 0.011374 | 0.0077415 | No
24/10/2019 | 21:59 | MR13 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 105.2 | 0.00016613 | 0.00015799 | No
25/10/2019 | 03:07 | FSH22 | Urban | Unknown | Unknown | 1 | 38 | 6.0036e-05 | 0.00015799 | No
25/10/2019 | 03:30 | NB22 | Urban | Vegetation | Grow-in - NSP responsibility | 1,004 | 44.8 | 0.071127 | 0.15862 | No
25/10/2019 | 08:36 | STO21 | Rural Short | Asset Failure | LV | 1 | 74 | 0.0012443 | 0.0016815 | No
25/10/2019 | 09:10 | DSH21 | Urban | Asset Failure | LV | 1 | 259.6 | 0.00041017 | 0.00015799 | No
25/10/2019 | 09:23 | BR4 | Urban | Asset Failure | LV | 1 | 544.5 | 0.00086025 | 0.00015799 | No
25/10/2019 | 12:10 | MGE33 | Urban | Asset Failure | LV | 1 | 70 | 0.00011059 | 0.00015799 | No
26/10/2019 | 00:28 | NP36 | Urban | Asset Failure | LV | 8 | 62 | 0.00078363 | 0.0012639 | No
26/10/2019 | 02:37 | BR9 | Urban | Animal | Animal impact | 1 | 53 | 8.3682e-05 | 0.00015799 | No
26/10/2019 | 07:10 | STO21 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 185 | 0.0031108 | 0.0016815 | No
26/10/2019 | 07:15 | LD3 | Urban | Asset Failure | LV | 1 | 156 | 0.00024646 | 0.00015799 | No
26/10/2019 | 09:02 | MGE34 | Urban | Vegetation | Grow-in - NSP responsibility | 69 | 78 | 0.0084587 | 0.010844 | No
26/10/2019 | 13:35 | GW6 | Urban | Unknown | Unknown | 23 | 55 | 0.0019786 | 0.0035974 | No
26/10/2019 | 15:59 | MTN31 | Urban | Asset Failure | LV | 1 | 126 | 0.00019907 | 0.00015799 | No
26/10/2019 | 20:04 | M13 | Urban | Asset Failure | LV | 1 | 65 | 0.00010275 | 0.00015799 | No
27/10/2019 | 09:14 | STO14 | Rural Short | Asset Failure | LV | 1 | 121 | 0.0020346 | 0.0016815 | No
27/10/2019 | 11:28 | BR6 | Urban | Weather |  | 11 | 113 | 0.0019638 | 0.0017379 | No
27/10/2019 | 12:01 | BR13 | Urban | Asset Failure | LV | 1 | 118.2 | 0.00018669 | 0.00015799 | No
27/10/2019 | 18:05 | OAK26 | Urban | Asset Failure | LV | 1 | 61 | 9.6374e-05 | 0.00015799 | No
28/10/2019 | 10:00 | HGS32 | Urban | Animal | Animal impact | 2,043 | 52.6 | 0.16967 | 0.32277 | No
28/10/2019 | 10:14 | HT9 | Urban | Asset Failure | LV | 1 | 71.5 | 0.00011299 | 0.00015799 | No
28/10/2019 | 15:53 | GW7 | Urban | Third Party | Vehicle Impact | 1,184 | 49.9 | 0.093393 | 0.18706 | No
29/10/2019 | 08:03 | CDA22 | Urban | Weather |  | 1 | 109.9 | 0.00017358 | 0.00015799 | No
29/10/2019 | 12:29 | HGS23 | Rural Short | Planned |  | 4 | 76 | 0.0048561 | 0.0063897 | No
29/10/2019 | 16:30 | STO14 | Rural Short | Asset Failure | LV | 1 | 89 | 0.0014971 | 0.0016815 | No
29/10/2019 | 20:55 | EM10 | Urban | Asset Failure | LV | 11 | 85 | 0.0015215 | 0.00179 | No
30/10/2019 | 00:30 | EL7 | Urban | Unknown | Unknown | 50 | 114.3 | 0.0090304 | 0.0078995 | No
30/10/2019 | 02:42 | DMA23 | Rural Short | Animal | Other | 1 | 382.1 | 0.0064247 | 0.0016815 | No
30/10/2019 | 06:50 | BU6 | Urban | Asset Failure | LV | 1 | 55 | 8.6894e-05 | 0.00015799 | No
30/10/2019 | 14:29 | BR4 | Urban | Asset Failure | HV | 422 | 350.3 | 0.23356 | 0.066672 | No
30/10/2019 | 14:34 | BR4 | Urban | Asset Failure | HV | 1,017 | 30.7 | 0.049327 | 0.16068 | No
30/10/2019 | 17:08 | MTN24 | Rural Short | Asset Failure | Distribution substation | 5 | 67 | 0.0056302 | 0.0084075 | No
30/10/2019 | 21:43 | CFD13 | Urban | Third Party | Other | 1 | 138 | 0.00021803 | 0.00015799 | No
30/10/2019 | 22:35 | SR15 | Urban | Vegetation | Grow-in - Other responsible party | 39 | 85 | 0.0052736 | 0.0062043 | No
31/10/2019 | 09:50 | M11 | Urban | Third Party | Dig-in | 2 | 400 | 0.0012639 | 0.00031598 | No
31/10/2019 | 11:01 | RWT24 | Urban | Overloads |  | 22 | 85 | 0.0030135 | 0.0035453 | No
31/10/2019 | 11:31 | BR6 | Urban | Vegetation | Grow-in - Other responsible party | 27 | 134 | 0.0057288 | 0.0042752 | No
31/10/2019 | 11:48 | K2 | Urban | Asset Failure | LV | 14 | 87 | 0.0018652 | 0.0021439 | No
31/10/2019 | 15:37 | HGS23 | Rural Short | Asset Failure | LV | 12 | 232.9 | 0.046994 | 0.020178 | No
31/10/2019 | 15:43 | HGS23 | Rural Short | Asset Failure | LV | 1 | 226.6 | 0.00381 | 0.0016815 | No
31/10/2019 | 20:10 | DN10 | Urban | Unknown | Unknown | 51 | 100 | 0.0081333 | 0.0081333 | No
31/10/2019 | 20:23 | M22 | Urban | Asset Failure | LV | 110 | 151 | 0.026242 | 0.017379 | No
01/11/2019 | 05:32 | NP25 | Urban | Asset Failure | LV | 32 | 106 | 0.0053858 | 0.005081 | No
01/11/2019 | 08:39 | MTN21 | Urban | Overloads |  | 1 | 65.3 | 0.00010312 | 0.00015799 | No
01/11/2019 | 09:32 | BH12 | Urban | Asset Failure | LV | 1 | 67.5 | 0.00010659 | 0.00015799 | No
01/11/2019 | 14:51 | MC4 | Urban | Asset Failure | LV | 2 | 228.2 | 0.00072117 | 0.00031598 | No
01/11/2019 | 16:17 | CFD15 | Urban | Asset Failure | LV | 8 | 158 | 0.001997 | 0.0012639 | No
01/11/2019 | 16:42 | OAK33 | Urban | Asset Failure | LV | 1 | 287.3 | 0.00045388 | 0.00015799 | No
01/11/2019 | 17:34 | MGE23 | Urban | Asset Failure | LV | 1 | 258 | 0.00040761 | 0.00015799 | No
01/11/2019 | 17:54 | DC5 | Urban | Asset Failure | LV | 1 | 170.2 | 0.00026885 | 0.00015799 | No
01/11/2019 | 18:11 | M32 | Urban | Overloads |  | 1 | 228.8 | 0.00036148 | 0.00015799 | No
01/11/2019 | 18:41 | STO13 | Urban | Asset Failure | LV | 13 | 154 | 0.0031313 | 0.0020333 | No
01/11/2019 | 22:28 | EL7 | Urban | Unknown | Unknown | 50 | 146.5 | 0.011574 | 0.0078995 | No
02/11/2019 | 07:02 | SVW53 | Urban | Asset Failure | LV | 1 | 173 | 0.00027332 | 0.00015799 | No
02/11/2019 | 07:36 | EW1 | Urban | Asset Failure | LV | 1 | 338 | 0.00053401 | 0.00015799 | No
02/11/2019 | 11:16 | MC3 | Urban | Asset Failure | LV | 1 | 100.7 | 0.00015912 | 0.00015799 | No
02/11/2019 | 11:46 | BT2 | Urban | Asset Failure | LV | 1 | 149 | 0.00023541 | 0.00015799 | No
02/11/2019 | 11:59 | NW33 | Urban | Asset Failure | LV | 1 | 265 | 0.00041867 | 0.00015799 | No
02/11/2019 | 12:12 | MC9 | Urban | Animal | Other | 1 | 272.5 | 0.0004305 | 0.00015799 | No
02/11/2019 | 13:45 | BH22 | Urban | Asset Failure | LV | 2 | 195 | 0.00072707 | 0.00037286 | No
02/11/2019 | 15:22 | GW11 | Urban | Asset Failure | LV | 1 | 271.3 | 0.0004286 | 0.00015799 | No
02/11/2019 | 15:44 | HT11 | Urban | Asset Failure | HV | 1,535 | 7.6 | 0.018453 | 0.24251 | No
02/11/2019 | 16:03 | OAK23 | Urban | Asset Failure | LV | 1 | 197 | 0.00031124 | 0.00015799 | No
02/11/2019 | 18:52 | DMA23 | Rural Short | Vegetation | Grow-in - NSP responsibility | 34 | 268 | 0.15322 | 0.057171 | No
02/11/2019 | 21:42 | RWT35 | Urban | Asset Failure | LV | 48 | 213 | 0.016153 | 0.0075835 | No
02/11/2019 | 22:32 | STO21 | Rural Short | Asset Failure | LV | 9 | 238 | 0.035657 | 0.014982 | No
03/11/2019 | 00:54 | LD2 | Urban | Unknown | Unknown | 30 | 228 | 0.010807 | 0.0047397 | No
03/11/2019 | 00:54 | LD2 | Urban | Third Party | Vehicle Impact | 43 | 228.8 | 0.015544 | 0.0067936 | No
03/11/2019 | 11:01 | CRM21 | Urban | Animal | Other | 6 | 212.5 | 0.0020141 | 0.00094794 | No
03/11/2019 | 16:08 | OE9 | Urban | Asset Failure | LV | 1 | 111.3 | 0.00017579 | 0.00015799 | No
04/11/2019 | 08:13 | EL6 | Urban | Asset Failure | LV | 1 | 100 | 0.00015799 | 0.00015799 | No
04/11/2019 | 09:40 | EM10 | Urban | Unknown | Unknown | 1 | 214.1 | 0.0003382 | 0.00015799 | No
04/11/2019 | 10:26 | NP11 | Urban | Asset Failure | LV | 1 | 153.1 | 0.00024194 | 0.00015799 | No
04/11/2019 | 14:35 | CFD26 | Urban | Asset Failure | LV | 1 | 144.3 | 0.00022795 | 0.00015799 | No
04/11/2019 | 14:40 | OAK33 | Urban | Asset Failure | LV | 1 | 514.9 | 0.00081346 | 0.00015799 | No
04/11/2019 | 17:11 | CDA23 | Urban | Unknown | Unknown | 1 | 39 | 6.1616e-05 | 0.00015799 | No
04/11/2019 | 18:31 | NP33 | Urban | Asset Failure | LV | 1 | 223.6 | 0.00035332 | 0.00015799 | No
04/11/2019 | 22:53 | NB25 | Urban | Asset Failure | LV | 1 | 73 | 0.00011538 | 0.00015799 | No
05/11/2019 | 01:30 | BW22 | Urban | Asset Failure | HV | 2 | 494.3 | 0.0015619 | 0.00031598 | No
05/11/2019 | 06:33 | HGS23 | Rural Short | Animal | Animal impact | 1 | 252 | 0.0042374 | 0.0016815 | No
05/11/2019 | 09:41 | BT9 | Urban | Asset Failure | LV | 1 | 93.2 | 0.00014727 | 0.00015799 | No
05/11/2019 | 10:11 | STO21 | Rural Short | Asset Failure | LV | 1 | 139 | 0.0023373 | 0.0016815 | No
05/11/2019 | 12:26 | EB33 | Urban | Asset Failure | LV | 1 | 168.9 | 0.00026677 | 0.00015799 | No
05/11/2019 | 12:47 | LWN35 | Urban | Weather |  | 1 | 103 | 0.00016265 | 0.00015799 | No
05/11/2019 | 14:37 | OE4 | Urban | Unknown | Unknown | 1 | 233 | 0.00036812 | 0.00015799 | No
05/11/2019 | 20:32 | M31 | Urban | Unknown | Unknown | 1 | 217.6 | 0.00034384 | 0.00015799 | No
05/11/2019 | 20:41 | RBD11 | Urban | Asset Failure | LV | 1 | 66.7 | 0.0001053 | 0.00015799 | No
06/11/2019 | 06:14 | NW13 | Urban | Asset Failure | LV | 2 | 402.3 | 0.0012711 | 0.00031598 | No
06/11/2019 | 11:18 | EB31 | Urban | Vegetation | Grow-in - NSP responsibility | 1,749 | 16 | 0.044182 | 0.27632 | No
06/11/2019 | 12:28 | EB31 | Urban | Asset Failure | LV | 31 | 166.9 | 0.0081811 | 0.0049008 | No
06/11/2019 | 12:39 | SS12 | Urban | Asset Failure | LV | 1 | 90.1 | 0.00014227 | 0.00015799 | No
06/11/2019 | 12:42 | HT10 | Urban | Asset Failure | LV | 1 | 337.8 | 0.00053366 | 0.00015799 | No
06/11/2019 | 17:46 | HGS21 | Rural Short | Asset Failure | LV | 1 | 224 | 0.0037665 | 0.0016815 | No
06/11/2019 | 18:09 | FTN12 | Urban | Asset Failure | LV | 43 | 171 | 0.011617 | 0.0067936 | No
06/11/2019 | 18:34 | HGS22 | Rural Short | Asset Failure | LV | 1 | 286 | 0.0048091 | 0.0016815 | No
07/11/2019 | 07:38 | MGE32 | Urban | Network Business | Networ Error | 1 | 77 | 0.00012165 | 0.00015799 | No
07/11/2019 | 11:05 | SS22 | Urban | Asset Failure | LV | 1 | 159.7 | 0.00025236 | 0.00015799 | No
07/11/2019 | 13:24 | MTN31 | Urban | Asset Failure | LV | 1 | 66 | 0.00010422 | 0.00015799 | No
07/11/2019 | 15:45 | HGS22 | Rural Short | Third Party | Vehicle Impact | 15 | 345 | 0.087017 | 0.025222 | No
07/11/2019 | 16:05 | OR32 | Urban | Asset Failure | LV | 1 | 165.7 | 0.00026184 | 0.00015799 | No
07/11/2019 | 17:07 | MC3 | Urban | Asset Failure | LV | 12 | 562.1 | 0.010657 | 0.0018959 | No
07/11/2019 | 18:21 | MTN21 | Urban | Asset Failure | LV | 35 | 204 | 0.01128 | 0.0055296 | No
07/11/2019 | 19:15 | OE9 | Urban | Asset Failure | LV | 1 | 129 | 0.00020383 | 0.00015799 | No
07/11/2019 | 19:36 | OR33 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 234 | 0.0003697 | 0.00015799 | No
07/11/2019 | 19:54 | LD2 | Urban | Asset Failure | LV | 1 | 65 | 0.00010269 | 0.00015799 | No
07/11/2019 | 20:10 | KBH31 | Urban | Asset Failure | HV | 68 | 20 | 0.0021487 | 0.010743 | No
07/11/2019 | 22:08 | NW33 | Urban | Animal | Animal impact | 106 | 122 | 0.020431 | 0.016747 | No
07/11/2019 | 22:18 | LWN21 | Rural Short | Unknown | Unknown | 2 | 196.6 | 0.0066111 | 0.003363 | No
08/11/2019 | 02:02 | SH24 | Urban | Asset Failure | HV | 23 | 43 | 0.0015625 | 0.0036338 | No
08/11/2019 | 11:14 | DSH14 | Urban | Asset Failure | LV | 1 | 135.7 | 0.00021445 | 0.00015799 | No
08/11/2019 | 11:54 | CDA11 | Urban | Third Party | Vehicle Impact | 55 | 111 | 0.0096067 | 0.0086547 | No
08/11/2019 | 13:40 | DC10 | Urban | Overloads |  | 14 | 60 | 0.0013271 | 0.0022119 | No
08/11/2019 | 14:03 | LD1 | Urban | Overloads |  | 1 | 86.9 | 0.00013727 | 0.00015799 | No
08/11/2019 | 14:22 | DC10 | Urban | Overloads |  | 11 | 17.5 | 0.00029224 | 0.0016684 | No
08/11/2019 | 16:29 | CFD14 | Urban | Asset Failure | LV | 1 | 113.5 | 0.00017932 | 0.00015799 | No
08/11/2019 | 17:41 | NW31 | Urban | Asset Failure | LV | 1 | 77.1 | 0.00012181 | 0.00015799 | No
08/11/2019 | 19:32 | DMA21 | Urban | Asset Failure | LV | 43 | 43 | 0.0028879 | 0.0067161 | No
08/11/2019 | 19:52 | RBD21 | Rural Short | Asset Failure | LV | 2 | 163 | 0.0054817 | 0.003363 | No
08/11/2019 | 23:30 | FSH12 | Rural Short | Asset Failure | LV | 1 | 180 | 0.0030267 | 0.0016815 | No
09/11/2019 | 00:21 | MC6 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 59 | 1.2 | 0.0001072 | 0.0093214 | No
09/11/2019 | 08:14 | EW3 | Urban | Asset Failure | LV | 1 | 80.5 | 0.00012718 | 0.00015799 | No
09/11/2019 | 12:27 | SR15 | Urban | Asset Failure | LV | 1 | 301.1 | 0.00047563 | 0.00015799 | No
09/11/2019 | 18:05 | HGS32 | Urban | Third Party | Other | 1 | 285 | 0.00045027 | 0.00015799 | No
10/11/2019 | 12:45 | STO14 | Rural Short | Asset Failure | LV | 1 | 219.8 | 0.0036951 | 0.0016815 | No
10/11/2019 | 16:28 | STO14 | Rural Short | Asset Failure | LV | 1 | 61.2 | 0.0010282 | 0.0016815 | No
10/11/2019 | 19:26 | BR15 | Urban | Asset Failure | LV | 1 | 183.7 | 0.00029015 | 0.00015799 | No
10/11/2019 | 19:57 | RBD21 | Rural Short | Asset Failure | LV | 1 | 197.5 | 0.0033201 | 0.0016815 | No
11/11/2019 | 07:44 | NB35 | Urban | Unknown | Unknown | 19 | 106 | 0.0031501 | 0.0029718 | No
11/11/2019 | 07:46 | BT9 | Urban | Vegetation | Grow-in - Other responsible party | 904 | 57.7 | 0.082337 | 0.14282 | No
11/11/2019 | 07:47 | BT9 | Urban |  | HV | 1,061 | 123.5 | 0.20708 | 0.16763 | No
11/11/2019 | 07:47 | CFD15 | Urban |  | HV | 1,633 | 4.5 | 0.011524 | 0.258 | No
11/11/2019 | 09:55 | BT9 | Urban | Vegetation | Grow-in - Other responsible party | 168 | 465 | 0.12342 | 0.026542 | No
11/11/2019 | 09:55 | BT9 | Urban | Vegetation | Grow-in - Other responsible party | 149 | 477 | 0.11229 | 0.02354 | No
11/11/2019 | 10:39 | DMA14 | Urban | Vegetation | Grow-in - Other responsible party | 35 | 169 | 0.0093451 | 0.0055296 | No
11/11/2019 | 19:33 | DC3 | Urban | Unknown | Unknown | 1 | 143.2 | 0.00022619 | 0.00015799 | No
12/11/2019 | 00:15 | MGE24 | Urban | Asset Failure | LV | 1 | 64 | 0.00010111 | 0.00015799 | No
12/11/2019 | 00:41 | BT9 | Urban | Asset Failure | LV | 1 | 97.2 | 0.00015351 | 0.00015799 | No
12/11/2019 | 01:00 | RWT23 | Urban | Asset Failure | HV | 468 | 107 | 0.079115 | 0 | No
12/11/2019 | 09:23 | MR11 | Urban | Third Party | Other | 1 | 102 | 0.00016115 | 0.00015799 | No
12/11/2019 | 10:32 | MTN32 | Rural Short | Asset Failure | LV | 1 | 437.5 | 0.007356 | 0.0016815 | No
12/11/2019 | 16:43 | DN7 | Urban | Asset Failure | LV | 1 | 193.2 | 0.00030516 | 0.00015799 | No
12/11/2019 | 20:40 | M11 | Urban | Asset Failure | LV | 1 | 154.5 | 0.00024404 | 0.00015799 | No
13/11/2019 | 00:43 | RBD14 | Urban | Third Party | Vehicle Impact | 895 | 195.6 | 0.27658 | 0.1414 | No
13/11/2019 | 05:19 | DMA24 | Rural Short | Animal | Other | 2 | 241 | 0.0081048 | 0.003363 | No
13/11/2019 | 09:23 | FTN21 | Urban | Asset Failure | LV | 1 | 292 | 0.00046133 | 0.00015799 | No
13/11/2019 | 16:51 | RBD24 | Urban | Asset Failure | LV | 1 | 274 | 0.00043289 | 0.00015799 | No
13/11/2019 | 17:31 | MGE23 | Urban | Asset Failure | LV | 41 | 464 | 0.030056 | 0.0064776 | No
13/11/2019 | 19:26 | MGE23 | Urban | Asset Failure | LV | 15 | 384 | 0.0091002 | 0.0023698 | No
13/11/2019 | 23:03 | CM25 | Urban | Asset Failure | LV | 47 | 117 | 0.0086879 | 0.0074255 | No
14/11/2019 | 00:12 | LD7 | Urban | Asset Failure | LV | 6 | 68 | 0.0006446 | 0.00094794 | No
14/11/2019 | 05:22 | LWN21 | Rural Short | Animal | Animal impact | 1 | 127.1 | 0.0021369 | 0.0016815 | No
14/11/2019 | 10:50 | RD4 | Urban | Asset Failure | LV | 1 | 106.3 | 0.00016786 | 0.00015799 | No
14/11/2019 | 12:40 | DC5 | Urban | Asset Failure | LV | 1 | 115.9 | 0.00018316 | 0.00015799 | No
14/11/2019 | 13:36 | LD4 | Urban | Unknown | Unknown | 1 | 144 | 0.0002275 | 0.00015799 | No
14/11/2019 | 16:02 | NO7 | Urban | Asset Failure | LV | 1 | 238 | 0.00037602 | 0.00015799 | No
14/11/2019 | 17:40 | NB22 | Urban | Asset Failure | LV | 1 | 249.8 | 0.00039463 | 0.00015799 | No
14/11/2019 | 17:44 | FSH21 | Rural Short | Other | XXX | 30 | 17 | 0.0085756 | 0.050445 | No
14/11/2019 | 22:22 | EB31 | Urban | Asset Failure | LV | 1 | 157.1 | 0.0002482 | 0.00015799 | No
15/11/2019 | 00:20 | FSH13 | Urban | Asset Failure | LV | 6 | 70 | 0.00066356 | 0.00094794 | No
15/11/2019 | 07:53 | FTN24 | Urban | Third Party | Vehicle Impact | 27 | 163 | 0.0069531 | 0.0042657 | No
15/11/2019 | 13:34 | EL14 | Urban | Asset Failure | LV | 1 | 105.9 | 0.00016736 | 0.00015799 | No
15/11/2019 | 16:19 | RBD24 | Urban | Asset Failure | Distribution substation | 38 | 11 | 0.00065379 | 0.0059436 | No
15/11/2019 | 22:39 | HGS21 | Rural Short | Animal | Other | 4 | 63.9 | 0.0042945 | 0.006726 | No
16/11/2019 | 08:19 | EW2 | Urban | Asset Failure | LV | 22 | 101 | 0.0035807 | 0.0035453 | No
16/11/2019 | 10:19 | NP33 | Urban | Third Party | Vehicle Impact | 1 | 180.7 | 0.00028551 | 0.00015799 | No
16/11/2019 | 11:26 | EW14 | Urban | Asset Failure | LV | 1 | 104 | 0.00016431 | 0.00015799 | No
17/11/2019 | 07:05 | K4 | Urban | Asset Failure | LV | 1 | 130 | 0.00020539 | 0.00015799 | No
17/11/2019 | 10:21 | WD14 | Urban | Asset Failure | LV | 1 | 85 | 0.00013429 | 0.00015799 | No
18/11/2019 | 00:06 | CDA24 | Urban | Asset Failure | LV | 4 | 124 | 0.00080322 | 0.00064776 | No
18/11/2019 | 06:39 | K7 | Urban | Asset Failure | LV | 1 | 34 | 5.3717e-05 | 0.00015799 | No
18/11/2019 | 10:40 | EB12 | Urban | Asset Failure | LV | 1 | 50 | 7.8995e-05 | 0.00015799 | No
18/11/2019 | 10:48 | DSH32 | Urban | Asset Failure | LV | 2 | 101.6 | 0.00032088 | 0.00031598 | No
18/11/2019 | 12:25 | MGE34 | Urban | Asset Failure | LV | 18 | 35 | 0.0010036 | 0.0028675 | No
18/11/2019 | 13:53 | OR23 | Urban | Third Party | Other | 1 | 35.5 | 5.6113e-05 | 0.00015799 | No
18/11/2019 | 14:52 | FSH34 | Urban | Unknown | Unknown | 1 | 72.4 | 0.00011436 | 0.00015799 | No
18/11/2019 | 15:05 | EB31 | Urban | Network Business | Networ Error | 61 | 10 | 0.00096374 | 0.0096374 | No
18/11/2019 | 15:44 | RWT24 | Urban | Asset Failure | LV | 1 | 56 | 8.8474e-05 | 0.00015799 | No
18/11/2019 | 16:11 | BU4 | Urban | Asset Failure | LV | 17 | 72 | 0.0018769 | 0.0026068 | No
18/11/2019 | 19:44 | MGE34 | Urban | Asset Failure | LV | 3 | 135.2 | 0.00064057 | 0.00047397 | No
19/11/2019 | 07:14 | OR35 | Urban | Asset Failure | LV | 1 | 119 | 0.00018801 | 0.00015799 | No
19/11/2019 | 09:35 | NW22 | Urban | Third Party | Other | 1 | 60.7 | 9.5873e-05 | 0.00015799 | No
19/11/2019 | 11:42 | LWN24 | Urban | Third Party | Other | 1 | 78 | 0.00012323 | 0.00015799 | No
19/11/2019 | 13:00 | GW8 | Urban | Asset Failure | LV | 1 | 240 | 0.00037918 | 0.00015799 | No
20/11/2019 | 01:58 | HGS33 | Rural Short | Animal | Animal impact | 3 | 106.8 | 0.005385 | 0.0050445 | No
20/11/2019 | 04:12 | HGS22 | Rural Short | Animal | Animal impact | 4 | 47.2 | 0.0031713 | 0.006726 | No
20/11/2019 | 05:05 | MC2 | Urban | Unknown | Unknown | 2 | 143 | 0.00045185 | 0.00031598 | No
20/11/2019 | 07:07 | HGS31 | Rural Short | Unknown | Unknown | 2 | 52.4 | 0.0017605 | 0.003363 | No
20/11/2019 | 08:02 | BW23 | Urban | Asset Failure | LV | 8 | 128 | 0.0015349 | 0.0011991 | No
20/11/2019 | 10:21 | STO13 | Urban | Unknown | Unknown | 3 | 219 | 0.001038 | 0.00047397 | No
20/11/2019 | 11:47 | HGS23 | Rural Short | Unknown | Unknown | 5 | 402.5 | 0.03384 | 0.0084075 | No
20/11/2019 | 12:09 | STO13 | Urban | Network Business | Networ Error | 1 | 365.3 | 0.00057716 | 0.00015799 | No
20/11/2019 | 12:12 | BH31 | Urban | Asset Failure | LV | 89 | 78 | 0.010968 | 0.014061 | No
20/11/2019 | 12:57 | DN21 | Urban | Asset Failure | LV | 1 | 192.6 | 0.00030431 | 0.00015799 | No
20/11/2019 | 13:12 | DN11 | Urban | Third Party | Vehicle Impact | 1 | 77.1 | 0.00012178 | 0.00015799 | No
20/11/2019 | 16:14 | FSH31 | Urban | Asset Failure | LV | 1 | 343.2 | 0.00054225 | 0.00015799 | No
20/11/2019 | 16:34 | RD4 | Urban | Vegetation | Grow-in - Other responsible party | 60 | 56 | 0.0053138 | 0.0094889 | No
20/11/2019 | 17:07 | K3 | Urban | Other | XXX | 33 | 352.5 | 0.018377 | 0.0052137 | No
20/11/2019 | 17:07 | K6 | Urban | Other | XXX | 53 | 352.5 | 0.029515 | 0.0083735 | No
20/11/2019 | 17:33 | FSH33 | Urban | Unknown | Unknown | 6 | 157 | 0.0013915 | 0.00088632 | No
20/11/2019 | 20:41 | FTN14 | Urban | Asset Failure | LV | 3 | 84 | 0.00035036 | 0.00041709 | No
20/11/2019 | 20:42 | LD7 | Urban | Third Party | Other | 1 | 117.4 | 0.00018548 | 0.00015799 | No
21/11/2019 | 00:24 | RWT12 | Urban | Animal | Other | 1 | 67.2 | 0.00010622 | 0.00015799 | No
21/11/2019 | 00:31 | FSH33 | Urban | Third Party | Other | 17 | 359 | 0.0096421 | 0.0026858 | No
21/11/2019 | 08:33 | FTN11 | Urban | Unknown | Unknown | 1 | 116.5 | 0.00018409 | 0.00015799 | No
21/11/2019 | 09:03 | K4 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 789 | 27.6 | 0.034456 | 0.12465 | No
21/11/2019 | 09:19 | DC1 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 2 | 491 | 0.0015515 | 0.00031598 | No
21/11/2019 | 09:24 | NB35 | Urban | Asset Failure | Distribution substation | 74 | 176 | 0.020577 | 0.011691 | No
21/11/2019 | 09:25 | K8 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 43 | 605 | 0.041101 | 0.0067936 | No
21/11/2019 | 09:57 | CM25 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 34 | 23.5 | 0.0012597 | 0.0053717 | No
21/11/2019 | 09:57 | CM13 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1,056 | 353.5 | 0.58975 | 0.16684 | No
21/11/2019 | 10:18 | BU9 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 43 | 667 | 0.045313 | 0.0067936 | No
21/11/2019 | 10:21 | BU9 | Urban | Weather |  | 17 | 54 | 0.001464 | 0.0027111 | No
21/11/2019 | 10:35 | SS11 | Urban | Weather |  | 20 | 100 | 0.0032325 | 0.0032325 | No
21/11/2019 | 10:40 | BH23 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 64 | 225 | 0.022758 | 0.010115 | No
21/11/2019 | 11:00 | BH34 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1,171 | 26.2 | 0.048441 | 0.18501 | No
21/11/2019 | 11:09 | HGS22 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2,604 | 68.4 | 2.9956 | 4.3786 | No
21/11/2019 | 11:35 | DC3 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1,559 | 21.5 | 0.052886 | 0.24631 | No
21/11/2019 | 11:51 | SR25 | Urban | Third Party | Other | 51 | 894 | 0.072034 | 0.0080575 | No
21/11/2019 | 12:05 | OAK35 | Urban | Weather |  | 1 | 1,371.2 | 0.0021663 | 0.00015799 | No
21/11/2019 | 12:08 | GW4 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 684 | 68.5 | 0.074031 | 0.10807 | No
21/11/2019 | 12:12 | GW7 | Urban | Overloads |  | 25 | 511 | 0.019981 | 0.0039102 | No
21/11/2019 | 12:56 | GW4 | Urban | Third Party | Other | 1 | 57.3 | 9.0476e-05 | 0.00015799 | No
21/11/2019 | 13:04 | FSH32 | Rural Short | Weather |  | 37 | 104 | 0.064704 | 0.062215 | No
21/11/2019 | 13:34 | GW4 | Urban | Overloads |  | 28 | 428.6 | 0.018992 | 0.0044316 | No
21/11/2019 | 13:34 | GW4 | Urban | Overloads |  | 28 | 428.4 | 0.019206 | 0.0044838 | No
21/11/2019 | 13:39 | MTN24 | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 7 | 48.3 | 0.0056851 | 0.01177 | No
21/11/2019 | 14:14 | BW33 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 731 | 36 | 0.041519 | 0.11549 | No
21/11/2019 | 14:23 | RWT24 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 3,148 | 34.3 | 0.17066 | 0.49735 | No
21/11/2019 | 14:25 | RD10 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 971 | 123.8 | 0.18992 | 0.15341 | No
21/11/2019 | 14:27 | RWT24 | Urban | Overloads |  | 141 | 93 | 0.020717 | 0.022277 | No
21/11/2019 | 14:31 | RWT12 | Urban | Overloads |  | 71 | 104 | 0.011666 | 0.011217 | No
21/11/2019 | 14:32 | MR13 | Urban | Overloads |  | 19 | 268 | 0.0080914 | 0.0030192 | No
21/11/2019 | 14:35 | WD34 | Urban | Weather |  | 23 | 430 | 0.015693 | 0.0036496 | No
21/11/2019 | 14:36 | RWT12 | Urban | Weather |  | 8 | 369 | 0.0046639 | 0.0012639 | No
21/11/2019 | 14:36 | DC8 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1,009 | 117.8 | 0.18781 | 0.15941 | No
21/11/2019 | 14:42 | CFD22 | Urban | Asset Failure | HV | 1,311 | 96.8 | 0.20059 | 0.20712 | No
21/11/2019 | 14:47 | BU14 | Urban | Weather |  | 6 | 443 | 0.0043883 | 0.0009906 | No
21/11/2019 | 15:00 | FSH23 | Rural Short | Overloads |  | 1 | 404.3 | 0.0067974 | 0.0016815 | No
21/11/2019 | 15:02 | WD23 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 476 | 46.7 | 0.035082 | 0.075203 | No
21/11/2019 | 15:04 | BU14 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 100 | 416 | 0.065724 | 0.015799 | No
21/11/2019 | 15:07 | MGE23 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 943 | 48.5 | 0.072257 | 0.14898 | No
21/11/2019 | 15:10 | DC10 | Urban | Weather |  | 45 | 445 | 0.031637 | 0.0071095 | No
21/11/2019 | 15:18 | DC7 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 342 | 8.2 | 0.004412 | 0.054033 | No
21/11/2019 | 15:18 | DC8 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 2,040 | 43.4 | 0.13994 | 0.3223 | No
21/11/2019 | 15:19 | BU9 | Urban | Asset Failure | LV | 20 | 61 | 0.001966 | 0.003223 | No
21/11/2019 | 15:19 | BU9 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 33 | 439 | 0.022888 | 0.0052137 | No
21/11/2019 | 15:23 | OR33 | Urban | Asset Failure | HV | 39 | 547 | 0.033704 | 0.0061616 | No
21/11/2019 | 15:23 | BU6 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 50.9 | 8.0364e-05 | 0.00015799 | No
21/11/2019 | 15:23 | BU4 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1,479 | 59.8 | 0.1398 | 0.23367 | No
21/11/2019 | 15:27 | MC5 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 411 | 15.8 | 0.010249 | 0.064934 | No
21/11/2019 | 15:38 | DC2 | Urban | Weather |  | 9 | 416.6 | 0.0059241 | 0.0014219 | No
21/11/2019 | 15:38 | GW2 | Urban | Unknown | Unknown | 1 | 636.6 | 0.0010057 | 0.00015799 | No
21/11/2019 | 15:44 | MC6 | Urban | Weather |  | 13 | 46 | 0.00091135 | 0.0019812 | No
21/11/2019 | 15:45 | MC6 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 176.1 | 0.00027822 | 0.00015799 | No
21/11/2019 | 16:26 | SH24 | Urban | Overloads |  | 37 | 179 | 0.010452 | 0.0058393 | No
21/11/2019 | 16:27 | DC8 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 9 | 139.7 | 0.0019864 | 0 | No
21/11/2019 | 16:28 | BH31 | Urban | Overloads |  | 17 | 297 | 0.0077423 | 0.0026068 | No
21/11/2019 | 16:30 | STO14 | Rural Short | Weather |  | 145 | 420 | 1.024 | 0.24382 | No
21/11/2019 | 16:36 | EM7 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 535 | 84.1 | 0.071098 | 0.084525 | No
21/11/2019 | 16:36 | EM5 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1,570 | 57.2 | 0.14192 | 0.24804 | No
21/11/2019 | 16:53 | DMA24 | Rural Short |  | Zone substation | 1,970 | 3.1 | 0.10214 | 3.3125 | No
21/11/2019 | 16:53 | DMA23 | Rural Short |  | Zone substation | 2,495 | 39.6 | 1.6617 | 4.1953 | No
21/11/2019 | 16:53 | DMA21 | Urban |  | Zone substation | 3,108 | 3.1 | 0.01514 | 0.49103 | No
21/11/2019 | 17:41 | EB32 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 251.2 | 0.00039692 | 0.00015799 | No
21/11/2019 | 18:00 | EM7 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 533 | 39.6 | 0.033305 | 0.084209 | No
21/11/2019 | 18:20 | EL8 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 1,059.5 | 0.0016739 | 0.00015799 | No
21/11/2019 | 18:44 | STO21 | Rural Short | Asset Failure | LV | 1 | 361 | 0.0060702 | 0.0016815 | No
21/11/2019 | 18:47 | HT10 | Urban | Weather |  | 57 | 178 | 0.01603 | 0.0090054 | No
21/11/2019 | 19:15 | SR20 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 1,004.5 | 0.0015869 | 0.00015799 | No
21/11/2019 | 19:21 | BT15 | Urban | Weather |  | 141 | 168.9 | 0.037618 | 0.022277 | No
21/11/2019 | 20:17 | BT15 | Urban | Third Party | Other | 1 | 132.6 | 0.00020952 | 0.00015799 | No
21/11/2019 | 20:25 | EL8 | Urban | Asset Failure | LV | 1 | 910 | 0.0014377 | 0.00015799 | No
21/11/2019 | 21:01 | CFD14 | Urban | Third Party | Other | 1 | 700.1 | 0.001106 | 0.00015799 | No
21/11/2019 | 22:28 | BR6 | Urban | Asset Failure | LV | 1 | 108 | 0.00017063 | 0.00015799 | No
22/11/2019 | 00:56 | BU1 | Urban | Asset Failure | HV | 1,317 | 69.3 | 0.14428 | 0.20807 | No
22/11/2019 | 02:51 | BU1 | Urban | Unknown | Unknown | 412 | 9.9 | 0.006455 | 0 | No
22/11/2019 | 02:53 | BU1 | Urban | Unknown | Unknown | 402 | 2.1 | 0.001302 | 0 | No
22/11/2019 | 02:53 | BU9 | Urban | Unknown | Unknown | 1,002 | 2.1 | 0.0032453 | 0 | No
22/11/2019 | 07:14 | K2 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 482.3 | 0.00076191 | 0.00015799 | No
22/11/2019 | 07:33 | FSH31 | Urban | Animal | Animal impact | 114 | 100 | 0.018011 | 0.018011 | No
22/11/2019 | 08:08 | SS14 | Urban | Overloads |  | 1 | 559.6 | 0.00088403 | 0.00015799 | No
22/11/2019 | 08:17 | SS13 | Urban | Unknown | Unknown | 1 | 357.6 | 0.000565 | 0.00015799 | No
22/11/2019 | 08:46 | RWT34 | Urban | Asset Failure | LV | 1 | 279 | 0.00044079 | 0.00015799 | No
22/11/2019 | 08:46 | SR20 | Urban | Third Party | Other | 1 | 445 | 0.00070305 | 0.00015799 | No
22/11/2019 | 09:29 | OR34 | Urban | Asset Failure | LV | 1 | 376 | 0.00059404 | 0.00015799 | No
22/11/2019 | 09:39 | NW11 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 95.6 | 0.00015104 | 0.00015799 | No
22/11/2019 | 09:41 | AR6 | Urban | Unknown | Unknown | 94 | 224 | 0.033266 | 0.014851 | No
22/11/2019 | 12:53 | AR6 | Urban | Asset Failure | LV | 1 | 711.4 | 0.001124 | 0.00015799 | No
22/11/2019 | 13:32 | SV32 | Urban | Asset Failure | LV | 1 | 328 | 0.00051821 | 0.00015799 | No
22/11/2019 | 16:35 | K6 | Urban | Unknown | Unknown | 1 | 573.6 | 0.00090626 | 0.00015799 | No
22/11/2019 | 18:08 | K8 | Urban | Vegetation | Grow-in - Other responsible party | 74 | 57 | 0.006664 | 0.011691 | No
22/11/2019 | 18:09 | NW21 | Urban | Vegetation | Grow-in - Other responsible party | 108 | 89 | 0.015186 | 0.017063 | No
23/11/2019 | 07:46 | BW34 | Urban | Asset Failure | LV | 1 | 189.1 | 0.00029876 | 0.00015799 | No
23/11/2019 | 13:00 | DN13 | Urban | Third Party | Vehicle Impact | 75 | 380.3 | 0.045067 | 0.011849 | No
23/11/2019 | 14:41 | CDA23 | Urban | Unknown | Unknown | 1 | 129 | 0.00020381 | 0.00015799 | No
23/11/2019 | 16:58 | SS12 | Urban | Asset Failure | LV | 1 | 32 | 5.0557e-05 | 0.00015799 | No
23/11/2019 | 18:39 | DC6 | Urban | Overloads |  | 1 | 73.8 | 0.00011654 | 0.00015799 | No
23/11/2019 | 20:38 | LD7 | Urban | Asset Failure | LV | 1 | 81.8 | 0.00012924 | 0.00015799 | No
24/11/2019 | 12:54 | RBD12 | Rural Short | Asset Failure | HV | 27 | 82.5 | 0.037433 | 0.0454 | No
24/11/2019 | 16:21 | NP23 | Urban | Asset Failure | LV | 1 | 94 | 0.00014851 | 0.00015799 | No
24/11/2019 | 17:43 | BT10 | Urban | Asset Failure | LV | 35 | 52 | 0.0028738 | 0.0055265 | No
25/11/2019 | 04:07 | NP23 | Urban |  | Other | 66 | 107.3 | 0.011192 | 0.010427 | No
25/11/2019 | 06:24 | DVY24 | Rural Short | Third Party | Other | 7 | 456 | 0.050606 | 0.011098 | No
25/11/2019 | 07:56 | SR11 | Urban | Asset Failure | LV | 1 | 109 | 0.00017221 | 0.00015799 | No
25/11/2019 | 08:20 | DN10 | Urban | Asset Failure | LV | 1 | 804.2 | 0.0012705 | 0.00015799 | No
25/11/2019 | 08:40 | BU13 | Urban | Asset Failure | LV | 7 | 215 | 0.0022928 | 0.0010664 | No
25/11/2019 | 08:52 | EB33 | Urban | Third Party | Other | 1 | 298 | 0.00047081 | 0.00015799 | No
25/11/2019 | 10:50 | FSH13 | Urban | Asset Failure | LV | 1 | 164.5 | 0.00025992 | 0.00015799 | No
25/11/2019 | 13:54 | GW7 | Urban | Asset Failure | LV | 12 | 141 | 0.0026732 | 0.0018959 | No
25/11/2019 | 17:07 | MC2 | Urban | Asset Failure | LV | 1 | 72.3 | 0.00011417 | 0.00015799 | No
25/11/2019 | 17:43 | OAK21 | Urban | Overloads |  | 1 | 276.6 | 0.00043695 | 0.00015799 | No
25/11/2019 | 18:05 | RWT23 | Urban | Asset Failure | HV | 82 | 170.9 | 0.022138 | 0.012955 | No
25/11/2019 | 19:05 | CRM24 | Urban | Asset Failure | LV | 1 | 235 | 0.00037128 | 0.00015799 | No
25/11/2019 | 19:08 | OR35 | Urban | Vegetation | Grow-in - Other responsible party | 97 | 32 | 0.004904 | 0.015325 | No
25/11/2019 | 19:16 | DN10 | Urban | Unknown | Unknown | 24 | 14 | 0.00053085 | 0.0037918 | No
25/11/2019 | 22:02 | DMA23 | Rural Short | Asset Failure | LV | 2 | 852.7 | 0.028674 | 0.003363 | No
25/11/2019 | 22:16 | EW1 | Urban | Third Party | Other | 1 | 129 | 0.00020381 | 0.00015799 | No
25/11/2019 | 22:42 | DMA15 | Rural Short |  | HV | 1,055 | 5.9 | 0.10466 | 1.774 | No
25/11/2019 | 23:43 | LD33 | Urban | Unknown | Unknown | 3,005 | 37.5 | 0.17819 | 0.47476 | No
25/11/2019 | 23:47 | LD2 | Urban | Unknown | Unknown | 72 | 39 | 0.0044364 | 0.011375 | No
26/11/2019 | 00:33 | HGS33 | Rural Short | Animal | Animal impact | 3 | 57 | 0.0028754 | 0.0050445 | No
26/11/2019 | 04:07 | MGE13 | Urban | Asset Failure | HV | 3 | 362.8 | 0.0017195 | 0.00047397 | No
26/11/2019 | 05:25 | DC12 | Urban | Weather |  | 1,551 | 171.2 | 0.41942 | 0.24504 | No
26/11/2019 | 08:06 | NO6 | Urban | Asset Failure | LV | 1 | 99 | 0.00015641 | 0.00015799 | No
26/11/2019 | 09:30 | STO23 | Urban | Asset Failure | LV | 1 | 99.4 | 0.00015696 | 0.00015799 | No
26/11/2019 | 11:06 | EL10 | Urban | Asset Failure | LV | 2 | 378.4 | 0.0011957 | 0.00031598 | No
26/11/2019 | 11:44 | CRM34 | Urban | Asset Failure | LV | 1 | 90 | 0.00014224 | 0.00015799 | No
26/11/2019 | 12:37 | EM8 | Urban | Asset Failure | LV | 1 | 562.7 | 0.00088896 | 0.00015799 | No
26/11/2019 | 13:42 | WD26 | Urban | Asset Failure | LV | 1 | 217.3 | 0.00034334 | 0.00015799 | No
26/11/2019 | 17:25 | NW21 | Urban | Vegetation | Grow-in - NSP responsibility | 396 | 43 | 0.026903 | 0.062564 | No
26/11/2019 | 18:59 | LD6 | Urban | Asset Failure | LV | 1 | 189.4 | 0.00029921 | 0.00015799 | No
26/11/2019 | 19:29 | CDA23 | Urban | Vegetation | Grow-in - Other responsible party | 23 | 96 | 0.0035536 | 0.0037017 | No
26/11/2019 | 20:14 | NW13 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 166 | 0.00026226 | 0.00015799 | No
27/11/2019 | 09:45 | LD32 | Urban | Third Party | Vehicle Impact | 115 | 135 | 0.024528 | 0.018169 | No
27/11/2019 | 10:13 | DN25 | Urban | Overloads |  | 1 | 66.5 | 0.00010506 | 0.00015799 | No
27/11/2019 | 10:46 | WD14 | Urban | Asset Failure | LV | 1 | 163.7 | 0.00025858 | 0.00015799 | No
27/11/2019 | 11:17 | MTN24 | Rural Short | Asset Failure | LV | 1 | 192.6 | 0.003238 | 0.0016815 | No
27/11/2019 | 12:30 | SVW42 | Urban | Asset Failure | HV | 8 | 10 | 0.00012639 | 0.0012639 | No
27/11/2019 | 21:16 | DMA15 | Rural Short | Animal | Other | 48 | 94 | 0.075869 | 0.080712 | No
28/11/2019 | 06:33 | NW21 | Urban | Asset Failure | LV | 1 | 73 | 0.00011528 | 0.00015799 | No
28/11/2019 | 09:08 | CDA23 | Urban | Asset Failure | LV | 1 | 201.5 | 0.00031832 | 0.00015799 | No
28/11/2019 | 09:41 | FTN23 | Urban | Asset Failure | LV | 1 | 50 | 7.8995e-05 | 0.00015799 | No
28/11/2019 | 10:15 | OAK22 | Urban | Unknown | Unknown | 1 | 104.6 | 0.00016526 | 0.00015799 | No
28/11/2019 | 10:29 | CDA23 | Urban | Third Party | Other | 1 | 65.7 | 0.00010383 | 0.00015799 | No
28/11/2019 | 11:43 | NP11 | Urban | Overloads |  | 1 | 197.8 | 0.00031245 | 0.00015799 | No
28/11/2019 | 12:32 | EM8 | Urban | Asset Failure | LV | 74 | 338 | 0.039516 | 0.011691 | No
28/11/2019 | 12:44 | OR23 | Urban | Asset Failure | LV | 1 | 286.2 | 0.00045219 | 0.00015799 | No
28/11/2019 | 13:27 | DN11 | Urban | Third Party | Other | 1 | 53.5 | 8.4498e-05 | 0.00015799 | No
28/11/2019 | 16:54 | CDA23 | Urban | Asset Failure | LV | 1 | 171 | 0.00027016 | 0.00015799 | No
28/11/2019 | 17:20 | DN7 | Urban | Overloads |  | 1 | 374.4 | 0.00059143 | 0.00015799 | No
28/11/2019 | 19:07 | NW23 | Urban | Asset Failure | LV | 1 | 95 | 0.00015009 | 0.00015799 | No
28/11/2019 | 20:03 | WD14 | Urban | Asset Failure | LV | 8 | 96 | 0.001274 | 0.0013271 | No
29/11/2019 | 00:09 | HGS22 | Rural Short | Animal | Animal impact | 2 | 101 | 0.0033966 | 0.003363 | No
29/11/2019 | 09:11 | EB22 | Urban | Third Party | Other | 1 | 138 | 0.00021803 | 0.00015799 | No
29/11/2019 | 09:14 | NW21 | Urban | Network Business | Networ Error | 1 | 320.1 | 0.00050575 | 0.00015799 | No
29/11/2019 | 10:11 | STO14 | Rural Short | Weather |  | 1 | 113 | 0.0019001 | 0.0016815 | No
29/11/2019 | 10:45 | FSH32 | Rural Short | Asset Failure | LV | 1 | 295 | 0.0049604 | 0.0016815 | No
29/11/2019 | 15:17 | RBD14 | Urban | Asset Failure | LV | 1 | 133 | 0.00021013 | 0.00015799 | No
29/11/2019 | 17:09 | FSH13 | Urban | Asset Failure | LV | 1 | 96 | 0.00015167 | 0.00015799 | No
29/11/2019 | 17:22 | DC12 | Urban | Asset Failure | LV | 1 | 113 | 0.00017853 | 0.00015799 | No
29/11/2019 | 20:01 | DVY34 | Urban | Animal | Other | 3 | 269 | 0.001275 | 0.00047397 | No
29/11/2019 | 22:55 | MC2 | Urban | Third Party | Other | 2 | 52 | 0.00016436 | 0.00031598 | No
30/11/2019 | 06:24 | HGS23 | Rural Short | Animal | Animal impact | 9 | 180 | 0.02724 | 0.015133 | No
30/11/2019 | 07:41 | MR12 | Urban | Asset Failure | LV | 1 | 98.3 | 0.00015522 | 0.00015799 | No
30/11/2019 | 08:05 | DMA13 | Rural Short | Animal | Animal impact | 1,352 | 24.5 | 0.55697 | 2.2734 | No
30/11/2019 | 08:37 | NB35 | Urban | Asset Failure | LV | 1 | 87 | 0.00013748 | 0.00015799 | No
30/11/2019 | 09:01 | SV32 | Urban | Asset Failure | LV | 1 | 358.7 | 0.00056676 | 0.00015799 | No
30/11/2019 | 09:20 | FTN24 | Urban | Asset Failure | LV | 31 | 55 | 0.0026955 | 0.0049008 | No
30/11/2019 | 09:54 | MTN22 | Rural Short | Vegetation | Grow-in - Other responsible party | 1 | 125.4 | 0.0021092 | 0.0016815 | No
30/11/2019 | 11:52 | OE14 | Urban | Asset Failure | LV | 1 | 83 | 0.00013113 | 0.00015799 | No
30/11/2019 | 12:04 | MC4 | Urban | Asset Failure | HV | 20 | 51.3 | 0.0016215 | 0.0031598 | No
30/11/2019 | 13:58 | RWT23 | Urban | Asset Failure | LV | 1 | 122 | 0.00019275 | 0.00015799 | No
30/11/2019 | 18:23 | DN10 | Urban | Asset Failure | LV | 1 | 192 | 0.00030334 | 0.00015799 | No
30/11/2019 | 18:49 | MGE23 | Urban | Asset Failure | LV | 1 | 41 | 6.4776e-05 | 0.00015799 | No
01/12/2019 | 08:58 | DVY34 | Urban | Asset Failure | Distribution substation | 3 | 515.9 | 0.0024454 | 0.00047397 | No
01/12/2019 | 13:19 | DVY31 | Urban | Asset Failure | LV | 2 | 100.5 | 0.00031761 | 0.00031598 | No
01/12/2019 | 15:51 | FTN13 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 78.9 | 0.00012458 | 0.00015799 | No
01/12/2019 | 16:29 | NB31 | Urban | Asset Failure | LV | 1 | 91 | 0.00014377 | 0.00015799 | No
01/12/2019 | 17:38 | OR35 | Urban | Unknown | Unknown | 1 | 81.5 | 0.00012871 | 0.00015799 | No
01/12/2019 | 20:42 | HGS31 | Rural Short | Unknown | Unknown | 61 | 298 | 0.30561 | 0.10257 | No
01/12/2019 | 20:59 | HGS31 | Rural Short | Vegetation | Grow-in - Other responsible party | 62 | 281 | 0.29295 | 0.10425 | No
01/12/2019 | 21:17 | HGS31 | Rural Short | Unknown | Unknown | 32 | 8 | 0.0043046 | 0.053808 | No
01/12/2019 | 21:58 | RBD13 | Urban | Asset Failure | LV | 5 | 152 | 0.0011599 | 0.00076309 | No
02/12/2019 | 08:00 | HGS23 | Rural Short | Weather |  | 29 | 109.4 | 0.053335 | 0.048763 | No
02/12/2019 | 08:58 | CRM34 | Urban | Asset Failure | LV | 1 | 251.5 | 0.00039732 | 0.00015799 | No
02/12/2019 | 12:59 | FSH31 | Urban | Asset Failure | LV | 45 | 165.8 | 0.011786 | 0.0071095 | No
02/12/2019 | 13:42 | NO6 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 770 | 25.6 | 0.031123 | 0.12165 | No
02/12/2019 | 13:46 | MGE33 | Urban | Asset Failure | LV | 1 | 268 | 0.00042341 | 0.00015799 | No
02/12/2019 | 14:56 | FTN24 | Urban | Asset Failure | LV | 1 | 154 | 0.0002433 | 0.00015799 | No
02/12/2019 | 15:25 | CDA21 | Urban | Asset Failure | LV | 4 | 106.1 | 0.00060858 | 0.0005735 | No
02/12/2019 | 15:54 | LD1 | Urban | Asset Failure | LV | 1 | 90.1 | 0.00014235 | 0.00015799 | No
02/12/2019 | 16:44 | EW12 | Urban | Asset Failure | LV | 1 | 75.2 | 0.00011876 | 0.00015799 | No
02/12/2019 | 18:49 | NB26 | Urban | Asset Failure | LV | 1 | 120.2 | 0.00018996 | 0.00015799 | No
03/12/2019 | 01:27 | K13 | Urban | Asset Failure | LV | 1 | 119.6 | 0.00018896 | 0.00015799 | No
03/12/2019 | 07:46 | MC1 | Urban | Overloads |  | 1 | 163.9 | 0.00025892 | 0.00015799 | No
03/12/2019 | 08:33 | HT6 | Urban | Third Party | Vehicle Impact | 1 | 357 | 0.00056402 | 0.00015799 | No
03/12/2019 | 11:19 | FTN24 | Urban |  | Networ Error | 1 | 282.4 | 0.00044616 | 0.00015799 | No
03/12/2019 | 13:24 | M13 | Urban | Weather |  | 10 | 116 | 0.0018748 | 0.0016162 | No
03/12/2019 | 13:44 | MR32 | Urban | Asset Failure | LV | 2 | 300.5 | 0.00094957 | 0.00031598 | No
03/12/2019 | 15:03 | NW13 | Urban | Asset Failure | LV | 2 | 208.8 | 0.00076185 | 0.00036496 | No
03/12/2019 | 18:16 | MGE23 | Urban | Asset Failure | LV | 1 | 203.4 | 0.00032133 | 0.00015799 | No
03/12/2019 | 18:50 | NP36 | Urban | Asset Failure | LV | 1 | 145 | 0.00022908 | 0.00015799 | No
03/12/2019 | 20:58 | BW21 | Urban | Asset Failure | LV | 1 | 121.7 | 0.00019222 | 0.00015799 | No
04/12/2019 | 06:01 | RBD12 | Rural Short | Asset Failure | Distribution substation | 2 | 239 | 0.0080375 | 0.003363 | No
04/12/2019 | 09:10 | SS14 | Urban | Asset Failure | LV | 1 | 76.3 | 0.00012055 | 0.00015799 | No
04/12/2019 | 10:20 | DMA23 | Rural Short | Unknown | Unknown | 1 | 210 | 0.0035311 | 0.0016815 | No
04/12/2019 | 10:58 | EB33 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 167 | 0.00026384 | 0.00015799 | No
04/12/2019 | 12:33 | KBH32 | Urban | Vegetation | Grow-in - Other responsible party | 8 | 237 | 0.0029955 | 0.0012639 | No
04/12/2019 | 16:56 | FSH13 | Urban | Asset Failure | LV | 1 | 213.2 | 0.00033683 | 0.00015799 | No
04/12/2019 | 17:09 | FSH31 | Urban | Asset Failure | LV | 1 | 65.8 | 0.00010391 | 0.00015799 | No
04/12/2019 | 18:36 | HGS22 | Rural Short | Asset Failure | HV | 34 | 126 | 0.072035 | 0.057171 | No
05/12/2019 | 10:12 | EB33 | Urban | Third Party | Other | 1 | 186 | 0.00029386 | 0.00015799 | No
05/12/2019 | 10:59 | CRM35 | Urban | Asset Failure | LV | 2 | 16 | 5.0557e-05 | 0.00031598 | No
05/12/2019 | 13:47 | FSH34 | Urban |  | HV | 1,732 | 55.3 | 0.15121 | 0.27364 | No
06/12/2019 | 01:08 | OAK33 | Urban | Asset Failure | LV | 16 | 22 | 0.00055056 | 0.0025026 | No
06/12/2019 | 10:37 | MR32 | Urban | Third Party | Dig-in | 1 | 593 | 0.00093688 | 0.00015799 | No
06/12/2019 | 13:11 | CM13 | Urban | Asset Failure | LV | 1 | 167.4 | 0.0002644 | 0.00015799 | No
06/12/2019 | 22:48 | SVW54 | Urban | Asset Failure | LV | 6 | 101.1 | 0.00094909 | 0.00093846 | No
06/12/2019 | 22:49 | K13 | Urban | Animal | Animal impact | 2 | 34.9 | 0.00012136 | 0.00034758 | No
07/12/2019 | 09:24 | FSH22 | Urban | Asset Failure | LV | 61 | 137 | 0.013203 | 0.0096374 | No
07/12/2019 | 17:31 | NW22 | Urban | Vegetation | Grow-in - Other responsible party | 50 | 29 | 0.0022909 | 0.0078995 | No
08/12/2019 | 04:37 | MC2 | Urban | Third Party | Vehicle Impact | 57 | 113 | 0.010176 | 0.0090054 | No
08/12/2019 | 11:00 | KBH35 | Urban | Animal | Other | 1,728 | 72.8 | 0.19863 | 0.27301 | No
08/12/2019 | 13:46 | SR15 | Urban | Asset Failure | LV | 243 | 104 | 0.039927 | 0.038392 | No
09/12/2019 | 03:25 | EM10 | Urban | Asset Failure | LV | 7 | 238 | 0.0026321 | 0.0011059 | No
09/12/2019 | 07:49 | M13 | Urban | Asset Failure | LV | 1 | 65.6 | 0.00010362 | 0.00015799 | No
09/12/2019 | 14:04 | FTN12 | Urban | Overloads |  | 1 | 161 | 0.00025436 | 0.00015799 | No
09/12/2019 | 14:51 | MC10 | Urban | Overloads |  | 1 | 218.4 | 0.00034497 | 0.00015799 | No
09/12/2019 | 15:11 | RBD22 | Urban | Asset Failure | HV | 15 | 79 | 0.0018722 | 0.0023698 | No
09/12/2019 | 15:28 | K6 | Urban | Overloads |  | 29 | 47 | 0.0021564 | 0.004588 | No
09/12/2019 | 15:59 | EM5 | Urban | Other | XXX | 1 | 420 | 0.00066358 | 0.00015799 | No
09/12/2019 | 16:38 | NW33 | Urban | Asset Failure | LV | 20 | 97 | 0.0030344 | 0.0031282 | No
09/12/2019 | 17:18 | CDA22 | Urban | Overloads |  | 80 | 162 | 0.020475 | 0.012639 | No
09/12/2019 | 17:31 | SR20 | Urban | Asset Failure | LV | 15 | 459 | 0.010878 | 0.0023698 | No
09/12/2019 | 18:18 | EB31 | Urban | Asset Failure | LV | 1 | 57 | 9.0054e-05 | 0.00015799 | No
09/12/2019 | 18:51 | NW31 | Urban | Weather |  | 37 | 170.5 | 0.009957 | 0.0058393 | No
09/12/2019 | 20:27 | EW14 | Urban | Vegetation | Grow-in - NSP responsibility | 751 | 11.3 | 0.013447 | 0.11865 | No
09/12/2019 | 22:30 | CDA11 | Urban | Unknown | Unknown | 27 | 120 | 0.0051928 | 0.0043273 | No
09/12/2019 | 22:44 | BT10 | Urban | Asset Failure | LV | 1 | 178 | 0.00028122 | 0.00015799 | No
10/12/2019 | 06:49 | MGE12 | Urban | Asset Failure | HV | 24 | 685.2 | 0.025979 | 0.0037918 | No
10/12/2019 | 06:56 | NO7 | Urban | Asset Failure | HV | 203 | 293.1 | 0.093988 | 0.032072 | No
10/12/2019 | 07:22 | NP12 | Urban | Asset Failure | LV | 2 | 207.8 | 0.00065655 | 0.00031598 | No
10/12/2019 | 07:49 | NP34 | Urban | Asset Failure | LV | 1 | 310 | 0.00048982 | 0.00015799 | No
10/12/2019 | 10:43 | NW22 | Urban | Asset Failure | HV | 648 | 47 | 0.048147 | 0.10238 | No
10/12/2019 | 12:05 | SR11 | Urban | Weather |  | 103 | 105 | 0.017087 | 0.016273 | No
11/12/2019 | 08:45 | WD23 | Urban | Asset Failure | LV | 15 | 45 | 0.0010465 | 0.0023256 | No
11/12/2019 | 15:01 | DMA15 | Rural Short | Unknown | Unknown | 260 | 19 | 0.083066 | 0.43719 | No
11/12/2019 | 15:25 | LWN23 | Urban | Unknown | Unknown | 1 | 80 | 0.00012639 | 0.00015799 | No
11/12/2019 | 21:37 | WD14 | Urban | Asset Failure | LV | 9 | 162.3 | 0.0023688 | 0.0014598 | No
11/12/2019 | 21:51 | NP25 | Urban | Animal | Animal impact | 1,663 | 54 | 0.14176 | 0.26274 | No
11/12/2019 | 22:57 | NP25 | Urban | Animal | Other | 17 | 722.3 | 0.019399 | 0.0026858 | No
12/12/2019 | 07:50 | NP12 | Urban | Animal | Other | 49 | 107 | 0.0082834 | 0.0077415 | No
12/12/2019 | 10:35 | DC6 | Urban | Asset Failure | LV | 1 | 115 | 0.00018169 | 0.00015799 | No
12/12/2019 | 10:58 | STO21 | Rural Short |  | Distribution substation | 2 | 331 | 0.011132 | 0.003363 | No
12/12/2019 | 11:13 | LD33 | Urban | Asset Failure | LV | 1 | 122 | 0.00019275 | 0.00015799 | No
12/12/2019 | 15:48 | DC4 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 106.2 | 0.00016773 | 0.00015799 | No
12/12/2019 | 15:53 | EL14 | Urban | Asset Failure | LV | 1 | 112 | 0.00017695 | 0.00015799 | No
13/12/2019 | 01:52 | HGS33 | Rural Short | Animal | Animal impact | 17 | 210 | 0.060034 | 0.028585 | No
13/12/2019 | 08:52 | LD6 | Urban | Asset Failure | LV | 1 | 397.5 | 0.00062804 | 0.00015799 | No
13/12/2019 | 14:30 | OR32 | Urban | Asset Failure | LV | 19 | 299.9 | 0.0092241 | 0.0030761 | No
14/12/2019 | 05:26 | MTN32 | Rural Short | Animal | Animal impact | 419 | 70 | 0.49318 | 0.70455 | No
14/12/2019 | 10:15 | SVW53 | Urban | Weather |  | 211 | 59.3 | 0.019756 | 0.033336 | No
14/12/2019 | 10:51 | NW21 | Urban |  | XXX | 11 | 128.5 | 0.0022332 | 0.0017379 | No
14/12/2019 | 11:04 | RBD23 | Urban | Asset Failure | LV | 1 | 81 | 0.00012797 | 0.00015799 | No
14/12/2019 | 11:41 | NW22 | Urban | Asset Failure | LV | 4 | 139 | 0.00096627 | 0.00069516 | No
14/12/2019 | 23:57 | OAK34 | Urban | Third Party | Other | 1 | 53 | 8.3735e-05 | 0.00015799 | No
15/12/2019 | 08:01 | EW14 | Urban | Planned |  | 1 | 17 | 2.6858e-05 | 0.00015799 | No
15/12/2019 | 10:17 | BU14 | Urban | Vegetation | Grow-in - Other responsible party | 4 | 83 | 0.00051928 | 0.00062564 | No
15/12/2019 | 23:58 | STO21 | Rural Short | Asset Failure | LV | 22 | 192 | 0.072447 | 0.037733 | No
16/12/2019 | 00:21 | STO21 | Rural Short | Asset Failure | LV | 1 | 173.7 | 0.0029202 | 0.0016815 | No
16/12/2019 | 09:29 | SR20 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 210.9 | 0.00033315 | 0.00015799 | No
16/12/2019 | 10:11 | CRM21 | Urban | Third Party | Other | 2 | 79 | 0.00024962 | 0.00031598 | No
16/12/2019 | 10:32 | DC2 | Urban | Planned |  | 1 | 81.2 | 0.00012834 | 0.00015799 | No
16/12/2019 | 16:04 | DN6 | Urban | Third Party | Other | 48 | 577.7 | 0.043807 | 0.0075835 | No
16/12/2019 | 16:43 | SS22 | Urban | Asset Failure | LV | 2 | 122 | 0.00034695 | 0.00028438 | No
16/12/2019 | 18:05 | NW13 | Urban | Vegetation | Grow-in - NSP responsibility | 315 | 100 | 0.049767 | 0.049767 | No
16/12/2019 | 19:35 | SR15 | Urban | Asset Failure | LV | 50 | 334.6 | 0.026644 | 0.0079627 | No
16/12/2019 | 20:14 | CFD13 | Urban | Third Party | Other | 1 | 61 | 9.6374e-05 | 0.00015799 | No
17/12/2019 | 00:10 | NP12 | Urban | Asset Failure | HV | 113 | 125.8 | 0.022456 | 0.017853 | No
17/12/2019 | 03:04 | RBD22 | Urban | Asset Failure | LV | 1 | 46 | 7.2675e-05 | 0.00015799 | No
17/12/2019 | 08:22 | DMA24 | Rural Short | Animal | Other | 2 | 77.8 | 0.0026175 | 0.003363 | No
17/12/2019 | 08:50 | CRM23 | Urban | Asset Failure | LV | 1 | 84.7 | 0.00013384 | 0.00015799 | No
17/12/2019 | 10:18 | DMA21 | Urban | Vegetation | Grow-in - Other responsible party | 1 | 86.4 | 0.0001365 | 0.00015799 | No
17/12/2019 | 13:09 | FSH22 | Urban | Asset Failure | LV | 21 | 491 | 0.016337 | 0.0033273 | No
17/12/2019 | 15:10 | NP14 | Urban | Third Party | Vehicle Impact | 71 | 354.6 | 0.039776 | 0.011217 | No
17/12/2019 | 15:52 | EM5 | Urban | Asset Failure | LV | 1 | 83 | 0.00013113 | 0.00015799 | No
17/12/2019 | 16:35 | M33 | Urban | Third Party | Other | 1 | 89.5 | 0.00014145 | 0.00015799 | No
17/12/2019 | 17:35 | CRM13 | Urban | Asset Failure | LV | 1 | 115 | 0.00018169 | 0.00015799 | No
18/12/2019 | 00:17 | RBD12 | Rural Short | Animal | Animal impact | 4 | 58 | 0.0039011 | 0.006726 | No
18/12/2019 | 07:19 | DVY34 | Urban | Animal | Animal impact | 3 | 80.4 | 0.00038107 | 0.00047397 | No
18/12/2019 | 07:19 | DVY24 | Rural Short | Animal | Animal impact | 391 | 101.5 | 0.66735 | 0.65746 | No
18/12/2019 | 15:18 | EL5 | Urban | Weather |  | 16 | 67 | 0.0016418 | 0.0024504 | No
18/12/2019 | 16:12 | CDA22 | Urban | Weather |  | 26 | 88 | 0.0036704 | 0.0041709 | No
18/12/2019 | 16:18 | FSH13 | Urban | Unknown | Unknown | 55 | 146.4 | 0.012723 | 0.0086894 | No
18/12/2019 | 16:46 | DC1 | Urban | Asset Failure | LV | 8 | 134 | 0.0016069 | 0.0011991 | No
18/12/2019 | 16:54 | RWT34 | Urban | Asset Failure | Distribution substation | 32 | 51 | 0.0026058 | 0.0051094 | No
18/12/2019 | 17:17 | K6 | Urban | Weather |  | 59 | 28 | 0.0026277 | 0.0093846 | No
18/12/2019 | 17:29 | DMA14 | Urban | Overloads |  | 3 | 71 | 0.00037017 | 0.00052137 | No
18/12/2019 | 17:32 | M23 | Urban | Third Party | Other | 1 | 328 | 0.00051821 | 0.00015799 | No
18/12/2019 | 17:52 | DC1 | Urban | Asset Failure | LV | 3 | 503 | 0.0020978 | 0.00041709 | No
18/12/2019 | 17:56 | K12 | Urban | Overloads |  | 21 | 114 | 0.0038435 | 0.0033715 | No
18/12/2019 | 18:00 | K6 | Urban | Overloads |  | 18 | 140 | 0.0039858 | 0.002847 | No
18/12/2019 | 18:14 | DN13 | Urban | Overloads |  | 15 | 226 | 0.005313 | 0.0023509 | No
18/12/2019 | 18:18 | BW23 | Urban | Unknown | Unknown | 323 | 297 | 0.15156 | 0.051031 | No
18/12/2019 | 18:18 | OR24 | Urban | Asset Failure | LV | 33 | 102 | 0.0053582 | 0.0052532 | No
18/12/2019 | 18:21 | MGE21 | Urban | Overloads |  | 10 | 159 | 0.0025774 | 0.001621 | No
18/12/2019 | 18:22 | CFD14 | Urban | Asset Failure | LV | 16 | 148 | 0.003643 | 0.0024615 | No
18/12/2019 | 18:25 | CDA24 | Urban | Overloads |  | 23 | 70 | 0.0025481 | 0.0036401 | No
18/12/2019 | 18:26 | STO14 | Rural Short | Unknown | Unknown | 10 | 148.3 | 0.024928 | 0.016815 | No
18/12/2019 | 18:31 | OR35 | Urban | Overloads |  | 23 | 170 | 0.0061156 | 0.0035974 | No
18/12/2019 | 18:32 | NW33 | Urban | Asset Failure | LV | 32 | 133 | 0.006682 | 0.0050241 | No
18/12/2019 | 18:47 | CRM24 | Urban | Asset Failure | HV | 19 | 973 | 0.029208 | 0.0030018 | No
18/12/2019 | 18:51 | BR9 | Urban | Asset Failure | LV | 1 | 364 | 0.00057508 | 0.00015799 | No
18/12/2019 | 18:58 | FSH12 | Rural Short | Overloads |  | 1 | 128 | 0.0014205 | 0.0011098 | No
18/12/2019 | 19:15 | K6 | Urban | Overloads |  | 59 | 155 | 0.014546 | 0.0093846 | No
18/12/2019 | 19:16 | CDA22 | Urban | Overloads |  | 26 | 133.5 | 0.0055675 | 0.0041709 | No
18/12/2019 | 19:18 | CRM21 | Urban | Overloads |  | 11 | 411 | 0.0072856 | 0.0017726 | No
18/12/2019 | 19:58 | RWT12 | Urban | Overloads |  | 1 | 232 | 0.00036654 | 0.00015799 | No
18/12/2019 | 20:00 | BW35 | Urban | Overloads |  | 27 | 100 | 0.0043273 | 0.0043273 | No
18/12/2019 | 20:22 | FSH12 | Rural Short | Asset Failure | LV | 1 | 398 | 0.0066923 | 0.0016815 | No
18/12/2019 | 20:29 | BW35 | Urban | Asset Failure | LV | 1 | 166 | 0.00026226 | 0.00015799 | No
18/12/2019 | 22:13 | OR24 | Urban | Third Party | Other | 2,131 | 56.4 | 0.18988 | 0.33668 | No
18/12/2019 | 23:03 | OR24 | Urban | Third Party | Other | 123 | 171 | 0.03323 | 0.019433 | No
18/12/2019 | 23:07 | OR24 | Urban | Overloads |  | 9 | 172.4 | 0.0023535 | 0.001365 | No
19/12/2019 | 00:29 | CRM24 | Urban | Asset Failure | HV | 1 | 7.8 | 1.2271e-05 | 0.00015799 | No
19/12/2019 | 00:29 | CRM22 | Urban | Asset Failure | HV | 28 | 7.8 | 0.00034358 | 0.0044237 | No
19/12/2019 | 03:06 | MC6 | Urban | Animal | Animal impact | 1,399 | 140 | 0.30954 | 0.22103 | No
19/12/2019 | 04:00 | MC6 | Urban | Animal | Other | 82 | 564.5 | 0.073134 | 0.012955 | No
19/12/2019 | 12:39 | DC10 | Urban | Asset Failure | LV | 1 | 82 | 0.00012955 | 0.00015799 | No
19/12/2019 | 14:29 | MC6 | Urban | Unknown | Unknown | 1 | 61 | 9.6347e-05 | 0.00015799 | No
19/12/2019 | 16:33 | RWT34 | Urban | Overloads |  | 3 | 42 | 0.00017186 | 0.00040919 | No
19/12/2019 | 17:20 | RWT35 | Urban | Asset Failure | LV | 1 | 61 | 9.6374e-05 | 0.00015799 | No
19/12/2019 | 19:33 | MC1 | Urban | Asset Failure | LV | 1 | 147 | 0.00023225 | 0.00015799 | No
19/12/2019 | 21:44 | STO21 | Rural Short | Asset Failure | LV | 1 | 101 | 0.0016983 | 0.0016815 | No
20/12/2019 | 02:07 | MC1 | Urban | Asset Failure | LV | 24 | 87.2 | 0.0032721 | 0.0037538 | No
20/12/2019 | 03:57 | STO14 | Rural Short | Asset Failure | LV | 1 | 77.2 | 0.0012987 | 0.0016815 | No
20/12/2019 | 07:35 | FSH31 | Urban | Asset Failure | LV | 1 | 70 | 0.00011059 | 0.00015799 | No
20/12/2019 | 09:10 | CDA23 | Urban | Asset Failure | LV | 1 | 49.3 | 7.7836e-05 | 0.00015799 | No
20/12/2019 | 10:30 | BR10 | Urban | Overloads |  | 1 | 149.8 | 7.8075e-05 | 5.2137e-05 | No
20/12/2019 | 11:09 | SVW53 | Urban | Asset Failure | LV | 1 | 141 | 0.00022277 | 0.00015799 | No
20/12/2019 | 14:06 | BW22 | Urban | Overloads |  | 1 | 113.6 | 0.00011849 | 0.00010427 | No
20/12/2019 | 15:49 | K6 | Urban | Asset Failure | LV | 1 | 55.2 | 8.721e-05 | 0.00015799 | No
20/12/2019 | 16:31 | K10 | Urban | Overloads |  | 26 | 26 | 0.0010709 | 0.0041188 | No
20/12/2019 | 16:31 | K12 | Urban | Overloads |  | 16 | 26 | 0.00063752 | 0.002452 | No
20/12/2019 | 16:33 | SR13 | Urban | Asset Failure | LV | 57 | 79.3 | 0.0071067 | 0.0089675 | No
20/12/2019 | 16:38 | CRM35 | Urban | Overloads |  | 35 | 102 | 0.0056902 | 0.0055786 | No
20/12/2019 | 17:03 | FSH31 | Urban | Overloads |  | 21 | 72 | 0.0023342 | 0.003242 | No
20/12/2019 | 17:06 | CRM15 | Urban | Asset Failure | LV | 71 | 151 | 0.016926 | 0.011209 | No
20/12/2019 | 17:18 | FSH13 | Urban | Overloads |  | 36 | 122 | 0.0069967 | 0.005735 | No
20/12/2019 | 17:19 | EL12 | Urban | Asset Failure | LV | 13 | 100.2 | 0.0020364 | 0.0020333 | No
20/12/2019 | 17:22 | FSH33 | Urban | Weather |  | 14 | 232.1 | 0.005203 | 0.0022419 | No
20/12/2019 | 17:44 | FSH12 | Rural Short | Overloads |  | 35 | 269 | 0.15822 | 0.058819 | No
20/12/2019 | 17:47 | LD4 | Urban | Asset Failure | LV | 2 | 132.6 | 0.0004503 | 0.00033968 | No
20/12/2019 | 17:50 | BT14 | Urban | Overloads |  | 23 | 55 | 0.0020359 | 0.0037017 | No
20/12/2019 | 17:50 | OR35 | Urban | Overloads |  | 28 | 190 | 0.0085101 | 0.004479 | No
20/12/2019 | 17:56 | CFD25 | Urban | Overloads |  | 25 | 184 | 0.0073867 | 0.0040145 | No
20/12/2019 | 18:04 | HT1 | Urban | Overloads |  | 18 | 36 | 0.0010278 | 0.0028549 | No
20/12/2019 | 18:07 | DN13 | Urban | Overloads |  | 16 | 218 | 0.0054556 | 0.0025026 | No
20/12/2019 | 18:07 | DN13 | Urban | Overloads |  | 26 | 218 | 0.008979 | 0.0041188 | No
20/12/2019 | 18:12 | FSH33 | Urban | Asset Failure | HV | 3,230 | 115.1 | 0.58747 | 0.51031 | No
20/12/2019 | 18:13 | M22 | Urban | Overloads |  | 25 | 277 | 0.01112 | 0.0040145 | No
20/12/2019 | 18:16 | NW23 | Urban | Vegetation | Grow-in - Other responsible party | 3,391 | 45.1 | 0.24155 | 0.53574 | No
20/12/2019 | 18:18 | MTN32 | Rural Short | Overloads |  | 2 | 267 | 0.0088894 | 0.0033294 | No
20/12/2019 | 18:20 | BH21 | Urban | Overloads |  | 15 | 390 | 0.0089467 | 0.002294 | No
20/12/2019 | 18:24 | HT1 | Urban | Overloads |  | 20 | 61 | 0.0019718 | 0.0032325 | No
20/12/2019 | 18:26 | EM8 | Urban | Overloads |  | 24 | 379 | 0.014622 | 0.0038581 | No
20/12/2019 | 18:26 | BU6 | Urban | Vegetation | Grow-in - Other responsible party | 1,502 | 54.2 | 0.12854 | 0.2373 | No
20/12/2019 | 18:28 | AR12 | Urban | Overloads |  | 21 | 352 | 0.011745 | 0.0033367 | No
20/12/2019 | 18:33 | NP12 | Urban | Overloads |  | 56 | 821 | 0.072339 | 0.0088111 | No
20/12/2019 | 18:48 | MR33 | Urban | Overloads |  | 19 | 417 | 0.01261 | 0.0030239 | No
20/12/2019 | 18:54 | HGS22 | Rural Short | Asset Failure | LV | 43 | 257.2 | 0.18412 | 0.071581 | No
20/12/2019 | 19:07 | K3 | Urban | Overloads |  | 13 | 562.4 | 0.011434 | 0.0020333 | No
20/12/2019 | 19:17 | SS22 | Urban | Overloads |  | 32 | 577.6 | 0.029208 | 0.0050573 | No
20/12/2019 | 19:22 | MR32 | Urban | Overloads |  | 12 | 568 | 0.010957 | 0.0019291 | No
20/12/2019 | 19:24 | M11 | Urban | Overloads |  | 17 | 656 | 0.017785 | 0.0027111 | No
20/12/2019 | 19:25 | CDA23 | Urban | Overloads |  | 25 | 765 | 0.030711 | 0.0040145 | No
20/12/2019 | 19:25 | CRM23 | Urban | Overloads |  | 35 | 10 | 0.00054743 | 0.0054743 | No
20/12/2019 | 19:29 | BU6 | Urban | Overloads |  | 27 | 480.2 | 0.020531 | 0.0042752 | No
20/12/2019 | 19:30 | SR25 | Urban | Overloads |  | 17 | 856 | 0.022314 | 0.0026068 | No
20/12/2019 | 19:37 | BR6 | Urban | Overloads |  | 18 | 253 | 0.0072548 | 0.0028675 | No
20/12/2019 | 19:40 | EB14 | Urban | Overloads |  | 23 | 447 | 0.016081 | 0.0035974 | No
20/12/2019 | 19:41 | NB35 | Urban | Overloads |  | 1 | 1,015.5 | 0.0016044 | 0.00015799 | No
20/12/2019 | 19:46 | NB33 | Urban | Asset Failure | LV | 4 | 909 | 0.0052131 | 0.0005735 | No
20/12/2019 | 19:49 | OR35 | Urban | Overloads |  | 27 | 111 | 0.0048033 | 0.0043273 | No
20/12/2019 | 19:51 | CRM35 | Urban | Asset Failure | LV | 27 | 464 | 0.020079 | 0.0043273 | No
20/12/2019 | 19:53 | MR15 | Urban | Overloads |  | 25 | 597 | 0.023967 | 0.0040145 | No
20/12/2019 | 20:00 | MR24 | Urban | Overloads |  | 18 | 855 | 0.024517 | 0.0028675 | No
20/12/2019 | 20:08 | CFD15 | Urban | Asset Failure | LV | 1 | 1,117.0 | 0.0017647 | 0.00015799 | No
20/12/2019 | 20:08 | BW35 | Urban | Overloads |  | 27 | 351 | 0.015189 | 0.0043273 | No
20/12/2019 | 20:10 | NB35 | Urban | Overloads |  | 19 | 887 | 0.02636 | 0.0029718 | No
20/12/2019 | 20:11 | RWT34 | Urban | Overloads |  | 27 | 564 | 0.024112 | 0.0042752 | No
20/12/2019 | 20:12 | BT14 | Urban | Overloads |  | 23 | 663 | 0.024542 | 0.0037017 | No
20/12/2019 | 20:17 | OR35 | Urban | Overloads |  | 23 | 793 | 0.028941 | 0.0036496 | No
20/12/2019 | 20:19 | CRM15 | Urban | Overloads |  | 56 | 79.1 | 0.0070093 | 0.0088632 | No
20/12/2019 | 20:22 | OAK23 | Urban | Overloads |  | 65 | 203 | 0.02085 | 0.010271 | No
20/12/2019 | 20:25 | RBD13 | Urban | Overloads |  | 45 | 155 | 0.01091 | 0.0070384 | No
20/12/2019 | 20:26 | LWN24 | Urban | Overloads |  | 36 | 104 | 0.0059102 | 0.0056829 | No
20/12/2019 | 20:27 | MC1 | Urban | Overloads |  | 28 | 130.6 | 0.0058565 | 0.0044838 | No
20/12/2019 | 20:30 | OAK23 | Urban | Overloads |  | 53 | 480 | 0.040041 | 0.0083419 | No
20/12/2019 | 20:32 | DC5 | Urban | Overloads |  | 20 | 473 | 0.014796 | 0.0031282 | No
20/12/2019 | 20:33 | HT1 | Urban | Overloads |  | 20 | 851.3 | 0.027517 | 0.0032325 | No
20/12/2019 | 20:45 | CDA24 | Urban | Overloads |  | 27 | 770 | 0.032846 | 0.0042657 | No
20/12/2019 | 20:57 | EL12 | Urban | Overloads |  | 42 | 792.4 | 0.05288 | 0.0066735 | No
20/12/2019 | 20:58 | SR24 | Urban | Overloads |  | 56 | 697 | 0.061777 | 0.0088632 | No
20/12/2019 | 21:04 | BU14 | Urban | Overloads |  | 33 | 421 | 0.02195 | 0.0052137 | No
20/12/2019 | 21:14 | EM7 | Urban | Overloads |  | 27 | 641 | 0.02707 | 0.0042231 | No
20/12/2019 | 21:15 | MR21 | Urban | Overloads |  | 22 | 769 | 0.026461 | 0.003441 | No
20/12/2019 | 21:15 | K6 | Urban | Overloads |  | 17 | 384.8 | 0.010633 | 0.0027632 | No
20/12/2019 | 21:18 | CRM35 | Urban | Asset Failure | LV | 24 | 332 | 0.012809 | 0.0038581 | No
20/12/2019 | 21:24 | NB35 | Urban | Overloads |  | 9 | 396 | 0.0057809 | 0.0014598 | No
20/12/2019 | 21:25 | MGE12 | Urban | Overloads |  | 4 | 874.5 | 0.0050153 | 0.0005735 | No
20/12/2019 | 21:37 | EM8 | Urban | Overloads |  | 20 | 373 | 0.011863 | 0.0031803 | No
20/12/2019 | 21:40 | OR35 | Urban | Overloads |  | 35 | 454.4 | 0.024877 | 0.0054743 | No
20/12/2019 | 21:53 | FSH12 | Rural Short | Asset Failure | LV | 21 | 246.7 | 0.087617 | 0.035513 | No
20/12/2019 | 21:56 | BU1 | Urban | Asset Failure | LV | 1 | 1,039.0 | 0.0016415 | 0.00015799 | No
20/12/2019 | 22:00 | DN13 | Urban | Overloads |  | 16 | 60 | 0.0015015 | 0.0025026 | No
20/12/2019 | 22:14 | BU6 | Urban | Vegetation | Grow-in - Other responsible party | 110 | 556 | 0.096627 | 0.017379 | No
20/12/2019 | 23:12 | OE4 | Urban | Asset Failure | LV | 1 | 998 | 0.0015767 | 0.00015799 | No
21/12/2019 | 04:13 | FTN23 | Urban | Overloads |  | 21 | 411.8 | 0.013524 | 0.0032846 | No
21/12/2019 | 05:17 | MTN22 | Rural Short | Asset Failure | HV | 2 | 817 | 0.027476 | 0.003363 | No
21/12/2019 | 08:25 | K3 | Urban | Overloads |  | 6 | 164.4 | 0.0016284 | 0.0009906 | No
21/12/2019 | 08:38 | RBD21 | Rural Short | Weather |  | 1 | 491.4 | 0.0082629 | 0.0016815 | No
21/12/2019 | 09:21 | BT14 | Urban | Asset Failure | LV | 1 | 459 | 0.00072515 | 0.00015799 | No
21/12/2019 | 11:09 | FSH33 | Urban | Asset Failure | LV | 1 | 360.8 | 0.00057003 | 0.00015799 | No
21/12/2019 | 11:39 | NW23 | Urban | Asset Failure | LV | 1 | 321 | 0.00050715 | 0.00015799 | No
21/12/2019 | 11:50 | STO21 | Rural Short | Overloads |  | 28 | 100 | 0.047721 | 0.047721 | No
21/12/2019 | 12:47 | STO23 | Urban | Asset Failure | LV | 1 | 148 | 0.00023383 | 0.00015799 | No
21/12/2019 | 18:45 | BT9 | Urban | Overloads |  | 1 | 29.6 | 4.6765e-05 | 0.00015799 | No
21/12/2019 | 21:30 | EM8 | Urban | Vegetation | Grow-in - Other responsible party | 75 | 40 | 0.0047397 | 0.011849 | No
21/12/2019 | 23:59 | FTN22 | Urban | Asset Failure | HV | 11 | 75.4 | 0.0013095 | 0.0017379 | No
22/12/2019 | 07:25 | BR10 | Urban | Asset Failure | LV | 1 | 135 | 0.00021329 | 0.00015799 | No
22/12/2019 | 20:11 | LD7 | Urban | Third Party | Other | 12 | 168.5 | 0.0031952 | 0.0018959 | No
22/12/2019 | 21:04 | STO21 | Rural Short | Overloads |  | 1 | 40.5 | 0.00068016 | 0.0016815 | No
23/12/2019 | 01:24 | EM5 | Urban | Asset Failure | LV | 1 | 90.5 | 0.0001429 | 0.00015799 | No
23/12/2019 | 04:34 | GW7 | Urban | Animal | Animal impact | 82 | 76 | 0.0098147 | 0.012914 | No
23/12/2019 | 08:05 | DN21 | Urban | Asset Failure | LV | 1 | 235 | 0.00037122 | 0.00015799 | No
23/12/2019 | 09:44 | CRM35 | Urban | Unknown | Unknown | 1 | 382.7 | 0.00060465 | 0 | No
23/12/2019 | 11:04 | NB35 | Urban | Overloads |  | 9 | 10 | 0.00014598 | 0.0014598 | No
23/12/2019 | 11:35 | FSH12 | Rural Short | Asset Failure | LV | 1 | 445 | 0.0074821 | 0.0016815 | No
23/12/2019 | 12:05 | DMA15 | Rural Short | Asset Failure | HV | 2 | 461.6 | 0.015522 | 0.003363 | No
23/12/2019 | 14:55 | SR24 | Urban | Asset Failure | LV | 1 | 110 | 0.00017379 | 0.00015799 | No
23/12/2019 | 16:07 | CRM35 | Urban | Asset Failure | LV | 22 | 313 | 0.010879 | 0.0034758 | No
23/12/2019 | 16:58 | CRM23 | Urban | Third Party | Vehicle Impact | 41 | 62 | 0.0040161 | 0.0064776 | No
23/12/2019 | 17:06 | CRM23 | Urban | Third Party | Vehicle Impact | 50 | 54 | 0.0042657 | 0.0078995 | No
23/12/2019 | 22:17 | SV33 | Urban | Third Party | Other | 1 | 34 | 5.3717e-05 | 0.00015799 | No
24/12/2019 | 08:44 | STO13 | Urban | Asset Failure | Distribution substation | 1 | 116 | 0.00018327 | 0.00015799 | No
24/12/2019 | 10:08 | SS21 | Urban | Asset Failure | HV | 17 | 127 | 0.0034119 | 0.0026858 | No
24/12/2019 | 11:06 | MTN21 | Urban | Third Party | Other | 1 | 116.6 | 0.00018414 | 0.00015799 | No
24/12/2019 | 14:36 | WD14 | Urban | Overloads |  | 9 | 67 | 0.00097808 | 0.0014598 | No
24/12/2019 | 20:08 | CRM35 | Urban | Asset Failure | LV | 1 | 102 | 0.00016115 | 0.00015799 | No
24/12/2019 | 21:51 | HGS33 | Rural Short | Asset Failure | LV | 1 | 34 | 0.00057171 | 0.0016815 | No
25/12/2019 | 01:27 | DMA23 | Rural Short | Animal | Animal impact | 6 | 91 | 0.0091809 | 0.010089 | No
25/12/2019 | 03:03 | OAK24 | Urban | Third Party | Vehicle Impact | 10 | 297 | 0.004758 | 0.001602 | No
25/12/2019 | 10:43 | STO23 | Urban | Asset Failure | LV | 1 | 127 | 0.00020065 | 0.00015799 | No
25/12/2019 | 11:55 | NW31 | Urban | Asset Failure | LV | 1 | 50 | 7.8995e-05 | 0.00015799 | No
25/12/2019 | 14:35 | BU4 | Urban | Asset Failure | LV | 1 | 70 | 0.00011059 | 0.00015799 | No
26/12/2019 | 02:46 | LWN32 | Rural Short | Animal | Other | 1 | 44 | 0.00073986 | 0.0016815 | No
26/12/2019 | 14:06 | DMA15 | Rural Short | Unknown | Unknown | 1 | 34 | 0.00057171 | 0.0016815 | No
26/12/2019 | 14:35 | MC1 | Urban | Overloads |  | 1 | 99.3 | 0.00015694 | 0.00015799 | No
26/12/2019 | 17:55 | NW31 | Urban | Overloads |  | 1 | 70 | 0.00011059 | 0.00015799 | No
26/12/2019 | 18:02 | RBD23 | Urban | Asset Failure | LV | 1 | 137.8 | 0.00021766 | 0.00015799 | No
26/12/2019 | 20:20 | STO13 | Urban | Asset Failure | LV | 1 | 60 | 9.4794e-05 | 0.00015799 | No
26/12/2019 | 21:25 | FTN14 | Urban | Asset Failure | LV | 1 | 145 | 0.00022908 | 0.00015799 | No
27/12/2019 | 02:34 | LWN32 | Rural Short | Animal | Other | 1 | 51 | 0.00085756 | 0.0016815 | No
27/12/2019 | 07:56 | MTN35 | Rural Short | Unknown | Unknown | 1 | 66 | 0.0011098 | 0.0016815 | No
27/12/2019 | 09:04 | FSH12 | Rural Short | Asset Failure | HV | 69 | 161 | 0.1868 | 0.11602 | No
27/12/2019 | 09:10 | FSH12 | Rural Short | Overloads |  | 11 | 33.1 | 0.0058685 | 0.017757 | No
27/12/2019 | 10:31 | CRM24 | Urban | Asset Failure | LV | 17 | 98.8 | 0.0026781 | 0.0027111 | No
27/12/2019 | 11:44 | RWT34 | Urban | Asset Failure | LV | 4 | 31 | 0.00019591 | 0.00063196 | No
27/12/2019 | 12:45 | FTN14 | Urban | Asset Failure | LV | 1 | 116 | 0.00018327 | 0.00015799 | No
27/12/2019 | 14:46 | SR15 | Urban | Unknown | Unknown | 1 | 203.5 | 0.00032148 | 0.00015799 | No
27/12/2019 | 15:00 | KBH35 | Urban | Asset Failure | HV | 1,736 | 64.4 | 0.17674 | 0.27427 | No
27/12/2019 | 18:07 | STO21 | Rural Short | Unknown | Unknown | 1 | 67.4 | 0.0011328 | 0.0016815 | No
27/12/2019 | 19:04 | RBD23 | Urban | Asset Failure | LV | 1 | 81 | 0.00012797 | 0.00015799 | No
27/12/2019 | 19:22 | CRM52 | Urban | Asset Failure | LV | 1 | 78 | 0.00012323 | 0.00015799 | No
28/12/2019 | 00:12 | STO14 | Rural Short | Asset Failure | Distribution substation | 14 | 51 | 0.011886 | 0.023305 | No
28/12/2019 | 01:30 | FSH31 | Urban | Third Party | Other | 1 | 135 | 0.00021329 | 0.00015799 | No
28/12/2019 | 12:29 | SV33 | Urban | Third Party | Other | 1 | 90.5 | 0.0001429 | 0.00015799 | No
28/12/2019 | 13:33 | CRM13 | Urban | Asset Failure | LV | 11 | 117 | 0.0020518 | 0.0017537 | No
28/12/2019 | 17:31 | M34 | Urban | Asset Failure | LV | 1 | 275 | 0.00043447 | 0.00015799 | No
28/12/2019 | 20:29 | SS23 | Urban | Asset Failure | LV | 13 | 76 | 0.001609 | 0.0021171 | No
29/12/2019 | 04:02 | RWT35 | Urban | Animal | Animal impact | 122 | 78 | 0.015034 | 0.019275 | No
29/12/2019 | 08:50 | EW2 | Urban | Planned |  | 8 | 70 | 0.00088474 | 0.0012639 | No
29/12/2019 | 10:15 | DMA15 | Rural Short | Overloads |  | 2 | 89.8 | 0.0030183 | 0.003363 | No
29/12/2019 | 11:31 | BU14 | Urban | Asset Failure | HV | 28 | 100 | 0.0044237 | 0.0044237 | No
29/12/2019 | 15:36 | DMA12 | Urban | Overloads |  | 11 | 69 | 0.0011872 | 0.0017205 | No
29/12/2019 | 16:47 | EB32 | Urban | Overloads |  | 39 | 145.7 | 0.0090396 | 0.0062043 | No
29/12/2019 | 19:56 | BR1 | Urban | Unknown | Unknown | 1 | 144 | 0.0002275 | 0.00015799 | No
30/12/2019 | 00:51 | FTN25 | Urban | Asset Failure | Distribution substation | 31 | 48 | 0.0023274 | 0.0048487 | No
30/12/2019 | 06:55 | HGS33 | Rural Short | Unknown | Unknown | 1 | 94.3 | 0.0015848 | 0.0016815 | No
30/12/2019 | 08:19 | SV16 | Urban | Asset Failure | LV | 1 | 98.9 | 0.00015631 | 0.00015799 | No
30/12/2019 | 09:27 | SV32 | Urban | Asset Failure | LV | 7 | 154.8 | 0.0017756 | 0.001147 | No
30/12/2019 | 09:36 | NP33 | Urban | Overloads |  | 1 | 73.3 | 0.00011578 | 0.00015799 | No
30/12/2019 | 10:33 | MGE12 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 8 | 1,472.0 | 0.019535 | 0.0013271 | No
30/12/2019 | 11:36 | LD33 | Urban | Overloads |  | 18 | 63 | 0.0018394 | 0.0029197 | No
30/12/2019 | 12:18 | NP23 | Urban | Overloads |  | 1 | 71.9 | 0.00011365 | 0.00015799 | No
30/12/2019 | 12:45 | DC12 | Urban |  | HV | 49 | 41 | 0.0031714 | 0.0077415 | No
30/12/2019 | 12:45 | BH23 | Urban |  | HV | 2,957 | 58.1 | 0.2713 | 0.46718 | No
30/12/2019 | 13:32 | NW14 | Urban | Weather |  | 23 | 48 | 0.0017768 | 0.0037017 | No
30/12/2019 | 14:01 | STO21 | Rural Short | Asset Failure | LV | 28 | 74 | 0.035313 | 0.047721 | No
30/12/2019 | 14:12 | RWT35 | Urban | Overloads |  | 5 | 287.7 | 0.0020996 | 0.00072991 | No
30/12/2019 | 14:33 | DMA23 | Rural Short | Asset Failure | HV | 2,502 | 137.5 | 5.7846 | 4.2071 | No
30/12/2019 | 14:50 | NW14 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 21 | 235 | 0.0079639 | 0.0033889 | No
30/12/2019 | 14:52 | FTN24 | Urban | Overloads |  | 1 | 558 | 0.00088158 | 0.00015799 | No
30/12/2019 | 15:05 | MGE23 | Urban | Asset Failure | LV | 17 | 25 | 0.00067146 | 0.0026858 | No
30/12/2019 | 15:11 | STO22 | Urban | Overloads |  | 2 | 413.3 | 0.0012733 | 0.00030808 | No
30/12/2019 | 15:15 | STO13 | Urban | Overloads |  | 23 | 75 | 0.0026981 | 0.0035974 | No
30/12/2019 | 15:31 | STO13 | Urban | Overloads |  | 100 | 104 | 0.016431 | 0.015799 | No
30/12/2019 | 15:41 | BR9 | Urban | Overloads |  | 23 | 67 | 0.0024452 | 0.0036496 | No
30/12/2019 | 15:47 | STO21 | Rural Short | Asset Failure | LV | 1 | 621 | 0.010442 | 0.0016815 | No
30/12/2019 | 16:15 | WD23 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 478 | 22.9 | 0.017306 | 0.075519 | No
30/12/2019 | 16:16 | DMA14 | Urban | Overloads |  | 14 | 419 | 0.0093935 | 0.0022419 | No
30/12/2019 | 16:18 | NP34 | Urban | Overloads |  | 41 | 331 | 0.021572 | 0.0065171 | No
30/12/2019 | 16:29 | BH23 | Urban | Weather |  | 65 | 76 | 0.0078035 | 0.010268 | No
30/12/2019 | 16:40 | OR34 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 236.4 | 0.00037351 | 0.00015799 | No
30/12/2019 | 16:43 | DC3 | Urban | Overloads |  | 1 | 218.3 | 0.00034484 | 0.00015799 | No
30/12/2019 | 17:04 | RBD23 | Urban | Overloads |  | 56 | 326 | 0.028894 | 0.0088632 | No
30/12/2019 | 17:17 | OR23 | Urban | Overloads |  | 45 | 93 | 0.0065458 | 0.0070384 | No
30/12/2019 | 17:18 | HT1 | Urban | Overloads |  | 20 | 111 | 0.003588 | 0.0032325 | No
30/12/2019 | 17:32 | STO13 | Urban | Overloads |  | 26 | 163 | 0.0067986 | 0.0041709 | No
30/12/2019 | 17:49 | CRM34 | Urban | Third Party | Other | 44 | 66.6 | 0.0046274 | 0.0069516 | No
30/12/2019 | 18:02 | EL13 | Urban | Overloads |  | 69 | 303 | 0.033031 | 0.010901 | No
30/12/2019 | 18:14 | NW21 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 259.9 | 0.00041056 | 0.00015799 | No
30/12/2019 | 18:26 | WD16 | Urban | Asset Failure | LV | 19 | 199 | 0.0059139 | 0.0029718 | No
30/12/2019 | 18:36 | CRM23 | Urban | Overloads |  | 38 | 169 | 0.010045 | 0.0059436 | No
30/12/2019 | 18:37 | NW13 | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 9 | 23 | 0.00032704 | 0.0014219 | No
30/12/2019 | 18:37 | CFD16 | Urban | Asset Failure | LV | 1 | 139.3 | 0.00022013 | 0.00015799 | No
30/12/2019 | 19:28 | HGS21 | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 31 | 174 | 0.090717 | 0.052126 | No
30/12/2019 | 19:53 | MTN23 | Urban | Asset Failure | LV | 13 | 127 | 0.0026004 | 0.0020475 | No
30/12/2019 | 21:24 | NP36 | Urban | Unknown | Unknown | 1 | 141 | 0.00022277 | 0.00015799 | No
30/12/2019 | 23:10 | MR13 | Urban | Asset Failure | LV | 1 | 94.5 | 0.00014925 | 0.00015799 | No
31/12/2019 | 00:04 | STO14 | Rural Short | Weather |  | 133 | 76 | 0.16997 | 0.22364 | No
31/12/2019 | 00:08 | NW13 | Urban | Asset Failure | LV | 1 | 109 | 0.00017221 | 0.00015799 | No
31/12/2019 | 03:55 | EW9 | Urban | Asset Failure | LV | 1 | 295 | 0.00046607 | 0.00015799 | No
31/12/2019 | 04:50 | BU1 | Urban | Asset Failure | HV | 917 | 71.3 | 0.10326 | 0.14488 | No
31/12/2019 | 05:30 | BH31 | Urban | Asset Failure | HV | 908 | 161.6 | 0.23188 | 0.14345 | No
31/12/2019 | 06:20 | DVY34 | Urban | Weather |  | 1 | 499.6 | 0.00078927 | 0.00015799 | No
31/12/2019 | 06:59 | FSH31 | Urban | Weather |  | 57 | 68 | 0.0061237 | 0.0090054 | No
31/12/2019 | 06:59 | FSH32 | Rural Short | Weather |  | 4 | 633.7 | 0.042621 | 0.006726 | No
31/12/2019 | 08:18 | STO23 | Urban | Asset Failure | LV | 1 | 291.8 | 0.00046099 | 0.00015799 | No
31/12/2019 | 09:25 | FSH32 | Rural Short | Weather |  | 33 | 13.5 | 0.0075095 | 0.055489 | No
31/12/2019 | 10:08 | NO7 | Urban | Unknown | Unknown | 1 | 231.6 | 0.00036593 | 0.00015799 | No
31/12/2019 | 12:43 | GW12 | Urban | Overloads |  | 6 | 126.1 | 0.0012486 | 0.0009906 | No
31/12/2019 | 12:51 | NW14 | Urban | Vegetation | Grow-in - NSP responsibility | 65 | 147 | 0.015096 | 0.010269 | No
31/12/2019 | 15:44 | MGE13 | Urban | Asset Failure | HV | 2 | 1,455.2 | 0.0045982 | 0.00031598 | No
31/12/2019 | 17:21 | OAK26 | Urban | Overloads |  | 1 | 114 | 0.00018006 | 0.00015799 | No
31/12/2019 | 19:19 | BU6 | Urban | Overloads |  | 1 | 61 | 9.6374e-05 | 0.00015799 | No
31/12/2019 | 19:54 | BW21 | Urban | Asset Failure | LV | 1 | 56 | 8.8474e-05 | 0.00015799 | No
31/12/2019 | 23:44 | DN6 | Urban | Asset Failure | LV | 1 | 91 | 0.00014377 | 0.00015799 | No
02/01/2019 | 08:50 | DMA23 | Rural Short | Planned |  | 22 | 130 |  |  | No
02/01/2019 | 09:20 | WD36 | Urban | Planned |  | 2 | 212 |  |  | No
02/01/2019 | 11:55 | CRM34 | Urban | Planned |  | 21 | 35 |  |  | No
03/01/2019 | 08:05 | SV20 | Urban | Planned |  | 3 | 10 |  |  | No
03/01/2019 | 08:31 | HGS33 | Rural Short | Planned |  | 34 | 111 |  |  | No
03/01/2019 | 08:35 | DVY11 | Urban | Planned |  | 3 | 40 |  |  | No
03/01/2019 | 08:45 | HGS21 | Rural Short | Planned |  | 13 | 115 |  |  | No
03/01/2019 | 09:01 | WD36 | Urban | Planned |  | 95 | 255 |  |  | No
03/01/2019 | 11:01 | HGS22 | Rural Short | Planned |  | 13 | 102 |  |  | No
04/01/2019 | 08:30 | OAK26 | Urban | Planned |  | 11 | 70 |  |  | No
04/01/2019 | 14:49 | DVY24 | Rural Short | Planned |  | 4 | 69 |  |  | No
06/01/2019 | 08:35 | SVW45 | Urban | Planned |  | 1 | 620 |  |  | No
07/01/2019 | 08:40 | BR4 | Urban | Planned |  | 23 | 205 |  |  | No
07/01/2019 | 08:45 | MC2 | Urban | Planned |  | 32 | 55 |  |  | No
07/01/2019 | 09:10 | LWN35 | Urban | Planned |  | 9 | 160 |  |  | No
08/01/2019 | 08:05 | SS23 | Urban | Planned |  | 233 | 475 |  |  | No
08/01/2019 | 08:13 | LWN35 | Urban | Planned |  | 50 | 140 |  |  | No
08/01/2019 | 08:23 | GW7 | Urban | Planned |  | 121 | 260 |  |  | No
08/01/2019 | 08:30 | EL5 | Urban | Planned |  | 100 | 65 |  |  | No
08/01/2019 | 08:30 | FTN14 | Urban | Planned |  | 96 | 230 |  |  | No
08/01/2019 | 08:30 | KBH32 | Urban | Planned |  | 23 | 160 |  |  | No
08/01/2019 | 08:30 | NP36 | Urban | Planned |  | 147 | 160 |  |  | No
08/01/2019 | 08:50 | LD32 | Urban | Planned |  | 14 | 190 |  |  | No
09/01/2019 | 07:00 | EL5 | Urban | Planned |  | 2 | 620 |  |  | No
09/01/2019 | 08:00 | CDA23 | Urban | Planned |  | 209 | 370 |  |  | No
09/01/2019 | 08:30 | DMA24 | Rural Short | Planned |  | 16 | 248 |  |  | No
09/01/2019 | 08:30 | EB12 | Urban | Planned |  | 54 | 60 |  |  | No
09/01/2019 | 08:42 | LWN35 | Urban | Planned |  | 19 | 240 |  |  | No
09/01/2019 | 08:50 | M32 | Urban | Planned |  | 24 | 240 |  |  | No
09/01/2019 | 09:04 | K2 | Urban | Planned |  | 118 | 97 |  |  | No
09/01/2019 | 10:00 | GW2 | Urban | Planned |  | 48 | 85 |  |  | No
10/01/2019 | 08:00 | EM5 | Urban | Planned |  | 28 | 385 |  |  | No
10/01/2019 | 08:28 | RBD12 | Rural Short | Planned |  | 36 | 222 |  |  | No
10/01/2019 | 08:40 | DVY24 | Rural Short | Planned |  | 2 | 215 |  |  | No
10/01/2019 | 08:40 | MGE34 | Urban | Planned |  | 42 | 165 |  |  | No
10/01/2019 | 08:45 | NP12 | Urban | Planned |  | 33 | 150 |  |  | No
10/01/2019 | 09:45 | M22 | Urban | Planned |  | 114 | 295 |  |  | No
10/01/2019 | 10:00 | MGE22 | Urban | Planned |  | 3 | 120 |  |  | No
10/01/2019 | 12:30 | FSH12 | Rural Short | Planned |  | 1 | 180 |  |  | No
11/01/2019 | 08:00 | FSH13 | Urban | Planned |  | 8 | 239 |  |  | No
11/01/2019 | 08:00 | CFD11 | Urban | Planned |  | 4 | 6,179.5 |  |  | No
11/01/2019 | 08:02 | EM5 | Urban | Planned |  | 57 | 320 |  |  | No
11/01/2019 | 08:02 | LD4 | Urban | Planned |  | 95 | 331 |  |  | No
11/01/2019 | 08:20 | M22 | Urban | Planned |  | 45 | 250 |  |  | No
11/01/2019 | 08:40 | M32 | Urban | Planned |  | 3 | 90 |  |  | No
11/01/2019 | 08:50 | EB11 | Urban | Planned |  | 31 | 295 |  |  | No
11/01/2019 | 09:16 | DMA14 | Urban | Planned |  | 41 | 150 |  |  | No
11/01/2019 | 09:19 | FSH34 | Urban | Planned |  | 65 | 220 |  |  | No
12/01/2019 | 08:00 | NB32 | Urban | Planned |  | 23 | 420 |  |  | No
12/01/2019 | 08:06 | CM25 | Urban | Planned |  | 436 | 547 |  |  | No
12/01/2019 | 08:59 | EB22 | Urban | Planned |  | 163 | 399 |  |  | No
13/01/2019 | 07:15 | K7 | Urban | Planned |  | 66 | 505 |  |  | No
13/01/2019 | 08:05 | HT9 | Urban | Planned |  | 1 | 380 |  |  | No
13/01/2019 | 09:57 | NO2 | Urban | Planned |  | 25 | 153 |  |  | No
13/01/2019 | 09:57 | NO6 | Urban | Planned |  | 23 | 153 |  |  | No
14/01/2019 | 08:38 | NP16 | Urban | Planned |  | 72 | 157 |  |  | No
15/01/2019 | 08:00 | CFD11 | Urban | Planned |  | 4 | 450 |  |  | No
15/01/2019 | 08:17 | FTN14 | Urban | Planned |  | 45 | 158 |  |  | No
15/01/2019 | 08:17 | OAK23 | Urban | Planned |  | 20 | 583 |  |  | No
15/01/2019 | 08:17 | OAK26 | Urban | Planned |  | 7 | 583 |  |  | No
15/01/2019 | 08:40 | NW33 | Urban | Planned |  | 36 | 227 |  |  | No
15/01/2019 | 08:43 | BR15 | Urban | Planned |  | 36 | 201 |  |  | No
15/01/2019 | 08:43 | BR6 | Urban | Planned |  | 92 | 201 |  |  | No
15/01/2019 | 09:12 | MR33 | Urban | Planned |  | 6 | 288 |  |  | No
15/01/2019 | 10:15 | FSH21 | Rural Short | Planned |  | 3 | 30 |  |  | No
15/01/2019 | 12:10 | FSH21 | Rural Short | Planned |  | 2 | 15 |  |  | No
16/01/2019 | 08:10 | GW7 | Urban | Planned |  | 54 | 180 |  |  | No
16/01/2019 | 08:45 | EB12 | Urban | Planned |  | 39 | 75 |  |  | No
16/01/2019 | 08:46 | MR22 | Urban | Planned |  | 59 | 49 |  |  | No
16/01/2019 | 09:46 | SR12 | Urban | Planned |  | 1 | 271 |  |  | No
16/01/2019 | 09:46 | SR15 | Urban | Planned |  | 8 | 271 |  |  | No
17/01/2019 | 07:00 | GW2 | Urban | Planned |  | 2 | 540 |  |  | No
17/01/2019 | 07:57 | DMA23 | Rural Short | Planned |  | 28 | 473 |  |  | No
17/01/2019 | 08:34 | NP36 | Urban | Planned |  | 132 | 196 |  |  | No
17/01/2019 | 08:45 | BR1 | Urban | Planned |  | 133 | 87 |  |  | No
17/01/2019 | 08:47 | EM7 | Urban | Planned |  | 134 | 134 |  |  | No
17/01/2019 | 09:36 | BC23 | Urban | Planned |  | 24 | 130 |  |  | No
17/01/2019 | 09:45 | STO13 | Urban | Planned |  | 41 | 105 |  |  | No
18/01/2019 | 08:00 | CRM13 | Urban | Planned |  | 8 | 195 |  |  | No
18/01/2019 | 08:00 | DSH31 | Urban | Planned |  | 1 | 130 |  |  | No
18/01/2019 | 08:03 | FTN12 | Urban | Planned |  | 89 | 286 |  |  | No
18/01/2019 | 08:25 | STO13 | Urban | Planned |  | 2 | 425 |  |  | No
18/01/2019 | 08:35 | KBH32 | Urban | Planned |  | 61 | 210 |  |  | No
18/01/2019 | 08:35 | NP36 | Urban | Planned |  | 49 | 210 |  |  | No
18/01/2019 | 08:40 | K4 | Urban | Planned |  | 102 | 275 |  |  | No
18/01/2019 | 10:31 | OAK23 | Urban | Planned |  | 44 | 164 |  |  | No
18/01/2019 | 11:30 | MGE31 | Urban | Planned |  | 54 | 240 |  |  | No
18/01/2019 | 11:30 | MGE33 | Urban | Planned |  | 22 | 240 |  |  | No
19/01/2019 | 08:00 | CRM21 | Urban | Planned |  | 476 | 120 |  |  | No
19/01/2019 | 08:28 | RWT23 | Urban | Planned |  | 59 | 434 |  |  | No
19/01/2019 | 08:35 | M31 | Urban | Planned |  | 84 | 304 |  |  | No
20/01/2019 | 07:00 | EM6 | Urban | Planned |  | 2 | 270 |  |  | No
20/01/2019 | 07:30 | BC22 | Urban | Planned |  | 31 | 435 |  |  | No
20/01/2019 | 07:31 | SR15 | Urban | Planned |  | 47 | 686 |  |  | No
20/01/2019 | 07:40 | OAK22 | Urban | Planned |  | 19 | 425 |  |  | No
20/01/2019 | 08:30 | NO7 | Urban | Planned |  | 403 | 507 |  |  | No
20/01/2019 | 08:34 | NO7 | Urban | Planned |  | 1 | 523 |  |  | No
20/01/2019 | 08:34 | NO7 | Urban | Planned |  | 24 | 524 |  |  | No
20/01/2019 | 09:15 | CM13 | Urban | Planned |  | 2 | 175 |  |  | No
21/01/2019 | 11:30 | EB22 | Urban | Planned |  | 15 | 89.6 |  |  | No
22/01/2019 | 08:00 | CRM21 | Urban | Planned |  | 8 | 175 |  |  | No
22/01/2019 | 08:15 | EB14 | Urban | Planned |  | 79 | 225 |  |  | No
22/01/2019 | 08:30 | NP16 | Urban | Planned |  | 19 | 300 |  |  | No
22/01/2019 | 08:30 | RWT34 | Urban | Planned |  | 57 | 570 |  |  | No
22/01/2019 | 08:45 | CDA23 | Urban | Planned |  | 45 | 270 |  |  | No
22/01/2019 | 08:52 | GW2 | Urban | Planned |  | 21 | 291 |  |  | No
22/01/2019 | 09:00 | M23 | Urban | Planned |  | 333 | 380 |  |  | No
22/01/2019 | 09:18 | LWN21 | Rural Short | Planned |  | 11 | 287 |  |  | No
22/01/2019 | 12:44 | CDA23 | Urban | Planned |  | 10 | 166 |  |  | No
23/01/2019 | 08:06 | NP11 | Urban | Planned |  | 30 | 408 |  |  | No
23/01/2019 | 08:15 | GW3 | Urban | Planned |  | 71 | 175 |  |  | No
23/01/2019 | 08:17 | MR15 | Urban | Planned |  | 130 | 213 |  |  | No
23/01/2019 | 08:20 | GW10 | Urban | Planned |  | 135 | 260 |  |  | No
23/01/2019 | 08:26 | FSH32 | Rural Short | Planned |  | 55 | 557 |  |  | No
23/01/2019 | 08:50 | K3 | Urban | Planned |  | 78 | 200 |  |  | No
23/01/2019 | 09:00 | FSH33 | Urban | Planned |  | 15 | 195 |  |  | No
23/01/2019 | 09:00 | OAK21 | Urban | Planned |  | 28 | 462 |  |  | No
24/01/2019 | 08:31 | CFD26 | Urban | Planned |  | 116 | 140 |  |  | No
25/01/2019 | 00:00 | RWT23 | Urban | Planned |  | 105 | 191 |  |  | No
25/01/2019 | 08:00 | MTN24 | Rural Short | Planned |  | 2 | 510 |  |  | No
25/01/2019 | 10:30 | EB22 | Urban | Planned |  | 95 | 330 |  |  | No
25/01/2019 | 11:31 | GW8 | Urban | Planned |  | 73 | 210 |  |  | No
27/01/2019 | 08:17 | DN22 | Urban | Planned |  | 238 | 163 |  |  | No
27/01/2019 | 08:30 | EB31 | Urban | Planned |  | 211 | 230 |  |  | No
27/01/2019 | 08:36 | DVY22 | Urban | Planned |  | 30 | 388 |  |  | No
27/01/2019 | 08:36 | DVY32 | Urban | Planned |  | 46 | 388 |  |  | No
27/01/2019 | 10:00 | NP36 | Urban | Planned |  | 12 | 25 |  |  | No
27/01/2019 | 14:31 | NP11 | Urban | Planned |  | 24 | 12 |  |  | No
29/01/2019 | 08:56 | OE4 | Urban | Planned |  | 41 | 280 |  |  | No
29/01/2019 | 10:00 | SS23 | Urban | Planned |  | 35 | 95 |  |  | No
30/01/2019 | 01:12 | KBH32 | Urban | Planned |  | 17 | 90 |  |  | No
30/01/2019 | 08:00 | SS23 | Urban | Planned |  | 46 | 285 |  |  | No
30/01/2019 | 08:01 | NB35 | Urban | Planned |  | 38 | 317 |  |  | No
30/01/2019 | 08:05 | EM5 | Urban | Planned |  | 92 | 210 |  |  | No
30/01/2019 | 09:10 | OE4 | Urban | Planned |  | 56 | 390 |  |  | No
31/01/2019 | 08:10 | SS13 | Urban | Planned |  | 60 | 250 |  |  | No
31/01/2019 | 08:30 | CM13 | Urban | Planned |  | 6 | 500 |  |  | No
31/01/2019 | 08:38 | NP24 | Urban | Planned |  | 111 | 351 |  |  | No
31/01/2019 | 08:50 | CRM21 | Urban | Planned |  | 47 | 225 |  |  | No
31/01/2019 | 09:30 | DC10 | Urban | Planned |  | 142 | 105 |  |  | No
31/01/2019 | 09:45 | GW8 | Urban | Planned |  | 61 | 165 |  |  | No
31/01/2019 | 12:39 | LD2 | Urban | Planned |  | 18 | 76 |  |  | No
01/02/2019 | 08:00 | DVY24 | Rural Short | Planned |  | 1 | 300 |  |  | No
01/02/2019 | 08:01 | DVY24 | Rural Short | Planned |  | 9 | 215 |  |  | No
01/02/2019 | 08:10 | SS23 | Urban | Planned |  | 492 | 260 |  |  | No
01/02/2019 | 08:52 | EB21 | Urban | Planned |  | 2 | 193 |  |  | No
01/02/2019 | 09:00 | NB22 | Urban | Planned |  | 44 | 361 |  |  | No
01/02/2019 | 13:10 | MC2 | Urban | Planned |  | 1 | 81 |  |  | No
02/02/2019 | 08:10 | K6 | Urban | Planned |  | 14 | 470 |  |  | No
02/02/2019 | 08:30 | NP11 | Urban | Planned |  | 4 | 120 |  |  | No
02/02/2019 | 08:34 | DVY22 | Urban | Planned |  | 9 | 80 |  |  | No
02/02/2019 | 08:40 | KBH33 | Urban | Planned |  | 17 | 322 |  |  | No
03/02/2019 | 07:30 | RD4 | Urban | Planned |  | 50 | 95 |  |  | No
03/02/2019 | 08:20 | DVY11 | Urban | Planned |  | 17 | 45 |  |  | No
04/02/2019 | 08:00 | RD4 | Urban | Planned |  | 2 | 420 |  |  | No
04/02/2019 | 08:03 | BR15 | Urban | Planned |  | 128 | 481.9 |  |  | No
04/02/2019 | 08:34 | EB21 | Urban | Planned |  | 48 | 418 |  |  | No
04/02/2019 | 08:40 | BR4 | Urban | Planned |  | 22 | 310 |  |  | No
04/02/2019 | 08:45 | HGS33 | Rural Short | Planned |  | 7 | 60 |  |  | No
05/02/2019 | 08:00 | OAK33 | Urban | Planned |  | 119 | 370 |  |  | No
05/02/2019 | 08:15 | MR24 | Urban | Planned |  | 1 | 1,993.0 |  |  | No
05/02/2019 | 08:15 | OR33 | Urban | Planned |  | 31 | 360 |  |  | No
05/02/2019 | 08:15 | OR35 | Urban | Planned |  | 202 | 360 |  |  | No
05/02/2019 | 08:18 | NP25 | Urban | Planned |  | 388 | 401 |  |  | No
05/02/2019 | 08:32 | LD32 | Urban | Planned |  | 211 | 376 |  |  | No
05/02/2019 | 09:04 | FTN22 | Urban | Planned |  | 120 | 180 |  |  | No
05/02/2019 | 10:00 | EW3 | Urban | Planned |  | 20 | 225 |  |  | No
05/02/2019 | 10:08 | OR25 | Urban | Planned |  | 75 | 382 |  |  | No
05/02/2019 | 10:10 | OR33 | Urban | Planned |  | 76 | 100 |  |  | No
05/02/2019 | 11:30 | LWN21 | Rural Short | Planned |  | 3 | 225 |  |  | No
05/02/2019 | 12:37 | OR33 | Urban | Planned |  | 66 | 198 |  |  | No
05/02/2019 | 13:02 | DC3 | Urban | Planned |  | 93 | 15 |  |  | No
06/02/2019 | 08:00 | EM8 | Urban | Planned |  | 155 | 515 |  |  | No
06/02/2019 | 08:00 | GW11 | Urban | Planned |  | 111 | 345 |  |  | No
06/02/2019 | 08:15 | MR24 | Urban | Planned |  | 53 | 553 |  |  | No
06/02/2019 | 08:26 | OR25 | Urban | Planned |  | 70 | 258 |  |  | No
06/02/2019 | 08:36 | STO23 | Urban | Planned |  | 61 | 297 |  |  | No
06/02/2019 | 08:48 | RBD24 | Urban | Planned |  | 81 | 100 |  |  | No
06/02/2019 | 10:44 | EB22 | Urban | Planned |  | 40 | 147 |  |  | No
07/02/2019 | 08:00 | NO32 | Urban | Planned |  | 1 | 480 |  |  | No
07/02/2019 | 08:00 | KBH35 | Urban | Planned |  | 53 | 405 |  |  | No
07/02/2019 | 08:30 | GW2 | Urban | Planned |  | 34 | 435 |  |  | No
07/02/2019 | 08:32 | FSH34 | Urban | Planned |  | 84 | 304 |  |  | No
07/02/2019 | 08:38 | NP36 | Urban | Planned |  | 226 | 212 |  |  | No
07/02/2019 | 09:10 | MR22 | Urban | Planned |  | 50 | 275 |  |  | No
07/02/2019 | 09:14 | SR15 | Urban | Planned |  | 15 | 310 |  |  | No
07/02/2019 | 09:14 | SR24 | Urban | Planned |  | 15 | 310 |  |  | No
07/02/2019 | 09:15 | MTN31 | Urban | Planned |  | 31 | 255 |  |  | No
07/02/2019 | 14:06 | MR13 | Urban | Planned |  | 19 | 204 |  |  | No
07/02/2019 | 18:10 | BH22 | Urban | Planned |  | 21 | 130 |  |  | No
08/02/2019 | 08:00 | NW33 | Urban | Planned |  | 11 | 179.4 |  |  | No
08/02/2019 | 08:30 | DMA12 | Urban | Planned |  | 23 | 210 |  |  | No
08/02/2019 | 08:44 | FTN23 | Urban | Planned |  | 83 | 199 |  |  | No
08/02/2019 | 09:00 | NW31 | Urban | Planned |  | 12 | 120 |  |  | No
08/02/2019 | 09:03 | GW8 | Urban | Planned |  | 20 | 263 |  |  | No
08/02/2019 | 09:15 | NW23 | Urban | Planned |  | 48 | 190 |  |  | No
08/02/2019 | 09:51 | CFD11 | Urban | Planned |  | 12 | 349 |  |  | No
08/02/2019 | 09:51 | CFD16 | Urban | Planned |  | 2 | 349 |  |  | No
08/02/2019 | 10:04 | HGS23 | Rural Short | Planned |  | 1 | 200 |  |  | No
09/02/2019 | 07:26 | BW23 | Urban | Planned |  | 6 | 300 |  |  | No
09/02/2019 | 07:30 | AR12 | Urban | Planned |  | 2 | 580 |  |  | No
09/02/2019 | 08:00 | HGS31 | Rural Short | Planned |  | 1 | 180 |  |  | No
09/02/2019 | 08:40 | CDA24 | Urban | Planned |  | 17 | 150 |  |  | No
10/02/2019 | 07:42 | EM7 | Urban | Planned |  | 2 | 304 |  |  | No
10/02/2019 | 07:46 | FTN11 | Urban | Planned |  | 24 | 334 |  |  | No
10/02/2019 | 08:12 | KBH32 | Urban | Planned |  | 4 | 222 |  |  | No
10/02/2019 | 08:16 | OAK22 | Urban | Planned |  | 35 | 110 |  |  | No
10/02/2019 | 08:20 | OAK22 | Urban | Planned |  | 22 | 160 |  |  | No
10/02/2019 | 08:32 | RBD21 | Rural Short | Planned |  | 20 | 58 |  |  | No
10/02/2019 | 08:36 | LD32 | Urban | Planned |  | 165 | 387 |  |  | No
10/02/2019 | 10:16 | RBD21 | Rural Short | Planned |  | 49 | 93 |  |  | No
10/02/2019 | 11:35 | OAK32 | Urban | Planned |  | 8 | 55 |  |  | No
11/02/2019 | 08:45 | NP34 | Urban | Planned |  | 36 | 96 |  |  | No
11/02/2019 | 09:20 | K4 | Urban | Planned |  | 102 | 300 |  |  | No
11/02/2019 | 11:35 | NP14 | Urban | Planned |  | 21 | 95 |  |  | No
12/02/2019 | 08:05 | DMA23 | Rural Short | Planned |  | 2 | 55 |  |  | No
12/02/2019 | 08:38 | BH21 | Urban | Planned |  | 87 | 142 |  |  | No
12/02/2019 | 08:40 | M31 | Urban | Planned |  | 40 | 405 |  |  | No
12/02/2019 | 08:45 | BW34 | Urban | Planned |  | 34 | 300 |  |  | No
12/02/2019 | 09:15 | NW23 | Urban | Planned |  | 62 | 230 |  |  | No
12/02/2019 | 09:21 | DMA21 | Urban | Planned |  | 14 | 239 |  |  | No
12/02/2019 | 09:21 | RBD13 | Urban | Planned |  | 27 | 239 |  |  | No
12/02/2019 | 09:30 | EL8 | Urban | Planned |  | 16 | 270 |  |  | No
12/02/2019 | 09:45 | NP33 | Urban | Planned |  | 56 | 308 |  |  | No
12/02/2019 | 10:18 | RWT34 | Urban | Planned |  | 121 | 281 |  |  | No
12/02/2019 | 13:30 | DVY14 | Urban | Planned |  | 6 | 20 |  |  | No
12/02/2019 | 13:30 | NW23 | Urban | Planned |  | 69 | 60 |  |  | No
13/02/2019 | 08:05 | EW12 | Urban | Planned |  | 136 | 400 |  |  | No
13/02/2019 | 08:10 | FSH12 | Rural Short | Planned |  | 19 | 55 |  |  | No
13/02/2019 | 08:15 | SH32 | Urban | Planned |  | 41 | 143 |  |  | No
13/02/2019 | 08:18 | LWN21 | Rural Short | Planned |  | 86 | 367 |  |  | No
13/02/2019 | 08:34 | M11 | Urban | Planned |  | 132 | 394 |  |  | No
13/02/2019 | 08:36 | CRM21 | Urban | Planned |  | 1 | 288 |  |  | No
13/02/2019 | 08:36 | RBD23 | Urban | Planned |  | 68 | 288 |  |  | No
13/02/2019 | 08:40 | GW8 | Urban | Planned |  | 90 | 130 |  |  | No
13/02/2019 | 08:40 | OAK33 | Urban | Planned |  | 55 | 410 |  |  | No
13/02/2019 | 08:45 | EL13 | Urban | Planned |  | 206 | 229 |  |  | No
13/02/2019 | 09:00 | GW7 | Urban | Planned |  | 20 | 135 |  |  | No
13/02/2019 | 09:30 | MR32 | Urban | Planned |  | 46 | 207 |  |  | No
13/02/2019 | 09:32 | MTN24 | Rural Short | Planned |  | 2 | 78 |  |  | No
13/02/2019 | 10:20 | FSH21 | Rural Short | Planned |  | 4 | 30 |  |  | No
13/02/2019 | 11:00 | MTN22 | Rural Short | Planned |  | 27 | 213 |  |  | No
13/02/2019 | 14:11 | MTN24 | Rural Short | Planned |  | 4 | 66 |  |  | No
13/02/2019 | 17:00 | MGE31 | Urban | Planned |  | 2 | 90 |  |  | No
14/02/2019 | 07:00 | NP14 | Urban | Planned |  | 13 | 30 |  |  | No
14/02/2019 | 08:00 | CM25 | Urban | Planned |  | 271 | 743 |  |  | No
14/02/2019 | 08:08 | EL12 | Urban | Planned |  | 64 | 357 |  |  | No
14/02/2019 | 08:08 | EL9 | Urban | Planned |  | 51 | 357 |  |  | No
14/02/2019 | 08:25 | RWT24 | Urban | Planned |  | 31 | 420 |  |  | No
14/02/2019 | 08:30 | FTN24 | Urban | Planned |  | 18 | 75 |  |  | No
14/02/2019 | 08:34 | STO14 | Rural Short | Planned |  | 47 | 27 |  |  | No
14/02/2019 | 08:35 | RBD24 | Urban | Planned |  | 119 | 45 |  |  | No
14/02/2019 | 08:45 | GW5 | Urban | Planned |  | 80 | 240 |  |  | No
14/02/2019 | 09:00 | EM2 | Urban | Planned |  | 99 | 150 |  |  | No
14/02/2019 | 09:30 | RBD13 | Urban | Planned |  | 44 | 190 |  |  | No
14/02/2019 | 09:30 | RBD24 | Urban | Planned |  | 60 | 190 |  |  | No
14/02/2019 | 09:40 | BT15 | Urban | Planned |  | 84 | 235 |  |  | No
14/02/2019 | 11:10 | NP12 | Urban | Planned |  | 53 | 125 |  |  | No
14/02/2019 | 11:43 | LWN24 | Urban | Planned |  | 60 | 101 |  |  | No
14/02/2019 | 12:01 | EM2 | Urban | Planned |  | 1 | 23 |  |  | No
14/02/2019 | 23:21 | OR24 | Urban | Planned |  | 9 | 68 |  |  | No
15/02/2019 | 08:00 | HGS22 | Rural Short | Planned |  | 40 | 469.5 |  |  | No
15/02/2019 | 08:02 | RBD11 | Urban | Planned |  | 61 | 297 |  |  | No
15/02/2019 | 08:05 | BW34 | Urban | Planned |  | 4 | 65 |  |  | No
15/02/2019 | 08:20 | FTN11 | Urban | Planned |  | 71 | 282 |  |  | No
15/02/2019 | 09:00 | MTN35 | Rural Short | Planned |  | 1 | 300 |  |  | No
15/02/2019 | 09:10 | MC2 | Urban | Planned |  | 81 | 260 |  |  | No
15/02/2019 | 09:10 | MC3 | Urban | Planned |  | 29 | 260 |  |  | No
15/02/2019 | 09:15 | GW11 | Urban | Planned |  | 2 | 180 |  |  | No
15/02/2019 | 10:55 | MTN22 | Rural Short | Planned |  | 42 | 140 |  |  | No
15/02/2019 | 13:30 | BU9 | Urban | Planned |  | 67 | 50 |  |  | No
15/02/2019 | 13:45 | NO7 | Urban | Planned |  | 66 | 30 |  |  | No
17/02/2019 | 08:00 | DN11 | Urban | Planned |  | 3 | 60 |  |  | No
17/02/2019 | 08:02 | FTN22 | Urban | Planned |  | 53 | 287 |  |  | No
17/02/2019 | 08:02 | OE1 | Urban | Planned |  | 44 | 403 |  |  | No
17/02/2019 | 08:02 | OE9 | Urban | Planned |  | 4 | 403 |  |  | No
17/02/2019 | 08:17 | CDA23 | Urban | Planned |  | 75 | 432 |  |  | No
17/02/2019 | 08:20 | K7 | Urban | Planned |  | 66 | 460 |  |  | No
17/02/2019 | 18:30 | MR23 | Urban | Planned |  | 3 | 729.4 |  |  | No
18/02/2019 | 08:55 | DC7 | Urban | Planned |  | 2 | 420 |  |  | No
18/02/2019 | 11:06 | DC2 | Urban | Planned |  | 74 | 2 |  |  | No
18/02/2019 | 18:00 | NB32 | Urban | Planned |  | 2 | 710 |  |  | No
19/02/2019 | 07:12 | NP33 | Urban | Planned |  | 117 | 376 |  |  | No
19/02/2019 | 07:30 | BH12 | Urban | Planned |  | 122 | 343 |  |  | No
19/02/2019 | 08:00 | MTN23 | Urban | Planned |  | 1 | 180 |  |  | No
19/02/2019 | 08:18 | GW5 | Urban | Planned |  | 62 | 528 |  |  | No
19/02/2019 | 08:22 | GW8 | Urban | Planned |  | 73 | 132 |  |  | No
19/02/2019 | 08:45 | RBD23 | Urban | Planned |  | 19 | 170 |  |  | No
19/02/2019 | 09:25 | BT15 | Urban | Planned |  | 61 | 265 |  |  | No
19/02/2019 | 09:25 | BT4 | Urban | Planned |  | 98 | 265 |  |  | No
19/02/2019 | 10:57 | EB22 | Urban | Planned |  | 95 | 137 |  |  | No
20/02/2019 | 07:22 | EM8 | Urban | Planned |  | 15 | 137 |  |  | No
20/02/2019 | 07:38 | NP16 | Urban | Planned |  | 181 | 197 |  |  | No
20/02/2019 | 07:49 | MR33 | Urban | Planned |  | 8 | 460 |  |  | No
20/02/2019 | 08:05 | EB12 | Urban | Planned |  | 197 | 335 |  |  | No
20/02/2019 | 08:14 | FSH34 | Urban | Planned |  | 46 | 145 |  |  | No
20/02/2019 | 08:20 | OAK33 | Urban | Planned |  | 50 | 235 |  |  | No
20/02/2019 | 08:20 | SS23 | Urban | Planned |  | 3 | 100 |  |  | No
20/02/2019 | 08:40 | NP33 | Urban | Planned |  | 4 | 95 |  |  | No
21/02/2019 | 07:26 | GW12 | Urban | Planned |  | 33 | 274 |  |  | No
21/02/2019 | 08:00 | EW1 | Urban | Planned |  | 272 | 480 |  |  | No
21/02/2019 | 08:00 | RD4 | Urban | Planned |  | 2 | 419.3 |  |  | No
21/02/2019 | 08:07 | DN22 | Urban | Planned |  | 90 | 308 |  |  | No
21/02/2019 | 08:10 | MC3 | Urban | Planned |  | 188 | 355 |  |  | No
21/02/2019 | 08:20 | M33 | Urban | Planned |  | 38 | 330 |  |  | No
21/02/2019 | 08:51 | GW7 | Urban | Planned |  | 33 | 112 |  |  | No
21/02/2019 | 09:00 | SR25 | Urban | Planned |  | 1 | 30 |  |  | No
21/02/2019 | 09:15 | EM7 | Urban | Planned |  | 24 | 60 |  |  | No
21/02/2019 | 09:15 | MGE23 | Urban | Planned |  | 28 | 430 |  |  | No
21/02/2019 | 11:15 | NW23 | Urban | Planned |  | 34 | 105 |  |  | No
21/02/2019 | 11:53 | MR13 | Urban | Planned |  | 100 | 107 |  |  | No
22/02/2019 | 04:40 | DN9 | Urban | Planned |  | 2 | 80 |  |  | No
22/02/2019 | 07:41 | MTN22 | Rural Short | Planned |  | 6 | 179 |  |  | No
22/02/2019 | 08:00 | BW34 | Urban | Planned |  | 49 | 300 |  |  | No
22/02/2019 | 08:00 | SS23 | Urban | Planned |  | 143 | 660 |  |  | No
22/02/2019 | 08:05 | NP23 | Urban | Planned |  | 65 | 305 |  |  | No
22/02/2019 | 08:40 | HGS22 | Rural Short | Planned |  | 5 | 65 |  |  | No
22/02/2019 | 08:42 | NP33 | Urban | Planned |  | 16 | 148 |  |  | No
22/02/2019 | 09:00 | OE14 | Urban | Planned |  | 37 | 133 |  |  | No
22/02/2019 | 09:10 | NB25 | Urban | Planned |  | 10 | 175 |  |  | No
22/02/2019 | 09:51 | GW12 | Urban | Planned |  | 130 | 407 |  |  | No
22/02/2019 | 11:55 | EM3 | Urban | Planned |  | 19 | 88 |  |  | No
23/02/2019 | 07:06 | CM25 | Urban | Planned |  | 4 | 354 |  |  | No
23/02/2019 | 07:11 | NP11 | Urban | Planned |  | 58 | 304 |  |  | No
23/02/2019 | 07:57 | KBH35 | Urban | Planned |  | 7 | 251 |  |  | No
23/02/2019 | 08:10 | MGE31 | Urban | Planned |  | 124 | 140 |  |  | No
24/02/2019 | 07:05 | SVW42 | Urban | Planned |  | 8 | 580 |  |  | No
24/02/2019 | 08:00 | DN7 | Urban | Planned |  | 2 | 480 |  |  | No
24/02/2019 | 08:00 | M31 | Urban | Planned |  | 179 | 450 |  |  | No
24/02/2019 | 08:15 | BC22 | Urban | Planned |  | 34 | 375 |  |  | No
24/02/2019 | 08:20 | FTN23 | Urban | Planned |  | 15 | 85 |  |  | No
24/02/2019 | 08:30 | GW12 | Urban | Planned |  | 114 | 346 |  |  | No
24/02/2019 | 08:30 | GW2 | Urban | Planned |  | 163 | 346 |  |  | No
24/02/2019 | 08:35 | NW22 | Urban | Planned |  | 307 | 305 |  |  | No
24/02/2019 | 12:50 | LWN21 | Rural Short | Planned |  | 5 | 92 |  |  | No
25/02/2019 | 08:00 | OE1 | Urban | Planned |  | 27 | 359.4 |  |  | No
25/02/2019 | 08:00 | OE9 | Urban | Planned |  | 1 | 359.4 |  |  | No
25/02/2019 | 08:43 | MC3 | Urban | Planned |  | 63 | 603 |  |  | No
25/02/2019 | 09:00 | LD2 | Urban | Planned |  | 29 | 285 |  |  | No
25/02/2019 | 09:35 | SR13 | Urban | Planned |  | 25 | 265 |  |  | No
26/02/2019 | 08:10 | BR9 | Urban | Planned |  | 30 | 280 |  |  | No
26/02/2019 | 08:24 | BW35 | Urban | Planned |  | 10 | 498 |  |  | No
26/02/2019 | 08:30 | BR1 | Urban | Planned |  | 29 | 420 |  |  | No
26/02/2019 | 08:30 | MTN34 | Urban | Planned |  | 129 | 300 |  |  | No
26/02/2019 | 08:30 | OR35 | Urban | Planned |  | 124 | 210 |  |  | No
26/02/2019 | 08:35 | RD4 | Urban | Planned |  | 82 | 180 |  |  | No
26/02/2019 | 08:42 | LD6 | Urban | Planned |  | 51 | 186 |  |  | No
26/02/2019 | 09:30 | OR33 | Urban | Planned |  | 133 | 195 |  |  | No
26/02/2019 | 09:36 | NW14 | Urban | Planned |  | 110 | 84 |  |  | No
26/02/2019 | 10:20 | OR35 | Urban | Planned |  | 29 | 110 |  |  | No
27/02/2019 | 08:00 | CRM21 | Urban | Planned |  | 159 | 522 |  |  | No
27/02/2019 | 08:00 | M22 | Urban | Planned |  | 68 | 502 |  |  | No
27/02/2019 | 08:02 | DN22 | Urban | Planned |  | 30 | 233 |  |  | No
27/02/2019 | 08:20 | MR24 | Urban | Planned |  | 53 | 95 |  |  | No
27/02/2019 | 08:20 | SR15 | Urban | Planned |  | 72 | 155 |  |  | No
27/02/2019 | 08:30 | EW12 | Urban | Planned |  | 223 | 615 |  |  | No
27/02/2019 | 08:30 | MTN32 | Rural Short | Planned |  | 130 | 415 |  |  | No
27/02/2019 | 09:00 | EL5 | Urban | Planned |  | 88 | 260 |  |  | No
27/02/2019 | 09:30 | OE9 | Urban | Planned |  | 105 | 290 |  |  | No
27/02/2019 | 10:00 | DN11 | Urban | Planned |  | 35 | 345 |  |  | No
27/02/2019 | 22:40 | DC7 | Urban | Planned |  | 7 | 360 |  |  | No
28/02/2019 | 04:00 | CRM14 | Urban | Planned |  | 2 | 270 |  |  | No
28/02/2019 | 08:00 | HGS23 | Rural Short | Planned |  | 4 | 480 |  |  | No
28/02/2019 | 08:01 | MTN31 | Urban | Planned |  | 100 | 558 |  |  | No
28/02/2019 | 08:02 | MTN22 | Rural Short | Planned |  | 107 | 222 |  |  | No
28/02/2019 | 08:04 | DN6 | Urban | Planned |  | 10 | 386 |  |  | No
28/02/2019 | 08:30 | FTN12 | Urban | Planned |  | 205 | 170 |  |  | No
28/02/2019 | 08:52 | MR32 | Urban | Planned |  | 46 | 259 |  |  | No
28/02/2019 | 09:05 | HGS23 | Rural Short | Planned |  | 2 | 167 |  |  | No
28/02/2019 | 09:30 | SS23 | Urban | Planned |  | 45 | 70 |  |  | No
28/02/2019 | 09:41 | BT14 | Urban | Planned |  | 41 | 339 |  |  | No
28/02/2019 | 10:28 | BH21 | Urban | Planned |  | 107 | 87 |  |  | No
01/03/2019 | 07:35 | DC5 | Urban | Planned |  | 29 | 320 |  |  | No
01/03/2019 | 08:00 | MR24 | Urban | Planned |  | 101 | 9 |  |  | No
01/03/2019 | 08:00 | MR33 | Urban | Planned |  | 62 | 9 |  |  | No
01/03/2019 | 08:05 | MTN22 | Rural Short | Planned |  | 35 | 235 |  |  | No
01/03/2019 | 08:23 | OE15 | Urban | Planned |  | 44 | 139 |  |  | No
01/03/2019 | 08:30 | HGS23 | Rural Short | Planned |  | 37 | 125 |  |  | No
01/03/2019 | 09:25 | EW14 | Urban | Planned |  | 11 | 216 |  |  | No
02/03/2019 | 08:00 | KBH31 | Urban | Planned |  | 51 | 75 |  |  | No
02/03/2019 | 08:10 | BW35 | Urban | Planned |  | 37 | 415 |  |  | No
02/03/2019 | 11:39 | SV33 | Urban | Planned |  | 2 | 85 |  |  | No
03/03/2019 | 07:15 | NW32 | Urban | Planned |  | 1 | 30 |  |  | No
03/03/2019 | 07:17 | CDA22 | Urban | Planned |  | 2 | 181 |  |  | No
03/03/2019 | 07:30 | GW7 | Urban | Planned |  | 1 | 540 |  |  | No
03/03/2019 | 07:30 | OE14 | Urban | Planned |  | 44 | 300 |  |  | No
03/03/2019 | 07:30 | OE15 | Urban | Planned |  | 83 | 300 |  |  | No
03/03/2019 | 08:00 | EW12 | Urban | Planned |  | 84 | 301 |  |  | No
03/03/2019 | 08:00 | FTN13 | Urban | Planned |  | 285 | 303 |  |  | No
03/03/2019 | 08:00 | RBD11 | Urban | Planned |  | 42 | 214 |  |  | No
03/03/2019 | 08:10 | MTN23 | Urban | Planned |  | 8 | 455 |  |  | No
03/03/2019 | 08:20 | M22 | Urban | Planned |  | 135 | 188 |  |  | No
03/03/2019 | 08:56 | MTN23 | Urban | Planned |  | 19 | 105 |  |  | No
03/03/2019 | 10:00 | OE15 | Urban | Planned |  | 33 | 145 |  |  | No
03/03/2019 | 11:10 | RWT23 | Urban | Planned |  | 9 | 85 |  |  | No
03/03/2019 | 12:34 | RBD21 | Rural Short | Planned |  | 1 | 25 |  |  | No
03/03/2019 | 12:35 | OE4 | Urban | Planned |  | 16 | 145 |  |  | No
04/03/2019 | 08:05 | MR11 | Urban | Planned |  | 29 | 321 |  |  | No
04/03/2019 | 08:05 | SR24 | Urban | Planned |  | 199 | 321 |  |  | No
04/03/2019 | 08:19 | BR1 | Urban | Planned |  | 122 | 360 |  |  | No
05/03/2019 | 08:32 | MC3 | Urban | Planned |  | 232 | 246 |  |  | No
05/03/2019 | 08:48 | FTN22 | Urban | Planned |  | 9 | 42 |  |  | No
05/03/2019 | 09:00 | MR15 | Urban | Planned |  | 18 | 80 |  |  | No
05/03/2019 | 09:00 | NP16 | Urban | Planned |  | 253 | 310 |  |  | No
05/03/2019 | 09:15 | DC10 | Urban | Planned |  | 32 | 215 |  |  | No
05/03/2019 | 10:32 | STO14 | Rural Short | Planned |  | 119 | 75 |  |  | No
06/03/2019 | 08:00 | FSH31 | Urban | Planned |  | 188 | 260 |  |  | No
06/03/2019 | 08:05 | MTN22 | Rural Short | Planned |  | 4 | 15 |  |  | No
06/03/2019 | 08:05 | NP36 | Urban | Planned |  | 54 | 370 |  |  | No
06/03/2019 | 08:15 | NP16 | Urban | Planned |  | 160 | 230 |  |  | No
06/03/2019 | 08:15 | NP25 | Urban | Planned |  | 2 | 230 |  |  | No
06/03/2019 | 08:30 | DC2 | Urban | Planned |  | 40 | 385 |  |  | No
06/03/2019 | 08:30 | GW2 | Urban | Planned |  | 32 | 450 |  |  | No
06/03/2019 | 08:35 | FSH22 | Urban | Planned |  | 81 | 130 |  |  | No
06/03/2019 | 08:59 | NO7 | Urban | Planned |  | 4 | 191 |  |  | No
06/03/2019 | 09:00 | CM25 | Urban | Planned |  | 25 | 310 |  |  | No
06/03/2019 | 09:30 | SH22 | Urban | Planned |  | 262 | 420 |  |  | No
06/03/2019 | 09:35 | FSH32 | Rural Short | Planned |  | 6 | 140 |  |  | No
06/03/2019 | 09:50 | FSH12 | Rural Short | Planned |  | 11 | 25 |  |  | No
06/03/2019 | 12:10 | FSH21 | Rural Short | Planned |  | 56 | 15 |  |  | No
07/03/2019 | 07:50 | DSH14 | Urban | Planned |  | 1 | 25 |  |  | No
07/03/2019 | 08:00 | GW5 | Urban | Planned |  | 7 | 554.5 |  |  | No
07/03/2019 | 08:20 | NP16 | Urban | Planned |  | 259 | 395 |  |  | No
07/03/2019 | 08:31 | FTN13 | Urban | Planned |  | 20 | 220 |  |  | No
07/03/2019 | 08:36 | NW23 | Urban | Planned |  | 68 | 133 |  |  | No
07/03/2019 | 08:41 | HGS33 | Rural Short | Planned |  | 14 | 203 |  |  | No
07/03/2019 | 08:45 | FTN25 | Urban | Planned |  | 39 | 165 |  |  | No
07/03/2019 | 09:38 | NP34 | Urban | Planned |  | 10 | 430 |  |  | No
07/03/2019 | 10:00 | FSH21 | Rural Short | Planned |  | 3 | 20 |  |  | No
07/03/2019 | 12:00 | LWN33 | Urban | Planned |  | 49 | 110 |  |  | No
07/03/2019 | 22:30 | DVY13 | Urban | Planned |  | 1 | 360 |  |  | No
08/03/2019 | 08:15 | MC3 | Urban | Planned |  | 115 | 360 |  |  | No
08/03/2019 | 08:20 | BR1 | Urban | Planned |  | 54 | 260 |  |  | No
08/03/2019 | 08:24 | BH21 | Urban | Planned |  | 86 | 323 |  |  | No
08/03/2019 | 08:31 | NP33 | Urban | Planned |  | 141 | 284 |  |  | No
08/03/2019 | 08:31 | SS13 | Urban | Planned |  | 106 | 284 |  |  | No
08/03/2019 | 08:37 | MR11 | Urban | Planned |  | 12 | 443 |  |  | No
08/03/2019 | 08:40 | BH22 | Urban | Planned |  | 9 | 290 |  |  | No
08/03/2019 | 08:40 | EB21 | Urban | Planned |  | 134 | 270 |  |  | No
08/03/2019 | 08:40 | FSH21 | Rural Short | Planned |  | 67 | 80 |  |  | No
08/03/2019 | 09:20 | BU13 | Urban | Planned |  | 43 | 200 |  |  | No
08/03/2019 | 10:00 | FTN23 | Urban | Planned |  | 92 | 145 |  |  | No
08/03/2019 | 10:15 | MTN31 | Urban | Planned |  | 38 | 120 |  |  | No
08/03/2019 | 12:00 | HGS33 | Rural Short | Planned |  | 4 | 45 |  |  | No
09/03/2019 | 07:30 | GW4 | Urban | Planned |  | 10 | 210 |  |  | No
09/03/2019 | 11:20 | GW4 | Urban | Planned |  | 19 | 266 |  |  | No
09/03/2019 | 12:30 | OE5 | Urban | Planned |  | 2 | 420 |  |  | No
10/03/2019 | 06:30 | MTN23 | Urban | Planned |  | 1 | 569.5 |  |  | No
10/03/2019 | 08:00 | NO32 | Urban | Planned |  | 46 | 420 |  |  | No
10/03/2019 | 23:00 | GW10 | Urban | Planned |  | 39 | 5 |  |  | No
11/03/2019 | 08:07 | SR15 | Urban | Planned |  | 14 | 630 |  |  | No
12/03/2019 | 08:00 | SS23 | Urban | Planned |  | 265 | 135 |  |  | No
12/03/2019 | 08:30 | NP33 | Urban | Planned |  | 48 | 153 |  |  | No
12/03/2019 | 08:30 | OAK33 | Urban | Planned |  | 121 | 270 |  |  | No
12/03/2019 | 09:00 | RBD12 | Rural Short | Planned |  | 126 | 215 |  |  | No
13/03/2019 | 08:00 | GW11 | Urban | Planned |  | 101 | 340 |  |  | No
13/03/2019 | 08:15 | CRM22 | Urban | Planned |  | 64 | 415 |  |  | No
13/03/2019 | 08:15 | FSH13 | Urban | Planned |  | 55 | 320 |  |  | No
13/03/2019 | 08:15 | FSH33 | Urban | Planned |  | 17 | 320 |  |  | No
13/03/2019 | 08:28 | GW12 | Urban | Planned |  | 135 | 338 |  |  | No
13/03/2019 | 08:30 | BRA21 | Urban | Planned |  | 54 | 175 |  |  | No
13/03/2019 | 08:51 | NO7 | Urban | Planned |  | 41 | 375 |  |  | No
13/03/2019 | 08:51 | OAK33 | Urban | Planned |  | 5 | 375 |  |  | No
13/03/2019 | 09:00 | EW14 | Urban | Planned |  | 135 | 345 |  |  | No
13/03/2019 | 09:00 | MR32 | Urban | Planned |  | 29 | 180 |  |  | No
13/03/2019 | 09:10 | LD2 | Urban | Planned |  | 29 | 200 |  |  | No
13/03/2019 | 09:45 | FTN23 | Urban | Planned |  | 40 | 315 |  |  | No
13/03/2019 | 10:30 | FSH12 | Rural Short | Planned |  | 56 | 255 |  |  | No
13/03/2019 | 13:00 | NP11 | Urban | Planned |  | 11 | 45 |  |  | No
13/03/2019 | 14:25 | EB13 | Urban | Planned |  | 28 | 70 |  |  | No
14/03/2019 | 07:59 | HGS33 | Rural Short | Planned |  | 66 | 309 |  |  | No
14/03/2019 | 08:00 | NP24 | Urban | Planned |  | 28 | 139.9 |  |  | No
14/03/2019 | 08:14 | BU4 | Urban | Planned |  | 67 | 254 |  |  | No
14/03/2019 | 08:30 | M23 | Urban | Planned |  | 333 | 367 |  |  | No
14/03/2019 | 08:30 | MTN35 | Rural Short | Planned |  | 12 | 110 |  |  | No
14/03/2019 | 08:30 | NP24 | Urban | Planned |  | 35 | 240 |  |  | No
14/03/2019 | 08:30 | NP36 | Urban | Planned |  | 78 | 110 |  |  | No
14/03/2019 | 09:15 | BU14 | Urban | Planned |  | 19 | 165 |  |  | No
14/03/2019 | 09:15 | STO14 | Rural Short | Planned |  | 30 | 105 |  |  | No
14/03/2019 | 09:20 | GW7 | Urban | Planned |  | 38 | 168 |  |  | No
14/03/2019 | 09:33 | RBD21 | Rural Short | Planned |  | 3 | 32 |  |  | No
14/03/2019 | 10:15 | MC1 | Urban | Planned |  | 9 | 180 |  |  | No
14/03/2019 | 11:38 | STO13 | Urban | Planned |  | 46 | 102 |  |  | No
14/03/2019 | 12:20 | GW7 | Urban | Planned |  | 56 | 178 |  |  | No
15/03/2019 | 07:43 | FSH21 | Rural Short | Planned |  | 9 | 154 |  |  | No
15/03/2019 | 08:00 | SR11 | Urban | Planned |  | 373 | 345 |  |  | No
15/03/2019 | 08:15 | EM5 | Urban | Planned |  | 49 | 270 |  |  | No
15/03/2019 | 08:18 | NP33 | Urban | Planned |  | 75 | 132 |  |  | No
15/03/2019 | 08:18 | SS13 | Urban | Planned |  | 124 | 132 |  |  | No
15/03/2019 | 08:45 | NP33 | Urban | Planned |  | 54 | 90 |  |  | No
15/03/2019 | 08:55 | EB32 | Urban | Planned |  | 20 | 140 |  |  | No
15/03/2019 | 09:00 | EM5 | Urban | Planned |  | 25 | 240 |  |  | No
15/03/2019 | 09:15 | OR23 | Urban | Planned |  | 65 | 405 |  |  | No
15/03/2019 | 09:25 | MR11 | Urban | Planned |  | 12 | 365.9 |  |  | No
15/03/2019 | 17:00 | BH22 | Urban | Planned |  | 2 | 1,450.0 |  |  | No
16/03/2019 | 07:54 | EB21 | Urban | Planned |  | 106 | 356 |  |  | No
16/03/2019 | 13:10 | FTN23 | Urban | Planned |  | 31 | 202 |  |  | No
17/03/2019 | 06:27 | HT7 | Urban | Planned |  | 39 | 372 |  |  | No
17/03/2019 | 07:02 | OAK22 | Urban | Planned |  | 35 | 276 |  |  | No
17/03/2019 | 07:03 | FTN11 | Urban | Planned |  | 11 | 14 |  |  | No
17/03/2019 | 07:30 | FGY31 | Urban | Planned |  | 25 | 445 |  |  | No
17/03/2019 | 07:30 | SV23 | Urban | Planned |  | 18 | 75 |  |  | No
17/03/2019 | 07:35 | K6 | Urban | Planned |  | 68 | 340 |  |  | No
17/03/2019 | 08:39 | K3 | Urban | Planned |  | 3 | 29 |  |  | No
17/03/2019 | 08:50 | HT3 | Urban | Planned |  | 2 | 270 |  |  | No
17/03/2019 | 08:55 | SR24 | Urban | Planned |  | 47 | 260 |  |  | No
17/03/2019 | 10:30 | K3 | Urban | Planned |  | 3 | 134 |  |  | No
17/03/2019 | 14:30 | OE14 | Urban | Planned |  | 45 | 120 |  |  | No
17/03/2019 | 14:30 | OE15 | Urban | Planned |  | 21 | 120 |  |  | No
18/03/2019 | 07:29 | FSH22 | Urban | Planned |  | 30 | 147 |  |  | No
18/03/2019 | 07:56 | GW5 | Urban | Planned |  | 46 | 355 |  |  | No
18/03/2019 | 07:59 | BR1 | Urban | Planned |  | 64 | 232 |  |  | No
18/03/2019 | 08:10 | FSH21 | Rural Short | Planned |  | 6 | 215 |  |  | No
18/03/2019 | 10:07 | RBD24 | Urban | Planned |  | 2 | 53 |  |  | No
18/03/2019 | 11:00 | FSH12 | Rural Short | Planned |  | 36 | 123 |  |  | No
19/03/2019 | 07:00 | FSH33 | Urban | Planned |  | 175 | 335 |  |  | No
19/03/2019 | 07:23 | EM8 | Urban | Planned |  | 19 | 432 |  |  | No
19/03/2019 | 08:00 | HGS21 | Rural Short | Planned |  | 27 | 455 |  |  | No
19/03/2019 | 08:00 | RBD24 | Urban | Planned |  | 7 | 420 |  |  | No
19/03/2019 | 08:20 | EB22 | Urban | Planned |  | 65 | 310 |  |  | No
19/03/2019 | 08:30 | M22 | Urban | Planned |  | 65 | 410 |  |  | No
19/03/2019 | 08:40 | EM10 | Urban | Planned |  | 58 | 360 |  |  | No
19/03/2019 | 08:55 | EM10 | Urban | Planned |  | 65 | 330 |  |  | No
20/03/2019 | 08:00 | CRM22 | Urban | Planned |  | 31 | 240 |  |  | No
20/03/2019 | 08:00 | FTN14 | Urban | Planned |  | 88 | 230 |  |  | No
20/03/2019 | 08:00 | NP23 | Urban | Planned |  | 44 | 102 |  |  | No
20/03/2019 | 08:03 | FSH12 | Rural Short | Planned |  | 143 | 396 |  |  | No
20/03/2019 | 08:08 | M22 | Urban | Planned |  | 45 | 300 |  |  | No
20/03/2019 | 08:10 | EB32 | Urban | Planned |  | 79 | 290 |  |  | No
20/03/2019 | 08:10 | GW8 | Urban | Planned |  | 33 | 290 |  |  | No
20/03/2019 | 08:42 | SR25 | Urban | Planned |  | 2 | 103 |  |  | No
20/03/2019 | 08:45 | FTN25 | Urban | Planned |  | 17 | 270 |  |  | No
20/03/2019 | 08:51 | CFD14 | Urban | Planned |  | 228 | 9 |  |  | No
20/03/2019 | 09:08 | NP16 | Urban | Planned |  | 198 | 267 |  |  | No
20/03/2019 | 09:15 | BW35 | Urban | Planned |  | 121 | 335 |  |  | No
20/03/2019 | 09:15 | EB22 | Urban | Planned |  | 130 | 315 |  |  | No
20/03/2019 | 09:19 | CFD14 | Urban | Planned |  | 34 | 7 |  |  | No
20/03/2019 | 09:50 | NW13 | Urban | Planned |  | 2 | 245 |  |  | No
20/03/2019 | 21:11 | CFD16 | Urban | Planned |  | 97 | 2 |  |  | No
20/03/2019 | 22:22 | NB33 | Urban | Planned |  | 50 | 5 |  |  | No
21/03/2019 | 07:47 | MTN24 | Rural Short | Planned |  | 29 | 394 |  |  | No
21/03/2019 | 08:05 | SR13 | Urban | Planned |  | 71 | 20 |  |  | No
21/03/2019 | 08:10 | HGS33 | Rural Short | Planned |  | 1 | 3,360.0 |  |  | No
21/03/2019 | 08:15 | EB12 | Urban | Planned |  | 90 | 315 |  |  | No
21/03/2019 | 08:16 | EB32 | Urban | Planned |  | 102 | 187 |  |  | No
21/03/2019 | 08:25 | GW4 | Urban | Planned |  | 56 | 315 |  |  | No
21/03/2019 | 08:30 | LD2 | Urban | Planned |  | 116 | 509.6 |  |  | No
21/03/2019 | 08:40 | BT2 | Urban | Planned |  | 15 | 365 |  |  | No
21/03/2019 | 08:46 | GW4 | Urban | Planned |  | 127 | 338 |  |  | No
21/03/2019 | 09:18 | MGE12 | Urban | Planned |  | 108 | 3 |  |  | No
21/03/2019 | 09:30 | MC6 | Urban | Planned |  | 30 | 440 |  |  | No
21/03/2019 | 10:05 | CM21 | Urban | Planned |  | 2 | 20 |  |  | No
21/03/2019 | 13:00 | GW2 | Urban | Planned |  | 56 | 30 |  |  | No
21/03/2019 | 13:23 | DMA14 | Urban | Planned |  | 99 | 1 |  |  | No
22/03/2019 | 08:00 | CRM22 | Urban | Planned |  | 52 | 360 |  |  | No
22/03/2019 | 08:00 | FTN25 | Urban | Planned |  | 60 | 180 |  |  | No
22/03/2019 | 08:20 | BR10 | Urban | Planned |  | 23 | 190 |  |  | No
22/03/2019 | 08:24 | BR15 | Urban | Planned |  | 36 | 219 |  |  | No
22/03/2019 | 08:24 | BR6 | Urban | Planned |  | 91 | 219 |  |  | No
22/03/2019 | 08:30 | EM5 | Urban | Planned |  | 84 | 425 |  |  | No
22/03/2019 | 08:30 | NW11 | Urban | Planned |  | 77 | 270 |  |  | No
22/03/2019 | 09:00 | EM5 | Urban | Planned |  | 19 | 250 |  |  | No
22/03/2019 | 09:45 | BW21 | Urban | Planned |  | 44 | 135 |  |  | No
22/03/2019 | 09:45 | EM5 | Urban | Planned |  | 24 | 135 |  |  | No
22/03/2019 | 10:24 | DC10 | Urban | Planned |  | 115 | 115 |  |  | No
23/03/2019 | 08:00 | CRM21 | Urban | Planned |  | 504 | 430 |  |  | No
23/03/2019 | 16:26 | CRM21 | Urban | Planned |  | 99 | 125 |  |  | No
24/03/2019 | 07:10 | MGE13 | Urban | Planned |  | 22 | 505 |  |  | No
24/03/2019 | 07:30 | HGS32 | Urban | Planned |  | 1 | 210 |  |  | No
24/03/2019 | 07:45 | DSH34 | Urban | Planned |  | 79 | 420 |  |  | No
24/03/2019 | 08:00 | MTN21 | Urban | Planned |  | 216 | 420 |  |  | No
24/03/2019 | 08:05 | RD4 | Urban | Planned |  | 196 | 495 |  |  | No
24/03/2019 | 08:10 | MGE32 | Urban | Planned |  | 49 | 565 |  |  | No
25/03/2019 | 08:20 | NP33 | Urban | Planned |  | 36 | 180 |  |  | No
25/03/2019 | 08:30 | FTN12 | Urban | Planned |  | 11 | 180 |  |  | No
25/03/2019 | 08:44 | NW33 | Urban | Planned |  | 36 | 215 |  |  | No
26/03/2019 | 08:20 | BR1 | Urban | Planned |  | 68 | 270 |  |  | No
26/03/2019 | 08:21 | M25 | Urban | Planned |  | 209 | 479 |  |  | No
26/03/2019 | 08:25 | NP25 | Urban | Planned |  | 55 | 190 |  |  | No
26/03/2019 | 08:30 | EL13 | Urban | Planned |  | 4 | 370 |  |  | No
26/03/2019 | 08:30 | MGE31 | Urban | Planned |  | 84 | 345 |  |  | No
26/03/2019 | 08:50 | STO23 | Urban | Planned |  | 50 | 185 |  |  | No
26/03/2019 | 09:11 | SR13 | Urban | Planned |  | 50 | 316 |  |  | No
26/03/2019 | 10:30 | CRM33 | Urban | Planned |  | 31 | 180 |  |  | No
26/03/2019 | 13:30 | SR20 | Urban | Planned |  | 4 | 65 |  |  | No
27/03/2019 | 08:00 | LD1 | Urban | Planned |  | 120 | 440 |  |  | No
27/03/2019 | 08:15 | NP36 | Urban | Planned |  | 4 | 415 |  |  | No
27/03/2019 | 08:29 | RD10 | Urban | Planned |  | 64 | 296 |  |  | No
27/03/2019 | 08:35 | RBD21 | Rural Short | Planned |  | 19 | 275 |  |  | No
27/03/2019 | 08:40 | CFD14 | Urban | Planned |  | 84 | 245 |  |  | No
27/03/2019 | 09:15 | MR14 | Urban | Planned |  | 87 | 325 |  |  | No
27/03/2019 | 09:30 | HGS21 | Rural Short | Planned |  | 49 | 135 |  |  | No
27/03/2019 | 10:05 | OAK26 | Urban | Planned |  | 3 | 210 |  |  | No
27/03/2019 | 11:05 | FTN14 | Urban | Planned |  | 20 | 115 |  |  | No
28/03/2019 | 05:30 | DSH24 | Urban | Planned |  | 2 | 15 |  |  | No
28/03/2019 | 07:57 | SR11 | Urban | Planned |  | 287 | 343 |  |  | No
28/03/2019 | 08:00 | K12 | Urban | Planned |  | 27 | 525 |  |  | No
28/03/2019 | 08:00 | LD5 | Urban | Planned |  | 65 | 450 |  |  | No
28/03/2019 | 08:00 | LD7 | Urban | Planned |  | 223 | 450 |  |  | No
28/03/2019 | 08:05 | CRM22 | Urban | Planned |  | 63 | 470 |  |  | No
28/03/2019 | 08:05 | EM5 | Urban | Planned |  | 35 | 220 |  |  | No
28/03/2019 | 08:05 | EM9 | Urban | Planned |  | 46 | 390 |  |  | No
28/03/2019 | 08:10 | NP34 | Urban | Planned |  | 42 | 110 |  |  | No
28/03/2019 | 08:16 | BW21 | Urban | Planned |  | 9 | 91 |  |  | No
28/03/2019 | 08:20 | BU14 | Urban | Planned |  | 45 | 174 |  |  | No
28/03/2019 | 08:33 | FSH21 | Rural Short | Planned |  | 38 | 417 |  |  | No
28/03/2019 | 08:40 | MC6 | Urban | Planned |  | 30 | 365 |  |  | No
28/03/2019 | 08:50 | HGS21 | Rural Short | Planned |  | 20 | 280 |  |  | No
28/03/2019 | 08:50 | HGS31 | Rural Short | Planned |  | 31 | 280 |  |  | No
28/03/2019 | 08:59 | OE2 | Urban | Planned |  | 8 | 389 |  |  | No
28/03/2019 | 08:59 | OE9 | Urban | Planned |  | 23 | 389 |  |  | No
28/03/2019 | 09:10 | RWT24 | Urban | Planned |  | 7 | 260 |  |  | No
28/03/2019 | 11:18 | CFD14 | Urban | Planned |  | 1 | 1 |  |  | No
29/03/2019 | 08:00 | MC3 | Urban | Planned |  | 18 | 314.5 |  |  | No
29/03/2019 | 08:01 | NB35 | Urban | Planned |  | 51 | 384 |  |  | No
29/03/2019 | 08:03 | BT6 | Urban | Planned |  | 47 | 161 |  |  | No
29/03/2019 | 08:11 | GW3 | Urban | Planned |  | 79 | 342 |  |  | No
29/03/2019 | 08:15 | CRM14 | Urban | Planned |  | 112 | 401 |  |  | No
29/03/2019 | 08:15 | MC3 | Urban | Planned |  | 26 | 160 |  |  | No
29/03/2019 | 08:23 | RWT23 | Urban | Planned |  | 23 | 246 |  |  | No
29/03/2019 | 08:30 | CM25 | Urban | Planned |  | 64 | 250 |  |  | No
29/03/2019 | 09:00 | GW4 | Urban | Planned |  | 81 | 270 |  |  | No
29/03/2019 | 09:25 | KBH34 | Urban | Planned |  | 181 | 485 |  |  | No
30/03/2019 | 07:32 | CRM34 | Urban | Planned |  | 46 | 523 |  |  | No
30/03/2019 | 08:25 | NO6 | Urban | Planned |  | 58 | 360 |  |  | No
30/03/2019 | 09:25 | MR13 | Urban | Planned |  | 23 | 96 |  |  | No
30/03/2019 | 09:25 | MR21 | Urban | Planned |  | 79 | 96 |  |  | No
30/03/2019 | 09:30 | GW4 | Urban | Planned |  | 104 | 405 |  |  | No
30/03/2019 | 11:55 | CM25 | Urban | Planned |  | 69 | 223 |  |  | No
31/03/2019 | 08:10 | CM15 | Urban | Planned |  | 3 | 350 |  |  | No
31/03/2019 | 08:31 | MR31 | Urban | Planned |  | 211 | 520 |  |  | No
31/03/2019 | 08:35 | FTN14 | Urban | Planned |  | 22 | 465 |  |  | No
31/03/2019 | 08:51 | EM5 | Urban | Planned |  | 45 | 418 |  |  | No
01/04/2019 | 07:30 | DC1 | Urban | Planned |  | 34 | 560 |  |  | No
01/04/2019 | 07:30 | DC2 | Urban | Planned |  | 18 | 560 |  |  | No
01/04/2019 | 08:00 | RD4 | Urban | Planned |  | 2 | 329.8 |  |  | No
01/04/2019 | 08:50 | MGE31 | Urban | Planned |  | 44 | 220 |  |  | No
01/04/2019 | 09:45 | BR15 | Urban | Planned |  | 54 | 375 |  |  | No
02/04/2019 | 08:10 | MC2 | Urban | Planned |  | 19 | 180 |  |  | No
02/04/2019 | 08:25 | BR6 | Urban | Planned |  | 20 | 240 |  |  | No
02/04/2019 | 08:25 | MGE23 | Urban | Planned |  | 37 | 210 |  |  | No
02/04/2019 | 08:30 | EB32 | Urban | Planned |  | 40 | 240 |  |  | No
02/04/2019 | 08:30 | LWN23 | Urban | Planned |  | 130 | 185 |  |  | No
02/04/2019 | 08:35 | CM25 | Urban | Planned |  | 24 | 400 |  |  | No
02/04/2019 | 08:35 | FSH13 | Urban | Planned |  | 112 | 360 |  |  | No
02/04/2019 | 08:45 | EB32 | Urban | Planned |  | 102 | 155 |  |  | No
02/04/2019 | 08:45 | EM5 | Urban | Planned |  | 145 | 355 |  |  | No
02/04/2019 | 08:50 | EM5 | Urban | Planned |  | 30 | 350 |  |  | No
02/04/2019 | 08:50 | EM8 | Urban | Planned |  | 69 | 350 |  |  | No
02/04/2019 | 10:00 | BR1 | Urban | Planned |  | 55 | 220 |  |  | No
02/04/2019 | 10:00 | STO22 | Urban | Planned |  | 4 | 660 |  |  | No
02/04/2019 | 10:50 | K7 | Urban | Planned |  | 322 | 235 |  |  | No
02/04/2019 | 10:55 | SH22 | Urban | Planned |  | 252 | 380 |  |  | No
02/04/2019 | 11:38 | K6 | Urban | Planned |  | 186 | 203 |  |  | No
02/04/2019 | 11:50 | HT11 | Urban | Planned |  | 190 | 170 |  |  | No
02/04/2019 | 19:00 | CFD26 | Urban | Planned |  | 1 | 720 |  |  | No
03/04/2019 | 08:00 | MC2 | Urban | Planned |  | 91 | 210 |  |  | No
03/04/2019 | 08:00 | NW11 | Urban | Planned |  | 73 | 555 |  |  | No
03/04/2019 | 08:07 | RD4 | Urban | Planned |  | 72 | 426 |  |  | No
03/04/2019 | 08:08 | HGS23 | Rural Short | Planned |  | 265 | 502.4 |  |  | No
03/04/2019 | 08:10 | KBH35 | Urban | Planned |  | 63 | 465 |  |  | No
03/04/2019 | 08:30 | K13 | Urban | Planned |  | 130 | 420 |  |  | No
03/04/2019 | 08:30 | MR12 | Urban | Planned |  | 67 | 175 |  |  | No
03/04/2019 | 08:35 | EB12 | Urban | Planned |  | 25 | 370 |  |  | No
03/04/2019 | 08:35 | LWN24 | Urban | Planned |  | 107 | 325 |  |  | No
03/04/2019 | 08:52 | K6 | Urban | Planned |  | 15 | 117 |  |  | No
03/04/2019 | 08:52 | K7 | Urban | Planned |  | 71 | 117 |  |  | No
03/04/2019 | 09:20 | RBD23 | Urban | Planned |  | 22 | 75 |  |  | No
03/04/2019 | 09:59 | CFD14 | Urban | Planned |  | 35 | 287 |  |  | No
03/04/2019 | 11:45 | CFD14 | Urban | Planned |  | 69 | 297 |  |  | No
04/04/2019 | 07:54 | MTN24 | Rural Short | Planned |  | 29 | 578 |  |  | No
04/04/2019 | 08:03 | MC2 | Urban | Planned |  | 35 | 332 |  |  | No
04/04/2019 | 08:23 | CFD22 | Urban | Planned |  | 17 | 305 |  |  | No
04/04/2019 | 08:23 | CFD23 | Urban | Planned |  | 2 | 305 |  |  | No
04/04/2019 | 08:28 | LWN35 | Urban | Planned |  | 37 | 137 |  |  | No
04/04/2019 | 08:30 | EM5 | Urban | Planned |  | 54 | 180 |  |  | No
04/04/2019 | 08:30 | GW7 | Urban | Planned |  | 69 | 240 |  |  | No
04/04/2019 | 08:31 | LWN35 | Urban | Planned |  | 68 | 124 |  |  | No
04/04/2019 | 08:32 | SS13 | Urban | Planned |  | 60 | 291 |  |  | No
04/04/2019 | 08:33 | EB12 | Urban | Planned |  | 64 | 220 |  |  | No
04/04/2019 | 08:45 | FTN25 | Urban | Planned |  | 104 | 280 |  |  | No
04/04/2019 | 09:15 | NP16 | Urban | Planned |  | 51 | 135 |  |  | No
04/04/2019 | 10:30 | EW1 | Urban | Planned |  | 68 | 67 |  |  | No
04/04/2019 | 11:33 | SS23 | Urban | Planned |  | 25 | 202 |  |  | No
04/04/2019 | 17:10 | DSH33 | Urban | Planned |  | 1 | 110 |  |  | No
05/04/2019 | 08:05 | KBH32 | Urban | Planned |  | 78 | 135 |  |  | No
05/04/2019 | 08:05 | MR24 | Urban | Planned |  | 100 | 337 |  |  | No
05/04/2019 | 08:05 | MR33 | Urban | Planned |  | 62 | 337 |  |  | No
05/04/2019 | 08:10 | GW5 | Urban | Planned |  | 48 | 170 |  |  | No
05/04/2019 | 08:25 | LWN35 | Urban | Planned |  | 30 | 220 |  |  | No
05/04/2019 | 08:30 | LWN24 | Urban | Planned |  | 46 | 150 |  |  | No
05/04/2019 | 08:30 | LWN35 | Urban | Planned |  | 66 | 150 |  |  | No
05/04/2019 | 08:40 | GW5 | Urban | Planned |  | 155 | 155 |  |  | No
05/04/2019 | 08:42 | GW5 | Urban | Planned |  | 22 | 78 |  |  | No
05/04/2019 | 08:55 | OE2 | Urban | Planned |  | 132 | 320 |  |  | No
05/04/2019 | 09:00 | NP25 | Urban | Planned |  | 215 | 199 |  |  | No
05/04/2019 | 09:00 | NP36 | Urban | Planned |  | 68 | 199 |  |  | No
05/04/2019 | 09:05 | EM6 | Urban | Planned |  | 45 | 430 |  |  | No
05/04/2019 | 09:45 | DC1 | Urban | Planned |  | 29 | 262 |  |  | No
05/04/2019 | 10:30 | GW5 | Urban | Planned |  | 63 | 175 |  |  | No
06/04/2019 | 08:00 | SV31 | Urban | Planned |  | 58 | 555 |  |  | No
06/04/2019 | 08:46 | OE1 | Urban | Planned |  | 12 | 231 |  |  | No
06/04/2019 | 13:49 | OE9 | Urban | Planned |  | 62 | 40 |  |  | No
07/04/2019 | 07:00 | EL10 | Urban | Planned |  | 1 | 480 |  |  | No
07/04/2019 | 07:06 | MGE21 | Urban | Planned |  | 28 | 413 |  |  | No
07/04/2019 | 08:00 | OAK32 | Urban | Planned |  | 15 | 461 |  |  | No
07/04/2019 | 08:00 | BC23 | Urban | Planned |  | 28 | 509.8 |  |  | No
07/04/2019 | 08:20 | FTN23 | Urban | Planned |  | 9 | 80 |  |  | No
07/04/2019 | 09:50 | SS14 | Urban | Planned |  | 14 | 205 |  |  | No
08/04/2019 | 08:34 | NP33 | Urban | Planned |  | 19 | 114 |  |  | No
08/04/2019 | 08:47 | M31 | Urban | Planned |  | 86 | 422 |  |  | No
08/04/2019 | 10:30 | K2 | Urban | Planned |  | 45 | 266 |  |  | No
08/04/2019 | 11:01 | K6 | Urban | Planned |  | 15 | 228 |  |  | No
09/04/2019 | 08:00 | CRM22 | Urban | Planned |  | 50 | 360 |  |  | No
09/04/2019 | 08:10 | MC3 | Urban | Planned |  | 79 | 330 |  |  | No
09/04/2019 | 08:22 | LWN35 | Urban | Planned |  | 31 | 351 |  |  | No
09/04/2019 | 08:25 | LWN21 | Rural Short | Planned |  | 91 | 401 |  |  | No
09/04/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 2 | 45 |  |  | No
09/04/2019 | 08:30 | EB32 | Urban | Planned |  | 39 | 145 |  |  | No
09/04/2019 | 08:34 | BRA21 | Urban | Planned |  | 163 | 456 |  |  | No
09/04/2019 | 08:45 | EM10 | Urban | Planned |  | 114 | 110 |  |  | No
10/04/2019 | 09:16 | HGS21 | Rural Short | Planned |  | 2 | 232 |  |  | No
11/04/2019 | 08:00 | SVW41 | Urban | Planned |  | 91 | 480 |  |  | No
11/04/2019 | 08:25 | M35 | Urban | Planned |  | 123 | 345 |  |  | No
11/04/2019 | 08:30 | FSH12 | Rural Short | Planned |  | 15 | 325 |  |  | No
11/04/2019 | 08:30 | FSH21 | Rural Short | Planned |  | 38 | 405 |  |  | No
11/04/2019 | 08:50 | EL5 | Urban | Planned |  | 12 | 385 |  |  | No
11/04/2019 | 09:00 | LWN35 | Urban | Planned |  | 26 | 90 |  |  | No
11/04/2019 | 09:05 | MC3 | Urban | Planned |  | 15 | 130 |  |  | No
11/04/2019 | 09:30 | MR33 | Urban | Planned |  | 4 | 330 |  |  | No
12/04/2019 | 08:05 | DC10 | Urban | Planned |  | 88 | 502 |  |  | No
12/04/2019 | 08:30 | FSH13 | Urban | Planned |  | 99 | 283 |  |  | No
12/04/2019 | 08:30 | FSH13 | Urban | Planned |  | 31 | 390 |  |  | No
12/04/2019 | 09:00 | DC10 | Urban | Planned |  | 47 | 325 |  |  | No
12/04/2019 | 09:20 | GW4 | Urban | Planned |  | 132 | 270 |  |  | No
12/04/2019 | 09:29 | CRM22 | Urban | Planned |  | 63 | 394 |  |  | No
13/04/2019 | 08:00 | DVY34 | Urban | Planned |  | 1 | 390 |  |  | No
13/04/2019 | 08:15 | OE2 | Urban | Planned |  | 73 | 432 |  |  | No
13/04/2019 | 08:30 | FSH32 | Rural Short | Planned |  | 35 | 465 |  |  | No
13/04/2019 | 08:58 | HT2 | Urban | Planned |  | 4 | 228 |  |  | No
13/04/2019 | 08:58 | HT7 | Urban | Planned |  | 73 | 228 |  |  | No
14/04/2019 | 06:00 | FTN11 | Urban | Planned |  | 15 | 575 |  |  | No
14/04/2019 | 06:00 | FTN11 | Urban | Planned |  | 90 | 74.6 |  |  | No
14/04/2019 | 07:02 | OE9 | Urban | Planned |  | 41 | 397 |  |  | No
14/04/2019 | 08:00 | KBH34 | Urban | Planned |  | 2 | 520 |  |  | No
14/04/2019 | 08:00 | K12 | Urban | Planned |  | 19 | 575 |  |  | No
14/04/2019 | 08:10 | KBH32 | Urban | Planned |  | 12 | 170 |  |  | No
14/04/2019 | 08:10 | NP34 | Urban | Planned |  | 181 | 295 |  |  | No
14/04/2019 | 09:00 | LD2 | Urban | Planned |  | 1 | 360 |  |  | No
14/04/2019 | 09:10 | FTN14 | Urban | Planned |  | 7 | 380 |  |  | No
14/04/2019 | 10:20 | EM5 | Urban | Planned |  | 40 | 185 |  |  | No
15/04/2019 | 07:00 | EW1 | Urban | Planned |  | 15 | 155 |  |  | No
15/04/2019 | 08:45 | EW8 | Urban | Planned |  | 71 | 295 |  |  | No
15/04/2019 | 08:45 | EW9 | Urban | Planned |  | 17 | 295 |  |  | No
16/04/2019 | 07:50 | HGS23 | Rural Short | Planned |  | 1 | 525 |  |  | No
16/04/2019 | 08:10 | GW8 | Urban | Planned |  | 14 | 65 |  |  | No
16/04/2019 | 08:10 | K13 | Urban | Planned |  | 21 | 515 |  |  | No
16/04/2019 | 08:31 | DMA23 | Rural Short | Planned |  | 2 | 363 |  |  | No
16/04/2019 | 08:40 | FSH13 | Urban | Planned |  | 19 | 80 |  |  | No
16/04/2019 | 08:50 | GW8 | Urban | Planned |  | 30 | 160 |  |  | No
16/04/2019 | 09:03 | CRM22 | Urban | Planned |  | 43 | 470 |  |  | No
16/04/2019 | 09:07 | CRM21 | Urban | Planned |  | 3 | 219 |  |  | No
16/04/2019 | 09:07 | DVY24 | Rural Short | Planned |  | 10 | 219 |  |  | No
17/04/2019 | 05:50 | DVY23 | Urban | Planned |  | 5 | 25 |  |  | No
17/04/2019 | 08:00 | NP23 | Urban | Planned |  | 47 | 555 |  |  | No
17/04/2019 | 08:00 | NP33 | Urban | Planned |  | 132 | 555 |  |  | No
17/04/2019 | 08:10 | EB22 | Urban | Planned |  | 60 | 385 |  |  | No
17/04/2019 | 08:12 | BT5 | Urban | Planned |  | 56 | 258 |  |  | No
17/04/2019 | 08:15 | EB11 | Urban | Planned |  | 1 | 420 |  |  | No
17/04/2019 | 08:30 | CRM22 | Urban | Planned |  | 2 | 315 |  |  | No
17/04/2019 | 08:37 | NP14 | Urban | Planned |  | 105 | 229 |  |  | No
17/04/2019 | 08:54 | LD33 | Urban | Planned |  | 220 | 38 |  |  | No
17/04/2019 | 08:55 | EL6 | Urban | Planned |  | 130 | 480 |  |  | No
17/04/2019 | 08:58 | AR12 | Urban | Planned |  | 42 | 212 |  |  | No
17/04/2019 | 09:10 | RBD22 | Urban | Planned |  | 60 | 325 |  |  | No
17/04/2019 | 10:09 | HT11 | Urban | Planned |  | 27 | 319 |  |  | No
17/04/2019 | 10:09 | M11 | Urban | Planned |  | 195 | 319 |  |  | No
18/04/2019 | 08:00 | OE14 | Urban | Planned |  | 43 | 85 |  |  | No
18/04/2019 | 08:00 | NB22 | Urban | Planned |  | 11 | 479.9 |  |  | No
18/04/2019 | 08:11 | NP25 | Urban | Planned |  | 124 | 437 |  |  | No
18/04/2019 | 08:15 | HGS23 | Rural Short | Planned |  | 2 | 45 |  |  | No
18/04/2019 | 08:20 | RWT35 | Urban | Planned |  | 60 | 380 |  |  | No
18/04/2019 | 08:30 | NP25 | Urban | Planned |  | 214 | 369 |  |  | No
18/04/2019 | 08:30 | EM10 | Urban | Planned |  | 65 | 169.5 |  |  | No
18/04/2019 | 08:31 | K7 | Urban | Planned |  | 344 | 120 |  |  | No
18/04/2019 | 08:32 | FTN24 | Urban | Planned |  | 152 | 403 |  |  | No
18/04/2019 | 08:46 | EM5 | Urban | Planned |  | 19 | 109 |  |  | No
18/04/2019 | 09:00 | HT2 | Urban | Planned |  | 24 | 210 |  |  | No
18/04/2019 | 09:30 | OE4 | Urban | Planned |  | 69 | 258 |  |  | No
18/04/2019 | 09:55 | MTN32 | Rural Short | Planned |  | 1 | 45 |  |  | No
18/04/2019 | 13:15 | DMA15 | Rural Short | Planned |  | 7 | 25 |  |  | No
23/04/2019 | 08:07 | BH11 | Urban | Planned |  | 232 | 421 |  |  | No
24/04/2019 | 08:35 | DC10 | Urban | Planned |  | 48 | 108 |  |  | No
24/04/2019 | 09:00 | RWT24 | Urban | Planned |  | 30 | 195 |  |  | No
24/04/2019 | 10:42 | DC5 | Urban | Planned |  | 85 | 134 |  |  | No
26/04/2019 | 08:40 | MR32 | Urban | Planned |  | 30 | 365 |  |  | No
27/04/2019 | 07:56 | DVY34 | Urban | Planned |  | 3 | 156 |  |  | No
27/04/2019 | 08:19 | OAK22 | Urban | Planned |  | 21 | 376 |  |  | No
28/04/2019 | 07:40 | EB22 | Urban | Planned |  | 60 | 380 |  |  | No
28/04/2019 | 07:52 | SS14 | Urban | Planned |  | 2 | 702 |  |  | No
28/04/2019 | 08:30 | FTN21 | Urban | Planned |  | 10 | 465 |  |  | No
28/04/2019 | 09:24 | DSH34 | Urban | Planned |  | 6 | 209 |  |  | No
29/04/2019 | 08:20 | NW31 | Urban | Planned |  | 27 | 305 |  |  | No
29/04/2019 | 08:31 | MTN22 | Rural Short | Planned |  | 1 | 59 |  |  | No
29/04/2019 | 09:03 | NB22 | Urban | Planned |  | 50 | 268 |  |  | No
29/04/2019 | 09:03 | NB34 | Urban | Planned |  | 30 | 268 |  |  | No
30/04/2019 | 08:15 | KBH35 | Urban | Planned |  | 70 | 370 |  |  | No
30/04/2019 | 08:20 | EM9 | Urban | Planned |  | 19 | 355 |  |  | No
30/04/2019 | 08:31 | LD2 | Urban | Planned |  | 103 | 250 |  |  | No
30/04/2019 | 08:35 | GW11 | Urban | Planned |  | 23 | 145 |  |  | No
30/04/2019 | 08:40 | HGS33 | Rural Short | Planned |  | 8 | 463 |  |  | No
30/04/2019 | 08:45 | OR33 | Urban | Planned |  | 254 | 285 |  |  | No
30/04/2019 | 09:00 | NP33 | Urban | Planned |  | 57 | 497 |  |  | No
30/04/2019 | 09:47 | MTN24 | Rural Short | Planned |  | 2 | 109 |  |  | No
30/04/2019 | 10:50 | GW12 | Urban | Planned |  | 99 | 145 |  |  | No
30/04/2019 | 10:50 | GW7 | Urban | Planned |  | 79 | 145 |  |  | No
01/05/2019 | 08:00 | KBH34 | Urban | Planned |  | 61 | 260 |  |  | No
01/05/2019 | 08:00 | MGE31 | Urban | Planned |  | 2 | 4,830.0 |  |  | No
01/05/2019 | 08:00 | OAK26 | Urban | Planned |  | 52 | 256.7 |  |  | No
01/05/2019 | 08:10 | EM9 | Urban | Planned |  | 46 | 160 |  |  | No
01/05/2019 | 08:24 | LWN35 | Urban | Planned |  | 50 | 356 |  |  | No
01/05/2019 | 08:30 | MGE23 | Urban | Planned |  | 46 | 480 |  |  | No
01/05/2019 | 08:41 | MR31 | Urban | Planned |  | 67 | 159 |  |  | No
01/05/2019 | 09:37 | MC3 | Urban | Planned |  | 30 | 222 |  |  | No
01/05/2019 | 09:45 | GW3 | Urban | Planned |  | 137 | 175 |  |  | No
01/05/2019 | 10:00 | OR23 | Urban | Planned |  | 65 | 275 |  |  | No
01/05/2019 | 13:00 | GW3 | Urban | Planned |  | 32 | 120 |  |  | No
02/05/2019 | 07:36 | DN11 | Urban | Planned |  | 154 | 464 |  |  | No
02/05/2019 | 08:00 | NB35 | Urban | Planned |  | 55 | 500 |  |  | No
02/05/2019 | 08:15 | GW11 | Urban | Planned |  | 65 | 120 |  |  | No
02/05/2019 | 08:15 | NP16 | Urban | Planned |  | 109 | 335 |  |  | No
02/05/2019 | 08:15 | RD4 | Urban | Planned |  | 142 | 385 |  |  | No
02/05/2019 | 08:20 | OE2 | Urban | Planned |  | 131 | 80 |  |  | No
02/05/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 8 | 100 |  |  | No
02/05/2019 | 09:00 | MC3 | Urban | Planned |  | 22 | 185 |  |  | No
02/05/2019 | 09:13 | DN11 | Urban | Planned |  | 258 | 224 |  |  | No
02/05/2019 | 09:13 | MR32 | Urban | Planned |  | 42 | 224 |  |  | No
02/05/2019 | 09:29 | K2 | Urban | Planned |  | 197 | 252 |  |  | No
02/05/2019 | 09:35 | LWN21 | Rural Short | Planned |  | 35 | 175 |  |  | No
02/05/2019 | 09:35 | LWN32 | Rural Short | Planned |  | 34 | 175 |  |  | No
02/05/2019 | 09:37 | HGS33 | Rural Short | Planned |  | 8 | 181 |  |  | No
02/05/2019 | 10:00 | EW14 | Urban | Planned |  | 136 | 300 |  |  | No
03/05/2019 | 08:00 | K4 | Urban | Planned |  | 222 | 480 |  |  | No
03/05/2019 | 08:00 | NW23 | Urban | Planned |  | 124 | 510 |  |  | No
03/05/2019 | 08:05 | FTN13 | Urban | Planned |  | 48 | 305 |  |  | No
03/05/2019 | 08:10 | EM8 | Urban | Planned |  | 18 | 285 |  |  | No
03/05/2019 | 08:10 | FSH13 | Urban | Planned |  | 112 | 200 |  |  | No
03/05/2019 | 08:10 | MR12 | Urban | Planned |  | 62 | 245 |  |  | No
03/05/2019 | 09:44 | GW2 | Urban | Planned |  | 10 | 346 |  |  | No
03/05/2019 | 10:10 | OR33 | Urban | Planned |  | 211 | 175 |  |  | No
04/05/2019 | 10:45 | OAK32 | Urban | Planned |  | 30 | 45 |  |  | No
04/05/2019 | 12:30 | OE10 | Urban | Planned |  | 3 | 75 |  |  | No
05/05/2019 | 06:42 | DC1 | Urban | Planned |  | 2 | 11 |  |  | No
05/05/2019 | 07:30 | FTN14 | Urban | Planned |  | 22 | 450 |  |  | No
05/05/2019 | 07:30 | DN21 | Urban | Planned |  | 4 | 15 |  |  | No
05/05/2019 | 08:02 | BH23 | Urban | Planned |  | 70 | 576 |  |  | No
05/05/2019 | 08:02 | DC5 | Urban | Planned |  | 20 | 576 |  |  | No
05/05/2019 | 08:30 | DVY14 | Urban | Planned |  | 7 | 400 |  |  | No
05/05/2019 | 08:45 | DVY34 | Urban | Planned |  | 16 | 70 |  |  | No
05/05/2019 | 09:04 | DSH32 | Urban | Planned |  | 1 | 11 |  |  | No
05/05/2019 | 09:18 | DN8 | Urban | Planned |  | 25 | 246 |  |  | No
05/05/2019 | 10:20 | DVY34 | Urban | Planned |  | 20 | 50 |  |  | No
05/05/2019 | 10:20 | MGE13 | Urban | Planned |  | 2 | 40 |  |  | No
05/05/2019 | 10:30 | LWN21 | Rural Short | Planned |  | 14 | 44.9 |  |  | No
05/05/2019 | 11:55 | DVY34 | Urban | Planned |  | 1 | 90 |  |  | No
05/05/2019 | 12:50 | STO14 | Rural Short | Planned |  | 4 | 10 |  |  | No
06/05/2019 | 08:10 | MTN32 | Rural Short | Planned |  | 61 | 275 |  |  | No
06/05/2019 | 08:20 | M33 | Urban | Planned |  | 54 | 220 |  |  | No
06/05/2019 | 08:45 | NB31 | Urban | Planned |  | 4 | 120 |  |  | No
06/05/2019 | 14:10 | FSH33 | Urban | Planned |  | 12 | 110 |  |  | No
07/05/2019 | 08:00 | NP16 | Urban | Planned |  | 6 | 220 |  |  | No
07/05/2019 | 08:10 | EM5 | Urban | Planned |  | 84 | 205 |  |  | No
07/05/2019 | 08:10 | GW7 | Urban | Planned |  | 165 | 627 |  |  | No
07/05/2019 | 08:10 | MGE23 | Urban | Planned |  | 29 | 627 |  |  | No
07/05/2019 | 08:30 | SR13 | Urban | Planned |  | 26 | 160 |  |  | No
07/05/2019 | 08:31 | FTN25 | Urban | Planned |  | 41 | 161 |  |  | No
07/05/2019 | 09:40 | MC6 | Urban | Planned |  | 27 | 421 |  |  | No
08/05/2019 | 08:00 | CRM14 | Urban | Planned |  | 28 | 233 |  |  | No
08/05/2019 | 08:00 | CRM22 | Urban | Planned |  | 155 | 125 |  |  | No
08/05/2019 | 08:05 | DN22 | Urban | Planned |  | 57 | 550 |  |  | No
08/05/2019 | 08:20 | NP12 | Urban | Planned |  | 32 | 325 |  |  | No
08/05/2019 | 08:22 | EB32 | Urban | Planned |  | 23 | 244 |  |  | No
08/05/2019 | 08:31 | EB11 | Urban | Planned |  | 99 | 265 |  |  | No
08/05/2019 | 08:35 | LWN35 | Urban | Planned |  | 48 | 330 |  |  | No
08/05/2019 | 08:38 | EM1 | Urban | Planned |  | 112 | 127 |  |  | No
08/05/2019 | 08:45 | FTN24 | Urban | Planned |  | 40 | 95 |  |  | No
08/05/2019 | 08:46 | MC3 | Urban | Planned |  | 79 | 274 |  |  | No
08/05/2019 | 09:00 | FTN13 | Urban | Planned |  | 12 | 210 |  |  | No
08/05/2019 | 09:00 | FTN25 | Urban | Planned |  | 12 | 210 |  |  | No
08/05/2019 | 09:25 | GW11 | Urban | Planned |  | 57 | 189 |  |  | No
08/05/2019 | 09:30 | DN13 | Urban | Planned |  | 75 | 235 |  |  | No
08/05/2019 | 11:30 | CRM22 | Urban | Planned |  | 62 | 80 |  |  | No
09/05/2019 | 08:00 | LWN21 | Rural Short | Planned |  | 1 | 629.4 |  |  | No
09/05/2019 | 08:10 | DVY11 | Urban | Planned |  | 1 | 130 |  |  | No
09/05/2019 | 08:18 | RWT35 | Urban | Planned |  | 60 | 430 |  |  | No
09/05/2019 | 08:25 | SR15 | Urban | Planned |  | 53 | 285 |  |  | No
09/05/2019 | 08:31 | MR21 | Urban | Planned |  | 145 | 578 |  |  | No
09/05/2019 | 08:43 | EM1 | Urban | Planned |  | 171 | 185 |  |  | No
09/05/2019 | 09:08 | LWN21 | Rural Short | Planned |  | 152 | 389 |  |  | No
09/05/2019 | 09:10 | EB32 | Urban | Planned |  | 72 | 300 |  |  | No
09/05/2019 | 09:30 | GW3 | Urban | Planned |  | 48 | 300 |  |  | No
09/05/2019 | 10:35 | HGS21 | Rural Short | Planned |  | 10 | 15 |  |  | No
10/05/2019 | 08:22 | FSH12 | Rural Short | Planned |  | 165 | 278 |  |  | No
10/05/2019 | 08:22 | FSH33 | Urban | Planned |  | 12 | 278 |  |  | No
10/05/2019 | 08:30 | EM9 | Urban | Planned |  | 18 | 360 |  |  | No
10/05/2019 | 08:40 | NW22 | Urban | Planned |  | 25 | 170 |  |  | No
10/05/2019 | 08:45 | GW2 | Urban | Planned |  | 52 | 195 |  |  | No
11/05/2019 | 20:30 | GW2 | Urban | Planned |  | 42 | 576 |  |  | No
12/05/2019 | 07:00 | SV16 | Urban | Planned |  | 1 | 540 |  |  | No
12/05/2019 | 07:10 | SV16 | Urban | Planned |  | 98 | 440 |  |  | No
12/05/2019 | 08:00 | DSH24 | Urban | Planned |  | 8 | 314 |  |  | No
12/05/2019 | 08:10 | LD33 | Urban | Planned |  | 134 | 310 |  |  | No
12/05/2019 | 08:45 | FTN14 | Urban | Planned |  | 5 | 470 |  |  | No
12/05/2019 | 09:19 | SVW53 | Urban | Planned |  | 59 | 368 |  |  | No
12/05/2019 | 10:10 | GW5 | Urban | Planned |  | 14 | 175 |  |  | No
13/05/2019 | 08:45 | CFD16 | Urban | Planned |  | 45 | 485 |  |  | No
14/05/2019 | 08:07 | FSH12 | Rural Short | Planned |  | 26 | 148 |  |  | No
14/05/2019 | 08:15 | MR14 | Urban | Planned |  | 88 | 355 |  |  | No
14/05/2019 | 08:30 | FTN25 | Urban | Planned |  | 110 | 235 |  |  | No
14/05/2019 | 08:30 | K13 | Urban | Planned |  | 65 | 290 |  |  | No
14/05/2019 | 08:30 | WD23 | Urban | Planned |  | 3 | 450 |  |  | No
14/05/2019 | 08:56 | MGE33 | Urban | Planned |  | 31 | 286 |  |  | No
14/05/2019 | 09:00 | GW12 | Urban | Planned |  | 42 | 150 |  |  | No
14/05/2019 | 09:00 | GW12 | Urban | Planned |  | 33 | 160 |  |  | No
14/05/2019 | 09:00 | WD23 | Urban | Planned |  | 42 | 440 |  |  | No
14/05/2019 | 10:35 | FTN25 | Urban | Planned |  | 44 | 255 |  |  | No
14/05/2019 | 12:40 | GW12 | Urban | Planned |  | 32 | 130 |  |  | No
15/05/2019 | 08:00 | HT11 | Urban | Planned |  | 1 | 480 |  |  | No
15/05/2019 | 08:08 | FSH34 | Urban | Planned |  | 13 | 191 |  |  | No
15/05/2019 | 08:10 | EB31 | Urban | Planned |  | 15 | 350 |  |  | No
15/05/2019 | 08:10 | HT11 | Urban | Planned |  | 237 | 225 |  |  | No
15/05/2019 | 08:17 | LWN35 | Urban | Planned |  | 3 | 101 |  |  | No
15/05/2019 | 08:30 | EM3 | Urban | Planned |  | 134 | 430 |  |  | No
15/05/2019 | 08:30 | FSH34 | Urban | Planned |  | 75 | 320 |  |  | No
15/05/2019 | 08:30 | GW8 | Urban | Planned |  | 51 | 110 |  |  | No
15/05/2019 | 08:38 | EB32 | Urban | Planned |  | 28 | 92 |  |  | No
15/05/2019 | 10:00 | CRM12 | Urban | Planned |  | 2 | 201 |  |  | No
15/05/2019 | 10:00 | CRM22 | Urban | Planned |  | 23 | 201 |  |  | No
15/05/2019 | 11:00 | MGE24 | Urban | Planned |  | 52 | 129 |  |  | No
15/05/2019 | 11:00 | SVW53 | Urban | Planned |  | 32 | 129 |  |  | No
16/05/2019 | 08:01 | FTN21 | Urban | Planned |  | 52 | 392 |  |  | No
16/05/2019 | 08:15 | FSH31 | Urban | Planned |  | 54 | 240 |  |  | No
16/05/2019 | 08:34 | GW12 | Urban | Planned |  | 39 | 91 |  |  | No
16/05/2019 | 08:34 | GW4 | Urban | Planned |  | 15 | 91 |  |  | No
16/05/2019 | 09:00 | EL8 | Urban | Planned |  | 102 | 330 |  |  | No
16/05/2019 | 21:30 | MC4 | Urban | Planned |  | 14 | 379.1 |  |  | No
17/05/2019 | 08:00 | FTN11 | Urban | Planned |  | 151 | 300 |  |  | No
17/05/2019 | 09:15 | GW5 | Urban | Planned |  | 64 | 105 |  |  | No
17/05/2019 | 09:30 | DC2 | Urban | Planned |  | 53 | 435 |  |  | No
17/05/2019 | 09:30 | EB32 | Urban | Planned |  | 10 | 285 |  |  | No
17/05/2019 | 09:30 | GW11 | Urban | Planned |  | 356 | 285 |  |  | No
17/05/2019 | 10:30 | BR1 | Urban | Planned |  | 1 | 90 |  |  | No
18/05/2019 | 08:00 | NP12 | Urban | Planned |  | 142 | 597 |  |  | No
18/05/2019 | 08:00 | NP12 | Urban | Planned |  | 142 | 598 |  |  | No
18/05/2019 | 08:00 | SS23 | Urban | Planned |  | 46 | 597 |  |  | No
18/05/2019 | 08:00 | SS23 | Urban | Planned |  | 46 | 598 |  |  | No
18/05/2019 | 08:45 | EB32 | Urban | Planned |  | 5 | 119 |  |  | No
18/05/2019 | 12:09 | EB32 | Urban | Planned |  | 4 | 209 |  |  | No
18/05/2019 | 21:35 | OR22 | Urban | Planned |  | 2 | 35 |  |  | No
19/05/2019 | 07:00 | MGE12 | Urban | Planned |  | 5 | 660 |  |  | No
19/05/2019 | 07:30 | OR22 | Urban | Planned |  | 2 | 630 |  |  | No
19/05/2019 | 08:00 | OE10 | Urban | Planned |  | 79 | 498 |  |  | No
19/05/2019 | 08:00 | OE2 | Urban | Planned |  | 3 | 498 |  |  | No
19/05/2019 | 08:00 | K13 | Urban | Planned |  | 2 | 450 |  |  | No
19/05/2019 | 08:32 | AR6 | Urban | Planned |  | 92 | 253 |  |  | No
19/05/2019 | 09:00 | K4 | Urban | Planned |  | 1 | 360 |  |  | No
20/05/2019 | 04:00 | OR22 | Urban | Planned |  | 2 | 24.1 |  |  | No
20/05/2019 | 08:27 | NB35 | Urban | Planned |  | 55 | 332 |  |  | No
21/05/2019 | 08:00 | STO13 | Urban | Planned |  | 1 | 480 |  |  | No
21/05/2019 | 08:00 | RBD24 | Urban | Planned |  | 6 | 480 |  |  | No
21/05/2019 | 08:10 | STO13 | Urban | Planned |  | 192 | 470 |  |  | No
21/05/2019 | 08:22 | MGE32 | Urban | Planned |  | 45 | 210 |  |  | No
21/05/2019 | 08:32 | GW11 | Urban | Planned |  | 163 | 368 |  |  | No
21/05/2019 | 08:35 | EB13 | Urban | Planned |  | 63 | 380 |  |  | No
21/05/2019 | 08:45 | MTN34 | Urban | Planned |  | 33 | 555 |  |  | No
21/05/2019 | 09:00 | HGS22 | Rural Short | Planned |  | 177 | 420 |  |  | No
21/05/2019 | 09:15 | RBD14 | Urban | Planned |  | 81 | 514 |  |  | No
21/05/2019 | 09:43 | HGS22 | Rural Short | Planned |  | 27 | 137 |  |  | No
21/05/2019 | 10:30 | EB13 | Urban | Planned |  | 76 | 95 |  |  | No
22/05/2019 | 08:00 | EW8 | Urban | Planned |  | 71 | 210 |  |  | No
22/05/2019 | 08:00 | FSH34 | Urban | Planned |  | 95 | 325 |  |  | No
22/05/2019 | 08:00 | MTN34 | Urban | Planned |  | 29 | 400 |  |  | No
22/05/2019 | 08:10 | EB12 | Urban | Planned |  | 55 | 435 |  |  | No
22/05/2019 | 08:10 | GW8 | Urban | Planned |  | 53 | 435 |  |  | No
22/05/2019 | 08:15 | SS23 | Urban | Planned |  | 59 | 215 |  |  | No
22/05/2019 | 08:30 | EW1 | Urban | Planned |  | 73 | 405 |  |  | No
22/05/2019 | 08:30 | EW9 | Urban | Planned |  | 236 | 405 |  |  | No
22/05/2019 | 08:30 | GW11 | Urban | Planned |  | 1 | 450 |  |  | No
22/05/2019 | 08:35 | DMA14 | Urban | Planned |  | 31 | 125 |  |  | No
22/05/2019 | 08:47 | BW33 | Urban | Planned |  | 10 | 289 |  |  | No
22/05/2019 | 09:15 | GW11 | Urban | Planned |  | 34 | 240 |  |  | No
22/05/2019 | 09:20 | CRM14 | Urban | Planned |  | 58 | 232 |  |  | No
22/05/2019 | 09:30 | DMA21 | Urban | Planned |  | 11 | 270 |  |  | No
22/05/2019 | 09:30 | GW5 | Urban | Planned |  | 25 | 80 |  |  | No
22/05/2019 | 09:45 | MC3 | Urban | Planned |  | 330 | 290 |  |  | No
22/05/2019 | 11:40 | GW10 | Urban | Planned |  | 66 | 100 |  |  | No
22/05/2019 | 12:30 | GW8 | Urban | Planned |  | 46 | 263 |  |  | No
23/05/2019 | 08:00 | CRM22 | Urban | Planned |  | 1 | 630 |  |  | No
23/05/2019 | 08:03 | EB21 | Urban | Planned |  | 10 | 521 |  |  | No
23/05/2019 | 08:10 | K13 | Urban | Planned |  | 18 | 270 |  |  | No
23/05/2019 | 08:30 | FSH34 | Urban | Planned |  | 250 | 220 |  |  | No
23/05/2019 | 08:40 | GW10 | Urban | Planned |  | 207 | 480 |  |  | No
23/05/2019 | 08:42 | K8 | Urban | Planned |  | 56 | 127 |  |  | No
23/05/2019 | 08:53 | GW10 | Urban | Planned |  | 16 | 129 |  |  | No
23/05/2019 | 08:56 | CRM22 | Urban | Planned |  | 299 | 368 |  |  | No
23/05/2019 | 10:39 | CRM21 | Urban | Planned |  | 2 | 89 |  |  | No
23/05/2019 | 11:13 | OR25 | Urban | Planned |  | 115 | 313 |  |  | No
24/05/2019 | 08:00 | K8 | Urban | Planned |  | 29 | 486.2 |  |  | No
24/05/2019 | 08:02 | NW31 | Urban | Planned |  | 27 | 80 |  |  | No
24/05/2019 | 08:03 | FSH12 | Rural Short | Planned |  | 42 | 398 |  |  | No
24/05/2019 | 08:25 | CRM12 | Urban | Planned |  | 68 | 215 |  |  | No
24/05/2019 | 08:30 | GW6 | Urban | Planned |  | 2 | 450 |  |  | No
24/05/2019 | 08:32 | CFD24 | Urban | Planned |  | 177 | 321 |  |  | No
24/05/2019 | 08:40 | GW10 | Urban | Planned |  | 14 | 245 |  |  | No
24/05/2019 | 08:40 | GW7 | Urban | Planned |  | 66 | 95 |  |  | No
24/05/2019 | 08:40 | MGE23 | Urban | Planned |  | 40 | 95 |  |  | No
24/05/2019 | 08:45 | GW6 | Urban | Planned |  | 108 | 355 |  |  | No
24/05/2019 | 09:17 | DN13 | Urban | Planned |  | 57 | 223 |  |  | No
24/05/2019 | 12:20 | EM10 | Urban | Planned |  | 70 | 115 |  |  | No
25/05/2019 | 07:17 | DN21 | Urban | Planned |  | 2 | 169 |  |  | No
25/05/2019 | 08:25 | GW6 | Urban | Planned |  | 7 | 125 |  |  | No
25/05/2019 | 08:30 | MR11 | Urban | Planned |  | 21 | 510 |  |  | No
25/05/2019 | 10:10 | OAK22 | Urban | Planned |  | 55 | 360 |  |  | No
25/05/2019 | 10:10 | OE14 | Urban | Planned |  | 16 | 360 |  |  | No
26/05/2019 | 07:15 | NP11 | Urban | Planned |  | 3 | 516 |  |  | No
26/05/2019 | 07:42 | OAK22 | Urban | Planned |  | 253 | 403 |  |  | No
26/05/2019 | 08:13 | FTN11 | Urban | Planned |  | 1 | 235 |  |  | No
26/05/2019 | 08:13 | LWN35 | Urban | Planned |  | 20 | 235 |  |  | No
26/05/2019 | 09:35 | SR25 | Urban | Planned |  | 1 | 243 |  |  | No
26/05/2019 | 10:55 | FGY21 | Urban | Planned |  | 1 | 292 |  |  | No
27/05/2019 | 08:00 | CDA24 | Urban | Planned |  | 1 | 480 |  |  | No
27/05/2019 | 08:30 | CDA24 | Urban | Planned |  | 58 | 495 |  |  | No
27/05/2019 | 09:09 | DMA24 | Rural Short | Planned |  | 62 | 68 |  |  | No
28/05/2019 | 01:30 | HT9 | Urban | Planned |  | 1 | 240 |  |  | No
28/05/2019 | 02:51 | HT9 | Urban | Planned |  | 46 | 102 |  |  | No
28/05/2019 | 08:15 | GW12 | Urban | Planned |  | 37 | 325 |  |  | No
28/05/2019 | 08:15 | MGE23 | Urban | Planned |  | 33 | 325 |  |  | No
28/05/2019 | 08:23 | SS23 | Urban | Planned |  | 59 | 202 |  |  | No
28/05/2019 | 08:40 | FSH34 | Urban | Planned |  | 89 | 330 |  |  | No
28/05/2019 | 08:45 | GW12 | Urban | Planned |  | 33 | 195 |  |  | No
28/05/2019 | 09:00 | MTN24 | Rural Short | Planned |  | 3 | 35 |  |  | No
28/05/2019 | 09:05 | GW12 | Urban | Planned |  | 37 | 205 |  |  | No
28/05/2019 | 09:05 | MGE23 | Urban | Planned |  | 35 | 205 |  |  | No
28/05/2019 | 10:21 | CRM21 | Urban | Planned |  | 52 | 117 |  |  | No
28/05/2019 | 11:30 | CM22 | Urban | Planned |  | 52 | 245 |  |  | No
28/05/2019 | 12:30 | GW11 | Urban | Planned |  | 27 | 185 |  |  | No
28/05/2019 | 12:50 | GW12 | Urban | Planned |  | 6 | 28 |  |  | No
28/05/2019 | 12:55 | CRM35 | Urban | Planned |  | 3 | 16 |  |  | No
28/05/2019 | 14:06 | CRM35 | Urban | Planned |  | 3 | 22 |  |  | No
29/05/2019 | 08:00 | KBH35 | Urban | Planned |  | 1 | 480 |  |  | No
29/05/2019 | 08:13 | KBH35 | Urban | Planned |  | 76 | 412 |  |  | No
29/05/2019 | 08:25 | GW3 | Urban | Planned |  | 34 | 230 |  |  | No
29/05/2019 | 08:25 | GW3 | Urban | Planned |  | 71 | 395 |  |  | No
29/05/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 5 | 460 |  |  | No
29/05/2019 | 08:30 | LD2 | Urban | Planned |  | 27 | 180 |  |  | No
29/05/2019 | 09:10 | NW13 | Urban | Planned |  | 3 | 190 |  |  | No
29/05/2019 | 09:29 | SS23 | Urban | Planned |  | 13 | 171 |  |  | No
29/05/2019 | 09:32 | OAK21 | Urban | Planned |  | 29 | 147 |  |  | No
29/05/2019 | 09:34 | DC4 | Urban | Planned |  | 56 | 372 |  |  | No
29/05/2019 | 09:46 | OE10 | Urban | Planned |  | 6 | 69 |  |  | No
30/05/2019 | 08:15 | MGE34 | Urban | Planned |  | 30 | 445 |  |  | No
30/05/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 59 | 265 |  |  | No
30/05/2019 | 08:30 | NP16 | Urban | Planned |  | 63 | 240 |  |  | No
30/05/2019 | 09:00 | CM13 | Urban | Planned |  | 62 | 267 |  |  | No
30/05/2019 | 09:00 | MGE32 | Urban | Planned |  | 13 | 300 |  |  | No
30/05/2019 | 09:02 | DN10 | Urban | Planned |  | 20 | 258 |  |  | No
30/05/2019 | 09:35 | LWN23 | Urban | Planned |  | 54 | 265 |  |  | No
30/05/2019 | 09:35 | LWN32 | Rural Short | Planned |  | 38 | 265 |  |  | No
30/05/2019 | 11:46 | CRM14 | Urban | Planned |  | 10 | 114 |  |  | No
31/05/2019 | 08:24 | GW12 | Urban | Planned |  | 53 | 156 |  |  | No
31/05/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 60 | 123 |  |  | No
31/05/2019 | 08:30 | GW11 | Urban | Planned |  | 1 | 450 |  |  | No
31/05/2019 | 08:45 | GW11 | Urban | Planned |  | 43 | 255 |  |  | No
31/05/2019 | 08:45 | GW8 | Urban | Planned |  | 14 | 255 |  |  | No
31/05/2019 | 08:45 | LD2 | Urban | Planned |  | 18 | 300 |  |  | No
31/05/2019 | 09:00 | GW11 | Urban | Planned |  | 73 | 240 |  |  | No
31/05/2019 | 10:36 | DVY24 | Rural Short | Planned |  | 10 | 194 |  |  | No
01/06/2019 | 08:00 | EW9 | Urban | Planned |  | 242 | 240 |  |  | No
01/06/2019 | 08:00 | EW9 | Urban | Planned |  | 1 | 270 |  |  | No
01/06/2019 | 08:17 | OAK26 | Urban | Planned |  | 12 | 138 |  |  | No
01/06/2019 | 12:00 | DVY23 | Urban | Planned |  | 1 | 70 |  |  | No
02/06/2019 | 08:00 | OE10 | Urban | Planned |  | 1 | 570 |  |  | No
02/06/2019 | 08:02 | FTN25 | Urban | Planned |  | 17 | 538 |  |  | No
02/06/2019 | 08:30 | OE10 | Urban | Planned |  | 12 | 735 |  |  | No
02/06/2019 | 08:45 | FTN13 | Urban | Planned |  | 69 | 295 |  |  | No
02/06/2019 | 19:30 | EM3 | Urban | Planned |  | 16 | 575 |  |  | No
02/06/2019 | 19:30 | OAK34 | Urban | Planned |  | 20 | 575 |  |  | No
03/06/2019 | 08:23 | RWT35 | Urban | Planned |  | 60 | 152 |  |  | No
03/06/2019 | 09:00 | GW5 | Urban | Planned |  | 40 | 200 |  |  | No
03/06/2019 | 09:15 | CRM21 | Urban | Planned |  | 65 | 45 |  |  | No
03/06/2019 | 12:00 | CRM14 | Urban | Planned |  | 1 | 240 |  |  | No
03/06/2019 | 12:02 | CRM14 | Urban | Planned |  | 74 | 86 |  |  | No
04/06/2019 | 08:00 | DN10 | Urban | Planned |  | 51 | 200 |  |  | No
04/06/2019 | 08:05 | OR24 | Urban | Planned |  | 125 | 335 |  |  | No
04/06/2019 | 08:20 | FSH12 | Rural Short | Planned |  | 59 | 220 |  |  | No
04/06/2019 | 08:30 | GW7 | Urban | Planned |  | 78 | 195 |  |  | No
04/06/2019 | 08:35 | DN10 | Urban | Planned |  | 22 | 175 |  |  | No
04/06/2019 | 08:45 | CFD14 | Urban | Planned |  | 134 | 225 |  |  | No
04/06/2019 | 09:00 | RWT23 | Urban | Planned |  | 38 | 79 |  |  | No
04/06/2019 | 09:06 | RWT12 | Urban | Planned |  | 25 | 219 |  |  | No
04/06/2019 | 09:10 | GW10 | Urban | Planned |  | 28 | 95 |  |  | No
04/06/2019 | 09:30 | FSH12 | Rural Short | Planned |  | 54 | 270 |  |  | No
04/06/2019 | 10:40 | NW23 | Urban | Planned |  | 27 | 185 |  |  | No
04/06/2019 | 11:20 | GW10 | Urban | Planned |  | 81 | 115 |  |  | No
04/06/2019 | 12:00 | GW7 | Urban | Planned |  | 9 | 70 |  |  | No
05/06/2019 | 08:00 | NO32 | Urban | Planned |  | 1 | 300 |  |  | No
05/06/2019 | 08:20 | GW10 | Urban | Planned |  | 15 | 205 |  |  | No
05/06/2019 | 08:20 | NO32 | Urban | Planned |  | 64 | 205 |  |  | No
05/06/2019 | 08:30 | GW6 | Urban | Planned |  | 50 | 225 |  |  | No
05/06/2019 | 08:33 | HGS32 | Urban | Planned |  | 12 | 386 |  |  | No
05/06/2019 | 08:40 | FSH34 | Urban | Planned |  | 69 | 365 |  |  | No
05/06/2019 | 08:42 | MGE23 | Urban | Planned |  | 28 | 318 |  |  | No
05/06/2019 | 09:00 | FSH13 | Urban | Planned |  | 146 | 155 |  |  | No
05/06/2019 | 09:00 | GW6 | Urban | Planned |  | 44 | 120 |  |  | No
05/06/2019 | 09:00 | HT11 | Urban | Planned |  | 61 | 315 |  |  | No
05/06/2019 | 09:02 | CRM13 | Urban | Planned |  | 33 | 404 |  |  | No
05/06/2019 | 09:12 | NW11 | Urban | Planned |  | 114 | 221 |  |  | No
05/06/2019 | 10:02 | BW35 | Urban | Planned |  | 32 | 318 |  |  | No
05/06/2019 | 12:05 | GW3 | Urban | Planned |  | 40 | 105 |  |  | No
06/06/2019 | 08:12 | GW3 | Urban | Planned |  | 41 | 367 |  |  | No
06/06/2019 | 08:51 | CRM14 | Urban | Planned |  | 3 | 127 |  |  | No
06/06/2019 | 09:00 | EM8 | Urban | Planned |  | 36 | 320 |  |  | No
06/06/2019 | 09:01 | SV33 | Urban | Planned |  | 205 | 238 |  |  | No
06/06/2019 | 09:15 | NW23 | Urban | Planned |  | 2 | 240 |  |  | No
06/06/2019 | 10:15 | NW13 | Urban | Planned |  | 21 | 120 |  |  | No
06/06/2019 | 12:56 | LWN21 | Rural Short | Planned |  | 7 | 151 |  |  | No
07/06/2019 | 07:59 | CDA22 | Urban | Planned |  | 47 | 271 |  |  | No
07/06/2019 | 08:00 | CRM35 | Urban | Planned |  | 98 | 360 |  |  | No
07/06/2019 | 08:00 | FSH21 | Rural Short | Planned |  | 1 | 155 |  |  | No
07/06/2019 | 08:30 | DMA14 | Urban | Planned |  | 36 | 75 |  |  | No
07/06/2019 | 08:30 | LD33 | Urban | Planned |  | 56 | 420 |  |  | No
07/06/2019 | 09:15 | EB22 | Urban | Planned |  | 51 | 300 |  |  | No
07/06/2019 | 09:15 | FSH33 | Urban | Planned |  | 16 | 330 |  |  | No
07/06/2019 | 09:30 | CDA22 | Urban | Planned |  | 20 | 360 |  |  | No
07/06/2019 | 09:45 | LWN35 | Urban | Planned |  | 23 | 180 |  |  | No
07/06/2019 | 10:39 | MTN31 | Urban | Planned |  | 54 | 65 |  |  | No
07/06/2019 | 12:55 | K10 | Urban | Planned |  | 16 | 214 |  |  | No
07/06/2019 | 13:40 | CRM35 | Urban | Planned |  | 2 | 35 |  |  | No
08/06/2019 | 08:05 | GW12 | Urban | Planned |  | 59 | 185 |  |  | No
08/06/2019 | 08:45 | HT1 | Urban | Planned |  | 7 | 180 |  |  | No
08/06/2019 | 08:45 | M21 | Urban | Planned |  | 8 | 180 |  |  | No
08/06/2019 | 09:05 | MTN32 | Rural Short | Planned |  | 4 | 30 |  |  | No
09/06/2019 | 07:48 | SH22 | Urban | Planned |  | 114 | 482 |  |  | No
09/06/2019 | 07:59 | DN21 | Urban | Planned |  | 65 | 328 |  |  | No
09/06/2019 | 08:05 | FTN14 | Urban | Planned |  | 36 | 335 |  |  | No
09/06/2019 | 08:12 | DN2 | Urban | Planned |  | 13 | 380 |  |  | No
11/06/2019 | 08:30 | OR25 | Urban | Planned |  | 73 | 320 |  |  | No
11/06/2019 | 08:50 | HGS23 | Rural Short | Planned |  | 16 | 355 |  |  | No
11/06/2019 | 09:00 | HGS31 | Rural Short | Planned |  | 10 | 90 |  |  | No
11/06/2019 | 09:30 | DVY34 | Urban | Planned |  | 1 | 175 |  |  | No
11/06/2019 | 09:30 | EM8 | Urban | Planned |  | 77 | 280 |  |  | No
12/06/2019 | 08:09 | RBD14 | Urban | Planned |  | 81 | 494 |  |  | No
12/06/2019 | 08:15 | HGS21 | Rural Short | Planned |  | 4 | 12 |  |  | No
12/06/2019 | 08:38 | LD33 | Urban | Planned |  | 61 | 84 |  |  | No
12/06/2019 | 08:40 | MGE23 | Urban | Planned |  | 21 | 295 |  |  | No
12/06/2019 | 09:15 | CRM11 | Urban | Planned |  | 1 | 19 |  |  | No
12/06/2019 | 09:33 | BW35 | Urban | Planned |  | 154 | 25 |  |  | No
13/06/2019 | 08:00 | DN22 | Urban | Planned |  | 46 | 289 |  |  | No
13/06/2019 | 08:00 | DC2 | Urban | Planned |  | 97 | 364.7 |  |  | No
13/06/2019 | 08:11 | FSH11 | Urban | Planned |  | 41 | 176 |  |  | No
13/06/2019 | 08:20 | NO7 | Urban | Planned |  | 19 | 393 |  |  | No
13/06/2019 | 08:25 | MR32 | Urban | Planned |  | 37 | 205 |  |  | No
13/06/2019 | 08:30 | DMA12 | Urban | Planned |  | 3 | 140 |  |  | No
13/06/2019 | 08:30 | MTN31 | Urban | Planned |  | 52 | 522 |  |  | No
13/06/2019 | 09:01 | FSH13 | Urban | Planned |  | 33 | 144 |  |  | No
13/06/2019 | 09:02 | GW8 | Urban | Planned |  | 73 | 297 |  |  | No
13/06/2019 | 09:15 | FSH33 | Urban | Planned |  | 212 | 355 |  |  | No
13/06/2019 | 12:00 | FSH22 | Urban | Planned |  | 1 | 77 |  |  | No
13/06/2019 | 12:53 | FSH13 | Urban | Planned |  | 48 | 94 |  |  | No
13/06/2019 | 22:30 | K3 | Urban | Planned |  | 4 | 420 |  |  | No
14/06/2019 | 08:00 | RBD13 | Urban | Planned |  | 57 | 210 |  |  | No
14/06/2019 | 08:10 | LWN34 | Urban | Planned |  | 42 | 236 |  |  | No
14/06/2019 | 08:30 | GW7 | Urban | Planned |  | 80 | 205 |  |  | No
14/06/2019 | 08:35 | EB12 | Urban | Planned |  | 55 | 150 |  |  | No
14/06/2019 | 08:35 | GW7 | Urban | Planned |  | 79 | 320 |  |  | No
14/06/2019 | 08:45 | NW22 | Urban | Planned |  | 11 | 170 |  |  | No
14/06/2019 | 09:20 | SVW45 | Urban | Planned |  | 12 | 355 |  |  | No
14/06/2019 | 09:40 | MTN32 | Rural Short | Planned |  | 1 | 6 |  |  | No
14/06/2019 | 11:42 | GW7 | Urban | Planned |  | 50 | 170 |  |  | No
15/06/2019 | 03:30 | FTN11 | Urban | Planned |  | 1 | 2,190.0 |  |  | No
15/06/2019 | 07:45 | BH22 | Urban | Planned |  | 1 | 555 |  |  | No
15/06/2019 | 08:05 | FTN14 | Urban | Planned |  | 44 | 295 |  |  | No
15/06/2019 | 08:20 | SS23 | Urban | Planned |  | 249 | 320 |  |  | No
15/06/2019 | 09:40 | NO31 | Urban | Planned |  | 19 | 150 |  |  | No
15/06/2019 | 17:00 | RWT24 | Urban | Planned |  | 42 | 115 |  |  | No
15/06/2019 | 20:15 | MGE24 | Urban | Planned |  | 7 | 160 |  |  | No
16/06/2019 | 00:00 | GW4 | Urban | Planned |  | 9 | 35 |  |  | No
16/06/2019 | 07:00 | DVY33 | Urban | Planned |  | 1 | 240 |  |  | No
16/06/2019 | 07:00 | NO4 | Urban | Planned |  | 64 | 465 |  |  | No
16/06/2019 | 07:00 | DVY33 | Urban | Planned |  | 1 | 480 |  |  | No
16/06/2019 | 07:30 | K13 | Urban | Planned |  | 1 | 540 |  |  | No
16/06/2019 | 07:45 | K13 | Urban | Planned |  | 11 | 445 |  |  | No
16/06/2019 | 07:50 | GW5 | Urban | Planned |  | 1 | 445 |  |  | No
16/06/2019 | 07:59 | DSH24 | Urban | Planned |  | 17 | 145 |  |  | No
16/06/2019 | 08:00 | NB35 | Urban | Planned |  | 8 | 95 |  |  | No
16/06/2019 | 08:30 | FTN13 | Urban | Planned |  | 51 | 300 |  |  | No
16/06/2019 | 09:00 | GW7 | Urban | Planned |  | 245 | 435 |  |  | No
16/06/2019 | 09:32 | NO4 | Urban | Planned |  | 121 | 311 |  |  | No
16/06/2019 | 09:32 | NO7 | Urban | Planned |  | 39 | 311 |  |  | No
17/06/2019 | 08:20 | LWN24 | Urban | Planned |  | 83 | 280 |  |  | No
17/06/2019 | 08:50 | MR24 | Urban | Planned |  | 52 | 560 |  |  | No
17/06/2019 | 11:01 | CRM35 | Urban | Planned |  | 46 | 53 |  |  | No
18/06/2019 | 08:20 | FSH21 | Rural Short | Planned |  | 2 | 20 |  |  | No
18/06/2019 | 08:24 | EL5 | Urban | Planned |  | 77 | 208 |  |  | No
18/06/2019 | 08:37 | MR12 | Urban | Planned |  | 89 | 448 |  |  | No
18/06/2019 | 08:45 | FSH33 | Urban | Planned |  | 17 | 109 |  |  | No
18/06/2019 | 08:50 | FTN22 | Urban | Planned |  | 18 | 145 |  |  | No
18/06/2019 | 08:56 | MGE22 | Urban | Planned |  | 53 | 244 |  |  | No
18/06/2019 | 09:00 | BT15 | Urban | Planned |  | 36 | 490 |  |  | No
18/06/2019 | 09:10 | NW23 | Urban | Planned |  | 47 | 275 |  |  | No
18/06/2019 | 09:15 | GW2 | Urban | Planned |  | 22 | 165 |  |  | No
19/06/2019 | 08:00 | CDA22 | Urban | Planned |  | 58 | 315 |  |  | No
19/06/2019 | 08:08 | EL6 | Urban | Planned |  | 100 | 256 |  |  | No
19/06/2019 | 08:09 | M23 | Urban | Planned |  | 335 | 319 |  |  | No
19/06/2019 | 08:15 | OAK26 | Urban | Planned |  | 18 | 105 |  |  | No
19/06/2019 | 08:28 | DN21 | Urban | Planned |  | 27 | 396 |  |  | No
19/06/2019 | 08:29 | BR10 | Urban | Planned |  | 53 | 101 |  |  | No
19/06/2019 | 08:37 | EB12 | Urban | Planned |  | 61 | 164 |  |  | No
19/06/2019 | 08:40 | LWN35 | Urban | Planned |  | 21 | 530 |  |  | No
19/06/2019 | 08:46 | EM6 | Urban | Planned |  | 14 | 57 |  |  | No
19/06/2019 | 08:52 | HT11 | Urban | Planned |  | 46 | 183 |  |  | No
19/06/2019 | 09:35 | NO7 | Urban | Planned |  | 60 | 420 |  |  | No
19/06/2019 | 12:04 | EB21 | Urban | Planned |  | 132 | 132 |  |  | No
20/06/2019 | 08:35 | SR19 | Urban | Planned |  | 60 | 205 |  |  | No
20/06/2019 | 08:37 | EL6 | Urban | Planned |  | 82 | 465 |  |  | No
20/06/2019 | 08:37 | EL8 | Urban | Planned |  | 15 | 465 |  |  | No
20/06/2019 | 09:30 | EL8 | Urban | Planned |  | 19 | 300 |  |  | No
20/06/2019 | 09:33 | DC8 | Urban | Planned |  | 62 | 206 |  |  | No
20/06/2019 | 11:30 | EB22 | Urban | Planned |  | 13 | 80 |  |  | No
20/06/2019 | 12:25 | NW31 | Urban | Planned |  | 3 | 95 |  |  | No
20/06/2019 | 23:30 | RD4 | Urban | Planned |  | 55 | 360 |  |  | No
21/06/2019 | 08:00 | LWN24 | Urban | Planned |  | 105 | 350 |  |  | No
21/06/2019 | 08:00 | LWN24 | Urban | Planned |  | 52 | 480 |  |  | No
21/06/2019 | 08:30 | HT11 | Urban | Planned |  | 17 | 210 |  |  | No
21/06/2019 | 08:30 | NW23 | Urban | Planned |  | 57 | 240 |  |  | No
21/06/2019 | 08:45 | EL5 | Urban | Planned |  | 23 | 125 |  |  | No
21/06/2019 | 08:50 | NP12 | Urban | Planned |  | 2 | 430 |  |  | No
21/06/2019 | 09:05 | GW10 | Urban | Planned |  | 40 | 130 |  |  | No
21/06/2019 | 09:05 | MGE33 | Urban | Planned |  | 44 | 90 |  |  | No
21/06/2019 | 09:29 | MTN21 | Urban | Planned |  | 1 | 479 |  |  | No
21/06/2019 | 09:29 | MTN23 | Urban | Planned |  | 108 | 479 |  |  | No
21/06/2019 | 10:00 | WD14 | Urban | Planned |  | 175 | 93 |  |  | No
22/06/2019 | 08:00 | BR6 | Urban | Planned |  | 13 | 350 |  |  | No
22/06/2019 | 14:06 | OE10 | Urban | Planned |  | 13 | 31 |  |  | No
22/06/2019 | 20:55 | DN11 | Urban | Planned |  | 100 | 430 |  |  | No
22/06/2019 | 20:55 | LD7 | Urban | Planned |  | 120 | 430 |  |  | No
23/06/2019 | 07:00 | OE2 | Urban | Planned |  | 2 | 630 |  |  | No
23/06/2019 | 07:30 | OE2 | Urban | Planned |  | 72 | 570 |  |  | No
23/06/2019 | 07:50 | DVY31 | Urban | Planned |  | 4 | 420 |  |  | No
23/06/2019 | 08:00 | CDA24 | Urban | Planned |  | 34 | 210 |  |  | No
23/06/2019 | 08:00 | SVW45 | Urban | Planned |  | 2 | 30 |  |  | No
23/06/2019 | 08:20 | FTN11 | Urban | Planned |  | 210 | 345 |  |  | No
23/06/2019 | 08:33 | SVW53 | Urban | Planned |  | 77 | 267 |  |  | No
23/06/2019 | 09:09 | DMA15 | Rural Short | Planned |  | 6 | 362 |  |  | No
23/06/2019 | 09:34 | SVW55 | Urban | Planned |  | 3 | 14 |  |  | No
23/06/2019 | 11:30 | FTN21 | Urban | Planned |  | 26 | 47 |  |  | No
23/06/2019 | 12:02 | DN23 | Urban | Planned |  | 6 | 7 |  |  | No
23/06/2019 | 14:00 | RBD21 | Rural Short | Planned |  | 44 | 116 |  |  | No
24/06/2019 | 08:00 | HGS23 | Rural Short | Planned |  | 1 | 240 |  |  | No
24/06/2019 | 08:17 | HGS23 | Rural Short | Planned |  | 1 | 18 |  |  | No
24/06/2019 | 08:20 | MTN22 | Rural Short | Planned |  | 2 | 110 |  |  | No
24/06/2019 | 08:30 | HGS21 | Rural Short | Planned |  | 26 | 190 |  |  | No
24/06/2019 | 10:04 | DVY34 | Urban | Planned |  | 3 | 380 |  |  | No
24/06/2019 | 12:43 | MTN22 | Rural Short | Planned |  | 1 | 97 |  |  | No
25/06/2019 | 08:00 | LWN34 | Urban | Planned |  | 7 | 710 |  |  | No
25/06/2019 | 08:05 | CDA22 | Urban | Planned |  | 172 | 395 |  |  | No
25/06/2019 | 08:05 | RWT34 | Urban | Planned |  | 123 | 375 |  |  | No
25/06/2019 | 08:05 | RWT35 | Urban | Planned |  | 58 | 375 |  |  | No
25/06/2019 | 08:07 | OE4 | Urban | Planned |  | 54 | 173 |  |  | No
25/06/2019 | 08:30 | GW11 | Urban | Planned |  | 43 | 150 |  |  | No
25/06/2019 | 08:30 | GW8 | Urban | Planned |  | 14 | 150 |  |  | No
25/06/2019 | 08:30 | HGS23 | Rural Short | Planned |  | 41 | 205 |  |  | No
25/06/2019 | 08:30 | HGS23 | Rural Short | Planned |  | 1 | 420 |  |  | No
25/06/2019 | 08:30 | MR31 | Urban | Planned |  | 15 | 155 |  |  | No
25/06/2019 | 08:30 | SVW53 | Urban | Planned |  | 65 | 90 |  |  | No
25/06/2019 | 08:40 | CRM24 | Urban | Planned |  | 24 | 220 |  |  | No
25/06/2019 | 08:49 | DC6 | Urban | Planned |  | 65 | 126 |  |  | No
25/06/2019 | 09:00 | SR14 | Urban | Planned |  | 31 | 404.7 |  |  | No
25/06/2019 | 09:45 | HGS21 | Rural Short | Planned |  | 6 | 155 |  |  | No
25/06/2019 | 10:45 | CDA24 | Urban | Planned |  | 5 | 195 |  |  | No
25/06/2019 | 11:00 | FSH22 | Urban | Planned |  | 35 | 225 |  |  | No
25/06/2019 | 11:45 | HGS21 | Rural Short | Planned |  | 46 | 150 |  |  | No
26/06/2019 | 08:20 | KBH34 | Urban | Planned |  | 51 | 140 |  |  | No
26/06/2019 | 08:25 | DC3 | Urban | Planned |  | 19 | 366 |  |  | No
26/06/2019 | 08:30 | BH21 | Urban | Planned |  | 50 | 240 |  |  | No
26/06/2019 | 08:30 | RBD11 | Urban | Planned |  | 27 | 210 |  |  | No
26/06/2019 | 08:35 | BH21 | Urban | Planned |  | 101 | 188 |  |  | No
26/06/2019 | 08:40 | DMA23 | Rural Short | Planned |  | 1 | 86 |  |  | No
26/06/2019 | 11:00 | M25 | Urban | Planned |  | 23 | 45 |  |  | No
27/06/2019 | 08:00 | MR22 | Urban | Planned |  | 2 | 480 |  |  | No
27/06/2019 | 08:05 | MR22 | Urban | Planned |  | 75 | 160 |  |  | No
27/06/2019 | 08:30 | NW22 | Urban | Planned |  | 65 | 185 |  |  | No
27/06/2019 | 08:30 | NW33 | Urban | Planned |  | 3 | 185 |  |  | No
27/06/2019 | 08:31 | SVW41 | Urban | Planned |  | 197 | 496 |  |  | No
27/06/2019 | 08:40 | LD33 | Urban | Planned |  | 58 | 380 |  |  | No
27/06/2019 | 08:40 | MTN32 | Rural Short | Planned |  | 59 | 240 |  |  | No
27/06/2019 | 08:45 | BR6 | Urban | Planned |  | 14 | 145 |  |  | No
27/06/2019 | 09:00 | HGS33 | Rural Short | Planned |  | 34 | 206 |  |  | No
28/06/2019 | 08:06 | GW7 | Urban | Planned |  | 42 | 357 |  |  | No
28/06/2019 | 08:13 | BT14 | Urban | Planned |  | 66 | 167 |  |  | No
28/06/2019 | 08:30 | DC8 | Urban | Planned |  | 122 | 250 |  |  | No
28/06/2019 | 08:30 | SH34 | Urban | Planned |  | 75 | 225 |  |  | No
28/06/2019 | 08:35 | BH21 | Urban | Planned |  | 39 | 201 |  |  | No
28/06/2019 | 08:40 | LD6 | Urban | Planned |  | 30 | 320 |  |  | No
28/06/2019 | 11:18 | NW13 | Urban | Planned |  | 14 | 97 |  |  | No
29/06/2019 | 08:00 | CDA24 | Urban | Planned |  | 1 | 510 |  |  | No
29/06/2019 | 08:00 | FSH13 | Urban | Planned |  | 64 | 309.1 |  |  | No
29/06/2019 | 08:53 | MR11 | Urban | Planned |  | 52 | 324 |  |  | No
29/06/2019 | 10:15 | EL5 | Urban | Planned |  | 2 | 106 |  |  | No
30/06/2019 | 05:30 | MGE13 | Urban | Planned |  | 1 | 240 |  |  | No
30/06/2019 | 07:00 | DSH34 | Urban | Planned |  | 1 | 585 |  |  | No
30/06/2019 | 07:30 | DC2 | Urban | Planned |  | 88 | 570 |  |  | No
30/06/2019 | 08:00 | OAK25 | Urban | Planned |  | 95 | 530 |  |  | No
30/06/2019 | 08:00 | OAK34 | Urban | Planned |  | 6 | 530 |  |  | No
30/06/2019 | 08:14 | DMA23 | Rural Short | Planned |  | 27 | 2 |  |  | No
30/06/2019 | 08:45 | DC2 | Urban | Planned |  | 240 | 475 |  |  | No
30/06/2019 | 12:04 | SS13 | Urban | Planned |  | 55 | 14 |  |  | No
01/07/2019 | 07:30 | LWN21 | Rural Short | Planned |  | 1 | 510 |  |  | No
01/07/2019 | 08:30 | BT15 | Urban | Planned |  | 54 | 369 |  |  | No
01/07/2019 | 08:30 | BT9 | Urban | Planned |  | 41 | 369 |  |  | No
01/07/2019 | 08:39 | CRM33 | Urban | Planned |  | 44 | 66 |  |  | No
01/07/2019 | 09:00 | GW8 | Urban | Planned |  | 27 | 230 |  |  | No
01/07/2019 | 09:16 | LWN21 | Rural Short | Planned |  | 92 | 234 |  |  | No
01/07/2019 | 20:05 | OAK33 | Urban | Planned |  | 1 | 730 |  |  | No
02/07/2019 | 05:42 | DC6 | Urban | Planned |  | 10 | 2 |  |  | No
02/07/2019 | 07:00 | EW12 | Urban | Planned |  | 1 | 540 |  |  | No
02/07/2019 | 08:00 | MTN24 | Rural Short | Planned |  | 1 | 480 |  |  | No
02/07/2019 | 08:00 | MTN32 | Rural Short | Planned |  | 36 | 210 |  |  | No
02/07/2019 | 08:00 | MC2 | Urban | Planned |  | 2 | 390 |  |  | No
02/07/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 1 | 330 |  |  | No
02/07/2019 | 08:30 | K2 | Urban | Planned |  | 12 | 510 |  |  | No
02/07/2019 | 08:45 | RBD21 | Rural Short | Planned |  | 7 | 290 |  |  | No
02/07/2019 | 08:53 | EL13 | Urban | Planned |  | 67 | 416 |  |  | No
02/07/2019 | 09:40 | EB22 | Urban | Planned |  | 25 | 320 |  |  | No
02/07/2019 | 10:28 | MTN24 | Rural Short | Planned |  | 8 | 92 |  |  | No
02/07/2019 | 20:30 | BW33 | Urban | Planned |  | 41 | 509.9 |  |  | No
03/07/2019 | 08:00 | HGS32 | Urban | Planned |  | 1 | 260 |  |  | No
03/07/2019 | 08:00 | M12 | Urban | Planned |  | 6 | 210 |  |  | No
03/07/2019 | 08:00 | M22 | Urban | Planned |  | 66 | 210 |  |  | No
03/07/2019 | 08:00 | BR1 | Urban | Planned |  | 1 | 480 |  |  | No
03/07/2019 | 08:30 | NP14 | Urban | Planned |  | 11 | 330 |  |  | No
03/07/2019 | 08:45 | GW11 | Urban | Planned |  | 73 | 150 |  |  | No
03/07/2019 | 08:47 | RBD13 | Urban | Planned |  | 29 | 210 |  |  | No
03/07/2019 | 09:00 | MC3 | Urban | Planned |  | 63 | 300 |  |  | No
03/07/2019 | 09:00 | RBD13 | Urban | Planned |  | 16 | 200 |  |  | No
03/07/2019 | 09:01 | K10 | Urban | Planned |  | 148 | 222 |  |  | No
03/07/2019 | 09:11 | BR1 | Urban | Planned |  | 133 | 334 |  |  | No
03/07/2019 | 09:30 | EB22 | Urban | Planned |  | 13 | 239 |  |  | No
03/07/2019 | 09:35 | EL9 | Urban | Planned |  | 17 | 433 |  |  | No
03/07/2019 | 09:38 | CFD15 | Urban | Planned |  | 64 | 394 |  |  | No
03/07/2019 | 10:15 | CDA23 | Urban | Planned |  | 132 | 137 |  |  | No
03/07/2019 | 10:15 | OE5 | Urban | Planned |  | 56 | 137 |  |  | No
03/07/2019 | 12:15 | DMA23 | Rural Short | Planned |  | 25 | 73 |  |  | No
03/07/2019 | 12:20 | MGE31 | Urban | Planned |  | 11 | 30 |  |  | No
04/07/2019 | 08:00 | OR33 | Urban | Planned |  | 28 | 215 |  |  | No
04/07/2019 | 08:10 | NW21 | Urban | Planned |  | 2 | 160 |  |  | No
04/07/2019 | 08:25 | SR25 | Urban | Planned |  | 53 | 190 |  |  | No
04/07/2019 | 08:37 | GW10 | Urban | Planned |  | 14 | 118 |  |  | No
04/07/2019 | 08:40 | STO14 | Rural Short | Planned |  | 19 | 245 |  |  | No
04/07/2019 | 08:55 | GW8 | Urban | Planned |  | 121 | 335 |  |  | No
04/07/2019 | 09:03 | FSH34 | Urban | Planned |  | 25 | 252 |  |  | No
04/07/2019 | 09:10 | MC7 | Urban | Planned |  | 33 | 278 |  |  | No
04/07/2019 | 09:15 | RBD12 | Rural Short | Planned |  | 55 | 176 |  |  | No
05/07/2019 | 08:00 | GW12 | Urban | Planned |  | 45 | 394 |  |  | No
05/07/2019 | 08:10 | FSH33 | Urban | Planned |  | 51 | 295 |  |  | No
05/07/2019 | 08:30 | STO22 | Urban | Planned |  | 7 | 250 |  |  | No
05/07/2019 | 08:41 | MGE22 | Urban | Planned |  | 156 | 50 |  |  | No
05/07/2019 | 08:42 | GW8 | Urban | Planned |  | 51 | 249 |  |  | No
05/07/2019 | 08:57 | STO23 | Urban | Planned |  | 49 | 331 |  |  | No
05/07/2019 | 09:10 | CDA24 | Urban | Planned |  | 24 | 111 |  |  | No
06/07/2019 | 08:04 | HT3 | Urban | Planned |  | 24 | 474 |  |  | No
07/07/2019 | 07:00 | EM10 | Urban | Planned |  | 1 | 540 |  |  | No
07/07/2019 | 07:30 | HT2 | Urban | Planned |  | 70 | 485 |  |  | No
07/07/2019 | 07:35 | EM10 | Urban | Planned |  | 187 | 515 |  |  | No
07/07/2019 | 09:15 | HT11 | Urban | Planned |  | 268 | 291 |  |  | No
08/07/2019 | 08:30 | RBD24 | Urban | Planned |  | 65 | 175 |  |  | No
08/07/2019 | 08:30 | RBD24 | Urban | Planned |  | 3 | 360 |  |  | No
08/07/2019 | 11:55 | RBD24 | Urban | Planned |  | 27 | 160 |  |  | No
09/07/2019 | 08:00 | HT1 | Urban | Planned |  | 3 | 480 |  |  | No
09/07/2019 | 08:18 | HT1 | Urban | Planned |  | 22 | 307 |  |  | No
09/07/2019 | 08:30 | STO13 | Urban | Planned |  | 254 | 340 |  |  | No
09/07/2019 | 08:36 | DMA13 | Rural Short | Planned |  | 258 | 324 |  |  | No
09/07/2019 | 08:40 | OAK33 | Urban | Planned |  | 80 | 225 |  |  | No
09/07/2019 | 09:00 | BH12 | Urban | Planned |  | 27 | 380 |  |  | No
09/07/2019 | 11:20 | NB24 | Urban | Planned |  | 20 | 160 |  |  | No
09/07/2019 | 11:25 | K10 | Urban | Planned |  | 47 | 140 |  |  | No
09/07/2019 | 12:50 | RBD24 | Urban | Planned |  | 219 | 180 |  |  | No
10/07/2019 | 04:27 | DSH24 | Urban | Planned |  | 5 | 1 |  |  | No
10/07/2019 | 08:05 | DMA21 | Urban | Planned |  | 102 | 175 |  |  | No
10/07/2019 | 08:17 | CDA23 | Urban | Planned |  | 157 | 234 |  |  | No
10/07/2019 | 08:25 | STO14 | Rural Short | Planned |  | 4 | 20 |  |  | No
10/07/2019 | 08:30 | DC10 | Urban | Planned |  | 3 | 450 |  |  | No
10/07/2019 | 08:34 | MGE24 | Urban | Planned |  | 36 | 99 |  |  | No
10/07/2019 | 08:40 | DC10 | Urban | Planned |  | 174 | 290 |  |  | No
10/07/2019 | 08:40 | M32 | Urban | Planned |  | 24 | 240 |  |  | No
10/07/2019 | 08:50 | DMA21 | Urban | Planned |  | 29 | 57 |  |  | No
10/07/2019 | 09:15 | FSH32 | Rural Short | Planned |  | 29 | 148 |  |  | No
10/07/2019 | 11:30 | DMA21 | Urban | Planned |  | 95 | 175 |  |  | No
11/07/2019 | 07:00 | EW14 | Urban | Planned |  | 118 | 360 |  |  | No
11/07/2019 | 07:00 | EW14 | Urban | Planned |  | 1 | 540 |  |  | No
11/07/2019 | 08:00 | NW23 | Urban | Planned |  | 125 | 415 |  |  | No
11/07/2019 | 08:21 | MTN35 | Rural Short | Planned |  | 54 | 182 |  |  | No
11/07/2019 | 08:34 | LD5 | Urban | Planned |  | 29 | 339 |  |  | No
11/07/2019 | 08:35 | GW8 | Urban | Planned |  | 57 | 468 |  |  | No
11/07/2019 | 08:50 | EM9 | Urban | Planned |  | 112 | 395 |  |  | No
11/07/2019 | 09:55 | SH24 | Urban | Planned |  | 56 | 130 |  |  | No
11/07/2019 | 11:50 | BH21 | Urban | Planned |  | 65 | 180 |  |  | No
12/07/2019 | 08:00 | FSH33 | Urban | Planned |  | 187 | 104 |  |  | No
12/07/2019 | 08:30 | BH21 | Urban | Planned |  | 32 | 360 |  |  | No
12/07/2019 | 08:30 | NP33 | Urban | Planned |  | 38 | 180 |  |  | No
12/07/2019 | 09:00 | DC7 | Urban | Planned |  | 154 | 270 |  |  | No
12/07/2019 | 09:30 | CRM14 | Urban | Planned |  | 86 | 230 |  |  | No
12/07/2019 | 09:47 | BH21 | Urban | Planned |  | 41 | 103 |  |  | No
12/07/2019 | 10:37 | NB33 | Urban | Planned |  | 86 | 242 |  |  | No
12/07/2019 | 12:15 | SH32 | Urban | Planned |  | 92 | 50 |  |  | No
13/07/2019 | 07:05 | NO3 | Urban | Planned |  | 13 | 1,970.0 |  |  | No
13/07/2019 | 08:07 | FTN14 | Urban | Planned |  | 155 | 297 |  |  | No
13/07/2019 | 09:45 | DC8 | Urban | Planned |  | 28 | 325 |  |  | No
13/07/2019 | 22:26 | SV16 | Urban | Planned |  | 7 | 145 |  |  | No
14/07/2019 | 06:45 | SV31 | Urban | Planned |  | 48 | 405 |  |  | No
14/07/2019 | 07:45 | EB11 | Urban | Planned |  | 3 | 278 |  |  | No
14/07/2019 | 07:45 | EB21 | Urban | Planned |  | 17 | 278 |  |  | No
14/07/2019 | 08:16 | OE4 | Urban | Planned |  | 79 | 705 |  |  | No
14/07/2019 | 08:18 | NO6 | Urban | Planned |  | 1 | 4 |  |  | No
14/07/2019 | 08:20 | SVW41 | Urban | Planned |  | 18 | 470 |  |  | No
14/07/2019 | 10:22 | EM10 | Urban | Planned |  | 25 | 187 |  |  | No
15/07/2019 | 08:11 | GW3 | Urban | Planned |  | 2 | 637 |  |  | No
15/07/2019 | 08:14 | HT2 | Urban | Planned |  | 16 | 240 |  |  | No
15/07/2019 | 08:15 | CFD12 | Urban | Planned |  | 18 | 405 |  |  | No
15/07/2019 | 08:30 | DC6 | Urban | Planned |  | 3 | 135 |  |  | No
15/07/2019 | 08:40 | BR4 | Urban | Planned |  | 22 | 250 |  |  | No
15/07/2019 | 08:47 | STO13 | Urban | Planned |  | 24 | 95 |  |  | No
15/07/2019 | 12:15 | BH21 | Urban | Planned |  | 2 | 105 |  |  | No
16/07/2019 | 07:30 | LWN21 | Rural Short | Planned |  | 3 | 570 |  |  | No
16/07/2019 | 07:33 | EW1 | Urban | Planned |  | 30 | 50 |  |  | No
16/07/2019 | 08:25 | LWN21 | Rural Short | Planned |  | 212 | 425 |  |  | No
16/07/2019 | 08:30 | LD33 | Urban | Planned |  | 20 | 105 |  |  | No
16/07/2019 | 08:35 | SR23 | Urban | Planned |  | 104 | 250 |  |  | No
16/07/2019 | 08:38 | FTN14 | Urban | Planned |  | 16 | 195 |  |  | No
16/07/2019 | 08:38 | OR23 | Urban | Planned |  | 54 | 195 |  |  | No
16/07/2019 | 08:40 | DC10 | Urban | Planned |  | 117 | 443 |  |  | No
16/07/2019 | 08:50 | LWN23 | Urban | Planned |  | 54 | 210 |  |  | No
16/07/2019 | 13:15 | BH21 | Urban | Planned |  | 19 | 85 |  |  | No
17/07/2019 | 08:00 | DC10 | Urban | Planned |  | 1 | 510 |  |  | No
17/07/2019 | 08:00 | SVW41 | Urban | Planned |  | 197 | 230 |  |  | No
17/07/2019 | 08:00 | SVW41 | Urban | Planned |  | 1 | 510 |  |  | No
17/07/2019 | 08:13 | DC10 | Urban | Planned |  | 154 | 361 |  |  | No
17/07/2019 | 08:13 | NW23 | Urban | Planned |  | 60 | 361 |  |  | No
17/07/2019 | 08:46 | FTN24 | Urban | Planned |  | 112 | 219 |  |  | No
17/07/2019 | 08:53 | EL9 | Urban | Planned |  | 33 | 277 |  |  | No
17/07/2019 | 09:00 | MGE22 | Urban | Planned |  | 26 | 360 |  |  | No
17/07/2019 | 09:30 | CFD16 | Urban | Planned |  | 47 | 165 |  |  | No
17/07/2019 | 09:30 | EB22 | Urban | Planned |  | 65 | 100 |  |  | No
18/07/2019 | 08:30 | EW14 | Urban | Planned |  | 23 | 308 |  |  | No
18/07/2019 | 08:40 | NB34 | Urban | Planned |  | 56 | 215 |  |  | No
18/07/2019 | 08:40 | SR13 | Urban | Planned |  | 62 | 210 |  |  | No
18/07/2019 | 08:50 | MC1 | Urban | Planned |  | 69 | 310 |  |  | No
18/07/2019 | 09:00 | CFD23 | Urban | Planned |  | 55 | 140 |  |  | No
18/07/2019 | 09:00 | EL12 | Urban | Planned |  | 25 | 140 |  |  | No
18/07/2019 | 09:07 | GW3 | Urban | Planned |  | 43 | 237 |  |  | No
18/07/2019 | 09:20 | FSH33 | Urban | Planned |  | 54 | 348 |  |  | No
18/07/2019 | 09:30 | K6 | Urban | Planned |  | 8 | 165 |  |  | No
18/07/2019 | 10:37 | FTN21 | Urban | Planned |  | 13 | 128 |  |  | No
19/07/2019 | 04:10 | BH23 | Urban | Planned |  | 1 | 40 |  |  | No
19/07/2019 | 08:00 | HT8 | Urban | Planned |  | 123 | 385 |  |  | No
19/07/2019 | 08:30 | EB14 | Urban | Planned |  | 107 | 450 |  |  | No
19/07/2019 | 08:40 | RBD24 | Urban | Planned |  | 83 | 140 |  |  | No
19/07/2019 | 08:45 | EB14 | Urban | Planned |  | 70 | 180 |  |  | No
19/07/2019 | 08:45 | NW33 | Urban | Planned |  | 10 | 360 |  |  | No
19/07/2019 | 09:50 | K6 | Urban | Planned |  | 33 | 187 |  |  | No
19/07/2019 | 12:30 | RBD12 | Rural Short | Planned |  | 14 | 90 |  |  | No
20/07/2019 | 08:30 | BH23 | Urban | Planned |  | 65 | 160 |  |  | No
20/07/2019 | 08:39 | EM10 | Urban | Planned |  | 66 | 487 |  |  | No
20/07/2019 | 08:39 | OR33 | Urban | Planned |  | 345 | 487 |  |  | No
21/07/2019 | 07:30 | EL8 | Urban | Planned |  | 75 | 110 |  |  | No
21/07/2019 | 08:00 | CFD23 | Urban | Planned |  | 1 | 450 |  |  | No
21/07/2019 | 08:00 | FSH33 | Urban | Planned |  | 148 | 385 |  |  | No
21/07/2019 | 08:00 | FSH33 | Urban | Planned |  | 1 | 480 |  |  | No
21/07/2019 | 08:00 | FTN21 | Urban | Planned |  | 96 | 720 |  |  | No
21/07/2019 | 08:30 | CFD23 | Urban | Planned |  | 64 | 390 |  |  | No
22/07/2019 | 08:00 | FSH22 | Urban | Planned |  | 5 | 480 |  |  | No
22/07/2019 | 08:05 | NB35 | Urban | Planned |  | 57 | 330 |  |  | No
22/07/2019 | 08:30 | DMA14 | Urban | Planned |  | 206 | 145 |  |  | No
22/07/2019 | 08:30 | EL9 | Urban | Planned |  | 21 | 390 |  |  | No
22/07/2019 | 12:14 | HGS31 | Rural Short | Planned |  | 12 | 81 |  |  | No
23/07/2019 | 08:00 | DC10 | Urban | Planned |  | 1 | 510 |  |  | No
23/07/2019 | 08:00 | FTN23 | Urban | Planned |  | 161 | 510 |  |  | No
23/07/2019 | 08:00 | HT11 | Urban | Planned |  | 48 | 270 |  |  | No
23/07/2019 | 08:25 | HGS31 | Rural Short | Planned |  | 1 | 210 |  |  | No
23/07/2019 | 08:30 | CRM21 | Urban | Planned |  | 98 | 160 |  |  | No
23/07/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 76 | 450 |  |  | No
23/07/2019 | 08:30 | EL8 | Urban | Planned |  | 19 | 450 |  |  | No
23/07/2019 | 08:31 | DN11 | Urban | Planned |  | 52 | 65 |  |  | No
23/07/2019 | 08:45 | EL8 | Urban | Planned |  | 18 | 120 |  |  | No
23/07/2019 | 09:20 | DC10 | Urban | Planned |  | 187 | 425 |  |  | No
23/07/2019 | 09:30 | SR14 | Urban | Planned |  | 36 | 360 |  |  | No
23/07/2019 | 09:45 | BT9 | Urban | Planned |  | 2 | 150 |  |  | No
23/07/2019 | 22:45 | BH23 | Urban | Planned |  | 1 | 110 |  |  | No
24/07/2019 | 08:00 | LWN33 | Urban | Planned |  | 103 | 245 |  |  | No
24/07/2019 | 08:00 | WD23 | Urban | Planned |  | 42 | 754.1 |  |  | No
24/07/2019 | 08:30 | DMA14 | Urban | Planned |  | 37 | 175 |  |  | No
24/07/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 10 | 130 |  |  | No
24/07/2019 | 08:30 | GW6 | Urban | Planned |  | 33 | 150 |  |  | No
24/07/2019 | 08:40 | HGS33 | Rural Short | Planned |  | 41 | 295 |  |  | No
24/07/2019 | 08:55 | EL11 | Urban | Planned |  | 18 | 129 |  |  | No
24/07/2019 | 08:57 | BR13 | Urban | Planned |  | 35 | 130 |  |  | No
24/07/2019 | 09:25 | NW23 | Urban | Planned |  | 47 | 255 |  |  | No
24/07/2019 | 09:47 | DMA23 | Rural Short | Planned |  | 2 | 15 |  |  | No
24/07/2019 | 10:43 | MGE24 | Urban | Planned |  | 32 | 407 |  |  | No
24/07/2019 | 10:50 | DMA23 | Rural Short | Planned |  | 30 | 15 |  |  | No
24/07/2019 | 10:50 | MGE21 | Urban | Planned |  | 44 | 220 |  |  | No
24/07/2019 | 13:05 | DVY24 | Rural Short | Planned |  | 1 | 20 |  |  | No
25/07/2019 | 08:00 | DMA24 | Rural Short | Planned |  | 13 | 480 |  |  | No
25/07/2019 | 08:00 | DMA24 | Rural Short | Planned |  | 208 | 645 |  |  | No
25/07/2019 | 08:00 | FSH33 | Urban | Planned |  | 2 | 480 |  |  | No
25/07/2019 | 08:02 | OR24 | Urban | Planned |  | 53 | 338 |  |  | No
25/07/2019 | 08:02 | OR25 | Urban | Planned |  | 41 | 338 |  |  | No
25/07/2019 | 08:11 | MR24 | Urban | Planned |  | 67 | 115 |  |  | No
25/07/2019 | 08:15 | MR22 | Urban | Planned |  | 80 | 195 |  |  | No
25/07/2019 | 08:24 | FSH33 | Urban | Planned |  | 244 | 305 |  |  | No
25/07/2019 | 08:36 | NW23 | Urban | Planned |  | 294 | 441 |  |  | No
25/07/2019 | 08:44 | FTN24 | Urban | Planned |  | 154 | 285 |  |  | No
25/07/2019 | 08:46 | DN6 | Urban | Planned |  | 90 | 283 |  |  | No
25/07/2019 | 10:00 | CRM13 | Urban | Planned |  | 1 | 150 |  |  | No
25/07/2019 | 10:00 | FTN12 | Urban | Planned |  | 82 | 150 |  |  | No
25/07/2019 | 17:30 | NP11 | Urban | Planned |  | 8 | 760 |  |  | No
26/07/2019 | 08:00 | RD10 | Urban | Planned |  | 73 | 259 |  |  | No
26/07/2019 | 08:01 | MGE21 | Urban | Planned |  | 12 | 162 |  |  | No
26/07/2019 | 08:15 | RWT34 | Urban | Planned |  | 41 | 425 |  |  | No
26/07/2019 | 08:30 | HGS23 | Rural Short | Planned |  | 16 | 240 |  |  | No
26/07/2019 | 08:30 | HGS31 | Rural Short | Planned |  | 3 | 180 |  |  | No
26/07/2019 | 08:30 | OAK35 | Urban | Planned |  | 46 | 250 |  |  | No
26/07/2019 | 08:40 | MTN32 | Rural Short | Planned |  | 1 | 355 |  |  | No
26/07/2019 | 09:00 | CRM14 | Urban | Planned |  | 73 | 226 |  |  | No
26/07/2019 | 09:12 | EL13 | Urban | Planned |  | 23 | 100 |  |  | No
26/07/2019 | 09:12 | EL5 | Urban | Planned |  | 1 | 100 |  |  | No
26/07/2019 | 09:12 | EL7 | Urban | Planned |  | 53 | 100 |  |  | No
26/07/2019 | 10:30 | EL5 | Urban | Planned |  | 21 | 330 |  |  | No
26/07/2019 | 10:47 | K2 | Urban | Planned |  | 92 | 113 |  |  | No
27/07/2019 | 06:40 | EM11 | Urban | Planned |  | 21 | 55 |  |  | No
27/07/2019 | 08:20 | BR6 | Urban | Planned |  | 123 | 229 |  |  | No
27/07/2019 | 09:30 | NO5 | Urban | Planned |  | 2 | 330 |  |  | No
28/07/2019 | 07:30 | EB21 | Urban | Planned |  | 3 | 510 |  |  | No
28/07/2019 | 07:30 | SR24 | Urban | Planned |  | 51 | 715 |  |  | No
28/07/2019 | 08:00 | HT13 | Urban | Planned |  | 14 | 405 |  |  | No
28/07/2019 | 08:00 | HT3 | Urban | Planned |  | 22 | 405 |  |  | No
28/07/2019 | 08:00 | OR23 | Urban | Planned |  | 75 | 510 |  |  | No
28/07/2019 | 08:03 | BT4 | Urban | Planned |  | 97 | 513 |  |  | No
28/07/2019 | 08:03 | BT6 | Urban | Planned |  | 83 | 513 |  |  | No
28/07/2019 | 08:05 | OR23 | Urban | Planned |  | 43 | 337 |  |  | No
28/07/2019 | 08:06 | DSH34 | Urban | Planned |  | 33 | 7 |  |  | No
28/07/2019 | 08:30 | EB11 | Urban | Planned |  | 27 | 420 |  |  | No
28/07/2019 | 08:30 | EB21 | Urban | Planned |  | 7 | 420 |  |  | No
29/07/2019 | 09:06 | MGE21 | Urban | Planned |  | 1 | 348 |  |  | No
29/07/2019 | 09:24 | CFD14 | Urban | Planned |  | 39 | 256 |  |  | No
29/07/2019 | 09:38 | HGS33 | Rural Short | Planned |  | 41 | 426 |  |  | No
29/07/2019 | 10:30 | FTN25 | Urban | Planned |  | 103 | 270 |  |  | No
30/07/2019 | 08:00 | FSH33 | Urban | Planned |  | 1 | 480 |  |  | No
30/07/2019 | 08:15 | HGS22 | Rural Short | Planned |  | 1 | 65 |  |  | No
30/07/2019 | 08:20 | BR4 | Urban | Planned |  | 35 | 385 |  |  | No
30/07/2019 | 08:30 | EL13 | Urban | Planned |  | 1 | 390 |  |  | No
30/07/2019 | 08:30 | FTN14 | Urban | Planned |  | 1 | 216 |  |  | No
30/07/2019 | 08:30 | LD6 | Urban | Planned |  | 51 | 105 |  |  | No
30/07/2019 | 08:30 | MGE12 | Urban | Planned |  | 86 | 465 |  |  | No
30/07/2019 | 08:40 | FSH13 | Urban | Planned |  | 6 | 180 |  |  | No
30/07/2019 | 08:40 | LD6 | Urban | Planned |  | 13 | 280 |  |  | No
30/07/2019 | 08:43 | FSH33 | Urban | Planned |  | 45 | 300 |  |  | No
30/07/2019 | 08:45 | GW11 | Urban | Planned |  | 4 | 435 |  |  | No
30/07/2019 | 09:00 | EL13 | Urban | Planned |  | 131 | 164 |  |  | No
30/07/2019 | 09:10 | FTN25 | Urban | Planned |  | 68 | 310 |  |  | No
30/07/2019 | 12:52 | FTN12 | Urban | Planned |  | 123 | 186 |  |  | No
31/07/2019 | 08:00 | BR4 | Urban | Planned |  | 37 | 450 |  |  | No
31/07/2019 | 08:00 | LWN21 | Rural Short | Planned |  | 1 | 480 |  |  | No
31/07/2019 | 08:05 | LWN21 | Rural Short | Planned |  | 41 | 298 |  |  | No
31/07/2019 | 08:13 | BR4 | Urban | Planned |  | 171 | 360 |  |  | No
31/07/2019 | 08:15 | FTN25 | Urban | Planned |  | 59 | 275 |  |  | No
31/07/2019 | 08:26 | MTN31 | Urban | Planned |  | 193 | 290 |  |  | No
31/07/2019 | 08:30 | NP33 | Urban | Planned |  | 40 | 300 |  |  | No
31/07/2019 | 08:35 | MR12 | Urban | Planned |  | 41 | 425 |  |  | No
31/07/2019 | 08:40 | LD6 | Urban | Planned |  | 30 | 290 |  |  | No
31/07/2019 | 09:08 | MGE32 | Urban | Planned |  | 68 | 237 |  |  | No
31/07/2019 | 09:25 | FTN23 | Urban | Planned |  | 108 | 95 |  |  | No
31/07/2019 | 09:45 | K10 | Urban | Planned |  | 16 | 225 |  |  | No
31/07/2019 | 09:45 | K6 | Urban | Planned |  | 47 | 225 |  |  | No
01/08/2019 | 07:30 | DC10 | Urban | Planned |  | 1 | 540 |  |  | No
01/08/2019 | 07:30 | LWN21 | Rural Short | Planned |  | 6 | 540 |  |  | No
01/08/2019 | 08:30 | RBD23 | Urban | Planned |  | 18 | 420 |  |  | No
01/08/2019 | 09:00 | LD6 | Urban | Planned |  | 43 | 300 |  |  | No
01/08/2019 | 09:00 | NW22 | Urban | Planned |  | 64 | 230 |  |  | No
01/08/2019 | 09:01 | LWN21 | Rural Short | Planned |  | 214 | 493 |  |  | No
01/08/2019 | 09:14 | EL13 | Urban | Planned |  | 19 | 217 |  |  | No
01/08/2019 | 09:23 | M35 | Urban | Planned |  | 23 | 425 |  |  | No
01/08/2019 | 09:25 | HT8 | Urban | Planned |  | 10 | 275 |  |  | No
01/08/2019 | 09:25 | HT9 | Urban | Planned |  | 1 | 275 |  |  | No
01/08/2019 | 09:36 | RBD23 | Urban | Planned |  | 185 | 366 |  |  | No
01/08/2019 | 09:38 | GW6 | Urban | Planned |  | 166 | 330 |  |  | No
01/08/2019 | 09:41 | CFD15 | Urban | Planned |  | 159 | 380 |  |  | No
01/08/2019 | 09:45 | DC1 | Urban | Planned |  | 122 | 360 |  |  | No
01/08/2019 | 10:05 | MR15 | Urban | Planned |  | 29 | 205 |  |  | No
01/08/2019 | 15:17 | DC10 | Urban | Planned |  | 135 | 1 |  |  | No
02/08/2019 | 08:02 | LWN33 | Urban | Planned |  | 64 | 303 |  |  | No
02/08/2019 | 08:10 | MC2 | Urban | Planned |  | 55 | 225 |  |  | No
02/08/2019 | 08:15 | DC1 | Urban | Planned |  | 9 | 355 |  |  | No
02/08/2019 | 08:30 | RBD23 | Urban | Planned |  | 19 | 125 |  |  | No
02/08/2019 | 08:30 | RBD23 | Urban | Planned |  | 103 | 180 |  |  | No
02/08/2019 | 08:30 | RBD23 | Urban | Planned |  | 1 | 420 |  |  | No
02/08/2019 | 09:24 | MGE23 | Urban | Planned |  | 33 | 322 |  |  | No
02/08/2019 | 10:25 | DSH31 | Urban | Planned |  | 2 | 255 |  |  | No
02/08/2019 | 10:35 | MC6 | Urban | Planned |  | 1 | 171 |  |  | No
02/08/2019 | 12:47 | NW23 | Urban | Planned |  | 24 | 161 |  |  | No
02/08/2019 | 14:16 | DC10 | Urban | Planned |  | 41 | 53 |  |  | No
03/08/2019 | 07:00 | DSH24 | Urban | Planned |  | 6 | 459.9 |  |  | No
03/08/2019 | 08:05 | MC10 | Urban | Planned |  | 1 | 412 |  |  | No
03/08/2019 | 12:05 | OE10 | Urban | Planned |  | 11 | 85 |  |  | No
04/08/2019 | 07:00 | BW23 | Urban | Planned |  | 13 | 645 |  |  | No
04/08/2019 | 08:01 | RBD24 | Urban | Planned |  | 115 | 434 |  |  | No
04/08/2019 | 08:04 | MC2 | Urban | Planned |  | 82 | 413 |  |  | No
04/08/2019 | 08:22 | BH11 | Urban | Planned |  | 51 | 343 |  |  | No
05/08/2019 | 08:40 | LWN21 | Rural Short | Planned |  | 2 | 150 |  |  | No
05/08/2019 | 09:00 | GW7 | Urban | Planned |  | 42 | 270 |  |  | No
06/08/2019 | 08:00 | HGS31 | Rural Short | Planned |  | 11 | 319 |  |  | No
06/08/2019 | 08:20 | LD2 | Urban | Planned |  | 296 | 290 |  |  | No
06/08/2019 | 08:30 | BT9 | Urban | Planned |  | 421 | 480 |  |  | No
06/08/2019 | 08:30 | DC10 | Urban | Planned |  | 111 | 260 |  |  | No
06/08/2019 | 08:30 | OR34 | Urban | Planned |  | 157 | 435 |  |  | No
06/08/2019 | 08:40 | LD5 | Urban | Planned |  | 35 | 300 |  |  | No
06/08/2019 | 10:53 | DVY24 | Rural Short | Planned |  | 1 | 31 |  |  | No
07/08/2019 | 08:00 | HT1 | Urban | Planned |  | 97 | 450 |  |  | No
07/08/2019 | 08:00 | MR13 | Urban | Planned |  | 286 | 370 |  |  | No
07/08/2019 | 08:00 | MR13 | Urban | Planned |  | 1 | 450 |  |  | No
07/08/2019 | 08:00 | OR33 | Urban | Planned |  | 86 | 510 |  |  | No
07/08/2019 | 08:01 | OR33 | Urban | Planned |  | 47 | 473 |  |  | No
07/08/2019 | 08:03 | EM1 | Urban | Planned |  | 65 | 396 |  |  | No
07/08/2019 | 08:10 | LWN33 | Urban | Planned |  | 49 | 230 |  |  | No
07/08/2019 | 08:30 | DC10 | Urban | Planned |  | 208 | 348.3 |  |  | No
07/08/2019 | 08:30 | DC10 | Urban | Planned |  | 2 | 450 |  |  | No
07/08/2019 | 13:00 | LWN33 | Urban | Planned |  | 125 | 90 |  |  | No
07/08/2019 | 20:40 | NO7 | Urban | Planned |  | 17 | 561 |  |  | No
08/08/2019 | 08:00 | EL11 | Urban | Planned |  | 24 | 435 |  |  | No
08/08/2019 | 08:00 | HT11 | Urban | Planned |  | 119 | 715 |  |  | No
08/08/2019 | 08:30 | NO7 | Urban | Planned |  | 37 | 370 |  |  | No
08/08/2019 | 08:30 | RBD23 | Urban | Planned |  | 138 | 325 |  |  | No
08/08/2019 | 09:12 | EB22 | Urban | Planned |  | 57 | 76 |  |  | No
08/08/2019 | 11:30 | GW11 | Urban | Planned |  | 31 | 212 |  |  | No
09/08/2019 | 07:00 | DVY22 | Urban | Planned |  | 1 | 3,570.0 |  |  | No
09/08/2019 | 08:00 | K13 | Urban | Planned |  | 5 | 420 |  |  | No
09/08/2019 | 08:45 | CFD13 | Urban | Planned |  | 44 | 180 |  |  | No
09/08/2019 | 08:50 | DC10 | Urban | Planned |  | 162 | 250 |  |  | No
09/08/2019 | 08:50 | K13 | Urban | Planned |  | 40 | 160 |  |  | No
09/08/2019 | 10:30 | K13 | Urban | Planned |  | 117 | 220 |  |  | No
10/08/2019 | 07:30 | BT2 | Urban | Planned |  | 1 | 300 |  |  | No
10/08/2019 | 08:00 | HT10 | Urban | Planned |  | 1 | 180 |  |  | No
10/08/2019 | 08:10 | BT2 | Urban | Planned |  | 29 | 190 |  |  | No
10/08/2019 | 09:25 | FSH33 | Urban | Planned |  | 161 | 370 |  |  | No
11/08/2019 | 07:30 | FTN23 | Urban | Planned |  | 2 | 540 |  |  | No
11/08/2019 | 08:10 | MTN21 | Urban | Planned |  | 24 | 290 |  |  | No
11/08/2019 | 08:15 | SR20 | Urban | Planned |  | 65 | 360 |  |  | No
11/08/2019 | 08:29 | FTN23 | Urban | Planned |  | 134 | 429 |  |  | No
11/08/2019 | 09:04 | HT7 | Urban | Planned |  | 81 | 258 |  |  | No
12/08/2019 | 08:30 | CFD22 | Urban | Planned |  | 93 | 80 |  |  | No
12/08/2019 | 08:30 | DC3 | Urban | Planned |  | 22 | 225 |  |  | No
12/08/2019 | 09:05 | K3 | Urban | Planned |  | 24 | 383 |  |  | No
13/08/2019 | 07:30 | K7 | Urban | Planned |  | 1 | 4,620.0 |  |  | No
13/08/2019 | 08:00 | CFD15 | Urban | Planned |  | 5 | 480 |  |  | No
13/08/2019 | 08:05 | DMA14 | Urban | Planned |  | 11 | 390 |  |  | No
13/08/2019 | 08:06 | DC1 | Urban | Planned |  | 83 | 442 |  |  | No
13/08/2019 | 08:15 | K8 | Urban | Planned |  | 103 | 450 |  |  | No
13/08/2019 | 08:20 | DC3 | Urban | Planned |  | 33 | 580 |  |  | No
13/08/2019 | 08:30 | CFD15 | Urban | Planned |  | 108 | 190 |  |  | No
13/08/2019 | 08:40 | NP23 | Urban | Planned |  | 12 | 360 |  |  | No
13/08/2019 | 09:00 | CDA24 | Urban | Planned |  | 39 | 150 |  |  | No
13/08/2019 | 09:25 | FSH21 | Rural Short | Planned |  | 3 | 100 |  |  | No
13/08/2019 | 09:50 | FTN23 | Urban | Planned |  | 1 | 120 |  |  | No
13/08/2019 | 09:50 | FTN24 | Urban | Planned |  | 71 | 120 |  |  | No
13/08/2019 | 11:15 | FSH34 | Urban | Planned |  | 135 | 225 |  |  | No
13/08/2019 | 21:36 | SVW41 | Urban | Planned |  | 147 | 481 |  |  | No
14/08/2019 | 08:00 | CDA21 | Urban | Planned |  | 109 | 265 |  |  | No
14/08/2019 | 08:03 | EB32 | Urban | Planned |  | 35 | 350 |  |  | No
14/08/2019 | 08:05 | DMA24 | Rural Short | Planned |  | 37 | 335 |  |  | No
14/08/2019 | 08:05 | FSH33 | Urban | Planned |  | 156 | 355 |  |  | No
14/08/2019 | 08:05 | M25 | Urban | Planned |  | 32 | 310 |  |  | No
14/08/2019 | 08:10 | EM8 | Urban | Planned |  | 60 | 240 |  |  | No
14/08/2019 | 08:20 | HGS23 | Rural Short | Planned |  | 9 | 25 |  |  | No
14/08/2019 | 08:20 | LWN33 | Urban | Planned |  | 29 | 150 |  |  | No
14/08/2019 | 08:30 | HT11 | Urban | Planned |  | 26 | 189 |  |  | No
14/08/2019 | 08:30 | HT2 | Urban | Planned |  | 129 | 189 |  |  | No
14/08/2019 | 08:33 | EB14 | Urban | Planned |  | 154 | 552 |  |  | No
14/08/2019 | 08:33 | EB24 | Urban | Planned |  | 172 | 552 |  |  | No
14/08/2019 | 08:45 | OAK26 | Urban | Planned |  | 94 | 375 |  |  | No
14/08/2019 | 08:45 | RBD13 | Urban | Planned |  | 43 | 325 |  |  | No
14/08/2019 | 08:45 | RBD22 | Urban | Planned |  | 3 | 325 |  |  | No
14/08/2019 | 08:55 | M32 | Urban | Planned |  | 12 | 155 |  |  | No
14/08/2019 | 09:00 | EM7 | Urban | Planned |  | 20 | 334 |  |  | No
14/08/2019 | 09:30 | FSH12 | Rural Short | Planned |  | 54 | 280 |  |  | No
14/08/2019 | 09:30 | HT1 | Urban | Planned |  | 20 | 165 |  |  | No
14/08/2019 | 09:50 | CFD15 | Urban | Planned |  | 64 | 475 |  |  | No
14/08/2019 | 10:05 | LWN21 | Rural Short | Planned |  | 12 | 25 |  |  | No
14/08/2019 | 11:00 | EW14 | Urban | Planned |  | 17 | 84 |  |  | No
15/08/2019 | 08:02 | SS23 | Urban | Planned |  | 80 | 92 |  |  | No
15/08/2019 | 08:05 | DC10 | Urban | Planned |  | 47 | 445 |  |  | No
15/08/2019 | 08:08 | EB32 | Urban | Planned |  | 73 | 412 |  |  | No
15/08/2019 | 08:08 | MR31 | Urban | Planned |  | 43 | 287 |  |  | No
15/08/2019 | 08:12 | NP14 | Urban | Planned |  | 11 | 120 |  |  | No
15/08/2019 | 08:15 | GW2 | Urban | Planned |  | 74 | 515 |  |  | No
15/08/2019 | 08:15 | GW7 | Urban | Planned |  | 26 | 515 |  |  | No
15/08/2019 | 08:15 | MGE21 | Urban | Planned |  | 66 | 515 |  |  | No
15/08/2019 | 08:28 | M21 | Urban | Planned |  | 23 | 267 |  |  | No
15/08/2019 | 08:58 | STO14 | Rural Short | Planned |  | 50 | 359 |  |  | No
15/08/2019 | 08:58 | STO21 | Rural Short | Planned |  | 34 | 359 |  |  | No
15/08/2019 | 09:50 | MGE21 | Urban | Planned |  | 75 | 95 |  |  | No
15/08/2019 | 21:30 | SVW54 | Urban | Planned |  | 5 | 345 |  |  | No
16/08/2019 | 08:04 | EB12 | Urban | Planned |  | 24 | 306 |  |  | No
16/08/2019 | 08:04 | EB22 | Urban | Planned |  | 43 | 306 |  |  | No
16/08/2019 | 08:05 | BT15 | Urban | Planned |  | 19 | 485 |  |  | No
16/08/2019 | 08:05 | FSH31 | Urban | Planned |  | 94 | 460 |  |  | No
16/08/2019 | 08:05 | SS14 | Urban | Planned |  | 91 | 286 |  |  | No
16/08/2019 | 08:05 | SS23 | Urban | Planned |  | 31 | 286 |  |  | No
16/08/2019 | 08:32 | LD6 | Urban | Planned |  | 51 | 203 |  |  | No
16/08/2019 | 08:35 | HGS21 | Rural Short | Planned |  | 3 | 70 |  |  | No
16/08/2019 | 08:36 | MGE22 | Urban | Planned |  | 59 | 288 |  |  | No
16/08/2019 | 08:44 | EM9 | Urban | Planned |  | 124 | 234 |  |  | No
16/08/2019 | 09:00 | DC10 | Urban | Planned |  | 10 | 355 |  |  | No
16/08/2019 | 09:04 | MR12 | Urban | Planned |  | 83 | 330 |  |  | No
16/08/2019 | 09:04 | MR13 | Urban | Planned |  | 60 | 330 |  |  | No
16/08/2019 | 09:10 | LD33 | Urban | Planned |  | 59 | 220 |  |  | No
16/08/2019 | 10:10 | DMA15 | Rural Short | Planned |  | 4 | 30 |  |  | No
16/08/2019 | 12:10 | MTN32 | Rural Short | Planned |  | 4 | 105 |  |  | No
17/08/2019 | 07:00 | CDA22 | Urban | Planned |  | 45 | 540 |  |  | No
17/08/2019 | 07:30 | FTN23 | Urban | Planned |  | 1 | 451 |  |  | No
17/08/2019 | 07:30 | FTN23 | Urban | Planned |  | 216 | 480 |  |  | No
17/08/2019 | 08:02 | OAK22 | Urban | Planned |  | 55 | 442 |  |  | No
17/08/2019 | 08:02 | OE14 | Urban | Planned |  | 16 | 442 |  |  | No
17/08/2019 | 20:30 | DN11 | Urban | Planned |  | 117 | 600 |  |  | No
17/08/2019 | 20:30 | LD7 | Urban | Planned |  | 121 | 600 |  |  | No
18/08/2019 | 08:14 | HT7 | Urban | Planned |  | 56 | 795 |  |  | No
18/08/2019 | 08:17 | CDA24 | Urban | Planned |  | 19 | 237 |  |  | No
18/08/2019 | 08:18 | NO3 | Urban | Planned |  | 14 | 180 |  |  | No
19/08/2019 | 07:25 | DVY24 | Rural Short | Planned |  | 2 | 640 |  |  | No
19/08/2019 | 08:06 | RWT34 | Urban | Planned |  | 41 | 505 |  |  | No
19/08/2019 | 20:41 | OR33 | Urban | Planned |  | 20 | 151 |  |  | No
20/08/2019 | 07:00 | SV14 | Urban | Planned |  | 1 | 1,500.0 |  |  | No
20/08/2019 | 07:16 | EW9 | Urban | Planned |  | 11 | 305 |  |  | No
20/08/2019 | 07:57 | DSH34 | Urban | Planned |  | 93 | 458 |  |  | No
20/08/2019 | 08:10 | EB31 | Urban | Planned |  | 16 | 60 |  |  | No
20/08/2019 | 08:15 | DC10 | Urban | Planned |  | 87 | 320 |  |  | No
20/08/2019 | 08:25 | M21 | Urban | Planned |  | 52 | 230 |  |  | No
20/08/2019 | 08:40 | EW12 | Urban | Planned |  | 208 | 138 |  |  | No
20/08/2019 | 08:40 | MGE34 | Urban | Planned |  | 37 | 195 |  |  | No
20/08/2019 | 08:45 | KBH34 | Urban | Planned |  | 3 | 90 |  |  | No
20/08/2019 | 09:00 | BW21 | Urban | Planned |  | 1 | 110 |  |  | No
20/08/2019 | 09:40 | EM5 | Urban | Planned |  | 1 | 118 |  |  | No
20/08/2019 | 09:55 | MTN23 | Urban | Planned |  | 27 | 90 |  |  | No
20/08/2019 | 10:20 | BC12 | Urban | Planned |  | 11 | 175 |  |  | No
20/08/2019 | 10:20 | BC23 | Urban | Planned |  | 30 | 175 |  |  | No
20/08/2019 | 11:43 | CDA22 | Urban | Planned |  | 2 | 87 |  |  | No
20/08/2019 | 14:10 | EM10 | Urban | Planned |  | 2 | 50 |  |  | No
20/08/2019 | 21:30 | SV14 | Urban | Planned |  | 13 | 385 |  |  | No
20/08/2019 | 21:30 | SVW41 | Urban | Planned |  | 1 | 385 |  |  | No
21/08/2019 | 07:30 | MR31 | Urban | Planned |  | 3 | 360 |  |  | No
21/08/2019 | 07:38 | MTN21 | Urban | Planned |  | 35 | 252 |  |  | No
21/08/2019 | 08:00 | LD32 | Urban | Planned |  | 190 | 225 |  |  | No
21/08/2019 | 08:00 | MTN24 | Rural Short | Planned |  | 1 | 480 |  |  | No
21/08/2019 | 08:02 | MGE31 | Urban | Planned |  | 26 | 453 |  |  | No
21/08/2019 | 08:10 | CRM21 | Urban | Planned |  | 5 | 44 |  |  | No
21/08/2019 | 08:10 | DC10 | Urban | Planned |  | 147 | 305 |  |  | No
21/08/2019 | 08:10 | NO7 | Urban | Planned |  | 19 | 205 |  |  | No
21/08/2019 | 08:19 | MTN24 | Rural Short | Planned |  | 40 | 347 |  |  | No
21/08/2019 | 08:30 | SVW41 | Urban | Planned |  | 43 | 420 |  |  | No
21/08/2019 | 08:44 | EW14 | Urban | Planned |  | 76 | 194 |  |  | No
21/08/2019 | 08:50 | NW22 | Urban | Planned |  | 64 | 190 |  |  | No
21/08/2019 | 08:50 | STO13 | Urban | Planned |  | 65 | 380 |  |  | No
21/08/2019 | 09:03 | HGS21 | Rural Short | Planned |  | 245 | 69 |  |  | No
21/08/2019 | 09:55 | HGS21 | Rural Short | Planned |  | 3 | 81 |  |  | No
21/08/2019 | 10:49 | HGS21 | Rural Short | Planned |  | 2 | 66 |  |  | No
21/08/2019 | 13:15 | EW14 | Urban | Planned |  | 80 | 130 |  |  | No
21/08/2019 | 13:15 | EW2 | Urban | Planned |  | 113 | 130 |  |  | No
22/08/2019 | 07:55 | LWN34 | Urban | Planned |  | 18 | 185 |  |  | No
22/08/2019 | 08:00 | EB32 | Urban | Planned |  | 59 | 445 |  |  | No
22/08/2019 | 08:00 | EB32 | Urban | Planned |  | 1 | 510 |  |  | No
22/08/2019 | 08:00 | NP16 | Urban | Planned |  | 155 | 195 |  |  | No
22/08/2019 | 08:09 | SS14 | Urban | Planned |  | 183 | 348 |  |  | No
22/08/2019 | 08:14 | BW34 | Urban | Planned |  | 53 | 252 |  |  | No
22/08/2019 | 08:24 | LWN24 | Urban | Planned |  | 224 | 170 |  |  | No
22/08/2019 | 08:25 | SS14 | Urban | Planned |  | 258 | 324 |  |  | No
22/08/2019 | 08:30 | EM10 | Urban | Planned |  | 113 | 330 |  |  | No
22/08/2019 | 08:30 | STO13 | Urban | Planned |  | 9 | 260 |  |  | No
22/08/2019 | 08:42 | M33 | Urban | Planned |  | 16 | 109 |  |  | No
22/08/2019 | 08:45 | M25 | Urban | Planned |  | 115 | 180 |  |  | No
22/08/2019 | 09:05 | MTN32 | Rural Short | Planned |  | 45 | 341 |  |  | No
22/08/2019 | 09:15 | EL13 | Urban | Planned |  | 32 | 340 |  |  | No
22/08/2019 | 10:10 | HGS21 | Rural Short | Planned |  | 3 | 125 |  |  | No
22/08/2019 | 10:35 | DMA23 | Rural Short | Planned |  | 1 | 17 |  |  | No
23/08/2019 | 08:00 | EM6 | Urban | Planned |  | 70 | 90 |  |  | No
23/08/2019 | 08:00 | MR12 | Urban | Planned |  | 1 | 450 |  |  | No
23/08/2019 | 08:05 | LWN21 | Rural Short | Planned |  | 121 | 335 |  |  | No
23/08/2019 | 08:06 | BW34 | Urban | Planned |  | 70 | 359 |  |  | No
23/08/2019 | 08:15 | MR12 | Urban | Planned |  | 125 | 160 |  |  | No
23/08/2019 | 08:24 | OR23 | Urban | Planned |  | 8 | 246 |  |  | No
23/08/2019 | 08:35 | M33 | Urban | Planned |  | 66 | 205 |  |  | No
23/08/2019 | 08:45 | NW21 | Urban | Planned |  | 9 | 230 |  |  | No
23/08/2019 | 08:54 | MTN32 | Rural Short | Planned |  | 1 | 345 |  |  | No
23/08/2019 | 08:59 | DC2 | Urban | Planned |  | 22 | 18 |  |  | No
23/08/2019 | 09:00 | CFD14 | Urban | Planned |  | 118 | 340 |  |  | No
23/08/2019 | 12:40 | HGS22 | Rural Short | Planned |  | 1 | 115 |  |  | No
24/08/2019 | 08:10 | MTN22 | Rural Short | Planned |  | 45 | 405 |  |  | No
25/08/2019 | 05:00 | FTN23 | Urban | Planned |  | 1 | 120 |  |  | No
25/08/2019 | 05:50 | FTN23 | Urban | Planned |  | 5 | 9 |  |  | No
25/08/2019 | 07:00 | KBH34 | Urban | Planned |  | 5 | 240 |  |  | No
25/08/2019 | 07:30 | EB11 | Urban | Planned |  | 35 | 570 |  |  | No
25/08/2019 | 07:30 | K2 | Urban | Planned |  | 140 | 660 |  |  | No
25/08/2019 | 07:30 | SS21 | Urban | Planned |  | 3 | 540 |  |  | No
25/08/2019 | 07:30 | DSH33 | Urban | Planned |  | 2 | 180 |  |  | No
25/08/2019 | 07:37 | SS21 | Urban | Planned |  | 135 | 331 |  |  | No
25/08/2019 | 07:45 | DN24 | Urban | Planned |  | 2 | 540 |  |  | No
25/08/2019 | 08:00 | EB12 | Urban | Planned |  | 145 | 248 |  |  | No
25/08/2019 | 12:40 | EB32 | Urban | Planned |  | 102 | 162 |  |  | No
26/08/2019 | 08:25 | SS12 | Urban | Planned |  | 10 | 243 |  |  | No
26/08/2019 | 08:30 | GW7 | Urban | Planned |  | 96 | 360 |  |  | No
26/08/2019 | 08:30 | MTN32 | Rural Short | Planned |  | 2 | 87 |  |  | No
26/08/2019 | 09:00 | CRM33 | Urban | Planned |  | 19 | 225 |  |  | No
26/08/2019 | 09:02 | CRM21 | Urban | Planned |  | 8 | 403 |  |  | No
26/08/2019 | 09:15 | EM5 | Urban | Planned |  | 43 | 140 |  |  | No
26/08/2019 | 11:50 | MTN32 | Rural Short | Planned |  | 2 | 180 |  |  | No
26/08/2019 | 13:15 | OAK26 | Urban | Planned |  | 112 | 105 |  |  | No
27/08/2019 | 07:34 | LD1 | Urban | Planned |  | 220 | 373 |  |  | No
27/08/2019 | 08:02 | LD3 | Urban | Planned |  | 107 | 277 |  |  | No
27/08/2019 | 08:10 | DMA23 | Rural Short | Planned |  | 33 | 615 |  |  | No
27/08/2019 | 08:16 | BT2 | Urban | Planned |  | 15 | 341 |  |  | No
27/08/2019 | 08:20 | M33 | Urban | Planned |  | 66 | 205 |  |  | No
27/08/2019 | 08:34 | M33 | Urban | Planned |  | 12 | 297 |  |  | No
27/08/2019 | 08:40 | NO32 | Urban | Planned |  | 66 | 114 |  |  | No
27/08/2019 | 08:42 | BH34 | Urban | Planned |  | 20 | 216 |  |  | No
27/08/2019 | 08:52 | DMA23 | Rural Short | Planned |  | 80 | 321 |  |  | No
27/08/2019 | 09:00 | HGS33 | Rural Short | Planned |  | 26 | 192 |  |  | No
27/08/2019 | 09:05 | MGE31 | Urban | Planned |  | 113 | 452 |  |  | No
27/08/2019 | 09:42 | STO14 | Rural Short | Planned |  | 29 | 384 |  |  | No
27/08/2019 | 10:30 | FSH33 | Urban | Planned |  | 128 | 287 |  |  | No
27/08/2019 | 12:00 | EB14 | Urban | Planned |  | 54 | 60 |  |  | No
27/08/2019 | 21:30 | SVW41 | Urban | Planned |  | 1 | 540 |  |  | No
27/08/2019 | 21:30 | SVW54 | Urban | Planned |  | 1 | 540 |  |  | No
27/08/2019 | 21:31 | SVW41 | Urban | Planned |  | 190 | 477 |  |  | No
27/08/2019 | 21:31 | SVW54 | Urban | Planned |  | 40 | 477 |  |  | No
28/08/2019 | 08:00 | FSH12 | Rural Short | Planned |  | 2 | 480 |  |  | No
28/08/2019 | 08:00 | HGS22 | Rural Short | Planned |  | 90 | 255 |  |  | No
28/08/2019 | 08:00 | NP33 | Urban | Planned |  | 74 | 440 |  |  | No
28/08/2019 | 08:02 | DMA23 | Rural Short | Planned |  | 18 | 102 |  |  | No
28/08/2019 | 08:03 | BR13 | Urban | Planned |  | 38 | 372 |  |  | No
28/08/2019 | 08:20 | HT11 | Urban | Planned |  | 24 | 295 |  |  | No
28/08/2019 | 08:20 | HT2 | Urban | Planned |  | 150 | 295 |  |  | No
28/08/2019 | 08:30 | MTN35 | Rural Short | Planned |  | 12 | 150 |  |  | No
28/08/2019 | 09:09 | DC10 | Urban | Planned |  | 148 | 351 |  |  | No
28/08/2019 | 10:25 | CDA22 | Urban | Planned |  | 18 | 198 |  |  | No
29/08/2019 | 06:30 | EB24 | Urban | Planned |  | 1 | 780 |  |  | No
29/08/2019 | 07:00 | SV14 | Urban | Planned |  | 1 | 1,500.0 |  |  | No
29/08/2019 | 07:30 | MR33 | Urban | Planned |  | 1 | 1,920.0 |  |  | No
29/08/2019 | 08:00 | NP23 | Urban | Planned |  | 173 | 395 |  |  | No
29/08/2019 | 08:15 | KBH34 | Urban | Planned |  | 3 | 435 |  |  | No
29/08/2019 | 08:40 | SS13 | Urban | Planned |  | 61 | 118 |  |  | No
29/08/2019 | 08:45 | EM9 | Urban | Planned |  | 64 | 195 |  |  | No
29/08/2019 | 09:00 | EB14 | Urban | Planned |  | 157 | 630 |  |  | No
29/08/2019 | 09:00 | EB24 | Urban | Planned |  | 180 | 630 |  |  | No
29/08/2019 | 09:02 | HGS22 | Rural Short | Planned |  | 66 | 298 |  |  | No
29/08/2019 | 09:05 | RWT23 | Urban | Planned |  | 10 | 90 |  |  | No
29/08/2019 | 09:06 | HGS31 | Rural Short | Planned |  | 66 | 347 |  |  | No
29/08/2019 | 09:18 | FSH13 | Urban | Planned |  | 58 | 395 |  |  | No
29/08/2019 | 09:30 | MR32 | Urban | Planned |  | 87 | 170 |  |  | No
29/08/2019 | 09:31 | DMA15 | Rural Short | Planned |  | 14 | 254 |  |  | No
29/08/2019 | 09:31 | DMA24 | Rural Short | Planned |  | 5 | 254 |  |  | No
29/08/2019 | 09:59 | STO14 | Rural Short | Planned |  | 216 | 423 |  |  | No
29/08/2019 | 21:00 | SV14 | Urban | Planned |  | 14 | 400 |  |  | No
29/08/2019 | 21:00 | SVW41 | Urban | Planned |  | 190 | 400 |  |  | No
29/08/2019 | 21:00 | SVW41 | Urban | Planned |  | 3 | 570 |  |  | No
29/08/2019 | 21:00 | SVW54 | Urban | Planned |  | 38 | 400 |  |  | No
30/08/2019 | 08:06 | EL8 | Urban | Planned |  | 11 | 518 |  |  | No
30/08/2019 | 08:07 | M35 | Urban | Planned |  | 41 | 128 |  |  | No
30/08/2019 | 08:30 | MTN32 | Rural Short | Planned |  | 4 | 420 |  |  | No
30/08/2019 | 08:36 | LD2 | Urban | Planned |  | 19 | 194 |  |  | No
30/08/2019 | 08:50 | DMA13 | Rural Short | Planned |  | 130 | 150 |  |  | No
30/08/2019 | 09:03 | CRM14 | Urban | Planned |  | 69 | 131 |  |  | No
30/08/2019 | 09:20 | BR1 | Urban | Planned |  | 26 | 280 |  |  | No
30/08/2019 | 09:20 | BR15 | Urban | Planned |  | 42 | 280 |  |  | No
30/08/2019 | 09:35 | DC10 | Urban | Planned |  | 42 | 138 |  |  | No
30/08/2019 | 09:40 | MTN21 | Urban | Planned |  | 246 | 350 |  |  | No
30/08/2019 | 09:55 | LWN21 | Rural Short | Planned |  | 3 | 136 |  |  | No
30/08/2019 | 09:58 | CDA22 | Urban | Planned |  | 26 | 187 |  |  | No
30/08/2019 | 11:30 | LWN21 | Rural Short | Planned |  | 4 | 60 |  |  | No
30/08/2019 | 13:05 | MTN32 | Rural Short | Planned |  | 2 | 40 |  |  | No
31/08/2019 | 07:00 | HT7 | Urban | Planned |  | 2 | 300 |  |  | No
31/08/2019 | 07:04 | HT13 | Urban | Planned |  | 21 | 263 |  |  | No
31/08/2019 | 07:15 | NO3 | Urban | Planned |  | 24 | 305 |  |  | No
31/08/2019 | 08:10 | CDA24 | Urban | Planned |  | 63 | 108 |  |  | No
31/08/2019 | 08:15 | CRM21 | Urban | Planned |  | 7 | 218 |  |  | No
31/08/2019 | 08:23 | SS12 | Urban | Planned |  | 30 | 205 |  |  | No
31/08/2019 | 08:30 | CM13 | Urban | Planned |  | 33 | 300 |  |  | No
31/08/2019 | 08:30 | M32 | Urban | Planned |  | 6 | 300 |  |  | No
31/08/2019 | 08:32 | M21 | Urban | Planned |  | 206 | 362 |  |  | No
31/08/2019 | 08:32 | M34 | Urban | Planned |  | 13 | 362 |  |  | No
01/09/2019 | 08:03 | OR24 | Urban | Planned |  | 24 | 642 |  |  | No
01/09/2019 | 08:09 | EM6 | Urban | Planned |  | 11 | 437 |  |  | No
01/09/2019 | 08:09 | K13 | Urban | Planned |  | 47 | 437 |  |  | No
01/09/2019 | 08:30 | RD4 | Urban | Planned |  | 11 | 300 |  |  | No
01/09/2019 | 09:03 | DN6 | Urban | Planned |  | 262 | 102 |  |  | No
02/09/2019 | 09:15 | M11 | Urban | Planned |  | 78 | 315 |  |  | No
02/09/2019 | 10:03 | HGS31 | Rural Short | Planned |  | 119 | 206 |  |  | No
03/09/2019 | 08:00 | SR15 | Urban | Planned |  | 165 | 460 |  |  | No
03/09/2019 | 08:15 | FSH12 | Rural Short | Planned |  | 194 | 315 |  |  | No
03/09/2019 | 08:15 | HGS31 | Rural Short | Planned |  | 10 | 335 |  |  | No
03/09/2019 | 08:23 | HT1 | Urban | Planned |  | 102 | 159 |  |  | No
03/09/2019 | 08:37 | RWT34 | Urban | Planned |  | 41 | 403 |  |  | No
03/09/2019 | 08:50 | BU10 | Urban | Planned |  | 3 | 300 |  |  | No
03/09/2019 | 08:54 | NB32 | Urban | Planned |  | 27 | 120 |  |  | No
03/09/2019 | 09:15 | M12 | Urban | Planned |  | 141 | 80 |  |  | No
03/09/2019 | 11:18 | NW14 | Urban | Planned |  | 1 | 182 |  |  | No
04/09/2019 | 08:00 | HGS23 | Rural Short | Planned |  | 1 | 480 |  |  | No
04/09/2019 | 08:02 | STO13 | Urban | Planned |  | 3 | 228 |  |  | No
04/09/2019 | 08:05 | DMA14 | Urban | Planned |  | 38 | 385 |  |  | No
04/09/2019 | 08:10 | SR13 | Urban | Planned |  | 84 | 205 |  |  | No
04/09/2019 | 08:12 | HGS23 | Rural Short | Planned |  | 368 | 320 |  |  | No
04/09/2019 | 08:15 | M25 | Urban | Planned |  | 224 | 360 |  |  | No
04/09/2019 | 08:25 | SR13 | Urban | Planned |  | 38 | 185 |  |  | No
04/09/2019 | 08:30 | DMA15 | Rural Short | Planned |  | 32 | 400 |  |  | No
04/09/2019 | 08:30 | DMA15 | Rural Short | Planned |  | 1 | 420 |  |  | No
04/09/2019 | 08:30 | SS11 | Urban | Planned |  | 141 | 300 |  |  | No
04/09/2019 | 08:40 | LD5 | Urban | Planned |  | 30 | 320 |  |  | No
04/09/2019 | 09:00 | DC10 | Urban | Planned |  | 42 | 210 |  |  | No
04/09/2019 | 09:20 | HT11 | Urban | Planned |  | 48 | 281 |  |  | No
04/09/2019 | 09:31 | MR15 | Urban | Planned |  | 226 | 325 |  |  | No
04/09/2019 | 09:45 | RBD21 | Rural Short | Planned |  | 2 | 65 |  |  | No
04/09/2019 | 09:45 | RWT12 | Urban | Planned |  | 10 | 115 |  |  | No
04/09/2019 | 12:40 | RBD21 | Rural Short | Planned |  | 88 | 83 |  |  | No
04/09/2019 | 13:15 | FTN13 | Urban | Planned |  | 76 | 159 |  |  | No
05/09/2019 | 08:00 | LD2 | Urban | Planned |  | 49 | 420 |  |  | No
05/09/2019 | 08:00 | LD33 | Urban | Planned |  | 236 | 420 |  |  | No
05/09/2019 | 08:00 | M11 | Urban | Planned |  | 150 | 480 |  |  | No
05/09/2019 | 08:00 | M34 | Urban | Planned |  | 113 | 480 |  |  | No
05/09/2019 | 08:00 | EB22 | Urban | Planned |  | 74 | 480 |  |  | No
05/09/2019 | 08:00 | SV16 | Urban | Planned |  | 27 | 480 |  |  | No
05/09/2019 | 08:10 | LWN21 | Rural Short | Planned |  | 29 | 80 |  |  | No
05/09/2019 | 08:15 | NP36 | Urban | Planned |  | 3 | 425 |  |  | No
05/09/2019 | 08:30 | DC10 | Urban | Planned |  | 58 | 390 |  |  | No
05/09/2019 | 08:30 | RBD21 | Rural Short | Planned |  | 3 | 300 |  |  | No
05/09/2019 | 08:32 | MR33 | Urban | Planned |  | 31 | 110 |  |  | No
05/09/2019 | 08:35 | DMA23 | Rural Short | Planned |  | 6 | 145 |  |  | No
05/09/2019 | 09:05 | DC10 | Urban | Planned |  | 39 | 290 |  |  | No
05/09/2019 | 10:15 | LD33 | Urban | Planned |  | 99 | 515 |  |  | No
06/09/2019 | 08:00 | MGE21 | Urban | Planned |  | 144 | 525 |  |  | No
06/09/2019 | 08:15 | RBD12 | Rural Short | Planned |  | 53 | 250 |  |  | No
06/09/2019 | 08:27 | NP16 | Urban | Planned |  | 142 | 243 |  |  | No
06/09/2019 | 08:30 | CRM21 | Urban | Planned |  | 4 | 360 |  |  | No
06/09/2019 | 08:40 | BT15 | Urban | Planned |  | 25 | 390 |  |  | No
06/09/2019 | 08:44 | HGS23 | Rural Short | Planned |  | 1 | 38 |  |  | No
06/09/2019 | 09:14 | GW2 | Urban | Planned |  | 141 | 283 |  |  | No
06/09/2019 | 09:55 | HGS21 | Rural Short | Planned |  | 16 | 190 |  |  | No
06/09/2019 | 11:55 | HGS23 | Rural Short | Planned |  | 5 | 50 |  |  | No
07/09/2019 | 08:00 | M33 | Urban | Planned |  | 23 | 215 |  |  | No
07/09/2019 | 08:00 | M34 | Urban | Planned |  | 33 | 215 |  |  | No
08/09/2019 | 07:40 | MR33 | Urban | Planned |  | 4 | 365 |  |  | No
08/09/2019 | 07:56 | DC10 | Urban | Planned |  | 31 | 403 |  |  | No
08/09/2019 | 08:00 | CDA22 | Urban | Planned |  | 183 | 450 |  |  | No
08/09/2019 | 08:00 | MR12 | Urban | Planned |  | 36 | 360 |  |  | No
08/09/2019 | 08:00 | OE5 | Urban | Planned |  | 11 | 510 |  |  | No
08/09/2019 | 08:40 | RBD22 | Urban | Planned |  | 35 | 90 |  |  | No
08/09/2019 | 11:30 | DMA15 | Rural Short | Planned |  | 5 | 60 |  |  | No
09/09/2019 | 07:30 | MTN22 | Rural Short | Planned |  | 1 | 540 |  |  | No
09/09/2019 | 07:45 | MTN22 | Rural Short | Planned |  | 45 | 450 |  |  | No
09/09/2019 | 08:00 | EM9 | Urban | Planned |  | 112 | 419.1 |  |  | No
09/09/2019 | 08:22 | SS22 | Urban | Planned |  | 93 | 243 |  |  | No
09/09/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 2 | 240 |  |  | No
09/09/2019 | 09:17 | HGS31 | Rural Short | Planned |  | 35 | 266 |  |  | No
09/09/2019 | 09:30 | DMA23 | Rural Short | Planned |  | 2 | 330 |  |  | No
09/09/2019 | 10:30 | DMA23 | Rural Short | Planned |  | 1 | 180 |  |  | No
10/09/2019 | 08:00 | CDA24 | Urban | Planned |  | 1 | 480 |  |  | No
10/09/2019 | 08:00 | DMA23 | Rural Short | Planned |  | 183 | 410 |  |  | No
10/09/2019 | 08:00 | MGE34 | Urban | Planned |  | 31 | 329.4 |  |  | No
10/09/2019 | 08:05 | DC10 | Urban | Planned |  | 62 | 367 |  |  | No
10/09/2019 | 08:10 | HT1 | Urban | Planned |  | 62 | 335 |  |  | No
10/09/2019 | 08:20 | CDA24 | Urban | Planned |  | 140 | 240 |  |  | No
10/09/2019 | 08:45 | STO13 | Urban | Planned |  | 10 | 225 |  |  | No
10/09/2019 | 09:00 | DMA15 | Rural Short | Planned |  | 18 | 345 |  |  | No
10/09/2019 | 09:11 | EB21 | Urban | Planned |  | 33 | 245 |  |  | No
10/09/2019 | 09:11 | EB24 | Urban | Planned |  | 26 | 245 |  |  | No
10/09/2019 | 09:30 | MGE21 | Urban | Planned |  | 29 | 205 |  |  | No
10/09/2019 | 09:55 | RBD23 | Urban | Planned |  | 147 | 286 |  |  | No
11/09/2019 | 08:00 | RBD12 | Rural Short | Planned |  | 25 | 275 |  |  | No
11/09/2019 | 08:00 | RBD12 | Rural Short | Planned |  | 1 | 510 |  |  | No
11/09/2019 | 08:30 | RBD13 | Urban | Planned |  | 40 | 405 |  |  | No
11/09/2019 | 08:40 | DMA23 | Rural Short | Planned |  | 29 | 320 |  |  | No
11/09/2019 | 08:50 | HT1 | Urban | Planned |  | 17 | 260 |  |  | No
11/09/2019 | 09:31 | HGS32 | Urban | Planned |  | 7 | 203 |  |  | No
11/09/2019 | 10:00 | OAK35 | Urban | Planned |  | 3 | 240 |  |  | No
11/09/2019 | 10:10 | FSH23 | Rural Short | Planned |  | 14 | 25 |  |  | No
11/09/2019 | 11:00 | FSH32 | Rural Short | Planned |  | 1 | 300 |  |  | No
11/09/2019 | 11:20 | FSH32 | Rural Short | Planned |  | 55 | 65 |  |  | No
11/09/2019 | 14:30 | DMA23 | Rural Short | Planned |  | 1 | 25 |  |  | No
12/09/2019 | 08:00 | CRM21 | Urban | Planned |  | 9 | 95 |  |  | No
12/09/2019 | 08:00 | EM8 | Urban | Planned |  | 154 | 405 |  |  | No
12/09/2019 | 08:00 | EM8 | Urban | Planned |  | 1 | 480 |  |  | No
12/09/2019 | 08:00 | OAK22 | Urban | Planned |  | 4 | 525 |  |  | No
12/09/2019 | 09:54 | DMA23 | Rural Short | Planned |  | 3 | 89 |  |  | No
13/09/2019 | 07:30 | STO13 | Urban | Planned |  | 1 | 540 |  |  | No
13/09/2019 | 08:00 | GW2 | Urban | Planned |  | 25 | 315 |  |  | No
13/09/2019 | 08:00 | GW7 | Urban | Planned |  | 1 | 315 |  |  | No
13/09/2019 | 08:00 | HGS33 | Rural Short | Planned |  | 1 | 150 |  |  | No
13/09/2019 | 08:00 | MTN23 | Urban | Planned |  | 15 | 150 |  |  | No
13/09/2019 | 08:02 | LD6 | Urban | Planned |  | 24 | 102 |  |  | No
13/09/2019 | 08:05 | MTN32 | Rural Short | Planned |  | 2 | 110 |  |  | No
13/09/2019 | 08:10 | HGS33 | Rural Short | Planned |  | 46 | 52 |  |  | No
13/09/2019 | 08:10 | OR32 | Urban | Planned |  | 83 | 85 |  |  | No
13/09/2019 | 08:20 | BU14 | Urban | Planned |  | 12 | 250 |  |  | No
13/09/2019 | 08:30 | CFD13 | Urban | Planned |  | 46 | 280 |  |  | No
13/09/2019 | 08:30 | NP24 | Urban | Planned |  | 49 | 160 |  |  | No
13/09/2019 | 09:27 | FSH32 | Rural Short | Planned |  | 32 | 45 |  |  | No
13/09/2019 | 10:30 | LWN21 | Rural Short | Planned |  | 6 | 20 |  |  | No
13/09/2019 | 12:40 | GW12 | Urban | Planned |  | 20 | 135 |  |  | No
13/09/2019 | 13:30 | HGS33 | Rural Short | Planned |  | 13 | 122 |  |  | No
14/09/2019 | 08:00 | DMA13 | Rural Short | Planned |  | 15 | 320 |  |  | No
14/09/2019 | 08:00 | HT7 | Urban | Planned |  | 1 | 450 |  |  | No
14/09/2019 | 08:53 | HT7 | Urban | Planned |  | 40 | 242 |  |  | No
14/09/2019 | 09:10 | CRM14 | Urban | Planned |  | 3 | 90 |  |  | No
14/09/2019 | 10:00 | LD4 | Urban | Planned |  | 1 | 135 |  |  | No
14/09/2019 | 13:15 | BU1 | Urban | Planned |  | 53 | 75 |  |  | No
14/09/2019 | 13:58 | DMA15 | Rural Short | Planned |  | 61 | 75 |  |  | No
14/09/2019 | 13:58 | DMA24 | Rural Short | Planned |  | 5 | 75 |  |  | No
14/09/2019 | 14:15 | MC4 | Urban | Planned |  | 19 | 120 |  |  | No
15/09/2019 | 07:50 | NO4 | Urban | Planned |  | 120 | 183 |  |  | No
15/09/2019 | 07:51 | BW21 | Urban | Planned |  | 60 | 378 |  |  | No
15/09/2019 | 08:00 | CFD15 | Urban | Planned |  | 143 | 756 |  |  | No
15/09/2019 | 08:02 | CRM14 | Urban | Planned |  | 20 | 482 |  |  | No
15/09/2019 | 08:10 | M34 | Urban | Planned |  | 33 | 270 |  |  | No
15/09/2019 | 08:23 | OAK34 | Urban | Planned |  | 6 | 343 |  |  | No
15/09/2019 | 08:30 | FSH13 | Urban | Planned |  | 1 | 420 |  |  | No
15/09/2019 | 08:30 | FTN23 | Urban | Planned |  | 218 | 285 |  |  | No
15/09/2019 | 08:30 | FTN23 | Urban | Planned |  | 2 | 420 |  |  | No
15/09/2019 | 08:35 | FSH13 | Urban | Planned |  | 177 | 138 |  |  | No
16/09/2019 | 09:06 | MTN32 | Rural Short | Planned |  | 5 | 129 |  |  | No
16/09/2019 | 09:30 | DN22 | Urban | Planned |  | 76 | 270 |  |  | No
17/09/2019 | 08:00 | DMA15 | Rural Short | Planned |  | 1 | 510 |  |  | No
17/09/2019 | 08:00 | M25 | Urban | Planned |  | 1 | 450 |  |  | No
17/09/2019 | 08:03 | LD2 | Urban | Planned |  | 92 | 363 |  |  | No
17/09/2019 | 08:04 | OR32 | Urban | Planned |  | 37 | 321 |  |  | No
17/09/2019 | 08:30 | FSH34 | Urban | Planned |  | 89 | 285 |  |  | No
17/09/2019 | 08:30 | M22 | Urban | Planned |  | 23 | 270 |  |  | No
17/09/2019 | 08:30 | M25 | Urban | Planned |  | 91 | 270 |  |  | No
17/09/2019 | 09:06 | FSH13 | Urban | Planned |  | 152 | 409 |  |  | No
17/09/2019 | 09:09 | NW11 | Urban | Planned |  | 165 | 416 |  |  | No
17/09/2019 | 09:23 | LWN21 | Rural Short | Planned |  | 60 | 202 |  |  | No
17/09/2019 | 09:25 | M22 | Urban | Planned |  | 30 | 300 |  |  | No
17/09/2019 | 09:25 | M23 | Urban | Planned |  | 69 | 300 |  |  | No
17/09/2019 | 09:30 | LWN21 | Rural Short | Planned |  | 6 | 210 |  |  | No
17/09/2019 | 09:44 | DC10 | Urban | Planned |  | 79 | 206 |  |  | No
17/09/2019 | 09:48 | HGS31 | Rural Short | Planned |  | 28 | 324 |  |  | No
17/09/2019 | 10:00 | K3 | Urban | Planned |  | 51 | 277 |  |  | No
17/09/2019 | 10:00 | K7 | Urban | Planned |  | 63 | 277 |  |  | No
17/09/2019 | 10:37 | DMA15 | Rural Short | Planned |  | 43 | 333 |  |  | No
17/09/2019 | 21:30 | FTN11 | Urban | Planned |  | 8 | 395 |  |  | No
17/09/2019 | 21:30 | FTN22 | Urban | Planned |  | 10 | 395 |  |  | No
18/09/2019 | 08:00 | EW3 | Urban | Planned |  | 260 | 525 |  |  | No
18/09/2019 | 08:00 | FSH32 | Rural Short | Planned |  | 2 | 130 |  |  | No
18/09/2019 | 08:00 | FSH32 | Rural Short | Planned |  | 1 | 480 |  |  | No
18/09/2019 | 08:00 | SR23 | Urban | Planned |  | 98 | 360 |  |  | No
18/09/2019 | 08:28 | LD6 | Urban | Planned |  | 22 | 208 |  |  | No
18/09/2019 | 08:40 | M35 | Urban | Planned |  | 34 | 420 |  |  | No
18/09/2019 | 08:42 | DC2 | Urban | Planned |  | 38 | 324 |  |  | No
18/09/2019 | 09:05 | STO23 | Urban | Planned |  | 4 | 170 |  |  | No
18/09/2019 | 09:49 | HGS31 | Rural Short | Planned |  | 65 | 273 |  |  | No
18/09/2019 | 10:26 | MR12 | Urban | Planned |  | 41 | 260 |  |  | No
18/09/2019 | 10:48 | DMA23 | Rural Short | Planned |  | 4 | 79 |  |  | No
19/09/2019 | 08:00 | HGS23 | Rural Short | Planned |  | 2 | 510 |  |  | No
19/09/2019 | 08:10 | GW8 | Urban | Planned |  | 71 | 175 |  |  | No
19/09/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 58 | 325 |  |  | No
19/09/2019 | 08:30 | HGS31 | Rural Short | Planned |  | 1 | 450 |  |  | No
19/09/2019 | 08:55 | HGS31 | Rural Short | Planned |  | 13 | 237 |  |  | No
19/09/2019 | 09:10 | BU2 | Urban | Planned |  | 55 | 90 |  |  | No
19/09/2019 | 09:18 | NP25 | Urban | Planned |  | 43 | 227 |  |  | No
19/09/2019 | 10:06 | HGS23 | Rural Short | Planned |  | 88 | 233 |  |  | No
19/09/2019 | 15:04 | MTN32 | Rural Short | Planned |  | 2 | 39 |  |  | No
20/09/2019 | 08:00 | MTN32 | Rural Short | Planned |  | 24 | 112 |  |  | No
20/09/2019 | 08:00 | MTN32 | Rural Short | Planned |  | 1 | 510 |  |  | No
20/09/2019 | 08:15 | DMA23 | Rural Short | Planned |  | 44 | 55 |  |  | No
20/09/2019 | 08:25 | MTN32 | Rural Short | Planned |  | 25 | 157 |  |  | No
20/09/2019 | 08:30 | EM6 | Urban | Planned |  | 38 | 300 |  |  | No
20/09/2019 | 08:30 | HGS31 | Rural Short | Planned |  | 1 | 480 |  |  | No
20/09/2019 | 08:30 | STO21 | Rural Short | Planned |  | 105 | 190 |  |  | No
20/09/2019 | 08:31 | HGS31 | Rural Short | Planned |  | 152 | 257 |  |  | No
20/09/2019 | 08:55 | EW14 | Urban | Planned |  | 11 | 105 |  |  | No
20/09/2019 | 09:10 | BR13 | Urban | Planned |  | 4 | 62 |  |  | No
20/09/2019 | 09:31 | M13 | Urban | Planned |  | 31 | 223 |  |  | No
20/09/2019 | 11:00 | M13 | Urban | Planned |  | 1 | 28 |  |  | No
20/09/2019 | 12:10 | DMA15 | Rural Short | Planned |  | 1 | 112 |  |  | No
21/09/2019 | 05:30 | EB21 | Urban | Planned |  | 5 | 495 |  |  | No
21/09/2019 | 07:32 | MC6 | Urban | Planned |  | 29 | 513 |  |  | No
21/09/2019 | 07:35 | CDA24 | Urban | Planned |  | 61 | 395 |  |  | No
21/09/2019 | 08:15 | EM6 | Urban | Planned |  | 41 | 255 |  |  | No
22/09/2019 | 07:30 | BW21 | Urban | Planned |  | 1 | 539.1 |  |  | No
22/09/2019 | 07:30 | BW35 | Urban | Planned |  | 84 | 539.1 |  |  | No
22/09/2019 | 08:00 | CRM14 | Urban | Planned |  | 547 | 570 |  |  | No
22/09/2019 | 08:00 | CRM35 | Urban | Planned |  | 33 | 570 |  |  | No
22/09/2019 | 08:00 | MC10 | Urban | Planned |  | 4 | 315 |  |  | No
22/09/2019 | 08:00 | MC4 | Urban | Planned |  | 58 | 283 |  |  | No
22/09/2019 | 08:00 | NB34 | Urban | Planned |  | 92 | 370 |  |  | No
22/09/2019 | 08:06 | OE5 | Urban | Planned |  | 5 | 623 |  |  | No
22/09/2019 | 08:30 | FTN23 | Urban | Planned |  | 85 | 170 |  |  | No
23/09/2019 | 08:00 | CRM21 | Urban | Planned |  | 34 | 385 |  |  | No
23/09/2019 | 08:00 | HGS23 | Rural Short | Planned |  | 54 | 173 |  |  | No
23/09/2019 | 08:01 | MTN32 | Rural Short | Planned |  | 61 | 346 |  |  | No
23/09/2019 | 08:25 | DMA23 | Rural Short | Planned |  | 14 | 143 |  |  | No
23/09/2019 | 09:40 | FSH32 | Rural Short | Planned |  | 77 | 160 |  |  | No
23/09/2019 | 09:50 | HGS23 | Rural Short | Planned |  | 20 | 220 |  |  | No
23/09/2019 | 11:25 | HGS23 | Rural Short | Planned |  | 1 | 30 |  |  | No
23/09/2019 | 12:20 | HGS23 | Rural Short | Planned |  | 2 | 65 |  |  | No
23/09/2019 | 13:06 | LD2 | Urban | Planned |  | 27 | 188 |  |  | No
23/09/2019 | 13:35 | FSH32 | Rural Short | Planned |  | 4 | 50 |  |  | No
24/09/2019 | 07:30 | LD32 | Urban | Planned |  | 52 | 480 |  |  | No
24/09/2019 | 08:00 | EB22 | Urban | Planned |  | 31 | 420 |  |  | No
24/09/2019 | 08:00 | HGS31 | Rural Short | Planned |  | 243 | 510 |  |  | No
24/09/2019 | 08:00 | M33 | Urban | Planned |  | 230 | 350 |  |  | No
24/09/2019 | 08:00 | MTN32 | Rural Short | Planned |  | 43 | 480 |  |  | No
24/09/2019 | 08:40 | MTN32 | Rural Short | Planned |  | 2 | 120 |  |  | No
24/09/2019 | 09:00 | FSH23 | Rural Short | Planned |  | 47 | 110 |  |  | No
24/09/2019 | 10:05 | DC1 | Urban | Planned |  | 44 | 185 |  |  | No
24/09/2019 | 11:30 | DMA23 | Rural Short | Planned |  | 1 | 300 |  |  | No
25/09/2019 | 01:40 | MTN21 | Urban | Planned |  | 16 | 105 |  |  | No
25/09/2019 | 07:00 | EW12 | Urban | Planned |  | 1 | 600 |  |  | No
25/09/2019 | 08:00 | DMA23 | Rural Short | Planned |  | 233 | 510 |  |  | No
25/09/2019 | 08:00 | DN7 | Urban | Planned |  | 4 | 300 |  |  | No
25/09/2019 | 08:05 | HT11 | Urban | Planned |  | 58 | 190 |  |  | No
25/09/2019 | 08:13 | HGS23 | Rural Short | Planned |  | 37 | 357 |  |  | No
25/09/2019 | 08:15 | M21 | Urban | Planned |  | 49 | 431 |  |  | No
25/09/2019 | 08:15 | M34 | Urban | Planned |  | 172 | 431 |  |  | No
25/09/2019 | 08:16 | DMA23 | Rural Short | Planned |  | 38 | 288 |  |  | No
25/09/2019 | 08:30 | STO13 | Urban | Planned |  | 58 | 345 |  |  | No
25/09/2019 | 09:05 | DN22 | Urban | Planned |  | 29 | 215 |  |  | No
25/09/2019 | 09:11 | DMA23 | Rural Short | Planned |  | 88 | 347 |  |  | No
26/09/2019 | 07:00 | BR1 | Urban | Planned |  | 1 | 659.6 |  |  | No
26/09/2019 | 07:30 | CFD26 | Urban | Planned |  | 2 | 480 |  |  | No
26/09/2019 | 08:00 | EM5 | Urban | Planned |  | 90 | 330 |  |  | No
26/09/2019 | 08:00 | LD6 | Urban | Planned |  | 104 | 340 |  |  | No
26/09/2019 | 08:00 | MTN32 | Rural Short | Planned |  | 103 | 510 |  |  | No
26/09/2019 | 08:00 | OE9 | Urban | Planned |  | 2 | 410 |  |  | No
26/09/2019 | 08:15 | HGS31 | Rural Short | Planned |  | 12 | 175 |  |  | No
26/09/2019 | 08:30 | STO23 | Urban | Planned |  | 85 | 270 |  |  | No
26/09/2019 | 08:55 | FSH33 | Urban | Planned |  | 12 | 205 |  |  | No
26/09/2019 | 09:00 | OR25 | Urban | Planned |  | 57 | 270 |  |  | No
26/09/2019 | 09:33 | LWN24 | Urban | Planned |  | 59 | 335 |  |  | No
26/09/2019 | 11:00 | DC2 | Urban | Planned |  | 8 | 175 |  |  | No
26/09/2019 | 11:30 | RBD12 | Rural Short | Planned |  | 1 | 300 |  |  | No
26/09/2019 | 13:00 | RBD12 | Rural Short | Planned |  | 17 | 90 |  |  | No
26/09/2019 | 13:05 | HGS22 | Rural Short | Planned |  | 10 | 95 |  |  | No
27/09/2019 | 08:05 | MTN21 | Urban | Planned |  | 4 | 120 |  |  | No
27/09/2019 | 08:05 | MTN23 | Urban | Planned |  | 7 | 120 |  |  | No
29/09/2019 | 07:00 | RWT23 | Urban | Planned |  | 9 | 552 |  |  | No
29/09/2019 | 07:54 | HT8 | Urban | Planned |  | 4 | 372 |  |  | No
29/09/2019 | 07:54 | MR15 | Urban | Planned |  | 77 | 372 |  |  | No
29/09/2019 | 08:00 | SVW42 | Urban | Planned |  | 1 | 280 |  |  | No
29/09/2019 | 08:16 | NO6 | Urban | Planned |  | 66 | 450 |  |  | No
29/09/2019 | 08:30 | BW22 | Urban | Planned |  | 2 | 15 |  |  | No
29/09/2019 | 14:28 | DN2 | Urban | Planned |  | 5 | 29 |  |  | No
30/09/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 1 | 210 |  |  | No
30/09/2019 | 09:02 | EL13 | Urban | Planned |  | 34 | 437 |  |  | No
30/09/2019 | 10:50 | LWN21 | Rural Short | Planned |  | 19 | 153 |  |  | No
30/09/2019 | 11:30 | DMA23 | Rural Short | Planned |  | 2 | 150 |  |  | No
01/10/2019 | 08:10 | RBD23 | Urban | Planned |  | 158 | 210 |  |  | No
01/10/2019 | 08:30 | BU4 | Urban | Planned |  | 43 | 120 |  |  | No
01/10/2019 | 08:35 | HGS22 | Rural Short | Planned |  | 4 | 150 |  |  | No
01/10/2019 | 08:47 | LD6 | Urban | Planned |  | 44 | 279 |  |  | No
01/10/2019 | 12:00 | MTN32 | Rural Short | Planned |  | 6 | 90 |  |  | No
01/10/2019 | 12:23 | DMA23 | Rural Short | Planned |  | 1 | 112 |  |  | No
02/10/2019 | 07:35 | LWN34 | Urban | Planned |  | 18 | 115 |  |  | No
02/10/2019 | 08:00 | HGS21 | Rural Short | Planned |  | 105 | 182 |  |  | No
02/10/2019 | 08:10 | MR22 | Urban | Planned |  | 142 | 232 |  |  | No
02/10/2019 | 08:25 | K3 | Urban | Planned |  | 134 | 200 |  |  | No
02/10/2019 | 08:32 | CDA24 | Urban | Planned |  | 72 | 143 |  |  | No
02/10/2019 | 08:43 | NP23 | Urban | Planned |  | 93 | 250 |  |  | No
02/10/2019 | 08:46 | GW7 | Urban | Planned |  | 97 | 138 |  |  | No
02/10/2019 | 10:25 | DC3 | Urban | Planned |  | 28 | 108 |  |  | No
02/10/2019 | 11:30 | BC11 | Urban | Planned |  | 103 | 240 |  |  | No
02/10/2019 | 11:30 | EW8 | Urban | Planned |  | 5 | 240 |  |  | No
02/10/2019 | 12:00 | BU1 | Urban | Planned |  | 37 | 70 |  |  | No
02/10/2019 | 21:37 | DC4 | Urban | Planned |  | 9 | 15 |  |  | No
03/10/2019 | 07:55 | DMA24 | Rural Short | Planned |  | 18 | 391 |  |  | No
03/10/2019 | 08:00 | DMA23 | Rural Short | Planned |  | 8 | 165 |  |  | No
03/10/2019 | 08:00 | NP33 | Urban | Planned |  | 1 | 480 |  |  | No
03/10/2019 | 08:05 | HGS32 | Urban | Planned |  | 29 | 315 |  |  | No
03/10/2019 | 08:13 | CDA22 | Urban | Planned |  | 24 | 140 |  |  | No
03/10/2019 | 08:20 | GW11 | Urban | Planned |  | 4 | 150 |  |  | No
03/10/2019 | 08:30 | BU4 | Urban | Planned |  | 24 | 165 |  |  | No
03/10/2019 | 08:30 | HGS22 | Rural Short | Planned |  | 2 | 116 |  |  | No
03/10/2019 | 08:35 | FSH12 | Rural Short | Planned |  | 12 | 280 |  |  | No
03/10/2019 | 08:43 | NP23 | Urban | Planned |  | 101 | 215 |  |  | No
03/10/2019 | 08:43 | NP33 | Urban | Planned |  | 8 | 215 |  |  | No
03/10/2019 | 10:56 | HGS33 | Rural Short | Planned |  | 15 | 77 |  |  | No
04/10/2019 | 08:00 | DMA23 | Rural Short | Planned |  | 20 | 110 |  |  | No
04/10/2019 | 08:00 | HGS22 | Rural Short | Planned |  | 66 | 510 |  |  | No
04/10/2019 | 08:03 | HGS23 | Rural Short | Planned |  | 29 | 162 |  |  | No
04/10/2019 | 08:15 | DC10 | Urban | Planned |  | 71 | 230 |  |  | No
04/10/2019 | 08:15 | NW13 | Urban | Planned |  | 7 | 230 |  |  | No
04/10/2019 | 08:20 | LD33 | Urban | Planned |  | 233 | 145 |  |  | No
04/10/2019 | 08:33 | RBD21 | Rural Short | Planned |  | 9 | 237 |  |  | No
04/10/2019 | 08:37 | RWT12 | Urban | Planned |  | 9 | 335 |  |  | No
04/10/2019 | 08:38 | HGS21 | Rural Short | Planned |  | 52 | 102 |  |  | No
04/10/2019 | 08:42 | DMA15 | Rural Short | Planned |  | 73 | 582 |  |  | No
04/10/2019 | 08:49 | OR32 | Urban | Planned |  | 51 | 163 |  |  | No
04/10/2019 | 08:50 | CDA24 | Urban | Planned |  | 50 | 310 |  |  | No
04/10/2019 | 08:50 | LWN21 | Rural Short | Planned |  | 8 | 50 |  |  | No
04/10/2019 | 09:15 | LWN21 | Rural Short | Planned |  | 29 | 365 |  |  | No
04/10/2019 | 10:00 | FSH21 | Rural Short | Planned |  | 46 | 105 |  |  | No
04/10/2019 | 10:20 | MTN34 | Urban | Planned |  | 209 | 220 |  |  | No
04/10/2019 | 14:10 | LWN21 | Rural Short | Planned |  | 1 | 30 |  |  | No
05/10/2019 | 06:30 | SS14 | Urban | Planned |  | 1 | 660 |  |  | No
05/10/2019 | 06:30 | K13 | Urban | Planned |  | 11 | 600 |  |  | No
05/10/2019 | 08:00 | HGS33 | Rural Short | Planned |  | 10 | 300 |  |  | No
05/10/2019 | 08:00 | HGS33 | Rural Short | Planned |  | 3 | 510 |  |  | No
05/10/2019 | 08:00 | HT2 | Urban | Planned |  | 2 | 330 |  |  | No
05/10/2019 | 08:00 | HT7 | Urban | Planned |  | 102 | 330 |  |  | No
05/10/2019 | 08:00 | LWN21 | Rural Short | Planned |  | 16 | 510 |  |  | No
05/10/2019 | 08:00 | LWN32 | Rural Short | Planned |  | 148 | 510 |  |  | No
06/10/2019 | 07:31 | OR33 | Urban | Planned |  | 180 | 443 |  |  | No
06/10/2019 | 07:35 | CM15 | Urban | Planned |  | 2 | 280 |  |  | No
06/10/2019 | 07:45 | MC10 | Urban | Planned |  | 4 | 310 |  |  | No
06/10/2019 | 08:00 | DN6 | Urban | Planned |  | 1 | 510 |  |  | No
06/10/2019 | 08:00 | LWN21 | Rural Short | Planned |  | 1 | 540 |  |  | No
06/10/2019 | 08:07 | LWN21 | Rural Short | Planned |  | 92 | 488 |  |  | No
06/10/2019 | 08:17 | OE5 | Urban | Planned |  | 35 | 557 |  |  | No
06/10/2019 | 08:22 | LWN21 | Rural Short | Planned |  | 92 | 321 |  |  | No
06/10/2019 | 08:39 | DN6 | Urban | Planned |  | 132 | 232 |  |  | No
07/10/2019 | 08:00 | LWN21 | Rural Short | Planned |  | 48 | 300 |  |  | No
07/10/2019 | 08:00 | MTN22 | Rural Short | Planned |  | 4 | 510 |  |  | No
07/10/2019 | 08:15 | CDA22 | Urban | Planned |  | 17 | 160 |  |  | No
07/10/2019 | 08:17 | MTN22 | Rural Short | Planned |  | 63 | 305 |  |  | No
07/10/2019 | 08:20 | MTN22 | Rural Short | Planned |  | 95 | 305 |  |  | No
07/10/2019 | 08:23 | MTN22 | Rural Short | Planned |  | 12 | 299 |  |  | No
07/10/2019 | 09:10 | DMA23 | Rural Short | Planned |  | 71 | 320 |  |  | No
07/10/2019 | 09:45 | DMA23 | Rural Short | Planned |  | 71 | 272 |  |  | No
07/10/2019 | 09:52 | FTN11 | Urban | Planned |  | 142 | 121 |  |  | No
07/10/2019 | 13:05 | FTN22 | Urban | Planned |  | 122 | 125 |  |  | No
07/10/2019 | 21:50 | EL10 | Urban | Planned |  | 29 | 540 |  |  | No
08/10/2019 | 08:00 | CRM35 | Urban | Planned |  | 1 | 450 |  |  | No
08/10/2019 | 08:00 | MTN22 | Rural Short | Planned |  | 5 | 330 |  |  | No
08/10/2019 | 08:00 | MTN35 | Rural Short | Planned |  | 59 | 250 |  |  | No
08/10/2019 | 08:10 | CRM35 | Urban | Planned |  | 99 | 255 |  |  | No
08/10/2019 | 08:15 | DC1 | Urban | Planned |  | 37 | 355 |  |  | No
08/10/2019 | 08:33 | STO21 | Rural Short | Planned |  | 4 | 224 |  |  | No
08/10/2019 | 08:35 | SS23 | Urban | Planned |  | 63 | 315 |  |  | No
08/10/2019 | 08:37 | DMA15 | Rural Short | Planned |  | 5 | 59 |  |  | No
08/10/2019 | 08:38 | DC1 | Urban | Planned |  | 5 | 196 |  |  | No
08/10/2019 | 09:00 | DC10 | Urban | Planned |  | 10 | 469.2 |  |  | No
08/10/2019 | 10:10 | CDA22 | Urban | Planned |  | 10 | 365 |  |  | No
08/10/2019 | 10:39 | DMA15 | Rural Short | Planned |  | 1 | 44 |  |  | No
09/10/2019 | 08:00 | RBD21 | Rural Short | Planned |  | 1 | 420 |  |  | No
09/10/2019 | 08:05 | EB22 | Urban | Planned |  | 72 | 375 |  |  | No
09/10/2019 | 08:05 | RBD11 | Urban | Planned |  | 208 | 382 |  |  | No
09/10/2019 | 08:10 | RBD13 | Urban | Planned |  | 38 | 245 |  |  | No
09/10/2019 | 08:30 | M13 | Urban | Planned |  | 60 | 495 |  |  | No
09/10/2019 | 08:30 | MC5 | Urban | Planned |  | 39 | 225 |  |  | No
09/10/2019 | 08:50 | HT11 | Urban | Planned |  | 140 | 310 |  |  | No
09/10/2019 | 09:11 | HGS21 | Rural Short | Planned |  | 29 | 244 |  |  | No
09/10/2019 | 09:30 | HGS22 | Rural Short | Planned |  | 2 | 76 |  |  | No
09/10/2019 | 09:30 | RBD21 | Rural Short | Planned |  | 36 | 105 |  |  | No
09/10/2019 | 09:50 | STO13 | Urban | Planned |  | 4 | 220 |  |  | No
09/10/2019 | 12:00 | RBD12 | Rural Short | Planned |  | 4 | 60 |  |  | No
10/10/2019 | 07:35 | HGS31 | Rural Short | Planned |  | 65 | 445 |  |  | No
10/10/2019 | 08:10 | M32 | Urban | Planned |  | 59 | 170 |  |  | No
10/10/2019 | 08:15 | OE4 | Urban | Planned |  | 81 | 360 |  |  | No
10/10/2019 | 08:19 | M32 | Urban | Planned |  | 29 | 391 |  |  | No
10/10/2019 | 08:25 | HGS23 | Rural Short | Planned |  | 3 | 10 |  |  | No
10/10/2019 | 09:00 | CRM35 | Urban | Planned |  | 124 | 330 |  |  | No
10/10/2019 | 09:20 | LWN21 | Rural Short | Planned |  | 108 | 165 |  |  | No
10/10/2019 | 09:20 | MTN22 | Rural Short | Planned |  | 7 | 15 |  |  | No
10/10/2019 | 10:15 | MTN22 | Rural Short | Planned |  | 107 | 372 |  |  | No
11/10/2019 | 08:00 | NW23 | Urban | Planned |  | 141 | 270 |  |  | No
11/10/2019 | 08:00 | NW23 | Urban | Planned |  | 1 | 510 |  |  | No
11/10/2019 | 08:05 | MTN32 | Rural Short | Planned |  | 116 | 398 |  |  | No
11/10/2019 | 08:05 | MTN32 | Rural Short | Planned |  | 116 | 518 |  |  | No
11/10/2019 | 08:15 | DMA14 | Urban | Planned |  | 37 | 72 |  |  | No
11/10/2019 | 08:35 | MTN22 | Rural Short | Planned |  | 22 | 211 |  |  | No
11/10/2019 | 08:38 | NB34 | Urban | Planned |  | 31 | 540 |  |  | No
11/10/2019 | 08:46 | LWN21 | Rural Short | Planned |  | 1 | 50 |  |  | No
11/10/2019 | 08:46 | MTN32 | Rural Short | Planned |  | 100 | 119 |  |  | No
11/10/2019 | 08:50 | FSH12 | Rural Short | Planned |  | 156 | 357 |  |  | No
11/10/2019 | 08:50 | FSH33 | Urban | Planned |  | 1 | 357 |  |  | No
11/10/2019 | 10:00 | DMA23 | Rural Short | Planned |  | 82 | 65 |  |  | No
11/10/2019 | 11:25 | RBD12 | Rural Short | Planned |  | 44 | 185 |  |  | No
11/10/2019 | 11:30 | FSH13 | Urban | Planned |  | 16 | 110 |  |  | No
11/10/2019 | 11:50 | KBH35 | Urban | Planned |  | 1 | 265 |  |  | No
11/10/2019 | 13:05 | DMA23 | Rural Short | Planned |  | 18 | 85 |  |  | No
12/10/2019 | 07:30 | BH22 | Urban | Planned |  | 1 | 660 |  |  | No
12/10/2019 | 08:00 | SS23 | Urban | Planned |  | 132 | 392 |  |  | No
12/10/2019 | 08:00 | SS23 | Urban | Planned |  | 1 | 510 |  |  | No
12/10/2019 | 08:18 | RBD12 | Rural Short | Planned |  | 2 | 58 |  |  | No
12/10/2019 | 08:48 | RBD12 | Rural Short | Planned |  | 4 | 222 |  |  | No
12/10/2019 | 11:00 | DMA24 | Rural Short | Planned |  | 3 | 100 |  |  | No
13/10/2019 | 06:30 | KBH31 | Urban | Planned |  | 2 | 610 |  |  | No
13/10/2019 | 08:00 | BW35 | Urban | Planned |  | 3 | 600.2 |  |  | No
13/10/2019 | 08:00 | OR22 | Urban | Planned |  | 1 | 480 |  |  | No
13/10/2019 | 08:05 | DSH34 | Urban | Planned |  | 110 | 280 |  |  | No
13/10/2019 | 08:09 | GW7 | Urban | Planned |  | 1 | 287 |  |  | No
13/10/2019 | 08:10 | GW7 | Urban | Planned |  | 6 | 285 |  |  | No
13/10/2019 | 08:30 | HT13 | Urban | Planned |  | 46 | 215 |  |  | No
13/10/2019 | 09:15 | BW35 | Urban | Planned |  | 157 | 425 |  |  | No
13/10/2019 | 10:44 | DVY11 | Urban | Planned |  | 2 | 6 |  |  | No
13/10/2019 | 11:00 | GW7 | Urban | Planned |  | 3 | 15 |  |  | No
14/10/2019 | 08:05 | HGS22 | Rural Short | Planned |  | 47 | 86 |  |  | No
14/10/2019 | 08:30 | MTN31 | Urban | Planned |  | 65 | 450 |  |  | No
14/10/2019 | 08:40 | OR23 | Urban | Planned |  | 8 | 320 |  |  | No
14/10/2019 | 09:05 | HGS23 | Rural Short | Planned |  | 20 | 175 |  |  | No
14/10/2019 | 09:48 | HGS22 | Rural Short | Planned |  | 90 | 77 |  |  | No
14/10/2019 | 11:00 | HGS22 | Rural Short | Planned |  | 7 | 165 |  |  | No
14/10/2019 | 11:30 | MTN32 | Rural Short | Planned |  | 1 | 30 |  |  | No
15/10/2019 | 08:00 | DMA23 | Rural Short | Planned |  | 1 | 510 |  |  | No
15/10/2019 | 08:00 | HT11 | Urban | Planned |  | 88 | 269.9 |  |  | No
15/10/2019 | 08:01 | FSH23 | Rural Short | Planned |  | 47 | 281 |  |  | No
15/10/2019 | 08:05 | CRM52 | Urban | Planned |  | 182 | 295 |  |  | No
15/10/2019 | 08:30 | BU9 | Urban | Planned |  | 17 | 200 |  |  | No
15/10/2019 | 08:30 | K13 | Urban | Planned |  | 65 | 195 |  |  | No
15/10/2019 | 08:30 | LWN21 | Rural Short | Planned |  | 9 | 120 |  |  | No
15/10/2019 | 08:30 | STO23 | Urban | Planned |  | 57 | 85 |  |  | No
15/10/2019 | 08:35 | M13 | Urban | Planned |  | 113 | 220 |  |  | No
15/10/2019 | 08:40 | DMA23 | Rural Short | Planned |  | 30 | 70 |  |  | No
15/10/2019 | 08:45 | DMA23 | Rural Short | Planned |  | 222 | 380 |  |  | No
15/10/2019 | 08:50 | MTN22 | Rural Short | Planned |  | 35 | 126 |  |  | No
15/10/2019 | 09:00 | BU2 | Urban | Planned |  | 37 | 60 |  |  | No
15/10/2019 | 09:10 | HGS33 | Rural Short | Planned |  | 61 | 135 |  |  | No
15/10/2019 | 10:35 | CDA22 | Urban | Planned |  | 43 | 78 |  |  | No
15/10/2019 | 10:50 | MTN32 | Rural Short | Planned |  | 2 | 20 |  |  | No
15/10/2019 | 11:30 | RBD13 | Urban | Planned |  | 109 | 125 |  |  | No
15/10/2019 | 11:30 | RBD13 | Urban | Planned |  | 1 | 240 |  |  | No
15/10/2019 | 13:00 | FSH12 | Rural Short | Planned |  | 84 | 150 |  |  | No
15/10/2019 | 14:55 | FSH12 | Rural Short | Planned |  | 7 | 113 |  |  | No
15/10/2019 | 14:55 | FSH31 | Urban | Planned |  | 9 | 11 |  |  | No
16/10/2019 | 07:40 | DMA15 | Rural Short | Planned |  | 252 | 819 |  |  | No
16/10/2019 | 07:40 | LD7 | Urban | Planned |  | 77 | 585 |  |  | No
16/10/2019 | 08:00 | GW11 | Urban | Planned |  | 78 | 190 |  |  | No
16/10/2019 | 08:02 | M13 | Urban | Planned |  | 62 | 168 |  |  | No
16/10/2019 | 08:30 | CDA22 | Urban | Planned |  | 75 | 326 |  |  | No
16/10/2019 | 08:30 | STO23 | Urban | Planned |  | 164 | 170 |  |  | No
16/10/2019 | 08:40 | DC5 | Urban | Planned |  | 19 | 95 |  |  | No
16/10/2019 | 08:45 | WD23 | Urban | Planned |  | 65 | 215 |  |  | No
16/10/2019 | 09:30 | LD2 | Urban | Planned |  | 26 | 180 |  |  | No
16/10/2019 | 09:30 | LD33 | Urban | Planned |  | 78 | 365 |  |  | No
16/10/2019 | 10:10 | LD33 | Urban | Planned |  | 56 | 484 |  |  | No
16/10/2019 | 10:57 | HGS31 | Rural Short | Planned |  | 174 | 30 |  |  | No
16/10/2019 | 11:00 | DC5 | Urban | Planned |  | 33 | 120 |  |  | No
16/10/2019 | 21:12 | MTN21 | Urban | Planned |  | 29 | 84 |  |  | No
17/10/2019 | 01:36 | MTN21 | Urban | Planned |  | 31 | 57 |  |  | No
17/10/2019 | 08:00 | MTN34 | Urban | Planned |  | 45 | 265 |  |  | No
17/10/2019 | 08:05 | DMA23 | Rural Short | Planned |  | 8 | 325 |  |  | No
17/10/2019 | 08:20 | MR15 | Urban | Planned |  | 115 | 220 |  |  | No
17/10/2019 | 09:00 | AR12 | Urban | Planned |  | 25 | 300 |  |  | No
17/10/2019 | 09:17 | RWT23 | Urban | Planned |  | 26 | 185 |  |  | No
17/10/2019 | 10:00 | FSH34 | Urban | Planned |  | 30 | 75 |  |  | No
17/10/2019 | 10:45 | LWN23 | Urban | Planned |  | 104 | 168 |  |  | No
18/10/2019 | 07:36 | EB32 | Urban | Planned |  | 63 | 334 |  |  | No
18/10/2019 | 07:36 | GW11 | Urban | Planned |  | 34 | 334 |  |  | No
18/10/2019 | 08:00 | CRM35 | Urban | Planned |  | 17 | 385 |  |  | No
18/10/2019 | 08:00 | CRM35 | Urban | Planned |  | 1 | 480 |  |  | No
18/10/2019 | 08:00 | MR15 | Urban | Planned |  | 1 | 480 |  |  | No
18/10/2019 | 08:00 | STO22 | Urban | Planned |  | 1 | 540 |  |  | No
18/10/2019 | 08:04 | HGS21 | Rural Short | Planned |  | 39 | 212 |  |  | No
18/10/2019 | 08:20 | CDA24 | Urban | Planned |  | 56 | 145 |  |  | No
18/10/2019 | 08:20 | MR15 | Urban | Planned |  | 92 | 145 |  |  | No
18/10/2019 | 08:30 | EB13 | Urban | Planned |  | 23 | 360 |  |  | No
18/10/2019 | 08:30 | EB32 | Urban | Planned |  | 65 | 360 |  |  | No
18/10/2019 | 08:36 | FTN14 | Urban | Planned |  | 54 | 193 |  |  | No
18/10/2019 | 09:03 | STO23 | Urban | Planned |  | 15 | 161 |  |  | No
18/10/2019 | 09:50 | HGS21 | Rural Short | Planned |  | 212 | 200 |  |  | No
18/10/2019 | 11:18 | STO22 | Urban | Planned |  | 78 | 108 |  |  | No
18/10/2019 | 11:25 | EM5 | Urban | Planned |  | 42 | 125 |  |  | No
19/10/2019 | 08:00 | EB32 | Urban | Planned |  | 74 | 350 |  |  | No
19/10/2019 | 08:00 | EB32 | Urban | Planned |  | 1 | 510 |  |  | No
19/10/2019 | 08:05 | GW7 | Urban | Planned |  | 1 | 70 |  |  | No
19/10/2019 | 08:30 | EM7 | Urban | Planned |  | 14 | 150 |  |  | No
19/10/2019 | 08:30 | MC5 | Urban | Planned |  | 2 | 420.6 |  |  | No
19/10/2019 | 10:15 | DN7 | Urban | Planned |  | 2 | 230 |  |  | No
20/10/2019 | 06:41 | OR23 | Urban | Planned |  | 5 | 205 |  |  | No
20/10/2019 | 07:57 | HT3 | Urban | Planned |  | 13 | 520 |  |  | No
20/10/2019 | 08:00 | NW32 | Urban | Planned |  | 4 | 240 |  |  | No
20/10/2019 | 08:04 | M34 | Urban | Planned |  | 33 | 322 |  |  | No
20/10/2019 | 08:20 | GW11 | Urban | Planned |  | 155 | 449 |  |  | No
20/10/2019 | 08:34 | DVY24 | Rural Short | Planned |  | 4 | 499 |  |  | No
20/10/2019 | 08:34 | DVY34 | Urban | Planned |  | 25 | 499 |  |  | No
21/10/2019 | 08:19 | NO6 | Urban | Planned |  | 7 | 232 |  |  | No
21/10/2019 | 08:29 | EB32 | Urban | Planned |  | 114 | 349 |  |  | No
21/10/2019 | 08:30 | BU14 | Urban | Planned |  | 60 | 180 |  |  | No
22/10/2019 | 07:30 | DC2 | Urban | Planned |  | 1 | 510 |  |  | No
22/10/2019 | 07:44 | DC2 | Urban | Planned |  | 67 | 435 |  |  | No
22/10/2019 | 08:00 | STO23 | Urban | Planned |  | 39 | 350 |  |  | No
22/10/2019 | 08:00 | RWT35 | Urban | Planned |  | 1 | 1,890.0 |  |  | No
22/10/2019 | 08:01 | FSH13 | Urban | Planned |  | 82 | 487 |  |  | No
22/10/2019 | 08:04 | EL13 | Urban | Planned |  | 34 | 309 |  |  | No
22/10/2019 | 08:20 | BU10 | Urban | Planned |  | 98 | 445 |  |  | No
22/10/2019 | 08:36 | LWN21 | Rural Short | Planned |  | 121 | 75 |  |  | No
22/10/2019 | 09:10 | DN11 | Urban | Planned |  | 169 | 308 |  |  | No
22/10/2019 | 10:27 | LD2 | Urban | Planned |  | 27 | 98 |  |  | No
22/10/2019 | 23:05 | NW11 | Urban | Planned |  | 1 | 255 |  |  | No
23/10/2019 | 08:00 | DC8 | Urban | Planned |  | 76 | 439 |  |  | No
23/10/2019 | 08:00 | DN11 | Urban | Planned |  | 442 | 440 |  |  | No
23/10/2019 | 08:00 | KBH32 | Urban | Planned |  | 313 | 300 |  |  | No
23/10/2019 | 08:20 | STO23 | Urban | Planned |  | 393 | 315 |  |  | No
23/10/2019 | 08:34 | CRM35 | Urban | Planned |  | 97 | 298 |  |  | No
23/10/2019 | 08:40 | BU14 | Urban | Planned |  | 54 | 235 |  |  | No
23/10/2019 | 09:17 | DMA21 | Urban | Planned |  | 62 | 121 |  |  | No
23/10/2019 | 09:25 | MR15 | Urban | Planned |  | 37 | 277 |  |  | No
24/10/2019 | 08:00 | EB32 | Urban | Planned |  | 32 | 85 |  |  | No
24/10/2019 | 08:00 | EB32 | Urban | Planned |  | 1 | 300 |  |  | No
24/10/2019 | 08:00 | MR14 | Urban | Planned |  | 61 | 210 |  |  | No
24/10/2019 | 08:00 | MR22 | Urban | Planned |  | 85 | 210 |  |  | No
24/10/2019 | 08:00 | CFD13 | Urban | Planned |  | 49 | 67.9 |  |  | No
24/10/2019 | 08:00 | CFD13 | Urban | Planned |  | 1 | 450 |  |  | No
24/10/2019 | 08:00 | BR15 | Urban | Planned |  | 1 | 450 |  |  | No
24/10/2019 | 08:01 | BR15 | Urban | Planned |  | 81 | 361 |  |  | No
24/10/2019 | 08:21 | LWN23 | Urban | Planned |  | 28 | 78 |  |  | No
24/10/2019 | 08:22 | NW31 | Urban | Planned |  | 54 | 356 |  |  | No
24/10/2019 | 08:25 | STO14 | Rural Short | Planned |  | 5 | 410 |  |  | No
24/10/2019 | 08:25 | STO21 | Rural Short | Planned |  | 71 | 410 |  |  | No
24/10/2019 | 08:30 | FSH13 | Urban | Planned |  | 104 | 90 |  |  | No
24/10/2019 | 08:35 | M13 | Urban | Planned |  | 54 | 98 |  |  | No
24/10/2019 | 08:53 | FSH33 | Urban | Planned |  | 46 | 326 |  |  | No
24/10/2019 | 11:00 | MGE23 | Urban | Planned |  | 36 | 80 |  |  | No
24/10/2019 | 11:10 | RBD12 | Rural Short | Planned |  | 60 | 175 |  |  | No
25/10/2019 | 08:06 | MTN22 | Rural Short | Planned |  | 14 | 177 |  |  | No
25/10/2019 | 08:25 | LWN33 | Urban | Planned |  | 14 | 165 |  |  | No
25/10/2019 | 08:30 | NO6 | Urban | Planned |  | 175 | 420 |  |  | No
25/10/2019 | 08:45 | RBD13 | Urban | Planned |  | 37 | 275 |  |  | No
26/10/2019 | 07:29 | EB32 | Urban | Planned |  | 94 | 393 |  |  | No
26/10/2019 | 08:00 | MC7 | Urban | Planned |  | 13 | 80 |  |  | No
26/10/2019 | 08:33 | M13 | Urban | Planned |  | 64 | 318 |  |  | No
26/10/2019 | 10:25 | SS24 | Urban | Planned |  | 7 | 60 |  |  | No
27/10/2019 | 07:36 | K2 | Urban | Planned |  | 126 | 510 |  |  | No
27/10/2019 | 08:00 | NO31 | Urban | Planned |  | 19 | 240 |  |  | No
27/10/2019 | 08:12 | FTN14 | Urban | Planned |  | 99 | 330 |  |  | No
27/10/2019 | 08:15 | OR24 | Urban | Planned |  | 23 | 430 |  |  | No
27/10/2019 | 08:55 | MGE34 | Urban | Planned |  | 44 | 297 |  |  | No
27/10/2019 | 13:20 | NB34 | Urban | Planned |  | 53 | 75 |  |  | No
28/10/2019 | 07:35 | FSH12 | Rural Short | Planned |  | 39 | 243 |  |  | No
28/10/2019 | 08:00 | FSH13 | Urban | Planned |  | 1 | 510 |  |  | No
28/10/2019 | 08:05 | HGS31 | Rural Short | Planned |  | 52 | 38 |  |  | No
28/10/2019 | 08:45 | FSH13 | Urban | Planned |  | 101 | 355 |  |  | No
29/10/2019 | 07:03 | GW11 | Urban | Planned |  | 6 | 437 |  |  | No
29/10/2019 | 07:09 | GW11 | Urban | Planned |  | 90 | 728 |  |  | No
29/10/2019 | 07:20 | EM9 | Urban | Planned |  | 160 | 540 |  |  | No
29/10/2019 | 08:00 | DMA23 | Rural Short | Planned |  | 1 | 510 |  |  | No
29/10/2019 | 08:00 | MTN32 | Rural Short | Planned |  | 61 | 205 |  |  | No
29/10/2019 | 08:10 | MR22 | Urban | Planned |  | 234 | 480 |  |  | No
29/10/2019 | 08:28 | KBH34 | Urban | Planned |  | 166 | 162 |  |  | No
29/10/2019 | 08:33 | FTN11 | Urban | Planned |  | 102 | 64 |  |  | No
29/10/2019 | 08:50 | FSH21 | Rural Short | Planned |  | 12 | 335 |  |  | No
29/10/2019 | 08:51 | DMA23 | Rural Short | Planned |  | 54 | 529 |  |  | No
29/10/2019 | 09:03 | OR35 | Urban | Planned |  | 124 | 257 |  |  | No
29/10/2019 | 09:15 | SR25 | Urban | Planned |  | 51 | 335 |  |  | No
29/10/2019 | 09:25 | DMA24 | Rural Short | Planned |  | 3 | 91 |  |  | No
29/10/2019 | 09:45 | DMA23 | Rural Short | Planned |  | 113 | 355 |  |  | No
29/10/2019 | 10:07 | CDA22 | Urban | Planned |  | 155 | 373 |  |  | No
29/10/2019 | 10:08 | MGE23 | Urban | Planned |  | 163 | 252 |  |  | No
29/10/2019 | 11:30 | RBD12 | Rural Short | Planned |  | 1 | 300 |  |  | No
29/10/2019 | 11:50 | DMA24 | Rural Short | Planned |  | 17 | 17 |  |  | No
29/10/2019 | 13:01 | RBD12 | Rural Short | Planned |  | 18 | 39 |  |  | No
29/10/2019 | 22:32 | WD14 | Urban | Planned |  | 13 | 527 |  |  | No
30/10/2019 | 07:18 | EM7 | Urban | Planned |  | 192 | 497 |  |  | No
30/10/2019 | 07:30 | MTN24 | Rural Short | Planned |  | 1 | 540 |  |  | No
30/10/2019 | 07:43 | MTN24 | Rural Short | Planned |  | 89 | 341 |  |  | No
30/10/2019 | 08:00 | CDA24 | Urban | Planned |  | 32 | 360 |  |  | No
30/10/2019 | 08:00 | FSH12 | Rural Short | Planned |  | 65 | 285 |  |  | No
30/10/2019 | 08:05 | FSH33 | Urban | Planned |  | 78 | 105 |  |  | No
30/10/2019 | 08:15 | M31 | Urban | Planned |  | 51 | 155 |  |  | No
30/10/2019 | 08:21 | HGS31 | Rural Short | Planned |  | 579 | 271 |  |  | No
30/10/2019 | 08:27 | GW12 | Urban | Planned |  | 42 | 244 |  |  | No
30/10/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 8 | 80 |  |  | No
30/10/2019 | 08:46 | EM10 | Urban | Planned |  | 155 | 341 |  |  | No
30/10/2019 | 09:37 | RBD24 | Urban | Planned |  | 9 | 2 |  |  | No
31/10/2019 | 08:00 | BU14 | Urban | Planned |  | 47 | 435 |  |  | No
31/10/2019 | 08:00 | CDA24 | Urban | Planned |  | 35 | 320 |  |  | No
31/10/2019 | 08:00 | CM13 | Urban | Planned |  | 98 | 174 |  |  | No
31/10/2019 | 08:00 | HGS33 | Rural Short | Planned |  | 56 | 415 |  |  | No
31/10/2019 | 08:20 | DN11 | Urban | Planned |  | 44 | 190 |  |  | No
31/10/2019 | 08:20 | HGS21 | Rural Short | Planned |  | 36 | 400 |  |  | No
31/10/2019 | 08:30 | K8 | Urban | Planned |  | 17 | 240 |  |  | No
31/10/2019 | 08:32 | RBD24 | Urban | Planned |  | 197 | 380 |  |  | No
31/10/2019 | 08:40 | GW12 | Urban | Planned |  | 20 | 110 |  |  | No
31/10/2019 | 09:00 | FTN13 | Urban | Planned |  | 37 | 240 |  |  | No
31/10/2019 | 09:08 | MTN32 | Rural Short | Planned |  | 13 | 200 |  |  | No
31/10/2019 | 10:30 | HT11 | Urban | Planned |  | 88 | 235 |  |  | No
31/10/2019 | 10:48 | DN22 | Urban | Planned |  | 132 | 168 |  |  | No
31/10/2019 | 11:17 | FSH33 | Urban | Planned |  | 28 | 33 |  |  | No
01/11/2019 | 08:10 | LWN35 | Urban | Planned |  | 62 | 310 |  |  | No
01/11/2019 | 08:36 | BW21 | Urban | Planned |  | 189 | 330 |  |  | No
01/11/2019 | 08:49 | FSH21 | Rural Short | Planned |  | 76 | 183 |  |  | No
01/11/2019 | 09:00 | EW8 | Urban | Planned |  | 1 | 280 |  |  | No
01/11/2019 | 09:00 | HGS31 | Rural Short | Planned |  | 52 | 29.9 |  |  | No
01/11/2019 | 09:23 | DC3 | Urban | Planned |  | 35 | 267 |  |  | No
01/11/2019 | 09:30 | DSH14 | Urban | Planned |  | 1 | 20 |  |  | No
01/11/2019 | 09:57 | DMA23 | Rural Short | Planned |  | 3 | 237 |  |  | No
03/11/2019 | 08:00 | CDA21 | Urban | Planned |  | 12 | 431 |  |  | No
03/11/2019 | 08:00 | CDA24 | Urban | Planned |  | 18 | 431 |  |  | No
03/11/2019 | 08:00 | FSH21 | Rural Short | Planned |  | 2 | 480 |  |  | No
03/11/2019 | 08:06 | HT2 | Urban | Planned |  | 151 | 354 |  |  | No
03/11/2019 | 08:30 | MC6 | Urban | Planned |  | 4 | 345 |  |  | No
03/11/2019 | 12:33 | HT2 | Urban | Planned |  | 26 | 320 |  |  | No
04/11/2019 | 08:20 | MR13 | Urban | Planned |  | 57 | 270 |  |  | No
04/11/2019 | 09:37 | GW3 | Urban | Planned |  | 2 | 326 |  |  | No
06/11/2019 | 08:00 | LD4 | Urban | Planned |  | 47 | 165 |  |  | No
06/11/2019 | 08:05 | EB31 | Urban | Planned |  | 90 | 415 |  |  | No
06/11/2019 | 08:10 | DMA14 | Urban | Planned |  | 11 | 410 |  |  | No
06/11/2019 | 08:15 | SR13 | Urban | Planned |  | 116 | 420 |  |  | No
06/11/2019 | 08:30 | M31 | Urban | Planned |  | 42 | 300 |  |  | No
06/11/2019 | 08:31 | STO13 | Urban | Planned |  | 75 | 154 |  |  | No
06/11/2019 | 08:35 | EM5 | Urban | Planned |  | 35 | 383 |  |  | No
06/11/2019 | 08:36 | DMA14 | Urban | Planned |  | 203 | 401 |  |  | No
06/11/2019 | 08:45 | GW11 | Urban | Planned |  | 7 | 185 |  |  | No
06/11/2019 | 09:09 | BU9 | Urban | Planned |  | 61 | 105 |  |  | No
06/11/2019 | 09:50 | CDA24 | Urban | Planned |  | 125 | 370 |  |  | No
06/11/2019 | 10:04 | FTN11 | Urban | Planned |  | 42 | 176 |  |  | No
06/11/2019 | 12:00 | GW12 | Urban | Planned |  | 17 | 195 |  |  | No
06/11/2019 | 12:00 | MGE23 | Urban | Planned |  | 44 | 195 |  |  | No
07/11/2019 | 08:00 | SR23 | Urban | Planned |  | 63 | 88 |  |  | No
07/11/2019 | 08:05 | MR13 | Urban | Planned |  | 45 | 385 |  |  | No
07/11/2019 | 08:05 | RBD11 | Urban | Planned |  | 141 | 222 |  |  | No
07/11/2019 | 08:10 | EB22 | Urban | Planned |  | 65 | 140 |  |  | No
07/11/2019 | 08:27 | LWN24 | Urban | Planned |  | 57 | 236 |  |  | No
07/11/2019 | 08:28 | MTN32 | Rural Short | Planned |  | 10 | 194 |  |  | No
07/11/2019 | 08:40 | DC3 | Urban | Planned |  | 119 | 340 |  |  | No
07/11/2019 | 08:44 | EM3 | Urban | Planned |  | 25 | 193 |  |  | No
07/11/2019 | 08:53 | RBD24 | Urban | Planned |  | 31 | 377 |  |  | No
07/11/2019 | 08:57 | FSH13 | Urban | Planned |  | 64 | 231 |  |  | No
07/11/2019 | 09:03 | EW14 | Urban | Planned |  | 52 | 271 |  |  | No
07/11/2019 | 09:10 | OAK26 | Urban | Planned |  | 392 | 530 |  |  | No
07/11/2019 | 10:07 | MR12 | Urban | Planned |  | 127 | 194 |  |  | No
07/11/2019 | 10:22 | SR13 | Urban | Planned |  | 176 | 161 |  |  | No
07/11/2019 | 13:54 | SR13 | Urban | Planned |  | 34 | 88 |  |  | No
08/11/2019 | 07:32 | CDA22 | Urban | Planned |  | 31 | 245 |  |  | No
08/11/2019 | 08:00 | DN11 | Urban | Planned |  | 87 | 424.5 |  |  | No
08/11/2019 | 08:03 | NP31 | Urban | Planned |  | 38 | 287 |  |  | No
08/11/2019 | 08:05 | MR15 | Urban | Planned |  | 2 | 65 |  |  | No
08/11/2019 | 08:15 | DC10 | Urban | Planned |  | 12 | 85 |  |  | No
08/11/2019 | 08:15 | NW22 | Urban | Planned |  | 52 | 545 |  |  | No
08/11/2019 | 08:30 | NW23 | Urban | Planned |  | 6 | 380 |  |  | No
08/11/2019 | 08:50 | STO23 | Urban | Planned |  | 142 | 270 |  |  | No
08/11/2019 | 08:56 | MTN32 | Rural Short | Planned |  | 58 | 349 |  |  | No
08/11/2019 | 09:10 | HT11 | Urban | Planned |  | 53 | 275 |  |  | No
08/11/2019 | 09:16 | MTN35 | Rural Short | Planned |  | 142 | 354 |  |  | No
08/11/2019 | 09:18 | M25 | Urban | Planned |  | 11 | 371 |  |  | No
08/11/2019 | 09:18 | MC6 | Urban | Planned |  | 56 | 371 |  |  | No
08/11/2019 | 10:00 | DN13 | Urban | Planned |  | 178 | 150 |  |  | No
08/11/2019 | 10:31 | MR23 | Urban | Planned |  | 42 | 180 |  |  | No
08/11/2019 | 12:00 | K12 | Urban | Planned |  | 9 | 130 |  |  | No
08/11/2019 | 12:25 | NW23 | Urban | Planned |  | 66 | 85 |  |  | No
09/11/2019 | 06:30 | GW5 | Urban | Planned |  | 1 | 540 |  |  | No
09/11/2019 | 08:21 | LWN34 | Urban | Planned |  | 210 | 312 |  |  | No
09/11/2019 | 08:30 | EB21 | Urban | Planned |  | 8 | 440 |  |  | No
09/11/2019 | 14:38 | M34 | Urban | Planned |  | 1 | 69 |  |  | No
10/11/2019 | 05:30 | HT8 | Urban | Planned |  | 17 | 59 |  |  | No
10/11/2019 | 07:05 | SS14 | Urban | Planned |  | 2 | 575 |  |  | No
10/11/2019 | 07:14 | HT13 | Urban | Planned |  | 23 | 257 |  |  | No
10/11/2019 | 08:00 | LD7 | Urban | Planned |  | 33 | 225 |  |  | No
10/11/2019 | 08:00 | LWN32 | Rural Short | Planned |  | 1 | 540 |  |  | No
10/11/2019 | 08:25 | OR32 | Urban | Planned |  | 1 | 330 |  |  | No
10/11/2019 | 08:25 | OR33 | Urban | Planned |  | 92 | 330 |  |  | No
10/11/2019 | 09:45 | MGE13 | Urban | Planned |  | 24 | 168 |  |  | No
10/11/2019 | 12:03 | HT2 | Urban | Planned |  | 29 | 106 |  |  | No
11/11/2019 | 11:00 | M32 | Urban | Planned |  | 53 | 300 |  |  | No
12/11/2019 | 07:36 | LD2 | Urban | Planned |  | 16 | 354 |  |  | No
12/11/2019 | 08:00 | M25 | Urban | Planned |  | 1 | 600 |  |  | No
12/11/2019 | 08:01 | SR23 | Urban | Planned |  | 44 | 170 |  |  | No
12/11/2019 | 08:20 | M25 | Urban | Planned |  | 139 | 370 |  |  | No
12/11/2019 | 08:28 | MR13 | Urban | Planned |  | 15 | 422 |  |  | No
12/11/2019 | 08:32 | STO14 | Rural Short | Planned |  | 48 | 131 |  |  | No
12/11/2019 | 08:38 | GW4 | Urban | Planned |  | 1 | 179 |  |  | No
12/11/2019 | 08:38 | GW8 | Urban | Planned |  | 70 | 179 |  |  | No
12/11/2019 | 08:38 | NW23 | Urban | Planned |  | 39 | 207 |  |  | No
12/11/2019 | 08:45 | HT4 | Urban | Planned |  | 68 | 248 |  |  | No
12/11/2019 | 10:02 | FSH13 | Urban | Planned |  | 178 | 362 |  |  | No
12/11/2019 | 10:05 | EM5 | Urban | Planned |  | 22 | 115 |  |  | No
13/11/2019 | 07:30 | SR24 | Urban | Planned |  | 1 | 540 |  |  | No
13/11/2019 | 07:41 | MR11 | Urban | Planned |  | 71 | 182 |  |  | No
13/11/2019 | 07:41 | SR24 | Urban | Planned |  | 58 | 182 |  |  | No
13/11/2019 | 08:00 | CDA24 | Urban | Planned |  | 56 | 350 |  |  | No
13/11/2019 | 08:00 | CDA24 | Urban | Planned |  | 1 | 570 |  |  | No
13/11/2019 | 08:00 | DC10 | Urban | Planned |  | 1 | 480 |  |  | No
13/11/2019 | 08:00 | HGS22 | Rural Short | Planned |  | 130 | 494 |  |  | No
13/11/2019 | 08:00 | HGS23 | Rural Short | Planned |  | 37 | 240 |  |  | No
13/11/2019 | 08:00 | MR15 | Urban | Planned |  | 95 | 350 |  |  | No
13/11/2019 | 08:00 | RBD23 | Urban | Planned |  | 140 | 191 |  |  | No
13/11/2019 | 08:00 | SR19 | Urban | Planned |  | 56 | 234 |  |  | No
13/11/2019 | 08:04 | DC10 | Urban | Planned |  | 122 | 270 |  |  | No
13/11/2019 | 08:05 | KBH34 | Urban | Planned |  | 5 | 275 |  |  | No
13/11/2019 | 08:11 | MR22 | Urban | Planned |  | 103 | 464 |  |  | No
13/11/2019 | 08:20 | FSH33 | Urban | Planned |  | 46 | 325 |  |  | No
13/11/2019 | 08:29 | NW13 | Urban | Planned |  | 62 | 489 |  |  | No
13/11/2019 | 08:30 | HGS23 | Rural Short | Planned |  | 77 | 270 |  |  | No
13/11/2019 | 08:30 | NW31 | Urban | Planned |  | 15 | 75 |  |  | No
13/11/2019 | 08:52 | K6 | Urban | Planned |  | 87 | 764 |  |  | No
13/11/2019 | 09:01 | MTN35 | Rural Short | Planned |  | 230 | 370 |  |  | No
13/11/2019 | 09:30 | FSH22 | Urban | Planned |  | 80 | 313 |  |  | No
13/11/2019 | 10:10 | SR19 | Urban | Planned |  | 74 | 232 |  |  | No
13/11/2019 | 10:50 | BU4 | Urban | Planned |  | 50 | 100 |  |  | No
14/11/2019 | 08:00 | NW23 | Urban | Planned |  | 2 | 510 |  |  | No
14/11/2019 | 08:00 | RBD23 | Urban | Planned |  | 201 | 315 |  |  | No
14/11/2019 | 08:00 | BU14 | Urban | Planned |  | 28 | 284.6 |  |  | No
14/11/2019 | 08:02 | NW23 | Urban | Planned |  | 341 | 310 |  |  | No
14/11/2019 | 08:11 | HT2 | Urban | Planned |  | 232 | 386 |  |  | No
14/11/2019 | 08:30 | KBH32 | Urban | Planned |  | 3 | 280 |  |  | No
14/11/2019 | 08:55 | KBH32 | Urban | Planned |  | 127 | 235 |  |  | No
14/11/2019 | 09:05 | LWN34 | Urban | Planned |  | 75 | 305 |  |  | No
14/11/2019 | 09:27 | BR4 | Urban | Planned |  | 24 | 220 |  |  | No
14/11/2019 | 09:43 | HGS22 | Rural Short | Planned |  | 6 | 22 |  |  | No
14/11/2019 | 09:45 | HGS22 | Rural Short | Planned |  | 2 | 30 |  |  | No
14/11/2019 | 11:30 | CRM21 | Urban | Planned |  | 3 | 20 |  |  | No
15/11/2019 | 08:00 | RBD23 | Urban | Planned |  | 330 | 215 |  |  | No
15/11/2019 | 08:00 | CDA24 | Urban | Planned |  | 1 | 450 |  |  | No
15/11/2019 | 08:00 | MR11 | Urban | Planned |  | 188 | 270.6 |  |  | No
15/11/2019 | 08:10 | OR32 | Urban | Planned |  | 110 | 230 |  |  | No
15/11/2019 | 08:14 | EW3 | Urban | Planned |  | 105 | 165 |  |  | No
15/11/2019 | 08:20 | BT4 | Urban | Planned |  | 3 | 160 |  |  | No
15/11/2019 | 08:24 | CFD13 | Urban | Planned |  | 164 | 276 |  |  | No
15/11/2019 | 08:24 | CFD14 | Urban | Planned |  | 64 | 276 |  |  | No
15/11/2019 | 08:30 | EL6 | Urban | Planned |  | 76 | 165 |  |  | No
15/11/2019 | 08:30 | HT2 | Urban | Planned |  | 121 | 240 |  |  | No
15/11/2019 | 08:45 | EL6 | Urban | Planned |  | 82 | 140 |  |  | No
15/11/2019 | 08:45 | EL8 | Urban | Planned |  | 41 | 140 |  |  | No
15/11/2019 | 08:47 | FTN13 | Urban | Planned |  | 49 | 315 |  |  | No
15/11/2019 | 09:45 | CDA24 | Urban | Planned |  | 50 | 165 |  |  | No
15/11/2019 | 11:30 | OR32 | Urban | Planned |  | 1 | 300 |  |  | No
15/11/2019 | 12:30 | M21 | Urban | Planned |  | 8 | 90 |  |  | No
15/11/2019 | 12:45 | OR32 | Urban | Planned |  | 113 | 185 |  |  | No
15/11/2019 | 14:30 | BT2 | Urban | Planned |  | 7 | 20 |  |  | No
16/11/2019 | 08:00 | NB32 | Urban | Planned |  | 7 | 540 |  |  | No
16/11/2019 | 08:05 | CDA24 | Urban | Planned |  | 138 | 467 |  |  | No
17/11/2019 | 06:30 | LD5 | Urban | Planned |  | 2 | 540 |  |  | No
17/11/2019 | 07:20 | HT13 | Urban | Planned |  | 23 | 124 |  |  | No
17/11/2019 | 07:20 | LD5 | Urban | Planned |  | 4 | 190 |  |  | No
17/11/2019 | 07:28 | STO14 | Rural Short | Planned |  | 86 | 576 |  |  | No
17/11/2019 | 07:30 | EB22 | Urban | Planned |  | 66 | 240 |  |  | No
17/11/2019 | 07:53 | NW22 | Urban | Planned |  | 13 | 264 |  |  | No
17/11/2019 | 08:00 | MTN34 | Urban | Planned |  | 65 | 368 |  |  | No
17/11/2019 | 08:15 | FTN24 | Urban | Planned |  | 86 | 500 |  |  | No
17/11/2019 | 08:30 | HT2 | Urban | Planned |  | 21 | 50 |  |  | No
17/11/2019 | 08:30 | HT7 | Urban | Planned |  | 5 | 50 |  |  | No
17/11/2019 | 09:05 | CDA24 | Urban | Planned |  | 62 | 136 |  |  | No
17/11/2019 | 09:25 | FTN24 | Urban | Planned |  | 59 | 399 |  |  | No
18/11/2019 | 08:00 | NW22 | Urban | Planned |  | 1 | 510 |  |  | No
18/11/2019 | 08:04 | NW22 | Urban | Planned |  | 194 | 442 |  |  | No
18/11/2019 | 08:25 | STO23 | Urban | Planned |  | 235 | 385 |  |  | No
18/11/2019 | 09:01 | BU2 | Urban | Planned |  | 19 | 293 |  |  | No
19/11/2019 | 07:00 | DMA12 | Urban | Planned |  | 66 | 125 |  |  | No
19/11/2019 | 07:28 | WD36 | Urban | Planned |  | 2 | 542 |  |  | No
19/11/2019 | 08:00 | MC7 | Urban | Planned |  | 184 | 105 |  |  | No
19/11/2019 | 08:00 | OE2 | Urban | Planned |  | 168 | 455 |  |  | No
19/11/2019 | 08:00 | SR13 | Urban | Planned |  | 7 | 450.8 |  |  | No
19/11/2019 | 08:13 | CDA24 | Urban | Planned |  | 52 | 193 |  |  | No
19/11/2019 | 08:15 | NO7 | Urban | Planned |  | 199 | 360 |  |  | No
19/11/2019 | 08:16 | RBD21 | Rural Short | Planned |  | 4 | 24 |  |  | No
19/11/2019 | 08:30 | DMA24 | Rural Short | Planned |  | 2 | 150 |  |  | No
19/11/2019 | 08:40 | STO13 | Urban | Planned |  | 72 | 485 |  |  | No
19/11/2019 | 08:50 | EL6 | Urban | Planned |  | 198 | 330 |  |  | No
19/11/2019 | 09:00 | EM7 | Urban | Planned |  | 381 | 360 |  |  | No
19/11/2019 | 09:00 | NO6 | Urban | Planned |  | 7 | 180 |  |  | No
19/11/2019 | 09:05 | RBD12 | Rural Short | Planned |  | 4 | 15 |  |  | No
19/11/2019 | 10:00 | DMA14 | Urban | Planned |  | 64 | 117.5 |  |  | No
19/11/2019 | 10:02 | EB24 | Urban | Planned |  | 82 | 240 |  |  | No
19/11/2019 | 10:18 | DMA23 | Rural Short | Planned |  | 1 | 15 |  |  | No
19/11/2019 | 11:00 | DMA23 | Rural Short | Planned |  | 2 | 15 |  |  | No
19/11/2019 | 13:05 | DMA23 | Rural Short | Planned |  | 2 | 5 |  |  | No
19/11/2019 | 13:39 | EB21 | Urban | Planned |  | 75 | 81 |  |  | No
20/11/2019 | 07:21 | DMA23 | Rural Short | Planned |  | 11 | 129.7 |  |  | No
20/11/2019 | 08:00 | CDA24 | Urban | Planned |  | 46 | 510 |  |  | No
20/11/2019 | 08:00 | M13 | Urban | Planned |  | 1 | 450 |  |  | No
20/11/2019 | 08:00 | NP23 | Urban | Planned |  | 57 | 250 |  |  | No
20/11/2019 | 08:27 | NO7 | Urban | Planned |  | 130 | 185 |  |  | No
20/11/2019 | 08:30 | DC5 | Urban | Planned |  | 52 | 90 |  |  | No
20/11/2019 | 08:30 | DMA23 | Rural Short | Planned |  | 1 | 14.4 |  |  | No
20/11/2019 | 08:45 | M13 | Urban | Planned |  | 124 | 270 |  |  | No
20/11/2019 | 08:45 | MC6 | Urban | Planned |  | 91 | 270 |  |  | No
20/11/2019 | 09:30 | CFD14 | Urban | Planned |  | 149 | 220 |  |  | No
20/11/2019 | 11:29 | RBD21 | Rural Short | Planned |  | 1 | 12 |  |  | No
20/11/2019 | 13:00 | RBD21 | Rural Short | Planned |  | 2 | 24.7 |  |  | No
20/11/2019 | 21:00 | M12 | Urban | Planned |  | 2 | 510 |  |  | No
20/11/2019 | 21:00 | M12 | Urban | Planned |  | 1 | 660 |  |  | No
20/11/2019 | 21:05 | M12 | Urban | Planned |  | 91 | 590 |  |  | No
21/11/2019 | 08:00 | CRM44 | Urban | Planned |  | 2 | 450 |  |  | No
21/11/2019 | 08:00 | RBD12 | Rural Short | Planned |  | 15 | 232 |  |  | No
21/11/2019 | 08:00 | BT9 | Urban | Planned |  | 9 | 464.4 |  |  | No
21/11/2019 | 08:30 | BH22 | Urban | Planned |  | 43 | 140 |  |  | No
21/11/2019 | 08:30 | CRM15 | Urban | Planned |  | 94 | 75 |  |  | No
21/11/2019 | 08:30 | RBD24 | Urban | Planned |  | 197 | 80 |  |  | No
21/11/2019 | 08:30 | RBD24 | Urban | Planned |  | 1 | 240 |  |  | No
21/11/2019 | 08:39 | DC5 | Urban | Planned |  | 53 | 200 |  |  | No
21/11/2019 | 08:42 | EL6 | Urban | Planned |  | 130 | 197 |  |  | No
21/11/2019 | 11:15 | RBD21 | Rural Short | Planned |  | 8 | 35 |  |  | No
21/11/2019 | 12:00 | RBD24 | Urban | Planned |  | 36 | 105 |  |  | No
21/11/2019 | 12:10 | RBD21 | Rural Short | Planned |  | 4 | 50 |  |  | No
22/11/2019 | 08:00 | DMA14 | Urban | Planned |  | 74 | 165 |  |  | No
22/11/2019 | 08:12 | BW35 | Urban | Planned |  | 82 | 441 |  |  | No
22/11/2019 | 08:12 | OAK21 | Urban | Planned |  | 22 | 441 |  |  | No
22/11/2019 | 09:30 | EB11 | Urban | Planned |  | 24 | 90 |  |  | No
23/11/2019 | 08:22 | FSH12 | Rural Short | Planned |  | 5 | 167 |  |  | No
23/11/2019 | 08:32 | LWN21 | Rural Short | Planned |  | 45 | 420 |  |  | No
24/11/2019 | 02:44 | DN21 | Urban | Planned |  | 70 | 4 |  |  | No
24/11/2019 | 07:15 | MR15 | Urban | Planned |  | 21 | 390 |  |  | No
24/11/2019 | 07:19 | MR15 | Urban | Planned |  | 21 | 389 |  |  | No
24/11/2019 | 08:00 | SS21 | Urban | Planned |  | 1 | 510 |  |  | No
24/11/2019 | 08:05 | SS21 | Urban | Planned |  | 19 | 537 |  |  | No
24/11/2019 | 08:07 | DVY34 | Urban | Planned |  | 11 | 341 |  |  | No
24/11/2019 | 08:15 | M12 | Urban | Planned |  | 9 | 455 |  |  | No
24/11/2019 | 08:30 | FTN23 | Urban | Planned |  | 35 | 15 |  |  | No
24/11/2019 | 09:05 | LWN24 | Urban | Planned |  | 63 | 450 |  |  | No
25/11/2019 | 07:20 | EB14 | Urban | Planned |  | 2 | 165 |  |  | No
25/11/2019 | 08:00 | NP23 | Urban | Planned |  | 73 | 180 |  |  | No
25/11/2019 | 08:31 | CRM15 | Urban | Planned |  | 86 | 431 |  |  | No
25/11/2019 | 08:31 | HT11 | Urban | Planned |  | 265 | 424 |  |  | No
25/11/2019 | 08:40 | BW21 | Urban | Planned |  | 23 | 250 |  |  | No
25/11/2019 | 11:25 | MTN21 | Urban | Planned |  | 8 | 85 |  |  | No
25/11/2019 | 12:18 | EB21 | Urban | Planned |  | 17 | 99 |  |  | No
26/11/2019 | 08:12 | BW21 | Urban | Planned |  | 25 | 303 |  |  | No
26/11/2019 | 08:12 | BW32 | Urban | Planned |  | 35 | 303 |  |  | No
26/11/2019 | 08:30 | MC6 | Urban | Planned |  | 30 | 225 |  |  | No
26/11/2019 | 08:30 | STO14 | Rural Short | Planned |  | 60 | 465 |  |  | No
26/11/2019 | 08:40 | SR13 | Urban | Planned |  | 21 | 410.1 |  |  | No
26/11/2019 | 08:54 | RBD21 | Rural Short | Planned |  | 45 | 249 |  |  | No
26/11/2019 | 09:18 | MC6 | Urban | Planned |  | 148 | 297 |  |  | No
26/11/2019 | 11:30 | MGE12 | Urban | Planned |  | 93 | 190 |  |  | No
26/11/2019 | 11:30 | MGE21 | Urban | Planned |  | 3 | 190 |  |  | No
27/11/2019 | 08:00 | DMA14 | Urban | Planned |  | 152 | 350 |  |  | No
27/11/2019 | 08:00 | DMA14 | Urban | Planned |  | 1 | 480 |  |  | No
27/11/2019 | 08:00 | HT7 | Urban | Planned |  | 3 | 3,210.0 |  |  | No
27/11/2019 | 08:00 | MR22 | Urban | Planned |  | 2 | 450 |  |  | No
27/11/2019 | 08:00 | MR22 | Urban | Planned |  | 144 | 580 |  |  | No
27/11/2019 | 08:00 | NW13 | Urban | Planned |  | 80 | 420 |  |  | No
27/11/2019 | 08:00 | NW23 | Urban | Planned |  | 57 | 420 |  |  | No
27/11/2019 | 08:00 | RBD12 | Rural Short | Planned |  | 2 | 510 |  |  | No
27/11/2019 | 08:25 | EB14 | Urban | Planned |  | 80 | 170 |  |  | No
27/11/2019 | 08:30 | RBD12 | Rural Short | Planned |  | 113 | 290 |  |  | No
27/11/2019 | 09:00 | M23 | Urban | Planned |  | 55 | 120 |  |  | No
27/11/2019 | 12:45 | EB21 | Urban | Planned |  | 20 | 75 |  |  | No
28/11/2019 | 07:00 | NW13 | Urban | Planned |  | 36 | 595 |  |  | No
28/11/2019 | 07:03 | DC7 | Urban | Planned |  | 89 | 265 |  |  | No
28/11/2019 | 07:03 | M25 | Urban | Planned |  | 243 | 243 |  |  | No
28/11/2019 | 08:05 | MR22 | Urban | Planned |  | 56 | 233 |  |  | No
28/11/2019 | 08:15 | CDA24 | Urban | Planned |  | 104 | 385 |  |  | No
28/11/2019 | 08:25 | K7 | Urban | Planned |  | 70 | 505 |  |  | No
28/11/2019 | 08:30 | RBD23 | Urban | Planned |  | 143 | 250 |  |  | No
28/11/2019 | 08:30 | RBD23 | Urban | Planned |  | 1 | 420 |  |  | No
28/11/2019 | 08:40 | RBD21 | Rural Short | Planned |  | 1 | 10 |  |  | No
28/11/2019 | 08:57 | SR23 | Urban | Planned |  | 151 | 440 |  |  | No
28/11/2019 | 09:30 | BW32 | Urban | Planned |  | 65 | 180 |  |  | No
28/11/2019 | 09:45 | BW22 | Urban | Planned |  | 21 | 150 |  |  | No
28/11/2019 | 09:45 | BW32 | Urban | Planned |  | 125 | 150 |  |  | No
28/11/2019 | 09:50 | DMA23 | Rural Short | Planned |  | 2 | 10 |  |  | No
28/11/2019 | 10:25 | NW23 | Urban | Planned |  | 2 | 50 |  |  | No
29/11/2019 | 08:00 | CDA24 | Urban | Planned |  | 239 | 295 |  |  | No
29/11/2019 | 08:00 | EB11 | Urban | Planned |  | 117 | 180 |  |  | No
29/11/2019 | 08:00 | EB24 | Urban | Planned |  | 30 | 180 |  |  | No
29/11/2019 | 08:00 | MR15 | Urban | Planned |  | 59 | 295 |  |  | No
29/11/2019 | 08:30 | EB14 | Urban | Planned |  | 57 | 191 |  |  | No
29/11/2019 | 08:35 | EB24 | Urban | Planned |  | 108 | 275 |  |  | No
29/11/2019 | 08:35 | MC6 | Urban | Planned |  | 161 | 475 |  |  | No
29/11/2019 | 08:35 | RBD23 | Urban | Planned |  | 241 | 205 |  |  | No
29/11/2019 | 11:00 | EB14 | Urban | Planned |  | 1 | 300 |  |  | No
29/11/2019 | 11:46 | EB14 | Urban | Planned |  | 78 | 135 |  |  | No
29/11/2019 | 11:55 | EL9 | Urban | Planned |  | 100 | 185 |  |  | No
29/11/2019 | 12:45 | EB24 | Urban | Planned |  | 71 | 115 |  |  | No
30/11/2019 | 08:00 | BW32 | Urban | Planned |  | 89 | 177 |  |  | No
30/11/2019 | 08:00 | CRM22 | Urban | Planned |  | 95 | 340 |  |  | No
30/11/2019 | 08:00 | SVW53 | Urban | Planned |  | 85 | 176.6 |  |  | No
30/11/2019 | 08:06 | CRM34 | Urban | Planned |  | 46 | 390 |  |  | No
30/11/2019 | 10:20 | OAK21 | Urban | Planned |  | 48 | 320 |  |  | No
30/11/2019 | 10:20 | OAK26 | Urban | Planned |  | 4 | 320 |  |  | No
01/12/2019 | 06:51 | HT7 | Urban | Planned |  | 66 | 506 |  |  | No
01/12/2019 | 07:00 | NP11 | Urban | Planned |  | 8 | 620 |  |  | No
01/12/2019 | 07:28 | K2 | Urban | Planned |  | 113 | 322 |  |  | No
01/12/2019 | 07:30 | CDA24 | Urban | Planned |  | 2 | 540 |  |  | No
01/12/2019 | 07:30 | MR13 | Urban | Planned |  | 1 | 600 |  |  | No
01/12/2019 | 07:30 | K2 | Urban | Planned |  | 1 | 480 |  |  | No
01/12/2019 | 07:45 | M12 | Urban | Planned |  | 82 | 460 |  |  | No
01/12/2019 | 08:00 | CDA21 | Urban | Planned |  | 1 | 510 |  |  | No
01/12/2019 | 08:00 | CM12 | Urban | Planned |  | 84 | 315 |  |  | No
01/12/2019 | 08:02 | CDA21 | Urban | Planned |  | 29 | 448 |  |  | No
01/12/2019 | 08:15 | SS22 | Urban | Planned |  | 26 | 257 |  |  | No
01/12/2019 | 08:16 | RBD21 | Rural Short | Planned |  | 65 | 230 |  |  | No
01/12/2019 | 08:17 | CM13 | Urban | Planned |  | 162 | 273 |  |  | No
01/12/2019 | 08:23 | LD6 | Urban | Planned |  | 75 | 92 |  |  | No
01/12/2019 | 08:40 | MR13 | Urban | Planned |  | 90 | 395 |  |  | No
01/12/2019 | 08:45 | CDA24 | Urban | Planned |  | 247 | 514 |  |  | No
01/12/2019 | 09:30 | SR15 | Urban | Planned |  | 72 | 425 |  |  | No
01/12/2019 | 13:10 | RBD21 | Rural Short | Planned |  | 25 | 50 |  |  | No
02/12/2019 | 07:30 | MR21 | Urban | Planned |  | 1 | 510 |  |  | No
02/12/2019 | 08:00 | MR21 | Urban | Planned |  | 111 | 345 |  |  | No
02/12/2019 | 08:00 | MR32 | Urban | Planned |  | 1 | 510 |  |  | No
02/12/2019 | 08:08 | DC10 | Urban | Planned |  | 23 | 437 |  |  | No
02/12/2019 | 08:08 | NW23 | Urban | Planned |  | 96 | 437 |  |  | No
02/12/2019 | 08:11 | NW13 | Urban | Planned |  | 16 | 336 |  |  | No
02/12/2019 | 08:11 | NW22 | Urban | Planned |  | 130 | 336 |  |  | No
02/12/2019 | 09:09 | MR32 | Urban | Planned |  | 100 | 265 |  |  | No
02/12/2019 | 09:30 | HGS22 | Rural Short | Planned |  | 4 | 5 |  |  | No
02/12/2019 | 11:01 | DMA23 | Rural Short | Planned |  | 2 | 43 |  |  | No
03/12/2019 | 08:00 | EB24 | Urban | Planned |  | 5 | 510 |  |  | No
03/12/2019 | 08:00 | EM11 | Urban | Planned |  | 1 | 480 |  |  | No
03/12/2019 | 08:00 | MR22 | Urban | Planned |  | 1 | 510 |  |  | No
03/12/2019 | 08:01 | OR32 | Urban | Planned |  | 50 | 584 |  |  | No
03/12/2019 | 08:06 | FSH34 | Urban | Planned |  | 23 | 248 |  |  | No
03/12/2019 | 08:10 | EB21 | Urban | Planned |  | 86 | 260 |  |  | No
03/12/2019 | 08:17 | MR15 | Urban | Planned |  | 141 | 439 |  |  | No
03/12/2019 | 08:17 | MR22 | Urban | Planned |  | 60 | 439 |  |  | No
03/12/2019 | 08:23 | EM11 | Urban | Planned |  | 93 | 398 |  |  | No
03/12/2019 | 08:31 | FTN13 | Urban | Planned |  | 191 | 288 |  |  | No
03/12/2019 | 08:40 | EB21 | Urban | Planned |  | 15 | 212 |  |  | No
03/12/2019 | 08:40 | NW13 | Urban | Planned |  | 13 | 195 |  |  | No
03/12/2019 | 08:45 | MGE23 | Urban | Planned |  | 56 | 375 |  |  | No
03/12/2019 | 08:48 | DMA13 | Rural Short | Planned |  | 158 | 293 |  |  | No
03/12/2019 | 08:55 | MTN31 | Urban | Planned |  | 160 | 13 |  |  | No
03/12/2019 | 09:04 | EB24 | Urban | Planned |  | 77 | 362 |  |  | No
03/12/2019 | 09:07 | LD33 | Urban | Planned |  | 37 | 198 |  |  | No
03/12/2019 | 09:07 | LD6 | Urban | Planned |  | 173 | 198 |  |  | No
03/12/2019 | 09:20 | RBD12 | Rural Short | Planned |  | 4 | 58 |  |  | No
03/12/2019 | 10:34 | MTN35 | Rural Short | Planned |  | 29 | 6 |  |  | No
03/12/2019 | 12:00 | DC10 | Urban | Planned |  | 23 | 200 |  |  | No
03/12/2019 | 12:00 | NW23 | Urban | Planned |  | 22 | 200 |  |  | No
03/12/2019 | 12:06 | RBD12 | Rural Short | Planned |  | 2 | 97 |  |  | No
04/12/2019 | 07:35 | DC2 | Urban | Planned |  | 54 | 220 |  |  | No
04/12/2019 | 08:00 | LD33 | Urban | Planned |  | 4 | 570 |  |  | No
04/12/2019 | 08:12 | EB14 | Urban | Planned |  | 42 | 209 |  |  | No
04/12/2019 | 08:19 | HT11 | Urban | Planned |  | 183 | 397 |  |  | No
04/12/2019 | 08:25 | NB32 | Urban | Planned |  | 15 | 405 |  |  | No
04/12/2019 | 08:34 | BT6 | Urban | Planned |  | 12 | 363 |  |  | No
04/12/2019 | 08:34 | LD4 | Urban | Planned |  | 29 | 190 |  |  | No
04/12/2019 | 08:34 | MR31 | Urban | Planned |  | 117 | 363 |  |  | No
04/12/2019 | 08:40 | RBD23 | Urban | Planned |  | 134 | 320 |  |  | No
04/12/2019 | 09:00 | BW34 | Urban | Planned |  | 1 | 390 |  |  | No
04/12/2019 | 09:06 | BW34 | Urban | Planned |  | 52 | 328 |  |  | No
04/12/2019 | 09:30 | BU14 | Urban | Planned |  | 44 | 259.9 |  |  | No
04/12/2019 | 09:40 | BH23 | Urban | Planned |  | 98 | 130 |  |  | No
05/12/2019 | 08:10 | DMA14 | Urban | Planned |  | 21 | 320 |  |  | No
05/12/2019 | 08:10 | DMA21 | Urban | Planned |  | 183 | 320 |  |  | No
05/12/2019 | 08:15 | CRM35 | Urban | Planned |  | 37 | 480 |  |  | No
05/12/2019 | 08:30 | BW35 | Urban | Planned |  | 41 | 120 |  |  | No
05/12/2019 | 08:40 | HT1 | Urban | Planned |  | 440 | 420 |  |  | No
05/12/2019 | 08:45 | EM6 | Urban | Planned |  | 59 | 255 |  |  | No
05/12/2019 | 10:08 | NW23 | Urban | Planned |  | 21 | 114 |  |  | No
05/12/2019 | 11:08 | BH12 | Urban | Planned |  | 58 | 205 |  |  | No
05/12/2019 | 11:22 | SR23 | Urban | Planned |  | 44 | 172 |  |  | No
05/12/2019 | 11:39 | WD36 | Urban | Planned |  | 21 | 129 |  |  | No
05/12/2019 | 12:59 | RBD12 | Rural Short | Planned |  | 2 | 89 |  |  | No
06/12/2019 | 08:00 | CDA24 | Urban | Planned |  | 57 | 180 |  |  | No
06/12/2019 | 08:00 | EM11 | Urban | Planned |  | 1 | 360 |  |  | No
06/12/2019 | 08:00 | MR32 | Urban | Planned |  | 1 | 480 |  |  | No
06/12/2019 | 08:24 | EM3 | Urban | Planned |  | 55 | 191 |  |  | No
06/12/2019 | 08:30 | MTN32 | Rural Short | Planned |  | 54 | 200 |  |  | No
06/12/2019 | 08:32 | EM11 | Urban | Planned |  | 21 | 193 |  |  | No
06/12/2019 | 08:36 | FTN23 | Urban | Planned |  | 85 | 105 |  |  | No
06/12/2019 | 08:41 | MR32 | Urban | Planned |  | 41 | 212 |  |  | No
06/12/2019 | 08:44 | DC4 | Urban | Planned |  | 3 | 180 |  |  | No
06/12/2019 | 09:30 | LD4 | Urban | Planned |  | 21 | 140 |  |  | No
06/12/2019 | 13:06 | CFD22 | Urban | Planned |  | 15 | 104 |  |  | No
07/12/2019 | 07:20 | NO2 | Urban | Planned |  | 36 | 491 |  |  | No
07/12/2019 | 07:20 | SVW41 | Urban | Planned |  | 179 | 491 |  |  | No
07/12/2019 | 07:30 | SS12 | Urban | Planned |  | 1 | 420 |  |  | No
07/12/2019 | 08:08 | FTN23 | Urban | Planned |  | 1 | 377 |  |  | No
07/12/2019 | 08:08 | FTN24 | Urban | Planned |  | 72 | 377 |  |  | No
07/12/2019 | 08:20 | DC6 | Urban | Planned |  | 61 | 420 |  |  | No
07/12/2019 | 08:25 | DC8 | Urban | Planned |  | 70 | 370 |  |  | No
07/12/2019 | 08:27 | DC8 | Urban | Planned |  | 70 | 368 |  |  | No
07/12/2019 | 09:34 | K3 | Urban | Planned |  | 2 | 81 |  |  | No
07/12/2019 | 12:23 | BW22 | Urban | Planned |  | 34 | 67 |  |  | No
08/12/2019 | 06:30 | DVY23 | Urban | Planned |  | 1 | 630 |  |  | No
08/12/2019 | 06:30 | FTN14 | Urban | Planned |  | 1 | 600 |  |  | No
08/12/2019 | 07:00 | NO32 | Urban | Planned |  | 11 | 608 |  |  | No
08/12/2019 | 07:30 | EB21 | Urban | Planned |  | 58 | 300 |  |  | No
08/12/2019 | 07:30 | FTN14 | Urban | Planned |  | 11 | 320 |  |  | No
08/12/2019 | 07:30 | KBH33 | Urban | Planned |  | 1 | 120 |  |  | No
08/12/2019 | 07:45 | DSH31 | Urban | Planned |  | 24 | 180 |  |  | No
08/12/2019 | 08:00 | CDA24 | Urban | Planned |  | 163 | 70 |  |  | No
08/12/2019 | 09:55 | SS21 | Urban | Planned |  | 64 | 180 |  |  | No
08/12/2019 | 13:10 | HT10 | Urban | Planned |  | 2 | 130 |  |  | No
09/12/2019 | 08:00 | NW31 | Urban | Planned |  | 1 | 480 |  |  | No
09/12/2019 | 08:00 | STO22 | Urban | Planned |  | 2 | 510 |  |  | No
09/12/2019 | 08:10 | NW31 | Urban | Planned |  | 204 | 380 |  |  | No
09/12/2019 | 08:15 | NW31 | Urban | Planned |  | 203 | 309 |  |  | No
09/12/2019 | 09:50 | STO22 | Urban | Planned |  | 16 | 165 |  |  | No
09/12/2019 | 10:00 | DMA23 | Rural Short | Planned |  | 73 | 265 |  |  | No
10/12/2019 | 07:55 | MTN24 | Rural Short | Planned |  | 4 | 20 |  |  | No
10/12/2019 | 08:02 | LD7 | Urban | Planned |  | 298 | 458 |  |  | No
10/12/2019 | 08:15 | BR13 | Urban | Planned |  | 13 | 210 |  |  | No
10/12/2019 | 08:15 | BR6 | Urban | Planned |  | 30 | 195 |  |  | No
10/12/2019 | 08:15 | CRM15 | Urban | Planned |  | 36 | 225 |  |  | No
10/12/2019 | 08:15 | CRM35 | Urban | Planned |  | 56 | 225 |  |  | No
10/12/2019 | 08:35 | RBD13 | Urban | Planned |  | 21 | 205 |  |  | No
10/12/2019 | 08:40 | EM9 | Urban | Planned |  | 70 | 265 |  |  | No
10/12/2019 | 09:00 | BR4 | Urban | Planned |  | 22 | 360 |  |  | No
10/12/2019 | 09:00 | FTN21 | Urban | Planned |  | 106 | 518 |  |  | No
10/12/2019 | 09:14 | K3 | Urban | Planned |  | 45 | 205 |  |  | No
10/12/2019 | 09:35 | FSH32 | Rural Short | Planned |  | 45 | 153 |  |  | No
10/12/2019 | 09:50 | MTN22 | Rural Short | Planned |  | 8 | 45 |  |  | No
10/12/2019 | 10:13 | DC2 | Urban | Planned |  | 19 | 396 |  |  | No
10/12/2019 | 12:05 | MTN32 | Rural Short | Planned |  | 8 | 15 |  |  | No
11/12/2019 | 07:46 | DMA23 | Rural Short | Planned |  | 21 | 314 |  |  | No
11/12/2019 | 08:00 | CDA24 | Urban | Planned |  | 1 | 510 |  |  | No
11/12/2019 | 08:00 | CDA24 | Urban | Planned |  | 278 | 520 |  |  | No
11/12/2019 | 08:00 | FSH23 | Rural Short | Planned |  | 180 | 250 |  |  | No
11/12/2019 | 08:05 | SVW53 | Urban | Planned |  | 48 | 160 |  |  | No
11/12/2019 | 08:11 | EM9 | Urban | Planned |  | 2 | 344 |  |  | No
11/12/2019 | 08:15 | FSH23 | Rural Short | Planned |  | 40 | 140 |  |  | No
11/12/2019 | 08:24 | FSH31 | Urban | Planned |  | 15 | 244 |  |  | No
11/12/2019 | 08:35 | SR25 | Urban | Planned |  | 51 | 550 |  |  | No
11/12/2019 | 08:40 | RBD12 | Rural Short | Planned |  | 2 | 195 |  |  | No
11/12/2019 | 12:21 | RBD12 | Rural Short | Planned |  | 5 | 61 |  |  | No
12/12/2019 | 07:00 | DC3 | Urban | Planned |  | 4 | 402 |  |  | No
12/12/2019 | 07:30 | NW23 | Urban | Planned |  | 66 | 364.5 |  |  | No
12/12/2019 | 08:03 | NP36 | Urban | Planned |  | 2 | 477 |  |  | No
12/12/2019 | 08:04 | SS22 | Urban | Planned |  | 138 | 398 |  |  | No
12/12/2019 | 08:08 | MGE13 | Urban | Planned |  | 5 | 157 |  |  | No
12/12/2019 | 08:25 | OE9 | Urban | Planned |  | 1 | 312 |  |  | No
12/12/2019 | 08:45 | EM9 | Urban | Planned |  | 49 | 225 |  |  | No
12/12/2019 | 09:11 | DC8 | Urban | Planned |  | 152 | 484 |  |  | No
12/12/2019 | 09:53 | CDA24 | Urban | Planned |  | 70 | 263 |  |  | No
12/12/2019 | 13:00 | EM9 | Urban | Planned |  | 35 | 130 |  |  | No
13/12/2019 | 03:05 | MTN23 | Urban | Planned |  | 2 | 115 |  |  | No
13/12/2019 | 08:00 | BH21 | Urban | Planned |  | 1 | 480 |  |  | No
13/12/2019 | 08:04 | DC5 | Urban | Planned |  | 21 | 303 |  |  | No
13/12/2019 | 08:15 | SS13 | Urban | Planned |  | 155 | 255 |  |  | No
13/12/2019 | 08:21 | LWN24 | Urban | Planned |  | 151 | 271 |  |  | No
13/12/2019 | 08:25 | BH21 | Urban | Planned |  | 75 | 245 |  |  | No
13/12/2019 | 08:28 | EB24 | Urban | Planned |  | 77 | 377 |  |  | No
13/12/2019 | 08:49 | EM7 | Urban | Planned |  | 277 | 354 |  |  | No
14/12/2019 | 07:00 | MGE21 | Urban | Planned |  | 1 | 600 |  |  | No
14/12/2019 | 07:29 | HGS33 | Rural Short | Planned |  | 116 | 571 |  |  | No
14/12/2019 | 08:00 | MGE21 | Urban | Planned |  | 51 | 462 |  |  | No
14/12/2019 | 08:03 | RBD12 | Rural Short | Planned |  | 2 | 137 |  |  | No
14/12/2019 | 10:36 | DVY11 | Urban | Planned |  | 1 | 10 |  |  | No
14/12/2019 | 11:49 | RBD12 | Rural Short | Planned |  | 5 | 29 |  |  | No
15/12/2019 | 06:43 | DSH24 | Urban | Planned |  | 2 | 345 |  |  | No
15/12/2019 | 07:20 | DSH14 | Urban | Planned |  | 2 | 145 |  |  | No
15/12/2019 | 07:28 | HGS33 | Rural Short | Planned |  | 116 | 378 |  |  | No
15/12/2019 | 07:30 | BH21 | Urban | Planned |  | 189 | 420 |  |  | No
15/12/2019 | 07:47 | HT3 | Urban | Planned |  | 12 | 518 |  |  | No
15/12/2019 | 08:00 | MGE31 | Urban | Planned |  | 124 | 173 |  |  | No
15/12/2019 | 08:06 | DSH14 | Urban | Planned |  | 16 | 477 |  |  | No
15/12/2019 | 08:25 | MTN22 | Rural Short | Planned |  | 3 | 45 |  |  | No
15/12/2019 | 08:34 | LWN21 | Rural Short | Planned |  | 116 | 4 |  |  | No
15/12/2019 | 08:48 | DSH24 | Urban | Planned |  | 2 | 80 |  |  | No
16/12/2019 | 08:30 | BT15 | Urban | Planned |  | 25 | 340 |  |  | No
16/12/2019 | 08:49 | GW6 | Urban | Planned |  | 6 | 215 |  |  | No
16/12/2019 | 09:00 | DC2 | Urban | Planned |  | 50 | 175 |  |  | No
16/12/2019 | 10:07 | RWT23 | Urban | Planned |  | 41 | 399 |  |  | No
16/12/2019 | 11:30 | DC8 | Urban | Planned |  | 29 | 110 |  |  | No
17/12/2019 | 08:00 | BH21 | Urban | Planned |  | 197 | 325 |  |  | No
17/12/2019 | 08:00 | CM22 | Urban | Planned |  | 203 | 405 |  |  | No
17/12/2019 | 08:00 | SH32 | Urban | Planned |  | 136 | 325 |  |  | No
17/12/2019 | 08:00 | SS12 | Urban | Planned |  | 66 | 300 |  |  | No
17/12/2019 | 08:19 | DN2 | Urban | Planned |  | 11 | 144 |  |  | No
17/12/2019 | 08:20 | FTN21 | Urban | Planned |  | 3 | 40 |  |  | No
17/12/2019 | 08:30 | NP14 | Urban | Planned |  | 28 | 240 |  |  | No
17/12/2019 | 08:35 | HGS31 | Rural Short | Planned |  | 5 | 290 |  |  | No
17/12/2019 | 08:45 | BH21 | Urban | Planned |  | 58 | 120 |  |  | No
17/12/2019 | 08:45 | BH31 | Urban | Planned |  | 70 | 120 |  |  | No
17/12/2019 | 08:50 | SS14 | Urban | Planned |  | 103 | 190 |  |  | No
17/12/2019 | 09:00 | NW11 | Urban | Planned |  | 9 | 245 |  |  | No
17/12/2019 | 09:55 | BC23 | Urban | Planned |  | 2 | 86 |  |  | No
18/12/2019 | 07:36 | NW13 | Urban | Planned |  | 19 | 217 |  |  | No
18/12/2019 | 08:00 | NB22 | Urban | Planned |  | 36 | 320 |  |  | No
18/12/2019 | 08:00 | NB32 | Urban | Planned |  | 43 | 320 |  |  | No
18/12/2019 | 08:04 | OR25 | Urban | Planned |  | 13 | 160 |  |  | No
18/12/2019 | 08:05 | HGS23 | Rural Short | Planned |  | 265 | 175 |  |  | No
18/12/2019 | 08:30 | MR22 | Urban | Planned |  | 14 | 90 |  |  | No
18/12/2019 | 08:36 | DC5 | Urban | Planned |  | 10 | 98 |  |  | No
18/12/2019 | 08:45 | CFD14 | Urban | Planned |  | 86 | 165 |  |  | No
18/12/2019 | 08:47 | DMA23 | Rural Short | Planned |  | 2 | 110 |  |  | No
18/12/2019 | 08:50 | DMA23 | Rural Short | Planned |  | 7 | 145 |  |  | No
18/12/2019 | 09:20 | DC8 | Urban | Planned |  | 115 | 150 |  |  | No
18/12/2019 | 09:41 | OR32 | Urban | Planned |  | 50 | 116 |  |  | No
19/12/2019 | 07:30 | CFD25 | Urban | Planned |  | 1 | 540 |  |  | No
19/12/2019 | 07:30 | EL6 | Urban | Planned |  | 203 | 315 |  |  | No
19/12/2019 | 08:00 | EM9 | Urban | Planned |  | 130 | 295 |  |  | No
19/12/2019 | 08:00 | EM9 | Urban | Planned |  | 1 | 450 |  |  | No
19/12/2019 | 08:00 | SH34 | Urban | Planned |  | 1 | 510 |  |  | No
19/12/2019 | 08:00 | SS12 | Urban | Planned |  | 173 | 240 |  |  | No
19/12/2019 | 08:10 | MTN32 | Rural Short | Planned |  | 26 | 450 |  |  | No
19/12/2019 | 08:11 | LD33 | Urban | Planned |  | 34 | 466 |  |  | No
19/12/2019 | 08:11 | LD6 | Urban | Planned |  | 3 | 466 |  |  | No
19/12/2019 | 08:30 | DC5 | Urban | Planned |  | 96 | 315 |  |  | No
19/12/2019 | 08:40 | SR11 | Urban | Planned |  | 62 | 240 |  |  | No
19/12/2019 | 08:55 | EL10 | Urban | Planned |  | 61 | 375 |  |  | No
19/12/2019 | 09:06 | OAK26 | Urban | Planned |  | 33 | 245 |  |  | No
19/12/2019 | 09:42 | CDA24 | Urban | Planned |  | 62 | 271 |  |  | No
19/12/2019 | 09:50 | MGE24 | Urban | Planned |  | 94 | 184 |  |  | No
19/12/2019 | 09:50 | SH34 | Urban | Planned |  | 89 | 230 |  |  | No
19/12/2019 | 15:44 | CDA24 | Urban | Planned |  | 3 | 131 |  |  | No
20/12/2019 | 06:16 | NW23 | Urban | Planned |  | 65 | 31 |  |  | No
20/12/2019 | 09:19 | EB21 | Urban | Planned |  | 141 | 118 |  |  | No
22/12/2019 | 07:30 | NW23 | Urban | Planned |  | 43 | 300 |  |  | No
22/12/2019 | 11:06 | DN9 | Urban | Planned |  | 60 | 118 |  |  | No
23/12/2019 | 20:27 | DVY34 | Urban | Planned |  | 7 | 8 |  |  | No
24/12/2019 | 09:00 | DC8 | Urban | Planned |  | 1 | 150 |  |  | No
27/12/2019 | 07:39 | MGE31 | Urban | Planned |  | 215 | 472 |  |  | No
27/12/2019 | 08:00 | MGE22 | Urban | Planned |  | 39 | 130 |  |  | No
27/12/2019 | 10:54 | EM11 | Urban | Planned |  | 118 | 78 |  |  | No
28/12/2019 | 07:55 | GW1 | Urban | Planned |  | 24 | 323 |  |  | No
29/12/2019 | 05:41 | BC11 | Urban | Planned |  | 8 | 219 |  |  | No
29/12/2019 | 07:26 | KBH35 | Urban | Planned |  | 11 | 27 |  |  | No
29/12/2019 | 07:34 | NW23 | Urban | Planned |  | 44 | 430 |  |  | No
29/12/2019 | 08:00 | HT6 | Urban | Planned |  | 1 | 420 |  |  | No
29/12/2019 | 08:46 | EW14 | Urban | Planned |  | 23 | 387 |  |  | No
29/12/2019 | 08:46 | EW2 | Urban | Planned |  | 115 | 387 |  |  | No
29/12/2019 | 11:31 | EL5 | Urban | Planned |  | 77 | 131 |  |  | No
29/12/2019 | 12:56 | HT6 | Urban | Planned |  | 18 | 182 |  |  | No
31/12/2019 | 08:08 | CRM21 | Urban | Planned |  | 3 | 22 |  |  | No
Contents
Instructions

## Amendments
This sheet may be used to identify amendments made to data resubmitted to the AER.
NSP data amendments
Worksheet | Table | Comments
Contents
Instructions