## Contents
ANNUAL INFORMATION ORDER
United Energy
REPORTING STATEMENT: 2024-25
| TEMPLATE DATE | 2025-01-01
CONTENTS
Business & other details
Assurance requirements by table
| Category Analysis RIN | 2.1 Expenditure summary
2.2 Repex
2.3 Augex
2.5 Connections
2.6 Non-network
2.7 Vegetation management
2.8 Maintenance
2.9 Emergency Response
2.10 Overheads
2.11 Labour
2.12 Input tables
4.1 Public lighting
4.2 Metering
4.3 Fee-based services
4.4 Quoted services
5.2 Asset Age Profile
5.3 MD - Network level
5.4 MD & utilisation
6.3 Sustained interruptions
| Economic Benchmarking RIN | 3.1 Revenue
3.2 Operating expenditure
3.2.3 Provisions
3.3 Assets (RAB)
3.4 Operational data
3.5 Physical assets
3.6 Quality of service
3.7 Operating environment
| Annual Reporting RIN | 3.6.8 Network feeders
6.2.4 STPIS Customer summary
6.6 STPIS Customer Service
6.7 STPIS Daily Performance
6.9 STPIS GSL
7.10 Juris Scheme
7.11 DMIS-DMIAM
8.1 Income
8.2 Capex
8.4 Opex
9.5 TUoS
P1.1 Cost reflective tariffs
P1.2 Non-cost reflective tariffs
| Reset RIN | 7.4 Shared Assets
| Other data | P1.3 Secondary tariffs
3.4B Total Customers
3.9 Export Services
7.5 Large Projects
8.6 Indicative asset base roll forward
8.7 Profitability - Tax data
| Additional disclosures | NSP additional information

## Business & other details
ANNUAL INFORMATION ORDER
United Energy
REPORTING STATEMENT: 2024-25
BUSINESS & OTHER DETAILS
INSTRUCTIONS
Complete the following business details regulatory template before entering data or values in any other regulatory template. This regulatory template is linked to other cells within the spreadsheet and automatically generates column headings and conditional formatting to distinguish business specific input and non-input cells.
SUBMISSION PARTICULARS INPUT SHEET
ENTITY DETAILS
Business Name
|  | Short name |  |  | United Energy
|  | Full name |  |  | United Energy Pty Ltd
|  | ACN/ABN |  |  | 70 064 651 029
|  | Business Address | [7 empty] | Postal Address
|  | Address 1 |  |  | 635 Waverley Road |  |  |  | Address 1 | PO Box 449
|  | Address 2 | [6 empty] | Address 2
|  | Suburb |  |  | Glen Waverley |  |  |  | Suburb | Mount Waverley
|  | State |  |  | VIC | Post code | 3150 |  | State | VIC | Post code | 3149
`
Contact Names
|  | Name | [6 empty] | Name
|  | Phone | [6 empty] | Phone
|  | Email | [6 empty] | Email
| ANNUAL INFORMATION ORDER |  |  | Reporting year | 2024-25
SUBMISSION DETAILS
|  |  |  | SUBMISSION type | Annual Information Order
|  |  |  | Source | Reporting
|  |  | THIS FILE | Data Quality | Consolidated
|  |  |  | Confidentiality Status | Public
|  |  |  | Amended SUBMISSION: Amendment Reason | .
|  |  |  | Submission Date | 2025-11-28

## Assurance requirements by table
ANNUAL INFORMATION ORDER
United Energy
REPORTING STATEMENT: 2024-25
ASSURANCE REQUIREMENTS
The information provided in response to the annual information order is subject to the assurance requirements set out in section 6 of the Order.
This worksheet provides a summary list of the relevant assurance standard for each table on each worksheet in this data submission workbook.
Worksheet | Table | Table disaggregation (if needed) |  | Assurance standard
|  | Sub table | Column heading | Actual information | Estimated information
2.1 Expenditure summary | 2.1.1 - STANDARD CONTROL SERVICES CAPEX BY PURPOSE |  |  | ASA805 | ASRE2405
2.1 Expenditure summary | 2.1.2 - STANDARD CONTROL SERVICES OPEX BY PURPOSE |  |  | ASA805 | ASRE2405
2.1 Expenditure summary | 2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX |  |  | ASA805 | ASRE2405
2.1 Expenditure summary | 2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX |  |  | ASA805 | ASRE2405
2.2 Repex | 2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY |  | Standard Control Services - Direct expenditure | ASA805 | ASRE2405
2.2 Repex | 2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY |  | Replacements | ASAE3000
2.2 Repex | 2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY |  | Failures | ASAE3000
2.2 Repex | 2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY | PUBLIC LIGHTING BY: ASSET TYPE; LIGHTING OBLIGATION | Direct expenditure | ASA805 | ASRE2405
2.2 Repex | 2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY | PUBLIC LIGHTING BY: ASSET TYPE; LIGHTING OBLIGATION | Operational outputs | ASAE3000
2.2 Repex | 2.2.2 - SELECTED ASSET CHARACTERISTICS | TOTAL POLES BY FEEDER TYPE |  | ASAE3000
2.2 Repex | 2.2.2 - SELECTED ASSET CHARACTERISTICS | OVERHEAD CONDUCTORS /UNDERGROUND CABLES |  | ASAE3000
2.2 Repex | 2.2.2 - SELECTED ASSET CHARACTERISTICS | TRANSFORMERS |  | ASAE3000
2.3 Augex | 2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS ¦ DESCRIPTOR METRICS |  |  | ASAE3000
2.3 Augex | 2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS ¦ COST METRICS |  |  | ASA805 | ASRE2405
2.3 Augex | 2.3.4 - AUGEX DATA - TOTAL EXPENDITURE |  |  | ASA805 | ASRE2405
2.5 Connections | 2.5.1 - DESCRIPTOR METRICS |  | Activity | ASAE3000
2.5 Connections | 2.5.1 - DESCRIPTOR METRICS |  | Expenditure | ASA805 | ASRE2405
2.5 Connections | 2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION |  | SCS Direct expenditure | ASA805 | ASRE2405
2.5 Connections | 2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION |  | New connections SCS | ASAE3000
2.5 Connections | 2.5.3 - CAPITAL CONTRIBUTIONS (TYPE 1) BY CONNECTION CLASSIFICATION |  | SCS Total expenditure | ASA805 | ASRE2405
2.5 Connections | 2.5.3 - CAPITAL CONTRIBUTIONS (TYPE 1) BY CONNECTION CLASSIFICATION |  | Connections - Type 1 capital contributions | ASA805 | ASRE2405
2.5 Connections | 2.5.4 - NEW CONNECTIONS BY CONNECTION CLASSIFICATION |  | New connections excluding SCS | ASAE3000
2.5 Connections | 2.5.4 - NEW CONNECTIONS BY CONNECTION CLASSIFICATION |  | Subdivision | ASAE3000
2.6 Non-network | 2.6.1 - NON-NETWORK EXPENDITURE |  |  | ASA805 | ASRE2405
2.6 Non-network | 2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE |  |  | ASAE3000
2.6 Non-network | 2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES |  |  | ASAE3000
2.7 Vegetation management | 2.7.1 - DESCRIPTOR METRICS BY ZONE |  |  | ASAE3000
2.7 Vegetation management | 2.7.2 - EXPENDITURE METRICS BY ZONE |  |  | ASRE2405 | ASRE2405
2.7 Vegetation management | 2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS |  |  | ASAE3000
2.8 Maintenance | 2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE |  |  | ASAE3000
2.8 Maintenance | 2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE |  |  | Not required
2.9 Emergency response | 2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX) |  |  | ASA805 | ASRE2405
2.10 Overheads | 2.10.1 - NETWORK OVERHEADS EXPENDITURE |  |  | ASA805 | ASRE2405
2.10 Overheads | 2.10.2 - CORPORATE OVERHEADS EXPENDITURE |  |  | ASA805 | ASRE2405
2.11 Labour | 2.11.3 - LABOUR / NON-LABOUR EXPENDITURE SPLIT - STANDARD CONTROL SERVICES |  |  | ASA805 | ASRE2405
2.12 Input tables | 2.12.1 - INPUT TABLES |  |  | ASRE2405 | ASRE2405
4.1 Public lighting | 4.1.1 - DESCRIPTOR METRICS OVER YEAR |  |  | ASAE3000
4.1 Public lighting | 4.1.2 - DESCRIPTOR METRICS ANNUALLY |  | Assets and services | ASAE3000
4.1 Public lighting | 4.1.2 - DESCRIPTOR METRICS ANNUALLY |  | ACS - total revenue | ASA805 | ASRE2405
4.1 Public lighting | 4.1.3 - COST METRICS |  |  | ASAE3000
4.1 Public lighting | 4.1.4 - PUBLIC LIGHTING METRICS BY TARIFF |  | Volume | ASAE3000
4.1 Public lighting | 4.1.4 - PUBLIC LIGHTING METRICS BY TARIFF |  | ACS Revenues | ASA805 | ASRE2405
4.2 Metering | 4.2.1 - METERING DESCRIPTOR METRIC |  |  | ASAE3000
4.2 Metering | 4.2.2 - COST METRICS |  | Assets and Services | ASAE3000
4.2 Metering | 4.2.2 - COST METRICS |  | Operating expenditure | ASA805 | ASRE2405
4.2 Metering | 4.2.2 - COST METRICS |  | Capital expenditure | ASA805 | ASRE2405
4.3 Fee based services | 4.3.1 - COST METRICS FOR FEE-BASED SERVICES |  | Activities and services | ASAE3000
4.3 Fee based services | 4.3.1 - COST METRICS FOR FEE-BASED SERVICES |  | Alternative Control Services - Direct expenditure | ASA805 | ASRE2405
4.4 Quoted services | 4.4.1 - COST METRICS FOR QUOTED SERVICES |  | Activities and services | ASAE3000
4.4 Quoted services | 4.4.1 - COST METRICS FOR QUOTED SERVICES |  | Alternative Control Services - Direct expenditure | ASA805 | ASRE2405
5.2 Asset Age Profile | 5.2.1 - ASSET AGE PROFILE |  |  | ASAE3000
5.3 MD - Network level | 5.3.1 - MAXIMUM DEMAND CHARACTERISTICS |  |  | ASAE3000
5.4 MD & utilisation-Spatial | 5.4.1 - NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND - SUBTRANSMISSION SUBSTATION |  |  | ASAE3000
5.4 MD & utilisation-Spatial | 5.4.1 - NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND - ZONE SUBSTATION |  |  | ASAE3000
6.3 Sustained interruptions | 6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY |  |  | ASAE3000
3.1 Revenue | 3.1.1 - REVENUE GROUPING BY CHARGEABLE QUANTITY |  |  | ASA805 | ASRE2405
3.1 Revenue | 3.1.2 - REVENUE GROUPING BY CUSTOMER TYPE OR CLASS |  |  | ASA805 | ASRE2405
3.1 Revenue | 3.1.3 - REVENUE (penalties) ALLOWED (deducted) THROUGH INCENTIVE SCHEMES |  |  | ASA805 | ASRE2405
3.2 Operating expenditure | 3.2.1 - OPEX CATEGORIES |  |  | Not required
3.2 Operating expenditure | 3.2.2 - OPEX CONSISTENCY |  |  | ASA805 | ASRE2405
3.2.3 Provisions | 3.2.3 - PROVISIONS | TOTAL PROVISIONS |  | Not required
3.2.3 Provisions | 3.2.3 - PROVISIONS | BUSINESS SPECIFIED PROVISIONS |  | ASA805 | ASRE2405
3.3 Assets (RAB) | 3.3.1 - REGULATORY ASSET BASE VALUES |  |  | Not required
3.3 Assets (RAB) | 3.3.2 - ASSET VALUE ROLL FORWARD |  | Network services | ASA805 | ASRE2405
3.3 Assets (RAB) | 3.3.2 - ASSET VALUE ROLL FORWARD |  | Standard Control Services | ASRE2405 | ASRE2405
3.3 Assets (RAB) | 3.3.2 - ASSET VALUE ROLL FORWARD |  | Alternative Control Services | ASRE2405 | ASRE2405
3.3 Assets (RAB) | 3.3.4 - ASSET LIVES |  | Network services | ASAE3000
3.3 Assets (RAB) | 3.3.4 - ASSET LIVES |  | Standard Control Services | Not required
3.3 Assets (RAB) | 3.3.4 - ASSET LIVES |  | Alternative Control Services | Not required
3.4 Operational data | 3.4.1 - ENERGY DELIVERY |  |  | ASAE3000
3.4 Operational data | 3.4.2 - CUSTOMER NUMBERS |  |  | ASAE3000
3.4 Operational data | 3.4.3 - SYSTEM DEMAND |  |  | ASAE3000
3.5 Physical assets | 3.5.1 - NETWORK CAPACITIES |  |  | ASAE3000
3.5 Physical assets | 3.5.2 - TRANSFORMER CAPACITIES |  |  | ASAE3000
3.5 Physical assets | 3.5.3 - PUBLIC LIGHTING |  |  | ASAE3000
3.6 Quality of services | 3.6.1 - RELIABILITY |  |  | ASAE3000
3.6 Quality of services | 3.6.2 - ENERGY NOT SUPPLIED |  |  | ASAE3000
3.6 Quality of services | 3.6.3 - SYSTEM LOSSES |  |  | ASAE3000
3.6 Quality of services | 3.6.4 - CAPACITY UTILISATION |  |  | ASAE3000
3.7 Operating environment | 3.7.2 - TERRAIN FACTORS |  |  | ASAE3000
3.7 Operating environment | 3.7.3 - SERVICE AREA FACTORS |  |  | ASAE3000
3.6.8 Network-feeders | 3.6.8 - NETWORK FEEDER RELIABILITY |  |  | ASAE3000
6.2.4 STPIS Customer summary | 6.2.4 - STPIS Customer summary |  |  | Not required
6.6 STPIS Customer Service | 6.6.2 - INADEQUATELY SERVED CUSTOMERS |  |  | ASAE3000
6.7 STPIS Daily Performance | 6.7.1 - DAILY PERFORMANCE DATA - UNPLANNED |  |  | ASAE3000
6.9 STPIS GSL | 6.9.1 - GUARANTEED SERVICE LEVELS - JURISDICTIONAL GSL SCHEME |  | GSL payments | ASA805 | ASRE2405
6.9 STPIS GSL | 6.9.1 - GUARANTEED SERVICE LEVELS - JURISDICTIONAL GSL SCHEME |  | Instances where GSL not met | ASAE3000
7.10 Juris Scheme | 7.10.1 - JURISDICTIONAL SCHEME PAYMENTS |  |  | ASA805 | ASRE2405
7.11 DMIA-DMIAM | 7.11.1 - DMIS - PROJECTS SUBMITTED FOR APPROVAL |  |  | ASA805 | ASRE2405
7.11 DMIA-DMIAM | 7.11.2 - DMIAM - PROJECTS SUBMITTED FOR APPROVAL |  |  | ASA805 | ASRE2405
8.1 Income | All tables |  |  | ASA805 | ASRE2405
8.2 Capex | All tables |  |  | ASA805 | ASRE2405
8.4 Opex | All tables |  |  | ASA805 | ASRE2405
9.5 TUoS | All tables |  |  | ASA805 | ASRE2405
P1.1 Cost reflective tariffs | All tables |  |  | ASAE3000
P1.2 Non-cost reflective tariffs | All tables |  |  | ASAE3000
7.4 Shared Assets | 7.4.1 - TOTAL UNREGULATED REVENUE EARNED WITH SHARED ASSETS |  |  | ASA805 | ASRE2405
P1.3 Secondary tariffs | All tables |  |  | ASAE3000
3.4B Total Customers | All tables |  |  | ASAE3000
3.9 Export Services | 3.9.1 - NET METERED VOLUME OF ENERGY EXPORTED BY CUSTOMERS WITH SMART METERS |  |  | Not required
3.9 Export Services | 3.9.2 - Network metrics - all tables |  |  | Not required
3.9 Export Services | 3.9.3 - UTILISATION AND CURTAILED ENERGY |  |  | Not required
3.9 Export Services | 3.9.4 - EXPORTING CUSTOMERS - All tables |  |  | Not required
3.9 Export Services | 3.9.5 - EXPORTING CUSTOMERS - All tables |  |  | Not required
3.9 Export Services | 3.9.6 - AS4777.2 MEASURES - COMPLIANT INVERTERS |  |  | Not required
3.9 Export Services | 3.9.7 - Service performance - All tables |  |  | Not required
3.9 Export Services | 3.9.8 - Service performance - All tables |  |  | Not required
3.9 Export Services | 3.9.9 - AVERAGE TIME OF OFFER |  |  | Not required
3.9 Export Services | 3.9.10 - EXPORT SERVICES OPEX |  |  | ASRE2405 | ASRE2405
3.9 Export Services | 3.9.11 - EXPORT SERVICES CAPEX |  |  | ASRE2405 | ASRE2405
7.5 Large projects | 7.5.1 - LARGE PROJECT EXPENDITURE |  | Standard control services (Total expenditure) |  | ASRE2405
8.6 Indicative Asset Base Roll Forward | All tables |  |  | ASA805 | ASRE2405
8.7 Profitability - tax data | 8.7.1 - PROFITABILITY TAX DATA | OWNERSHIP STRUCTURE |  | ASA805 | ASRE2405
8.7 Profitability - tax data | 8.7.1 - PROFITABILITY TAX DATA | TAX RELATED INFORMATION |  | ASA805 | ASRE2405
8.7 Profitability - tax data | 8.7.1 - PROFITABILITY TAX DATA | INTEREST EXPENSE |  | ASA805 | ASRE2405

## 2.1 Expenditure summary
| ANNUAL INFORMATION ORDER | [6 empty] | #25C6FF |  | Protected (SOCI)
| United Energy | [6 empty] | #FFCCCC |  | Confidential
| REPORTING STATEMENT: 2024-25 | [6 empty] | 12.5% Grey |  | Amended
| CA RIN 2.1 EXPENDITURE SUMMARY | [6 empty] | #FFCCCC & 12.5% Grey |  | Amended Confidential
DC07 - Capital expenditure ¦ Standard control
Capex by purpose
2.1.1 - STANDARD CONTROL SERVICES CAPEX BY PURPOSE
Former Tables:
2.1.1 - STANDARD CONTROL SERVICES CAPEX EXCLUDING DUAL FUNCTION ASSETS
2.1.5 - DUAL FUNCTION ASSETS CAPEX
2.10.1 - NETWORK OVERHEADS EXPENDITURE
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
| CAPEX BY PURPOSE |  | Excluding dual function assets |  | Dual function assets
| CAPEX BY PURPOSE (INCLUDING TOTAL CAPITAL CONTRIBUTIONS) - AER DEFINED | Units | Direct | Indirect | Direct | Indirect
| Replacement | $ | 97617155
| Export services | $ | 7076848
| Augmentation | $ | 14298220
| Connections | $ | 111231678
| ICT | $ | 30817068
| Property | $ | 13340893
| Fleet | $ | 6223564
| Other non-network | $ | 14306
| Network overheads | $ | 33884865 | 0
| Corporate overheads | $ | 0 | 0
| Total capex by purpose (including total capital contributions) | $ | 314504597 | 0 | 0 | 0
CAPITAL CONTRIBUTIONS BY PURPOSE - TYPE 1
| Replacement | $ | 0
| Export services | $ | 0
| Augmentation | $ | 0
| Connections | $ | 89899368
| ICT | $ | 0
| Property | $ | 0
| Fleet | $ | 0
| Other non-network | $ | 0
| Network overheads | $ | 0 | 0
| Corporate overheads | $ | 0 | 0
CAPITAL CONTRIBUTIONS BY PURPOSE - TYPE 2
| Replacement | $ | 0
| Export services | $ | 0
| Augmentation | $ | 0
| Connections | $ | 11661939
| ICT | $ | 0
| Property | $ | 0
| Fleet | $ | 0
| Other non-network | $ | 0
| Network overheads | $ | 0 | 0
| Corporate overheads | $ | 0 | 0
CAPITAL CONTRIBUTIONS BY PURPOSE - PWC UNDERGROUNDING CAPEX
| Replacement | $ | 0
| Export services | $ | 0
| Augmentation | $ | 0
| Connections | $ | 0
| ICT | $ | 0
| Property | $ | 0
| Fleet | $ | 0
| Other non-network | $ | 0
| Network overheads | $ | 0 | 0
| Corporate overheads | $ | 0 | 0
DC06 - Operating expenditure ¦ Standard control
Opex by purpose
2.1.2 - STANDARD CONTROL SERVICES OPEX BY PURPOSE
Former Tables:
2.1.2 - STANDARD CONTROL SERVICES OPEX - EXCLUDING DUAL FUNCTION ASSETS
2.1.6 - STANDARD CONTROL SERVICES OPEX - DUAL FUNCTION ASSETS
2.10.1 - NETWORK OVERHEADS EXPENDITURE
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
|  |  | Excluding dual function assets |  | Dual function assets
| OPEX BY PURPOSE | Units | Direct | Indirect | Direct | Indirect
| Vegetation management | $ | 18091098
| Maintenance | $ | 25552064
| Emergency response | $ | 12221255
| Non-network | $ | 48182973
| Export services | $ | 45150
| Network overheads | $ | 14310113 | 0
| Corporate overheads | $ | 33799317 | 0
| Total | $ | 152201970 | 0 | 0 | 0
DC07 - Capital expenditure ¦ Alternative control
Overheads expenditure
2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX
Alternative Control Services
|  |  | Total | Direct | [7 empty] | Indirect
|  |  |  | Public Lighting |  |  | Metering |  |  | Fee based services | Quoted services
| OVERHEADS EXPENDITURE | Units |  | Total | Energy Efficient | Non-energy efficient | Total | Smart | Legacy
| Network Overheads | $ | 1639599 | 931812 | 930252 | 1560 | 707787 | 707787 |  |  |  | 0
| Corporate overheads | $ | 0 | 0 |  |  | 0 |  |  |  |  | 0
DC06 - Operating expenditure ¦ Alternative control
Opex by purpose
2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX
Alternative Control Services
|  |  | Total | Direct | [7 empty] | Indirect
|  |  |  | Public Lighting |  |  | Metering |  |  | Fee based services | Quoted services
| OPEX BY PURPOSE | Units |  | Total | Energy Efficient | Non-energy efficient | Total | Smart | Legacy
| Operating Expenditure | $ | 17472809 | 3296569 | 1666075 | 1630494 | 1789775 | 1789775 | 0 | 5256410 | 7130055 | 0
| Network overheads | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Corporate overheads | $ | 7687171 | 985096 | 490118 | 494978 | 4415689 | 4415689 | 0 | 1251431 | 1034955 | 0
| Other ACS expenditure | $ | 0 | 0 |  |  | 0

## 2.2 Repex
| ANNUAL INFORMATION ORDER | [6 empty] | #25C6FF | Protected (SOCI)
| United Energy | [6 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [6 empty] | 12.5% Grey | Amended
| CA RIN 2.2 REPEX | [6 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
AR RIN (Workbook 2) 2.2 REPEX
DC02 - Operational outputs ¦ Replacement and maintenance
Asset replacement and maintenance activities
DC07 - Capital expenditure ¦ Standard control
Replacement expenditure
2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY
| ASSET REPLACEMENT AND MAINTENANCE ACTIVITIES AND EXPENDITURE |  | Standard Control Services - Direct expenditure | Replacements | Failures
| POLES BY: HIGHEST OPERATING VOLTAGE; MATERIAL TYPE | Units | $ | Number of assets | Number of assets
| ˂ = 1 kV; wood |  | 6841661 | 540 | 1
| > 1 kV & < = 11 kV; wood |  | 2445956 | 115 | 0
| ˃ 11 kV & < = 22 kV; wood |  | 6679020 | 325 | 0
| > 22 kV & < = 66 kV; wood |  | 2390883 | 68 | 0
| > 66 kV & < = 132 kV; wood |  | 0 | 0 | 0
| > 132 kV; wood |  | 0 | 0 | 0
| ˂ = 1 kV; concrete |  | 0 | 0 | 0
| > 1 kV & < = 11 kV; concrete |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; concrete |  | 0 | 0 | 0
| > 22 kV & < = 66 kV; concrete |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; concrete |  | 0 | 0 | 0
| > 132 kV; concrete |  | 0 | 0 | 0
| ˂ = 1 kV; steel |  | 0 | 0 | 2
| > 1 kV & < = 11 kV; steel |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; steel |  | 0 | 0 | 0
| > 22 kV & < = 66 kV; steel |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; steel |  | 0 | 0 | 0
| > 132 kV; steel |  | 0 | 0 | 0
| ˂ = 1 kV; composite pole |  | 0 | 0 | 0
| > 1 kV & < = 11 kV; composite pole |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; composite pole |  | 0 | 0 | 0
| > 22 kV & < = 66 kV; composite pole |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; composite pole |  | 0 | 0 | 0
| > 132 kV; composite pole |  | 0 | 0 | 0
| ˂ = 1 kV; pole - other technology |  | 0 | 0 | 0
| > 1 kV & < = 11 kV; pole - other technology |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; pole - other technology |  | 0 | 0 | 0
| > 22 kV & < = 66 kV; pole - other technology |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; pole - other technology |  | 0 | 0 | 0
| > 132 kV; pole - other technology |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
| Total poles |  | 18357520 | 1048 | 3
| STAKING OF/ STAKED WOODEN POLES BY: HIGHEST OPERATING VOLTAGE | Units | $ | Number of assets | Number of assets
| ˂ = 1 KV |  | 689196 | 620 | 0
| > 1 kV & < = 11 kV |  | 132104 | 114 | 0
| ˃ 11 kV & < = 22 kV |  | 358072 | 309 | 0
| > 22 kV & < = 66 kV |  | 61260 | 39 | 0
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Total wooden poles |  | 1240632 | 1082 | 0
| POLE TOP STRUCTURES BY: HIGHEST OPERATING VOLTAGE | Units | $ | Number of assets | Number of assets
| ˂ = 1 Kv |  | 14782226 | 4077 | 19
| > 1 kV & < = 11 kV |  | 1796276 | 424 | 3
| ˃ 11 kV & < = 22 kV |  | 4016846 | 995 | 9
| > 22 kV & < = 66 kV |  | 872977 | 233 | 1
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 414863 | 105 | 0
| Total pole top structures |  | 21883188 | 5834 | 32
| OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | Units | $ | km | Number of assets
| ˂ = 1 kV |  | 598410 | 2.68 | 26
| > 1 kV & < = 11 kV |  | 191945 | 0.54 | 1
| ˃ 11 kV & < = 22 kV; SWER |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; single phase |  | 150137 | 1.1 | 0
| ˃ 11 kV & < = 22 kV; multiple phase |  | 1759748 | 7.16 | 9
| > 22 kV & < = 66 kV |  | 901 | 0.06 | 0
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 3321086 | 3593 | 6
| Total overhead conductors |  | 6022227 | 3604.54 | 42
| UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | Units | $ | km | Number of assets
| ˂ = 1 kV |  | 2099151 | 5.58 | 29
| > 1 kV & < = 11 kV |  | 2201959 | 2.12 | 2
| > 11 kV & < = 22 kV |  | 2540064 | 2.75 | 10
| > 22 kV & < = 33 kV |  | 0 | 0 | 0
| > 33 kV & < = 66 kV |  | 0 | 0 | 0
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 3913216 | 613 | 6
| Total underground cables |  | 10754390 | 623.45 | 47
| SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | Units | $ | Number of assets | Number of assets
| ˂ = 11 kV; residential; simple type |  | 2821109 | 2486 | 1155
| ˂ = 11 kV; commercial & industrial; simple type |  | 244756 | 214 | 100
| ˂ = 11 kV; residential; complex type |  | 216273 | 189 | 88
| ˂ = 11 kV; commercial & industrial; complex type |  | 53122 | 46 | 22
| ˂ = 11 kV; subdivision; complex type |  | 0 | 0 | 0
| > 11 kV & < = 22 kV; commercial & industrial |  | 0 | 0 | 0
| > 11 kV & < = 22 kV; subdivision |  | 0 | 0 | 0
| > 22 kV & < = 33 kV; commercial & industrial |  | 0 | 0 | 0
| > 22 kV & < = 33 kV; subdivision |  | 0 | 0 | 0
| > 33 kV & < = 66 kV; commercial & industrial |  | 0 | 0 | 0
| > 33 kV & < = 66 kV; subdivision |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; commercial & industrial |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; subdivision |  | 0 | 0 | 0
| > 132 kV; commercial & industrial |  | 0 | 0 | 0
| > 132 kV; subdivision |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
| Total service lines |  | 3335260 | 2935 | 1365
| TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE; AMPERE RATING; NUMBER OF PHASES (AT LV) | Units | $ | Number of assets | Number of assets
| Pole mounted; < = 22kV; < = 60 kVA; single phase |  | 243952 | 25 | 2
| Pole mounted; < = 22kV; > 60 kVA and < = 600 kVA; single phase |  | 0 | 0 | 0
| Pole mounted; < = 22kV; > 600 kVA; single phase |  | 0 | 0 | 0
| Pole mounted; < = 22kV; < = 60 kVA ; multiple phase |  | 19660 | 2 | 0
| Pole mounted; < = 22kV; > 60 kVA and < = 600 kVA ; multiple phase |  | 1772951 | 83 | 24
| Pole mounted; < = 22kV; > 600 kVA ; multiple phase |  | 23121 | 0 | 0
| Kiosk mounted; < = 22kV; < = 60 kVA; single phase |  | 0 | 0 | 0
| Kiosk mounted; < = 22kV; > 60 kVA and < = 600 kVA; single phase |  | 0 | 0 | 0
| Kiosk mounted; < = 22kV; > 600 kVA; single phase |  | 0 | 0 | 0
| Kiosk mounted; < = 22kV; < = 60 kVA ; multiple phase |  | 0 | 0 | 0
| Kiosk mounted; < = 22kV; > 60 kVA and < = 600 kVA ; multiple phase |  | 2652380 | 29 | 2
| Kiosk mounted; < = 22kV; > 600 kVA ; multiple phase |  | 315385 | 3 | 0
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; < = 60 kVA; single phase |  | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; > 60 kVA and < = 600 kVA; single phase |  | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; > 600 kVA; single phase |  | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; < = 60 kVA; multiple phase |  | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; > 60 kVA and < = 600 kVA; multiple phase |  | 53961 | 2 | 1
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; > 600 kVA; multiple phase |  | 56034 | 1 | 0
| Ground outdoor / Indoor chamber mounted; > = 22 kV & < = 33 kV; < = 15 MVA |  | 3321061 | 47 | 2
| Ground outdoor / Indoor chamber mounted; > = 22 kV & < = 33 kV; > 15 MVA and < = 40 MVA |  | 4698 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > = 22 kV & < = 33 kV; > 40 MVA |  | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 33 kV & < = 66 kV; < = 15 MVA |  | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 33 kV & < = 66 kV; > 15 MVA and < = 40 MVA |  | 15825 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 33 kV & < = 66 kV; > 40 MVA |  | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 66 kV & < = 132 kV; < = 100 MVA |  | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 66 kV & < = 132 kV; > 100 MVA |  | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 132 kV; < = 100 MVA |  | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 132 kV; > 100 MVA |  | 0 | 0 | 0
| Other |  | 2305024 | 498 | 0
| Total transformers |  | 10784052 | 690 | 31
| SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE;SWITCH FUNCTION | Units | $ | Number of assets | Number of assets
| ˂ = 11 kV; fuse |  | 563548 | 440 | 70
| ˂ = 11 kV; switch |  | 4066745 | 1179 | 207
| ˂ = 11 kV; circuit breaker |  | 717327 | 2 | 0
| > 11 kV & < = 22 kV; switch |  | 5886339 | 329 | 21
| > 11 kV & < = 22 kV; circuit breaker |  | 188019 | 0 | 3
| > 22 kV & < = 33 kV; switch |  | 0 | 0 | 0
| > 22 kV & < = 33 kV; circuit breaker |  | 0 | 0 | 0
| > 33 kV & < = 66 kV; switch |  | 261600 | 2 | 0
| > 33 kV & < = 66 kV; circuit breaker |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; switch |  | 0 | 0 | 0
| > 66 kV & < = 132 kV ; circuit breaker |  | 0 | 0 | 0
| > 132 kV; switch |  | 0 | 0 | 0
| > 132 kV; circuit breaker |  | 0 | 0 | 0
| Other |  | 1659433 | 804 | 1
| Total switchgear |  | 13343011 | 2756 | 302
| SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Units | $ | Number of assets/km | Number of assets
| Field devices |  | 4119735 | 7 | 4
| Local network wiring assets | replacements km | 617543 | 0 | 0
| Communications network assets |  | 2180229 | 55 | 0
| Master station assets |  | 0 | 0 | 0
| Communications site infrastructure |  | 0 | 0 | 0
| Communications linear assets | replacements km | 0 | 0 | 0
| AFLC |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
| Total SCADA, network control and protection systems |  | 6917507 | 62 | 4
| OTHER BY: BUSINESS SPECIFIED | Units | $ | Number of assets | Number of assets
| Buildings |  | 1858465 | 15 | 0
| Civil |  | 793608 | 120 | 0
| Capacitor Banks - Large |  | 0 | 0 | 0
| Fences |  | 413441 | 430 | 0
| CTs and VTs |  | 142748 | 3 | 0
| NERs |  | 39111 | 0 | 0
| Bunding/Noise |  | 32209 | 0 | 0
| Lines Miscellaneous |  | 1700000 | 0 | 0
| Total other business specified |  | 4979582 | 568 | 0
DC02 - Operational outputs ¦ Replacement and maintenance
Asset replacement and maintenance activities
DC07 - Capital expenditure ¦ Alternative control
Replacement expenditure
2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY
|  |  | Direct expenditure |  |  | Operational outputs
| ASSET REPLACEMENT AND MAINTENANCE ACTIVITIES AND EXPENDITURE |  | Total Public Lighting expenditure | Energy Efficient | Non-energy efficient | Asset replacements | Asset failures
| PUBLIC LIGHTING BY: ASSET TYPE; LIGHTING OBLIGATION | Units | $ | $ | $ | Number of assets | Number of assets
| Luminaires; major road |  | 1313472 | 1304225 | 9247 | 603 | 0
| Luminaires; minor road |  | 3621099 | 3617384 | 3715 | 4468 | 0
| Brackets; major road |  | 0 | 0 | 0 | 0 | 0
| Brackets; minor road |  | 0 | 0 | 0 | 0 | 0
| Lamps; major road |  | 0 | 0 | 0 | 0 | 0
| Lamps; minor road |  | 0 | 0 | 0 | 0 | 0
| Poles / columns; major road |  | 1382104 | 1382104 | 0 | 153 | 0
| Poles / columns; minor road |  | 1164956 | 1164956 | 0 | 277 | 0
| Other |  | 15781 | 15781 | 0 | 26 | 0
DC03 - Network metrics ¦ Network assets - volume
Total poles by feeder type
2.2.2 - SELECTED ASSET CHARACTERISTICS
SELECTED ASSET CHARACTERISTICS
| TOTAL POLES BY: FEEDER TYPE | Units | Asset currently in commission
| CBD | Number of assets | 0
| Urban | Number of assets | 176195
| Long rural | Number of assets | 0
| Short rural | Number of assets | 26924
| Feeders other | Number of assets
DC03 - Network metrics ¦ Length
Selected asset characteristics
| SELECTED ASSET CHARACTERISTICS |  | Length
| OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH BY FEEDER TYPE | Units | Assets in Commission | Asset Replacements
| CBD | km | 0 | 0
| Urban | km | 8137 | 3.68
| Short rural | km | 1860 | 7.86
| Long rural | km | 0 | 0
| Feeders other | km
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH MATERIAL TYPE
| OH conductor LV ABC | km | 502 | 1
| OH conductor steel | km | 312 | 3
| OH conductor ACSR | km | 3461 | 4
| OH conductor AAAC | km | 15 | 0
| OH conductor AAC | km | 4158 | 2
| OH conductor HDBC | km | 1489 | 0
| Other material | km | 61 | 0
UNDERGROUND CABLES BY: CABLE LENGTH BY FEEDER TYPE
| CBD | km | 0 | 0
| Urban | km | 3087 | 10
| Short rural | km | 469 | 0
| Long rural | km | 0 | 0
| Feeders other | km
DC03 - Network metrics ¦ Capacity
Selected asset characteristics - capacity data
2.2.2 - SELECTED ASSET CHARACTERISTICS
SELECTED ASSET CHARACTERISTICS
| TRANSFORMERS | Units | Assets in Commission | Asset Replacements | Assets Decommissioned
| Transformer capacity | MVA | 9369.33 | 109.39
| Transformer capacity decommissioned | MVA |  |  | 73.95

## 2.3 Augex
| ANNUAL INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| CA RIN 2.3(b) AUGEX |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC02 - operational outputs ¦ Other outputs
Asset augmentation activities
2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS ¦ DESCRIPTOR METRICS
Activities and Services
| ASSET AUGMENTATION ACTIVITIES | Units | Units added | Units upgraded
| HV Feeder Augmentations - Overhead Lines | km | 0.42 | 1.885
| HV Feeder Augmentations - Underground Cables | km | 1.73 | 0
| LV Feeder Augmentations - Overhead Lines | km | 0.001 | 0
| LV Feeder Augmentations - Underground Cables | km | 0 | 0
| Distribution Substation Augmentations - Pole Mounted | number of assets | 1 | 26
| Distribution Substation Augmentations - Ground Mounted | number of assets | 0 | 0
| Distribution Substation Augmentations - Indoor | number of assets | 0 | 0
DC07 - capital expenditure ¦ Standard control
Augmentation expenditure
2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS ¦ COST METRICS
Standard Control Services
| ASSET AUGMENTATION EXPENDITURE | Units | Direct expenditure
| HV feeder augmentations - overhead conductor | $ | 0
| HV feeder augmentations - underground asset (cable) | $ | 0
| HV feeder non-material projects | $ | 908259
| LV feeder augmentations - overhead conductor | $ | 0
| LV feeder augmentations - underground asset (cable) | $ | 0
| LV feeder non-material projects | $ | 1093331
| Distribution substation augmentations - pole mounted | $ | 3598444
| Distribution substation augmentations - ground mounted | $ | 0
| Distribution substation augmentations - indoor | $ | 0
2.3.4 - AUGEX DATA - TOTAL EXPENDITURE
Standard Control Services
| ASSET AUGMENTATION EXPENDITURE | Units | Total expenditure
| Subtransmission substations, switching stations, zone substations | $ | 32021
| Subtransmission lines | $ | 0
| HV feeders | $ | 908259
| HV feeders - land purchases and easements | $ | 0
| Distribution substations | $ | 3598444
| Distribution substations - land purchases and easements | $ | 0
| LV feeders | $ | 1093331
| LV feeders - land purchases and easements | $ | 0
| Other assets | $ | 8666164

## 2.5 Connections
| ANNUAL INFORMATION ORDER |  |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  |  | 12.5% Grey | Amended
| CA RIN 2.5 CONNECTIONS |  |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
AR RIN (Workbook 2) 2.5 CONNECTIONS
DC02 - Operational outputs ¦ Connections
Other connection activities
DC07 - Capital expenditure ¦ Standard control
Connections
DC10 - Prices ¦ Connections and public lighting
Connections
2.5.1 - DESCRIPTOR METRICS (STANDARD CONTROL SERVICES)
CONNECTIONS (STANDARD CONTROL SERVICES)
| RESIDENTIAL | Units | Activity and expenditure
| Distribution substations installed | MVA | 0
| Distribution substations installed | Number of substations | 0
| Distribution substation installed (including capital contributions) | $ | 0
| Augmentation HV - net circuit length | km added | 0
| Augmentation HV (including capital contributions) | $ | 0
| Augmentation LV - net circuit length | km added | 0
| Augmentation LV (including capital contributions) | $ | 25534853
COMMERCIAL/INDUSTRIAL
| Distribution substations installed | MVA | 84
| Distribution substations installed | Number of substations | 140
| Distribution substation installed (including capital contributions) | $ | 20726513
| Augmentation HV - net circuit length | km added | 33
| Augmentation HV (including capital contributions) | $ | 50283205
| Augmentation LV - net circuit length | km added | 14
| Augmentation LV (including capital contributions) | $ | 6658479
SUBDIVISION
| Distribution substations installed | MVA | 4
| Distribution substations installed | Number of substations | 24
| Distribution substation installed (including capital contributions) | $ | 1407930
| Augmentation HV - net circuit length | km added | 5
| Augmentation HV (including capital contributions) | $ | 2554847
| Augmentation LV - net circuit length | km added | 5
| Augmentation LV (including capital contributions) | $ | 3928430
| Average connection costs | $/lot | 0
EMBEDDED GENERATION
| Distribution substations installed | MVA | 0
| Distribution substations installed | Number of substations | 0
| Distribution substation installed (including capital contributions) | $ | 0
| Augmentation HV - net circuit length | km added | 2
| Augmentation HV (including capital contributions) | $ | 137420
| Augmentation LV - net circuit length | km added | 0
| Augmentation LV (including capital contributions) | $ | 0
DC02 - Operational outputs ¦ Connections
New Connections - standard control services
DC07 - Capital expenditure ¦ Standard control
Connections
2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION
|  |  | Standard control services | New connections - Standard control services
| CONNECTIONS (STANDARD CONTROL) |  | Direct expenditure (Excluding capital contributions) | Overhead | Underground
| RESIDENTIAL | Units | $ | Number of connections | Number of connections
| Simple connection LV |  | 416800 | 0 | 3103
| Complex connection LV |  | 0 | 0 | 0
| Complex connection HV |  | 0 | 0 | 0
COMMERCIAL/INDUSTRIAL
| Simple connection LV |  | 3759180 | 385 | 0
| Complex connection HV (customer connected at LV, minor HV works) |  | 7683820 | 824 | 0
| Complex connection HV (customer connected at LV, upstream asset works) |  | 85755 | 0 | 8
| Complex connection HV (customer connected at HV) |  | -6061688 | 0 | 22
| Complex connection sub-transmission |  | 358299 | 0 | 4
SUBDIVISION
| Complex connection LV |  | 2258896 | 0 | 158
| Complex connection HV (no upstream asset works) |  | 1595719 | 0 | 82
| Complex connection HV (with upstream asset works) |  | 0 | 0 | 0
EMBEDDED GENERATION
| Simple connection LV |  | 4006 | 0 | 1
| Complex connection HV (small capacity) |  | 0 | 0 | 0
| Complex connection HV (large capacity) |  | -430417 | 0 | 5
DC07 - Capital expenditure ¦ Standard control
Connections - Type 1 capital contributions
2.5.3 - CAPITAL CONTRIBUTIONS (TYPE 1) BY CONNECTION CLASSIFICATION
| CONNECTIONS |  | Standard control services
| RESIDENTIAL | Units | Total expenditure
| Simple connection LV | $ | 25118053
| Complex connection LV | $ | 0
| Complex connection HV | $ | 0
COMMERCIAL/INDUSTRIAL
| Simple connection LV | $ | 4359388
| Complex connection HV (customer connected at LV, minor HV works) | $ | 34959745
| Complex connection HV (customer connected at LV, upstream asset works) | $ | 1724986
| Complex connection HV (customer connected at HV) | $ | 22308799
| Complex connection sub-transmission | $ | 0
SUBDIVISION
| Complex connection LV | $ | 532363
| Complex connection HV (no upstream asset works) | $ | 332204
| Complex connection HV (with upstream asset works) | $ | 0
EMBEDDED GENERATION
| Simple connection LV | $ | 0
| Complex connection HV (small capacity) | $ | 0
| Complex connection HV (large capacity) | $ | 563831
DC02 - Operational outputs ¦ Connections
New connections
2.5.4 - NEW CONNECTIONS BY CONNECTION CLASSIFICATION - ALL OTHER SERVICES EXCLUDING STANDARD CONTROL SERVICES
CONNECTIONS
| RESIDENTIAL |  | Overhead | Underground
| Simple connection LV | Number of connections | 166 | 6672
| Complex connection LV | Number of connections | 0 | 0
| Complex connection HV | Number of connections | 0 | 0
COMMERCIAL/INDUSTRIAL
| Simple connection LV | Number of connections | 869 | 1278
| Complex connection HV (customer connected at LV, minor HV works) | Number of connections | 0 | 7
| Complex connection HV (customer connected at LV, upstream asset works) | Number of connections | 0 | 0
| Complex connection HV (customer connected at HV) | Number of connections | 0 | 0
| Complex connection sub-transmission | number of connections | 0 | 2
SUBDIVISION
| Complex connection LV | Number of connections | 0 | 0
| Complex connection HV (no upstream asset works) | Number of connections | 0 | 0
| Complex connection HV (with upstream asset works) | Number of connections | 0 | 0
EMBEDDED GENERATION
| Simple connection LV | Number of connections | 0 | 0
| Complex connection HV (small capacity) | Number of connections | 0 | 0
| Complex connection HV (large capacity) | Number of connections | 0 | 0

## 2.6 Non-network
| ANNUAL INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| CA RIN 2.6 NON NETWORK EXPENDITURE |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC07 - Capital expenditure ¦ Standard Control
Non-network
DC06 - Operating expenditure ¦ Standard Control
Non-network
2.6.1 - NON-NETWORK EXPENDITURE
| NON-NETWORK EXPENDITURE |  | Standard Control Services - Direct expenditure
| INFORMATION AND COMMUNICATION TECHNOLOGY | Units | Operating expenditure | Capital expenditure
| Device expenditure | $ | 0 | 903034
| Recurrent expenditure | $ | 32989304 | 23410393
| Opex | $ | 32989304 | 0
| Market Compliance | $ | 0 | 3877273
| Customer Engagement | $ | 0 | 94061
| Corporate Services | $ | 0 | 10471226
| Field Work & Construction | $ | 0 | 866322
| Service Management and Ops | $ | 0 | -80231
| Network Assets and Network Operations | $ | 0 | 7046955
| Cyber Security | $ | 0 | 1134787
| Non-recurrent expenditure | $ | 0 | 6503640.59
| Opex | $ | 0 | 0
| Market Compliance | $ | 0 | 2635167
| Customer Engagement | $ | 0 | 1440623
| Corporate Services | $ | 0 | 0
| Field Work & Construction | $ | 0 | 0
| Service Management and Ops | $ | 0 | 0
| Network Assets and Network Operations | $ | 0 | 268295.59
| Cyber Security | $ | 0 | 2159555
| Total ICT expenditure | $ | 32989304 | 30817067.59
MOTOR VEHICLES
| Car | $ | 241628 | 223986
| Light commercial vehicle | $ | 4162048 | 786988
| Elevated work platform (LCV) | $ | 0 | 0
| Elevated work platform (HCV) | $ | 5371642 | 2324812
| Heavy commercial vehicle | $ | 930918 | 2887778
| Total motor vehicle expenditure | $ | 10706236 | 6223564
BUILDINGS & PROPERTY EXPENDITURE
| Buildings and property expenditure | $ | 4487433 | 13340893
OTHER NON-NETWORK EXPENDITURE
| Other expenditure | $ | 0 | 14306
| Total other non-network expenditure | $ | 0 | 14306
| Total non-network | $ | 48182973 | 50395830.59
DC03 - Network metrics ¦ Non-network assets - volume
IT & Communications
2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE
| IT & COMMUNICATIONS | Units | Volume
| Number of devices | Number of devices | 576
DC02 - Operational outputs ¦ Other outputs
Motor vehicles
DC03 - Network metrics ¦ Non-network assets - volume
Motor vehicles
2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES
MOTOR VEHICLES
| CAR | Units | Volume
| Number purchased | Number of assets | 21
| Number leased | Number of assets | 10
| Number in fleet | Number of vehicles | 31
| Proportion of total fleet expenditure allocated as regulatory expenditure |  | 100%
LIGHT COMMERCIAL VEHICLE
| Number purchased | Number of assets | 38
| Number leased | Number of assets | 132
| Number in fleet | Number of vehicles | 170
| Proportion of total fleet expenditure allocated as regulatory expenditure |  | 100%
ELEVATED WORK PLATFORM (LCV)
| Number purchased | Number of assets | 0
| Number leased | Number of assets | 0
| Number in fleet | Number of vehicles | 0
| Proportion of total fleet expenditure allocated as regulatory expenditure |  | 0%
ELEVATED WORK PLATFORM (HCV)
| Number purchased | Number of assets | 47
| Number leased | Number of assets | 43
| Number in fleet | Number of vehicles | 90
| Proportion of total fleet expenditure allocated as regulatory expenditure |  | 100%
HEAVY COMMERCIAL VEHICLE
| Number purchased | Number of assets | 31
| Number leased | Number of assets | 17
| Number in fleet | Number of vehicles | 48
| Proportion of total fleet expenditure allocated as regulatory expenditure |  | 100%

## 2.7 Vegetation management
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| CA RIN 2.7 VEGETATION MANAGEMENT |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
EB RIN 3.7 OPERATING ENVIRONMENT
DC03 - Network metrics ¦ Length
Service area factors
` | 2.7.1 - DESCRIPTOR METRICS BY ZONE
3.7.3 - SERVICE AREA FACTORS
| TOTAL ROUTE LINE LENGTH | Units | Length
| Route line length - urban and CBD feeders | km | 5563.1327
| Route line length - rural feeders | km | 1239.4408
DOEF0301 | Route Line length - total | km | 6802.5735
DC03 - Network metrics ¦ Length
Maintenance spans
| TOTAL LENGTH OF MAINTENANCE SPANS | Units | Length
| Length of maintenance spans - urban and CBD feeders | km | 841
| Length of maintenance spans - rural feeders | km | 659
| Total length of maintenance spans | km | 1500
DC03 - Network metrics ¦ Terrain factors
Terrain factors
2.7.1 - DESCRIPTOR METRICS BY ZONE
3.7.2 - TERRAIN FACTORS
Terrain factors
| URBAN AND CBD | Units | Asset Volume
| Average frequency of cutting cycle | years | 2.46
| Number of maintenance spans | number of spans | 161629
DOEF0202 | Number of vegetation maintenance spans | number of spans | 21882
DOEF0210 | Average number of defects per vegetation maintenance span | number of defects | 1.02
DOEF0208 | Average number of trees per vegetation maintenance span | number of trees | 20.1
RURAL
| Average frequency of cutting cycle | years | 2.04
| Number of maintenance spans | number of spans | 26606
DOEF0203 | Number of vegetation maintenance spans | number of spans | 10807
DOEF0211 | Average number of defects per vegetation maintenance span | number of defects | 1.06
DOEF0209 | Average number of trees per vegetation maintenance span | number of trees | 16.57
OTHER
DOEF0205 | Total number of spans | number of spans | 188235
DOEF0212 | Tropical Proportion (number of spans) | number of spans | 0
DOEF0213 | Bushfire Risk (number of spans) | number of spans | 17377
DOEF0214 | Standard Vehicle Access | km | 68.03
DC05 - Service performance ¦ Other service measures
Fire starts
2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS
| Fire starts | Units | Service Performance
| Number of fire starts caused by vegetation grow-ins (NSP responsibility) | number of events | 5
| Number of fire starts caused by vegetation blow-ins and fall-ins (NSP responsibility) | number of events | 20
| Number of fire starts caused by vegetation grow-ins (other party responsibility) | number of events | 4
| Number of fire starts caused by vegetation blow-ins and fall-ins (other party responsibility) | number of events | 9
| Number of fire starts caused by asset failure (poles) | number of events | 0
| Number of fire starts caused by asset failure (pole top structures) | number of events | 59
| Number of fire starts caused by asset failure (other) | number of events | 29
DC06 - Operating expenditure ¦ Standard control
Vegetation management
2.7.2 - EXPENDITURE METRICS BY ZONE
| Vegetation management | Units | Standard control services - Direct expenditure
| Tree trimming (excluding hazard trees) | $ | 15798017.05
| Hazard tree cutting | $ | 229895.96
| Ground clearance | $ | 0
| Vegetation corridor clearance | $ | 23462.99
| Vegetation inspection | $ | 1329830
| Vegetation audit | $ | 0
| Contractor liaison expenditure | $ | 0
| Tree replacement program expenditure | $ | 0
| Other vegetation management expenditure | $ | 709892
| Total vegetation management | $ | 18091098

## 2.8 Maintenance
| ANNUAL INFORMATION ORDER | [5 empty] | #25C6FF | Protected (SOCI)
| United Energy | [5 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [5 empty] | 12.5% Grey | Amended
| CA RIN 2.8 MAINTENANCE | [5 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
DC02 - Operational outputs ¦ Replacement and maintenance
Asset replacement and maintenance activities
DC03 - Network metrics ¦ Asset metrics
Inspection and maintenance cycles
2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
|  |  | Assets maintained | Assets inspected | Inspection cycle | Maintenance cycle
| Maintenance | Units | Number of assets | Number of assets | Years | Years
| Poles |  | 642 | 22133 | 5 | 3
| Pole top structures |  | 1252 | 33440 | 5 | 3
| Staked wooden poles |  | 12 | 5143 | 5 | 3
| Overhead conductors |  | 1677 | 1129 | 5 | 0
| Underground cables |  | 680 | 1885 | 5 | 0
| Service lines |  | 41 | 48713 | 5 | 0
| Transformers |  | 433 | 981 | 1 | 3
| Switchgear |  | 962 | 384 | 10 | 0
| Public lighting |  | 22958 | 19181 | 0.3 | 6.8
| SCADA, network control and protection systems |  | 403 | 297 | 9 | 9
| Other business specified categories - total |  | 2936 | 509
| Buildings |  | 2867 | 493 | 0 | 0
| Civil |  | 3 | 0 | 0 | 0
| Capacitor Banks - Large |  |  |  | 0 | 0
| Fences |  | 0 | 0 | 0 | 0
| CTs and VTs |  | 66 | 0 | 0 | 0
| NERs |  | 0 | 16 | 0 | 0
| Bunding/Noise |  |  |  | 0 | 0
| Lines Miscellaneous |  |  |  | 0 | 0
DC06 - Operating expenditure ¦ Standard control
Maintenance
2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
Standard control services - Direct Expenditure
| Maintenance | Units | Routine maintenance | Non-routine maintenance
| Pole top, overhead line & service line maintenance | $ | 2870544 | 484231
| Service lines | $ | 4691 | 18658
| Pole inspection and treatment (all poles) | $ | 2272151 | 516786
| Overhead asset inspection - all overhead assets | $ | 157022 | 567387
| Network underground cable maintenance | $ | 25081 | 1711640
| Distribution substation equipment & property maintenance | $ | 1549171 | 2065999
| Zone substation equipment maintenance | $ | 2264252 | 754114
| Zone substation property maintenance | $ | 1084035 | 63161
| Public lighting maintenance - minor roads | $ | 971496 | 1290450
| Public lighting maintenance - major roads | $ | 51531 | 1073747
| SCADA, network control systems maintenance | $ | 50585 | 27075
| Protection systems maintenance | $ | 712964 | 393495
| Subtransmission asset maintenance - for DNSPs with dual function assets | $ | 0 | 0
| Ground clearance - access tracks | $ | 0 | 0
| Other routine maintenance | $ | 2618080 | 4591455
| Total | $ | 14631603 | 13558198

## 2.9 Emergency Response
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| CA RIN 2.9 EMERGENCY RESPONSE |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC06 - Operating expenditure ¦ Standard control
Emergency response
2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX)
| Emergency response | Units | Standard control services - Direct Expenditure
| Total emergency response opex | $ | 12221255

## 2.10 Overheads
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| AR RIN (Workbook 2) 2.10 OVERHEADS |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC09 - Revenue and financial statements ¦ Other services
Overheads expenditure
2.10.1 - NETWORK OVERHEADS EXPENDITURE
| OTHER DISTRIBUTION SERVICES | Units | Total expenditure
| Negotiated Services | $ | 0
| Unregulated Services | $ | 0
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
| OTHER DISTRIBUTION SERVICES | Units | Total expenditure
| Negotiated Services | $ | 0
| Unregulated Services | $ | 0

## 2.11 Labour
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| AR RIN (Workbook 2) 2.11 LABOUR |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC06 - Operating expenditure ¦ Standard control
DC07 - Capital expenditure ¦ Standard control
Labour / non-labour expenditure split
2.11.3 - LABOUR / NON-LABOUR EXPENDITURE SPLIT - STANDARD CONTROL SERVICES
Standard Control - Direct expenditure
| Labour / non-labour expenditure split | Units | Operating expenditure
| In-house labour expenditure | $
| Labour expenditure outsourced to related parties | $
| Labour expenditure outsourced to unrelated parties | $
| Non-labour expenditure | $
Standard Control - Direct expenditure
| Labour / non-labour expenditure split | Units | Capital expenditure
| In-house labour expenditure | $
| Labour expenditure outsourced to related parties | $
| Labour expenditure outsourced to unrelated parties | $
| Non-labour expenditure | $

## 2.12 Input tables
| ANNUAL INFORMATION ORDER | [6 empty] | #25C6FF | Protected (SOCI)
| United Energy | [6 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [6 empty] | 12.5% Grey | Amended
| (replaces) CA RIN 2.12 INPUT TABLES | [6 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
DC06 - Operating expenditure ¦ Standard control
Input expenditure category
2.12.1 - INPUT TABLES
Standard Control Services
| Input expenditure category | Units | Direct material expenditure | Direct labour expenditure | Contract expenditure - labour | Contract expenditure - non labour | Other expenditure
| Vegetation management | $ | 0 | 0 | 15506330 | 2584767 | 0
| Routine maintenance | $ | 4727049 | 0 | 8772436 | 1127338 | 0
| Non-routine maintenance | $ | 3532012 | 0 | 6572804 | 820426 | 0
| Emergency response opex | $ | 1378816 | 0 | 9127107 | 1715332 | 0
| Non-network expenditure | $ | 0 | 0 | 38323150 | 9859823 | 0
| IT and communications | $ | 0 | 0 | 32568927 | 420377 | 0
| Motor vehicles | $ | 0 | 0 | 4054720 | 6651516 | 0
| Buildings and property | $ | 0 | 0 | 1699503 | 2787930 | 0
| Other non network | $ | 0 | 0 | 0 | 0 | 0
| Export services | $ | 5094 | 0 | 33719 | 6337 | 0
| Overheads expenditure | $ | 0 | 0 | 24238287 | 23871143 | 0
| Network overheads | $ | 0 | 0 | 12726222 | 1583890 | 0
| Corporate overheads | $ | 0 | 0 | 11512065 | 22287253 | 0

## 4.1 Public lighting
| ANNUAL INFORMATION ORDER | [5 empty] | #25C6FF | Protected (SOCI)
| United Energy | [5 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [5 empty] | 12.5% Grey | Amended
| CA RIN 4.1 PUBLIC LIGHTING | [5 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
AR RIN 4.1 PUBLIC LIGHTING
DC03 - Network metrics ¦ Network assets - volume
Public lighting
4.1.1 - DESCRIPTOR METRICS OVER YEAR
| PUBLIC LIGHTING BY LIGHT TYPE | Units | Volume
| Category P LED Standard Output | Number of assets | 57887
| Category P LED High Output | Number of assets | 865
| Category V L1 LED Standard Output | Number of assets | 10442
| Category V L2 LED Medium Output | Number of assets | 4321
| Category V L4 LED High Output | Number of assets | 220
| Fluorescent 40W | Number of assets | 0
| Fluorescent Compact 32W | Number of assets | 1365
| Fluorescent Compact 42W | Number of assets | 560
| Fluorescent T5 (2x14W) | Number of assets | 23294
| Fluorescent T5 (2x24W) | Number of assets | 255
| HP Sodium 70W | Number of assets | 59
| HP Sodium 100W | Number of assets | 505
| HP Sodium 150W | Number of assets | 14004
| HP Sodium 250W | Number of assets | 7392
| HP Sodium 400W | Number of assets | 186
| Mercury Vapour 80W | Number of assets | 2366
| Mercury Vapour 125W | Number of assets | 24
| Mercury Vapour 250W | Number of assets | 0
| Mercury Vapour 400W | Number of assets | 0
| Metal Halide 70W | Number of assets | 0
| Metal Halide 100W | Number of assets | 6
| Metal Halide 150W | Number of assets | 9
| Metal Halide 250W | Number of assets | 73
| Metal Halide 400W | Number of assets | 35
| Total activities | Number of assets | 123868
DC02 - Operational outputs ¦ Other outputs
DC09 - Revenue and financial statements ¦ Alternative control
Public lighting activities
4.1.2 - DESCRIPTOR METRICS ANNUALLY
| Public lighting activities |  | Activities and Services | Alternative control services - Total expenditure
| LIGHT INSTALLATION | Units | Number installed | $
| Major road |  | 1746 | 2992874
| Minor road |  | 3509 | 9037398
| Number of poles |  | 0 | 0
| LIGHT REPLACEMENT | Units | Number replaced | $
| Major road |  | 296 | 1313472
| Minor road |  | 1875 | 3621099
| Number of poles |  | 256 | 2475647
| LIGHT MAINTENANCE | Units | Number maintained | $
| Major road |  | 5250 | 908178
| Minor road |  | 15916 | 2062905
| Number of poles |  | 212 | 325485
DC03 - Network metrics ¦ Network assets - volume
Public lighting
DC09 - Revenue and financial statements ¦ Alternative control
Public lighting revenue by tariff
4.1.4 - PUBLIC LIGHTING METRICS BY TARIFF
Public Lighting
|  |  | Volume | Alternative Control Services
| Public lighting |  |  | Total revenue | Energy Efficient | Non-energy efficient
| BUSINESS DEFINED TARIFF CATEGORIES | Units | Number of assets | $ | $ | $
| Category P LED Standard Output |  | 57887 | 1700873 | 1700873
| Category P LED High Output |  | 865 | 20524 | 20524
| Category V L1 LED Standard Output |  | 10442 | 506387 | 506387
| Category V L2 LED Medium Output |  | 4321 | 260466 | 260466
| Category V L4 LED High Output |  | 220 | 12439 | 12439
| Fluorescent 40W |  | 0 | 0 | 0
| Fluorescent Compact 32W |  | 1365 | 77382 | 77382
| Fluorescent Compact 42W |  | 560 | 30025 | 30025
| Fluorescent T5 (2x14W) |  | 23294 | 1289464 | 1289464
| Fluorescent T5 (2x24W) |  | 255 | 14856 | 14856
| HP Sodium 70W |  | 59 | 15680 |  | 15680
| HP Sodium 100W |  | 505 | 104512 |  | 104512
| HP Sodium 150W |  | 14004 | 2277801 |  | 2277801
| HP Sodium 250W |  | 7392 | 1166391 |  | 1166391
| HP Sodium 400W |  | 186 | 42662 |  | 42662
| Mercury Vapour 80W |  | 2366 | 323371 |  | 323371
| Mercury Vapour 125W |  | 24 | 6045 |  | 6045
| Mercury Vapour 250W |  | 0 | 0 |  | 0
| Mercury Vapour 400W |  | 0 | 0 |  | 0
| Metal Halide 70W |  | 0 | 0 |  | 0
| Metal Halide 100W |  | 6 | 1605 |  | 1605
| Metal Halide 150W |  | 9 | 1751 |  | 1751
| Metal Halide 250W |  | 73 | 16393 |  | 16393
| Metal Halide 400W |  | 35 | 7359 |  | 7359
| Total assets |  | 123868 | 7875986 | 3912416 | 3963570
DC10 - Prices ¦ Connections and public lighting
Public lighting activities
4.1.3 - COST METRICS
Public lighting activities
| PUBLIC LIGHT INSTALLATION | Units | Average unit cost
| New Light Major Road (CNJ) | $/light installation | 1606
| Pb.Light CapProj - Major Scheme (CLJ) | $/light installation | 1643
| New Light Minor Road (CNM) | $/light installation | 475
| New Light Watchman (CNW)* service withdrawn | $/light installation | 0
| New Sustainable Light (CNG) | $/light installation | 738
| New Sustainable Lantern & Bracket (CNS) | $/light installation | 2766
| Pb.Light CapProj - Minor Scheme (CLN) | $/light installation | 2880
PUBLIC LIGHT REPLACEMENT
| SINGLE MAJOR RD REPL (RLJ) | $/light replacement | 795
| POLE REPLACE P/L (RPA) | $/light replacement | 8092
| SINGLE MINOR RD REPL (RLM) | $/light replacement | 519
| SINGLE SUSTAINABLE LANTERN REPL (RLG) | $/light replacement | 683
| Single Sustainable Lantern Replacement (RLS) | $/light replacement | 1798
| Pole Reinforcememt (RRP) | $/light replacement | 626
| POLE REPLACE P/L (RPB) | $/light replacement | 3555
PUBLIC LIGHT MAINTENANCE
| PL Major Road Patrols (MLP) | $/light maintenance | 24495
| PL Luminaires (MLF) | $/light maintenance | 274
| PL Poles (MLR) | $/light maintenance | 233
| PL Minor Road Bulk (MRB) | $/light maintenance | 65
| PL Luminaires (MRF) | $/light maintenance | 240
| PL Poles (MRR) | $/light maintenance | 243
| PL Minor Road Bulk - Sustainable (MRS) | $/light maintenance | 58

## 4.2 Metering
| ANNUAL INFORMATION ORDER | [8 empty] | #25C6FF | Protected (SOCI)
| United Energy | [8 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [8 empty] | 12.5% Grey | Amended
| CA RIN 4.2 METERING | [8 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
DC03 - Network metrics ¦ Network assets - volume
Meter population
4.2.1 - METERING DESCRIPTOR METRIC
METER POPULATION
| METER TYPE 1-3 | Units | Volume
| Single phase meters | number of assets | 0
| Multi phase meters | number of assets | 0
| Current transformer connected meters | number of assets | 0
| Direct connect meters | number of assets | 0
METER TYPE 4
| Single phase meters | number of assets | 590296
| Multi phase meters | number of assets | 129995
| Current transformer connected meters | number of assets | 4737
| Direct connect meters | number of assets | 715554
METER TYPE 5
| Single phase meters | number of assets | 50
| Multi phase meters | number of assets | 12
| Current transformer connected meters | number of assets | 1
| Direct connect meters | number of assets | 61
METER TYPE 6
| Single phase meters | number of assets | 1474
| Multi phase meters | number of assets | 548
| Current transformer connected meters | number of assets | 7
| Direct connect meters | number of assets | 2015
DC02 - Operational outputs ¦ Other outputs
DC06 - Operating expenditure ¦ Alternative control
DC07 - Capital expenditure ¦ Alternative control
Metering activities
4.2.2 - COST METRICS
|  |  | Assets and Services | Operating expenditure |  |  | Capital expenditure
|  |  |  | Alternative Control Services - Direct Expenditure (Metering) |  |  | Alternative Control Services - Direct Expenditure (Metering)
| METERING ACTIVITIES |  |  | Total | Smart | Legacy | Total | Smart | Legacy
| METER PURCHASE | Units | Number of activities | $ | $ | $ | $ | $ | $
| Meter type 1-3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 4 |  | 12247 | 0 | 0 | 0 | 3470840 | 3470840 | 0
| Meter type 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| METER TESTING | Units | Number of activities
| Meter type 1-3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 4 |  | 1639 | 569891 | 569891 | 0 | 0 | 0 | 0
| Meter type 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| METER INVESTIGATION | Units | Number of activities
| Meter type 1-3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 4 |  | 853 | 139624 | 139624 | 0 | 0 | 0 | 0
| Meter type 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCHEDULED METER READING | Units | Number of activities
| Meter type 1-3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 4 |  | 261338962 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 5 |  | 258 | 14061 | 0 | 14061 | 0 | 0 | 0
| Meter type 6 |  | 8780 | 478515 | 0 | 478515 | 0 | 0 | 0
| SPECIAL METER READING | Units | Number of activities
| Meter type 1-3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 5 |  | 2 | 109 | 0 | 109 | 0 | 0 | 0
| Meter type 6 |  | 193 | 10519 | 0 | 10519 | 0 | 0 | 0
| NEW METER INSTALLATION | Units | Number of activities
| Meter type 1-3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 4 |  | 9589 | 2689864 | 2689864 | 0 | 0 | 0 | 0
| Meter type 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| METER REPLACEMENT | Units | Number of activities
| Meter type 1-3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 4 |  | 4063 | 0 | 0 | 0 | 860725 | 860725 | 0
| Meter type 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Whole Meter Replacement | Units
| Meter Type 1-3 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter Type 4 | $ | 4063 | 0 | 0 | 0 | 860725 | 860725 | 0
| Meter Type 5 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter Type 6 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Component / Software Replacement | Units
| Meter Type 1-3 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter Type 4 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter Type 5 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter Type 6 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0
| METER MAINTENANCE | Units | Number of activities
| Meter type 1-3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REMOTE METER READING | Units | Number of activities
| Meter type 1-3 |  | 0 |  | 0 | 0 |  | 0 | 0
| Meter type 4 |  | 261338962 | 0 | 0 | 0 | 0 | 0 | 0
| Meter type 5 |  | 0 |  | 0 | 0 |  | 0 | 0
| REMOTE METER RE-CONFIGURATION | Units | Number of activities
| Meter type 1-3 |  | 0 |  | 0 | 0 |  | 0 | 0
| Meter Type 4 |  | 7393 | 0 | 0 | 0 | 0 | 0 | 0
| OTHER METERING SERVICES | Units | Number of services provided
| Meter Type 4 |  | 0 | 2357938 | 2357938 | 0 | 0 | 0 | 0
| Meter Type 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter Type 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meter Type 7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IT INFRASTRUCTURE | Units
| Meter Type 4 | $ | NA | 1847317 | 1847317 | 0 | 41331 | 41331 | 0
| COMMUNICATIONS INFRASTRUCTURE | Units
| Meter Type 4 | $ | NA | 607230 | 607230 | 0 | 603855 | 603855 | 0

## 4.3 Fee-based services
| ANNUAL INFORMATION ORDER |  |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  |  | 12.5% Grey | Amended
| CA RIN 4.3 ANCILLARY SERVICES - FEE BASED SERVICES |  |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC02 - Operational outputs ¦ Other outputs
DC06 - Operating expenditure ¦ Alternative control
DC07 - Capital expenditure ¦ Alternative control
Fee based services
4.3.1 - COST METRICS FOR FEE-BASED SERVICES - DIRECT EXPENDITURE INCLUDING CAPITAL CONTRIBUTIONS
|  |  | Activities and services | Alternative Control Services - Direct expenditure
|  |  |  | Operating expenditure | Capital expenditure
| FEE-BASED SERVICES | Units | Number of services provided | $ | $
| Energisation |  | 0 | 0 | 0
| De-energisation |  | 433 | 25690 | 0
| Re-energisation |  | 2458 | 158722 | 0
| Other |  | 5059 | 3265459 | 0
| Failed field visit (simple) |  | 911 | 138910 | 0
| Failed field visit (complex AH) |  | 0 | 0 | 0
| Failed field visit (complex AB) |  | 413 | 62621 | 0
| Complex Alteration (AH) |  | 93 | 80337 | 0
| Complex Alternation (AB) |  | 2216 | 1807507 | 0
| Isolation of supply and reconnection BH |  | 229 | 186650 | 0
| Isolation of supply or reconnection BH |  | 567 | 472045 | 0
| Isolation of supply or reconnection AH |  | 40 | 36716 | 0
| Standard alteration AH |  | 14 | 11312 | 0
| Standard alteration BH |  | 576 | 469361 | 0
| Manual de-energisation |  | 0 | 0 | 0
| Manual re-energisation AH |  | 0 | 0 | 0
| Manual re-energisation BH |  | 0 | 0 | 0
| Manual re-energisation same day BH |  | 0 | 0 | 0

## 4.4 Quoted services
| ANNUAL INFORMATION ORDER |  |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  |  | 12.5% Grey | Amended
| CA RIN 4.4 ANCILLARY SERVICES - QUOTED SERVICES |  |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC02 - Operational outputs ¦ Other outputs
DC06 - Operating expenditure ¦ Alternative control
DC07 - Capital expenditure ¦ Alternative control
Quoted services
4.4.1 - COST METRICS FOR QUOTED SERVICES - DIRECT EXPENDITURE INCLUDING CAPITAL CONTRIBUTIONS
|  |  | Activities and services | Alternative Control Services - Direct expenditure
|  |  |  | Operating expenditure | Capital expenditure
| QUOTED SERVICES | Units | Number of services provided | $ | $
| Elective underground |  | 11046 | 2491235 | 0
| Recoverable Works |  | 3483 | 2113813 | 0
| No Go Zone |  | 3255 | 1289662 | 0
| Spec and Audit Design |  | 87 | 1870238 | 0
| High load escorts |  | 40 | 256775 | 0
| Reserve Feeder |  | 2 | 143286 | 0

## 5.2 Asset Age Profile
| ANNUAL INFORMATION ORDER | [92 empty] | #25C6FF | Protected (SOCI)
| United Energy | [92 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [92 empty] | 12.5% Grey | Amended
| CA RIN 5.2 ASSET AGE PROFILE | [92 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
DC03 - Network metrics ¦ Asset age profile
Installed assets - quantity currently in commission by year installed
5.2.1 - ASSET AGE PROFILE
Installed assets - quantity currently in commission by year installed
| POLES BY: HIGHEST OPERATING VOLTAGE; MATERIAL TYPE | Units | 2024-25 | 2023-24 | 2022-23 | 2021-22 | 2020-21 | 2019-20 | 2018-19 | 2017-18 | 2016-17 | 2015-16 | 2014-15 | 2013-14 | 2012-13 | 2011-12 | 2010-11 | 2009-10 | 2008-09 | 2007-08 | 2006-07 | 2005-06 | 2004-05 | 2003-04 | 2002-03 | 2001-02 | 2000-01 | 1999-00 | 1998-99 | 1997-98 | 1996-97 | 1995-96 | 1994-95 | 1993-94 | 1992-93 | 1991-92 | 1990-91 | 1989-90 | 1988-89 | 1987-88 | 1986-87 | 1985-86 | 1984-85 | 1983-84 | 1982-83 | 1981-82 | 1980-81 | 1979-80 | 1978-79 | 1977-78 | 1976-77 | 1975-76 | 1974-75 | 1973-74 | 1972-73 | 1971-72 | 1970-71 | 1969-70 | 1968-69 | 1967-68 | 1966-67 | 1965-66 | 1964-65 | 1963-64 | 1962-63 | 1961-62 | 1960-61 | 1959-60 | 1958-59 | 1957-58 | 1956-57 | 1955-56 | 1954-55 | 1953-54 | 1952-53 | 1951-52 | 1950-51 | 1949-50 | 1948-49 | 1947-48 | 1946-47 | 1945-46 | 1944-45 | 1943-44 | 1942-43 | 1941-42 | 1940-41 | 1939-40 | 1938-39 | 1937-38 | 1936-37 | 1935-36 | 1934-35
| ˂ = 1 kV; wood | number of assets | 617 | 463 | 629 | 569 | 527 | 607 | 461 | 543 | 498 | 551 | 477 | 326 | 232 | 227 | 337 | 519 | 403 | 302 | 219 | 297 | 411 | 628 | 693 | 341 | 399 | 361 | 380 | 270 | 436 | 110 | 12 | 17 | 35 | 46 | 68 | 145 | 351 | 565 | 541 | 1020 | 764 | 950 | 1014 | 1246 | 1365 | 1482 | 1025 | 1029 | 730 | 1077 | 1421 | 1334 | 1682 | 2107 | 1689 | 1779 | 1972 | 2118 | 1975 | 1321 | 1676 | 1365 | 1103 | 1009 | 842 | 977 | 777 | 584 | 451 | 202 | 150 | 184 | 130 | 105 | 76 | 389 | 103 | 104 | 126 | 80 | 30 | 18 | 50 | 109 | 261 | 317 | 320 | 371 | 329 | 238 | 1095
| > 1 kV & < = 11 kV; wood | number of assets | 170 | 158 | 154 | 198 | 197 | 209 | 186 | 169 | 240 | 256 | 256 | 254 | 250 | 275 | 197 | 314 | 276 | 183 | 189 | 165 | 127 | 111 | 147 | 161 | 137 | 123 | 144 | 91 | 115 | 97 | 82 | 168 | 161 | 75 | 220 | 310 | 186 | 228 | 241 | 351 | 271 | 207 | 167 | 275 | 235 | 221 | 216 | 183 | 117 | 134 | 155 | 176 | 223 | 256 | 171 | 243 | 314 | 421 | 292 | 296 | 339 | 254 | 177 | 179 | 176 | 113 | 110 | 90 | 33 | 18 | 28 | 41 | 34 | 6 | 15 | 72 | 10 | 7 | 3 | 4 | 3 | 1 | 9 | 48 | 49 | 77 | 57 | 104 | 40 | 32 | 218
| ˃ 11 kV & < = 22 kV; wood | number of assets | 472 | 513 | 555 | 524 | 495 | 548 | 424 | 408 | 541 | 543 | 512 | 505 | 480 | 416 | 506 | 712 | 675 | 558 | 486 | 478 | 451 | 403 | 442 | 417 | 526 | 401 | 387 | 199 | 264 | 149 | 94 | 132 | 229 | 208 | 320 | 388 | 488 | 633 | 510 | 970 | 898 | 736 | 901 | 692 | 853 | 788 | 520 | 625 | 853 | 1004 | 831 | 940 | 810 | 879 | 912 | 799 | 1107 | 888 | 817 | 886 | 1035 | 747 | 515 | 352 | 336 | 367 | 309 | 280 | 175 | 77 | 42 | 54 | 67 | 90 | 50 | 161 | 64 | 56 | 13 | 18 | 11 | 17 | 11 | 49 | 50 | 198 | 48 | 170 | 166 | 33 | 206
| > 22 kV & < = 66 kV; wood | number of assets | 95 | 125 | 81 | 76 | 84 | 56 | 58 | 61 | 117 | 113 | 131 | 55 | 141 | 130 | 146 | 152 | 146 | 85 | 181 | 98 | 162 | 97 | 131 | 152 | 213 | 153 | 75 | 57 | 34 | 57 | 59 | 39 | 57 | 26 | 61 | 108 | 65 | 70 | 50 | 134 | 98 | 295 | 256 | 187 | 173 | 72 | 49 | 77 | 138 | 251 | 97 | 59 | 53 | 69 | 109 | 155 | 311 | 287 | 277 | 223 | 328 | 208 | 176 | 81 | 30 | 16 | 14 | 9 | 25 | 57 | 26 | 31 | 15 | 30 | 7 | 6 | 17 | 1 | 2 | 1 | 0 | 2 | 3 | 3 | 3 | 4 | 2 | 2 | 7 | 1 | 3
| > 66 kV & < = 132 kV; wood | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; wood | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; concrete | number of assets | 1 | 22 | 3 | 0 | 7 | 5 | 8 | 6 | 9 | 8 | 0 | 1 | 0 | 1 | 5 | 1 | 1 | 4 | 1 | 6 | 1 | 0 | 4 | 2 | 6 | 40 | 44 | 45 | 142 | 164 | 422 | 764 | 1249 | 937 | 784 | 1034 | 1215 | 1438 | 1051 | 1032 | 999 | 505 | 192 | 97 | 181 | 356 | 40 | 456 | 478 | 185 | 89 | 42 | 425 | 228 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; concrete | number of assets | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24 | 10 | 9 | 24 | 32 | 28 | 19 | 14 | 38 | 26 | 67 | 29 | 36 | 32 | 36 | 22 | 12 | 30 | 32 | 2 | 22 | 9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; concrete | number of assets | 0 | 0 | 0 | 1 | 1 | 12 | 15 | 0 | 5 | 3 | 0 | 0 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4 | 8 | 34 | 47 | 64 | 141 | 257 | 296 | 418 | 471 | 449 | 711 | 866 | 837 | 749 | 624 | 719 | 394 | 104 | 133 | 229 | 177 | 30 | 318 | 248 | 72 | 30 | 0 | 10 | 17 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; concrete | number of assets | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 1 | 2 | 0 | 7 | 10 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 10 | 7 | 42 | 76 | 39 | 76 | 50 | 47 | 46 | 67 | 57 | 25 | 36 | 49 | 205 | 38 | 30 | 78 | 12 | 1 | 25 | 11 | 1 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; concrete | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; concrete | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; steel | number of assets | 1 | 2 | 7 | 4 | 10 | 12 | 10 | 12 | 15 | 9 | 0 | 2 | 3 | 3 | 3 | 18 | 5 | 5 | 1 | 1 | 3 | 1 | 4 | 4 | 30 | 32 | 20 | 5 | 7 | 5 | 1 | 4 | 9 | 4 | 16 | 20 | 3 | 12 | 9 | 9 | 14 | 4 | 0 | 2 | 8 | 8 | 13 | 6 | 1 | 0 | 0 | 1 | 2 | 0 | 6 | 2 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; steel | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; steel | number of assets | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; steel | number of assets | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; steel | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; steel | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 1 kV; composite pole | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; composite pole | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| ˃ 11 kV & < = 22 kV; composite pole | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| > 22 kV & < = 66 kV; composite pole | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| > 66 kV & < = 132 kV; composite pole | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| > 132 kV; composite pole | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| ˂ = 1 kV; pole - other technology | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| > 1 kV & < = 11 kV; pole - other technology | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| ˃ 11 kV & < = 22 kV; pole - other technology | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| > 22 kV & < = 66 kV; pole - other technology | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| > 66 kV & < = 132 kV; pole - other technology | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| > 132 kV; pole - other technology | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| Other | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [44 empty] | 0
| Total poles | number of assets | 1356 | 1283 | 1429 | 1372 | 1322 | 1457 | 1168 | 1203 | 1429 | 1487 | 1379 | 1145 | 1109 | 1053 | 1204 | 1726 | 1512 | 1139 | 1077 | 1045 | 1155 | 1241 | 1421 | 1078 | 1317 | 1121 | 1090 | 748 | 1079 | 774 | 1027 | 1491 | 2262 | 1836 | 1979 | 2800 | 3267 | 3908 | 3205 | 4212 | 3845 | 3332 | 2694 | 2674 | 3153 | 3149 | 1896 | 2741 | 2585 | 2724 | 2623 | 2552 | 3206 | 3556 | 2895 | 2982 | 3704 | 3717 | 3362 | 2727 | 3378 | 2576 | 1971 | 1623 | 1385 | 1474 | 1210 | 963 | 684 | 354 | 246 | 310 | 246 | 231 | 149 | 650 | 194 | 168 | 144 | 103 | 44 | 38 | 73 | 209 | 363 | 596 | 427 | 647 | 542 | 304 | 1522
STAKING OF/ STAKED WOODEN POLES BY: HIGHEST OPERATING VOLTAGE
| ˂ = 1 kV | number of assets | 673 | 550 | 517 | 418 | 334 | 445 | 739 | 617 | 464 | 465 | 551 | 612 | 309 | 242 | 96 | 280 | 210 | 379 | 206 | 182 | 409 | 193 | 166 | 206 | 222 | 262 | 298 | 446 | 120 | 152 | 130 | 363 | 396 | 311 | 538 | 455 | 109 | 0 | 41 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | number of assets | 127 | 62 | 63 | 76 | 55 | 105 | 118 | 69 | 99 | 74 | 120 | 91 | 38 | 13 | 16 | 46 | 30 | 43 | 50 | 50 | 82 | 31 | 23 | 44 | 67 | 101 | 88 | 141 | 17 | 44 | 16 | 53 | 55 | 68 | 51 | 88 | 35 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV | number of assets | 284 | 320 | 212 | 199 | 182 | 166 | 270 | 265 | 216 | 187 | 182 | 227 | 90 | 109 | 36 | 76 | 70 | 117 | 92 | 105 | 211 | 79 | 82 | 110 | 110 | 153 | 154 | 204 | 66 | 37 | 60 | 56 | 155 | 80 | 168 | 172 | 24 | 0 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV | number of assets | 48 | 54 | 27 | 27 | 48 | 50 | 54 | 68 | 34 | 29 | 35 | 25 | 17 | 18 | 9 | 15 | 9 | 16 | 17 | 9 | 27 | 13 | 10 | 7 | 11 | 20 | 18 | 13 | 3 | 9 | 7 | 3 | 12 | 17 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total staking of/ staked wooden poles | number of assets | 1132 | 986 | 819 | 720 | 619 | 766 | 1181 | 1019 | 813 | 755 | 888 | 955 | 454 | 382 | 157 | 417 | 319 | 555 | 365 | 346 | 729 | 316 | 281 | 367 | 410 | 536 | 558 | 804 | 206 | 242 | 213 | 475 | 618 | 476 | 762 | 718 | 168 | 0 | 51 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV)
| ˂ = 1 kV | km | 13676 | 13624 | 11922 | 11725 | 11819 | 10252 | 10241 | 10999 | 13676 | 24872 | 34605 | 34159 | 44338 | 29427 | 28524 | 39835 | 31658 | 27580 | 46247 | 34408 | 13500 | 21344 | 46133 | 82408 | 31035 | 59539 | 18013 | 42055 | 25733 | 159369 | 13987 | 20535 | 33100 | 32208 | 39036 | 64001 | 71835 | 114149 | 98803 | 131779 | 152230 | 148588 | 157066 | 155073 | 169195 | 176884 | 160552 | 155053 | 145538 | 144759 | 126310 | 107789 | 111327 | 127016 | 116328 | 44556 | 142944 | 139748 | 144023 | 109532 | 151815 | 127535 | 97578 | 88831 | 87680 | 84857 | 74740 | 65215 | 48364 | 26553 | 19590 | 26646 | 20348 | 19663 | 13084 | 61127 | 16685 | 14132 | 12410 | 12275 | 4773 | 2470 | 5240 | 15813 | 23232 | 32820 | 33214 | 48364 | 39087 | 28172 | 150985
| > 1 kV & < = 11 kV | km | 2521 | 1174 | 1701 | 2834 | 638 | 1265 | 911 | 1498 | 2936 | 7268 | 5466 | 4748 | 8584 | 9728 | 8756 | 9860 | 7633 | 4829 | 2703 | 1610 | 3169 | 3401 | 3685 | 3665 | 5568 | 1599 | 4049 | 2703 | 192 | 385 | 769 | 1589 | 1529 | 1012 | 2592 | 6803 | 5497 | 16551 | 12350 | 19568 | 19193 | 17908 | 14891 | 19295 | 25318 | 24842 | 31422 | 33852 | 31372 | 30187 | 13818 | 19811 | 16511 | 8989 | 9242 | 1964 | 7866 | 7926 | 7410 | 5406 | 6661 | 11480 | 7117 | 4545 | 8098 | 5001 | 2622 | 3158 | 820 | 1721 | 911 | 1589 | 1407 | 506 | 12138 | 1751 | 425 | 709 | 1650 | 698 | 445 | 0 | 1286 | 3482 | 1711 | 4181 | 5153 | 6914 | 4829 | 3513 | 20246
| ˃ 11 kV & < = 22 kV; SWER | km | 0 | 0 | 0 | 970 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 130 | 100 | 770 | 0 | 120 | 1100 | 330 | 0 | 930 | 530 | 410 | 790 | 790 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1790 | 840 | 2350 | 2590 | 0 | 3730 | 4110 | 9340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 320 | 1680 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; single phase | km | 1064 | 0 | 446 | 0 | 1104 | 3748 | 0 | 51 | 770 | 618 | 172 | 1266 | 41 | 1337 | 922 | 557 | 942 | 1337 | 972 | 1438 | 598 | 719 | 3252 | 2573 | 821 | 2867 | 1276 | 2624 | 0 | 466 | 1327 | 3171 | 2492 | 1043 | 5146 | 7202 | 9492 | 15438 | 8590 | 20655 | 7952 | 6544 | 15124 | 9471 | 13361 | 8134 | 4680 | 5176 | 7111 | 3738 | 1803 | 3252 | 598 | 1692 | 1104 | 0 | 517 | 0 | 0 | 0 | 1317 | 0 | 0 | 0 | 456 | 0 | 0 | 0 | 0 | 81 | 638 | 0 | 0 | 0 | 41 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 20 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; multiple phase | km | 14378 | 13804 | 9804 | 12665 | 9421 | 14187 | 16545 | 9471 | 49946 | 29150 | 23719 | 16494 | 23819 | 23668 | 36394 | 43609 | 42460 | 20575 | 17905 | 18661 | 15396 | 22459 | 47357 | 28565 | 40284 | 27245 | 32696 | 8444 | 8333 | 15174 | 13512 | 20797 | 34570 | 29492 | 44324 | 55851 | 69977 | 88950 | 78834 | 138896 | 132498 | 158131 | 163844 | 147350 | 127601 | 96023 | 103328 | 90542 | 69614 | 55800 | 45986 | 27568 | 17220 | 17391 | 8041 | 4685 | 10449 | 13643 | 8837 | 8696 | 6902 | 6660 | 6277 | 5270 | 9985 | 6076 | 5955 | 5512 | 1884 | 7214 | 2972 | 2438 | 1441 | 3980 | 12162 | 9703 | 1441 | 3527 | 2106 | 1360 | 191 | 0 | 393 | 554 | 272 | 1804 | 1652 | 2529 | 4887 | 846 | 15416
| > 22 kV & < = 66 kV | km | 8266 | 2474 | 332 | 654 | 996 | 533 | 1609 | 8779 | 1086 | 60 | 42516 | 282 | 3912 | 11172 | 2645 | 18905 | 1508 | 4686 | 442 | 2253 | 4445 | 0 | 2403 | 3288 | 18684 | 8075 | 14631 | 191 | 0 | 0 | 0 | 412 | 272 | 794 | 493 | 3047 | 1267 | 7451 | 14913 | 7824 | 11645 | 19750 | 36624 | 29484 | 36714 | 26568 | 21178 | 30540 | 29112 | 14853 | 18945 | 5883 | 17115 | 55670 | 3087 | 0 | 4686 | 10870 | 2816 | 734 | 2112 | 10478 | 442 | 1257 | 1187 | 533 | 0 | 0 | 5279 | 181 | 0 | 0 | 302 | 0 | 7451 | 0 | 644 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 0 | 141 | 0 | 0 | 0 | 0 | 764
| > 66 kV & < = 132 kV | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total overhead conductors | km | 39905 | 31076 | 24205 | 28848 | 23978 | 29985 | 29306 | 31558 | 68414 | 61968 | 106478 | 56949 | 80824 | 75432 | 78011 | 112766 | 84321 | 60107 | 68599 | 58370 | 38038 | 48453 | 103240 | 121289 | 97182 | 99525 | 70665 | 56017 | 34258 | 175394 | 29595 | 46504 | 71963 | 64549 | 91591 | 136904 | 159858 | 243379 | 215840 | 321312 | 323518 | 354651 | 391659 | 370013 | 372189 | 332451 | 321160 | 315163 | 282747 | 249337 | 206862 | 164303 | 162771 | 210758 | 137802 | 51205 | 166462 | 172187 | 163086 | 124368 | 168807 | 156153 | 111414 | 100113 | 107406 | 96467 | 83637 | 75565 | 56417 | 35750 | 24111 | 30673 | 23498 | 24149 | 44876 | 73331 | 19195 | 18368 | 16166 | 14333 | 5409 | 2470 | 6919 | 21400 | 25215 | 38946 | 40019 | 57827 | 48803 | 32531 | 187411
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE
| ˂ = 1 kV | km | 20472 | 28933 | 27017 | 23246 | 32782 | 35355 | 35446 | 31101 | 37192 | 28015 | 31589 | 35460 | 43202 | 51055 | 32614 | 30541 | 26684 | 24312 | 29610 | 25546 | 41390 | 55649 | 63276 | 44399 | 77251 | 100796 | 119652 | 53246 | 35735 | 64080 | 65570 | 37560 | 28392 | 37044 | 65616 | 61681 | 52423 | 71083 | 62526 | 46892 | 56708 | 55993 | 36847 | 24075 | 31551 | 23725 | 34897 | 50291 | 53236 | 28590 | 38770 | 20722 | 13262 | 12689 | 2188 | 799 | 740 | 1540 | 979 | 218 | 469 | 67 | 506 | 284 | 1844 | 77 | 93 | 0 | 0 | 125 | 232 | 11 | 0 | 0 | 232 | 148 | 56 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | km | 4718 | 7914 | 5580 | 6692 | 10669 | 5580 | 5379 | 7253 | 9577 | 15106 | 6331 | 3436 | 6662 | 6712 | 6471 | 7683 | 5049 | 4328 | 7703 | 5309 | 19594 | 1242 | 3236 | 2124 | 3636 | 721 | 3186 | 511 | 2444 | 180 | 160 | 2294 | 751 | 301 | 351 | 1493 | 1843 | 651 | 371 | 3105 | 2755 | 2134 | 1523 | 2765 | 411 | 551 | 851 | 821 | 601 | 511 | 561 | 641 | 1292 | 1443 | 1232 | 551 | 4117 | 3346 | 2454 | 1793 | 2294 | 2705 | 1983 | 5880 | 3576 | 4037 | 4458 | 5600 | 0 | 140 | 1272 | 0 | 0 | 0 | 40 | 381 | 571 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 311 | 1172 | 30 | 0 | 0 | 50 | 2544
| > 11 kV & < = 22 kV | km | 15567 | 29012 | 13054 | 18150 | 26008 | 20032 | 20012 | 18200 | 25748 | 28511 | 30263 | 17789 | 22514 | 24066 | 24387 | 24507 | 26579 | 31424 | 36229 | 37781 | 55801 | 23966 | 24947 | 19201 | 16007 | 21243 | 15927 | 12474 | 16998 | 2723 | 4485 | 2122 | 2703 | 1852 | 4705 | 7959 | 12193 | 13905 | 9050 | 8810 | 3153 | 13144 | 5086 | 2793 | 1732 | 6647 | 6447 | 15227 | 16098 | 17129 | 18390 | 6177 | 9590 | 9400 | 12083 | 5936 | 5356 | 3834 | 2903 | 9070 | 5136 | 5316 | 5496 | 3213 | 4315 | 5626 | 5136 | 491 | 3013 | 3163 | 771 | 50 | 0 | 110 | 150 | 2483 | 3884 | 1782 | 1712 | 270 | 2543 | 140 | 0 | 0 | 761 | 400 | 310 | 0 | 220 | 0 | 0
| > 22 kV & < = 33 kV | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV | km | 0 | 0 | 0 | 120 | 50 | 0 | 180 | 80 | 110 | 140 | 50 | 0 | 0 | 360 | 0 | 940 | 0 | 420 | 0 | 0 | 0 | 740 | 0 | 0 | 340 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | km | 3978 | 3860 | 4976 | 4297 | 4526 | 4581 | 4814 | 5546 | 4809 | 5536 | 5126 | 4076 | 4091 | 4518 | 4595 | 4297 | 4438 | 4544 | 4278 | 4590 | 3958 | 4488 | 3897 | 4243 | 4285 | 5204 | 4724 | 4195 | 3266 | 2674 | 3470 | 2479 | 2008 | 1578 | 1500 | 3101 | 2768 | 2331 | 2177 | 2022 | 1589 | 1395 | 1384 | 910 | 626 | 705 | 748 | 1383 | 1181 | 1326 | 908 | 722 | 439 | 263 | 245 | 209 | 83 | 96 | 97 | 92 | 100 | 68 | 59 | 49 | 49 | 42 | 82 | 17 | 14 | 13 | 8 | 8 | 4 | 2 | 2 | 94 | 7 | 1 | 0 | 0 | 2 | 2 | 0 | 6 | 9 | 17 | 5 | 16 | 18 | 3 | 42
| Total underground cables | km | 44735 | 69719 | 50627 | 52505 | 74035 | 65548 | 65831 | 62180 | 77436 | 77308 | 73359 | 60761 | 76469 | 86711 | 68067 | 67968 | 62750 | 65028 | 77820 | 73226 | 120743 | 86085 | 95356 | 69967 | 101519 | 127994 | 143589 | 70426 | 58443 | 69657 | 73685 | 44455 | 33854 | 40775 | 72172 | 74234 | 69227 | 87970 | 74124 | 60829 | 64205 | 72666 | 44840 | 30543 | 34320 | 31628 | 42943 | 67722 | 71116 | 47556 | 58629 | 28262 | 24583 | 23795 | 15748 | 7495 | 10296 | 8816 | 6433 | 11173 | 7999 | 8156 | 8044 | 9426 | 9784 | 9782 | 9769 | 6108 | 3027 | 3441 | 2283 | 69 | 4 | 112 | 424 | 3106 | 4518 | 2026 | 1712 | 270 | 2545 | 272 | 0 | 6 | 1417 | 1589 | 345 | 16 | 238 | 53 | 2586
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY
| ˂ = 11 kV; residential; simple type | number of assets | 4427 | 3016 | 3772 | 6452 | 5908 | 7186 | 7314 | 6136 | 4183 | 6030 | 21486 | 36046 | 37336 | 29650 | 20274 | 12650 | 7061 | 5994 | 4777 | 3534 | 3148 | 3606 | 2334 | 1095 | 961 | 937 | 926 | 1994 | 1841 | 624 | 785 | 1439 | 1683 | 1310 | 1663 | 2004 | 2119 | 2077 | 2270 | 2532 | 1940 | 1419 | 1285 | 1293 | 1425 | 1247 | 1285 | 1580 | 1389 | 1300 | 1326 | 1607 | 1946 | 1731 | 1702 | 1973 | 1978 | 1853 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV; commercial & industrial; simple type | number of assets | 381 | 260 | 325 | 556 | 508 | 619 | 632 | 511 | 374 | 438 | 1109 | 1881 | 1801 | 1266 | 873 | 620 | 461 | 413 | 363 | 288 | 274 | 315 | 248 | 318 | 537 | 475 | 257 | 967 | 1004 | 220 | 175 | 217 | 230 | 185 | 255 | 356 | 406 | 356 | 324 | 320 | 257 | 209 | 213 | 235 | 239 | 193 | 170 | 246 | 249 | 172 | 172 | 201 | 218 | 206 | 327 | 354 | 202 | 195 | 196 | 189 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV; residential; complex type | number of assets | 337 | 230 | 287 | 491 | 450 | 547 | 559 | 457 | 339 | 353 | 807 | 1381 | 1969 | 1714 | 861 | 505 | 322 | 351 | 335 | 246 | 258 | 361 | 271 | 137 | 155 | 157 | 125 | 1991 | 2070 | 164 | 79 | 107 | 124 | 135 | 144 | 156 | 171 | 192 | 216 | 218 | 188 | 166 | 181 | 183 | 181 | 147 | 116 | 116 | 107 | 122 | 119 | 119 | 125 | 109 | 210 | 228 | 121 | 124 | 135 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV; commercial & industrial; complex type | number of assets | 83 | 56 | 71 | 121 | 111 | 135 | 139 | 113 | 73 | 69 | 116 | 200 | 219 | 168 | 139 | 107 | 73 | 78 | 72 | 54 | 55 | 61 | 68 | 87 | 157 | 175 | 120 | 518 | 506 | 59 | 37 | 40 | 48 | 43 | 58 | 69 | 66 | 64 | 73 | 79 | 63 | 48 | 48 | 62 | 66 | 47 | 34 | 44 | 54 | 43 | 33 | 37 | 35 | 40 | 144 | 130 | 27 | 32 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV; subdivision; complex type | number of assets
| > 11 kV & < = 22 kV; commercial & industrial | number of assets
| > 11 kV & < = 22 kV; subdivision | number of assets
| > 22 kV & < = 33 kV; commercial & industrial | number of assets
| > 22 kV & < = 33 kV; subdivision | number of assets
| > 33 kV & < = 66 kV; commercial & industrial | number of assets
| > 33 kV & < = 66 kV; subdivision | number of assets
| > 66 kV & < = 132 kV; commercial & industrial | number of assets
| > 66 kV & < = 132 kV; subdivision | number of assets
| > 132 kV; commercial & industrial | number of assets
| > 132 kV; subdivision | number of assets
| Other | number of assets
| Total service lines | number of assets | 5228 | 3562 | 4455 | 7620 | 6977 | 8487 | 8644 | 7217 | 4969 | 6890 | 23518 | 39508 | 41325 | 32798 | 22147 | 13882 | 7917 | 6836 | 5547 | 4122 | 3735 | 4343 | 2921 | 1637 | 1810 | 1744 | 1428 | 5470 | 5421 | 1067 | 1076 | 1803 | 2085 | 1673 | 2120 | 2585 | 2762 | 2689 | 2883 | 3149 | 2448 | 1842 | 1727 | 1773 | 1911 | 1634 | 1605 | 1986 | 1799 | 1637 | 1650 | 1964 | 2324 | 2086 | 2383 | 2685 | 2328 | 2204 | 800 | 189 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE; AMPERE RATING; NUMBER OF PHASES (AT LV)
| Pole mounted; < = 22kV; < = 60 kVA; single phase | number of assets | 32 | 32 | 21 | 24 | 37 | 21 | 17 | 34 | 21 | 15 | 20 | 15 | 26 | 22 | 17 | 25 | 24 | 16 | 1 | 25 | 15 | 15 | 13 | 16 | 20 | 17 | 13 | 11 | 12 | 13 | 15 | 6 | 21 | 10 | 31 | 50 | 61 | 42 | 59 | 75 | 59 | 30 | 21 | 20 | 24 | 18 | 19 | 11 | 12 | 6 | 5 | 1 | 2 | 6 | 4 | 5 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | 4 | 0 | 3 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole mounted; < = 22kV; > 60 kVA and < = 600 kVA; single phase | number of assets | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole mounted; < = 22kV; > 600 kVA; single phase | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole mounted; < = 22kV; < = 60 kVA ; multiple phase | number of assets | 13 | 13 | 4 | 7 | 7 | 3 | 9 | 3 | 4 | 4 | 7 | 8 | 2 | 4 | 4 | 2 | 6 | 1 | 0 | 12 | 11 | 2 | 7 | 7 | 16 | 29 | 19 | 10 | 8 | 17 | 27 | 14 | 7 | 7 | 13 | 25 | 19 | 19 | 24 | 18 | 13 | 8 | 9 | 6 | 10 | 6 | 6 | 7 | 10 | 4 | 4 | 3 | 3 | 3 | 2 | 3 | 1 | 7 | 1 | 1 | 0 | 1 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0
| Pole mounted; < = 22kV; > 60 kVA and < = 600 kVA ; multiple phase | number of assets | 197 | 189 | 200 | 203 | 195 | 199 | 210 | 162 | 189 | 265 | 296 | 178 | 339 | 196 | 143 | 217 | 597 | 278 | 256 | 243 | 102 | 182 | 187 | 175 | 220 | 97 | 81 | 44 | 32 | 30 | 43 | 40 | 61 | 47 | 71 | 131 | 141 | 100 | 114 | 115 | 60 | 44 | 65 | 59 | 55 | 49 | 69 | 107 | 89 | 45 | 51 | 32 | 42 | 30 | 34 | 42 | 12 | 30 | 32 | 22 | 18 | 15 | 13 | 14 | 12 | 10 | 6 | 1 | 2 | 2 | 3 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole mounted; < = 22kV; > 600 kVA ; multiple phase | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk mounted; < = 22kV; < = 60 kVA; single phase | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk mounted; < = 22kV; > 60 kVA and < = 600 kVA; single phase | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk mounted; < = 22kV; > 600 kVA; single phase | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk mounted; < = 22kV; < = 60 kVA ; multiple phase | number of assets | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk mounted; < = 22kV; > 60 kVA and < = 600 kVA ; multiple phase | number of assets | 43 | 53 | 53 | 58 | 51 | 56 | 77 | 56 | 62 | 80 | 54 | 55 | 63 | 54 | 35 | 56 | 88 | 55 | 57 | 68 | 46 | 52 | 55 | 65 | 46 | 40 | 31 | 28 | 22 | 15 | 29 | 20 | 9 | 24 | 21 | 32 | 32 | 23 | 21 | 14 | 14 | 12 | 9 | 8 | 8 | 7 | 21 | 19 | 5 | 11 | 2 | 1 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk mounted; < = 22kV; > 600 kVA ; multiple phase | number of assets | 31 | 37 | 35 | 25 | 23 | 29 | 31 | 41 | 38 | 32 | 15 | 25 | 39 | 41 | 22 | 25 | 25 | 40 | 35 | 37 | 27 | 29 | 13 | 12 | 19 | 11 | 4 | 4 | 1 | 1 | 5 | 5 | 4 | 1 | 3 | 4 | 1 | 4 | 0 | 0 | 2 | 2 | 0 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; < = 60 kVA; single phase | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; > 60 kVA and < = 600 kVA; single phase | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; > 600 kVA; single phase | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; < = 60 kVA; multiple phase | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; > 60 kVA and < = 600 kVA; multiple phase | number of assets | 0 | 3 | 4 | 5 | 4 | 8 | 13 | 17 | 7 | 10 | 7 | 6 | 6 | 8 | 3 | 9 | 4 | 2 | 2 | 0 | 0 | 2 | 2 | 2 | 0 | 1 | 0 | 2 | 0 | 0 | 4 | 1 | 3 | 1 | 1 | 4 | 1 | 7 | 1 | 4 | 10 | 6 | 2 | 0 | 3 | 2 | 2 | 1 | 3 | 3 | 6 | 13 | 6 | 2 | 1 | 2 | 1 | 5 | 3 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; ˂ 22 kV; > 600 kVA; multiple phase | number of assets | 11 | 10 | 5 | 13 | 6 | 4 | 7 | 7 | 6 | 14 | 14 | 5 | 13 | 11 | 5 | 11 | 12 | 15 | 12 | 16 | 4 | 4 | 4 | 7 | 5 | 0 | 6 | 10 | 0 | 4 | 4 | 4 | 0 | 1 | 4 | 8 | 7 | 8 | 9 | 4 | 0 | 3 | 2 | 1 | 1 | 6 | 2 | 1 | 0 | 1 | 4 | 1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > = 22 kV & < = 33 kV; < = 15 MVA | number of assets | 40 | 38 | 22 | 19 | 40 | 33 | 23 | 20 | 22 | 27 | 19 | 10 | 42 | 10 | 7 | 17 | 20 | 17 | 14 | 12 | 22 | 17 | 17 | 14 | 21 | 25 | 15 | 34 | 9 | 13 | 30 | 32 | 24 | 26 | 61 | 70 | 69 | 42 | 44 | 39 | 28 | 22 | 26 | 24 | 23 | 24 | 26 | 22 | 18 | 9 | 11 | 11 | 12 | 7 | 3 | 11 | 2 | 7 | 5 | 3 | 4 | 6 | 1 | 7 | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 4 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0
| Ground outdoor / Indoor chamber mounted; > = 22 kV & < = 33 kV; > 15 MVA and < = 40 MVA | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > = 22 kV & < = 33 kV; > 40 MVA | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 33 kV & < = 66 kV; < = 15 MVA | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 33 kV & < = 66 kV; > 15 MVA and < = 40 MVA | number of assets | 0 | 0 | 1 | 3 | 1 | 1 | 0 | 4 | 2 | 1 | 2 | 1 | 4 | 4 | 0 | 4 | 3 | 3 | 2 | 3 | 1 | 4 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 0 | 0 | 4 | 0 | 2 | 0 | 0 | 4 | 1 | 0 | 0 | 2 | 0 | 4 | 5 | 3 | 7 | 6 | 0 | 4 | 7 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 33 kV & < = 66 kV; > 40 MVA | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 66 kV & < = 132 kV; < = 100 MVA | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 66 kV & < = 132 kV; > 100 MVA | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 132 kV; < = 100 MVA | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground outdoor / Indoor chamber mounted; > 132 kV; > 100 MVA | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total transformers | number of assets | 367 | 375 | 345 | 358 | 364 | 356 | 387 | 344 | 351 | 448 | 434 | 303 | 535 | 350 | 237 | 366 | 779 | 427 | 379 | 416 | 229 | 308 | 300 | 299 | 347 | 223 | 169 | 143 | 88 | 93 | 158 | 123 | 132 | 127 | 205 | 326 | 331 | 245 | 274 | 270 | 186 | 128 | 134 | 120 | 128 | 113 | 148 | 168 | 138 | 83 | 84 | 62 | 69 | 51 | 46 | 72 | 23 | 54 | 49 | 36 | 24 | 27 | 25 | 28 | 18 | 14 | 10 | 5 | 2 | 6 | 5 | 3 | 1 | 0 | 4 | 1 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE;SWITCH FUNCTION
| ˂ = 11 kV; fuse | number of assets | 38 | 37 | 32 | 18 | 21 | 31 | 32 | 26 | 50 | 52 | 39 | 67 | 59 | 104 | 73 | 92 | 95 | 64 | 70 | 50 | 38 | 36 | 63 | 40 | 31 | 20 | 25 | 29 | 15 | 46 | 15 | 25 | 29 | 15 | 17 | 40 | 26 | 61 | 38 | 37 | 38 | 29 | 13 | 14 | 17 | 35 | 4 | 21 | 13 | 7 | 10 | 11 | 15 | 17 | 11 | 16 | 16 | 13 | 22 | 16 | 33 | 15 | 9 | 15 | 13 | 7 | 12 | 3 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 3
| ˂ = 11 kV; switch | number of assets | 1276 | 1183 | 1028 | 722 | 777 | 720 | 888 | 817 | 841 | 1636 | 1231 | 1276 | 1578 | 1679 | 1349 | 1476 | 2425 | 1325 | 1214 | 1576 | 1368 | 3845 | 3314 | 6495 | 2390 | 1475 | 723 | 621 | 517 | 1143 | 708 | 691 | 943 | 999 | 746 | 1446 | 1434 | 1411 | 1280 | 1490 | 1313 | 1058 | 627 | 907 | 666 | 861 | 418 | 625 | 533 | 498 | 461 | 562 | 675 | 638 | 582 | 1114 | 712 | 655 | 674 | 492 | 695 | 601 | 377 | 330 | 320 | 367 | 270 | 204 | 146 | 60 | 43 | 68 | 31 | 52 | 25 | 200 | 36 | 21 | 23 | 26 | 16 | 4 | 11 | 40 | 78 | 104 | 62 | 125 | 98 | 52 | 376
| ˂ = 11 kV; circuit breaker | number of assets | 5 | 4 | 11 | 67 | 19 | 24 | 5 | 11 | 43 | 11 | 30 | 32 | 54 | 10 | 12 | 4 | 21 | 22 | 10 | 27 | 22 | 2 | 6 | 1 | 5 | 0 | 0 | 0 | 1 | 5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 27 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV; switch | number of assets | 633 | 549 | 487 | 494 | 480 | 581 | 466 | 290 | 413 | 618 | 535 | 537 | 599 | 544 | 554 | 573 | 646 | 426 | 387 | 472 | 473 | 382 | 480 | 331 | 442 | 344 | 219 | 188 | 188 | 505 | 753 | 186 | 173 | 570 | 137 | 311 | 379 | 414 | 314 | 356 | 448 | 313 | 182 | 166 | 219 | 197 | 65 | 192 | 199 | 197 | 112 | 137 | 132 | 146 | 166 | 182 | 155 | 120 | 118 | 110 | 126 | 80 | 79 | 55 | 51 | 52 | 38 | 30 | 18 | 13 | 7 | 2 | 5 | 11 | 4 | 46 | 2 | 4 | 4 | 1 | 3 | 1 | 2 | 1 | 1 | 18 | 2 | 12 | 6 | 0 | 22
| > 11 kV & < = 22 kV; circuit breaker | number of assets | 11 | 18 | 24 | 23 | 30 | 59 | 14 | 9 | 34 | 12 | 43 | 36 | 53 | 11 | 10 | 37 | 22 | 32 | 37 | 58 | 12 | 27 | 23 | 21 | 8 | 17 | 7 | 3 | 4 | 9 | 22 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 4 | 0 | 1 | 11 | 8 | 0 | 4 | 15 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 12 | 4 | 9 | 23 | 8 | 6 | 10 | 6 | 12 | 0 | 0 | 0 | 3 | 4 | 1 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV; switch | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV; circuit breaker | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV; switch | number of assets | 3 | 2 | 5 | 2 | 4 | 2 | 1 | 9 | 3 | 3 | 17 | 4 | 32 | 6 | 15 | 6 | 6 | 9 | 6 | 18 | 12 | 1 | 10 | 3 | 0 | 6 | 0 | 0 | 52 | 0 | 0 | 0 | 14 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV; circuit breaker | number of assets | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 4 | 0 | 1 | 5 | 3 | 12 | 0 | 7 | 2 | 6 | 5 | 4 | 6 | 4 | 2 | 7 | 2 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 4 | 6 | 0 | 3 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV; switch | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; circuit breaker | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; switch | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; circuit breaker | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | number of assets | 5 | 9 | 7 | 20 | 46 | 67 | 74 | 53 | 48 | 84 | 95 | 104 | 254 | 34 | 15 | 60 | 24 | 42 | 42 | 56 | 35 | 68 | 65 | 155 | 311 | 1008 | 322 | 66 | 201 | 0 | 11 | 7 | 33 | 231 | 40 | 36 | 157 | 6 | 24 | 42 | 8 | 0 | 35 | 0 | 0 | 0 | 0 | 9 | 4 | 88 | 56 | 17 | 14 | 0 | 0 | 1 | 7 | 3 | 15 | 8 | 0 | 46 | 0 | 0 | 24 | 7 | 14 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7
| Total switchgear | number of assets | 1971 | 1803 | 1596 | 1346 | 1377 | 1484 | 1481 | 1219 | 1432 | 2417 | 1995 | 2059 | 2641 | 2388 | 2035 | 2250 | 3245 | 1925 | 1770 | 2263 | 1964 | 4363 | 3968 | 7048 | 3188 | 2870 | 1298 | 907 | 978 | 1708 | 1513 | 909 | 1196 | 1998 | 940 | 1835 | 1996 | 1892 | 1660 | 1925 | 1808 | 1411 | 865 | 1088 | 906 | 1108 | 511 | 848 | 749 | 790 | 642 | 727 | 836 | 804 | 759 | 1321 | 896 | 803 | 851 | 669 | 877 | 753 | 471 | 414 | 415 | 446 | 334 | 294 | 166 | 77 | 54 | 71 | 39 | 65 | 29 | 271 | 38 | 25 | 27 | 27 | 19 | 5 | 14 | 41 | 80 | 124 | 64 | 138 | 105 | 53 | 408
PUBLIC LIGHTING BY: ASSET TYPE; LIGHTING OBLIGATION
| Luminaires; major road | number of assets | 3352 | 2299 | 1736 | 1112 | 396 | 388 | 398 | 303 | 137 | 158 | 222 | 49 | 115 | 118 | 82 | 81 | 95 | 141 | 57 | 84 | 391 | 339 | 99 | 37 | 830 | 93 | 117 | 30 | 498 | 2101 | 221 | 527 | 1832 | 276 | 305 | 66 | 0 | 0 | 0 | 5 | 7 | 9 | 12 | 8 | 8 | 2 | 6 | 5 | 9 | 5 | 4 | 2 | 6 | 19 | 10 | 140 | 9 | 15 | 17 | 9 | 3 | 0 | 0 | 0 | 0 | 4160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Luminaires; minor road | number of assets | 16617 | 12525 | 6403 | 7024 | 9722 | 2997 | 19034 | 8453 | 4424 | 7714 | 205 | 55 | 104 | 134 | 152 | 215 | 143 | 113 | 99 | 202 | 85 | 385 | 112 | 88 | 209 | 97 | 93 | 29 | 171 | 183 | 36 | 80 | 89 | 18 | 55 | 47 | 3 | 0 | 1 | 2 | 2 | 2 | 1 | 1 | 4 | 2 | 1 | 2 | 1 | 0 | 1 | 5 | 1 | 5 | 27 | 33 | 16 | 13 | 22 | 19 | 8 | 0 | 0 | 0 | 0 | 1737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brackets; major road | number of assets | 3352 | 2299 | 1736 | 1112 | 396 | 388 | 398 | 303 | 137 | 158 | 222 | 49 | 115 | 118 | 82 | 81 | 95 | 141 | 57 | 84 | 391 | 339 | 99 | 37 | 830 | 93 | 117 | 30 | 498 | 2101 | 221 | 527 | 1832 | 276 | 305 | 66 | 0 | 0 | 0 | 5 | 7 | 9 | 12 | 8 | 8 | 2 | 6 | 5 | 9 | 5 | 4 | 2 | 6 | 19 | 10 | 140 | 9 | 15 | 17 | 9 | 3 | 0 | 0 | 0 | 0 | 4160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brackets; minor road | number of assets | 16617 | 12525 | 6403 | 7024 | 9722 | 2997 | 19034 | 8453 | 4424 | 7714 | 205 | 55 | 104 | 134 | 152 | 215 | 143 | 113 | 99 | 202 | 85 | 385 | 112 | 88 | 209 | 97 | 93 | 29 | 171 | 183 | 36 | 80 | 89 | 18 | 55 | 47 | 3 | 0 | 1 | 2 | 2 | 2 | 1 | 1 | 4 | 2 | 1 | 2 | 1 | 0 | 1 | 5 | 1 | 5 | 27 | 33 | 16 | 13 | 22 | 19 | 8 | 0 | 0 | 0 | 0 | 1737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lamps; major road | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lamps; minor road | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poles / Columns; major road | number of assets | 108 | 118 | 173 | 144 | 163 | 129 | 137 | 145 | 171 | 163 | 68 | 117 | 130 | 116 | 74 | 88 | 107 | 118 | 156 | 90 | 55 | 61 | 163 | 195 | 66 | 90 | 54 | 22 | 2560 | 186 | 6 | 31 | 20 | 20 | 13 | 39 | 37 | 33 | 20 | 52 | 39 | 43 | 36 | 33 | 74 | 59 | 21 | 54 | 42 | 31 | 8 | 21 | 27 | 46 | 23 | 35 | 14 | 15 | 24 | 25 | 27 | 18 | 31 | 8 | 23 | 10 | 5 | 9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 1 | 3
| Poles / Columns; minor road | number of assets | 448 | 283 | 498 | 334 | 445 | 477 | 373 | 458 | 405 | 474 | 397 | 448 | 313 | 330 | 583 | 497 | 655 | 684 | 710 | 764 | 525 | 867 | 1045 | 771 | 629 | 791 | 319 | 246 | 11295 | 312 | 53 | 19 | 62 | 31 | 40 | 74 | 130 | 232 | 56 | 51 | 88 | 20 | 35 | 43 | 6 | 52 | 40 | 28 | 33 | 26 | 28 | 29 | 33 | 32 | 49 | 41 | 37 | 24 | 40 | 14 | 18 | 53 | 17 | 15 | 61 | 6 | 14 | 6 | 2 | 5 | 1 | 8 | 1 | 0 | 0 | 44 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 3 | 3 | 1 | 1 | 6 | 2 | 17
| Other | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total public lighting | number of assets | 40494 | 30049 | 16949 | 16750 | 20844 | 7376 | 39374 | 18115 | 9698 | 16381 | 1319 | 773 | 881 | 950 | 1125 | 1177 | 1238 | 1310 | 1178 | 1426 | 1532 | 2376 | 1630 | 1216 | 2773 | 1261 | 793 | 386 | 15193 | 5066 | 573 | 1264 | 3924 | 639 | 773 | 339 | 173 | 265 | 78 | 117 | 145 | 85 | 97 | 94 | 104 | 119 | 75 | 96 | 95 | 67 | 46 | 64 | 74 | 126 | 146 | 422 | 101 | 95 | 142 | 95 | 67 | 71 | 48 | 23 | 84 | 11810 | 19 | 15 | 3 | 5 | 1 | 8 | 1 | 0 | 0 | 103 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 3 | 5 | 1 | 1 | 8 | 3 | 20
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION
| Field devices | number of assets | 5 | 117 | 151 | 99 | 75 | 139 | 199 | 162 | 62 | 82 | 188 | 229 | 91 | 30 | 114 | 115 | 106 | 243 | 86 | 34 | 76 | 5 | 59 | 16 | 8 | 51 | 22 | 0 | 5 | 45 | 5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 1 | 1 | 1 | 21 | 1 | 2 | 0 | 4 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Local network wiring assets | km | 5 | 16 | 21 | 6 | 12 | 26 | 7 | 20 | 16 | 8 | 33 | 14 | 9 | 2 | 3 | 14 | 5 | 8 | 10 | 11 | 6 | 0 | 6 | 7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 3 | 2 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications network assets | number of assets | 3 | 34 | 34 | 13 | 27 | 26 | 75 | 24 | 17 | 12 | 56 | 35 | 36 | 7 | 22 | 15 | 30 | 24 | 24 | 84 | 22 | 6 | 1 | 0 | 0 | 1 | 12 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Master station assets | number of assets
| Communications site infrastructure | number of assets
| Communications linear assets | km | 5.35 | 0 | 8.31 | 0 | 0 | 0.83 | 2.9 | 0.82 | 9.24 | 2.28 | 5.57 | 4.48 | 18.44 | 4.01 | 3.12 | 44.91 | 51.72 | 43.06 | 41.79 | 45.83 | 64.63 | 39.33 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AFLC | number of assets
| Other | number of assets
| Total SCADA network control and protection systems | number of assets | 18.35 | 167 | 214.31 | 118 | 114 | 191.83 | 283.9 | 206.82 | 104.24 | 104.28 | 282.57 | 282.48 | 154.44 | 43.01 | 142.12 | 188.91 | 192.72 | 318.06 | 161.79 | 174.83 | 168.63 | 50.33 | 66.05 | 23 | 8 | 53 | 34 | 1 | 8 | 45 | 5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 2 | 11 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 0 | 0 | 1 | 1 | 4 | 4 | 25 | 3 | 8 | 6 | 5 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BY: BUSINESS SPECIFIED
| Buildings | number of assets | 0 | 0 | 3 | 2 | 2 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 4 | 1 | 0 | 1 | 2 | 1 | 2 | 1 | 2 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 2 | 2 | 4 | 3 | 11 | 6 | 1 | 0 | 8 | 3 | 1 | 1 | 0 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| Civil | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 6 | 3 | 3 | 0 | 4 | 4 | 1 | 2 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacitor Banks - Large | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 9 | 1 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 2 | 1 | 1 | 0 | 0 | 9 | 0 | 0 | 1 | 6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fences | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 3 | 2 | 5 | 4 | 2 | 2 | 1 | 1 | 4 | 2 | 7 | 2 | 1 | 1 | 1 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTs and VTs | number of assets | 1 | 4 | 17 | 63 | 10 | 40 | 0 | 22 | 12 | 13 | 21 | 21 | 67 | 31 | 9 | 19 | 15 | 14 | 6 | 13 | 9 | 3 | 19 | 6 | 0 | 26 | 3 | 0 | 54 | 0 | 0 | 0 | 38 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NERs | number of assets | 0 | 0 | 1 | 2 | 0 | 3 | 0 | 1 | 2 | 0 | 2 | 2 | 3 | 0 | 5 | 5 | 1 | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bunding/Noise | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lines Miscellaneous | number of assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total assets - other by business specified categories | number of assets | 1 | 4 | 21 | 67 | 12 | 44 | 1 | 24 | 15 | 20 | 36 | 27 | 82 | 42 | 17 | 28 | 19 | 18 | 13 | 17 | 20 | 8 | 22 | 13 | 4 | 31 | 6 | 1 | 64 | 0 | 0 | 3 | 45 | 255 | 3 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 3 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 2 | 8 | 6 | 3 | 19 | 9 | 5 | 0 | 15 | 7 | 2 | 3 | 0 | 3 | 3 | 0 | 1 | 0 | 2 | 0 | 1 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0

## 5.3 MD - Network level
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| CA RIN 5.3 MAXIMUM DEMAND AT NETWORK LEVEL |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC02 - Operational outputs ¦ Maximum demand
System maximum demand
5.3.1 MAXIMUM DEMAND CHARACTERISTICS
| System maximum demand | Units | Demand
| Date Coincident Raw System Annual Maximum Demand occurred | DD MM YYYY | 2024-12-16
| Time Coincident Raw System Annual Maximum Demand occurred | hh:mm:ss | 18:30
| Summer/winter peaking classification | Summer / Winter | Summer
| Embedded generation at time of Coincident raw system annual maximum demand | MW | 6.682

## 5.4 MD & utilisation
| ANNUAL INFORMATION ORDER | [13 empty] | #25C6FF | Protected (SOCI)
| United Energy | [13 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [13 empty] | 12.5% Grey | Amended
| CA RIN 5.4 MAXIMUM DEMAND AND UTILISATION AT SPATIAL LEVEL | [13 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
DC02 - Operational outputs ¦maximum demand
Coincident maximum demand by sub-transmission substation
Non-coincident maximum demand by sub-transmission substation
Coincident maximum demand by zone substation
Non-coincident maximum demand by zone substation
5.4.1 NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND - SUBTRANSMISSION SUBSTATION & ZONE SUBSTATION
| Substation | Network Level | Incidence | Date Maximum Demand Occurred | Half Hour Time Period Maximum Demand Occurred | Seasonal peak | Substation Rating | Raw Adjusted Maximum Demand MW | Raw Adjusted Maximum Demand MVA | Adjustments - Embedded Generation | Weather corrected maximum demand 10% POE MW | Weather corrected maximum demand 10% POE MVA | Weather corrected maximum demand 50% POE MW | Weather corrected maximum demand 50% POE MVA
| Name | Subtransmission / Zone | Coincident / non-coincident | DD/MM/YYYY | hh:mm | Summer/Winter | MVA | MW | MVA | MW | MW | MVA | MW | MVA
| BH | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 99 | 41.854 | 42.482 | 0 | 55.888 | 56.727 | 49.212 | 49.951
| BH | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 99 | 45.267 | 46.096 | 0 | 60.445 | 62.114 | 53.225 | 54.621
| BR | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 60 | 27.925 | 28.19 | 0 | 29.986 | 30.271 | 26.367 | 26.617
| BR | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 60 | 28.996 | 29.282 | 0 | 31.136 | 31.547 | 27.378 | 27.663
| BT | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 60 | 30.932 | 30.937 | 0 | 33.177 | 33.182 | 29.669 | 29.673
| BT | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 60 | 32.508 | 32.54 | 0 | 34.867 | 34.885 | 31.18 | 31.191
| BU | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 60 | 27.769 | 27.999 | 0 | 28.288 | 28.523 | 25.902 | 26.118
| BU | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 60 | 31.554 | 31.886 | 0 | 32.144 | 32.209 | 29.433 | 29.492
| BW | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 40.5 | 22.482 | 22.493 | 0 | 23.314 | 23.326 | 21.325 | 21.336
| BW | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 40.5 | 23.982 | 24.053 | 0 | 24.869 | 24.93 | 22.748 | 22.784
| CDA | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 53 | 24.201 | 24.356 | 0 | 26.973 | 27.146 | 25.011 | 25.171
| CDA | Zone | Non-coincident | 16/12/2024 | 18:30 | Summer | 53 | 24.201 | 24.356 | 0 | 26.973 | 27.177 | 25.011 | 25.172
| CFD | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 49.944 | 49.982 | 0 | 52.519 | 52.558 | 46.677 | 46.712
| CFD | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 66 | 50.851 | 50.895 | 0 | 53.473 | 53.501 | 47.525 | 47.529
| CM | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 60 | 18.715 | 18.722 | 0 | 23.437 | 23.446 | 22.004 | 22.013
| CM | Zone | Non-coincident | 2025-03-02 | 17:00 | Summer | 60 | 19.05 | 19.056 | 0 | 23.856 | 23.869 | 22.398 | 22.406
| CRM | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 99 | 75.291 | 75.295 | 0 | 88.629 | 88.634 | 78.881 | 78.885
| CRM | Zone | Non-coincident | 16/12/2024 | 18:30 | Summer | 99 | 75.291 | 75.295 | 0 | 88.629 | 88.877 | 78.881 | 79.054
| DC | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 84 | 74.223 | 74.262 | 0 | 77.785 | 77.826 | 70.678 | 70.716
| DC | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 84 | 82.338 | 82.342 | 0 | 86.289 | 86.289 | 78.406 | 78.423
| DMA | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 31.291 | 31.387 | 0 | 38.804 | 38.923 | 34.667 | 34.773
| DMA | Zone | Non-coincident | 2025-05-01 | 18:00 | Summer | 66 | 37.431 | 37.457 | 0 | 46.418 | 46.418 | 41.469 | 41.477
| DN | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 104 | 66.502 | 66.745 | 1.048 | 70.396 | 70.653 | 65.026 | 65.264
| DN | Zone | Non-coincident | 16/12/2024 | 16:30 | Summer | 104 | 69.078 | 69.521 | 1.186 | 73.122 | 73.502 | 67.545 | 67.825
| DSH | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 99 | 44.634 | 44.733 | 0 | 50.349 | 50.46 | 48.341 | 48.447
| DSH | Zone | Non-coincident | 2024-04-07 | 9:30 | Winter | 99 | 58.765 | 59.275 | 0 | 66.289 | 67.037 | 63.644 | 64.343
| DVY | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 99 | 60.283 | 61.048 | 0 | 68.146 | 69.01 | 64.319 | 65.135
| DVY | Zone | Non-coincident | 2024-03-07 | 8:30 | Winter | 99 | 77.282 | 78.632 | 0 | 87.361 | 89.086 | 82.456 | 84.015
| EB | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 93 | 52.489 | 52.5 | 0 | 55.263 | 55.275 | 50.632 | 50.642
| EB | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 93 | 54.323 | 54.386 | 0 | 57.194 | 57.248 | 52.401 | 52.428
| EL | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 60 | 31.3 | 31.551 | 0 | 36.385 | 36.676 | 32.566 | 32.827
| EL | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 60 | 32.37 | 32.637 | 0 | 37.628 | 38.322 | 33.679 | 34.155
| EM | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 54 | 33.994 | 34 | 0 | 34.277 | 34.284 | 30.79 | 30.795
| EM | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 54 | 35.492 | 35.537 | 0 | 35.788 | 35.843 | 32.146 | 32.18
| EW | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 60 | 22.423 | 22.479 | 0 | 26.936 | 27.004 | 23.666 | 23.725
| EW | Zone | Non-coincident | 15/07/2024 | 19:00 | Winter | 60 | 24.195 | 24.32 | 0 | 29.065 | 29.098 | 25.536 | 25.601
| FSH | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 93 | 67.781 | 67.785 | 0 | 80.129 | 80.134 | 69.223 | 69.226
| FSH | Zone | Non-coincident | 2025-03-02 | 19:30 | Summer | 93 | 83.795 | 84.189 | 0 | 99.06 | 99.162 | 85.577 | 85.616
| FTN | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 50.959 | 51.003 | 0 | 56.869 | 56.918 | 53.122 | 53.168
| FTN | Zone | Non-coincident | 16/12/2024 | 18:30 | Summer | 66 | 50.959 | 51.003 | 0 | 56.869 | 56.987 | 53.122 | 53.182
| GW | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 84 | 56.855 | 57.03 | 0.431 | 63.214 | 63.408 | 58.42 | 58.6
| GW | Zone | Non-coincident | 16/12/2024 | 18:00 | Summer | 84 | 57.245 | 57.483 | 0.429 | 63.647 | 63.647 | 58.82 | 58.82
| HGS | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 44.81 | 45.052 | 0 | 58.486 | 58.802 | 51.887 | 52.166
| HGS | Zone | Non-coincident | 16/12/2024 | 19:00 | Summer | 66 | 45.58 | 45.776 | 0 | 59.492 | 59.555 | 52.779 | 52.825
| HT | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 84 | 43.141 | 43.342 | 0 | 48.742 | 48.968 | 44.955 | 45.164
| HT | Zone | Non-coincident | 19/06/2025 | 10:00 | Winter | 84 | 44.943 | 45.161 | 0 | 50.777 | 50.788 | 46.832 | 46.842
| K | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 60 | 39.44 | 39.631 | 0 | 43.043 | 43.252 | 38.858 | 39.046
| K | Zone | Non-coincident | 16/12/2024 | 18:00 | Summer | 60 | 39.886 | 40.036 | 0 | 43.53 | 43.595 | 39.297 | 39.421
| KBH | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 33 | 29.221 | 29.271 | 0 | 31.42 | 31.474 | 29.245 | 29.295
| KBH | Zone | Non-coincident | 16/12/2024 | 18:30 | Summer | 33 | 29.221 | 29.271 | 0 | 31.42 | 31.51 | 29.245 | 29.305
| LD | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 93 | 48.616 | 48.913 | 0 | 50.975 | 51.139 | 46.653 | 46.771
| LD | Zone | Non-coincident | 16/12/2024 | 18:30 | Summer | 93 | 48.616 | 48.913 | 0 | 50.975 | 51.139 | 46.653 | 46.771
| LWN | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 45.223 | 45.281 | 0 | 52.333 | 52.401 | 47.237 | 47.298
| LWN | Zone | Non-coincident | 16/12/2024 | 19:00 | Summer | 66 | 45.869 | 45.926 | 0 | 53.082 | 53.153 | 47.913 | 47.951
| M | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 87 | 36.337 | 36.572 | 0 | 37.867 | 38.064 | 34.813 | 34.961
| M | Zone | Non-coincident | 16/12/2024 | 18:30 | Summer | 87 | 36.337 | 36.572 | 0 | 37.867 | 38.064 | 34.813 | 34.961
| MC | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 87 | 51.085 | 52.008 | 0 | 52.128 | 53.07 | 49.067 | 49.953
| MC | Zone | Non-coincident | 13/02/2025 | 17:00 | Summer | 87 | 55.942 | 56.719 | 0 | 57.085 | 58.761 | 53.732 | 55.194
| MGE | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 99 | 66.621 | 66.668 | 0 | 71.887 | 71.938 | 66.291 | 66.338
| MGE | Zone | Non-coincident | 2025-03-02 | 17:00 | Summer | 99 | 69.344 | 69.383 | 0 | 74.825 | 74.88 | 69 | 69.016
| MR | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 47.037 | 47.276 | 0 | 56.018 | 56.303 | 47.818 | 48.061
| MR | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 66 | 48.642 | 49.051 | 0 | 57.93 | 58.223 | 49.45 | 49.624
| MTN | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 59.522 | 59.534 | 0 | 67.59 | 67.604 | 60.548 | 60.56
| MTN | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 66 | 61.684 | 61.771 | 0 | 70.045 | 70.095 | 62.747 | 62.768
| NB | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 43.816 | 44.133 | 0 | 47.999 | 48.347 | 41.481 | 41.781
| NB | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 66 | 46.74 | 47.141 | 0 | 51.202 | 51.893 | 44.249 | 44.682
| NO | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 90 | 32.056 | 32.247 | 0 | 33.322 | 33.52 | 31.017 | 31.201
| NO | Zone | Non-coincident | 16/12/2024 | 16:00 | Summer | 90 | 37.376 | 37.433 | 0 | 38.852 | 39.008 | 36.164 | 36.26
| NP | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 90 | 53.706 | 53.874 | 0 | 55.753 | 55.804 | 52.285 | 52.321
| NP | Zone | Non-coincident | 16/12/2024 | 18:30 | Summer | 90 | 53.706 | 53.874 | 0 | 55.753 | 55.804 | 52.285 | 52.321
| NW | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 99 | 53.326 | 53.336 | 0 | 57.953 | 57.964 | 53.844 | 53.855
| NW | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 99 | 57.07 | 57.118 | 0 | 62.022 | 62.12 | 57.625 | 57.69
| OAK | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 99 | 37.154 | 37.157 | 0 | 38.436 | 38.478 | 34.095 | 34.095
| OAK | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 99 | 37.329 | 37.332 | 0 | 38.617 | 38.659 | 34.256 | 34.329
| OE | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 60 | 13.173 | 13.306 | 0 | 14.093 | 14.235 | 13.112 | 13.245
| OE | Zone | Non-coincident | 2024-04-07 | 10:00 | Winter | 60 | 14.438 | 14.468 | 0 | 15.447 | 15.596 | 14.372 | 14.503
| OR | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 54 | 34.921 | 35.017 | 0 | 38.063 | 38.168 | 33.335 | 33.427
| OR | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 54 | 36.826 | 36.944 | 0 | 40.139 | 40.212 | 35.154 | 35.2
| RBD | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 31.163 | 31.177 | 0 | 35.404 | 35.42 | 33.367 | 33.382
| RBD | Zone | Non-coincident | 2025-05-01 | 18:00 | Summer | 66 | 37.828 | 37.836 | 0 | 42.976 | 42.977 | 40.503 | 40.506
| SH | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 20 | 6.658 | 6.692 | 0 | 6.867 | 6.902 | 6.352 | 6.384
| SH | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 20 | 7.161 | 7.208 | 0 | 7.387 | 7.486 | 6.832 | 6.913
| SR | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 54 | 31.555 | 31.564 | 0 | 32.991 | 33.001 | 29.495 | 29.504
| SR | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 54 | 33.398 | 33.448 | 0 | 34.918 | 34.952 | 31.218 | 31.237
| SS | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 30.024 | 30.03 | 4.797 | 34.695 | 34.702 | 30.659 | 30.665
| SS | Zone | Non-coincident | 25/06/2025 | 18:30 | Winter | 66 | 31.165 | 31.172 | 0.768 | 36.013 | 36.12 | 31.824 | 31.893
| STO | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 20.231 | 22.312 | 0.406 | 25.998 | 28.672 | 22.976 | 25.339
| STO | Zone | Non-coincident | 2025-05-01 | 18:00 | Summer | 66 | 38.65 | 40.578 | 0.431 | 49.668 | 49.725 | 43.895 | 43.956
| SV | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 36.989 | 37.293 | 0 | 45.896 | 46.273 | 41.327 | 41.666
| SV | Zone | Non-coincident | 2025-12-03 | 15:30 | Summer | 66 | 39.216 | 39.664 | 0 | 48.658 | 48.687 | 43.814 | 43.829
| SVW | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 66 | 36.724 | 37.238 | 0 | 44.433 | 45.054 | 38.784 | 39.326
| SVW | Zone | Non-coincident | 2024-04-07 | 9:30 | Winter | 66 | 49.607 | 49.77 | 0 | 60.02 | 60.704 | 52.389 | 52.889
| WD | Zone | Coincident | 16/12/2024 | 18:30 | Summer | 87 | 49.353 | 49.628 | 0 | 53.488 | 53.787 | 49.668 | 49.945
| WD | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer | 87 | 51.576 | 51.885 | 0 | 55.898 | 56.551 | 51.905 | 52.402
| RWT | Zone | Coincident | 16/12/2024 | 18:30 | Summer |  | 30.351 | 30.351 | 0 | 32.65 | 32.65 | 29.987 | 29.987
| RWT | Zone | Non-coincident | 2025-02-02 | 19:00 | Summer |  | 31.81 | 31.81 | 0 | 34.22 | 34.22 | 31.429 | 31.429

## 6.3 Sustained interruptions
| ANNUAL INFORMATION ORDER | [15 empty] | #25C6FF | Protected (SOCI)
| United Energy | [15 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [15 empty] | 12.5% Grey | Amended
| CA RIN 6.3 SUSTAINED INTERRUPTIONS TO SUPPLY | [15 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
DC05 - Service performance ¦ Interruptions to supply
Interruptions to supply
6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY
Interruptions to supply
| Identify the service target performance incentive scheme (STPIS) that applied in the reporting period | [7 empty] | STPIS V2
| Incident reference number | Start date of interruption | Start time of interruption | End date of interruption | End time of interruption | Feeder ID | Feeder service area description | Feeder classification | Reason for interruption | Detailed reason for interruption | Customers (STPIS) affected by interruption | Total customer minutes off supply | Average duration of sustained customer interruptions | Restoration stage | Major event day | Reference to supporting evidence (DRMG Exclusions only)
Units | Free text | DD/MM/YYYY | HH:MM | DD/MM/YYYY | HH:MM | Free text | Free text | Select from options listed in column AG | Select from options listed in column AH | Select from options listed in column AI | Number of customers | number | minutes | stage number | Yes/No | free text |  |  | Feeder classification | Reason for interruption | Detailed reason for interruption
| 1814768 | 2024-01-07 | 0:26 | 2024-01-07 | 1:35 | NB31 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 69.7667 | 69.7667 | 1 | No |  |  |  | CBD | Animal | Animal impact
| 1814770 | 2024-01-07 | 0:34 | 2024-01-07 | 2:45 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 130.0167 | 130.0167 | 1 | No |  |  |  | Urban | Animal | Animal nesting/burrowing
| 1814772 | 2024-01-07 | 1:11 | 2024-01-07 | 3:45 | FTN11 | FRANKSTON | Urban | Animal | Animal impact | 75.71 | 11617.6995 | 153.45 | 1 | No |  |  |  | Short rural | Animal | Animal other
| 1814780 | 2024-01-07 | 6:19 | 2024-01-07 | 8:36 | NP36 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 137.95 | 137.95 | 1 | No |  |  |  | Long rural | Asset failure | HV
| 1814798 | 2024-01-07 | 8:14 | 2024-01-07 | 11:10 | OR34 | ORMOND | Urban | Asset Failure | LV | 1 | 176 | 176 | 1 | No |  |  |  | TAS - Urban and Regional Centres | Asset failure | LV
| 1814818 | 2024-01-07 | 8:35 | 2024-01-07 | 9:45 | M25 | MENTONE | Urban | Unknown | Unknown | 4 | 281.3332 | 70.3333 | 1 | No |  |  |  | TAS - Critical Infrastructure | Asset failure | Distribution substation
| 1814894 | 2024-01-07 | 11:00 | 2024-01-07 | 17:20 | RBD21 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 7 | 2655.2169 | 379.3167 | 1 | No |  |  |  | TAS - High density commercial | Asset failure | Zone substation
| 1814921 | 2024-01-07 | 11:39 | 2024-01-07 | 14:54 | CRM23 | CARRUM | Urban | Asset Failure | LV | 27 | 5260.4991 | 194.8333 | 1 | No |  |  |  | TAS - High density rural | Asset failure | Subtransmission
| 1814932 | 2024-01-07 | 12:06 | 2024-02-07 | 2:22 | DN10 | DANDENONG | Urban | Asset Failure | LV | 11 | 9414.7163 | 855.8833 | 1 | No |  |  |  | TAS - Lower density rural | Other
| 1814982 | 2024-01-07 | 15:23 | 2024-01-07 | 16:49 | RWT35 | RINGWOOD | Urban | Asset Failure | LV | 10.23 | 882.1667 | 86.2333 | 1 | No |  |  |  |  | Overloads
| 1814983 | 2024-01-07 | 17:38 | 2024-01-07 | 21:40 | CDA23 | CLARINDA | Urban | Overloads |  | 4 | 968 | 242 | 1 | No |  |  |  |  | Planned
| 1815012 | 2024-01-07 | 18:01 | 2024-01-07 | 20:35 | LWN23 | LANGWARRIN | Urban | Overloads |  | 1 | 154 | 154 | 1 | No |  |  |  |  | Network business | Network error
| 1815029 | 2024-01-07 | 19:37 | 2024-01-07 | 21:30 | MTN21 | MORNINGTON | Urban | Asset Failure | LV | 1 | 112.55 | 112.55 | 1 | No |  |  |  |  | Network business | Switching and protection error
| 1815044 | 2024-01-07 | 21:29 | 2024-01-07 | 23:11 | CFD15 | CAULFIELD | Urban | Overloads |  | 1 | 102.1333 | 102.1333 | 1 | No |  |  |  |  | Third party | Fire
| 1815045 | 2024-01-07 | 22:13 | 2024-02-07 | 0:12 | BT12 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 119.5667 | 119.5667 | 1 | No |  |  |  |  | Third party | Dig in
| 1815055 | 2024-02-07 | 0:38 | 2024-02-07 | 1:20 | RWT23 | RINGWOOD | Urban | Animal | Animal impact | 50.25 | 2066.9483 | 41.1333 | 1 | No |  |  |  |  | Third party | Unauthorised access
| 1815059 | 2024-02-07 | 4:28 | 2024-02-07 | 9:01 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 112 | 30516.2704 | 272.4667 | 1 | No |  |  |  |  | Third party | Vehicle impact
| 1815077 | 2024-02-07 | 7:04 | 2024-02-07 | 11:03 | RBD12 | ROSEBUD | Rural Short | Overloads |  | 1 | 238.4667 | 238.4667 | 1 | No |  |  |  |  | Third party | Third party other
| 1815112 | 2024-02-07 | 8:16 | 2024-02-07 | 9:02 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 56 | 2571.3352 | 45.9167 | 1 | No |  |  |  |  | Unknown
| 1815133 | 2024-02-07 | 8:43 | 2024-02-07 | 8:55 | FSH32 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 25 | 300 | 12 | 1 | No |  |  |  |  | Vegetation | Blow in/Fall in - NSP responsibility
| 1815037 | 2024-02-07 | 11:43 | 2024-02-07 | 13:49 | MC23 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 126.6333 | 126.6333 | 1 | No |  |  |  |  | Vegetation | Grow in - NSP responsibility
| 1815334 | 2024-02-07 | 15:15 | 2024-02-07 | 16:40 | MGE34 | MULGRAVE | Urban | Asset Failure | Distribution substation | 49 | 4152.75 | 84.75 | 1 | No |  |  |  |  | Vegetation | Blow in/Fall in - Other responsible party
| 1815358 | 2024-02-07 | 17:45 | 2024-02-07 | 19:10 | SH32 | SURREY HILLS | Urban | Asset Failure | LV | 29.37 | 2492.535 | 84.8667 | 1 | No |  |  |  |  | Vegetation | Grow in - Other responsible party
| 1815361 | 2024-02-07 | 17:56 | 2024-02-07 | 19:22 | MTN34 | MORNINGTON | Urban | Overloads |  | 97 | 8290.2699 | 85.4667 | 1 | No |  |  |  |  | Weather
| 1815359 | 2024-02-07 | 18:12 | 2024-02-07 | 19:41 | NW21 | NUNAWADING | Urban | Overloads |  | 1 | 89 | 89 | 1 | No |  |  |  |  | DRMG exclusion 3.3.1
| 1815380 | 2024-02-07 | 19:15 | 2024-02-07 | 21:59 | NP16 | NOBLE PARK | Urban | Overloads |  | 89.1 | 14604.978 | 163.9167 | 1 | No |  |  |  |  | DRMG exclusion 3.3.2
| 1815369 | 2024-02-07 | 19:17 | 2024-02-07 | 20:11 | FSH12 | FRANKSTON SOUTH | Rural Short | Overloads |  | 12.87 | 694.98 | 54 | 1 | No |  |  |  |  | DRMG exclusion 3.3.3
| 1815382 | 2024-02-07 | 19:26 | 2024-02-07 | 21:07 | NB25 | NORTH BRIGHTON | Urban | Overloads |  | 3 | 304.7499 | 101.5833 | 1 | No |  |  |  |  | DRMG exclusion 3.3.4
| 1815388 | 2024-02-07 | 19:57 | 2024-02-07 | 23:35 | DN11 | DANDENONG | Urban | Asset Failure | LV | 25.74 | 5608.3161 | 217.8833 | 1 | No |  |  |  |  | DRMG exclusion 3.3.5
| 1815390 | 2024-02-07 | 21:24 | 2024-03-07 | 0:04 | DN11 | DANDENONG | Urban | Overloads |  | 29.37 | 4674.726 | 159.1667 | 1 | No |  |  |  |  | DRMG exclusion 3.3.6
| 1815404 | 2024-02-07 | 23:33 | 2024-03-07 | 0:55 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 1 | 82 | 82 | 1 | No |  |  |  |  | DRMG exclusion 3.3.7
| 1815408 | 2024-03-07 | 0:41 | 2024-03-07 | 2:21 | STO13 | SORRENTO | Urban | Asset Failure | LV | 19.14 | 1898.0506 | 99.1667 | 1 | No
| 1815422 | 2024-03-07 | 5:37 | 2024-03-07 | 6:45 | NO32 | NOTTING HILL | Urban | Asset Failure | LV | 1 | 67.95 | 67.95 | 1 | No
| 1815438 | 2024-03-07 | 7:37 | 2024-03-07 | 8:24 | EB22 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 47.8 | 47.8 | 1 | No
| 1815441 | 2024-03-07 | 7:45 | 2024-03-07 | 8:35 | CRM23 | CARRUM | Urban | Asset Failure | LV | 84 | 4200 | 50 | 1 | No
| 1815461 | 2024-03-07 | 8:11 | 2024-03-07 | 9:04 | SV34 | SPRINGVALE | Urban | Overloads |  | 45.54 | 2391.6105 | 52.5167 | 1 | No
| 1815492 | 2024-03-07 | 8:44 | 2024-03-07 | 12:41 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 237.7167 | 237.7167 | 1 | No
| 1815407 | 2024-03-07 | 8:52 | 2024-03-07 | 9:50 | WD23 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 58 | 58 | 1 | No
| 1815439 | 2024-03-07 | 9:11 | 2024-03-07 | 11:30 | EW14 | ELWOOD | Urban | Asset Failure | LV | 1 | 139 | 139 | 1 | No
| 1815545 | 2024-03-07 | 11:04 | 2024-03-07 | 14:44 | MTN23 | MORNINGTON | Urban | Asset Failure | HV | 1 | 220.7 | 220.7 | 1 | No
| 1815562 | 2024-03-07 | 11:35 | 2024-03-07 | 13:41 | EL22 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 125.5833 | 125.5833 | 1 | No
| 1815591 | 2024-03-07 | 12:45 | 2024-03-07 | 13:43 | DC3 | DONCASTER | Urban | Unknown | Unknown | 1 | 57.6 | 57.6 | 1 | No
| 1815596 | 2024-03-07 | 12:56 | 2024-03-07 | 14:00 | NW23 | NUNAWADING | Urban | Other | XXX | 1 | 63.1 | 63.1 | 1 | No
| 1815688 | 2024-03-07 | 15:19 | 2024-03-07 | 18:31 | EM11 | EAST MALVERN | Urban | Overloads |  | 1 | 191.9333 | 191.9333 | 1 | No
| 1815700 | 2024-03-07 | 16:30 | 2024-04-07 | 0:36 | DVY31 | DANDENONG VALLEY | Urban | Overloads |  | 1 | 486.0667 | 486.0667 | 1 | No
| 1815709 | 2024-03-07 | 17:19 | 2024-03-07 | 20:19 | MR13 | MOORABBIN | Urban | Overloads |  | 18.48 | 3326.4 | 180 | 1 | No
| 1815426 | 2024-03-07 | 18:12 | 2024-03-07 | 20:51 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 159.6667 | 159.6667 | 1 | No
| 1815720 | 2024-03-07 | 18:19 | 2024-03-07 | 19:25 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 66 | 66 | 1 | No
| 1815730 | 2024-03-07 | 18:26 | 2024-03-07 | 19:50 | NP16 | NOBLE PARK | Urban | Overloads |  | 89.1 | 7468.068 | 83.8167 | 1 | No
| 1815732 | 2024-03-07 | 18:33 | 2024-03-07 | 21:23 | CFD14 | CAULFIELD | Urban | Asset Failure | LV | 1 | 170.2833 | 170.2833 | 1 | No
| 1815736 | 2024-03-07 | 18:41 | 2024-03-07 | 20:05 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 26.73 | 2234.1816 | 83.5833 | 1 | No
| 1815747 | 2024-03-07 | 19:35 | 2024-03-07 | 21:16 | BH11 | BOX HILL | Urban | Overloads |  | 1 | 100.8 | 100.8 | 1 | No
| 1815759 | 2024-03-07 | 20:03 | 2024-03-07 | 21:40 | NP36 | NOBLE PARK | Urban | Overloads |  | 46.86 | 4508.7146 | 96.2167 | 1 | No
| 1815772 | 2024-03-07 | 20:43 | 2024-03-07 | 21:59 | DN11 | DANDENONG | Urban | Overloads |  | 29.37 | 2229.183 | 75.9 | 1 | No
| 1815781 | 2024-03-07 | 21:16 | 2024-03-07 | 22:14 | CDA23 | CLARINDA | Urban | Overloads |  | 50.49 | 2917.4788 | 57.7833 | 1 | No
| 1815777 | 2024-03-07 | 21:27 | 2024-04-07 | 0:21 | MC15 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 174.3833 | 174.3833 | 1 | No
| 1815784 | 2024-03-07 | 21:55 | 2024-03-07 | 23:13 | SV34 | SPRINGVALE | Urban | Overloads |  | 45.54 | 3533.904 | 77.6 | 1 | No
| 1815820 | 2024-04-07 | 7:25 | 2024-04-07 | 8:24 | DC8 | DONCASTER | Urban | Unknown | Unknown | 55.61 | 3231.8697 | 58.1167 | 1 | No
| 1815890 | 2024-04-07 | 9:15 | 2024-04-07 | 10:35 | WD23 | WEST DONCASTER | Urban | Asset Failure | LV | 32.34 | 2587.2 | 80 | 1 | No
| 1815933 | 2024-04-07 | 10:37 | 2024-04-07 | 11:49 | MC15 | MORDIALLOC | Urban | Asset Failure | LV | 15.84 | 1151.3035 | 72.6833 | 1 | No
| 1815945 | 2024-04-07 | 11:13 | 2024-04-07 | 13:40 | MR32 | MOORABBIN | Urban | Asset Failure | LV | 1 | 146.9333 | 146.9333 | 1 | No
| 1815960 | 2024-04-07 | 11:32 | 2024-04-07 | 13:10 | MR15 | MOORABBIN | Urban | Asset Failure | HV | 96.48 | 9545.0848 | 98.9333 | 1 | No
| 1815827 | 2024-04-07 | 11:41 | 2024-04-07 | 13:00 | BH31 | BOX HILL | Urban | Asset Failure | LV | 33.99 | 2685.21 | 79 | 1 | No
| 1815968 | 2024-04-07 | 11:43 | 2024-04-07 | 13:18 | NP16 | NOBLE PARK | Urban | Unknown | Unknown | 1 | 95.2 | 95.2 | 1 | No
| 1815996 | 2024-04-07 | 12:55 | 2024-04-07 | 13:13 | MGE12 | MULGRAVE | Urban | Asset Failure | HV | 53 | 931.9149 | 17.5833 | 1 | No
| 1816002 | 2024-04-07 | 13:10 | 2024-04-07 | 14:20 | BH11 | BOX HILL | Urban | Asset Failure | LV | 1 | 70.0667 | 70.0667 | 1 | No
| 1816009 | 2024-04-07 | 14:05 | 2024-04-07 | 15:40 | MR33 | MOORABBIN | Urban | Asset Failure | LV | 60 | 5700 | 95 | 1 | No
| 1816032 | 2024-04-07 | 14:50 | 2024-04-07 | 16:59 | EM5 | EAST MALVERN | Urban | Third Party | Other | 1 | 129.0167 | 129.0167 | 1 | No
| 1815974 | 2024-04-07 | 15:16 | 2024-04-07 | 17:45 | NP34 | NOBLE PARK | Urban | Overloads |  | 1 | 149 | 149 | 1 | No
| 1816040 | 2024-04-07 | 15:29 | 2024-04-07 | 16:40 | BH21 | BOX HILL | Urban | Asset Failure | LV | 1 | 70.0667 | 70.0667 | 1 | No
| 1816052 | 2024-04-07 | 17:03 | 2024-04-07 | 18:46 | RBD11 | ROSEBUD | Urban | Asset Failure | LV | 1 | 102.6667 | 102.6667 | 1 | No
| 1816054 | 2024-04-07 | 18:11 | 2024-04-07 | 19:35 | CRM13 | CARRUM | Urban | Asset Failure | LV | 11 | 924 | 84 | 1 | No
| 1816075 | 2024-04-07 | 20:40 | 2024-05-07 | 1:02 | LD7 | LYNDALE | Urban | Overloads |  | 4.95 | 1297.8073 | 262.1833 | 1 | No
| 1816074 | 2024-04-07 | 20:56 | 2024-05-07 | 0:02 | SS13 | SPRINGVALE SOUTH | Urban | Overloads |  | 2.31 | 431.4694 | 186.7833 | 1 | No
| 1816079 | 2024-04-07 | 21:36 | 2024-04-07 | 23:50 | LWN23 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 133.1667 | 133.1667 | 1 | No
| 1816082 | 2024-04-07 | 22:08 | 2024-05-07 | 3:00 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 1 | 291.05 | 291.05 | 1 | No
| 1816094 | 2024-05-07 | 7:07 | 2024-05-07 | 8:00 | EB33 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 53 | 53 | 1 | No
| 1816123 | 2024-05-07 | 8:22 | 2024-05-07 | 10:36 | KBH32 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 133.45 | 133.45 | 1 | No
| 1816140 | 2024-05-07 | 8:57 | 2024-05-07 | 11:12 | CFD14 | CAULFIELD | Urban | Asset Failure | LV | 1 | 134.2667 | 134.2667 | 1 | No
| 1816175 | 2024-05-07 | 10:48 | 2024-05-07 | 12:33 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 104.5167 | 104.5167 | 1 | No
| 1816187 | 2024-05-07 | 11:12 | 2024-05-07 | 12:55 | KBH34 | KEYSBOROUGH | Urban | Animal | Animal impact | 22 | 2266 | 103 | 1 | No
| 1816092 | 2024-05-07 | 11:43 | 2024-05-07 | 13:37 | NP33 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 114.4667 | 114.4667 | 1 | No
| 1816200 | 2024-05-07 | 12:07 | 2024-05-07 | 13:21 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 1 | 74.0333 | 74.0333 | 1 | No
| 1816084 | 2024-05-07 | 12:58 | 2024-05-07 | 15:26 | FTN13 | FRANKSTON | Urban | Asset Failure | LV | 1 | 148.8 | 148.8 | 1 | No
| 1816208 | 2024-05-07 | 13:04 | 2024-05-07 | 15:26 | SV16 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 142.4833 | 142.4833 | 1 | No
| 1816214 | 2024-05-07 | 13:31 | 2024-05-07 | 16:20 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 168.5833 | 168.5833 | 1 | No
| 1816093 | 2024-05-07 | 15:45 | 2024-05-07 | 19:05 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 200 | 200 | 1 | No
| 1816231 | 2024-05-07 | 16:16 | 2024-05-07 | 17:12 | KBH34 | KEYSBOROUGH | Urban | Asset Failure | LV | 16 | 884 | 55.25 | 1 | No
| 1816245 | 2024-05-07 | 17:07 | 2024-05-07 | 19:30 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 143.3667 | 143.3667 | 1 | No
| 1816272 | 2024-05-07 | 18:13 | 2024-05-07 | 19:25 | FTN24 | FRANKSTON | Urban | Asset Failure | HV | 69.63 | 4962.3003 | 71.2667 | 1 | No
| 1816282 | 2024-05-07 | 18:29 | 2024-05-07 | 20:45 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 135.3333 | 135.3333 | 1 | No
| 1816285 | 2024-05-07 | 19:17 | 2024-05-07 | 21:46 | EM11 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 149.4 | 149.4 | 1 | No
| 1816262 | 2024-05-07 | 19:23 | 2024-05-07 | 21:01 | M12 | MENTONE | Urban | Asset Failure | LV | 1 | 98.0333 | 98.0333 | 1 | No
| 1816313 | 2024-06-07 | 7:54 | 2024-06-07 | 10:03 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 2 | 258 | 129 | 1 | No
| 1816312 | 2024-06-07 | 8:27 | 2024-06-07 | 11:03 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 156.9333 | 156.9333 | 1 | No
| 1816333 | 2024-06-07 | 10:11 | 2024-06-07 | 12:13 | GW3 | GLEN WAVERLEY | Urban | Asset Failure | LV | 34.32 | 4196.7629 | 122.2833 | 1 | No
| 1816344 | 2024-06-07 | 11:39 | 2024-06-07 | 14:14 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 155.1333 | 155.1333 | 1 | No
| 1816342 | 2024-06-07 | 11:44 | 2024-06-07 | 17:21 | GW6 | GLEN WAVERLEY | Urban | Asset Failure | LV | 31 | 10468.1823 | 337.6833 | 1 | No
| 1816410 | 2024-06-07 | 15:40 | 2024-06-07 | 17:58 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 137.8833 | 137.8833 | 1 | No
| 1816419 | 2024-06-07 | 17:54 | 2024-06-07 | 19:14 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 80.4333 | 80.4333 | 1 | No
| 1816422 | 2024-06-07 | 18:29 | 2024-06-07 | 20:53 | OAK33 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 144.1667 | 144.1667 | 1 | No
| 1816423 | 2024-06-07 | 18:53 | 2024-06-07 | 20:13 | NB21 | NORTH BRIGHTON | Urban | Asset Failure | LV | 31.35 | 2488.6665 | 79.3833 | 1 | No
| 1816439 | 2024-06-07 | 23:21 | 2024-07-07 | 0:10 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 49.05 | 49.05 | 1 | No
| 1816449 | 2024-07-07 | 1:13 | 2024-07-07 | 3:05 | FSH32 | FRANKSTON SOUTH | Rural Short | Overloads |  | 1.98 | 221.76 | 112 | 1 | No
| 1816461 | 2024-07-07 | 6:37 | 2024-07-07 | 13:45 | MC12 | MORDIALLOC | Urban | Third Party | Vehicle Impact | 2 | 854.1666 | 427.0833 | 1 | No
| 1816462 | 2024-07-07 | 7:01 | 2024-07-07 | 7:35 | CDA23 | CLARINDA | Urban | Overloads |  | 1 | 33.8167 | 33.8167 | 1 | No
| 1816446 | 2024-07-07 | 8:28 | 2024-07-07 | 11:11 | HT11 | HEATHERTON | Urban | Overloads |  | 1 | 163 | 163 | 1 | No
| 1816478 | 2024-07-07 | 8:43 | 2024-07-07 | 20:52 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 728.9667 | 728.9667 | 1 | No
| 1816463 | 2024-07-07 | 9:40 | 2024-07-07 | 11:58 | STO23 | SORRENTO | Urban | Overloads |  | 1.6 | 220.88 | 138.05 | 1 | No
| 1816489 | 2024-07-07 | 9:53 | 2024-07-07 | 14:55 | EL32 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 301.9667 | 301.9667 | 1 | No
| 1816488 | 2024-07-07 | 10:01 | 2024-07-07 | 13:27 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 206.85 | 206.85 | 1 | No
| 1816504 | 2024-07-07 | 11:22 | 2024-07-07 | 12:43 | CDA23 | CLARINDA | Urban | Overloads |  | 1 | 80.55 | 80.55 | 1 | No
| 1816510 | 2024-07-07 | 12:41 | 2024-07-07 | 13:37 | NW33 | NUNAWADING | Urban | Asset Failure | LV | 158 | 8745.3 | 55.35 | 1 | No
| 1816546 | 2024-07-07 | 17:53 | 2024-07-07 | 19:48 | M13 | MENTONE | Urban | Asset Failure | LV | 1 | 115.0167 | 115.0167 | 1 | No
| 1816548 | 2024-07-07 | 18:00 | 2024-07-07 | 20:48 | LWN21 | LANGWARRIN | Rural Short | Overloads |  | 2.31 | 387.2329 | 167.6333 | 1 | No
| 1816549 | 2024-07-07 | 18:06 | 2024-07-07 | 19:10 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 64.4333 | 64.4333 | 1 | No
| 1816541 | 2024-07-07 | 18:45 | 2024-07-07 | 21:43 | LWN33 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 178.9 | 178.9 | 1 | No
| 1816560 | 2024-07-07 | 19:00 | 2024-07-07 | 20:00 | WD36 | WEST DONCASTER | Urban | Animal | Animal impact | 24.75 | 1471.3875 | 59.45 | 1 | No
| 1816558 | 2024-07-07 | 19:17 | 2024-07-07 | 23:41 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 264.4 | 264.4 | 1 | No
| 1816563 | 2024-07-07 | 20:02 | 2024-07-07 | 21:48 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 1 | 106.5667 | 106.5667 | 1 | No
| 1816565 | 2024-07-07 | 21:33 | 2024-07-07 | 23:00 | FSH11 | FRANKSTON SOUTH | Urban | Third Party | Other | 5.94 | 516.0868 | 86.8833 | 1 | No
| 1816571 | 2024-07-07 | 22:54 | 2024-08-07 | 1:45 | BW34 | BURWOOD | Urban | Asset Failure | LV | 1 | 170.5333 | 170.5333 | 1 | No
| 1816581 | 2024-08-07 | 5:33 | 2024-08-07 | 8:33 | DMA15 | DROMANA | Rural Short | Unknown | Unknown | 1 | 180.55 | 180.55 | 1 | No
| 1816574 | 2024-08-07 | 7:48 | 2024-08-07 | 10:00 | SS13 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 132 | 132 | 1 | No
| 1816619 | 2024-08-07 | 8:23 | 2024-08-07 | 11:22 | MTN32 | MORNINGTON | Rural Short | Overloads |  | 1 | 179.5167 | 179.5167 | 1 | No
| 1816596 | 2024-08-07 | 8:54 | 2024-08-07 | 11:00 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 126.8333 | 126.8333 | 1 | No
| 1816665 | 2024-08-07 | 9:41 | 2024-08-07 | 11:40 | RBD22 | ROSEBUD | Urban | Asset Failure | LV | 1 | 118.3167 | 118.3167 | 1 | No
| 1816775 | 2024-08-07 | 12:34 | 2024-08-07 | 14:10 | STO23 | SORRENTO | Urban | Asset Failure | LV | 24.79 | 2357.115 | 95.0833 | 1 | No
| 1816866 | 2024-08-07 | 17:49 | 2024-08-07 | 21:25 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 1 | 216.5333 | 216.5333 | 1 | No
| 1816663 | 2024-08-07 | 18:04 | 2024-08-07 | 19:53 | EM9 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 109.1833 | 109.1833 | 1 | No
| 1816870 | 2024-08-07 | 18:31 | 2024-08-07 | 20:07 | FSH32 | FRANKSTON SOUTH | Rural Short | Overloads |  | 1.98 | 190.8389 | 96.3833 | 1 | No
| 1816878 | 2024-08-07 | 18:56 | 2024-08-07 | 21:13 | KBH31 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 137.75 | 137.75 | 1 | No
| 1816884 | 2024-08-07 | 20:13 | 2024-08-07 | 20:52 | GW11 | GLEN WAVERLEY | Urban | Overloads |  | 1 | 39.45 | 39.45 | 1 | No
| 1816881 | 2024-08-07 | 21:14 | 2024-08-07 | 21:57 | DC8 | DONCASTER | Urban | Overloads |  | 1 | 43.6667 | 43.6667 | 1 | No
| 1816898 | 2024-08-07 | 23:09 | 2024-09-07 | 3:23 | SS13 | SPRINGVALE SOUTH | Urban | Asset Failure | HV | 86 | 21811.0362 | 253.6167 | 1 | No
| 1816909 | 2024-09-07 | 5:30 | 2024-09-07 | 7:54 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 144.45 | 144.45 | 1 | No
| 1816948 | 2024-09-07 | 8:28 | 2024-09-07 | 9:36 | CFD25 | CAULFIELD | Urban | Third Party | Other | 1 | 67.6333 | 67.6333 | 1 | No
| 1816957 | 2024-09-07 | 8:48 | 2024-09-07 | 9:46 | FTN13 | FRANKSTON | Urban | Asset Failure | LV | 1 | 57.3333 | 57.3333 | 1 | No
| 1816966 | 2024-09-07 | 9:11 | 2024-09-07 | 12:00 | NB24 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 168.2667 | 168.2667 | 1 | No
| 1816983 | 2024-09-07 | 9:36 | 2024-09-07 | 10:52 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 75.7833 | 75.7833 | 1 | No
| 1817002 | 2024-09-07 | 9:55 | 2024-09-07 | 13:21 | KBH32 | KEYSBOROUGH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 205.2667 | 205.2667 | 1 | No
| 1817007 | 2024-09-07 | 10:06 | 2024-09-07 | 12:32 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 13.53 | 1976.507 | 146.0833 | 1 | No
| 1817026 | 2024-09-07 | 11:09 | 2024-09-07 | 13:10 | HGS23 | HASTINGS | Rural Short | Other | XXX | 1 | 120.4333 | 120.4333 | 1 | No
| 1817083 | 2024-09-07 | 14:33 | 2024-09-07 | 17:09 | EB32 | EAST BURWOOD | Urban | Asset Failure | HV | 39.27 | 6126.7758 | 156.0167 | 1 | No
| 1817092 | 2024-09-07 | 14:39 | 2024-09-07 | 17:30 | MGE24 | MULGRAVE | Urban | Asset Failure | HV | 3 | 512.7501 | 170.9167 | 1 | No
| 1817103 | 2024-09-07 | 15:15 | 2024-09-07 | 18:36 | HGS33 | HASTINGS | Rural Short | Third Party | Other | 1 | 200.45 | 200.45 | 1 | No
| 1817104 | 2024-09-07 | 15:16 | 2024-09-07 | 18:10 | HGS33 | HASTINGS | Rural Short | Third Party | Other | 4 | 695.8668 | 173.9667 | 1 | No
| 1817105 | 2024-09-07 | 15:17 | 2024-09-07 | 17:40 | HGS33 | HASTINGS | Rural Short | Third Party | Other | 3 | 428.9499 | 142.9833 | 1 | No
| 1817129 | 2024-09-07 | 17:29 | 2024-09-07 | 18:56 | CFD14 | CAULFIELD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 12.21 | 1053.3164 | 86.2667 | 1 | No
| 1817141 | 2024-09-07 | 19:48 | 2024-09-07 | 20:08 | FTN21 | FRANKSTON | Urban | Third Party |  | 1 | 19.6833 | 19.6833 | 1 | No
| 1817168 | 2024-10-07 | 1:52 | 2024-10-07 | 3:36 | WD36 | WEST DONCASTER | Urban | Asset Failure | LV | 1.5 | 156.6 | 104.4 | 1 | No
| 1817173 | 2024-10-07 | 5:41 | 2024-10-07 | 7:33 | STO13 | SORRENTO | Urban | Animal | Other | 72.36 | 8056.0776 | 111.3333 | 1 | No
| 1817181 | 2024-10-07 | 6:30 | 2024-10-07 | 8:19 | CDA23 | CLARINDA | Urban | Unknown | Unknown | 1 | 109.5667 | 109.5667 | 1 | No
| 1817245 | 2024-10-07 | 6:35 | 2024-10-07 | 11:10 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 275.05 | 275.05 | 1 | No
| 1817283 | 2024-10-07 | 7:05 | 2024-10-07 | 10:50 | NP34 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 225.6667 | 225.6667 | 1 | No
| 1817215 | 2024-10-07 | 8:39 | 2024-10-07 | 10:51 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 132.15 | 132.15 | 1 | No
| 1817093 | 2024-10-07 | 9:05 | 2024-10-07 | 10:25 | NW22 | NUNAWADING | Urban | Unknown | Unknown | 1 | 80.1667 | 80.1667 | 1 | No
| 1817300 | 2024-10-07 | 10:26 | 2024-10-07 | 12:27 | FTN22 | FRANKSTON | Urban | Third Party | Other | 1 | 120.75 | 120.75 | 1 | No
| 1817316 | 2024-10-07 | 11:23 | 2024-10-07 | 14:05 | BC22 | BALACLAVA | Urban | Asset Failure | LV | 1 | 161.75 | 161.75 | 1 | No
| 1817353 | 2024-10-07 | 12:32 | 2024-10-07 | 13:45 | CRM33 | CARRUM | Urban | Overloads |  | 7.92 | 570.7683 | 72.0667 | 1 | No
| 1817402 | 2024-10-07 | 14:18 | 2024-10-07 | 14:41 | DMA14 | DROMANA | Urban | Asset Failure | LV | 2 | 47.0666 | 23.5333 | 1 | No
| 1817400 | 2024-10-07 | 16:31 | 2024-10-07 | 18:05 | CRM33 | CARRUM | Urban | Asset Failure | LV | 24 | 2256 | 94 | 1 | No
| 1817428 | 2024-10-07 | 16:48 | 2024-10-07 | 18:10 | DC10 | DONCASTER | Urban | Asset Failure | LV | 1 | 82.5 | 82.5 | 1 | No
| 1817310 | 2024-10-07 | 17:41 | 2024-10-07 | 19:35 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 114.8167 | 114.8167 | 1 | No
| 1817448 | 2024-10-07 | 18:56 | 2024-11-07 | 0:45 | CRM33 | CARRUM | Urban | Asset Failure | LV | 2 | 696.0666 | 348.0333 | 1 | No
| 1817463 | 2024-10-07 | 20:01 | 2024-10-07 | 21:12 | NW11 | NUNAWADING | Urban | Asset Failure | HV | 37.95 | 2712.7912 | 71.4833 | 1 | No
| 1817472 | 2024-10-07 | 21:13 | 2024-11-07 | 1:45 | MTN24 | MORNINGTON | Rural Short | Asset Failure | LV | 74 | 20128 | 272 | 1 | No
| 1817537 | 2024-11-07 | 8:42 | 2024-11-07 | 8:59 | BU12 | BULLEEN | Urban | Other | XXX | 1 | 16.4667 | 16.4667 | 1 | No
| 1817904 | 2024-11-07 | 9:22 | 2024-12-07 | 13:22 | DMA14 | DROMANA | Urban | Third Party | Other | 41 | 68880 | 1680 | 1 | No
| 1817678 | 2024-11-07 | 13:37 | 2024-11-07 | 17:43 | MTN24 | MORNINGTON | Rural Short | Third Party | Other | 1 | 246.3 | 246.3 | 1 | No
| 1817704 | 2024-11-07 | 14:28 | 2024-11-07 | 15:35 | FSH33 | FRANKSTON SOUTH | Urban | Third Party | Other | 1 | 66.7833 | 66.7833 | 1 | No
| 1817707 | 2024-11-07 | 14:33 | 2024-11-07 | 17:38 | CRM34 | CARRUM | Urban | Asset Failure | LV | 1 | 184.75 | 184.75 | 1 | No
| 1817717 | 2024-11-07 | 14:48 | 2024-11-07 | 18:10 | DC8 | DONCASTER | Urban | Asset Failure | LV | 1 | 201.5167 | 201.5167 | 1 | No
| 1817721 | 2024-11-07 | 14:59 | 2024-11-07 | 16:40 | DVY32 | DANDENONG VALLEY | Urban | Asset Failure | LV | 1 | 100.25 | 100.25 | 1 | No
| 1817755 | 2024-11-07 | 17:38 | 2024-11-07 | 21:28 | LWN32 | LANGWARRIN | Rural Short | Network Business | Network Error | 1 | 230.6667 | 230.6667 | 1 | No
| 1817727 | 2024-11-07 | 18:14 | 2024-11-07 | 22:14 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 240.45 | 240.45 | 1 | No
| 1817767 | 2024-11-07 | 18:35 | 2024-11-07 | 22:15 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 76 | 16736.4692 | 220.2167 | 1 | No
| 1817768 | 2024-11-07 | 18:56 | 2024-11-07 | 21:22 | EL24 | ELSTERNWICK | Urban | Overloads |  | 1 | 145.7333 | 145.7333 | 1 | No
| 1817773 | 2024-11-07 | 19:08 | 2024-11-07 | 21:40 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 51 | 7753.6983 | 152.0333 | 1 | No
| 1817788 | 2024-12-07 | 8:41 | 2024-12-07 | 10:34 | OAK24 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 113.5333 | 113.5333 | 1 | No
| 1817870 | 2024-12-07 | 9:25 | 2024-12-07 | 11:45 | OR23 | ORMOND | Urban | Asset Failure | LV | 1 | 139.7833 | 139.7833 | 1 | No
| 1817885 | 2024-12-07 | 9:52 | 2024-12-07 | 13:41 | HT1 | HEATHERTON | Urban | Network Business | Network Error | 55 | 12591.3315 | 228.9333 | 1 | No
| 1818008 | 2024-12-07 | 13:58 | 2024-12-07 | 16:46 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 168.8667 | 168.8667 | 1 | No
| 1818071 | 2024-12-07 | 15:04 | 2024-12-07 | 15:19 | BU14 | BULLEEN | Urban | Unknown | Unknown | 1 | 14.3333 | 14.3333 | 1 | No
| 1818085 | 2024-12-07 | 16:23 | 2024-12-07 | 20:14 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 231.6167 | 231.6167 | 1 | No
| 1818101 | 2024-12-07 | 18:37 | 2024-12-07 | 20:23 | BH11 | BOX HILL | Urban | Other | XXX | 1 | 106.1167 | 106.1167 | 1 | No
| 1818108 | 2024-12-07 | 20:19 | 2024-12-07 | 23:18 | RBD24 | ROSEBUD | Urban | Overloads |  | 197 | 35371.35 | 179.55 | 1 | No
| 1818119 | 2024-12-07 | 23:20 | 13/07/2024 | 0:35 | HGS23 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 75.1167 | 75.1167 | 1 | No
| 1818138 | 13/07/2024 | 8:25 | 13/07/2024 | 13:22 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 297.3333 | 297.3333 | 1 | No
| 1818164 | 13/07/2024 | 10:37 | 13/07/2024 | 11:50 | BH11 | BOX HILL | Urban | Asset Failure | LV | 26.13 | 1896.6016 | 72.5833 | 1 | No
| 1818170 | 13/07/2024 | 11:11 | 13/07/2024 | 14:00 | SR36 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 168.2167 | 168.2167 | 1 | No
| 1818140 | 13/07/2024 | 11:39 | 13/07/2024 | 15:03 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 204 | 204 | 1 | No
| 1818188 | 13/07/2024 | 13:36 | 13/07/2024 | 15:45 | OR24 | ORMOND | Urban | Asset Failure | LV | 22.77 | 2926.7032 | 128.5333 | 1 | No
| 1818150 | 13/07/2024 | 13:38 | 13/07/2024 | 16:49 | LD6 | LYNDALE | Urban | Asset Failure | LV | 1 | 191 | 191 | 1 | No
| 1818190 | 13/07/2024 | 13:42 | 13/07/2024 | 17:57 | BT22 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 254.9333 | 254.9333 | 1 | No
| 1818213 | 13/07/2024 | 19:28 | 13/07/2024 | 21:01 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 30.69 | 2850.5885 | 92.8833 | 1 | No
| 1818232 | 13/07/2024 | 21:31 | 13/07/2024 | 22:24 | NW21 | NUNAWADING | Urban | Asset Failure | LV | 1 | 53 | 53 | 1 | No
| 1818236 | 13/07/2024 | 22:24 | 14/07/2024 | 11:15 | BR9 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 770.15 | 770.15 | 1 | No
| 1818237 | 13/07/2024 | 23:22 | 14/07/2024 | 1:08 | CRM33 | CARRUM | Urban | Asset Failure | LV | 12.21 | 1295.2771 | 106.0833 | 1 | No
| 1818247 | 14/07/2024 | 2:17 | 14/07/2024 | 13:00 | MR22 | MOORABBIN | Urban | Asset Failure | LV | 1 | 643 | 643 | 1 | No
| 1818288 | 14/07/2024 | 10:44 | 14/07/2024 | 14:15 | NB36 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 211 | 211 | 1 | No
| 1818290 | 14/07/2024 | 11:24 | 14/07/2024 | 16:00 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 2 | 552 | 276 | 1 | No
| 1818296 | 14/07/2024 | 12:23 | 14/07/2024 | 13:20 | GW3 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 57.6 | 57.6 | 1 | No
| 1818248 | 14/07/2024 | 13:07 | 14/07/2024 | 14:02 | OAK24 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 55.55 | 55.55 | 1 | No
| 1818307 | 14/07/2024 | 14:04 | 14/07/2024 | 18:03 | HT11 | HEATHERTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 238.5333 | 238.5333 | 1 | No
| 1818324 | 14/07/2024 | 21:34 | 14/07/2024 | 22:59 | FSH32 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 3.84 | 326.976 | 85.15 | 1 | No
| 1818322 | 14/07/2024 | 22:17 | 15/07/2024 | 0:11 | BR15 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 114 | 114 | 1 | No
| 1818338 | 15/07/2024 | 6:04 | 15/07/2024 | 10:05 | OR34 | ORMOND | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 240.2 | 240.2 | 1 | No
| 1818348 | 15/07/2024 | 7:32 | 15/07/2024 | 8:26 | CFD12 | CAULFIELD | Urban | Asset Failure | LV | 1 | 54.4 | 54.4 | 1 | No
| 1818355 | 15/07/2024 | 7:45 | 15/07/2024 | 8:33 | NW33 | NUNAWADING | Urban | Asset Failure | LV | 2 | 94.6 | 47.3 | 1 | No
| 1818357 | 15/07/2024 | 7:48 | 15/07/2024 | 11:50 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 1 | 241.6833 | 241.6833 | 1 | No
| 1818362 | 15/07/2024 | 8:01 | 15/07/2024 | 12:42 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 281 | 281 | 1 | No
| 1818369 | 15/07/2024 | 8:15 | 15/07/2024 | 14:53 | KBH33 | KEYSBOROUGH | Urban | Third Party | Other | 1 | 397.45 | 397.45 | 1 | No
| 1818377 | 15/07/2024 | 9:02 | 15/07/2024 | 10:49 | OR23 | ORMOND | Urban | Asset Failure | LV | 1 | 107.4 | 107.4 | 1 | No
| 1818467 | 15/07/2024 | 11:01 | 15/07/2024 | 11:08 | MTN22 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 295 | 2168.25 | 7.35 | 1 | No
| 1818441 | 15/07/2024 | 11:43 | 15/07/2024 | 14:12 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 149.8833 | 149.8833 | 1 | No
| 1818331 | 15/07/2024 | 11:52 | 15/07/2024 | 14:00 | CDA23 | CLARINDA | Urban | Overloads |  | 1 | 128 | 128 | 1 | No
| 1818498 | 15/07/2024 | 11:57 | 15/07/2024 | 12:22 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 108 | 2750.4036 | 25.4667 | 1 | No
| 1818498 | 15/07/2024 | 11:57 | 15/07/2024 | 17:28 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 106 | 35070.1 | 330.85 | 2 | No
| 1818499 | 15/07/2024 | 12:08 | 15/07/2024 | 15:49 | DMA23 | DROMANA | Rural Short | Unknown | Unknown | 1 | 221.8 | 221.8 | 1 | No
| 1818509 | 15/07/2024 | 12:26 | 15/07/2024 | 17:16 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 67.65 | 19598.205 | 289.7 | 1 | No
| 1818510 | 15/07/2024 | 12:39 | 16/07/2024 | 11:58 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 1398.7667 | 1398.7667 | 1 | No
| 1818538 | 15/07/2024 | 14:41 | 15/07/2024 | 17:36 | LD7 | LYNDALE | Urban | Third Party | Other | 77 | 13480.1359 | 175.0667 | 1 | No
| 1818538 | 15/07/2024 | 14:41 | 15/07/2024 | 22:15 | LD7 | LYNDALE | Urban | Third Party | Other | 15 | 6816.2505 | 454.4167 | 2 | No
| 1818550 | 15/07/2024 | 15:16 | 15/07/2024 | 18:09 | DMA21 | DROMANA | Urban | Asset Failure | LV | 1 | 173.0833 | 173.0833 | 1 | No
| 1818559 | 15/07/2024 | 15:56 | 15/07/2024 | 21:53 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 29.04 | 10385.671 | 357.6333 | 1 | No
| 1818566 | 15/07/2024 | 16:22 | 16/07/2024 | 2:22 | FSH32 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 599.5833 | 599.5833 | 1 | No
| 1818584 | 15/07/2024 | 17:35 | 15/07/2024 | 20:53 | NB26 | NORTH BRIGHTON | Urban | Asset Failure | Distribution substation | 65.01 | 12848.1408 | 197.6333 | 1 | No
| 1818583 | 15/07/2024 | 17:36 | 15/07/2024 | 19:47 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 130.8667 | 130.8667 | 1 | No
| 1818588 | 15/07/2024 | 17:46 | 15/07/2024 | 21:07 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 200.1833 | 200.1833 | 1 | No
| 1818590 | 15/07/2024 | 17:54 | 15/07/2024 | 22:57 | EM10 | EAST MALVERN | Urban | Third Party | Other | 1 | 302.8667 | 302.8667 | 1 | No
| 1818607 | 15/07/2024 | 18:28 | 15/07/2024 | 20:00 | RWT24 | RINGWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 68 | 6197.0644 | 91.1333 | 1 | No
| 1818619 | 15/07/2024 | 19:15 | 15/07/2024 | 23:17 | LWN23 | LANGWARRIN | Urban | Weather |  | 8.04 | 1947.0203 | 242.1667 | 1 | No
| 1818619 | 15/07/2024 | 19:15 | 15/07/2024 | 23:18 | LWN23 | LANGWARRIN | Urban | Weather |  | 44.22 | 10752.093 | 243.15 | 2 | No
| 1818626 | 15/07/2024 | 19:20 | 16/07/2024 | 1:15 | SR25 | SANDRINGHAM | Urban | Third Party | Vehicle Impact | 68 | 24113.9356 | 354.6167 | 1 | No
| 1818640 | 15/07/2024 | 19:30 | 15/07/2024 | 20:28 | LD4 | LYNDALE | Urban | Asset Failure | LV | 86 | 4988 | 58 | 1 | No
| 1818636 | 15/07/2024 | 20:07 | 16/07/2024 | 8:20 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 732.6 | 732.6 | 1 | No
| 1818638 | 15/07/2024 | 20:19 | 16/07/2024 | 0:08 | MTN23 | MORNINGTON | Urban | Asset Failure | LV | 16.17 | 3702.93 | 229 | 1 | No
| 1818632 | 15/07/2024 | 20:36 | 16/07/2024 | 0:24 | NP36 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 228.0167 | 228.0167 | 1 | No
| 1818648 | 15/07/2024 | 20:59 | 16/07/2024 | 0:02 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 182.2167 | 182.2167 | 1 | No
| 1818652 | 15/07/2024 | 21:15 | 15/07/2024 | 22:08 | MGE13 | MULGRAVE | Urban | Asset Failure | LV | 9.24 | 484.176 | 52.4 | 1 | No
| 1818677 | 15/07/2024 | 23:54 | 16/07/2024 | 2:54 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 23.45 | 4225.69 | 180.2 | 1 | No
| 1818690 | 16/07/2024 | 0:43 | 16/07/2024 | 1:09 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 663 | 17713.1721 | 26.7167 | 1 | No
| 1818690 | 16/07/2024 | 0:43 | 16/07/2024 | 2:04 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 511 | 41697.6 | 81.6 | 2 | No
| 1818690 | 16/07/2024 | 0:43 | 16/07/2024 | 12:47 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 86 | 62269.7362 | 724.0667 | 3 | No
| 1818690 | 16/07/2024 | 0:43 | 16/07/2024 | 13:05 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 64 | 47515.7312 | 742.4333 | 4 | No
| 1818690 | 16/07/2024 | 0:43 | 16/07/2024 | 13:05 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 61 | 45293.5187 | 742.5167 | 5 | No
| 1818690 | 16/07/2024 | 0:43 | 16/07/2024 | 13:05 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 24 | 17823.6 | 742.65 | 6 | No
| 1818690 | 16/07/2024 | 0:43 | 16/07/2024 | 17:50 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 20 | 20551.666 | 1027.5833 | 7 | No
| 1818707 | 16/07/2024 | 2:43 | 16/07/2024 | 11:00 | FSH13 | FRANKSTON SOUTH | Urban | Weather |  | 1 | 496.8333 | 496.8333 | 1 | No
| 1818708 | 16/07/2024 | 2:47 | 16/07/2024 | 12:21 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 573.5167 | 573.5167 | 1 | No
| 1818710 | 16/07/2024 | 3:59 | 16/07/2024 | 4:33 | LWN34 | LANGWARRIN | Urban | Vegetation | Grow-in - Other responsible party | 1 | 33.65 | 33.65 | 1 | No
| 1818904 | 16/07/2024 | 4:47 | 16/07/2024 | 16:58 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 45 | 32875.5015 | 730.5667 | 1 | No
| 1818718 | 16/07/2024 | 4:49 | 16/07/2024 | 11:00 | HT4 | HEATHERTON | Urban | Third Party | Other | 1 | 370.2333 | 370.2333 | 1 | No
| 1818859 | 16/07/2024 | 5:45 | 16/07/2024 | 10:40 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | Distribution substation | 4.69 | 1379.5635 | 294.15 | 1 | No
| 1818770 | 16/07/2024 | 8:03 | 16/07/2024 | 11:39 | MTN24 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 215.7833 | 215.7833 | 1 | No
| 1818771 | 16/07/2024 | 8:04 | 16/07/2024 | 11:03 | STO21 | SORRENTO | Rural Short | Overloads |  | 1 | 178.5833 | 178.5833 | 1 | No
| 1818799 | 16/07/2024 | 8:51 | 16/07/2024 | 20:15 | SS14 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 683.8333 | 683.8333 | 1 | No
| 1818825 | 16/07/2024 | 9:20 | 16/07/2024 | 18:21 | MC12 | MORDIALLOC | Urban | Weather |  | 1 | 540.8833 | 540.8833 | 1 | No
| 1818866 | 16/07/2024 | 10:48 | 16/07/2024 | 11:50 | OE13 | OAKLEIGH EAST | Urban | Third Party | Other | 1 | 62 | 62 | 1 | No
| 1818877 | 16/07/2024 | 11:33 | 16/07/2024 | 12:30 | GW8 | GLEN WAVERLEY | Urban | Overloads |  | 1 | 56.3667 | 56.3667 | 1 | No
| 1818923 | 16/07/2024 | 13:20 | 16/07/2024 | 14:26 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 52 | 3423.3316 | 65.8333 | 1 | No
| 1818928 | 16/07/2024 | 13:40 | 16/07/2024 | 16:05 | OAK33 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 145.0167 | 145.0167 | 1 | No
| 1818929 | 16/07/2024 | 13:40 | 16/07/2024 | 15:15 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 94.7333 | 94.7333 | 1 | No
| 1818931 | 16/07/2024 | 13:58 | 16/07/2024 | 23:17 | EM8 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 558.55 | 558.55 | 1 | No
| 1818939 | 16/07/2024 | 14:52 | 17/07/2024 | 0:21 | DN13 | DANDENONG | Urban | Asset Failure | LV | 1 | 569.6167 | 569.6167 | 1 | No
| 1818945 | 16/07/2024 | 15:27 | 16/07/2024 | 17:22 | OAK26 | OAKLEIGH | Urban | Overloads |  | 1 | 114.3833 | 114.3833 | 1 | No
| 1818948 | 16/07/2024 | 15:56 | 16/07/2024 | 20:50 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 2.97 | 872.4375 | 293.75 | 1 | No
| 1818951 | 16/07/2024 | 16:32 | 17/07/2024 | 4:28 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 716.45 | 716.45 | 1 | No
| 1818954 | 16/07/2024 | 16:53 | 16/07/2024 | 23:21 | RBD11 | ROSEBUD | Urban | Asset Failure | LV | 1 | 388.3167 | 388.3167 | 1 | No
| 1818959 | 16/07/2024 | 17:24 | 17/07/2024 | 3:54 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 17 | 10713.1161 | 630.1833 | 1 | No
| 1818961 | 16/07/2024 | 17:41 | 16/07/2024 | 19:01 | WD26 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 79.6833 | 79.6833 | 1 | No
| 1818971 | 16/07/2024 | 18:56 | 17/07/2024 | 2:15 | SS12 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 438.65 | 438.65 | 1 | No
| 1818981 | 16/07/2024 | 19:46 | 16/07/2024 | 21:41 | BH31 | BOX HILL | Urban | Asset Failure | LV | 33.66 | 3838.3609 | 114.0333 | 1 | No
| 1818980 | 16/07/2024 | 19:48 | 17/07/2024 | 0:15 | FTN14 | FRANKSTON | Urban | Third Party | Vehicle Impact | 43 | 11446.6 | 266.2 | 1 | No
| 1819001 | 17/07/2024 | 1:54 | 17/07/2024 | 3:54 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | HV | 28 | 3360 | 120 | 1 | No
| 1819003 | 17/07/2024 | 5:55 | 17/07/2024 | 9:35 | SS23 | SPRINGVALE SOUTH | Urban | Unknown | Unknown | 4 | 882.4668 | 220.6167 | 1 | No
| 1819035 | 17/07/2024 | 8:37 | 17/07/2024 | 11:23 | OR34 | ORMOND | Urban | Unknown | Unknown | 1 | 165.75 | 165.75 | 1 | No
| 1819092 | 17/07/2024 | 11:42 | 17/07/2024 | 13:50 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 4.29 | 548.0475 | 127.75 | 1 | No
| 1819129 | 17/07/2024 | 13:22 | 17/07/2024 | 14:51 | EM10 | EAST MALVERN | Urban | Asset Failure | LV | 48 | 4260.8016 | 88.7667 | 1 | No
| 1819138 | 17/07/2024 | 14:17 | 17/07/2024 | 18:52 | MR32 | MOORABBIN | Urban | Asset Failure | LV | 1 | 275.4333 | 275.4333 | 1 | No
| 1819146 | 17/07/2024 | 14:54 | 17/07/2024 | 21:40 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 405.9833 | 405.9833 | 1 | No
| 1819164 | 17/07/2024 | 15:56 | 17/07/2024 | 18:42 | STO13 | SORRENTO | Urban | Weather |  | 1 | 165.4333 | 165.4333 | 1 | No
| 1819169 | 17/07/2024 | 16:22 | 17/07/2024 | 20:20 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 237.8333 | 237.8333 | 1 | No
| 1819179 | 17/07/2024 | 18:22 | 17/07/2024 | 21:10 | GW5 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 167.6333 | 167.6333 | 1 | No
| 1819173 | 17/07/2024 | 18:27 | 17/07/2024 | 20:35 | CRM15 | CARRUM | Urban | Asset Failure | LV | 1 | 128 | 128 | 1 | No
| 1819182 | 17/07/2024 | 18:52 | 17/07/2024 | 21:33 | WD34 | WEST DONCASTER | Urban | Third Party | Vehicle Impact | 51 | 8201.6517 | 160.8167 | 1 | No
| 1819188 | 17/07/2024 | 19:35 | 17/07/2024 | 20:30 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 54.9167 | 54.9167 | 1 | No
| 1819203 | 17/07/2024 | 21:57 | 17/07/2024 | 22:10 | NW21 | NUNAWADING | Urban | Animal | Animal impact | 1.32 | 16.104 | 12.2 | 1 | No
| 1819209 | 17/07/2024 | 23:14 | 18/07/2024 | 2:06 | FSH12 | FRANKSTON SOUTH | Rural Short | Other | XXX | 1 | 171.3167 | 171.3167 | 1 | No
| 1819222 | 18/07/2024 | 4:17 | 18/07/2024 | 8:40 | NP36 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 262.4667 | 262.4667 | 1 | No
| 1819259 | 18/07/2024 | 8:50 | 18/07/2024 | 10:35 | NW14 | NUNAWADING | Urban | Animal | Animal impact | 1.32 | 137.588 | 104.2333 | 1 | No
| 1819265 | 18/07/2024 | 9:07 | 18/07/2024 | 11:31 | MC23 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 144.0833 | 144.0833 | 1 | No
| 1819269 | 18/07/2024 | 9:33 | 18/07/2024 | 13:25 | MC14 | MORDIALLOC | Urban | Other | XXX | 1 | 231.4167 | 231.4167 | 1 | No
| 1819302 | 18/07/2024 | 12:02 | 18/07/2024 | 14:37 | WD36 | WEST DONCASTER | Urban | Third Party | Other | 1 | 155.0833 | 155.0833 | 1 | No
| 1819329 | 18/07/2024 | 13:12 | 18/07/2024 | 16:46 | SV32 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 214 | 214 | 1 | No
| 1819351 | 18/07/2024 | 15:30 | 18/07/2024 | 19:24 | BT14 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 234.35 | 234.35 | 1 | No
| 1819362 | 18/07/2024 | 17:51 | 18/07/2024 | 21:33 | HT2 | HEATHERTON | Urban | Asset Failure | LV | 1 | 221.85 | 221.85 | 1 | No
| 1819363 | 18/07/2024 | 18:05 | 18/07/2024 | 20:11 | BH31 | BOX HILL | Urban | Asset Failure | LV | 103 | 13070.7 | 126.9 | 1 | No
| 1819378 | 18/07/2024 | 20:11 | 18/07/2024 | 22:39 | K35 | GARDINER | Urban | Asset Failure | LV | 1 | 147.6 | 147.6 | 1 | No
| 1819381 | 18/07/2024 | 22:30 | 18/07/2024 | 23:48 | OR34 | ORMOND | Urban | Asset Failure | HV | 49 | 3854.6683 | 78.6667 | 1 | No
| 1819396 | 19/07/2024 | 7:11 | 19/07/2024 | 8:17 | DC10 | DONCASTER | Urban | Overloads |  | 1 | 65.2 | 65.2 | 1 | No
| 1819425 | 19/07/2024 | 8:22 | 19/07/2024 | 11:55 | NW31 | NUNAWADING | Urban | Asset Failure | LV | 1 | 213.6667 | 213.6667 | 1 | No
| 1819427 | 19/07/2024 | 8:25 | 19/07/2024 | 10:20 | RWT35 | RINGWOOD | Urban | Asset Failure | LV | 1 | 114.85 | 114.85 | 1 | No
| 1819464 | 19/07/2024 | 9:23 | 19/07/2024 | 11:05 | BU22 | BULLEEN | Urban | Overloads |  | 1 | 102 | 102 | 1 | No
| 1819484 | 19/07/2024 | 9:27 | 19/07/2024 | 10:37 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 1 | 69.2167 | 69.2167 | 1 | No
| 1819501 | 19/07/2024 | 9:45 | 19/07/2024 | 12:40 | RWT24 | RINGWOOD | Urban | Network Business | Switching and protection error | 1 | 174.25 | 174.25 | 1 | No
| 1819541 | 19/07/2024 | 10:55 | 19/07/2024 | 13:45 | EM9 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 169.6667 | 169.6667 | 1 | No
| 1819584 | 19/07/2024 | 12:11 | 19/07/2024 | 22:56 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 645.6 | 645.6 | 1 | No
| 1819593 | 19/07/2024 | 12:51 | 19/07/2024 | 13:17 | HGS21 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 68 | 1755.5356 | 25.8167 | 1 | No
| 1819588 | 19/07/2024 | 13:43 | 19/07/2024 | 15:50 | BW32 | BURWOOD | Urban | Asset Failure | LV | 1 | 127.8667 | 127.8667 | 1 | No
| 1819606 | 19/07/2024 | 13:46 | 19/07/2024 | 15:37 | LD7 | LYNDALE | Urban | Weather |  | 45 | 4981.5 | 110.7 | 1 | No
| 1819628 | 19/07/2024 | 14:47 | 19/07/2024 | 16:20 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 93.5667 | 93.5667 | 1 | No
| 1819631 | 19/07/2024 | 15:01 | 19/07/2024 | 15:33 | FSH31 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 585 | 18310.5 | 31.3 | 1 | No
| 1819631 | 19/07/2024 | 15:01 | 19/07/2024 | 17:26 | FSH31 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 170 | 24599 | 144.7 | 2 | No
| 1819631 | 19/07/2024 | 15:01 | 20/07/2024 | 0:46 | FSH31 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 125 | 73075 | 584.6 | 3 | No
| 1819631 | 19/07/2024 | 15:01 | 20/07/2024 | 2:35 | FSH31 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 13 | 9013.55 | 693.35 | 4 | No
| 1819631 | 19/07/2024 | 15:01 | 20/07/2024 | 2:35 | FSH31 | FRANKSTON SOUTH | Urban | Vegetation | Grow-in - NSP responsibility | 19 | 13186 | 694 | 5 | No
| 1819645 | 19/07/2024 | 16:08 | 19/07/2024 | 20:23 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 254.7167 | 254.7167 | 1 | No
| 1819650 | 19/07/2024 | 16:56 | 19/07/2024 | 20:11 | MTN32 | MORNINGTON | Rural Short | Vegetation | Grow-in - NSP responsibility | 47 | 9121.9151 | 194.0833 | 1 | No
| 1819661 | 19/07/2024 | 16:58 | 19/07/2024 | 20:34 | NB35 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 215.6 | 215.6 | 1 | No
| 1819663 | 19/07/2024 | 17:04 | 19/07/2024 | 17:54 | LD4 | LYNDALE | Urban | Unknown | Unknown | 1 | 50.4667 | 50.4667 | 1 | No
| 1819665 | 19/07/2024 | 17:32 | 19/07/2024 | 19:00 | NP25 | NOBLE PARK | Urban | Asset Failure | Distribution substation | 60.39 | 5285.1335 | 87.5167 | 1 | No
| 1819667 | 19/07/2024 | 17:38 | 20/07/2024 | 0:58 | DMA21 | DROMANA | Urban | Asset Failure | LV | 1 | 439.7 | 439.7 | 1 | No
| 1819669 | 19/07/2024 | 18:58 | 19/07/2024 | 20:12 | EL24 | ELSTERNWICK | Urban | Other | XXX | 13 | 968.9329 | 74.5333 | 1 | No
| 1819674 | 19/07/2024 | 19:12 | 19/07/2024 | 21:41 | KBH32 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 149.3 | 149.3 | 1 | No
| 1819675 | 19/07/2024 | 19:13 | 20/07/2024 | 2:25 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 431.85 | 431.85 | 1 | No
| 1819676 | 19/07/2024 | 19:29 | 19/07/2024 | 20:52 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 21.45 | 1762.4757 | 82.1667 | 1 | No
| 1819682 | 19/07/2024 | 20:47 | 19/07/2024 | 21:45 | EW14 | ELWOOD | Urban | Asset Failure | LV | 1 | 58.1667 | 58.1667 | 1 | No
| 1819687 | 19/07/2024 | 21:05 | 20/07/2024 | 0:08 | EB21 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 183.1 | 183.1 | 1 | No
| 1819691 | 19/07/2024 | 21:22 | 20/07/2024 | 4:37 | DMA23 | DROMANA | Rural Short | Vegetation | Grow-in - Other responsible party | 30 | 13051.5 | 435.05 | 1 | No
| 1819703 | 19/07/2024 | 21:42 | 20/07/2024 | 11:49 | DN11 | DANDENONG | Urban | Asset Failure | LV | 1 | 847.1167 | 847.1167 | 1 | No
| 1819712 | 19/07/2024 | 22:48 | 20/07/2024 | 0:17 | EL23 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 89.0833 | 89.0833 | 1 | No
| 1819713 | 19/07/2024 | 23:02 | 20/07/2024 | 0:27 | BU21 | BULLEEN | Urban | Weather |  | 24.42 | 2074.479 | 84.95 | 1 | No
| 1819714 | 19/07/2024 | 23:08 | 20/07/2024 | 1:27 | MGE21 | MULGRAVE | Urban | Asset Failure | HV | 7.37 | 1027.2549 | 139.3833 | 1 | No
| 1819765 | 19/07/2024 | 23:44 | 20/07/2024 | 14:17 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 1747.0666 | 873.5333 | 1 | No
| 1819719 | 20/07/2024 | 0:04 | 20/07/2024 | 3:04 | DN13 | DANDENONG | Urban | Asset Failure | HV | 53 | 9567.3851 | 180.5167 | 1 | No
| 1819719 | 20/07/2024 | 0:04 | 20/07/2024 | 3:05 | DN13 | DANDENONG | Urban | Asset Failure | HV | 82 | 14848.8306 | 181.0833 | 2 | No
| 1819718 | 20/07/2024 | 0:05 | 20/07/2024 | 9:46 | EW1 | ELWOOD | Urban | Unknown | Unknown | 1 | 581.3833 | 581.3833 | 1 | No
| 1819745 | 20/07/2024 | 6:04 | 20/07/2024 | 14:26 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 501.3333 | 501.3333 | 1 | No
| 1819750 | 20/07/2024 | 7:24 | 20/07/2024 | 8:38 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 74.25 | 74.25 | 1 | No
| 1819754 | 20/07/2024 | 8:21 | 20/07/2024 | 11:30 | NB35 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 188.55 | 188.55 | 1 | No
| 1819763 | 20/07/2024 | 11:01 | 20/07/2024 | 18:18 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1 | 437.4 | 437.4 | 1 | No
| 1819767 | 20/07/2024 | 12:00 | 20/07/2024 | 18:09 | MC32 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 368.6833 | 368.6833 | 1 | No
| 1819769 | 20/07/2024 | 12:13 | 20/07/2024 | 13:11 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 57.3167 | 57.3167 | 1 | No
| 1819771 | 20/07/2024 | 12:20 | 20/07/2024 | 13:55 | DC5 | DONCASTER | Urban | Asset Failure | LV | 1 | 94.4833 | 94.4833 | 1 | No
| 1819776 | 20/07/2024 | 13:08 | 20/07/2024 | 21:34 | DMA23 | DROMANA | Rural Short | Asset Failure | LV | 1 | 505.6 | 505.6 | 1 | No
| 1819778 | 20/07/2024 | 13:36 | 20/07/2024 | 14:44 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 67.7167 | 67.7167 | 1 | No
| 1819780 | 20/07/2024 | 13:55 | 20/07/2024 | 21:45 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 469.4167 | 469.4167 | 1 | No
| 1819796 | 20/07/2024 | 15:06 | 20/07/2024 | 15:50 | STO22 | SORRENTO | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 150 | 6670.005 | 44.4667 | 1 | No
| 1819796 | 20/07/2024 | 15:06 | 20/07/2024 | 16:00 | STO22 | SORRENTO | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 340 | 18280.678 | 53.7667 | 2 | No
| 1819796 | 20/07/2024 | 15:06 | 20/07/2024 | 17:11 | STO22 | SORRENTO | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 87 | 10864.8471 | 124.8833 | 3 | No
| 1819796 | 20/07/2024 | 15:06 | 20/07/2024 | 20:03 | STO22 | SORRENTO | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 37 | 10970.5 | 296.5 | 4 | No
| 1819797 | 20/07/2024 | 15:09 | 20/07/2024 | 16:39 | KBH34 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 90.15 | 90.15 | 1 | No
| 1819755 | 20/07/2024 | 15:12 | 20/07/2024 | 15:40 | DC2 | DONCASTER | Urban | Asset Failure | HV | 7.2 | 204.6002 | 28.4167 | 1 | No
| 1819808 | 20/07/2024 | 16:29 | 20/07/2024 | 21:52 | DMA23 | DROMANA | Rural Short | Unknown | Unknown | 1 | 323.1167 | 323.1167 | 1 | No
| 1819821 | 20/07/2024 | 17:17 | 21/07/2024 | 1:37 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 1 | 500.3833 | 500.3833 | 1 | No
| 1819817 | 20/07/2024 | 18:13 | 21/07/2024 | 1:09 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 52 | 21582.6 | 415.05 | 1 | No
| 1819818 | 20/07/2024 | 18:17 | 20/07/2024 | 19:40 | BR15 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 82.4 | 82.4 | 1 | No
| 1819846 | 21/07/2024 | 7:29 | 21/07/2024 | 10:05 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 155.3333 | 155.3333 | 1 | No
| 1819847 | 21/07/2024 | 7:34 | 21/07/2024 | 9:29 | K21 | GARDINER | Urban | Asset Failure | LV | 1 | 115.8167 | 115.8167 | 1 | No
| 1819864 | 21/07/2024 | 9:36 | 21/07/2024 | 14:55 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 318.1167 | 318.1167 | 1 | No
| 1819872 | 21/07/2024 | 10:11 | 21/07/2024 | 13:01 | SS12 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 170.05 | 170.05 | 1 | No
| 1819883 | 21/07/2024 | 12:17 | 21/07/2024 | 16:08 | GW10 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 231.8167 | 231.8167 | 1 | No
| 1819909 | 21/07/2024 | 16:49 | 21/07/2024 | 20:34 | MC22 | MORDIALLOC | Urban | Asset Failure | Distribution substation | 1 | 224.0833 | 224.0833 | 1 | No
| 1819917 | 21/07/2024 | 20:28 | 22/07/2024 | 0:05 | DN22 | DANDENONG | Urban | Asset Failure | LV | 1 | 216.4167 | 216.4167 | 1 | No
| 1819922 | 22/07/2024 | 4:09 | 22/07/2024 | 7:03 | NP14 | NOBLE PARK | Urban | Overloads |  | 1 | 173.9 | 173.9 | 1 | No
| 1819924 | 22/07/2024 | 7:13 | 22/07/2024 | 9:40 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1 | 146.7333 | 146.7333 | 1 | No
| 1819926 | 22/07/2024 | 7:42 | 22/07/2024 | 9:41 | SK1 | ST. KILDA | Urban | Overloads |  | 1 | 118.7 | 118.7 | 1 | No
| 1819930 | 22/07/2024 | 7:56 | 22/07/2024 | 9:50 | GW8 | GLEN WAVERLEY | Urban | Asset Failure | LV | 11 | 1252.1663 | 113.8333 | 1 | No
| 1819931 | 22/07/2024 | 8:09 | 22/07/2024 | 10:20 | MC12 | MORDIALLOC | Urban | Weather |  | 1 | 130.4167 | 130.4167 | 1 | No
| 1819934 | 22/07/2024 | 8:18 | 22/07/2024 | 10:50 | EB32 | EAST BURWOOD | Urban | Overloads |  | 1 | 151.0667 | 151.0667 | 1 | No
| 1819938 | 22/07/2024 | 8:41 | 22/07/2024 | 11:18 | SV33 | SPRINGVALE | Urban | Unknown | Unknown | 1 | 157.3167 | 157.3167 | 1 | No
| 1819944 | 22/07/2024 | 8:56 | 22/07/2024 | 12:20 | FTN24 | FRANKSTON | Urban | Asset Failure | LV | 1 | 203.05 | 203.05 | 1 | No
| 1819975 | 22/07/2024 | 10:13 | 22/07/2024 | 11:49 | NP11 | NOBLE PARK | Urban | Network Business | Network Error | 1 | 95.4333 | 95.4333 | 1 | No
| 1819984 | 22/07/2024 | 10:34 | 22/07/2024 | 14:10 | CRM35 | CARRUM | Urban | Overloads |  | 1 | 215.0833 | 215.0833 | 1 | No
| 1820012 | 22/07/2024 | 11:36 | 22/07/2024 | 15:10 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 1 | 213.25 | 213.25 | 1 | No
| 1820039 | 22/07/2024 | 12:16 | 22/07/2024 | 17:30 | CFD26 | CAULFIELD | Urban | Asset Failure | LV | 1 | 313.7167 | 313.7167 | 1 | No
| 1820076 | 22/07/2024 | 13:45 | 22/07/2024 | 18:01 | MC14 | MORDIALLOC | Urban | Overloads |  | 1 | 255.45 | 255.45 | 1 | No
| 1820157 | 22/07/2024 | 18:38 | 22/07/2024 | 21:17 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 70 | 11106.669 | 158.6667 | 1 | No
| 1820158 | 22/07/2024 | 18:38 | 22/07/2024 | 20:15 | MTN34 | MORNINGTON | Urban | Asset Failure | HV | 29.37 | 2822.457 | 96.1 | 1 | No
| 1820162 | 22/07/2024 | 18:59 | 22/07/2024 | 19:45 | CRM13 | CARRUM | Urban | Asset Failure | LV | 2 | 92.4666 | 46.2333 | 1 | No
| 1820149 | 22/07/2024 | 19:14 | 22/07/2024 | 21:00 | SS13 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 106.3333 | 106.3333 | 1 | No
| 1820165 | 22/07/2024 | 19:26 | 22/07/2024 | 23:55 | MTN22 | MORNINGTON | Rural Short | Unknown | Unknown | 1 | 269.0833 | 269.0833 | 1 | No
| 1820176 | 22/07/2024 | 21:37 | 22/07/2024 | 23:39 | RBD12 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 122.25 | 122.25 | 1 | No
| 1820199 | 23/07/2024 | 5:35 | 23/07/2024 | 8:10 | HGS23 | HASTINGS | Rural Short | Animal | Other | 2 | 308.6 | 154.3 | 1 | No
| 1820234 | 23/07/2024 | 8:09 | 23/07/2024 | 9:39 | EB32 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 89.3 | 89.3 | 1 | No
| 1820438 | 23/07/2024 | 13:29 | 23/07/2024 | 16:55 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 206.15 | 206.15 | 1 | No
| 1820418 | 23/07/2024 | 14:10 | 23/07/2024 | 15:55 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 105 | 105 | 1 | No
| 1820428 | 23/07/2024 | 14:31 | 23/07/2024 | 18:10 | EB33 | EAST BURWOOD | Urban | Asset Failure | LV | 5.94 | 1300.86 | 219 | 1 | No
| 1820196 | 23/07/2024 | 14:35 | 23/07/2024 | 19:00 | LD7 | LYNDALE | Urban | Third Party | Vehicle Impact | 1 | 265.0667 | 265.0667 | 1 | No
| 1820506 | 23/07/2024 | 19:00 | 23/07/2024 | 23:55 | CRM35 | CARRUM | Urban | Unknown | Unknown | 1 | 294.6667 | 294.6667 | 1 | No
| 1820513 | 23/07/2024 | 19:38 | 23/07/2024 | 20:46 | BH11 | BOX HILL | Urban | Asset Failure | LV | 1 | 67.2833 | 67.2833 | 1 | No
| 1820517 | 23/07/2024 | 20:10 | 23/07/2024 | 22:37 | LWN33 | LANGWARRIN | Urban | Asset Failure | LV | 34.32 | 5045.04 | 147 | 1 | No
| 1820528 | 23/07/2024 | 21:10 | 24/07/2024 | 12:04 | SR22 | SANDRINGHAM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 121 | 108129.6293 | 893.6333 | 1 | No
| 1820540 | 24/07/2024 | 4:10 | 24/07/2024 | 5:02 | SR22 | SANDRINGHAM | Urban | Asset Failure | HV | 718 | 37491.5906 | 52.2167 | 1 | No
| 1820547 | 24/07/2024 | 6:28 | 24/07/2024 | 8:30 | STO22 | SORRENTO | Urban | Asset Failure | LV | 1 | 121.5667 | 121.5667 | 1 | No
| 1820608 | 24/07/2024 | 8:55 | 24/07/2024 | 9:40 | DC12 | DONCASTER | Urban | Asset Failure | LV | 13.86 | 611.6875 | 44.1333 | 1 | No
| 1820768 | 24/07/2024 | 10:31 | 24/07/2024 | 18:59 | EM5 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 508.4833 | 508.4833 | 1 | No
| 1820812 | 24/07/2024 | 11:47 | 24/07/2024 | 12:46 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 58.2333 | 58.2333 | 1 | No
| 1820609 | 24/07/2024 | 11:55 | 24/07/2024 | 13:40 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 105 | 105 | 1 | No
| 1820927 | 24/07/2024 | 16:48 | 24/07/2024 | 18:42 | MR33 | MOORABBIN | Urban | Asset Failure | LV | 1 | 114.0667 | 114.0667 | 1 | No
| 1820952 | 24/07/2024 | 19:31 | 24/07/2024 | 20:30 | HGS23 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 59 | 59 | 1 | No
| 1821010 | 25/07/2024 | 7:19 | 25/07/2024 | 8:50 | DMA23 | DROMANA | Rural Short | Asset Failure | Distribution substation | 8.91 | 807.9882 | 90.6833 | 1 | No
| 1821038 | 25/07/2024 | 8:19 | 25/07/2024 | 11:00 | DMA15 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 18 | 2887.5006 | 160.4167 | 1 | No
| 1821089 | 25/07/2024 | 8:59 | 25/07/2024 | 11:19 | LD6 | LYNDALE | Urban | Asset Failure | LV | 34 | 4749.2322 | 139.6833 | 1 | No
| 1821103 | 25/07/2024 | 9:21 | 25/07/2024 | 11:49 | CFD13 | CAULFIELD | Urban | Unknown | Unknown | 1 | 148 | 148 | 1 | No
| 1821140 | 25/07/2024 | 10:19 | 25/07/2024 | 12:15 | BT25 | BENTLEIGH | Urban | Third Party | Other | 1 | 116.7167 | 116.7167 | 1 | No
| 1821165 | 25/07/2024 | 10:51 | 25/07/2024 | 13:00 | HGS31 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 128.4833 | 128.4833 | 1 | No
| 1821166 | 25/07/2024 | 10:52 | 25/07/2024 | 13:00 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 4 | 510.8 | 127.7 | 1 | No
| 1821236 | 25/07/2024 | 12:21 | 25/07/2024 | 14:30 | FTN24 | FRANKSTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 17 | 2177.4161 | 128.0833 | 1 | No
| 1821224 | 25/07/2024 | 13:40 | 25/07/2024 | 16:05 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 145.3833 | 145.3833 | 1 | No
| 1821269 | 25/07/2024 | 14:13 | 25/07/2024 | 15:04 | CFD14 | CAULFIELD | Urban | Asset Failure | LV | 1 | 51.5833 | 51.5833 | 1 | No
| 1821252 | 25/07/2024 | 14:56 | 25/07/2024 | 16:30 | SR21 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 94.0333 | 94.0333 | 1 | No
| 1821298 | 25/07/2024 | 15:56 | 25/07/2024 | 19:45 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 228.7 | 228.7 | 1 | No
| 1821334 | 25/07/2024 | 17:36 | 25/07/2024 | 18:40 | HGS22 | HASTINGS | Rural Short | Asset Failure | Distribution substation | 6.7 | 423.9981 | 63.2833 | 1 | No
| 1821332 | 25/07/2024 | 18:11 | 25/07/2024 | 20:01 | BT25 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 110.1667 | 110.1667 | 1 | No
| 1821347 | 25/07/2024 | 18:28 | 25/07/2024 | 21:31 | LWN32 | LANGWARRIN | Rural Short | Asset Failure | LV | 3 | 549.5499 | 183.1833 | 1 | No
| 1821354 | 25/07/2024 | 18:40 | 25/07/2024 | 19:38 | MC23 | MORDIALLOC | Urban | Animal | Animal impact | 79.73 | 4556.5695 | 57.15 | 1 | No
| 1821359 | 25/07/2024 | 19:24 | 25/07/2024 | 22:30 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 185.2333 | 185.2333 | 1 | No
| 1821361 | 25/07/2024 | 20:12 | 25/07/2024 | 21:45 | LWN24 | LANGWARRIN | Urban | Asset Failure | LV | 28.71 | 2670.03 | 93 | 1 | No
| 1821393 | 26/07/2024 | 7:36 | 26/07/2024 | 8:23 | LWN34 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 46.9667 | 46.9667 | 1 | No
| 1821448 | 26/07/2024 | 9:29 | 26/07/2024 | 11:07 | LWN21 | LANGWARRIN | Rural Short | Unknown | Unknown | 5 | 490 | 98 | 1 | No
| 1821475 | 26/07/2024 | 10:10 | 26/07/2024 | 12:01 | RBD14 | ROSEBUD | Urban | Asset Failure | LV | 1 | 111.8667 | 111.8667 | 1 | No
| 1821541 | 26/07/2024 | 11:13 | 26/07/2024 | 12:13 | DMA15 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 40 | 2378.668 | 59.4667 | 1 | No
| 1821545 | 26/07/2024 | 11:19 | 26/07/2024 | 12:09 | DMA15 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 27 | 1354.05 | 50.15 | 1 | No
| 1821661 | 26/07/2024 | 13:32 | 26/07/2024 | 15:37 | SR22 | SANDRINGHAM | Urban | Third Party | Other | 1 | 124.7833 | 124.7833 | 1 | No
| 1821665 | 26/07/2024 | 13:44 | 26/07/2024 | 17:04 | LWN24 | LANGWARRIN | Urban | Animal | Animal impact | 46.9 | 9394.07 | 200.3 | 1 | No
| 1821947 | 26/07/2024 | 16:25 | 27/07/2024 | 16:12 | NW13 | NUNAWADING | Urban | Asset Failure | LV | 10 | 14266.167 | 1426.6167 | 1 | No
| 1821725 | 26/07/2024 | 17:23 | 26/07/2024 | 19:50 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 146.5333 | 146.5333 | 1 | No
| 1821723 | 26/07/2024 | 17:54 | 26/07/2024 | 20:50 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 176 | 176 | 1 | No
| 1821733 | 26/07/2024 | 18:26 | 26/07/2024 | 19:46 | MTN32 | MORNINGTON | Rural Short | Overloads |  | 60 | 4780.002 | 79.6667 | 1 | No
| 1821750 | 26/07/2024 | 20:05 | 26/07/2024 | 20:42 | SH24 | SURREY HILLS | Urban | Unknown | Unknown | 114 | 4111.6038 | 36.0667 | 1 | No
| 1821753 | 26/07/2024 | 20:10 | 26/07/2024 | 20:58 | SH24 | SURREY HILLS | Urban | Overloads |  | 19.47 | 921.5794 | 47.3333 | 1 | No
| 1821743 | 26/07/2024 | 21:04 | 26/07/2024 | 22:00 | DC8 | DONCASTER | Urban | Asset Failure | LV | 1 | 56 | 56 | 1 | No
| 1821782 | 26/07/2024 | 21:41 | 26/07/2024 | 23:15 | EW1 | ELWOOD | Urban | Asset Failure | LV | 1 | 93.4 | 93.4 | 1 | No
| 1821786 | 26/07/2024 | 22:41 | 26/07/2024 | 23:54 | LWN23 | LANGWARRIN | Urban | Animal | Other | 229.81 | 16611.4252 | 72.2833 | 1 | No
| 1821797 | 26/07/2024 | 22:58 | 27/07/2024 | 1:26 | MTN35 | MORNINGTON | Rural Short | Animal | Animal impact | 3.35 | 495.0741 | 147.7833 | 1 | No
| 1821814 | 26/07/2024 | 23:22 | 27/07/2024 | 0:31 | LD7 | LYNDALE | Urban | Asset Failure | LV | 110.88 | 7645.176 | 68.95 | 1 | No
| 1821838 | 27/07/2024 | 1:26 | 27/07/2024 | 2:18 | LD7 | LYNDALE | Urban | Asset Failure | LV | 13 | 674.9171 | 51.9167 | 1 | No
| 1821849 | 27/07/2024 | 5:16 | 27/07/2024 | 8:32 | SVW55 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 196.0167 | 196.0167 | 1 | No
| 1821758 | 27/07/2024 | 10:00 | 27/07/2024 | 12:15 | EB33 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 135 | 135 | 1 | No
| 1821900 | 27/07/2024 | 10:08 | 27/07/2024 | 10:35 | FTN11 | FRANKSTON | Urban | Asset Failure | Distribution substation | 16.75 | 438.0125 | 26.15 | 1 | No
| 1821901 | 27/07/2024 | 10:11 | 27/07/2024 | 11:58 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 106.4167 | 106.4167 | 1 | No
| 1821894 | 27/07/2024 | 11:28 | 27/07/2024 | 14:22 | BR9 | BEAUMARIS | Urban | Asset Failure | LV | 2 | 348 | 174 | 1 | No
| 1821909 | 27/07/2024 | 11:43 | 27/07/2024 | 13:15 | FTN23 | FRANKSTON | Urban | Asset Failure | LV | 1 | 92 | 92 | 1 | No
| 1821913 | 27/07/2024 | 13:24 | 27/07/2024 | 16:10 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 1 | 166 | 166 | 1 | No
| 1821939 | 27/07/2024 | 15:20 | 27/07/2024 | 17:16 | LD6 | LYNDALE | Urban | Asset Failure | LV | 1 | 115.75 | 115.75 | 1 | No
| 1821941 | 27/07/2024 | 15:34 | 27/07/2024 | 17:11 | HT1 | HEATHERTON | Urban | Network Business | Network Error | 1 | 96.95 | 96.95 | 1 | No
| 1821950 | 27/07/2024 | 17:14 | 27/07/2024 | 21:25 | EL34 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 251 | 251 | 1 | No
| 1821961 | 27/07/2024 | 17:58 | 27/07/2024 | 20:48 | M22 | MENTONE | Urban | Overloads |  | 21.78 | 3697.155 | 169.75 | 1 | No
| 1821965 | 27/07/2024 | 18:34 | 27/07/2024 | 20:36 | CFD24 | CAULFIELD | Urban | Asset Failure | LV | 34.32 | 4187.04 | 122 | 1 | No
| 1821959 | 27/07/2024 | 19:38 | 27/07/2024 | 20:45 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 67 | 67 | 1 | No
| 1821967 | 27/07/2024 | 19:43 | 27/07/2024 | 21:15 | GW3 | GLEN WAVERLEY | Urban | Asset Failure | LV | 34.32 | 3143.712 | 91.6 | 1 | No
| 1821979 | 27/07/2024 | 20:24 | 27/07/2024 | 21:45 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 12.87 | 1038.609 | 80.7 | 1 | No
| 1821991 | 27/07/2024 | 23:11 | 28/07/2024 | 0:18 | NP36 | NOBLE PARK | Urban | Overloads |  | 18.81 | 1255.5675 | 66.75 | 1 | No
| 1822007 | 28/07/2024 | 4:42 | 28/07/2024 | 7:40 | GW7 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 73 | 12938.0309 | 177.2333 | 1 | No
| 1822012 | 28/07/2024 | 5:46 | 28/07/2024 | 20:55 | MTN32 | MORNINGTON | Rural Short | Asset Failure | HV | 1 | 909.65 | 909.65 | 1 | No
| 1822018 | 28/07/2024 | 8:08 | 28/07/2024 | 9:57 | NW11 | NUNAWADING | Urban | Asset Failure | LV | 1 | 109.4333 | 109.4333 | 1 | No
| 1822025 | 28/07/2024 | 9:09 | 28/07/2024 | 10:36 | GW5 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 87.1667 | 87.1667 | 1 | No
| 1822009 | 28/07/2024 | 12:02 | 28/07/2024 | 14:45 | CRM35 | CARRUM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 163 | 163 | 1 | No
| 1822047 | 28/07/2024 | 12:07 | 28/07/2024 | 12:53 | DVY12 | DANDENONG VALLEY | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1884 | 85345.2 | 45.3 | 1 | No
| 1822047 | 28/07/2024 | 12:07 | 28/07/2024 | 12:58 | DVY12 | DANDENONG VALLEY | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 1006 | 50.3 | 2 | No
| 1822047 | 28/07/2024 | 12:07 | 28/07/2024 | 16:02 | DVY12 | DANDENONG VALLEY | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 14 | 3279.5 | 234.25 | 3 | No
| 1822048 | 28/07/2024 | 12:08 | 28/07/2024 | 12:51 | DVY12 | DANDENONG VALLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 489 | 21157.4163 | 43.2667 | 1 | No
| 1822068 | 28/07/2024 | 13:15 | 28/07/2024 | 13:48 | NW22 | NUNAWADING | Urban | Asset Failure | LV | 1 | 33.2 | 33.2 | 1 | No
| 1822076 | 28/07/2024 | 13:47 | 28/07/2024 | 16:15 | SR24 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 148.3167 | 148.3167 | 1 | No
| 1822078 | 28/07/2024 | 14:32 | 28/07/2024 | 16:39 | EB22 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 126.9 | 126.9 | 1 | No
| 1822102 | 28/07/2024 | 18:18 | 29/07/2024 | 0:47 | CDA11 | CLARINDA | Urban | Asset Failure | LV | 1 | 389.45 | 389.45 | 1 | No
| 1822107 | 28/07/2024 | 18:57 | 28/07/2024 | 20:27 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 20.79 | 1858.9732 | 89.4167 | 1 | No
| 1822109 | 28/07/2024 | 19:26 | 28/07/2024 | 21:50 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 143.2833 | 143.2833 | 1 | No
| 1822111 | 28/07/2024 | 19:53 | 29/07/2024 | 1:56 | EL34 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 363.4333 | 363.4333 | 1 | No
| 1822115 | 28/07/2024 | 21:11 | 29/07/2024 | 0:31 | DC10 | DONCASTER | Urban | Overloads |  | 1 | 200 | 200 | 1 | No
| 1822116 | 28/07/2024 | 21:11 | 28/07/2024 | 22:40 | FSH33 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 26.8 | 2377.16 | 88.7 | 1 | No
| 1822122 | 28/07/2024 | 22:00 | 28/07/2024 | 23:30 | NP25 | NOBLE PARK | Urban | Overloads |  | 20.46 | 1823.3277 | 89.1167 | 1 | No
| 1822124 | 28/07/2024 | 22:19 | 28/07/2024 | 23:40 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 19.47 | 1569.6071 | 80.6167 | 1 | No
| 1822126 | 28/07/2024 | 22:54 | 29/07/2024 | 1:33 | EB21 | EAST BURWOOD | Urban | Overloads |  | 1 | 159 | 159 | 1 | No
| 1822129 | 29/07/2024 | 0:28 | 29/07/2024 | 3:41 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 2.04 | 393.8561 | 193.0667 | 1 | No
| 1822135 | 29/07/2024 | 1:49 | 29/07/2024 | 3:02 | EM10 | EAST MALVERN | Urban | Asset Failure | LV | 4.62 | 335.412 | 72.6 | 1 | No
| 1822011 | 29/07/2024 | 3:45 | 29/07/2024 | 7:20 | MGE34 | MULGRAVE | Urban | Asset Failure | LV | 1 | 215.55 | 215.55 | 1 | No
| 1822144 | 29/07/2024 | 6:32 | 29/07/2024 | 8:01 | NB25 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 88.5833 | 88.5833 | 1 | No
| 1822070 | 29/07/2024 | 11:20 | 29/07/2024 | 15:45 | DMA21 | DROMANA | Urban | Asset Failure | LV | 1 | 265 | 265 | 1 | No
| 1822327 | 29/07/2024 | 13:00 | 29/07/2024 | 14:07 | OE9 | OAKLEIGH EAST | Urban | Animal | Animal impact | 396 | 26525.3868 | 66.9833 | 1 | No
| 1822327 | 29/07/2024 | 13:00 | 29/07/2024 | 14:08 | OE9 | OAKLEIGH EAST | Urban | Animal | Animal impact | 166 | 11260.3278 | 67.8333 | 2 | No
| 1822327 | 29/07/2024 | 13:00 | 29/07/2024 | 14:45 | OE9 | OAKLEIGH EAST | Urban | Animal | Animal impact | 60 | 6303 | 105.05 | 3 | No
| 1822340 | 29/07/2024 | 13:41 | 29/07/2024 | 17:30 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 228.15 | 228.15 | 1 | No
| 1822341 | 29/07/2024 | 13:42 | 29/07/2024 | 16:19 | MC34 | MORDIALLOC | Urban | Overloads |  | 1 | 156.1667 | 156.1667 | 1 | No
| 1822362 | 29/07/2024 | 15:03 | 29/07/2024 | 16:44 | BH11 | BOX HILL | Urban | Asset Failure | LV | 1 | 100.9 | 100.9 | 1 | No
| 1822393 | 29/07/2024 | 17:51 | 29/07/2024 | 19:58 | EW2 | ELWOOD | Urban | Asset Failure | LV | 27.39 | 3453.879 | 126.1 | 1 | No
| 1822397 | 29/07/2024 | 18:02 | 29/07/2024 | 18:52 | CRM23 | CARRUM | Urban | Overloads |  | 22.44 | 1113.7713 | 49.6333 | 1 | No
| 1822399 | 29/07/2024 | 18:11 | 29/07/2024 | 19:17 | RWT23 | RINGWOOD | Urban | Asset Failure | LV | 47.19 | 3086.226 | 65.4 | 1 | No
| 1822403 | 29/07/2024 | 18:20 | 29/07/2024 | 20:26 | MGE24 | MULGRAVE | Urban | Overloads |  | 1 | 126 | 126 | 1 | No
| 1822407 | 29/07/2024 | 18:58 | 29/07/2024 | 23:09 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 122 | 30636.2374 | 251.1167 | 1 | No
| 1822424 | 29/07/2024 | 22:18 | 29/07/2024 | 23:05 | NP23 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 47.1333 | 47.1333 | 1 | No
| 1822428 | 30/07/2024 | 1:38 | 30/07/2024 | 2:46 | LD1 | LYNDALE | Urban | Unknown | Unknown | 49.58 | 3324.339 | 67.05 | 1 | No
| 1822433 | 30/07/2024 | 3:48 | 30/07/2024 | 4:40 | DN11 | DANDENONG | Urban | Overloads |  | 29.37 | 1515.0015 | 51.5833 | 1 | No
| 1822452 | 30/07/2024 | 7:29 | 30/07/2024 | 8:38 | MR31 | MOORABBIN | Urban | Animal | Animal impact | 2 | 137.8 | 68.9 | 1 | No
| 1822497 | 30/07/2024 | 8:36 | 30/07/2024 | 10:50 | LD32 | LYNDALE | Urban | Unknown | Unknown | 1 | 133.3333 | 133.3333 | 1 | No
| 1822532 | 30/07/2024 | 9:29 | 30/07/2024 | 10:42 | OAK33 | OAKLEIGH | Urban | Third Party | Other | 1 | 72.5667 | 72.5667 | 1 | No
| 1822556 | 30/07/2024 | 9:51 | 30/07/2024 | 11:38 | NW14 | NUNAWADING | Urban | Asset Failure | LV | 61 | 6494.4687 | 106.4667 | 1 | No
| 1822609 | 30/07/2024 | 11:05 | 30/07/2024 | 13:36 | MGE33 | MULGRAVE | Urban | Third Party | Other | 1 | 151.65 | 151.65 | 1 | No
| 1822629 | 30/07/2024 | 11:27 | 30/07/2024 | 12:11 | LD4 | LYNDALE | Urban | Animal | Animal impact | 32.16 | 1400.0309 | 43.5333 | 1 | No
| 1822650 | 30/07/2024 | 12:23 | 30/07/2024 | 16:57 | MC21 | MORDIALLOC | Urban | Third Party | Other | 1 | 274.5167 | 274.5167 | 1 | No
| 1822719 | 30/07/2024 | 16:02 | 30/07/2024 | 17:34 | MR21 | MOORABBIN | Urban | Asset Failure | LV | 1 | 91.45 | 91.45 | 1 | No
| 1822727 | 30/07/2024 | 16:37 | 30/07/2024 | 18:30 | LD4 | LYNDALE | Urban | Third Party | Vehicle Impact | 1 | 112.7667 | 112.7667 | 1 | No
| 1822758 | 30/07/2024 | 19:56 | 30/07/2024 | 22:44 | GW6 | GLEN WAVERLEY | Urban | Asset Failure | LV | 2 | 336.2666 | 168.1333 | 1 | No
| 1822762 | 30/07/2024 | 20:02 | 30/07/2024 | 21:45 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 13.2 | 1355.4196 | 102.6833 | 1 | No
| 1822771 | 30/07/2024 | 20:45 | 30/07/2024 | 22:14 | OR24 | ORMOND | Urban | Asset Failure | LV | 36 | 3183.0012 | 88.4167 | 1 | No
| 1822771 | 30/07/2024 | 20:45 | 30/07/2024 | 22:14 | OR24 | ORMOND | Urban | Asset Failure | LV | 73 | 6434.95 | 88.15 | 1 | No
| 1822771 | 30/07/2024 | 20:51 | 30/07/2024 | 22:14 | OR24 | ORMOND | Urban | Asset Failure | LV | 3 | 248.7999 | 82.9333 | 1 | No
| 1822771 | 30/07/2024 | 21:57 | 30/07/2024 | 22:14 | OR24 | ORMOND | Urban | Asset Failure | LV | 1 | 16.0333 | 16.0333 | 1 | No
| 1822779 | 30/07/2024 | 21:57 | 30/07/2024 | 22:16 | OR24 | ORMOND | Urban | Asset Failure | LV | 10 | 180.333 | 18.0333 | 1 | No
| 1822788 | 31/07/2024 | 1:08 | 31/07/2024 | 2:30 | DMA21 | DROMANA | Urban | Asset Failure | LV | 12.54 | 1020.5466 | 81.3833 | 1 | No
| 1822791 | 31/07/2024 | 1:36 | 31/07/2024 | 2:28 | WD23 | WEST DONCASTER | Urban | Overloads |  | 1 | 52.65 | 52.65 | 1 | No
| 1822783 | 31/07/2024 | 2:50 | 31/07/2024 | 4:26 | NB36 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 96.9333 | 96.9333 | 1 | No
| 1822793 | 31/07/2024 | 3:45 | 31/07/2024 | 4:28 | DN11 | DANDENONG | Urban | Third Party | Vehicle Impact | 83 | 3569 | 43 | 1 | No
| 1822835 | 31/07/2024 | 8:25 | 31/07/2024 | 10:03 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 97.9667 | 97.9667 | 1 | No
| 1822815 | 31/07/2024 | 8:38 | 31/07/2024 | 13:14 | OR32 | ORMOND | Urban | Asset Failure | LV | 1 | 276 | 276 | 1 | No
| 1822898 | 31/07/2024 | 9:44 | 31/07/2024 | 11:54 | FSH31 | FRANKSTON SOUTH | Urban | Overloads |  | 1 | 129.8333 | 129.8333 | 1 | No
| 1822902 | 31/07/2024 | 9:52 | 31/07/2024 | 10:28 | NW14 | NUNAWADING | Urban | Overloads |  | 1 | 35.7667 | 35.7667 | 1 | No
| 1822903 | 31/07/2024 | 10:02 | 31/07/2024 | 11:50 | NP33 | NOBLE PARK | Urban | Overloads |  | 1 | 108 | 108 | 1 | No
| 1822908 | 31/07/2024 | 10:02 | 31/07/2024 | 10:16 | MR22 | MOORABBIN | Urban | Other | XXX | 1 | 13.2667 | 13.2667 | 1 | No
| 1822921 | 31/07/2024 | 11:40 | 31/07/2024 | 12:20 | GW10 | GLEN WAVERLEY | Urban | Overloads |  | 1 | 40 | 40 | 1 | No
| 1823055 | 31/07/2024 | 14:37 | 31/07/2024 | 14:45 | FTN23 | FRANKSTON | Urban | Other | XXX | 1 | 7.3667 | 7.3667 | 1 | No
| 1822732 | 31/07/2024 | 15:38 | 31/07/2024 | 19:08 | DC3 | DONCASTER | Urban | Third Party | Other | 1 | 210.1333 | 210.1333 | 1 | No
| 1823074 | 31/07/2024 | 15:39 | 31/07/2024 | 17:21 | BH31 | BOX HILL | Urban | Third Party | Dig-in | 1 | 102.1833 | 102.1833 | 1 | No
| 1823009 | 31/07/2024 | 16:31 | 31/07/2024 | 18:19 | EW9 | ELWOOD | Urban | Overloads |  | 1 | 108 | 108 | 1 | No
| 1823098 | 31/07/2024 | 18:17 | 31/07/2024 | 20:50 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 57.09 | 8734.77 | 153 | 1 | No
| 1823105 | 31/07/2024 | 18:37 | 31/07/2024 | 20:22 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 26.07 | 2715.6259 | 104.1667 | 1 | No
| 1823110 | 31/07/2024 | 18:48 | 31/07/2024 | 21:03 | HGS33 | HASTINGS | Rural Short | Unknown | Unknown | 3 | 405 | 135 | 1 | No
| 1823111 | 31/07/2024 | 18:57 | 31/07/2024 | 20:43 | BH12 | BOX HILL | Urban | Asset Failure | LV | 38.61 | 4073.355 | 105.5 | 1 | No
| 1823112 | 31/07/2024 | 19:10 | 31/07/2024 | 22:05 | K21 | GARDINER | Urban | Other | XXX | 1 | 174.2833 | 174.2833 | 1 | No
| 1823109 | 31/07/2024 | 19:18 | 31/07/2024 | 21:03 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 105 | 105 | 1 | No
| 1823117 | 31/07/2024 | 19:32 | 31/07/2024 | 21:30 | OR33 | ORMOND | Urban | Overloads |  | 115.17 | 13551.6738 | 117.6667 | 1 | No
| 1823120 | 31/07/2024 | 19:37 | 31/07/2024 | 21:37 | FSH22 | FRANKSTON SOUTH | Urban | Overloads |  | 27.06 | 3228.7099 | 119.3167 | 1 | No
| 1823122 | 31/07/2024 | 19:48 | 2024-01-08 | 0:56 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 64 | 19667.2 | 307.3 | 1 | No
| 1823131 | 31/07/2024 | 22:05 | 31/07/2024 | 22:47 | CDA11 | CLARINDA | Urban | Third Party | Other | 110 | 4565 | 41.5 | 1 | No
| 1823136 | 31/07/2024 | 22:22 | 2024-01-08 | 1:41 | NP16 | NOBLE PARK | Urban | Overloads |  | 89.1 | 17747.232 | 199.1833 | 1 | No
| 1823141 | 31/07/2024 | 23:14 | 31/07/2024 | 23:33 | OAK26 | OAKLEIGH | Urban | Unknown | Unknown | 51.48 | 952.38 | 18.5 | 1 | No
| 1823165 | 2024-01-08 | 7:24 | 2024-01-08 | 11:17 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 1 | 232.8 | 232.8 | 1 | No
| 1823231 | 2024-01-08 | 9:10 | 2024-01-08 | 9:38 | FTN11 | FRANKSTON | Urban | Third Party | Other | 21 | 588 | 28 | 1 | No
| 1823286 | 2024-01-08 | 10:32 | 2024-01-08 | 17:58 | SR23 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 445.9833 | 445.9833 | 1 | No
| 1823311 | 2024-01-08 | 11:19 | 2024-01-08 | 14:02 | FSH23 | FRANKSTON SOUTH | Rural Short | Overloads |  | 1 | 162.9833 | 162.9833 | 1 | No
| 1823365 | 2024-01-08 | 15:39 | 2024-01-08 | 18:30 | M22 | MENTONE | Urban | Asset Failure | LV | 1 | 171 | 171 | 1 | No
| 1823423 | 2024-01-08 | 19:07 | 2024-01-08 | 21:57 | BC23 | BALACLAVA | Urban | Asset Failure | LV | 1 | 170.3833 | 170.3833 | 1 | No
| 1823453 | 2024-01-08 | 19:45 | 2024-01-08 | 20:50 | M22 | MENTONE | Urban | Overloads |  | 21.78 | 1414.611 | 64.95 | 1 | No
| 1823454 | 2024-01-08 | 20:22 | 2024-01-08 | 22:49 | RBD12 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 147.9167 | 147.9167 | 1 | No
| 1823450 | 2024-01-08 | 22:01 | 2024-02-08 | 0:22 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 141 | 141 | 1 | No
| 1823476 | 2024-01-08 | 23:22 | 2024-02-08 | 0:28 | SVW56 | SPRINGVALE WEST | Urban | Asset Failure | LV | 51.48 | 3359.07 | 65.25 | 1 | No
| 1823495 | 2024-02-08 | 6:47 | 2024-02-08 | 8:54 | OAK32 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 126.35 | 126.35 | 1 | No
| 1823507 | 2024-02-08 | 7:49 | 2024-02-08 | 9:48 | EW12 | ELWOOD | Urban | Overloads |  | 16.17 | 1908.33 | 118.0167 | 1 | No
| 1823537 | 2024-02-08 | 8:23 | 2024-02-08 | 11:05 | DC10 | DONCASTER | Urban | Asset Failure | LV | 9.9 | 1596.7047 | 161.2833 | 1 | No
| 1823488 | 2024-02-08 | 9:23 | 2024-02-08 | 13:10 | EB33 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 227.6667 | 227.6667 | 1 | No
| 1823602 | 2024-02-08 | 10:23 | 2024-02-08 | 13:27 | NP33 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 183.8 | 183.8 | 1 | No
| 1823616 | 2024-02-08 | 10:47 | 2024-02-08 | 17:59 | EM5 | EAST MALVERN | Urban | Asset Failure | LV | 2 | 863.9666 | 431.9833 | 1 | No
| 1823614 | 2024-02-08 | 11:21 | 2024-02-08 | 16:53 | MGE22 | MULGRAVE | Urban | Overloads |  | 1 | 332.6667 | 332.6667 | 1 | No
| 1823663 | 2024-02-08 | 12:18 | 2024-02-08 | 13:49 | GW5 | GLEN WAVERLEY | Urban | Third Party | Other | 1 | 91.0833 | 91.0833 | 1 | No
| 1823700 | 2024-02-08 | 13:44 | 2024-02-08 | 16:57 | KBH34 | KEYSBOROUGH | Urban | Third Party | Other | 4 | 769.2 | 192.3 | 1 | No
| 1823705 | 2024-02-08 | 13:58 | 2024-02-08 | 21:35 | BU25 | BULLEEN | Urban | Asset Failure | HV | 15 | 6855 | 457 | 1 | No
| 1823750 | 2024-02-08 | 16:27 | 2024-02-08 | 17:05 | CRM13 | CARRUM | Urban | Asset Failure | LV | 2 | 75.7666 | 37.8833 | 1 | No
| 1823736 | 2024-02-08 | 17:37 | 2024-02-08 | 20:25 | BT12 | BENTLEIGH | Urban | Overloads |  | 1 | 168 | 168 | 1 | No
| 1823771 | 2024-02-08 | 20:18 | 2024-02-08 | 21:10 | NO7 | NOTTING HILL | Urban | Animal | Animal impact | 8.71 | 444.5 | 51.0333 | 1 | No
| 1823782 | 2024-02-08 | 22:14 | 2024-02-08 | 23:28 | STO22 | SORRENTO | Urban | Asset Failure | LV | 1 | 73.3333 | 73.3333 | 1 | No
| 1823783 | 2024-02-08 | 23:00 | 2024-02-08 | 23:32 | EB24 | EAST BURWOOD | Urban | Overloads |  | 1 | 32.45 | 32.45 | 1 | No
| 1823784 | 2024-02-08 | 23:07 | 2024-03-08 | 1:45 | CRM35 | CARRUM | Urban | Third Party | Other | 1 | 157.5833 | 157.5833 | 1 | No
| 1823788 | 2024-03-08 | 2:47 | 2024-03-08 | 4:09 | CDA22 | CLARINDA | Urban | Asset Failure | LV | 1 | 81.3167 | 81.3167 | 1 | No
| 1823798 | 2024-03-08 | 5:17 | 2024-03-08 | 8:39 | EW14 | ELWOOD | Urban | Asset Failure | LV | 1 | 201.0667 | 201.0667 | 1 | No
| 1823941 | 2024-03-08 | 8:40 | 2024-03-08 | 22:30 | DVY12 | DANDENONG VALLEY | Urban | Asset Failure | LV | 37 | 30710 | 830 | 1 | No
| 1823901 | 2024-03-08 | 13:01 | 2024-03-08 | 15:26 | CRM23 | CARRUM | Urban | Asset Failure | LV | 18.15 | 2617.8344 | 144.2333 | 1 | No
| 1823919 | 2024-03-08 | 17:04 | 2024-03-08 | 19:37 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 153.5833 | 153.5833 | 1 | No
| 1823928 | 2024-03-08 | 18:18 | 2024-03-08 | 22:34 | RWT12 | RINGWOOD | Urban | Asset Failure | LV | 1 | 256.9333 | 256.9333 | 1 | No
| 1823953 | 2024-03-08 | 21:10 | 2024-03-08 | 21:35 | DC2 | DONCASTER | Urban | Asset Failure | LV | 87 | 2172.1029 | 24.9667 | 1 | No
| 1823962 | 2024-04-08 | 1:43 | 2024-04-08 | 2:00 | MR33 | MOORABBIN | Urban | Third Party | Vehicle Impact | 51 | 832.1517 | 16.3167 | 1 | No
| 1823963 | 2024-04-08 | 2:16 | 2024-04-08 | 3:29 | CDA11 | CLARINDA | Urban | Third Party | Other | 163 | 11956.05 | 73.35 | 1 | No
| 1823967 | 2024-04-08 | 3:28 | 2024-04-08 | 3:32 | CDA11 | CLARINDA | Urban | Third Party | Other | 289 | 1440.1737 | 4.9833 | 1 | No
| 1823982 | 2024-04-08 | 8:26 | 2024-04-08 | 11:27 | BU24 | BULLEEN | Urban | Asset Failure | LV | 42.24 | 7640.5106 | 180.8833 | 1 | No
| 1823987 | 2024-04-08 | 9:10 | 2024-04-08 | 10:57 | CM22 | CHELTENHAM | Urban | Asset Failure | LV | 1 | 106.5667 | 106.5667 | 1 | No
| 1823989 | 2024-04-08 | 10:16 | 2024-04-08 | 12:44 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 148.2 | 148.2 | 1 | No
| 1824009 | 2024-04-08 | 13:20 | 2024-04-08 | 17:40 | MR33 | MOORABBIN | Urban | Third Party | Other | 51 | 13260 | 260 | 1 | No
| 1824013 | 2024-04-08 | 15:25 | 2024-04-08 | 17:18 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1 | 113.9667 | 113.9667 | 1 | No
| 1824032 | 2024-04-08 | 19:55 | 2024-04-08 | 21:11 | NW14 | NUNAWADING | Urban | Asset Failure | LV | 1 | 75.6 | 75.6 | 1 | No
| 1824035 | 2024-04-08 | 20:23 | 2024-04-08 | 21:23 | LWN24 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 60.15 | 60.15 | 1 | No
| 1824044 | 2024-04-08 | 22:20 | 2024-05-08 | 7:52 | BT22 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 571.2 | 571.2 | 1 | No
| 1824181 | 2024-05-08 | 10:21 | 2024-05-08 | 13:32 | DVY24 | DANDENONG VALLEY | Rural Short | Unknown | Unknown | 26 | 4965.5658 | 190.9833 | 1 | No
| 1824167 | 2024-05-08 | 10:30 | 2024-05-08 | 13:04 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 50.49 | 7779.6658 | 154.0833 | 1 | No
| 1824175 | 2024-05-08 | 10:59 | 2024-05-08 | 12:04 | EL23 | ELSTERNWICK | Urban | Overloads |  | 15.84 | 1029.6 | 65 | 1 | No
| 1824212 | 2024-05-08 | 11:57 | 2024-05-08 | 14:10 | CDA11 | CLARINDA | Urban | Third Party | Other | 1 | 132.8833 | 132.8833 | 1 | No
| 1824291 | 2024-05-08 | 15:32 | 2024-05-08 | 17:09 | SVW45 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 97.2667 | 97.2667 | 1 | No
| 1824317 | 2024-05-08 | 18:04 | 2024-05-08 | 20:27 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 142.5 | 142.5 | 1 | No
| 1824023 | 2024-05-08 | 18:13 | 2024-05-08 | 21:30 | DMA24 | DROMANA | Rural Short | Unknown | Unknown | 1 | 197.7667 | 197.7667 | 1 | No
| 1824322 | 2024-05-08 | 18:28 | 2024-05-08 | 20:22 | MTN31 | MORNINGTON | Urban | Asset Failure | HV | 27.39 | 3109.6771 | 113.5333 | 1 | No
| 1824353 | 2024-06-08 | 0:58 | 2024-06-08 | 1:40 | EB31 | EAST BURWOOD | Urban | Animal | Animal impact | 79.06 | 3312.614 | 41.9 | 1 | No
| 1824358 | 2024-06-08 | 4:41 | 2024-06-08 | 9:49 | OR25 | ORMOND | Urban | Asset Failure | LV | 1 | 308.1333 | 308.1333 | 1 | No
| 1824477 | 2024-06-08 | 9:49 | 2024-06-08 | 12:03 | MGE34 | MULGRAVE | Urban | Unknown | Unknown | 1 | 133.3167 | 133.3167 | 1 | No
| 1824547 | 2024-06-08 | 12:26 | 2024-06-08 | 14:11 | FSH12 | FRANKSTON SOUTH | Rural Short | Overloads |  | 1 | 104.85 | 104.85 | 1 | No
| 1824565 | 2024-06-08 | 13:16 | 2024-06-08 | 14:30 | EB22 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 73.3667 | 73.3667 | 1 | No
| 1824627 | 2024-06-08 | 17:16 | 2024-06-08 | 19:52 | FTN11 | FRANKSTON | Urban | Asset Failure | Distribution substation | 22.44 | 3498.7707 | 155.9167 | 1 | No
| 1824631 | 2024-06-08 | 17:35 | 2024-07-08 | 3:50 | CRM35 | CARRUM | Urban | Asset Failure | LV | 8 | 4919.8664 | 614.9833 | 1 | No
| 1824640 | 2024-06-08 | 19:19 | 2024-06-08 | 22:26 | DMA21 | DROMANA | Urban | Asset Failure | LV | 2 | 375.1334 | 187.5667 | 1 | No
| 1824680 | 2024-07-08 | 7:17 | 2024-07-08 | 10:09 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 171.5 | 171.5 | 1 | No
| 1824766 | 2024-07-08 | 9:54 | 2024-07-08 | 12:50 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 175.75 | 175.75 | 1 | No
| 1824948 | 2024-07-08 | 12:55 | 2024-07-08 | 14:32 | GW2 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 96.8833 | 96.8833 | 1 | No
| 1824990 | 2024-07-08 | 14:44 | 2024-07-08 | 14:59 | HGS23 | HASTINGS | Rural Short | Other | XXX | 1 | 14.3667 | 14.3667 | 1 | No
| 1824995 | 2024-07-08 | 15:03 | 2024-07-08 | 15:32 | NW13 | NUNAWADING | Urban | Other | XXX | 1 | 28.5833 | 28.5833 | 1 | No
| 1825025 | 2024-07-08 | 17:49 | 2024-07-08 | 19:56 | RD4 | RIVERSDALE | Urban | Asset Failure | LV | 1 | 126.75 | 126.75 | 1 | No
| 1825029 | 2024-07-08 | 18:27 | 2024-07-08 | 21:00 | DN22 | DANDENONG | Urban | Asset Failure | LV | 1 | 152.75 | 152.75 | 1 | No
| 1825053 | 2024-07-08 | 22:02 | 2024-08-08 | 0:48 | DSH34 | DANDENONG SOUTH | Urban | Asset Failure | LV | 0.33 | 54.8625 | 166.25 | 1 | No
| 1825057 | 2024-07-08 | 23:11 | 2024-08-08 | 0:10 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 31.35 | 1847.559 | 58.9333 | 1 | No
| 1825056 | 2024-07-08 | 23:13 | 2024-08-08 | 0:26 | NP34 | NOBLE PARK | Urban | Animal | Animal impact | 5.36 | 391.4585 | 73.0333 | 1 | No
| 1825076 | 2024-08-08 | 7:20 | 2024-08-08 | 8:27 | NB31 | NORTH BRIGHTON | Urban | Third Party | Other | 1 | 66.5833 | 66.5833 | 1 | No
| 1825107 | 2024-08-08 | 8:25 | 2024-08-08 | 9:00 | EW8 | ELWOOD | Urban | Network Business | Switching and protection error | 125 | 4345.8375 | 34.7667 | 1 | No
| 1825169 | 2024-08-08 | 10:59 | 2024-08-08 | 12:30 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 36 | 3251.4012 | 90.3167 | 1 | No
| 1825251 | 2024-08-08 | 14:38 | 2024-08-08 | 20:30 | EB32 | EAST BURWOOD | Urban | Asset Failure | HV | 38 | 13360.8 | 351.6 | 1 | No
| 1825256 | 2024-08-08 | 14:51 | 2024-08-08 | 16:49 | BT12 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 117.95 | 117.95 | 1 | No
| 1825275 | 2024-08-08 | 16:26 | 2024-08-08 | 18:10 | BR9 | BEAUMARIS | Urban | Asset Failure | LV | 35 | 3624.8345 | 103.5667 | 1 | No
| 1825297 | 2024-08-08 | 19:10 | 2024-08-08 | 20:36 | LWN23 | LANGWARRIN | Urban | Animal | Animal impact | 343 | 29715.2219 | 86.6333 | 1 | No
| 1825329 | 2024-08-08 | 19:25 | 2024-08-08 | 20:39 | RWT23 | RINGWOOD | Urban | Animal | Animal impact | 6.03 | 445.3155 | 73.85 | 1 | No
| 1825338 | 2024-08-08 | 23:45 | 2024-09-08 | 0:10 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 9 | 225 | 25 | 1 | No
| 1825342 | 2024-09-08 | 0:59 | 2024-09-08 | 2:45 | KBH32 | KEYSBOROUGH | Urban | Third Party | Other | 14 | 1478.1662 | 105.5833 | 1 | No
| 1825352 | 2024-09-08 | 6:41 | 2024-09-08 | 8:26 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 104.1833 | 104.1833 | 1 | No
| 1825447 | 2024-09-08 | 10:06 | 2024-09-08 | 11:40 | DSH34 | DANDENONG SOUTH | Urban | Asset Failure | LV | 1 | 94.0667 | 94.0667 | 1 | No
| 1825491 | 2024-09-08 | 11:15 | 2024-09-08 | 13:45 | KBH31 | KEYSBOROUGH | Urban | Third Party | Other | 1 | 149.7333 | 149.7333 | 1 | No
| 1825507 | 2024-09-08 | 12:07 | 2024-09-08 | 15:19 | CRM22 | CARRUM | Urban | Asset Failure | LV | 1 | 192.1333 | 192.1333 | 1 | No
| 1825533 | 2024-09-08 | 13:19 | 2024-09-08 | 15:02 | DC2 | DONCASTER | Urban | Asset Failure | LV | 1 | 102.8833 | 102.8833 | 1 | No
| 1825544 | 2024-09-08 | 13:45 | 2024-09-08 | 14:19 | BW32 | BURWOOD | Urban | Overloads |  | 1 | 34.0667 | 34.0667 | 1 | No
| 1825581 | 2024-09-08 | 16:16 | 2024-09-08 | 16:42 | EB11 | EAST BURWOOD | Urban | Asset Failure | LV | 15 | 379.5 | 25.3 | 1 | No
| 1825607 | 2024-09-08 | 18:05 | 2024-09-08 | 19:37 | NW31 | NUNAWADING | Urban | Asset Failure | LV | 91 | 8399.3 | 92.3 | 1 | No
| 1825624 | 2024-09-08 | 23:03 | 2024-10-08 | 0:15 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 63 | 4536 | 72 | 1 | No
| 1825628 | 2024-09-08 | 23:18 | 2024-10-08 | 1:36 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 16 | 2209.8672 | 138.1167 | 1 | No
| 1825635 | 2024-10-08 | 3:05 | 2024-10-08 | 4:30 | CDA11 | CLARINDA | Urban | Animal | Animal impact | 60.3 | 5162.687 | 85.6167 | 1 | No
| 1825638 | 2024-10-08 | 6:21 | 2024-10-08 | 13:16 | FSH11 | FRANKSTON SOUTH | Urban | Third Party | Vehicle Impact | 11 | 4571.9663 | 415.6333 | 1 | No
| 1825636 | 2024-10-08 | 8:02 | 2024-10-08 | 11:00 | BC23 | BALACLAVA | Urban | Asset Failure | LV | 1 | 178 | 178 | 1 | No
| 1825652 | 2024-10-08 | 8:42 | 2024-10-08 | 9:45 | SR23 | SANDRINGHAM | Urban | Asset Failure | LV | 24.09 | 1517.67 | 63 | 1 | No
| 1825747 | 2024-10-08 | 22:23 | 2024-10-08 | 23:35 | CRM24 | CARRUM | Urban | Animal | Animal impact | 22.11 | 1583.8123 | 71.6333 | 1 | No
| 1825753 | 2024-11-08 | 0:49 | 2024-11-08 | 1:41 | SV33 | SPRINGVALE | Urban | Overloads |  | 1 | 52.85 | 52.85 | 1 | No
| 1825754 | 2024-11-08 | 7:43 | 2024-11-08 | 10:05 | NW21 | NUNAWADING | Urban | Third Party | Other | 1 | 142 | 142 | 1 | No
| 1825781 | 2024-11-08 | 10:41 | 2024-11-08 | 16:50 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 3 | 1104.6999 | 368.2333 | 1 | No
| 1825787 | 2024-11-08 | 11:16 | 2024-11-08 | 15:20 | BC23 | BALACLAVA | Urban | Asset Failure | LV | 1 | 243.9167 | 243.9167 | 1 | No
| 1825820 | 2024-11-08 | 16:21 | 2024-11-08 | 21:08 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 1 | 287.4667 | 287.4667 | 1 | No
| 1825836 | 2024-11-08 | 18:56 | 2024-11-08 | 20:30 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 94.0833 | 94.0833 | 1 | No
| 1825843 | 2024-11-08 | 22:13 | 2024-11-08 | 22:52 | GW10 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 39.2167 | 39.2167 | 1 | No
| 1825894 | 2024-12-08 | 8:15 | 2024-12-08 | 8:30 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 15.0333 | 15.0333 | 1 | No
| 1825927 | 2024-12-08 | 9:04 | 2024-12-08 | 10:52 | FSH32 | FRANKSTON SOUTH | Rural Short | Other | XXX | 1 | 107.5833 | 107.5833 | 1 | No
| 1825942 | 2024-12-08 | 9:27 | 2024-12-08 | 11:45 | KBH32 | KEYSBOROUGH | Urban | Third Party | Other | 14 | 1924.7662 | 137.4833 | 1 | No
| 1825980 | 2024-12-08 | 10:46 | 2024-12-08 | 12:30 | BH33 | BOX HILL | Urban | Other | XXX | 1 | 103.95 | 103.95 | 1 | No
| 1825849 | 2024-12-08 | 11:08 | 2024-12-08 | 11:41 | BW33 | BURWOOD | Urban | Overloads |  | 1 | 33.9667 | 33.9667 | 1 | No
| 1826035 | 2024-12-08 | 12:48 | 2024-12-08 | 13:52 | NB35 | NORTH BRIGHTON | Urban | Unknown | Unknown | 1 | 63.85 | 63.85 | 1 | No
| 1826074 | 2024-12-08 | 14:11 | 2024-12-08 | 15:26 | SH24 | SURREY HILLS | Urban | Third Party |  | 67 | 4961.35 | 74.05 | 1 | No
| 1826085 | 2024-12-08 | 14:45 | 2024-12-08 | 17:59 | NB35 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 193.7667 | 193.7667 | 1 | No
| 1826127 | 2024-12-08 | 18:24 | 2024-12-08 | 21:47 | LD6 | LYNDALE | Urban | Asset Failure | LV | 1 | 203.35 | 203.35 | 1 | No
| 1826281 | 13/08/2024 | 11:16 | 13/08/2024 | 14:40 | HGS31 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 204.7167 | 204.7167 | 1 | No
| 1826369 | 13/08/2024 | 16:19 | 13/08/2024 | 18:52 | EW1 | ELWOOD | Urban | Network Business | Switching and protection error | 1 | 152.2833 | 152.2833 | 1 | No
| 1826394 | 13/08/2024 | 19:51 | 13/08/2024 | 20:36 | K24 | GARDINER | Urban | Asset Failure | LV | 1 | 45 | 45 | 1 | No
| 1826408 | 13/08/2024 | 21:12 | 13/08/2024 | 22:08 | OE13 | OAKLEIGH EAST | Urban | Third Party | Vehicle Impact | 47 | 2649.2349 | 56.3667 | 1 | No
| 1826412 | 14/08/2024 | 0:12 | 14/08/2024 | 3:47 | MR11 | MOORABBIN | Urban | Asset Failure | LV | 1 | 215.5167 | 215.5167 | 1 | No
| 1826422 | 14/08/2024 | 2:17 | 14/08/2024 | 3:25 | FSH21 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 89.11 | 5973.3374 | 67.0333 | 1 | No
| 1826454 | 14/08/2024 | 7:04 | 14/08/2024 | 8:10 | SS12 | SPRINGVALE SOUTH | Urban | Animal | Animal impact | 1 | 65.2667 | 65.2667 | 1 | No
| 1826431 | 14/08/2024 | 11:32 | 14/08/2024 | 12:14 | MR15 | MOORABBIN | Urban | Asset Failure | LV | 1 | 42.5833 | 42.5833 | 1 | No
| 1826654 | 14/08/2024 | 13:06 | 14/08/2024 | 14:45 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 3.24 | 319.3561 | 98.5667 | 1 | No
| 1826714 | 14/08/2024 | 16:57 | 14/08/2024 | 20:20 | OR34 | ORMOND | Urban | Asset Failure | LV | 1 | 202.3667 | 202.3667 | 1 | No
| 1826723 | 14/08/2024 | 19:13 | 14/08/2024 | 19:20 | KBH31 | KEYSBOROUGH | Urban | Asset Failure | HV | 147 | 1031.4549 | 7.0167 | 1 | No
| 1826739 | 14/08/2024 | 20:25 | 14/08/2024 | 21:48 | DN8 | DANDENONG | Urban | Asset Failure | LV | 1 | 82.9833 | 82.9833 | 1 | No
| 1826741 | 14/08/2024 | 21:54 | 15/08/2024 | 0:17 | MR33 | MOORABBIN | Urban | Asset Failure | HV | 52 | 7429.0684 | 142.8667 | 1 | No
| 1826748 | 15/08/2024 | 0:55 | 15/08/2024 | 4:36 | M11 | MENTONE | Urban | Unknown | Unknown | 11.85 | 2626.1579 | 221.6167 | 1 | No
| 1826806 | 15/08/2024 | 8:19 | 15/08/2024 | 9:00 | STO13 | SORRENTO | Urban | Network Business | Switching and protection error | 15 | 601.9995 | 40.1333 | 1 | No
| 1826866 | 15/08/2024 | 9:26 | 15/08/2024 | 10:18 | EB33 | EAST BURWOOD | Urban | Third Party | Other | 1 | 52.25 | 52.25 | 1 | No
| 1826854 | 15/08/2024 | 12:18 | 15/08/2024 | 12:42 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 24.0667 | 24.0667 | 1 | No
| 1826954 | 15/08/2024 | 12:18 | 15/08/2024 | 13:21 | MC14 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 63.2667 | 63.2667 | 1 | No
| 1826998 | 15/08/2024 | 13:56 | 15/08/2024 | 16:49 | EM10 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 173 | 173 | 1 | No
| 1826759 | 15/08/2024 | 14:21 | 15/08/2024 | 17:02 | LD32 | LYNDALE | Urban | Asset Failure | LV | 1 | 161 | 161 | 1 | No
| 1827057 | 15/08/2024 | 19:18 | 15/08/2024 | 21:30 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 131.8167 | 131.8167 | 1 | No
| 1827076 | 16/08/2024 | 0:31 | 16/08/2024 | 17:56 | DN8 | DANDENONG | Urban | Third Party | Other | 19 | 19851.2 | 1044.8 | 1 | No
| 1827076 | 16/08/2024 | 0:31 | 16/08/2024 | 18:05 | DN8 | DANDENONG | Urban | Third Party | Other | 14 | 14755.5338 | 1053.9667 | 2 | No
| 1827080 | 16/08/2024 | 0:40 | 16/08/2024 | 2:05 | FSH12 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 2 | 170 | 85 | 1 | No
| 1827083 | 16/08/2024 | 1:18 | 16/08/2024 | 2:15 | RWT23 | RINGWOOD | Urban | Animal | Animal impact | 75.71 | 4278.8794 | 56.5167 | 1 | No
| 1827140 | 16/08/2024 | 7:49 | 16/08/2024 | 9:23 | NP23 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 94.5667 | 94.5667 | 1 | No
| 1827291 | 16/08/2024 | 12:28 | 16/08/2024 | 13:10 | FTN11 | FRANKSTON | Urban | Unknown | Unknown | 90 | 3735 | 41.5 | 1 | No
| 1827322 | 16/08/2024 | 14:16 | 16/08/2024 | 16:24 | CRM35 | CARRUM | Urban | Third Party | Vehicle Impact | 31 | 3955.6 | 127.6 | 1 | No
| 1827322 | 16/08/2024 | 14:16 | 16/08/2024 | 17:23 | CRM35 | CARRUM | Urban | Third Party | Vehicle Impact | 31 | 5777.8823 | 186.3833 | 2 | No
| 1827322 | 16/08/2024 | 14:16 | 16/08/2024 | 18:50 | CRM35 | CARRUM | Urban | Third Party | Vehicle Impact | 1 | 273.0833 | 273.0833 | 3 | No
| 1827370 | 16/08/2024 | 17:06 | 16/08/2024 | 21:14 | LD7 | LYNDALE | Urban | Third Party | Other | 3 | 743.6001 | 247.8667 | 1 | No
| 1827383 | 16/08/2024 | 17:43 | 16/08/2024 | 18:49 | CRM35 | CARRUM | Urban | Asset Failure | HV | 1 | 65.15 | 65.15 | 1 | No
| 1827384 | 16/08/2024 | 17:46 | 16/08/2024 | 18:53 | CRM35 | CARRUM | Urban | Third Party | Vehicle Impact | 1 | 66.8833 | 66.8833 | 1 | No
| 1827397 | 16/08/2024 | 18:41 | 16/08/2024 | 20:49 | LWN33 | LANGWARRIN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 127.35 | 127.35 | 1 | No
| 1827406 | 16/08/2024 | 19:21 | 16/08/2024 | 21:40 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 138.0833 | 138.0833 | 1 | No
| 1827413 | 16/08/2024 | 21:46 | 16/08/2024 | 22:43 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 56.95 | 56.95 | 1 | No
| 1827472 | 17/08/2024 | 15:49 | 17/08/2024 | 16:00 | FSH34 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 1 | 10.0167 | 10.0167 | 1 | No
| 1827485 | 17/08/2024 | 19:54 | 17/08/2024 | 21:54 | DC8 | DONCASTER | Urban | Asset Failure | LV | 20.13 | 2422.6455 | 120.35 | 1 | No
| 1827486 | 17/08/2024 | 21:13 | 17/08/2024 | 23:20 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 127 | 127 | 1 | No
| 1827490 | 17/08/2024 | 22:27 | 18/08/2024 | 9:45 | LD32 | LYNDALE | Urban | Asset Failure | LV | 2 | 1355.9334 | 677.9667 | 1 | No
| 1827505 | 18/08/2024 | 5:53 | 18/08/2024 | 7:41 | SV33 | SPRINGVALE | Urban | Animal | Animal impact | 133.32 | 14385.228 | 107.9 | 1 | No
| 1827528 | 18/08/2024 | 12:06 | 18/08/2024 | 13:13 | NW13 | NUNAWADING | Urban | Asset Failure | LV | 1 | 66.4167 | 66.4167 | 1 | No
| 1827539 | 18/08/2024 | 14:59 | 18/08/2024 | 17:42 | BU22 | BULLEEN | Urban | Asset Failure | LV | 1 | 163.5667 | 163.5667 | 1 | No
| 1827553 | 18/08/2024 | 17:18 | 18/08/2024 | 17:45 | FSH13 | FRANKSTON SOUTH | Urban | Network Business | Switching and protection error | 1 | 26.2833 | 26.2833 | 1 | No
| 1827554 | 18/08/2024 | 17:20 | 18/08/2024 | 17:45 | FSH13 | FRANKSTON SOUTH | Urban | Network Business | Switching and protection error | 1 | 24.1833 | 24.1833 | 1 | No
| 1827584 | 18/08/2024 | 22:46 | 19/08/2024 | 1:45 | FTN11 | FRANKSTON | Urban | Unknown | Unknown | 16 | 2864 | 179 | 1 | No
| 1827571 | 18/08/2024 | 23:19 | 19/08/2024 | 0:28 | NW13 | NUNAWADING | Urban | Asset Failure | LV | 1 | 69.0333 | 69.0333 | 1 | No
| 1827634 | 19/08/2024 | 5:21 | 19/08/2024 | 10:37 | HGS22 | HASTINGS | Rural Short | Animal | Other | 6 | 1892.5998 | 315.4333 | 1 | No
| 1827635 | 19/08/2024 | 5:21 | 19/08/2024 | 8:45 | HGS22 | HASTINGS | Rural Short | Asset Failure | HV | 30.15 | 6133.514 | 203.4333 | 1 | No
| 1827589 | 19/08/2024 | 5:37 | 19/08/2024 | 10:37 | HGS22 | HASTINGS | Rural Short | Animal | Animal impact | 3 | 900 | 300 | 1 | No
| 1827604 | 19/08/2024 | 6:38 | 19/08/2024 | 9:09 | CRM15 | CARRUM | Urban | Unknown | Unknown | 60.3 | 9065.098 | 150.3333 | 1 | No
| 1827618 | 19/08/2024 | 7:36 | 19/08/2024 | 8:25 | DN25 | DANDENONG | Urban | Unknown | Unknown | 10.56 | 508.1124 | 48.1167 | 1 | No
| 1827698 | 19/08/2024 | 9:53 | 19/08/2024 | 10:37 | HGS22 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 43.8833 | 43.8833 | 1 | No
| 1827733 | 19/08/2024 | 11:12 | 19/08/2024 | 12:30 | DC12 | DONCASTER | Urban | Asset Failure | LV | 1 | 77.8833 | 77.8833 | 1 | No
| 1827767 | 19/08/2024 | 12:02 | 19/08/2024 | 12:12 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 6.93 | 70.5703 | 10.1833 | 1 | No
| 1827767 | 19/08/2024 | 12:02 | 19/08/2024 | 12:21 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 19.8 | 380.4907 | 19.2167 | 2 | No
| 1827665 | 19/08/2024 | 12:06 | 19/08/2024 | 13:50 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 104 | 104 | 1 | No
| 1827782 | 19/08/2024 | 12:37 | 19/08/2024 | 13:26 | DC8 | DONCASTER | Urban | Third Party | Other | 1 | 49.6167 | 49.6167 | 1 | No
| 1827797 | 19/08/2024 | 13:52 | 19/08/2024 | 15:41 | GW7 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 109.4333 | 109.4333 | 1 | No
| 1827855 | 19/08/2024 | 17:28 | 19/08/2024 | 18:39 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 1 | 71.85 | 71.85 | 1 | No
| 1827931 | 20/08/2024 | 7:05 | 20/08/2024 | 8:36 | LD7 | LYNDALE | Urban | Animal | Other | 0.67 | 60.9142 | 90.9167 | 1 | No
| 1827915 | 20/08/2024 | 7:12 | 20/08/2024 | 9:02 | RWT35 | RINGWOOD | Urban | Unknown | Unknown | 0.67 | 74.1467 | 110.6667 | 1 | No
| 1827921 | 20/08/2024 | 7:38 | 20/08/2024 | 8:28 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 81 | 3974.4027 | 49.0667 | 1 | No
| 1827930 | 20/08/2024 | 7:58 | 20/08/2024 | 10:23 | DC4 | DONCASTER | Urban | Animal | Animal impact | 12.87 | 1872.1564 | 145.4667 | 1 | No
| 1827957 | 20/08/2024 | 8:48 | 20/08/2024 | 11:25 | LD5 | LYNDALE | Urban | Asset Failure | LV | 1 | 156.8833 | 156.8833 | 1 | No
| 1828085 | 20/08/2024 | 14:01 | 20/08/2024 | 16:21 | FTN11 | FRANKSTON | Urban | Third Party | Other | 12 | 1685.4 | 140.45 | 1 | No
| 1828137 | 20/08/2024 | 17:41 | 20/08/2024 | 18:30 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 48.2333 | 48.2333 | 1 | No
| 1828182 | 21/08/2024 | 5:22 | 21/08/2024 | 13:13 | WD16 | WEST DONCASTER | Urban | Third Party | Other | 42.88 | 20206.4839 | 471.2333 | 1 | No
| 1828170 | 21/08/2024 | 6:58 | 21/08/2024 | 8:35 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 97.85 | 97.85 | 1 | No
| 1828212 | 21/08/2024 | 8:13 | 21/08/2024 | 9:55 | RBD24 | ROSEBUD | Urban | Asset Failure | LV | 1 | 102.1667 | 102.1667 | 1 | No
| 1828220 | 21/08/2024 | 8:27 | 21/08/2024 | 10:11 | EB33 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 103.1167 | 103.1167 | 1 | No
| 1828432 | 21/08/2024 | 16:01 | 21/08/2024 | 20:55 | HGS31 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 294.55 | 294.55 | 1 | No
| 1828413 | 21/08/2024 | 16:06 | 21/08/2024 | 19:30 | LWN35 | LANGWARRIN | Urban | Unknown | Unknown | 1 | 204.1833 | 204.1833 | 1 | No
| 1828454 | 21/08/2024 | 17:27 | 21/08/2024 | 20:00 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 13 | 1984.6671 | 152.6667 | 1 | No
| 1828476 | 21/08/2024 | 20:11 | 21/08/2024 | 21:32 | OAK26 | OAKLEIGH | Urban | Third Party | Vehicle Impact | 1 | 81.4167 | 81.4167 | 1 | No
| 1828485 | 21/08/2024 | 21:59 | 21/08/2024 | 23:54 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 8.91 | 1023.759 | 114.9 | 1 | No
| 1828678 | 22/08/2024 | 14:21 | 22/08/2024 | 16:30 | FTN25 | FRANKSTON | Urban | Unknown | Unknown | 1 | 129.75 | 129.75 | 1 | No
| 1828714 | 22/08/2024 | 14:23 | 22/08/2024 | 15:45 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 3 | 244.35 | 81.45 | 1 | No
| 1828738 | 22/08/2024 | 16:41 | 22/08/2024 | 18:12 | FSH13 | FRANKSTON SOUTH | Urban | Other | XXX | 1 | 90.4833 | 90.4833 | 1 | No
| 1828750 | 22/08/2024 | 17:55 | 22/08/2024 | 22:53 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 297.6 | 297.6 | 1 | No
| 1828756 | 22/08/2024 | 18:57 | 22/08/2024 | 22:49 | NW33 | NUNAWADING | Urban | Asset Failure | LV | 1 | 232.0667 | 232.0667 | 1 | No
| 1828897 | 23/08/2024 | 9:39 | 23/08/2024 | 10:35 | NW21 | NUNAWADING | Urban | Animal | Animal impact | 1 | 56 | 56 | 1 | No
| 1828918 | 23/08/2024 | 11:02 | 23/08/2024 | 13:50 | SH22 | SURREY HILLS | Urban | Third Party | Other | 1 | 167.7667 | 167.7667 | 1 | No
| 1828955 | 23/08/2024 | 12:06 | 23/08/2024 | 14:07 | EB33 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 120.7667 | 120.7667 | 1 | No
| 1828966 | 23/08/2024 | 12:41 | 23/08/2024 | 15:55 | HT4 | HEATHERTON | Urban | Third Party | Other | 1 | 193.9333 | 193.9333 | 1 | No
| 1829019 | 23/08/2024 | 16:31 | 23/08/2024 | 18:19 | M11 | MENTONE | Urban | Asset Failure | LV | 1 | 107.7833 | 107.7833 | 1 | No
| 1829026 | 23/08/2024 | 17:56 | 23/08/2024 | 19:36 | KBH32 | KEYSBOROUGH | Urban | Asset Failure | HV | 1 | 100.25 | 100.25 | 1 | No
| 1828971 | 23/08/2024 | 18:25 | 23/08/2024 | 19:48 | NO7 | NOTTING HILL | Urban | Asset Failure | LV | 1 | 83.1833 | 83.1833 | 1 | No
| 1829054 | 24/08/2024 | 1:35 | 24/08/2024 | 2:53 | BW32 | BURWOOD | Urban | Animal | Animal impact | 18.76 | 1450.4613 | 77.3167 | 1 | No
| 1829058 | 24/08/2024 | 1:46 | 24/08/2024 | 4:30 | DVY21 | DANDENONG VALLEY | Urban | Weather |  | 14 | 2286.2 | 163.3 | 1 | No
| 1829072 | 24/08/2024 | 5:16 | 24/08/2024 | 13:58 | BT12 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 521.7333 | 521.7333 | 1 | No
| 1829077 | 24/08/2024 | 6:25 | 24/08/2024 | 11:47 | NP24 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 322.25 | 322.25 | 1 | No
| 1829112 | 24/08/2024 | 10:30 | 24/08/2024 | 11:25 | M13 | MENTONE | Urban | Asset Failure | LV | 3.6 | 198 | 55 | 1 | No
| 1829049 | 24/08/2024 | 11:40 | 24/08/2024 | 15:13 | SV32 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 213 | 213 | 1 | No
| 1829153 | 24/08/2024 | 12:33 | 24/08/2024 | 14:00 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 87 | 87 | 1 | No
| 1829135 | 24/08/2024 | 17:45 | 24/08/2024 | 19:37 | NP33 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 112.9 | 112.9 | 1 | No
| 1829213 | 25/08/2024 | 0:32 | 25/08/2024 | 1:35 | GW3 | GLEN WAVERLEY | Urban | Third Party | Other | 8 | 498.1336 | 62.2667 | 1 | No
| 1829213 | 25/08/2024 | 0:32 | 25/08/2024 | 1:38 | GW3 | GLEN WAVERLEY | Urban | Third Party | Other | 2 | 130.5334 | 65.2667 | 2 | No
| 1829213 | 25/08/2024 | 0:32 | 26/08/2024 | 13:00 | GW3 | GLEN WAVERLEY | Urban | Third Party | Other | 5 | 10936.3335 | 2187.2667 | 3 | No
| 1829218 | 25/08/2024 | 4:51 | 25/08/2024 | 6:00 | LWN21 | LANGWARRIN | Rural Short | Animal | Animal impact | 6 | 410.5998 | 68.4333 | 1 | No
| 1829221 | 25/08/2024 | 6:03 | 25/08/2024 | 8:23 | BH33 | BOX HILL | Urban | Asset Failure | LV | 1 | 139.2 | 139.2 | 1 | No
| 1829222 | 25/08/2024 | 6:13 | 25/08/2024 | 7:30 | FSH32 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 0.67 | 51.2997 | 76.5667 | 1 | No
| 1829208 | 25/08/2024 | 8:53 | 25/08/2024 | 10:54 | DN22 | DANDENONG | Urban | Third Party | Other | 1 | 121.4667 | 121.4667 | 1 | No
| 1829270 | 25/08/2024 | 12:55 | 25/08/2024 | 14:15 | BU21 | BULLEEN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 12.21 | 974.358 | 79.8 | 1 | No
| 1829280 | 25/08/2024 | 14:53 | 25/08/2024 | 16:00 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 67 | 67 | 1 | No
| 1829288 | 25/08/2024 | 15:44 | 25/08/2024 | 19:15 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 14.58 | 3072.2495 | 210.7167 | 1 | No
| 1829290 | 25/08/2024 | 16:39 | 25/08/2024 | 20:05 | FSH33 | FRANKSTON SOUTH | Urban | Weather |  | 1 | 206 | 206 | 1 | No
| 1829327 | 25/08/2024 | 18:57 | 25/08/2024 | 19:59 | NW33 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 62.0833 | 62.0833 | 1 | No
| 1829320 | 25/08/2024 | 19:43 | 25/08/2024 | 21:06 | BU11 | BULLEEN | Urban | Weather |  | 9.24 | 771.3857 | 83.4833 | 1 | No
| 1829350 | 25/08/2024 | 21:48 | 25/08/2024 | 22:55 | DC1 | DONCASTER | Urban | Animal | Animal impact | 39 | 2580.5013 | 66.1667 | 1 | No
| 1829315 | 25/08/2024 | 22:37 | 26/08/2024 | 0:20 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 3.3 | 339.9 | 103 | 1 | No
| 1829364 | 26/08/2024 | 3:27 | 26/08/2024 | 4:36 | DC1 | DONCASTER | Urban | Animal | Animal impact | 39 | 2691 | 69 | 1 | No
| 1829371 | 26/08/2024 | 7:25 | 26/08/2024 | 8:37 | EM11 | EAST MALVERN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 72.4 | 72.4 | 1 | No
| 1829419 | 26/08/2024 | 8:03 | 26/08/2024 | 12:00 | DSH33 | DANDENONG SOUTH | Urban | Third Party | Other | 1 | 236.3 | 236.3 | 1 | No
| 1829443 | 26/08/2024 | 10:37 | 26/08/2024 | 13:20 | MTN32 | MORNINGTON | Rural Short | Weather |  | 0.67 | 108.9643 | 162.6333 | 1 | No
| 1829463 | 26/08/2024 | 11:10 | 26/08/2024 | 13:30 | CFD23 | CAULFIELD | Urban | Third Party | Vehicle Impact | 1 | 139.05 | 139.05 | 1 | No
| 1829464 | 26/08/2024 | 11:13 | 26/08/2024 | 13:56 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 163.7833 | 163.7833 | 1 | No
| 1829547 | 26/08/2024 | 16:51 | 27/08/2024 | 0:20 | MGE21 | MULGRAVE | Urban | Asset Failure | HV | 2 | 897.5334 | 448.7667 | 1 | No
| 1829562 | 26/08/2024 | 18:32 | 26/08/2024 | 19:57 | BU25 | BULLEEN | Urban | Asset Failure | LV | 21.45 | 1833.6168 | 85.4833 | 1 | No
| 1829571 | 26/08/2024 | 19:17 | 26/08/2024 | 21:17 | EL26 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 119.4667 | 119.4667 | 1 | No
| 1829528 | 26/08/2024 | 22:57 | 27/08/2024 | 3:10 | MGE23 | MULGRAVE | Urban | Asset Failure | LV | 34 | 8602 | 253 | 1 | No
| 1829600 | 27/08/2024 | 1:52 | 27/08/2024 | 2:09 | DMA21 | DROMANA | Urban | Unknown | Unknown | 7 | 114.5669 | 16.3667 | 1 | No
| 1829602 | 27/08/2024 | 9:03 | 27/08/2024 | 10:37 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 94.4333 | 94.4333 | 1 | No
| 1829749 | 27/08/2024 | 10:48 | 27/08/2024 | 13:00 | FSH22 | FRANKSTON SOUTH | Urban | Animal | Other | 1 | 131.2833 | 131.2833 | 1 | No
| 1829783 | 27/08/2024 | 12:37 | 27/08/2024 | 14:59 | MC21 | MORDIALLOC | Urban | Third Party | Other | 1 | 142.5333 | 142.5333 | 1 | No
| 1829800 | 27/08/2024 | 13:48 | 27/08/2024 | 15:20 | MTN21 | MORNINGTON | Urban | Overloads |  | 1 | 92 | 92 | 1 | No
| 1829845 | 27/08/2024 | 15:45 | 27/08/2024 | 16:57 | EB31 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 72.3667 | 72.3667 | 1 | No
| 1829826 | 27/08/2024 | 15:54 | 27/08/2024 | 16:59 | CRM15 | CARRUM | Urban | Asset Failure | LV | 1 | 65.6167 | 65.6167 | 1 | No
| 1829893 | 27/08/2024 | 19:11 | 27/08/2024 | 19:50 | GW8 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 39.1667 | 39.1667 | 1 | No
| 1829902 | 27/08/2024 | 20:08 | 28/08/2024 | 12:01 | RBD12 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 89 | 84793.2637 | 952.7333 | 1 | No
| 1829913 | 27/08/2024 | 21:27 | 27/08/2024 | 22:56 | HGS21 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 499 | 44277.9167 | 88.7333 | 1 | No
| 1829934 | 27/08/2024 | 21:43 | 28/08/2024 | 1:26 | CM25 | CHELTENHAM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 113 | 25195.2371 | 222.9667 | 1 | No
| 1829941 | 27/08/2024 | 22:34 | 27/08/2024 | 23:05 | GW7 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1205 | 36692.25 | 30.45 | 1 | No
| 1829942 | 27/08/2024 | 22:34 | 27/08/2024 | 23:46 | GW12 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1308 | 93216.8436 | 71.2667 | 1 | No
| 1829942 | 27/08/2024 | 22:34 | 27/08/2024 | 23:47 | GW12 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1012 | 73724.2 | 72.85 | 2 | No
| 1829942 | 27/08/2024 | 22:34 | 27/08/2024 | 23:06 | GW2 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 2199 | 70294.7733 | 31.9667 | 1 | No
| 1829942 | 27/08/2024 | 22:34 | 27/08/2024 | 23:54 | GW2 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 238 | 18829.7746 | 79.1167 | 2 | No
| 1829942 | 27/08/2024 | 22:34 | 28/08/2024 | 0:25 | GW2 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 246 | 27248.6082 | 110.7667 | 3 | No
| 1829954 | 27/08/2024 | 22:35 | 28/08/2024 | 1:35 | NW14 | NUNAWADING | Urban | Asset Failure | HV | 19.43 | 3492.5425 | 179.75 | 1 | No
| 1829952 | 27/08/2024 | 23:02 | 28/08/2024 | 1:00 | CRM33 | CARRUM | Urban | Asset Failure | LV | 10.72 | 1264.424 | 117.95 | 1 | No
| 1829951 | 27/08/2024 | 23:04 | 28/08/2024 | 8:50 | OAK23 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 586.15 | 586.15 | 1 | No
| 1829950 | 27/08/2024 | 23:28 | 28/08/2024 | 2:47 | DN10 | DANDENONG | Urban | Asset Failure | LV | 1 | 199.15 | 199.15 | 1 | No
| 1829967 | 28/08/2024 | 1:52 | 28/08/2024 | 2:21 | K27 | GARDINER | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1293 | 38165.0931 | 29.5167 | 1 | Yes
| 1829970 | 28/08/2024 | 2:25 | 28/08/2024 | 4:35 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 39 | 5081.0487 | 130.2833 | 1 | Yes
| 1829978 | 28/08/2024 | 3:00 | 28/08/2024 | 4:11 | DC5 | DONCASTER | Urban | Asset Failure | LV | 78 | 5518.5 | 70.75 | 1 | Yes
| 1829975 | 28/08/2024 | 6:44 | 28/08/2024 | 8:09 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 85.6833 | 85.6833 | 1 | Yes
| 1829983 | 28/08/2024 | 6:59 | 28/08/2024 | 9:44 | BW21 | BURWOOD | Urban | Asset Failure | LV | 1 | 165.2333 | 165.2333 | 1 | Yes
| 1830107 | 28/08/2024 | 10:09 | 28/08/2024 | 11:55 | GW8 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 105.6333 | 105.6333 | 1 | Yes
| 1829985 | 28/08/2024 | 10:25 | 28/08/2024 | 13:44 | MC23 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 199.1833 | 199.1833 | 1 | Yes
| 1830117 | 28/08/2024 | 10:58 | 28/08/2024 | 16:36 | OE2 | OAKLEIGH EAST | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 338 | 338 | 1 | Yes
| 1830152 | 28/08/2024 | 11:23 | 28/08/2024 | 11:47 | LD6 | LYNDALE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 466 | 11261.6822 | 24.1667 | 1 | Yes
| 1830152 | 28/08/2024 | 11:23 | 28/08/2024 | 12:16 | LD6 | LYNDALE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 385 | 20642.4295 | 53.6167 | 2 | Yes
| 1830191 | 28/08/2024 | 12:16 | 28/08/2024 | 12:20 | CDA23 | CLARINDA | Urban | Unknown | Unknown | 1 | 3.3 | 3.3 | 1 | Yes
| 1830194 | 28/08/2024 | 12:21 | 28/08/2024 | 13:30 | DC4 | DONCASTER | Urban | Weather |  | 15.84 | 1081.872 | 68.3 | 1 | Yes
| 1830059 | 28/08/2024 | 12:39 | 28/08/2024 | 15:45 | MC15 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 186 | 186 | 1 | Yes
| 1830207 | 28/08/2024 | 12:44 | 29/08/2024 | 9:49 | EL35 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 1265.4667 | 1265.4667 | 1 | Yes
| 1830218 | 28/08/2024 | 13:09 | 28/08/2024 | 15:00 | DC10 | DONCASTER | Urban | Asset Failure | LV | 213 | 23575.5429 | 110.6833 | 1 | Yes
| 1830223 | 28/08/2024 | 13:22 | 28/08/2024 | 14:41 | EB32 | EAST BURWOOD | Urban | Asset Failure | LV | 20.96 | 1667.368 | 79.55 | 1 | Yes
| 1830232 | 28/08/2024 | 13:35 | 28/08/2024 | 17:30 | DC10 | DONCASTER | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 234.4333 | 234.4333 | 1 | Yes
| 1830236 | 28/08/2024 | 13:46 | 29/08/2024 | 9:30 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 1183.3667 | 1183.3667 | 1 | Yes
| 1830259 | 28/08/2024 | 14:25 | 28/08/2024 | 14:39 | GW7 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1205 | 17030.6265 | 14.1333 | 1 | Yes
| 1830259 | 28/08/2024 | 14:25 | 28/08/2024 | 15:35 | GW7 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1246 | 86783.9 | 69.65 | 2 | Yes
| 1830168 | 28/08/2024 | 14:29 | 28/08/2024 | 22:07 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 458.85 | 458.85 | 1 | Yes
| 1830262 | 28/08/2024 | 14:31 | 28/08/2024 | 15:04 | SR21 | SANDRINGHAM | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 998 | 33250.0666 | 33.3167 | 1 | Yes
| 1830262 | 28/08/2024 | 14:31 | 28/08/2024 | 18:07 | SR21 | SANDRINGHAM | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 389 | 84212.0037 | 216.4833 | 2 | Yes
| 1830262 | 28/08/2024 | 14:31 | 28/08/2024 | 14:36 | SR36 | SANDRINGHAM | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 375 | 1931.25 | 5.15 | 1 | Yes
| 1830262 | 28/08/2024 | 14:31 | 28/08/2024 | 15:06 | SR36 | SANDRINGHAM | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 906 | 32298.9 | 35.65 | 2 | Yes
| 1830497 | 28/08/2024 | 14:35 | 28/08/2024 | 19:13 | SR21 | SANDRINGHAM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 39 | 10827.6987 | 277.6333 | 1 | Yes
| 1830270 | 28/08/2024 | 14:39 | 28/08/2024 | 16:19 | MTN32 | MORNINGTON | Rural Short | Weather |  | 23 | 2296.9341 | 99.8667 | 1 | Yes
| 1830275 | 28/08/2024 | 15:15 | 28/08/2024 | 19:22 | STO13 | SORRENTO | Urban | Unknown | Unknown | 498 | 123379.5 | 247.75 | 1 | Yes
| 1830275 | 28/08/2024 | 15:15 | 28/08/2024 | 19:44 | STO13 | SORRENTO | Urban | Unknown | Unknown | 248 | 66935.2 | 269.9 | 2 | Yes
| 1830319 | 28/08/2024 | 15:16 | 28/08/2024 | 20:45 | STO13 | SORRENTO | Urban | Weather |  | 60 | 19683 | 328.05 | 1 | Yes
| 1830321 | 28/08/2024 | 15:22 | 28/08/2024 | 22:20 | STO13 | SORRENTO | Urban | Weather |  | 42.88 | 17914.5479 | 417.7833 | 1 | Yes
| 1830326 | 28/08/2024 | 15:29 | 28/08/2024 | 18:05 | RBD13 | ROSEBUD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 436 | 68008.7188 | 155.9833 | 1 | Yes
| 1830648 | 28/08/2024 | 15:30 | 29/08/2024 | 14:33 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 1383.3167 | 1383.3167 | 1 | Yes
| 1830283 | 28/08/2024 | 15:32 | 28/08/2024 | 15:37 | HGS21 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 535 | 2568 | 4.8 | 1 | Yes
| 1830283 | 28/08/2024 | 15:32 | 28/08/2024 | 16:32 | HGS21 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 242 | 14616.8 | 60.4 | 2 | Yes
| 1830283 | 28/08/2024 | 15:32 | 28/08/2024 | 16:34 | HGS21 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 205 | 12621.1735 | 61.5667 | 3 | Yes
| 1830283 | 28/08/2024 | 15:32 | 28/08/2024 | 16:35 | HGS21 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1267 | 79588.7589 | 62.8167 | 4 | Yes
| 1830283 | 28/08/2024 | 15:32 | 28/08/2024 | 18:16 | HGS21 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 354 | 58073.7 | 164.05 | 5 | Yes
| 1830283 | 28/08/2024 | 15:32 | 28/08/2024 | 18:29 | HGS21 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 377 | 66710.15 | 176.95 | 6 | Yes
| 1830283 | 28/08/2024 | 15:32 | 28/08/2024 | 18:42 | HGS21 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 171 | 32569.8057 | 190.4667 | 7 | Yes
| 1830283 | 28/08/2024 | 15:32 | 28/08/2024 | 20:04 | HGS21 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 24 | 6538.0008 | 272.4167 | 8 | Yes
| 1830284 | 28/08/2024 | 15:32 | 28/08/2024 | 17:47 | HGS23 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 183 | 24781.2561 | 135.4167 | 1 | Yes
| 1830284 | 28/08/2024 | 15:32 | 28/08/2024 | 20:17 | HGS23 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 38 | 10843.3 | 285.35 | 2 | Yes
| 1830285 | 28/08/2024 | 15:35 | 28/08/2024 | 15:58 | DMA23 | DROMANA | Rural Short | Weather |  | 1106 | 25825.1 | 23.35 | 1 | Yes
| 1830285 | 28/08/2024 | 15:35 | 28/08/2024 | 16:00 | DMA23 | DROMANA | Rural Short | Weather |  | 376 | 9280.9208 | 24.6833 | 2 | Yes
| 1830285 | 28/08/2024 | 15:35 | 28/08/2024 | 16:07 | DMA23 | DROMANA | Rural Short | Weather |  | 124 | 4017.6 | 32.4 | 3 | Yes
| 1830285 | 28/08/2024 | 15:35 | 28/08/2024 | 17:10 | DMA23 | DROMANA | Rural Short | Weather |  | 117 | 11144.25 | 95.25 | 4 | Yes
| 1830285 | 28/08/2024 | 15:35 | 28/08/2024 | 17:43 | DMA23 | DROMANA | Rural Short | Weather |  | 88 | 11249.3304 | 127.8333 | 5 | Yes
| 1830285 | 28/08/2024 | 15:35 | 28/08/2024 | 17:51 | DMA23 | DROMANA | Rural Short | Weather |  | 36 | 4888.8 | 135.8 | 6 | Yes
| 1830337 | 28/08/2024 | 15:41 | 28/08/2024 | 23:50 | M25 | MENTONE | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 24.48 | 11947.0552 | 488.0333 | 1 | Yes
| 1830410 | 28/08/2024 | 15:42 | 29/08/2024 | 5:22 | HGS33 | HASTINGS | Rural Short | Unknown | Unknown | 44 | 36061.6652 | 819.5833 | 1 | Yes
| 1830348 | 28/08/2024 | 15:47 | 29/08/2024 | 2:26 | SS14 | SPRINGVALE SOUTH | Urban | Weather |  | 30 | 19158.501 | 638.6167 | 1 | Yes
| 1830284 | 28/08/2024 | 15:51 | 28/08/2024 | 16:59 | HGS23 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 740 | 50369.358 | 68.0667 | 1 | Yes
| 1830284 | 28/08/2024 | 15:51 | 28/08/2024 | 17:02 | HGS23 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 144 | 10207.1952 | 70.8833 | 2 | Yes
| 1830302 | 28/08/2024 | 15:51 | 28/08/2024 | 15:59 | MTN32 | MORNINGTON | Rural Short | Weather |  | 534 | 4272 | 8 | 1 | Yes
| 1830302 | 28/08/2024 | 15:51 | 28/08/2024 | 16:08 | MTN32 | MORNINGTON | Rural Short | Weather |  | 2023 | 34256.0659 | 16.9333 | 2 | Yes
| 1830302 | 28/08/2024 | 15:51 | 28/08/2024 | 16:19 | MTN32 | MORNINGTON | Rural Short | Weather |  | 108 | 2991.6 | 27.7 | 3 | Yes
| 1830302 | 28/08/2024 | 15:51 | 28/08/2024 | 16:20 | MTN32 | MORNINGTON | Rural Short | Weather |  | 39 | 1124.4987 | 28.8333 | 4 | Yes
| 1830302 | 28/08/2024 | 15:51 | 28/08/2024 | 17:50 | MTN32 | MORNINGTON | Rural Short | Weather |  | 158 | 18823.0614 | 119.1333 | 5 | Yes
| 1830307 | 28/08/2024 | 16:00 | 29/08/2024 | 3:03 | HGS33 | HASTINGS | Rural Short | Unknown | Unknown | 0 | 663 | 663 | 1 | Yes
| 1830310 | 28/08/2024 | 16:03 | 28/08/2024 | 16:19 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 93 | 1480.2531 | 15.9167 | 1 | Yes
| 1830310 | 28/08/2024 | 16:03 | 28/08/2024 | 22:36 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 52 | 20409.1316 | 392.4833 | 2 | Yes
| 1830370 | 28/08/2024 | 16:05 | 29/08/2024 | 12:48 | CM22 | CHELTENHAM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 52 | 64622.1316 | 1242.7333 | 1 | Yes
| 1830341 | 28/08/2024 | 16:07 | 28/08/2024 | 19:43 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 107.87 | 23341.2666 | 216.3833 | 1 | Yes
| 1830350 | 28/08/2024 | 16:08 | 28/08/2024 | 20:47 | NW32 | NUNAWADING | Urban | Weather |  | 52.47 | 14639.13 | 279 | 1 | Yes
| 1830358 | 28/08/2024 | 16:28 | 28/08/2024 | 19:37 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 18.48 | 3495.492 | 189.15 | 1 | Yes
| 1830647 | 28/08/2024 | 16:32 | 29/08/2024 | 3:47 | HGS33 | HASTINGS | Rural Short | Unknown | Unknown | 3 | 2025 | 675 | 1 | Yes
| 1830372 | 28/08/2024 | 16:33 | 28/08/2024 | 17:14 | GW7 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1246 | 51605.2082 | 41.4167 | 1 | Yes
| 1830377 | 28/08/2024 | 16:35 | 28/08/2024 | 16:57 | GW4 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 276 | 6053.5908 | 21.9333 | 1 | Yes
| 1830377 | 28/08/2024 | 16:35 | 28/08/2024 | 17:28 | GW4 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 521 | 27673.8007 | 53.1167 | 2 | Yes
| 1830377 | 28/08/2024 | 16:35 | 28/08/2024 | 17:29 | GW4 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 377 | 20452.25 | 54.25 | 3 | Yes
| 1830386 | 28/08/2024 | 16:41 | 28/08/2024 | 16:49 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 39 | 336.0513 | 8.6167 | 1 | Yes
| 1830392 | 28/08/2024 | 16:43 | 28/08/2024 | 20:36 | BRA21 | BORONIA | Urban | Third Party | Other | 285 | 66405 | 233 | 1 | Yes
| 1830637 | 28/08/2024 | 16:43 | 28/08/2024 | 19:37 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 173.25 | 173.25 | 1 | Yes
| 1830416 | 28/08/2024 | 16:57 | 28/08/2024 | 19:18 | NW22 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 140.8333 | 140.8333 | 1 | Yes
| 1830421 | 28/08/2024 | 17:03 | 28/08/2024 | 17:42 | HGS23 | HASTINGS | Rural Short | Weather |  | 0 | 5512.7952 | 38.2833 | 1 | Yes
| 1830491 | 28/08/2024 | 18:01 | 28/08/2024 | 18:05 | EB24 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1368 | 6475.1544 | 4.7333 | 1 | Yes
| 1830509 | 28/08/2024 | 18:24 | 28/08/2024 | 19:45 | BH21 | BOX HILL | Urban | Asset Failure | LV | 2 | 160.1 | 80.05 | 1 | Yes
| 1830508 | 28/08/2024 | 18:33 | 28/08/2024 | 21:45 | EB32 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 191.9167 | 191.9167 | 1 | Yes
| 1830530 | 28/08/2024 | 18:41 | 28/08/2024 | 20:12 | SS14 | SPRINGVALE SOUTH | Urban | Unknown | Unknown | 1 | 90.8833 | 90.8833 | 1 | Yes
| 1830560 | 28/08/2024 | 18:54 | 29/08/2024 | 3:03 | HGS33 | HASTINGS | Rural Short | Unknown | Unknown | 2 | 978.3666 | 489.1833 | 1 | Yes
| 1830567 | 28/08/2024 | 19:02 | 29/08/2024 | 0:29 | SS14 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 326.7667 | 326.7667 | 1 | Yes
| 1830251 | 28/08/2024 | 19:21 | 29/08/2024 | 20:03 | BT16 | BENTLEIGH | Urban | Weather |  | 1 | 1482.85 | 1482.85 | 1 | Yes
| 1830585 | 28/08/2024 | 19:29 | 28/08/2024 | 21:15 | EM5 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 106 | 106 | 1 | Yes
| 1830779 | 28/08/2024 | 19:37 | 29/08/2024 | 11:15 | DMA15 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 1877.9 | 938.95 | 1 | Yes
| 1829844 | 28/08/2024 | 21:24 | 29/08/2024 | 5:15 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 471.7 | 471.7 | 1 | Yes
| 1830633 | 28/08/2024 | 21:55 | 28/08/2024 | 22:34 | STO14 | SORRENTO | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 73 | 2847 | 39 | 1 | Yes
| 1830147 | 28/08/2024 | 22:22 | 29/08/2024 | 1:00 | RBD22 | ROSEBUD | Urban | Asset Failure | LV | 1 | 158 | 158 | 1 | Yes
| 1830638 | 28/08/2024 | 23:30 | 29/08/2024 | 10:31 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 661.55 | 661.55 | 1 | Yes
| 1830642 | 29/08/2024 | 1:02 | 29/08/2024 | 1:26 | SR24 | SANDRINGHAM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 58 | 1392 | 24 | 1 | No
| 1830653 | 29/08/2024 | 6:48 | 29/08/2024 | 8:22 | GW5 | GLEN WAVERLEY | Urban | Weather |  | 1 | 94.3333 | 94.3333 | 1 | No
| 1830679 | 29/08/2024 | 8:26 | 29/08/2024 | 10:47 | SR24 | SANDRINGHAM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 140.3833 | 140.3833 | 1 | No
| 1830722 | 29/08/2024 | 9:01 | 29/08/2024 | 12:29 | HGS32 | HASTINGS | Urban | Third Party | Other | 87 | 18043.8 | 207.4 | 1 | No
| 1830747 | 29/08/2024 | 9:39 | 29/08/2024 | 12:29 | HGS32 | HASTINGS | Urban | Third Party | Other | 1 | 169.4 | 169.4 | 1 | No
| 1830752 | 29/08/2024 | 9:49 | 29/08/2024 | 10:37 | MC12 | MORDIALLOC | Urban | Asset Failure | HV | 1067 | 50166.8189 | 47.0167 | 1 | No
| 1830752 | 29/08/2024 | 9:49 | 29/08/2024 | 10:57 | MC12 | MORDIALLOC | Urban | Asset Failure | HV | 103 | 6979.9701 | 67.7667 | 2 | No
| 1830787 | 29/08/2024 | 10:43 | 29/08/2024 | 17:49 | NB32 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 425.95 | 425.95 | 1 | No
| 1830923 | 29/08/2024 | 15:03 | 29/08/2024 | 18:28 | STO14 | SORRENTO | Rural Short | Weather |  | 73 | 15019.75 | 205.75 | 1 | No
| 1830955 | 29/08/2024 | 17:14 | 29/08/2024 | 21:15 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 240.0667 | 240.0667 | 1 | No
| 1830598 | 29/08/2024 | 18:13 | 29/08/2024 | 19:30 | BW34 | BURWOOD | Urban | Asset Failure | LV | 1 | 77 | 77 | 1 | No
| 1830965 | 29/08/2024 | 19:25 | 29/08/2024 | 21:02 | DMA12 | DROMANA | Urban | Asset Failure | LV | 1 | 97.05 | 97.05 | 1 | No
| 1830972 | 29/08/2024 | 20:30 | 29/08/2024 | 22:01 | GW10 | GLEN WAVERLEY | Urban | Other | XXX | 1 | 90.3667 | 90.3667 | 1 | No
| 1830980 | 29/08/2024 | 23:53 | 31/08/2024 | 21:51 | RBD12 | ROSEBUD | Rural Short | Asset Failure | HV | 89 | 245410.0863 | 2757.4167 | 1 | No
| 1830985 | 30/08/2024 | 0:17 | 30/08/2024 | 0:47 | DN9 | DANDENONG | Urban | Third Party |  | 77 | 2311.2859 | 30.0167 | 1 | No
| 1830985 | 30/08/2024 | 0:17 | 30/08/2024 | 0:52 | DN9 | DANDENONG | Urban | Third Party |  | 16 | 560 | 35 | 2 | No
| 1830980 | 30/08/2024 | 0:31 | 30/08/2024 | 4:20 | RBD12 | ROSEBUD | Rural Short | Asset Failure | HV | 35 | 7992.25 | 228.35 | 1 | No
| 1830993 | 30/08/2024 | 0:59 | 30/08/2024 | 3:44 | CRM13 | CARRUM | Urban | Asset Failure | HV | 93 | 15309.3531 | 164.6167 | 1 | No
| 1830993 | 30/08/2024 | 0:59 | 30/08/2024 | 3:49 | CRM13 | CARRUM | Urban | Asset Failure | HV | 48 | 8171.1984 | 170.2333 | 2 | No
| 1830995 | 30/08/2024 | 1:04 | 30/08/2024 | 5:03 | HGS33 | HASTINGS | Rural Short | Weather |  | 12.54 | 2995.3884 | 238.8667 | 1 | No
| 1831011 | 30/08/2024 | 1:14 | 30/08/2024 | 1:30 | OE2 | OAKLEIGH EAST | Urban | Weather |  | 342 | 5392.2114 | 15.7667 | 1 | No
| 1831011 | 30/08/2024 | 1:14 | 30/08/2024 | 4:09 | OE2 | OAKLEIGH EAST | Urban | Weather |  | 1 | 175.0333 | 175.0333 | 2 | No
| 1831011 | 30/08/2024 | 1:14 | 30/08/2024 | 13:51 | OE2 | OAKLEIGH EAST | Urban | Weather |  | 75 | 56757.5025 | 756.7667 | 3 | No
| 1831017 | 30/08/2024 | 1:57 | 30/08/2024 | 2:37 | FSH23 | FRANKSTON SOUTH | Rural Short | Vegetation | Grow-in - NSP responsibility | 392 | 15725.7464 | 40.1167 | 1 | No
| 1831017 | 30/08/2024 | 1:57 | 30/08/2024 | 3:28 | FSH23 | FRANKSTON SOUTH | Rural Short | Vegetation | Grow-in - NSP responsibility | 157 | 14273.9219 | 90.9167 | 2 | No
| 1831017 | 30/08/2024 | 1:57 | 30/08/2024 | 12:18 | FSH23 | FRANKSTON SOUTH | Rural Short | Vegetation | Grow-in - NSP responsibility | 66 | 40991.4978 | 621.0833 | 3 | No
| 1831020 | 30/08/2024 | 1:58 | 30/08/2024 | 2:04 | BR10 | BEAUMARIS | Urban | Unknown | Unknown | 666 | 4084.7778 | 6.1333 | 1 | No
| 1831020 | 30/08/2024 | 1:58 | 30/08/2024 | 2:35 | BR10 | BEAUMARIS | Urban | Unknown | Unknown | 267 | 9883.4589 | 37.0167 | 2 | No
| 1831020 | 30/08/2024 | 1:58 | 30/08/2024 | 2:48 | BR10 | BEAUMARIS | Urban | Unknown | Unknown | 16 | 801.3328 | 50.0833 | 3 | No
| 1831020 | 30/08/2024 | 1:58 | 30/08/2024 | 21:43 | BR10 | BEAUMARIS | Urban | Unknown | Unknown | 68 | 80598.1356 | 1185.2667 | 4 | No
| 1831020 | 30/08/2024 | 1:58 | 30/08/2024 | 22:45 | BR10 | BEAUMARIS | Urban | Unknown | Unknown | 48 | 59839.2 | 1246.65 | 5 | No
| 1831020 | 30/08/2024 | 1:58 | 30/08/2024 | 2:04 | SR36 | SANDRINGHAM | Urban | Unknown | Unknown | 375 | 2299.9875 | 6.1333 | 1 | No
| 1831021 | 30/08/2024 | 2:10 | 30/08/2024 | 5:04 | CDA23 | CLARINDA | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 174.5333 | 174.5333 | 1 | No
| 1830990 | 30/08/2024 | 2:43 | 30/08/2024 | 9:03 | LD6 | LYNDALE | Urban | Asset Failure | LV | 1 | 380.25 | 380.25 | 1 | No
| 1831051 | 30/08/2024 | 4:31 | 30/08/2024 | 8:34 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 242.4667 | 242.4667 | 1 | No
| 1831041 | 30/08/2024 | 5:25 | 30/08/2024 | 9:01 | FSH22 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 216.35 | 216.35 | 1 | No
| 1831070 | 30/08/2024 | 7:14 | 30/08/2024 | 9:35 | BR4 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 140.5833 | 140.5833 | 1 | No
| 1830996 | 30/08/2024 | 8:10 | 30/08/2024 | 9:30 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 80.7167 | 80.7167 | 1 | No
| 1831106 | 30/08/2024 | 8:27 | 30/08/2024 | 10:24 | HGS23 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 117.4 | 117.4 | 1 | No
| 1831127 | 30/08/2024 | 8:40 | 30/08/2024 | 9:00 | KBH32 | KEYSBOROUGH | Urban | Network Business | Switching and protection error | 1 | 19.5667 | 19.5667 | 1 | No
| 1830766 | 30/08/2024 | 9:25 | 30/08/2024 | 11:46 | M25 | MENTONE | Urban | Third Party | Dig-in | 2 | 283.1 | 141.55 | 1 | No
| 1831169 | 30/08/2024 | 9:29 | 30/08/2024 | 13:28 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 239.6333 | 239.6333 | 1 | No
| 1831175 | 30/08/2024 | 9:38 | 30/08/2024 | 18:30 | BT16 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 531.2333 | 531.2333 | 1 | No
| 1831197 | 30/08/2024 | 10:00 | 30/08/2024 | 11:33 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 6.93 | 642.8732 | 92.7667 | 1 | No
| 1831227 | 30/08/2024 | 11:25 | 30/08/2024 | 14:48 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 9 | 1819.5003 | 202.1667 | 1 | No
| 1831089 | 30/08/2024 | 11:42 | 30/08/2024 | 14:10 | EB14 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 148 | 148 | 1 | No
| 1831245 | 30/08/2024 | 11:58 | 30/08/2024 | 13:14 | BW33 | BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 65 | 4958.4145 | 76.2833 | 1 | No
| 1831264 | 30/08/2024 | 12:25 | 30/08/2024 | 16:45 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 259.3 | 259.3 | 1 | No
| 1831336 | 30/08/2024 | 15:59 | 30/08/2024 | 17:28 | LD33 | LYNDALE | Urban | Unknown | Unknown | 1 | 89 | 89 | 1 | No
| 1831046 | 30/08/2024 | 18:18 | 30/08/2024 | 20:40 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 142 | 142 | 1 | No
| 1831381 | 30/08/2024 | 19:14 | 31/08/2024 | 0:06 | EW9 | ELWOOD | Urban | Animal | Animal impact | 54 | 15720.3018 | 291.1167 | 1 | No
| 1831383 | 30/08/2024 | 19:24 | 31/08/2024 | 0:06 | EW14 | ELWOOD | Urban | Animal | Animal impact | 1 | 281.4 | 281.4 | 1 | No
| 1831394 | 30/08/2024 | 21:09 | 30/08/2024 | 21:16 | STO22 | SORRENTO | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 179 | 1303.7107 | 7.2833 | 1 | No
| 1831397 | 30/08/2024 | 23:38 | 31/08/2024 | 0:28 | SS13 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 52 | 2600 | 50 | 1 | No
| 1831401 | 31/08/2024 | 0:20 | 31/08/2024 | 1:13 | MTN35 | MORNINGTON | Rural Short | Third Party | Other | 5 | 264.8335 | 52.9667 | 1 | No
| 1831404 | 31/08/2024 | 2:30 | 31/08/2024 | 4:10 | FSH33 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 20.1 | 2010 | 100 | 1 | No
| 1831402 | 31/08/2024 | 5:29 | 31/08/2024 | 7:38 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 1 | 129 | 129 | 1 | No
| 1831417 | 31/08/2024 | 7:22 | 31/08/2024 | 10:15 | NP12 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 172.7333 | 172.7333 | 1 | No
| 1831420 | 31/08/2024 | 8:00 | 31/08/2024 | 10:01 | RBD14 | ROSEBUD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 120.6 | 120.6 | 1 | No
| 1831446 | 31/08/2024 | 9:40 | 31/08/2024 | 11:10 | CFD23 | CAULFIELD | Urban | Asset Failure | LV | 1 | 89.45 | 89.45 | 1 | No
| 1831455 | 31/08/2024 | 9:43 | 31/08/2024 | 13:08 | CRM14 | CARRUM | Rural Short | Asset Failure | HV | 4.69 | 957.8542 | 204.2333 | 1 | No
| 1831413 | 31/08/2024 | 9:46 | 31/08/2024 | 12:13 | BT12 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 147 | 147 | 1 | No
| 1831464 | 31/08/2024 | 12:17 | 31/08/2024 | 14:57 | OE13 | OAKLEIGH EAST | Urban | Asset Failure | LV | 1 | 160.05 | 160.05 | 1 | No
| 1831490 | 31/08/2024 | 13:33 | 31/08/2024 | 14:01 | DN7 | DANDENONG | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 56 | 1568 | 28 | 1 | No
| 1831493 | 31/08/2024 | 14:37 | 31/08/2024 | 15:39 | LWN24 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 61.6667 | 61.6667 | 1 | No
| 1831503 | 31/08/2024 | 15:16 | 31/08/2024 | 19:10 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 233.85 | 233.85 | 1 | No
| 1831506 | 31/08/2024 | 15:33 | 31/08/2024 | 17:42 | RWT35 | RINGWOOD | Urban | Third Party | Other | 44 | 5633.4652 | 128.0333 | 1 | No
| 1831531 | 31/08/2024 | 20:16 | 2024-01-09 | 0:59 | BC23 | BALACLAVA | Urban | Asset Failure | LV | 1 | 283.0667 | 283.0667 | 1 | No
| 1831532 | 31/08/2024 | 20:18 | 31/08/2024 | 23:14 | BT21 | BENTLEIGH | Urban | Asset Failure | HV | 1 | 175.2833 | 175.2833 | 1 | No
| 1831537 | 31/08/2024 | 21:33 | 31/08/2024 | 23:39 | FTN13 | FRANKSTON | Urban | Asset Failure | LV | 1 | 125.8667 | 125.8667 | 1 | No
| 1831542 | 2024-01-09 | 4:18 | 2024-01-09 | 5:31 | DC3 | DONCASTER | Urban | Asset Failure | HV | 1 | 72.1667 | 72.1667 | 1 | No
| 1831545 | 2024-01-09 | 6:39 | 2024-01-09 | 8:50 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 29.04 | 3824.083 | 131.6833 | 1 | No
| 1831570 | 2024-01-09 | 11:23 | 2024-01-09 | 14:00 | K25 | GARDINER | Urban | Unknown | Unknown | 1 | 156.45 | 156.45 | 1 | No
| 1831573 | 2024-01-09 | 11:58 | 2024-01-09 | 13:30 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1 | 92 | 92 | 1 | No
| 1831580 | 2024-01-09 | 13:32 | 2024-01-09 | 19:42 | NP12 | NOBLE PARK | Urban | Asset Failure | LV | 40 | 14805.332 | 370.1333 | 1 | No
| 1831582 | 2024-01-09 | 13:32 | 2024-01-09 | 19:43 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 7 | 2594.55 | 370.65 | 1 | No
| 1831590 | 2024-01-09 | 14:15 | 2024-01-09 | 15:30 | SS22 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 74.7667 | 74.7667 | 1 | No
| 1831618 | 2024-01-09 | 19:38 | 2024-01-09 | 21:30 | FSH13 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 26.13 | 2913.0586 | 111.4833 | 1 | No
| 1831668 | 2024-01-09 | 22:45 | 2024-02-09 | 2:35 | STO14 | SORRENTO | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 95.81 | 21959.652 | 229.2 | 1 | No
| 1831662 | 2024-01-09 | 23:05 | 2024-02-09 | 19:19 | RBD24 | ROSEBUD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 111 | 134679.9963 | 1213.3333 | 1 | No
| 1831681 | 2024-01-09 | 23:44 | 2024-03-09 | 17:19 | BU21 | BULLEEN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 6 | 14973.1998 | 2495.5333 | 1 | No
| 1831715 | 2024-01-09 | 23:53 | 2024-02-09 | 3:44 | BC11 | BALACLAVA | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 103 | 23768.9701 | 230.7667 | 1 | No
| 1831687 | 2024-01-09 | 23:54 | 2024-02-09 | 0:55 | MTN35 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 86 | 5247.4362 | 61.0167 | 1 | No
| 1831687 | 2024-01-09 | 23:54 | 2024-02-09 | 1:10 | MTN35 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 346 | 26336.3782 | 76.1167 | 2 | No
| 1831712 | 2024-02-09 | 0:07 | 2024-02-09 | 1:14 | BR15 | BEAUMARIS | Urban | Weather |  | 23.43 | 1564.3438 | 66.7667 | 1 | Yes
| 1831731 | 2024-02-09 | 0:28 | 2024-03-09 | 13:10 | SR26 | SANDRINGHAM | Urban | Weather |  | 53 | 116693.6351 | 2201.7667 | 1 | Yes
| 1831733 | 2024-02-09 | 0:29 | 2024-02-09 | 1:21 | DC2 | DONCASTER | Urban | Animal | Animal impact | 127.3 | 6693.8541 | 52.5833 | 1 | Yes
| 1831751 | 2024-02-09 | 0:36 | 2024-02-09 | 16:51 | FSH23 | FRANKSTON SOUTH | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 11 | 10718.5837 | 974.4167 | 1 | Yes
| 1831758 | 2024-02-09 | 0:45 | 2024-02-09 | 0:50 | EW8 | ELWOOD | Urban | Asset Failure | HV | 932 | 3821.2 | 4.1 | 1 | Yes
| 1831758 | 2024-02-09 | 0:45 | 2024-02-09 | 0:58 | EW8 | ELWOOD | Urban | Asset Failure | HV | 735 | 9530.5245 | 12.9667 | 2 | Yes
| 1831766 | 2024-02-09 | 1:07 | 2024-02-09 | 17:14 | MTN34 | MORNINGTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 967.2667 | 967.2667 | 1 | Yes
| 1831769 | 2024-02-09 | 1:10 | 2024-02-09 | 1:23 | RWT23 | RINGWOOD | Urban | Weather |  | 447 | 5751.4149 | 12.8667 | 1 | Yes
| 1831769 | 2024-02-09 | 1:10 | 2024-02-09 | 5:27 | RWT23 | RINGWOOD | Urban | Weather |  | 987 | 253576.7829 | 256.9167 | 2 | Yes
| 1831775 | 2024-02-09 | 1:14 | 2024-02-09 | 16:00 | LD6 | LYNDALE | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 45.54 | 40364.379 | 886.35 | 1 | Yes
| 1832763 | 2024-02-09 | 1:16 | 2024-02-09 | 13:50 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 82 | 61828 | 754 | 1 | Yes
| 1831794 | 2024-02-09 | 1:17 | 2024-02-09 | 4:16 | RBD11 | ROSEBUD | Urban | Weather |  | 144 | 25735.2048 | 178.7167 | 1 | Yes
| 1831798 | 2024-02-09 | 1:21 | 2024-02-09 | 13:09 | HGS31 | HASTINGS | Rural Short | Vegetation | Grow-in - NSP responsibility | 168 | 118986 | 708.25 | 1 | Yes
| 1831798 | 2024-02-09 | 1:21 | 2024-02-09 | 16:12 | HGS31 | HASTINGS | Rural Short | Vegetation | Grow-in - NSP responsibility | 113 | 100658.5129 | 890.7833 | 2 | Yes
| 1831813 | 2024-02-09 | 1:48 | 2024-02-09 | 5:21 | MTN31 | MORNINGTON | Urban | Weather |  | 83 | 17627.8139 | 212.3833 | 1 | Yes
| 1831819 | 2024-02-09 | 2:04 | 2024-03-09 | 15:05 | EW12 | ELWOOD | Urban | Asset Failure | LV | 1 | 2220.2833 | 2220.2833 | 1 | Yes
| 1831821 | 2024-02-09 | 2:05 | 2024-02-09 | 2:08 | DMA23 | DROMANA | Rural Short | Weather |  | 495 | 1823.2335 | 3.6833 | 1 | Yes
| 1831821 | 2024-02-09 | 2:05 | 2024-02-09 | 9:08 | DMA23 | DROMANA | Rural Short | Weather |  | 412 | 174420.2 | 423.35 | 2 | Yes
| 1831821 | 2024-02-09 | 2:05 | 2024-03-09 | 5:54 | DMA23 | DROMANA | Rural Short | Weather |  | 59 | 98513.2853 | 1669.7167 | 3 | Yes
| 1831821 | 2024-02-09 | 2:05 | 2024-03-09 | 10:53 | DMA23 | DROMANA | Rural Short | Weather |  | 2 | 3936.9 | 1968.45 | 4 | Yes
| 1831821 | 2024-02-09 | 2:05 | 2024-03-09 | 16:10 | DMA23 | DROMANA | Rural Short | Weather |  | 43 | 98284.3819 | 2285.6833 | 5 | Yes
| 1833226 | 2024-02-09 | 2:06 | 2024-02-09 | 18:10 | LD33 | LYNDALE | Urban | Weather |  | 63 | 60681.6 | 963.2 | 1 | Yes
| 1831830 | 2024-02-09 | 2:06 | 2024-02-09 | 6:33 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 83 | 22104.2861 | 266.3167 | 1 | Yes
| 1831830 | 2024-02-09 | 2:06 | 2024-02-09 | 15:13 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 40 | 31466.668 | 786.6667 | 2 | Yes
| 1832041 | 2024-02-09 | 2:10 | 2024-02-09 | 7:32 | RBD12 | ROSEBUD | Rural Short | Weather |  | 35 | 11270 | 322 | 1 | Yes
| 1832041 | 2024-02-09 | 2:10 | 2024-02-09 | 8:01 | RBD12 | ROSEBUD | Rural Short | Weather |  | 89 | 31231.5863 | 350.9167 | 2 | Yes
| 1831843 | 2024-02-09 | 2:10 | 2024-02-09 | 8:00 | RBD12 | ROSEBUD | Rural Short | Weather |  | 2 | 698.0334 | 349.0167 | 1 | Yes
| 1831852 | 2024-02-09 | 2:14 | 2024-02-09 | 12:19 | DMA15 | DROMANA | Rural Short | Weather |  | 40 | 24224.668 | 605.6167 | 1 | Yes
| 1831867 | 2024-02-09 | 2:14 | 2024-02-09 | 16:20 | DMA15 | DROMANA | Rural Short | Weather |  | 34 | 28730.5678 | 845.0167 | 1 | Yes
| 1831851 | 2024-02-09 | 2:17 | 2024-02-09 | 8:50 | MTN32 | MORNINGTON | Rural Short | Weather |  | 499 | 196398.0667 | 393.5833 | 1 | Yes
| 1831866 | 2024-02-09 | 2:17 | 2024-02-09 | 5:27 | DMA23 | DROMANA | Rural Short | Weather |  | 460 | 87223.682 | 189.6167 | 1 | Yes
| 1833208 | 2024-02-09 | 2:19 | 2024-02-09 | 21:26 | DVY32 | DANDENONG VALLEY | Urban | Weather |  | 67 | 76860.1689 | 1147.1667 | 1 | Yes
| 1831884 | 2024-02-09 | 2:20 | 2024-02-09 | 5:27 | HGS31 | HASTINGS | Rural Short | Weather |  | 652 | 122141.3116 | 187.3333 | 1 | Yes
| 1831885 | 2024-02-09 | 2:21 | 2024-02-09 | 10:22 | MTN32 | MORNINGTON | Rural Short | Asset Failure | Distribution substation | 44 | 21204.3348 | 481.9167 | 1 | Yes
| 1831894 | 2024-02-09 | 2:21 | 2024-02-09 | 13:18 | HGS22 | HASTINGS | Rural Short | Weather |  | 2 | 1312.2666 | 656.1333 | 1 | Yes
| 1832488 | 2024-02-09 | 2:21 | 2024-02-09 | 14:00 | HGS22 | HASTINGS | Rural Short | Vegetation | Grow-in - Other responsible party | 52.93 | 36960.1351 | 698.2833 | 1 | Yes
| 1831908 | 2024-02-09 | 2:21 | 2024-02-09 | 13:20 | HGS22 | HASTINGS | Rural Short | Weather |  | 4 | 2632.4668 | 658.1167 | 1 | Yes
| 1831917 | 2024-02-09 | 2:22 | 2024-03-09 | 0:57 | DMA15 | DROMANA | Rural Short | Weather |  | 25 | 33885 | 1355.4 | 1 | Yes
| 1831888 | 2024-02-09 | 2:24 | 2024-02-09 | 5:27 | MTN31 | MORNINGTON | Urban | Weather |  | 942 | 173108.2314 | 183.7667 | 1 | Yes
| 1831922 | 2024-02-09 | 2:25 | 2024-02-09 | 5:27 | DMA15 | DROMANA | Rural Short | Weather |  | 969 | 176874.7677 | 182.5333 | 1 | Yes
| 1831922 | 2024-02-09 | 2:25 | 2024-02-09 | 5:27 | DMA23 | DROMANA | Rural Short | Weather |  | 495 | 90353.9835 | 182.5333 | 1 | Yes
| 1831923 | 2024-02-09 | 2:26 | 2024-03-09 | 16:23 | HGS23 | HASTINGS | Rural Short | Weather |  | 8 | 18216.5336 | 2277.0667 | 1 | Yes
| 1831923 | 2024-02-09 | 2:26 | 2024-03-09 | 16:23 | HGS23 | HASTINGS | Rural Short | Weather |  | 4 | 9109.2668 | 2277.3167 | 2 | Yes
| 1831923 | 2024-02-09 | 2:26 | 2024-03-09 | 16:24 | HGS23 | HASTINGS | Rural Short | Weather |  | 1 | 2277.6167 | 2277.6167 | 3 | Yes
| 1831923 | 2024-02-09 | 2:26 | 2024-03-09 | 16:24 | HGS23 | HASTINGS | Rural Short | Weather |  | 12 | 27334.8 | 2277.9 | 4 | Yes
| 1831923 | 2024-02-09 | 2:26 | 2024-03-09 | 16:24 | HGS23 | HASTINGS | Rural Short | Weather |  | 1 | 2278.2 | 2278.2 | 5 | Yes
| 1831923 | 2024-02-09 | 2:26 | 2024-03-09 | 16:24 | HGS23 | HASTINGS | Rural Short | Weather |  | 6 | 13670.8002 | 2278.4667 | 6 | Yes
| 1831923 | 2024-02-09 | 2:26 | 2024-03-09 | 16:25 | HGS23 | HASTINGS | Rural Short | Weather |  | 1 | 2278.7667 | 2278.7667 | 7 | Yes
| 1831923 | 2024-02-09 | 2:26 | 2024-03-09 | 16:25 | HGS23 | HASTINGS | Rural Short | Weather |  | 2 | 4558.2 | 2279.1 | 8 | Yes
| 1831938 | 2024-02-09 | 2:30 | 2024-02-09 | 20:45 | MTN32 | MORNINGTON | Rural Short | Weather |  | 10 | 10943.167 | 1094.3167 | 1 | Yes
| 1831933 | 2024-02-09 | 2:35 | 2024-02-09 | 8:00 | RBD12 | ROSEBUD | Rural Short | Weather |  | 1 | 324.2333 | 324.2333 | 1 | Yes
| 1831956 | 2024-02-09 | 2:37 | 2024-02-09 | 17:13 | HGS33 | HASTINGS | Rural Short | Weather |  | 10 | 8763.333 | 876.3333 | 1 | Yes
| 1831956 | 2024-02-09 | 2:37 | 2024-02-09 | 17:14 | HGS33 | HASTINGS | Rural Short | Weather |  | 32 | 28053.8656 | 876.6833 | 2 | Yes
| 1831965 | 2024-02-09 | 2:37 | 2024-02-09 | 14:48 | FSH21 | FRANKSTON SOUTH | Rural Short | Weather |  | 11 | 8037.15 | 730.65 | 1 | Yes
| 1831973 | 2024-02-09 | 2:39 | 2024-02-09 | 13:10 | DMA13 | DROMANA | Rural Short | Weather |  | 58 | 36582.5314 | 630.7333 | 1 | Yes
| 1831949 | 2024-02-09 | 2:40 | 2024-02-09 | 5:27 | HGS23 | HASTINGS | Rural Short | Weather |  | 221 | 36870.1593 | 166.8333 | 1 | Yes
| 1831892 | 2024-02-09 | 2:41 | 2024-02-09 | 13:18 | HGS22 | HASTINGS | Rural Short | Weather |  | 2 | 1274 | 637 | 1 | Yes
| 1831951 | 2024-02-09 | 2:41 | 2024-02-09 | 8:53 | DVY34 | DANDENONG VALLEY | Urban | Weather |  | 201 | 74765.3067 | 371.9667 | 1 | Yes
| 1832044 | 2024-02-09 | 2:49 | 2024-02-09 | 5:34 | BW34 | BURWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 359 | 59456.3953 | 165.6167 | 1 | Yes
| 1832044 | 2024-02-09 | 2:49 | 2024-02-09 | 5:35 | BW34 | BURWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 947 | 157675.5 | 166.5 | 2 | Yes
| 1832044 | 2024-02-09 | 2:53 | 2024-02-09 | 16:28 | BW34 | BURWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 331 | 269969.1277 | 815.6167 | 1 | Yes
| 1832481 | 2024-02-09 | 2:55 | 2024-02-09 | 22:35 | GW6 | GLEN WAVERLEY | Urban | Unknown | Unknown | 77.72 | 91648.7219 | 1179.2167 | 1 | Yes
| 1833101 | 2024-02-09 | 2:55 | 2024-02-09 | 21:20 | GW6 | GLEN WAVERLEY | Urban | Asset Failure | Distribution substation | 75 | 82869.9975 | 1104.9333 | 1 | Yes
| 1833101 | 2024-02-09 | 2:55 | 2024-02-09 | 21:20 | GW6 | GLEN WAVERLEY | Urban | Asset Failure | Distribution substation | 36 | 39780 | 1105 | 2 | Yes
| 1832383 | 2024-02-09 | 2:56 | 2024-02-09 | 18:33 | MGE22 | MULGRAVE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 11.22 | 10508.2784 | 936.5667 | 1 | Yes
| 1832177 | 2024-02-09 | 2:57 | 2024-02-09 | 17:20 | BW35 | BURWOOD | Urban | Weather |  | 60 | 51766.998 | 862.7833 | 1 | Yes
| 1832049 | 2024-02-09 | 2:57 | 2024-02-09 | 12:35 | FSH11 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1316 | 759485.5772 | 577.1167 | 1 | Yes
| 1833109 | 2024-02-09 | 3:00 | 2024-02-09 | 4:46 | DVY12 | DANDENONG VALLEY | Urban | Weather |  | 32 | 3364.8 | 105.15 | 1 | Yes
| 1833118 | 2024-02-09 | 3:01 | 2024-03-09 | 8:45 | M35 | MENTONE | Urban | Asset Failure | LV | 55.61 | 99196.1893 | 1783.7833 | 1 | Yes
| 1832042 | 2024-02-09 | 3:02 | 2024-02-09 | 9:27 | BR13 | BEAUMARIS | Urban | Vegetation | Grow-in - NSP responsibility | 230 | 88419.659 | 384.4333 | 1 | Yes
| 1832042 | 2024-02-09 | 3:02 | 2024-02-09 | 9:28 | BR13 | BEAUMARIS | Urban | Vegetation | Grow-in - NSP responsibility | 839 | 323784.1113 | 385.9167 | 2 | Yes
| 1832042 | 2024-02-09 | 3:02 | 2024-02-09 | 18:01 | BR13 | BEAUMARIS | Urban | Vegetation | Grow-in - NSP responsibility | 143 | 128545.0881 | 898.9167 | 3 | Yes
| 1832053 | 2024-02-09 | 3:03 | 2024-02-09 | 10:43 | HGS33 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 70 | 32189.5 | 459.85 | 1 | Yes
| 1832053 | 2024-02-09 | 3:03 | 2024-02-09 | 15:27 | HGS33 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 9 | 6694.0497 | 743.7833 | 2 | Yes
| 1832053 | 2024-02-09 | 3:03 | 2024-02-09 | 15:27 | HGS33 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 12 | 8935.8 | 744.65 | 3 | Yes
| 1832505 | 2024-02-09 | 3:06 | 2024-02-09 | 18:01 | BR13 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 48 | 42997.5984 | 895.7833 | 1 | Yes
| 1832192 | 2024-02-09 | 3:09 | 2024-02-09 | 22:45 | NB32 | NORTH BRIGHTON | Urban | Weather |  | 40 | 47006.668 | 1175.1667 | 1 | Yes
| 1832506 | 2024-02-09 | 3:09 | 2024-03-09 | 18:00 | BR1 | BEAUMARIS | Urban | Weather |  | 68 | 158450.2 | 2330.15 | 1 | Yes
| 1832041 | 2024-02-09 | 3:13 | 2024-02-09 | 6:59 | RBD12 | ROSEBUD | Rural Short | Weather |  | 137 | 30962 | 226 | 1 | Yes
| 1832316 | 2024-02-09 | 3:14 | 2024-02-09 | 14:25 | SVW53 | SPRINGVALE WEST | Urban | Weather |  | 35 | 23472.1655 | 670.6333 | 1 | Yes
| 1833277 | 2024-02-09 | 3:18 | 2024-02-09 | 19:52 | HT1 | HEATHERTON | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 16.75 | 16636.1 | 993.2 | 1 | Yes
| 1832117 | 2024-02-09 | 3:21 | 2024-02-09 | 10:17 | GW10 | GLEN WAVERLEY | Urban | Weather |  | 90 | 37501.497 | 416.6833 | 1 | Yes
| 1832072 | 2024-02-09 | 3:23 | 2024-02-09 | 10:40 | EM8 | EAST MALVERN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 51 | 22271.7 | 436.7 | 1 | Yes
| 1832048 | 2024-02-09 | 3:24 | 2024-02-09 | 8:55 | SV32 | SPRINGVALE | Urban | Weather |  | 1816 | 601882.8728 | 331.4333 | 1 | Yes
| 1832048 | 2024-02-09 | 3:24 | 2024-02-09 | 11:15 | SV32 | SPRINGVALE | Urban | Weather |  | 40 | 18839.332 | 470.9833 | 2 | Yes
| 1832037 | 2024-02-09 | 3:26 | 2024-02-09 | 6:49 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 495 | 100485 | 203 | 1 | Yes
| 1832037 | 2024-02-09 | 3:26 | 2024-02-09 | 6:49 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 741 | 150793.5 | 203.5 | 2 | Yes
| 1832037 | 2024-02-09 | 3:26 | 2024-02-09 | 7:13 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 776 | 176410.6408 | 227.3333 | 3 | Yes
| 1832103 | 2024-02-09 | 3:29 | 2024-02-09 | 21:32 | DC3 | DONCASTER | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 21.78 | 23577.5753 | 1082.5333 | 1 | Yes
| 1833745 | 2024-02-09 | 4:02 | 2024-03-09 | 23:20 | MTN22 | MORNINGTON | Rural Short | Weather |  | 21 | 54555.2007 | 2597.8667 | 1 | Yes
| 1832039 | 2024-02-09 | 4:17 | 2024-02-09 | 6:23 | DMA24 | DROMANA | Rural Short | Weather |  | 1676 | 212041.9892 | 126.5167 | 1 | Yes
| 1832039 | 2024-02-09 | 4:17 | 2024-02-09 | 9:13 | DMA24 | DROMANA | Rural Short | Weather |  | 124 | 36788.7292 | 296.6833 | 2 | Yes
| 1832040 | 2024-02-09 | 4:20 | 2024-02-09 | 7:47 | MTN35 | MORNINGTON | Rural Short | Weather |  | 1386 | 287017.4538 | 207.0833 | 1 | Yes
| 1832333 | 2024-02-09 | 4:24 | 2024-02-09 | 19:37 | FSH13 | FRANKSTON SOUTH | Urban | Weather |  | 20 | 18241 | 912.05 | 1 | Yes
| 1832051 | 2024-02-09 | 4:25 | 2024-02-09 | 7:01 | FSH33 | FRANKSTON SOUTH | Urban | Weather |  | 1029 | 160369.65 | 155.85 | 1 | Yes
| 1832051 | 2024-02-09 | 4:25 | 2024-02-09 | 8:56 | FSH33 | FRANKSTON SOUTH | Urban | Weather |  | 534 | 144429.2178 | 270.4667 | 2 | Yes
| 1832147 | 2024-02-09 | 4:25 | 2024-03-09 | 13:15 | DMA13 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 70 | 137884.831 | 1969.7833 | 1 | Yes
| 1832145 | 2024-02-09 | 4:27 | 2024-02-09 | 13:01 | FTN25 | FRANKSTON | Urban | Weather |  | 360 | 184722.012 | 513.1167 | 1 | Yes
| 1832038 | 2024-02-09 | 4:37 | 2024-02-09 | 6:14 | BW33 | BURWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 746 | 72735 | 97.5 | 1 | Yes
| 1832050 | 2024-02-09 | 4:37 | 2024-02-09 | 8:17 | FSH31 | FRANKSTON SOUTH | Urban | Weather |  | 708 | 155441.4 | 219.55 | 1 | Yes
| 1832050 | 2024-02-09 | 4:37 | 2024-02-09 | 8:38 | FSH31 | FRANKSTON SOUTH | Urban | Weather |  | 529 | 127365.5843 | 240.7667 | 2 | Yes
| 1832050 | 2024-02-09 | 4:37 | 2024-02-09 | 8:50 | FSH31 | FRANKSTON SOUTH | Urban | Weather |  | 1535 | 388764.3845 | 253.2667 | 3 | Yes
| 1832165 | 2024-02-09 | 4:39 | 2024-02-09 | 21:01 | LWN33 | LANGWARRIN | Urban | Weather |  | 77 | 75626.8359 | 982.1667 | 1 | Yes
| 1839564 | 2024-02-09 | 5:02 | 2024-03-09 | 15:50 | STO23 | SORRENTO | Urban | Overloads |  | 21.12 | 44098.56 | 2088 | 1 | Yes
| 1832039 | 2024-02-09 | 5:27 | 2024-02-09 | 6:23 | DMA24 | DROMANA | Rural Short | Weather |  | 31 | 1722.5677 | 55.5667 | 1 | Yes
| 1832040 | 2024-02-09 | 5:27 | 2024-02-09 | 7:47 | MTN35 | MORNINGTON | Rural Short | Weather |  | 298 | 41650.4766 | 139.7667 | 1 | Yes
| 1832040 | 2024-02-09 | 5:27 | 2024-02-09 | 8:20 | MTN35 | MORNINGTON | Rural Short | Weather |  | 53 | 9177.8351 | 173.1667 | 2 | Yes
| 1832041 | 2024-02-09 | 5:27 | 2024-02-09 | 6:30 | RBD12 | ROSEBUD | Rural Short | Weather |  | 57 | 3612.8481 | 63.3833 | 1 | Yes
| 1832042 | 2024-02-09 | 5:27 | 2024-02-09 | 9:08 | BR13 | BEAUMARIS | Urban | Vegetation | Grow-in - NSP responsibility | 319 | 70626.6 | 221.4 | 1 | Yes
| 1832043 | 2024-02-09 | 5:27 | 2024-02-09 | 6:10 | KBH31 | KEYSBOROUGH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 336 | 14397.6 | 42.85 | 1 | Yes
| 1832045 | 2024-02-09 | 5:27 | 2024-02-09 | 7:41 | DC2 | DONCASTER | Urban | Weather |  | 921 | 123153.0807 | 133.7167 | 1 | Yes
| 1832045 | 2024-02-09 | 5:27 | 2024-02-09 | 9:05 | DC2 | DONCASTER | Urban | Weather |  | 862 | 187844.1954 | 217.9167 | 2 | Yes
| 1832046 | 2024-02-09 | 5:27 | 2024-02-09 | 5:36 | KBH31 | KEYSBOROUGH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 358 | 3227.9786 | 9.0167 | 1 | Yes
| 1832046 | 2024-02-09 | 5:27 | 2024-02-09 | 5:54 | KBH31 | KEYSBOROUGH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 322 | 8533 | 26.5 | 2 | Yes
| 1832036 | 2024-02-09 | 5:27 | 2024-02-09 | 6:16 | HGS33 | HASTINGS | Rural Short | Weather |  | 687 | 33124.8729 | 48.2167 | 1 | Yes
| 1832047 | 2024-02-09 | 5:27 | 2024-02-09 | 9:58 | MC14 | MORDIALLOC | Urban | Weather |  | 446 | 120821.4 | 270.9 | 1 | Yes
| 1832048 | 2024-02-09 | 5:27 | 2024-02-09 | 8:43 | SV32 | SPRINGVALE | Urban | Weather |  | 152 | 29657.7384 | 195.1167 | 1 | Yes
| 1832049 | 2024-02-09 | 5:27 | 2024-02-09 | 6:39 | FSH11 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1641 | 116948.6547 | 71.2667 | 1 | Yes
| 1832049 | 2024-02-09 | 5:27 | 2024-02-09 | 6:42 | FSH11 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 597 | 44277.5199 | 74.1667 | 2 | Yes
| 1832050 | 2024-02-09 | 5:27 | 2024-02-09 | 7:59 | FSH31 | FRANKSTON SOUTH | Urban | Weather |  | 711 | 107894.25 | 151.75 | 1 | Yes
| 1832051 | 2024-02-09 | 5:27 | 2024-02-09 | 6:51 | FSH33 | FRANKSTON SOUTH | Urban | Weather |  | 610 | 51179 | 83.9 | 1 | Yes
| 1832661 | 2024-02-09 | 5:28 | 2024-03-09 | 1:33 | MTN24 | MORNINGTON | Rural Short | Weather |  | 28 | 33727.4 | 1204.55 | 1 | Yes
| 1832661 | 2024-02-09 | 5:28 | 2024-03-09 | 13:00 | MTN24 | MORNINGTON | Rural Short | Weather |  | 46 | 86990.6 | 1891.1 | 2 | Yes
| 1832235 | 2024-02-09 | 5:30 | 2024-03-09 | 1:10 | EB33 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 1180.55 | 1180.55 | 1 | Yes
| 1832054 | 2024-02-09 | 5:33 | 2024-02-09 | 11:59 | DMA23 | DROMANA | Rural Short | Weather |  | 20 | 7722.666 | 386.1333 | 1 | Yes
| 1832150 | 2024-02-09 | 5:36 | 2024-02-09 | 5:43 | HGS23 | HASTINGS | Rural Short | Weather |  | 25 | 161.25 | 6.45 | 1 | Yes
| 1832150 | 2024-02-09 | 5:36 | 2024-02-09 | 11:34 | HGS23 | HASTINGS | Rural Short | Weather |  | 82 | 29353.2694 | 357.9667 | 2 | Yes
| 1832150 | 2024-02-09 | 5:36 | 2024-03-09 | 11:02 | HGS23 | HASTINGS | Rural Short | Weather |  | 7 | 12363.4 | 1766.2 | 3 | Yes
| 1832117 | 2024-02-09 | 5:40 | 2024-02-09 | 10:18 | GW10 | GLEN WAVERLEY | Urban | Weather |  | 1 | 277.15 | 277.15 | 1 | Yes
| 1833306 | 2024-02-09 | 5:47 | 2024-02-09 | 20:20 | NW31 | NUNAWADING | Urban | Asset Failure | HV | 165 | 144028.5 | 872.9 | 1 | Yes
| 1832167 | 2024-02-09 | 6:13 | 2024-02-09 | 13:48 | HGS21 | HASTINGS | Rural Short | Weather |  | 22 | 10008.1674 | 454.9167 | 1 | Yes
| 1832173 | 2024-02-09 | 6:22 | 2024-02-09 | 9:58 | CRM13 | CARRUM | Urban | Weather |  | 669 | 144448.2723 | 215.9167 | 1 | Yes
| 1832173 | 2024-02-09 | 6:22 | 2024-02-09 | 10:06 | CRM13 | CARRUM | Urban | Weather |  | 327 | 73280.7 | 224.1 | 2 | Yes
| 1832173 | 2024-02-09 | 6:22 | 2024-02-09 | 11:28 | CRM13 | CARRUM | Urban | Weather |  | 83 | 25399.3861 | 306.0167 | 3 | Yes
| 1832173 | 2024-02-09 | 6:22 | 2024-02-09 | 16:57 | CRM13 | CARRUM | Urban | Weather |  | 155 | 98499.9115 | 635.4833 | 4 | Yes
| 1832175 | 2024-02-09 | 6:24 | 2024-03-09 | 1:18 | DMA23 | DROMANA | Rural Short | Asset Failure | LV | 1 | 1134.1833 | 1134.1833 | 1 | Yes
| 1832176 | 2024-02-09 | 6:27 | 2024-02-09 | 22:23 | DMA23 | DROMANA | Rural Short | Weather |  | 34 | 32511.3678 | 956.2167 | 1 | Yes
| 1832177 | 2024-02-09 | 6:29 | 2024-02-09 | 11:05 | BW35 | BURWOOD | Urban | Weather |  | 64 | 17642.6688 | 275.6667 | 1 | Yes
| 1832186 | 2024-02-09 | 6:34 | 2024-02-09 | 13:00 | LD6 | LYNDALE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 17.16 | 6614.8934 | 385.4833 | 1 | Yes
| 1832209 | 2024-02-09 | 6:49 | 2024-02-09 | 6:57 | NW21 | NUNAWADING | Urban | Weather |  | 495 | 3638.25 | 7.35 | 1 | Yes
| 1832209 | 2024-02-09 | 6:49 | 2024-02-09 | 8:53 | NW21 | NUNAWADING | Urban | Weather |  | 741 | 91414.7247 | 123.3667 | 2 | Yes
| 1832213 | 2024-02-09 | 6:52 | 2024-02-09 | 21:59 | EM2 | EAST MALVERN | Urban | Asset Failure | LV | 19.47 | 17658.6416 | 906.9667 | 1 | Yes
| 1832219 | 2024-02-09 | 6:55 | 2024-02-09 | 10:43 | HGS33 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 2 | 455.8 | 227.9 | 1 | Yes
| 1832318 | 2024-02-09 | 6:57 | 2024-02-09 | 19:23 | BW34 | BURWOOD | Urban | Weather |  | 92.46 | 68955.1239 | 745.7833 | 1 | Yes
| 1832244 | 2024-02-09 | 7:09 | 2024-03-09 | 11:30 | FSH21 | FRANKSTON SOUTH | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 1700.55 | 1700.55 | 1 | Yes
| 1832310 | 2024-02-09 | 7:39 | 2024-03-09 | 4:33 | BR13 | BEAUMARIS | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 1254 | 1254 | 1 | Yes
| 1832336 | 2024-02-09 | 7:49 | 2024-02-09 | 13:31 | CM13 | CHELTENHAM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 341.9 | 341.9 | 1 | Yes
| 1832347 | 2024-02-09 | 7:55 | 2024-02-09 | 8:56 | BR4 | BEAUMARIS | Urban | Third Party |  | 372 | 22865.6124 | 61.4667 | 1 | Yes
| 1832347 | 2024-02-09 | 7:55 | 2024-02-09 | 15:11 | BR4 | BEAUMARIS | Urban | Third Party |  | 339 | 147702.3 | 435.7 | 2 | Yes
| 1832363 | 2024-02-09 | 8:01 | 2024-02-09 | 9:11 | MTN21 | MORNINGTON | Urban | Asset Failure | LV | 1 | 69.0667 | 69.0667 | 1 | Yes
| 1832364 | 2024-02-09 | 8:02 | 2024-02-09 | 18:02 | CRM33 | CARRUM | Urban | Weather |  | 1 | 599.7167 | 599.7167 | 1 | Yes
| 1832372 | 2024-02-09 | 8:05 | 2024-02-09 | 8:52 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 0 | 36497.8408 | 47.0333 | 1 | Yes
| 1832378 | 2024-02-09 | 8:07 | 2024-03-09 | 16:25 | HGS23 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 5811.2001 | 1937.0667 | 1 | Yes
| 1832410 | 2024-02-09 | 8:25 | 2024-02-09 | 21:10 | NW21 | NUNAWADING | Urban | Asset Failure | LV | 32.01 | 24482.8485 | 764.85 | 1 | Yes
| 1833282 | 2024-02-09 | 8:27 | 2024-02-09 | 23:00 | RWT24 | RINGWOOD | Urban | Weather |  | 207 | 180662.7069 | 872.7667 | 1 | Yes
| 1832449 | 2024-02-09 | 8:52 | 2024-02-09 | 9:55 | FTN23 | FRANKSTON | Urban | Vegetation | Grow-in - NSP responsibility | 187 | 11715.55 | 62.65 | 1 | Yes
| 1832451 | 2024-02-09 | 8:52 | 2024-02-09 | 11:46 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 173.0167 | 173.0167 | 1 | Yes
| 1832449 | 2024-02-09 | 8:53 | 2024-02-09 | 9:53 | FTN23 | FRANKSTON | Urban | Vegetation | Grow-in - NSP responsibility | 1351 | 81375.1883 | 60.2333 | 1 | Yes
| 1832449 | 2024-02-09 | 8:53 | 2024-02-09 | 9:55 | FTN23 | FRANKSTON | Urban | Vegetation | Grow-in - NSP responsibility | 1424 | 88572.8 | 62.2 | 2 | Yes
| 1832459 | 2024-02-09 | 8:56 | 2024-02-09 | 11:20 | CM13 | CHELTENHAM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 143.4167 | 143.4167 | 1 | Yes
| 1832490 | 2024-02-09 | 9:16 | 2024-02-09 | 10:58 | DMA24 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 152 | 15372.2616 | 101.1333 | 1 | Yes
| 1832490 | 2024-02-09 | 9:16 | 2024-04-09 | 14:13 | DMA24 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 3 | 9529.4499 | 3176.4833 | 2 | Yes
| 1832959 | 2024-02-09 | 9:20 | 2024-03-09 | 16:37 | FSH31 | FRANKSTON SOUTH | Urban | Weather |  | 34 | 63814.0322 | 1876.8833 | 1 | Yes
| 1832561 | 2024-02-09 | 9:33 | 2024-03-09 | 16:11 | DMA23 | DROMANA | Rural Short | Weather |  | 4 | 7351.7332 | 1837.9333 | 1 | Yes
| 1832514 | 2024-02-09 | 9:34 | 2024-03-09 | 3:15 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 1061 | 1061 | 1 | Yes
| 1832532 | 2024-02-09 | 9:50 | 2024-02-09 | 20:03 | NW21 | NUNAWADING | Urban | Weather |  | 39 | 23915.4513 | 613.2167 | 1 | Yes
| 1832605 | 2024-02-09 | 10:24 | 2024-02-09 | 19:21 | DMA13 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 536.9333 | 536.9333 | 1 | Yes
| 1831955 | 2024-02-09 | 10:34 | 2024-02-09 | 15:20 | FSH21 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 3 | 860.6001 | 286.8667 | 1 | Yes
| 1832655 | 2024-02-09 | 10:47 | 2024-02-09 | 16:54 | MR24 | MOORABBIN | Urban | Asset Failure | LV | 1 | 366.7667 | 366.7667 | 1 | Yes
| 1832658 | 2024-02-09 | 10:48 | 2024-03-09 | 3:30 | SVW53 | SPRINGVALE WEST | Urban | Asset Failure | HV | 1 | 1002.0167 | 1002.0167 | 1 | Yes
| 1832659 | 2024-02-09 | 10:48 | 2024-02-09 | 22:40 | DMA14 | DROMANA | Urban | Asset Failure | Distribution substation | 25.74 | 18311.436 | 711.4 | 1 | Yes
| 1832660 | 2024-02-09 | 10:49 | 2024-03-09 | 0:42 | MGE23 | MULGRAVE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 832.5333 | 832.5333 | 1 | Yes
| 1832679 | 2024-02-09 | 11:05 | 2024-02-09 | 13:18 | HGS22 | HASTINGS | Rural Short | Weather |  | 1 | 132.4333 | 132.4333 | 1 | Yes
| 1832136 | 2024-02-09 | 11:15 | 2024-02-09 | 17:40 | HGS22 | HASTINGS | Rural Short | Weather |  | 54 | 20776.5 | 384.75 | 1 | Yes
| 1832696 | 2024-02-09 | 11:20 | 2024-03-09 | 16:50 | HGS33 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 4.02 | 7111.983 | 1769.15 | 1 | Yes
| 1833710 | 2024-02-09 | 11:54 | 2024-03-09 | 17:30 | MTN32 | MORNINGTON | Rural Short | Asset Failure | HV | 1 | 1775.1 | 1775.1 | 1 | Yes
| 1832733 | 2024-02-09 | 11:55 | 2024-04-09 | 8:57 | DMA21 | DROMANA | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 2701.7333 | 2701.7333 | 1 | Yes
| 1831717 | 2024-02-09 | 11:57 | 2024-02-09 | 23:33 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 696.3833 | 696.3833 | 1 | Yes
| 1832754 | 2024-02-09 | 12:05 | 2024-02-09 | 19:00 | CRM13 | CARRUM | Urban | Weather |  | 243.21 | 100753.8041 | 414.2667 | 1 | Yes
| 1832756 | 2024-02-09 | 12:10 | 2024-02-09 | 19:32 | CDA24 | CLARINDA | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 18 | 7943.0994 | 441.2833 | 1 | Yes
| 1833202 | 2024-02-09 | 12:21 | 2024-02-09 | 22:50 | EB32 | EAST BURWOOD | Urban | Weather |  | 31 | 19486.6 | 628.6 | 1 | Yes
| 1832776 | 2024-02-09 | 12:28 | 2024-03-09 | 1:00 | SH22 | SURREY HILLS | Urban | Overloads |  | 1 | 751.3667 | 751.3667 | 1 | Yes
| 1832827 | 2024-02-09 | 12:39 | 2024-03-09 | 1:43 | DMA24 | DROMANA | Rural Short | Third Party | Other | 1 | 783.7333 | 783.7333 | 1 | Yes
| 1832859 | 2024-02-09 | 12:42 | 2024-02-09 | 13:22 | K23 | GARDINER | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 72 | 2877.6024 | 39.9667 | 1 | Yes
| 1832859 | 2024-02-09 | 12:42 | 2024-02-09 | 14:23 | K23 | GARDINER | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 49 | 4952.2683 | 101.0667 | 2 | Yes
| 1832859 | 2024-02-09 | 12:42 | 2024-02-09 | 17:23 | K23 | GARDINER | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 275 | 77375.8425 | 281.3667 | 3 | Yes
| 1832865 | 2024-02-09 | 12:44 | 2024-02-09 | 18:39 | BW35 | BURWOOD | Urban | Unknown | Unknown | 1 | 354.3 | 354.3 | 1 | Yes
| 1831653 | 2024-02-09 | 12:45 | 2024-03-09 | 9:15 | STO21 | SORRENTO | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 1230 | 1230 | 1 | Yes
| 1832890 | 2024-02-09 | 12:52 | 2024-02-09 | 16:50 | SS12 | SPRINGVALE SOUTH | Urban | Weather |  | 13.53 | 3207.963 | 237.1 | 1 | Yes
| 1832902 | 2024-02-09 | 12:56 | 2024-02-09 | 19:35 | NP36 | NOBLE PARK | Urban | Weather |  | 76 | 30336.6692 | 399.1667 | 1 | Yes
| 1832929 | 2024-02-09 | 13:17 | 2024-02-09 | 18:13 | NP12 | NOBLE PARK | Urban | Overloads |  | 28.05 | 8281.2941 | 295.2333 | 1 | Yes
| 1832941 | 2024-02-09 | 13:32 | 2024-03-09 | 4:13 | BW23 | BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 881.4333 | 881.4333 | 1 | Yes
| 1832944 | 2024-02-09 | 13:35 | 2024-03-09 | 21:43 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 1927.1167 | 1927.1167 | 1 | Yes
| 1832963 | 2024-02-09 | 13:57 | 2024-03-09 | 12:19 | LWN21 | LANGWARRIN | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 1341.8833 | 1341.8833 | 1 | Yes
| 1832966 | 2024-02-09 | 14:01 | 2024-03-09 | 2:01 | BR13 | BEAUMARIS | Urban | Weather |  | 1 | 720.3833 | 720.3833 | 1 | Yes
| 1832973 | 2024-02-09 | 14:10 | 2024-02-09 | 14:25 | SVW53 | SPRINGVALE WEST | Urban | Weather |  | 39 | 589.5513 | 15.1167 | 1 | Yes
| 1832981 | 2024-02-09 | 14:18 | 2024-02-09 | 15:46 | HT2 | HEATHERTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 3 | 264.6999 | 88.2333 | 1 | Yes
| 1832982 | 2024-02-09 | 14:19 | 2024-03-09 | 1:26 | EB12 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 12.21 | 8144.07 | 667 | 1 | Yes
| 1832984 | 2024-02-09 | 14:22 | 2024-03-09 | 1:12 | RD4 | RIVERSDALE | Urban | Weather |  | 48 | 31207.2 | 650.15 | 1 | Yes
| 1832983 | 2024-02-09 | 14:24 | 2024-03-09 | 5:05 | MGE34 | MULGRAVE | Urban | Asset Failure | LV | 1 | 880.8167 | 880.8167 | 1 | Yes
| 1832987 | 2024-02-09 | 14:32 | 2024-03-09 | 1:12 | RD4 | RIVERSDALE | Urban | Weather |  | 23 | 14717.7 | 639.9 | 1 | Yes
| 1833004 | 2024-02-09 | 14:46 | 2024-02-09 | 22:51 | EB31 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 484.2667 | 484.2667 | 1 | Yes
| 1833009 | 2024-02-09 | 14:51 | 2024-02-09 | 22:05 | NW21 | NUNAWADING | Urban | Asset Failure | LV | 10.56 | 4576.8804 | 433.4167 | 1 | Yes
| 1833014 | 2024-02-09 | 14:54 | 2024-02-09 | 15:15 | SVW53 | SPRINGVALE WEST | Urban | Weather |  | 39 | 797.55 | 20.45 | 1 | Yes
| 1833035 | 2024-02-09 | 15:15 | 2024-02-09 | 21:17 | BH11 | BOX HILL | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 362.65 | 362.65 | 1 | Yes
| 1833045 | 2024-02-09 | 15:21 | 2024-02-09 | 21:30 | FTN13 | FRANKSTON | Urban | Unknown | Unknown | 3.96 | 1459.5241 | 368.5667 | 1 | Yes
| 1833052 | 2024-02-09 | 15:24 | 2024-03-09 | 3:00 | LD4 | LYNDALE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 26 | 18082.1342 | 695.4667 | 1 | Yes
| 1833066 | 2024-02-09 | 15:41 | 2024-02-09 | 16:37 | RWT34 | RINGWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 37 | 2049.8 | 55.4 | 1 | Yes
| 1833068 | 2024-02-09 | 15:45 | 2024-02-09 | 17:30 | FTN11 | FRANKSTON | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 25 | 2607.5 | 104.3 | 1 | Yes
| 1832323 | 2024-02-09 | 16:00 | 2024-03-09 | 14:20 | SS11 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 1340 | 1340 | 1 | Yes
| 1833081 | 2024-02-09 | 16:04 | 2024-03-09 | 2:05 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 601.1 | 601.1 | 1 | Yes
| 1833083 | 2024-02-09 | 16:06 | 2024-03-09 | 14:55 | MC34 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 1368.6667 | 1368.6667 | 1 | Yes
| 1833125 | 2024-02-09 | 16:33 | 2024-04-09 | 7:33 | DMA21 | DROMANA | Urban | Asset Failure | LV | 1 | 2340.1333 | 2340.1333 | 1 | Yes
| 1833134 | 2024-02-09 | 16:39 | 2024-03-09 | 3:48 | NP33 | NOBLE PARK | Urban | Asset Failure | LV | 71 | 47475.3357 | 668.6667 | 1 | Yes
| 1833145 | 2024-02-09 | 16:44 | 2024-03-09 | 2:47 | FSH12 | FRANKSTON SOUTH | Rural Short | Weather |  | 27 | 16289.9991 | 603.3333 | 1 | Yes
| 1833151 | 2024-02-09 | 16:48 | 2024-03-09 | 14:45 | DVY34 | DANDENONG VALLEY | Urban | Animal | Animal impact | 1 | 1317 | 1317 | 1 | Yes
| 1833153 | 2024-02-09 | 16:49 | 2024-03-09 | 12:59 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 1209.6 | 1209.6 | 1 | Yes
| 1833162 | 2024-02-09 | 16:56 | 2024-03-09 | 12:16 | DMA13 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 29 | 33636.1343 | 1159.8667 | 1 | Yes
| 1833174 | 2024-02-09 | 17:07 | 2024-03-09 | 1:25 | BR4 | BEAUMARIS | Urban | Weather |  | 51 | 25431.15 | 498.65 | 1 | Yes
| 1833185 | 2024-02-09 | 17:08 | 2024-03-09 | 2:20 | CRM15 | CARRUM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 70.29 | 38734.4783 | 551.0667 | 1 | Yes
| 1833200 | 2024-02-09 | 17:27 | 2024-03-09 | 13:43 | WD14 | WEST DONCASTER | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 1216.05 | 1216.05 | 1 | Yes
| 1833217 | 2024-02-09 | 17:51 | 2024-02-09 | 19:20 | BW35 | BURWOOD | Urban | Weather |  | 1 | 88.1667 | 88.1667 | 1 | Yes
| 1833219 | 2024-02-09 | 17:53 | 2024-02-09 | 19:06 | BW35 | BURWOOD | Urban | Weather |  | 1 | 72.2 | 72.2 | 1 | Yes
| 1833221 | 2024-02-09 | 17:55 | 2024-02-09 | 19:17 | BW35 | BURWOOD | Urban | Weather |  | 1 | 81.9167 | 81.9167 | 1 | Yes
| 1833224 | 2024-02-09 | 17:56 | 2024-02-09 | 19:07 | BW35 | BURWOOD | Urban | Weather |  | 1 | 70.7333 | 70.7333 | 1 | Yes
| 1833227 | 2024-02-09 | 17:58 | 2024-03-09 | 6:28 | FSH31 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 749.2833 | 749.2833 | 1 | Yes
| 1833234 | 2024-02-09 | 18:07 | 2024-02-09 | 21:57 | MTN32 | MORNINGTON | Rural Short | Weather |  | 57 | 13110 | 230 | 1 | Yes
| 1833246 | 2024-02-09 | 18:22 | 2024-03-09 | 0:47 | LD6 | LYNDALE | Urban | Asset Failure | HV | 24.42 | 9398.037 | 384.85 | 1 | Yes
| 1833251 | 2024-02-09 | 18:32 | 2024-02-09 | 19:19 | NW22 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 19 | 874.95 | 46.05 | 1 | Yes
| 1833253 | 2024-02-09 | 18:39 | 2024-03-09 | 14:35 | FTN13 | FRANKSTON | Urban | Asset Failure | LV | 1 | 1195.9167 | 1195.9167 | 1 | Yes
| 1833254 | 2024-02-09 | 18:41 | 2024-02-09 | 22:40 | KBH32 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 239 | 239 | 1 | Yes
| 1833256 | 2024-02-09 | 18:42 | 2024-03-09 | 4:06 | MTN35 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 564.2667 | 564.2667 | 1 | Yes
| 1833258 | 2024-02-09 | 18:45 | 2024-03-09 | 11:30 | FSH21 | FRANKSTON SOUTH | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 1004.9167 | 1004.9167 | 1 | Yes
| 1833272 | 2024-02-09 | 19:01 | 2024-02-09 | 20:01 | HGS21 | HASTINGS | Rural Short | Asset Failure | HV | 377 | 22601.15 | 59.95 | 1 | Yes
| 1833297 | 2024-02-09 | 19:05 | 2024-02-09 | 20:55 | HGS21 | HASTINGS | Rural Short | Asset Failure | HV | 257 | 28184.3419 | 109.6667 | 1 | Yes
| 1833297 | 2024-02-09 | 19:05 | 2024-02-09 | 20:50 | HGS21 | HASTINGS | Rural Short | Asset Failure | HV | 120 | 12626.004 | 105.2167 | 1 | Yes
| 1833278 | 2024-02-09 | 19:13 | 2024-03-09 | 7:04 | LWN35 | LANGWARRIN | Urban | Asset Failure | Distribution substation | 103 | 73145.45 | 710.15 | 1 | Yes
| 1833281 | 2024-02-09 | 19:22 | 2024-03-09 | 12:24 | FSH13 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 1 | 1021.9167 | 1021.9167 | 1 | Yes
| 1833286 | 2024-02-09 | 19:33 | 2024-02-09 | 21:32 | BC11 | BALACLAVA | Urban | Weather |  | 103 | 12251.85 | 118.95 | 1 | Yes
| 1833309 | 2024-02-09 | 20:30 | 2024-03-09 | 2:50 | FTN12 | FRANKSTON | Urban | Weather |  | 24.79 | 9414.828 | 379.7833 | 1 | Yes
| 1833316 | 2024-02-09 | 20:44 | 2024-03-09 | 5:44 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 539.2667 | 539.2667 | 1 | Yes
| 1833317 | 2024-02-09 | 20:47 | 2024-03-09 | 1:51 | EM6 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 303.4667 | 303.4667 | 1 | Yes
| 1831658 | 2024-02-09 | 20:51 | 2024-03-09 | 3:26 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 395 | 395 | 1 | Yes
| 1833320 | 2024-02-09 | 20:58 | 2024-03-09 | 12:25 | FSH13 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 1 | 926.9667 | 926.9667 | 1 | Yes
| 1833323 | 2024-02-09 | 21:03 | 2024-03-09 | 1:48 | OAK26 | OAKLEIGH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 285.65 | 285.65 | 1 | Yes
| 1833325 | 2024-02-09 | 21:06 | 2024-03-09 | 0:16 | DMA14 | DROMANA | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 190.0167 | 190.0167 | 1 | Yes
| 1833328 | 2024-02-09 | 21:10 | 2024-03-09 | 5:00 | FSH21 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 25.46 | 11965.3522 | 469.9667 | 1 | Yes
| 1833339 | 2024-02-09 | 21:42 | 2024-03-09 | 12:24 | FSH13 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 1 | 881.6333 | 881.6333 | 1 | Yes
| 1833342 | 2024-02-09 | 21:57 | 2024-02-09 | 22:03 | NW21 | NUNAWADING | Urban | Asset Failure | HV | 495 | 2936.9835 | 5.9333 | 1 | Yes
| 1833347 | 2024-02-09 | 22:12 | 2024-03-09 | 2:43 | DMA13 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 270.9667 | 270.9667 | 1 | Yes
| 1833351 | 2024-02-09 | 22:49 | 2024-03-09 | 2:48 | DMA13 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 238.6667 | 238.6667 | 1 | Yes
| 1833352 | 2024-02-09 | 22:53 | 2024-03-09 | 16:45 | GW11 | GLEN WAVERLEY | Urban | Vegetation | Grow-in - NSP responsibility | 27 | 28918.35 | 1071.05 | 1 | Yes
| 1833360 | 2024-02-09 | 23:57 | 2024-03-09 | 0:51 | EB33 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 90 | 4852.503 | 53.9167 | 1 | Yes
| 1833362 | 2024-03-09 | 0:10 | 2024-03-09 | 0:20 | EB22 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 62 | 584.8646 | 9.4333 | 1 | No
| 1833363 | 2024-03-09 | 0:14 | 2024-03-09 | 14:48 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 5 | 4374.5 | 874.9 | 1 | No
| 1833367 | 2024-03-09 | 0:49 | 2024-03-09 | 14:47 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 40 | 33519.332 | 837.9833 | 1 | No
| 1833376 | 2024-03-09 | 2:57 | 2024-03-09 | 3:25 | SVW53 | SPRINGVALE WEST | Urban | Weather |  | 1 | 28.2333 | 28.2333 | 1 | No
| 1833374 | 2024-03-09 | 5:31 | 2024-04-09 | 0:17 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 1 | 1126.2667 | 1126.2667 | 1 | No
| 1833385 | 2024-03-09 | 5:48 | 2024-03-09 | 6:15 | RWT24 | RINGWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 66 | 1820.4978 | 27.5833 | 1 | No
| 1833398 | 2024-03-09 | 6:47 | 2024-03-09 | 9:08 | BW34 | BURWOOD | Urban | Asset Failure | LV | 1 | 141.5167 | 141.5167 | 1 | No
| 1833403 | 2024-03-09 | 6:59 | 2024-03-09 | 8:20 | BW35 | BURWOOD | Urban | Asset Failure | LV | 1 | 81.6833 | 81.6833 | 1 | No
| 1833405 | 2024-03-09 | 7:10 | 2024-03-09 | 14:02 | STO22 | SORRENTO | Urban | Third Party | Other | 1 | 411.6667 | 411.6667 | 1 | No
| 1833379 | 2024-03-09 | 7:48 | 2024-03-09 | 14:23 | STO22 | SORRENTO | Urban | Third Party | Other | 1 | 395 | 395 | 1 | No
| 1833415 | 2024-03-09 | 7:52 | 2024-03-09 | 10:15 | LD7 | LYNDALE | Urban | Weather |  | 1 | 142.75 | 142.75 | 1 | No
| 1833436 | 2024-03-09 | 8:18 | 2024-03-09 | 10:40 | MTN22 | MORNINGTON | Rural Short | Overloads |  | 19 | 2680.2673 | 141.0667 | 1 | No
| 1833449 | 2024-03-09 | 8:36 | 2024-03-09 | 13:15 | EM5 | EAST MALVERN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 279.2167 | 279.2167 | 1 | No
| 1833474 | 2024-03-09 | 9:17 | 2024-03-09 | 21:00 | HT7 | HEATHERTON | Urban | Asset Failure | LV | 1 | 702.0333 | 702.0333 | 1 | No
| 1833513 | 2024-03-09 | 10:20 | 2024-03-09 | 12:37 | EW8 | ELWOOD | Urban | Asset Failure | LV | 26.4 | 3622.08 | 137.2 | 1 | No
| 1832226 | 2024-03-09 | 10:44 | 2024-03-09 | 11:53 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 69.5167 | 69.5167 | 1 | No
| 1833569 | 2024-03-09 | 11:41 | 2024-03-09 | 14:20 | EM5 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 158.45 | 158.45 | 1 | No
| 1833589 | 2024-03-09 | 12:16 | 2024-04-09 | 1:28 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 791.4667 | 791.4667 | 1 | No
| 1833622 | 2024-03-09 | 13:20 | 2024-03-09 | 19:45 | DMA24 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 384.3 | 384.3 | 1 | No
| 1833640 | 2024-03-09 | 13:46 | 2024-03-09 | 17:04 | STO21 | SORRENTO | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 197.9167 | 197.9167 | 1 | No
| 1833659 | 2024-03-09 | 14:32 | 2024-03-09 | 19:10 | RWT23 | RINGWOOD | Urban | Asset Failure | LV | 1 | 277.15 | 277.15 | 1 | No
| 1833669 | 2024-03-09 | 14:46 | 2024-03-09 | 18:55 | DMA23 | DROMANA | Rural Short | Asset Failure | Distribution substation | 4.02 | 998.4341 | 248.3667 | 1 | No
| 1833690 | 2024-03-09 | 15:19 | 2024-03-09 | 19:30 | NP33 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 250.2833 | 250.2833 | 1 | No
| 1833705 | 2024-03-09 | 15:56 | 2024-03-09 | 22:30 | CFD22 | CAULFIELD | Urban | Asset Failure | LV | 1 | 393.2333 | 393.2333 | 1 | No
| 1833715 | 2024-03-09 | 16:21 | 2024-04-09 | 5:09 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 767.7833 | 767.7833 | 1 | No
| 1833732 | 2024-03-09 | 16:37 | 2024-03-09 | 23:08 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 5 | 1950.9165 | 390.1833 | 1 | No
| 1833746 | 2024-03-09 | 17:19 | 2024-03-09 | 20:58 | RBD13 | ROSEBUD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 17 | 3718.4661 | 218.7333 | 1 | No
| 1833751 | 2024-03-09 | 17:28 | 2024-03-09 | 21:05 | DMA13 | DROMANA | Rural Short | Unknown | Unknown | 1 | 216.8 | 216.8 | 1 | No
| 1833753 | 2024-03-09 | 17:29 | 2024-03-09 | 18:50 | BW35 | BURWOOD | Urban | Asset Failure | LV | 1 | 80.7333 | 80.7333 | 1 | No
| 1831651 | 2024-03-09 | 17:46 | 2024-03-09 | 21:52 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 2 | 492.0334 | 246.0167 | 1 | No
| 1833786 | 2024-03-09 | 19:30 | 2024-03-09 | 22:26 | BH12 | BOX HILL | Urban | Asset Failure | LV | 1 | 176.6833 | 176.6833 | 1 | No
| 1833783 | 2024-03-09 | 19:34 | 2024-04-09 | 3:32 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 1 | 478 | 478 | 1 | No
| 1833824 | 2024-04-09 | 2:00 | 2024-04-09 | 2:51 | RBD12 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 63 | 3224.5479 | 51.1833 | 1 | No
| 1833830 | 2024-04-09 | 4:14 | 2024-04-09 | 6:05 | DC1 | DONCASTER | Urban | Animal | Animal impact | 28.38 | 3168.627 | 111.65 | 1 | No
| 1833909 | 2024-04-09 | 9:46 | 2024-04-09 | 16:50 | EL31 | ELSTERNWICK | Urban | Weather |  | 1 | 423.6833 | 423.6833 | 1 | No
| 1833818 | 2024-04-09 | 11:04 | 2024-04-09 | 16:17 | LD2 | LYNDALE | Urban | Asset Failure | LV | 1 | 313.35 | 313.35 | 1 | No
| 1834002 | 2024-04-09 | 12:10 | 2024-04-09 | 17:26 | CDA22 | CLARINDA | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 316.4333 | 316.4333 | 1 | No
| 1834038 | 2024-04-09 | 13:27 | 2024-04-09 | 18:31 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 303.7333 | 303.7333 | 1 | No
| 1834069 | 2024-04-09 | 14:33 | 2024-04-09 | 16:32 | SV34 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 118.85 | 118.85 | 1 | No
| 1834119 | 2024-04-09 | 18:30 | 2024-04-09 | 21:46 | M13 | MENTONE | Urban | Asset Failure | LV | 5 | 983.9165 | 196.7833 | 1 | No
| 1834110 | 2024-04-09 | 18:43 | 2024-04-09 | 19:25 | MR12 | MOORABBIN | Urban | Asset Failure | LV | 1 | 42.6667 | 42.6667 | 1 | No
| 1834141 | 2024-04-09 | 20:52 | 2024-05-09 | 0:55 | DN13 | DANDENONG | Urban | Weather |  | 150 | 36332.505 | 242.2167 | 1 | No
| 1834143 | 2024-04-09 | 21:08 | 2024-05-09 | 0:46 | DN13 | DANDENONG | Urban | Weather |  | 30 | 6517.5 | 217.25 | 1 | No
| 1834144 | 2024-04-09 | 21:16 | 2024-05-09 | 0:50 | DN13 | DANDENONG | Urban | Weather |  | 88 | 18777.7304 | 213.3833 | 1 | No
| 1834146 | 2024-04-09 | 21:26 | 2024-05-09 | 0:44 | DN13 | DANDENONG | Urban | Weather |  | 82 | 16158.1 | 197.05 | 1 | No
| 1834151 | 2024-04-09 | 22:50 | 2024-04-09 | 23:00 | GW6 | GLEN WAVERLEY | Urban | Weather |  | 439 | 4309.5313 | 9.8167 | 1 | No
| 1834166 | 2024-05-09 | 3:43 | 2024-05-09 | 5:40 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 4 | 465.6668 | 116.4167 | 1 | No
| 1834178 | 2024-05-09 | 6:40 | 2024-05-09 | 6:46 | CFD16 | CAULFIELD | Urban | Weather |  | 173 | 1009.1609 | 5.8333 | 1 | No
| 1834178 | 2024-05-09 | 6:40 | 2024-05-09 | 6:49 | CFD16 | CAULFIELD | Urban | Weather |  | 686 | 6539.8438 | 9.5333 | 2 | No
| 1834178 | 2024-05-09 | 6:40 | 2024-05-09 | 7:11 | CFD16 | CAULFIELD | Urban | Weather |  | 463 | 14275.8179 | 30.8333 | 3 | No
| 1834178 | 2024-05-09 | 6:40 | 2024-05-09 | 8:19 | CFD16 | CAULFIELD | Urban | Weather |  | 169 | 16823.95 | 99.55 | 4 | No
| 1834177 | 2024-05-09 | 6:40 | 2024-05-09 | 7:11 | AR7 | ARMADALE | Urban | Weather |  | 299 | 9358.7 | 31.3 | 1 | No
| 1834189 | 2024-05-09 | 7:12 | 2024-05-09 | 8:30 | AR7 | ARMADALE | Urban | Weather |  | 0 | 9969.0624 | 77.8833 | 1 | No
| 1834192 | 2024-05-09 | 7:27 | 2024-05-09 | 8:47 | GW11 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 80.1 | 80.1 | 1 | No
| 1834197 | 2024-05-09 | 7:36 | 2024-05-09 | 11:30 | DN10 | DANDENONG | Urban | Third Party | Other | 1 | 233.7333 | 233.7333 | 1 | No
| 1834198 | 2024-05-09 | 7:37 | 2024-05-09 | 9:25 | FTN11 | FRANKSTON | Urban | Asset Failure | HV | 25 | 2686.6675 | 107.4667 | 1 | No
| 1834158 | 2024-05-09 | 7:46 | 2024-05-09 | 9:50 | FSH11 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 1 | 124 | 124 | 1 | No
| 1834188 | 2024-05-09 | 7:49 | 2024-05-09 | 12:03 | BW32 | BURWOOD | Urban | Asset Failure | LV | 1 | 253.25 | 253.25 | 1 | No
| 1834182 | 2024-05-09 | 8:12 | 2024-05-09 | 11:05 | GW2 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 173.1667 | 173.1667 | 1 | No
| 1834296 | 2024-05-09 | 10:00 | 2024-05-09 | 13:44 | LWN34 | LANGWARRIN | Urban | Third Party | Other | 1 | 224.1167 | 224.1167 | 1 | No
| 1834306 | 2024-05-09 | 10:13 | 2024-05-09 | 13:13 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 180.65 | 180.65 | 1 | No
| 1834317 | 2024-05-09 | 10:28 | 2024-05-09 | 12:29 | FSH21 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 120.1833 | 120.1833 | 1 | No
| 1834401 | 2024-05-09 | 12:44 | 2024-05-09 | 12:58 | DMA15 | DROMANA | Rural Short | Other | XXX | 1 | 13.4333 | 13.4333 | 1 | No
| 1834565 | 2024-05-09 | 13:33 | 2024-06-09 | 8:33 | DVY12 | DANDENONG VALLEY | Urban | Animal | Animal impact | 0.67 | 763.2305 | 1139.15 | 1 | No
| 1834424 | 2024-05-09 | 14:06 | 2024-05-09 | 17:00 | BU25 | BULLEEN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 174.45 | 174.45 | 1 | No
| 1834452 | 2024-05-09 | 17:00 | 2024-05-09 | 19:20 | LWN24 | LANGWARRIN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 140.4333 | 140.4333 | 1 | No
| 1834457 | 2024-05-09 | 18:23 | 2024-05-09 | 20:28 | RBD21 | ROSEBUD | Rural Short | Vegetation | Grow-in - NSP responsibility | 271 | 33685.3 | 124.3 | 1 | No
| 1834459 | 2024-05-09 | 18:28 | 2024-05-09 | 20:57 | WD15 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 149.4833 | 149.4833 | 1 | No
| 1834477 | 2024-05-09 | 19:00 | 2024-05-09 | 22:30 | MR21 | MOORABBIN | Urban | Asset Failure | LV | 1 | 210.6667 | 210.6667 | 1 | No
| 1834338 | 2024-05-09 | 20:08 | 2024-06-09 | 0:09 | OR25 | ORMOND | Urban | Asset Failure | LV | 1 | 241.9833 | 241.9833 | 1 | No
| 1834511 | 2024-06-09 | 3:54 | 2024-06-09 | 6:01 | K31 | GARDINER | Urban | Animal | Animal impact | 15.41 | 1956.0422 | 126.9333 | 1 | No
| 1834545 | 2024-06-09 | 7:58 | 2024-06-09 | 10:15 | HT1 | HEATHERTON | Urban | Third Party | Vehicle Impact | 30.36 | 4150.212 | 136.7 | 1 | No
| 1834578 | 2024-06-09 | 8:44 | 2024-06-09 | 10:21 | DMA15 | DROMANA | Rural Short | Asset Failure | LV | 1 | 96.7833 | 96.7833 | 1 | No
| 1834599 | 2024-06-09 | 9:25 | 2024-06-09 | 11:21 | EL23 | ELSTERNWICK | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 116.0833 | 116.0833 | 1 | No
| 1834607 | 2024-06-09 | 9:38 | 2024-06-09 | 11:40 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 121.25 | 121.25 | 1 | No
| 1834625 | 2024-06-09 | 10:04 | 2024-06-09 | 11:34 | EM5 | EAST MALVERN | Urban | Third Party | Dig-in | 1 | 90.3333 | 90.3333 | 1 | No
| 1834643 | 2024-06-09 | 10:31 | 2024-06-09 | 12:03 | BW33 | BURWOOD | Urban | Third Party | Other | 1 | 91.6833 | 91.6833 | 1 | No
| 1834666 | 2024-06-09 | 11:22 | 2024-06-09 | 16:05 | OE6 | OAKLEIGH EAST | Urban | Third Party | Other | 1 | 282.1667 | 282.1667 | 1 | No
| 1834712 | 2024-06-09 | 12:44 | 2024-06-09 | 13:36 | BH11 | BOX HILL | Urban | Vegetation | Grow-in - NSP responsibility | 344 | 17744.6552 | 51.5833 | 1 | No
| 1834750 | 2024-06-09 | 14:15 | 2024-06-09 | 17:25 | NW33 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 65 | 12350 | 190 | 1 | No
| 1834752 | 2024-06-09 | 14:16 | 2024-06-09 | 17:22 | NW33 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 94 | 17454.2302 | 185.6833 | 1 | No
| 1834363 | 2024-06-09 | 15:24 | 2024-06-09 | 20:03 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 279.5833 | 279.5833 | 1 | No
| 1834778 | 2024-06-09 | 15:35 | 2024-06-09 | 18:51 | NW23 | NUNAWADING | Urban | Third Party | Other | 1 | 195.8333 | 195.8333 | 1 | No
| 1834819 | 2024-06-09 | 20:56 | 2024-07-09 | 1:22 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 265.4 | 265.4 | 1 | No
| 1834820 | 2024-06-09 | 21:01 | 2024-07-09 | 4:20 | BW22 | BURWOOD | Urban | Third Party | Vehicle Impact | 10 | 4386.333 | 438.6333 | 1 | No
| 1834821 | 2024-06-09 | 21:14 | 2024-07-09 | 4:29 | BW22 | BURWOOD | Urban | Third Party | Vehicle Impact | 1 | 434.7333 | 434.7333 | 1 | No
| 1834828 | 2024-06-09 | 22:41 | 2024-07-09 | 21:45 | CFD14 | CAULFIELD | Urban | Asset Failure | LV | 1 | 1383.5667 | 1383.5667 | 1 | No
| 1834829 | 2024-06-09 | 23:20 | 2024-07-09 | 1:59 | HGS31 | HASTINGS | Rural Short | Asset Failure | LV | 42 | 6654.9 | 158.45 | 1 | No
| 1834856 | 2024-07-09 | 9:39 | 2024-07-09 | 16:29 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 409.8333 | 409.8333 | 1 | No
| 1834864 | 2024-07-09 | 10:12 | 2024-07-09 | 10:54 | MTN22 | MORNINGTON | Rural Short | Vegetation | Grow-in - Other responsible party | 35 | 1474.0845 | 42.1167 | 1 | No
| 1834832 | 2024-07-09 | 10:27 | 2024-07-09 | 17:10 | SS12 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 403 | 403 | 1 | No
| 1834976 | 2024-07-09 | 11:43 | 2024-07-09 | 14:04 | BT21 | BENTLEIGH | Urban | Asset Failure | Distribution substation | 25.46 | 3566.946 | 140.1 | 1 | No
| 1834840 | 2024-07-09 | 12:02 | 2024-07-09 | 17:16 | SV34 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 314.4167 | 314.4167 | 1 | No
| 1834895 | 2024-07-09 | 12:41 | 2024-07-09 | 18:05 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 323.6667 | 323.6667 | 1 | No
| 1834902 | 2024-07-09 | 13:11 | 2024-07-09 | 15:01 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 109.8833 | 109.8833 | 1 | No
| 1834922 | 2024-07-09 | 15:20 | 2024-07-09 | 18:30 | HT11 | HEATHERTON | Urban | Third Party | Vehicle Impact | 63 | 12000.4479 | 190.4833 | 1 | No
| 1834930 | 2024-07-09 | 16:41 | 2024-07-09 | 18:45 | STO23 | SORRENTO | Urban | Asset Failure | LV | 18.48 | 2291.52 | 124 | 1 | No
| 1834932 | 2024-07-09 | 16:58 | 2024-07-09 | 18:00 | RBD14 | ROSEBUD | Urban | Asset Failure | LV | 59.07 | 3662.34 | 62 | 1 | No
| 1834937 | 2024-07-09 | 17:04 | 2024-07-09 | 19:23 | MC21 | MORDIALLOC | Urban | Third Party | Other | 1 | 139.0667 | 139.0667 | 1 | No
| 1834926 | 2024-07-09 | 17:06 | 2024-07-09 | 20:43 | MTN35 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 217.4333 | 217.4333 | 1 | No
| 1834950 | 2024-07-09 | 18:29 | 2024-07-09 | 20:23 | OR35 | ORMOND | Urban | Asset Failure | LV | 1 | 114.1 | 114.1 | 1 | No
| 1834923 | 2024-07-09 | 18:48 | 2024-07-09 | 22:54 | SV32 | SPRINGVALE | Urban | Third Party | Other | 1 | 246 | 246 | 1 | No
| 1834973 | 2024-07-09 | 23:06 | 2024-08-09 | 0:50 | DN25 | DANDENONG | Urban | Third Party | Other | 1 | 103.75 | 103.75 | 1 | No
| 1834983 | 2024-08-09 | 3:05 | 2024-08-09 | 4:26 | MC15 | MORDIALLOC | Urban | Animal | Animal impact | 83.08 | 6701.7894 | 80.6667 | 1 | No
| 1835003 | 2024-08-09 | 11:40 | 2024-08-09 | 13:03 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 15.18 | 1249.314 | 82.3 | 1 | No
| 1835006 | 2024-08-09 | 12:15 | 2024-08-09 | 21:50 | OR22 | ORMOND | Urban | Third Party | Other | 2 | 1148.7666 | 574.3833 | 1 | No
| 1835021 | 2024-08-09 | 13:45 | 2024-08-09 | 14:42 | RBD12 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 56.8 | 56.8 | 1 | No
| 1835022 | 2024-08-09 | 13:48 | 2024-08-09 | 15:10 | FSH31 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 1 | 81.2833 | 81.2833 | 1 | No
| 1835033 | 2024-08-09 | 15:49 | 2024-08-09 | 18:19 | EM7 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 149.2167 | 149.2167 | 1 | No
| 1835065 | 2024-08-09 | 17:07 | 2024-08-09 | 19:56 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 38.28 | 6469.32 | 169 | 1 | No
| 1835037 | 2024-08-09 | 17:23 | 2024-08-09 | 19:00 | HT7 | HEATHERTON | Urban | Asset Failure | LV | 9.57 | 928.29 | 97 | 1 | No
| 1835044 | 2024-08-09 | 17:30 | 2025-11-06 | 10:52 | OR31 | ORMOND | Urban | Third Party | Other | 1 | 397042.3833 | 397042.3833 | 1 | No
| 1835048 | 2024-08-09 | 18:07 | 2024-08-09 | 18:50 | DC2 | DONCASTER | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 774 | 33436.8 | 43.2 | 1 | No
| 1835059 | 2024-08-09 | 18:45 | 2024-08-09 | 21:51 | STO14 | SORRENTO | Rural Short | Asset Failure | HV | 5.94 | 1103.355 | 185.75 | 1 | No
| 1835062 | 2024-08-09 | 19:36 | 2024-08-09 | 22:51 | CM25 | CHELTENHAM | Urban | Asset Failure | LV | 1 | 194.8667 | 194.8667 | 1 | No
| 1835064 | 2024-08-09 | 19:46 | 2024-08-09 | 21:56 | CFD24 | CAULFIELD | Urban | Asset Failure | LV | 1 | 130.0333 | 130.0333 | 1 | No
| 1835079 | 2024-08-09 | 21:40 | 2024-09-09 | 0:02 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 1 | 141.3667 | 141.3667 | 1 | No
| 1835114 | 2024-09-09 | 7:41 | 2024-09-09 | 10:22 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 20 | 3218 | 160.9 | 1 | No
| 1835098 | 2024-09-09 | 7:52 | 2024-09-09 | 12:25 | LWN24 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 273.4 | 273.4 | 1 | No
| 1835102 | 2024-09-09 | 7:54 | 2024-09-09 | 11:23 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 209.2333 | 209.2333 | 1 | No
| 1835122 | 2024-09-09 | 8:18 | 2024-09-09 | 10:25 | SVW54 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 126.2 | 126.2 | 1 | No
| 1835131 | 2024-09-09 | 8:33 | 2024-09-09 | 11:25 | SVW42 | SPRINGVALE WEST | Urban | Overloads |  | 0.66 | 113.3 | 171.6667 | 1 | No
| 1835155 | 2024-09-09 | 9:14 | 2024-09-09 | 10:58 | CM13 | CHELTENHAM | Urban | Asset Failure | LV | 1 | 103.6667 | 103.6667 | 1 | No
| 1835311 | 2024-09-09 | 14:03 | 2024-09-09 | 16:57 | STO14 | SORRENTO | Rural Short | Network Business | Network Error | 1 | 173.6667 | 173.6667 | 1 | No
| 1835332 | 2024-09-09 | 14:48 | 2024-09-09 | 17:23 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 154.3833 | 154.3833 | 1 | No
| 1835374 | 2024-09-09 | 17:52 | 2024-09-09 | 20:45 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 45 | 7790.2515 | 173.1167 | 1 | No
| 1835361 | 2024-09-09 | 19:23 | 2024-09-09 | 21:20 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 117 | 117 | 1 | No
| 1835536 | 2024-09-09 | 21:07 | 2024-09-09 | 22:33 | DC2 | DONCASTER | Urban | Animal | Animal impact | 158 | 13588 | 86 | 1 | No
| 1835587 | 2024-10-09 | 8:33 | 2024-10-09 | 15:48 | RBD24 | ROSEBUD | Urban | Asset Failure | LV | 1 | 434.25 | 434.25 | 1 | No
| 1835633 | 2024-10-09 | 9:49 | 2024-10-09 | 11:50 | CRM11 | CARRUM | Urban | Animal | Animal impact | 1.34 | 161.5594 | 120.5667 | 1 | No
| 1835645 | 2024-10-09 | 10:07 | 2024-10-09 | 12:55 | FTN23 | FRANKSTON | Urban | Animal | Animal impact | 11 | 1840.4837 | 167.3167 | 1 | No
| 1835666 | 2024-10-09 | 10:53 | 2024-10-09 | 13:19 | CRM22 | CARRUM | Urban | Asset Failure | LV | 43 | 6243.6 | 145.2 | 1 | No
| 1835699 | 2024-10-09 | 12:49 | 2024-10-09 | 14:19 | OAK26 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 90.25 | 90.25 | 1 | No
| 1835640 | 2024-10-09 | 13:59 | 2024-10-09 | 15:46 | DN13 | DANDENONG | Urban | Asset Failure | LV | 1 | 107 | 107 | 1 | No
| 1835748 | 2024-10-09 | 14:40 | 2024-10-09 | 18:00 | KBH31 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 200 | 200 | 1 | No
| 1835800 | 2024-10-09 | 16:52 | 2024-10-09 | 22:12 | STO21 | SORRENTO | Rural Short | Weather |  | 1 | 319.7667 | 319.7667 | 1 | No
| 1835759 | 2024-10-09 | 16:53 | 2024-10-09 | 20:02 | SVW54 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 189.2167 | 189.2167 | 1 | No
| 1835782 | 2024-10-09 | 18:50 | 2024-10-09 | 20:29 | HT7 | HEATHERTON | Urban | Asset Failure | LV | 1 | 98.55 | 98.55 | 1 | No
| 1835819 | 2024-11-09 | 0:13 | 2024-11-09 | 1:41 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 20.46 | 1817.5293 | 88.8333 | 1 | No
| 1835824 | 2024-11-09 | 1:42 | 2024-11-09 | 3:49 | SR36 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 126.5 | 126.5 | 1 | No
| 1835825 | 2024-11-09 | 2:44 | 2024-11-09 | 4:24 | STO14 | SORRENTO | Rural Short | Asset Failure | Distribution substation | 85 | 8507.0805 | 100.0833 | 1 | No
| 1836040 | 2024-11-09 | 11:33 | 2024-11-09 | 13:40 | DN10 | DANDENONG | Urban | Network Business | Network Error | 1 | 127 | 127 | 1 | No
| 1836134 | 2024-11-09 | 12:38 | 2024-11-09 | 13:35 | K27 | GARDINER | Urban | Asset Failure | LV | 3 | 168.9999 | 56.3333 | 1 | No
| 1836209 | 2024-11-09 | 17:18 | 2024-11-09 | 18:41 | M22 | MENTONE | Urban | Asset Failure | LV | 1 | 82.7 | 82.7 | 1 | No
| 1836213 | 2024-11-09 | 17:25 | 2024-11-09 | 18:13 | OE6 | OAKLEIGH EAST | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 26 | 1264.9 | 48.65 | 1 | No
| 1836229 | 2024-11-09 | 22:24 | 2024-12-09 | 0:01 | MC22 | MORDIALLOC | Urban | Animal | Animal impact | 14 | 1365 | 97.5 | 1 | No
| 1836233 | 2024-11-09 | 23:14 | 2024-12-09 | 0:06 | GW4 | GLEN WAVERLEY | Urban | Asset Failure | LV | 56 | 2919.4648 | 52.1333 | 1 | No
| 1836253 | 2024-12-09 | 2:54 | 2024-12-09 | 4:05 | LWN32 | LANGWARRIN | Rural Short | Animal | Animal impact | 67.67 | 4818.104 | 71.2 | 1 | No
| 1836283 | 2024-12-09 | 7:46 | 2024-12-09 | 8:54 | BU11 | BULLEEN | Urban | Asset Failure | LV | 1 | 67.9833 | 67.9833 | 1 | No
| 1836365 | 2024-12-09 | 9:34 | 2024-12-09 | 11:50 | DN7 | DANDENONG | Urban | Unknown | Unknown | 1 | 135.7167 | 135.7167 | 1 | No
| 1836259 | 2024-12-09 | 10:31 | 2024-12-09 | 13:42 | EW9 | ELWOOD | Urban | Asset Failure | LV | 1 | 191.3167 | 191.3167 | 1 | No
| 1836516 | 2024-12-09 | 16:42 | 2024-12-09 | 23:01 | MR13 | MOORABBIN | Urban | Asset Failure | LV | 1 | 378.5 | 378.5 | 1 | No
| 1836517 | 2024-12-09 | 16:57 | 2024-12-09 | 18:09 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 1 | 71.3167 | 71.3167 | 1 | No
| 1836521 | 2024-12-09 | 17:27 | 2024-12-09 | 20:50 | EW9 | ELWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 5 | 1014.1665 | 202.8333 | 1 | No
| 1836525 | 2024-12-09 | 19:00 | 2024-12-09 | 22:40 | MC22 | MORDIALLOC | Urban | Asset Failure | LV | 2 | 440 | 220 | 1 | No
| 1836555 | 13/09/2024 | 6:35 | 13/09/2024 | 7:55 | FSH22 | FRANKSTON SOUTH | Urban | Third Party | Other | 1 | 80.3333 | 80.3333 | 1 | No
| 1836564 | 13/09/2024 | 7:23 | 13/09/2024 | 8:57 | LWN21 | LANGWARRIN | Rural Short | Network Business | Network Error | 1 | 94.2833 | 94.2833 | 1 | No
| 1836567 | 13/09/2024 | 7:47 | 13/09/2024 | 10:15 | MTN31 | MORNINGTON | Urban | Unknown | Unknown | 1 | 147.3667 | 147.3667 | 1 | No
| 1836576 | 13/09/2024 | 8:06 | 13/09/2024 | 10:39 | EW12 | ELWOOD | Urban | Third Party | Vehicle Impact | 1 | 152.9333 | 152.9333 | 1 | No
| 1836654 | 13/09/2024 | 9:36 | 13/09/2024 | 15:30 | SV20 | SPRINGVALE | Urban | Overloads |  | 1 | 353.4833 | 353.4833 | 1 | No
| 1836664 | 13/09/2024 | 9:41 | 13/09/2024 | 11:53 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 131.6167 | 131.6167 | 1 | No
| 1836669 | 13/09/2024 | 9:56 | 13/09/2024 | 10:32 | FSH13 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 1 | 35.9 | 35.9 | 1 | No
| 1836803 | 13/09/2024 | 16:15 | 13/09/2024 | 18:01 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 105.9 | 105.9 | 1 | No
| 1836806 | 13/09/2024 | 17:22 | 13/09/2024 | 18:53 | EL31 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 91.3333 | 91.3333 | 1 | No
| 1836816 | 13/09/2024 | 19:55 | 13/09/2024 | 21:32 | HGS23 | HASTINGS | Rural Short | Asset Failure | HV | 2 | 194.1334 | 97.0667 | 1 | No
| 1836861 | 14/09/2024 | 7:47 | 14/09/2024 | 10:11 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 20.13 | 2894.0237 | 143.7667 | 1 | No
| 1836859 | 14/09/2024 | 7:47 | 14/09/2024 | 11:33 | EW9 | ELWOOD | Urban | Overloads |  | 1 | 225.5667 | 225.5667 | 1 | No
| 1836860 | 14/09/2024 | 7:47 | 14/09/2024 | 12:01 | MTN22 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 4 | 1013.2668 | 253.3167 | 1 | No
| 1836863 | 14/09/2024 | 7:50 | 14/09/2024 | 16:03 | BR6 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 64 | 31502.9312 | 492.2333 | 1 | No
| 1836884 | 14/09/2024 | 9:23 | 14/09/2024 | 14:12 | DVY24 | DANDENONG VALLEY | Rural Short | Asset Failure | HV | 2 | 578 | 289 | 1 | No
| 1836893 | 14/09/2024 | 9:44 | 14/09/2024 | 13:32 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 228.2 | 228.2 | 1 | No
| 1836845 | 14/09/2024 | 10:03 | 14/09/2024 | 11:50 | SR36 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 107.0833 | 107.0833 | 1 | No
| 1836857 | 14/09/2024 | 10:06 | 14/09/2024 | 15:24 | CRM13 | CARRUM | Urban | Asset Failure | LV | 1 | 318.6333 | 318.6333 | 1 | No
| 1836912 | 14/09/2024 | 11:08 | 14/09/2024 | 16:42 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 334.2333 | 334.2333 | 1 | No
| 1836927 | 14/09/2024 | 12:49 | 14/09/2024 | 14:15 | BU25 | BULLEEN | Urban | Asset Failure | HV | 63.65 | 5455.868 | 85.7167 | 1 | No
| 1836931 | 14/09/2024 | 13:17 | 14/09/2024 | 19:35 | EM10 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 378.3167 | 378.3167 | 1 | No
| 1836940 | 14/09/2024 | 14:30 | 14/09/2024 | 17:02 | NB34 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 151.0667 | 151.0667 | 1 | No
| 1836945 | 14/09/2024 | 15:46 | 14/09/2024 | 18:26 | M25 | MENTONE | Urban | Asset Failure | LV | 1 | 159.9167 | 159.9167 | 1 | No
| 1836975 | 14/09/2024 | 19:12 | 14/09/2024 | 19:28 | EB33 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 28.05 | 427.7625 | 15.25 | 1 | No
| 1836988 | 14/09/2024 | 21:03 | 14/09/2024 | 22:06 | BH21 | BOX HILL | Urban | Asset Failure | LV | 1 | 62.8333 | 62.8333 | 1 | No
| 1837004 | 15/09/2024 | 2:31 | 15/09/2024 | 12:11 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 579.95 | 579.95 | 1 | No
| 1837012 | 15/09/2024 | 4:46 | 15/09/2024 | 6:33 | MC34 | MORDIALLOC | Urban | Asset Failure | HV | 644 | 68349.8452 | 106.1333 | 1 | No
| 1837012 | 15/09/2024 | 4:46 | 15/09/2024 | 7:27 | MC34 | MORDIALLOC | Urban | Asset Failure | HV | 246 | 39519.9 | 160.65 | 2 | No
| 1837012 | 15/09/2024 | 4:46 | 15/09/2024 | 7:47 | MC34 | MORDIALLOC | Urban | Asset Failure | HV | 89 | 16091.2 | 180.8 | 3 | No
| 1837012 | 15/09/2024 | 4:46 | 15/09/2024 | 10:26 | MC34 | MORDIALLOC | Urban | Asset Failure | HV | 21 | 7127.7507 | 339.4167 | 4 | No
| 1837012 | 15/09/2024 | 4:47 | 15/09/2024 | 6:59 | MC34 | MORDIALLOC | Urban | Asset Failure | HV | 396 | 52509.6 | 132.6 | 1 | No
| 1837014 | 15/09/2024 | 4:47 | 15/09/2024 | 4:54 | MC34 | MORDIALLOC | Urban | Asset Failure | HV | 332 | 2257.6 | 6.8 | 1 | No
| 1837014 | 15/09/2024 | 4:47 | 15/09/2024 | 8:36 | MC34 | MORDIALLOC | Urban | Asset Failure | HV | 247 | 56484.7751 | 228.6833 | 2 | No
| 1837020 | 15/09/2024 | 6:06 | 15/09/2024 | 7:45 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1 | 98.7167 | 98.7167 | 1 | No
| 1837021 | 15/09/2024 | 6:30 | 15/09/2024 | 9:05 | NP24 | NOBLE PARK | Urban | Animal | Animal impact | 97 | 15018.8301 | 154.8333 | 1 | No
| 1837054 | 15/09/2024 | 9:58 | 15/09/2024 | 11:25 | HT1 | HEATHERTON | Urban | Unknown | Unknown | 1 | 87.0333 | 87.0333 | 1 | No
| 1836904 | 15/09/2024 | 11:13 | 15/09/2024 | 14:37 | MR15 | MOORABBIN | Urban | Asset Failure | LV | 1 | 204.4 | 204.4 | 1 | No
| 1837069 | 15/09/2024 | 11:18 | 15/09/2024 | 12:20 | EB11 | EAST BURWOOD | Urban | Asset Failure | LV | 2.94 | 179.928 | 61.2 | 1 | No
| 1837119 | 15/09/2024 | 16:49 | 15/09/2024 | 19:40 | STO13 | SORRENTO | Urban | Unknown | Unknown | 1 | 171.3167 | 171.3167 | 1 | No
| 1837125 | 15/09/2024 | 17:48 | 15/09/2024 | 18:25 | NP14 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 36.6 | 36.6 | 1 | No
| 1837126 | 15/09/2024 | 18:09 | 15/09/2024 | 19:54 | BU15 | BULLEEN | Urban | Asset Failure | LV | 1 | 105.6333 | 105.6333 | 1 | No
| 1837136 | 15/09/2024 | 19:27 | 15/09/2024 | 20:25 | NP33 | NOBLE PARK | Urban | Third Party | Vehicle Impact | 965 | 55905.6345 | 57.9333 | 1 | No
| 1837136 | 15/09/2024 | 19:27 | 16/09/2024 | 1:12 | NP33 | NOBLE PARK | Urban | Third Party | Vehicle Impact | 22 | 7568.7326 | 344.0333 | 2 | No
| 1837137 | 15/09/2024 | 19:28 | 15/09/2024 | 19:38 | NP33 | NOBLE PARK | Urban | Asset Failure | HV | 921 | 10084.95 | 10.95 | 1 | No
| 1837137 | 15/09/2024 | 19:28 | 15/09/2024 | 21:09 | NP33 | NOBLE PARK | Urban | Asset Failure | HV | 526 | 53161.0842 | 101.0667 | 2 | No
| 1837137 | 15/09/2024 | 19:28 | 15/09/2024 | 23:16 | NP33 | NOBLE PARK | Urban | Asset Failure | HV | 638 | 145868.0454 | 228.6333 | 3 | No
| 1837144 | 15/09/2024 | 19:49 | 15/09/2024 | 21:16 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 86.6667 | 86.6667 | 1 | No
| 1837148 | 15/09/2024 | 21:10 | 15/09/2024 | 22:06 | BT16 | BENTLEIGH | Urban | Overloads |  | 2.97 | 166.32 | 56 | 1 | No
| 1837187 | 16/09/2024 | 8:23 | 16/09/2024 | 8:51 | HGS32 | HASTINGS | Urban | Weather |  | 1 | 27.9167 | 27.9167 | 1 | No
| 1837200 | 16/09/2024 | 8:33 | 16/09/2024 | 9:00 | DMA13 | DROMANA | Rural Short | Other | XXX | 1 | 26.9167 | 26.9167 | 1 | No
| 1837235 | 16/09/2024 | 9:48 | 16/09/2024 | 11:34 | OAK35 | OAKLEIGH | Urban | Unknown | Unknown | 1 | 106.0167 | 106.0167 | 1 | No
| 1837336 | 16/09/2024 | 13:14 | 16/09/2024 | 14:28 | AR6 | ARMADALE | Urban | Network Business | Switching and protection error | 70 | 5190.5 | 74.15 | 1 | No
| 1837384 | 16/09/2024 | 15:34 | 16/09/2024 | 17:05 | WD26 | WEST DONCASTER | Urban | Third Party | Other | 1 | 91.0833 | 91.0833 | 1 | No
| 1837303 | 16/09/2024 | 15:47 | 17/09/2024 | 11:00 | FTN25 | FRANKSTON | Urban | Asset Failure | HV | 1 | 1153 | 1153 | 1 | No
| 1837411 | 16/09/2024 | 18:18 | 16/09/2024 | 19:46 | GW8 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 88 | 88 | 1 | No
| 1837443 | 17/09/2024 | 1:16 | 17/09/2024 | 8:34 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 437.2833 | 437.2833 | 1 | No
| 1837448 | 17/09/2024 | 2:32 | 17/09/2024 | 3:33 | NO6 | NOTTING HILL | Urban | Animal | Other | 727 | 44577.2409 | 61.3167 | 1 | No
| 1837453 | 17/09/2024 | 3:56 | 17/09/2024 | 4:35 | RWT34 | RINGWOOD | Urban | Animal | Other | 73.7 | 2843.5892 | 38.5833 | 1 | No
| 1837446 | 17/09/2024 | 7:16 | 17/09/2024 | 8:42 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 1 | 86.1333 | 86.1333 | 1 | No
| 1837528 | 17/09/2024 | 9:16 | 17/09/2024 | 17:00 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1 | 463.35 | 463.35 | 1 | No
| 1837720 | 17/09/2024 | 16:08 | 17/09/2024 | 20:07 | MTN24 | MORNINGTON | Rural Short | Unknown | Unknown | 2.68 | 641.1008 | 239.2167 | 1 | No
| 1837774 | 18/09/2024 | 4:38 | 18/09/2024 | 8:10 | RBD12 | ROSEBUD | Rural Short | Animal | Animal impact | 6 | 1272.4002 | 212.0667 | 1 | No
| 1837781 | 18/09/2024 | 5:33 | 18/09/2024 | 7:17 | NP36 | NOBLE PARK | Urban | Animal | Animal impact | 44.89 | 4646.115 | 103.5 | 1 | No
| 1837804 | 18/09/2024 | 8:15 | 18/09/2024 | 9:42 | MGE34 | MULGRAVE | Urban | Asset Failure | LV | 1 | 87.25 | 87.25 | 1 | No
| 1837908 | 18/09/2024 | 9:13 | 18/09/2024 | 10:41 | LD1 | LYNDALE | Urban | Asset Failure | LV | 1 | 88.2833 | 88.2833 | 1 | No
| 1837945 | 18/09/2024 | 10:17 | 18/09/2024 | 12:18 | NB33 | NORTH BRIGHTON | Urban | Unknown | Unknown | 1 | 120.9833 | 120.9833 | 1 | No
| 1838073 | 18/09/2024 | 14:25 | 18/09/2024 | 15:06 | BW33 | BURWOOD | Urban | Asset Failure | LV | 1 | 40.5667 | 40.5667 | 1 | No
| 1838067 | 18/09/2024 | 15:43 | 18/09/2024 | 16:32 | OAK24 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 49.4833 | 49.4833 | 1 | No
| 1838143 | 18/09/2024 | 22:35 | 18/09/2024 | 23:26 | EL23 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 51.6 | 51.6 | 1 | No
| 1838154 | 19/09/2024 | 0:43 | 19/09/2024 | 1:41 | DSH21 | DANDENONG SOUTH | Urban | Third Party | Vehicle Impact | 164 | 9569.4 | 58.35 | 1 | No
| 1838158 | 19/09/2024 | 8:19 | 19/09/2024 | 9:55 | MGE34 | MULGRAVE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 96.8833 | 96.8833 | 1 | No
| 1838277 | 19/09/2024 | 10:09 | 19/09/2024 | 10:45 | NB35 | NORTH BRIGHTON | Urban | Third Party | Other | 5 | 179.4165 | 35.8833 | 1 | No
| 1838293 | 19/09/2024 | 10:27 | 19/09/2024 | 13:05 | HT1 | HEATHERTON | Urban | Asset Failure | LV | 31 | 4886.1177 | 157.6167 | 1 | No
| 1838355 | 19/09/2024 | 10:29 | 19/09/2024 | 18:05 | CRM34 | CARRUM | Urban | Asset Failure | Distribution substation | 2 | 913.3666 | 456.6833 | 1 | No
| 1838316 | 19/09/2024 | 11:20 | 19/09/2024 | 13:45 | CRM13 | CARRUM | Urban | Asset Failure | HV | 94.47 | 13655.6385 | 144.55 | 1 | No
| 1838397 | 19/09/2024 | 14:51 | 19/09/2024 | 15:26 | BR9 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 857 | 30280.6381 | 35.3333 | 1 | No
| 1838421 | 19/09/2024 | 16:35 | 19/09/2024 | 18:28 | NP36 | NOBLE PARK | Urban | Third Party | Other | 1 | 113.6 | 113.6 | 1 | No
| 1838426 | 19/09/2024 | 16:46 | 19/09/2024 | 18:46 | DMA24 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 52 | 6255.6 | 120.3 | 1 | No
| 1838438 | 19/09/2024 | 18:01 | 19/09/2024 | 20:58 | DMA21 | DROMANA | Urban | Asset Failure | LV | 1 | 177.4833 | 177.4833 | 1 | No
| 1838453 | 19/09/2024 | 19:13 | 19/09/2024 | 21:28 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 135.6333 | 135.6333 | 1 | No
| 1838449 | 19/09/2024 | 19:18 | 19/09/2024 | 22:05 | OR23 | ORMOND | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 167.1 | 167.1 | 1 | No
| 1838456 | 19/09/2024 | 19:52 | 19/09/2024 | 20:55 | DMA21 | DROMANA | Urban | Asset Failure | LV | 35 | 2219.5845 | 63.4167 | 1 | No
| 1838463 | 19/09/2024 | 20:49 | 19/09/2024 | 21:45 | MTN23 | MORNINGTON | Urban | Asset Failure | LV | 1 | 56.0333 | 56.0333 | 1 | No
| 1838462 | 19/09/2024 | 21:02 | 19/09/2024 | 23:02 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 120.6167 | 120.6167 | 1 | No
| 1838471 | 19/09/2024 | 22:36 | 19/09/2024 | 23:49 | GW10 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 72.9667 | 72.9667 | 1 | No
| 1838473 | 20/09/2024 | 0:40 | 20/09/2024 | 1:33 | RBD24 | ROSEBUD | Urban | Asset Failure | LV | 1 | 52.0667 | 52.0667 | 1 | No
| 1838480 | 20/09/2024 | 2:04 | 20/09/2024 | 2:47 | MC14 | MORDIALLOC | Urban | Third Party | Other | 19 | 824.9173 | 43.4167 | 1 | No
| 1838557 | 20/09/2024 | 8:40 | 20/09/2024 | 10:22 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 102.1167 | 102.1167 | 1 | No
| 1838579 | 20/09/2024 | 9:19 | 20/09/2024 | 12:07 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 168.0333 | 168.0333 | 1 | No
| 1838469 | 20/09/2024 | 9:25 | 20/09/2024 | 11:30 | SV32 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 125 | 125 | 1 | No
| 1838647 | 20/09/2024 | 11:05 | 20/09/2024 | 13:44 | DSH14 | DANDENONG SOUTH | Urban | Asset Failure | LV | 1 | 158.3333 | 158.3333 | 1 | No
| 1838691 | 20/09/2024 | 12:27 | 20/09/2024 | 12:34 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | HV | 1257 | 8861.85 | 7.05 | 1 | No
| 1838691 | 20/09/2024 | 12:27 | 20/09/2024 | 12:41 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | HV | 691 | 9720.0897 | 14.0667 | 2 | No
| 1838691 | 20/09/2024 | 12:27 | 20/09/2024 | 12:52 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | HV | 67 | 1686.1689 | 25.1667 | 3 | No
| 1838691 | 20/09/2024 | 12:27 | 20/09/2024 | 13:02 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | HV | 189 | 6684.3063 | 35.3667 | 4 | No
| 1838691 | 20/09/2024 | 12:27 | 20/09/2024 | 13:16 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | HV | 324 | 15940.8 | 49.2 | 5 | No
| 1838775 | 20/09/2024 | 17:22 | 20/09/2024 | 22:40 | LD1 | LYNDALE | Urban | Asset Failure | LV | 1 | 317.7 | 317.7 | 1 | No
| 1838782 | 20/09/2024 | 18:29 | 20/09/2024 | 22:58 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 269.3833 | 269.3833 | 1 | No
| 1838786 | 20/09/2024 | 18:42 | 20/09/2024 | 22:00 | EW1 | ELWOOD | Urban | Asset Failure | LV | 1 | 198.2 | 198.2 | 1 | No
| 1838792 | 20/09/2024 | 19:05 | 20/09/2024 | 20:15 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 69.8167 | 69.8167 | 1 | No
| 1838811 | 20/09/2024 | 19:40 | 20/09/2024 | 21:45 | RBD24 | ROSEBUD | Urban | Asset Failure | LV | 1 | 124.3333 | 124.3333 | 1 | No
| 1838790 | 20/09/2024 | 20:04 | 20/09/2024 | 22:45 | RBD21 | ROSEBUD | Rural Short | Unknown | Unknown | 2 | 322 | 161 | 1 | No
| 1838803 | 20/09/2024 | 20:13 | 20/09/2024 | 21:15 | RBD24 | ROSEBUD | Urban | Animal | Animal impact | 75.9 | 4686.825 | 61.75 | 1 | No
| 1838802 | 20/09/2024 | 20:13 | 20/09/2024 | 22:14 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 120.4833 | 120.4833 | 1 | No
| 1838845 | 21/09/2024 | 6:01 | 21/09/2024 | 8:00 | FSH22 | FRANKSTON SOUTH | Urban | Third Party | Other | 1 | 118.8167 | 118.8167 | 1 | No
| 1838999 | 21/09/2024 | 16:49 | 21/09/2024 | 22:26 | SS11 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 336.95 | 336.95 | 1 | No
| 1839001 | 21/09/2024 | 17:06 | 21/09/2024 | 19:35 | BC11 | BALACLAVA | Urban | Asset Failure | LV | 1 | 149.2 | 149.2 | 1 | No
| 1839006 | 21/09/2024 | 17:26 | 21/09/2024 | 20:52 | EW8 | ELWOOD | Urban | Asset Failure | LV | 1 | 206.35 | 206.35 | 1 | No
| 1839013 | 21/09/2024 | 18:16 | 21/09/2024 | 21:30 | MC34 | MORDIALLOC | Urban | Unknown | Unknown | 1 | 194 | 194 | 1 | No
| 1839017 | 21/09/2024 | 19:32 | 21/09/2024 | 23:30 | MC12 | MORDIALLOC | Urban | Weather |  | 2.31 | 548.7405 | 237.55 | 1 | No
| 1839019 | 21/09/2024 | 19:58 | 21/09/2024 | 22:30 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 7.92 | 1196.9757 | 151.1333 | 1 | No
| 1839024 | 21/09/2024 | 20:37 | 21/09/2024 | 21:47 | NO7 | NOTTING HILL | Urban | Third Party | Other | 149 | 10348.05 | 69.45 | 1 | No
| 1839077 | 22/09/2024 | 5:04 | 22/09/2024 | 10:03 | M12 | MENTONE | Urban | Asset Failure | LV | 1 | 298.5667 | 298.5667 | 1 | No
| 1839068 | 22/09/2024 | 6:00 | 22/09/2024 | 12:54 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 414.4333 | 414.4333 | 1 | No
| 1839104 | 22/09/2024 | 8:54 | 22/09/2024 | 10:12 | DVY14 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 78.25 | 78.25 | 1 | No
| 1839153 | 22/09/2024 | 14:21 | 22/09/2024 | 15:20 | DMA14 | DROMANA | Urban | Asset Failure | LV | 8.4 | 493.3597 | 58.7333 | 1 | No
| 1839169 | 22/09/2024 | 16:48 | 22/09/2024 | 18:50 | RBD24 | ROSEBUD | Urban | Asset Failure | LV | 1 | 121.4667 | 121.4667 | 1 | No
| 1839170 | 22/09/2024 | 19:06 | 22/09/2024 | 22:05 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 179 | 179 | 1 | No
| 1839183 | 22/09/2024 | 19:20 | 22/09/2024 | 20:50 | FSH33 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 26.8 | 2398.6 | 89.5 | 1 | No
| 1839202 | 22/09/2024 | 22:20 | 22/09/2024 | 23:35 | NW14 | NUNAWADING | Urban | Third Party | Vehicle Impact | 1442 | 107044.4186 | 74.2333 | 1 | No
| 1839202 | 22/09/2024 | 22:20 | 22/09/2024 | 23:44 | NW14 | NUNAWADING | Urban | Third Party | Vehicle Impact | 3 | 252.3999 | 84.1333 | 2 | No
| 1839202 | 22/09/2024 | 22:20 | 23/09/2024 | 0:31 | NW14 | NUNAWADING | Urban | Third Party | Vehicle Impact | 79 | 10304.2307 | 130.4333 | 3 | No
| 1839202 | 22/09/2024 | 22:20 | 23/09/2024 | 4:24 | NW14 | NUNAWADING | Urban | Third Party | Vehicle Impact | 14 | 5093.6662 | 363.8333 | 4 | No
| 1839202 | 22/09/2024 | 22:20 | 23/09/2024 | 4:29 | NW14 | NUNAWADING | Urban | Third Party | Vehicle Impact | 59 | 21737.5647 | 368.4333 | 5 | No
| 1839205 | 22/09/2024 | 22:24 | 23/09/2024 | 0:22 | NW21 | NUNAWADING | Urban | Unknown | Unknown | 54 | 6332.4018 | 117.2667 | 1 | No
| 1839205 | 22/09/2024 | 22:24 | 23/09/2024 | 0:25 | NW21 | NUNAWADING | Urban | Unknown | Unknown | 64 | 7733.3312 | 120.8333 | 2 | No
| 1839205 | 22/09/2024 | 22:24 | 23/09/2024 | 0:30 | NW21 | NUNAWADING | Urban | Unknown | Unknown | 69 | 8659.5 | 125.5 | 3 | No
| 1839208 | 22/09/2024 | 22:26 | 22/09/2024 | 23:44 | MTN22 | MORNINGTON | Rural Short | Animal | Other | 3 | 233.0499 | 77.6833 | 1 | No
| 1839214 | 22/09/2024 | 23:51 | 23/09/2024 | 0:40 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 1 | 48.2667 | 48.2667 | 1 | No
| 1839237 | 23/09/2024 | 8:10 | 23/09/2024 | 9:42 | BU25 | BULLEEN | Urban | Asset Failure | LV | 1 | 92.3 | 92.3 | 1 | No
| 1839250 | 23/09/2024 | 9:50 | 23/09/2024 | 12:22 | MGE21 | MULGRAVE | Urban | Asset Failure | LV | 1 | 151.9333 | 151.9333 | 1 | No
| 1839251 | 23/09/2024 | 9:51 | 23/09/2024 | 11:08 | BW33 | BURWOOD | Urban | Asset Failure | LV | 1 | 76.3333 | 76.3333 | 1 | No
| 1839255 | 23/09/2024 | 10:31 | 23/09/2024 | 11:59 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 1 | 88.8167 | 88.8167 | 1 | No
| 1839259 | 23/09/2024 | 11:02 | 23/09/2024 | 13:12 | CRM14 | CARRUM | Rural Short | Overloads |  | 1 | 130.1167 | 130.1167 | 1 | No
| 1839270 | 23/09/2024 | 12:09 | 23/09/2024 | 12:52 | RWT34 | RINGWOOD | Urban | Third Party | Other | 1 | 42.8667 | 42.8667 | 1 | No
| 1839289 | 23/09/2024 | 14:07 | 23/09/2024 | 18:00 | MR21 | MOORABBIN | Urban | Third Party | Vehicle Impact | 1 | 232.5833 | 232.5833 | 1 | No
| 1839332 | 23/09/2024 | 22:44 | 24/09/2024 | 0:25 | RBD13 | ROSEBUD | Urban | Animal | Other | 152.76 | 15352.38 | 100.5 | 1 | No
| 1839372 | 24/09/2024 | 7:50 | 24/09/2024 | 9:27 | FSH22 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 11 | 1074.8837 | 97.7167 | 1 | No
| 1839407 | 24/09/2024 | 8:42 | 24/09/2024 | 10:40 | DMA23 | DROMANA | Rural Short | Third Party | Other | 1 | 117.9833 | 117.9833 | 1 | No
| 1839456 | 24/09/2024 | 10:20 | 24/09/2024 | 12:00 | BR4 | BEAUMARIS | Urban | Third Party | Vehicle Impact | 5 | 496.4165 | 99.2833 | 1 | No
| 1839494 | 24/09/2024 | 11:58 | 24/09/2024 | 15:31 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 212.8333 | 212.8333 | 1 | No
| 1839510 | 24/09/2024 | 12:30 | 24/09/2024 | 14:40 | RWT12 | RINGWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 159.46 | 20689.935 | 129.75 | 1 | No
| 1839356 | 24/09/2024 | 13:00 | 24/09/2024 | 13:55 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 55 | 55 | 1 | No
| 1839539 | 24/09/2024 | 13:16 | 24/09/2024 | 15:53 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 156.85 | 156.85 | 1 | No
| 1839556 | 24/09/2024 | 14:23 | 24/09/2024 | 16:50 | EW9 | ELWOOD | Urban | Asset Failure | LV | 1 | 146.9 | 146.9 | 1 | No
| 1839578 | 24/09/2024 | 17:09 | 24/09/2024 | 22:20 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 310.4833 | 310.4833 | 1 | No
| 1839587 | 24/09/2024 | 19:05 | 24/09/2024 | 21:36 | FTN24 | FRANKSTON | Urban | Asset Failure | LV | 1 | 150.4833 | 150.4833 | 1 | No
| 1839594 | 24/09/2024 | 19:45 | 24/09/2024 | 22:25 | CRM22 | CARRUM | Urban | Third Party | Vehicle Impact | 87 | 13920 | 160 | 1 | No
| 1839603 | 25/09/2024 | 1:46 | 25/09/2024 | 1:52 | GW5 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 722 | 4067.2426 | 5.6333 | 1 | No
| 1839603 | 25/09/2024 | 1:46 | 25/09/2024 | 2:43 | GW5 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 934 | 52879.9978 | 56.6167 | 2 | No
| 1839605 | 25/09/2024 | 3:19 | 25/09/2024 | 4:09 | EM3 | EAST MALVERN | Urban | Animal | Animal impact | 201 | 10163.9067 | 50.5667 | 1 | No
| 1839619 | 25/09/2024 | 6:05 | 25/09/2024 | 8:26 | HGS32 | HASTINGS | Urban | Third Party | Vehicle Impact | 41.58 | 5872.4806 | 141.2333 | 1 | No
| 1839627 | 25/09/2024 | 7:12 | 25/09/2024 | 10:32 | BR13 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 199.9167 | 199.9167 | 1 | No
| 1839630 | 25/09/2024 | 7:23 | 26/09/2024 | 20:32 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 1 | 2228.5833 | 2228.5833 | 1 | No
| 1839634 | 25/09/2024 | 7:32 | 25/09/2024 | 8:39 | CFD12 | CAULFIELD | Urban | Asset Failure | LV | 1 | 66.5333 | 66.5333 | 1 | No
| 1839637 | 25/09/2024 | 7:32 | 25/09/2024 | 9:05 | STO23 | SORRENTO | Urban | Asset Failure | HV | 60.97 | 5614.3188 | 92.0833 | 1 | No
| 1839669 | 25/09/2024 | 8:33 | 25/09/2024 | 9:12 | NW14 | NUNAWADING | Urban | Asset Failure | HV | 1378 | 53259.7 | 38.65 | 1 | No
| 1839669 | 25/09/2024 | 8:33 | 25/09/2024 | 9:48 | NW14 | NUNAWADING | Urban | Asset Failure | HV | 219 | 16362.9573 | 74.7167 | 2 | No
| 1839689 | 25/09/2024 | 8:54 | 25/09/2024 | 9:05 | STO23 | SORRENTO | Urban | Asset Failure | HV | 1036 | 11326.8988 | 10.9333 | 1 | No
| 1839693 | 25/09/2024 | 9:05 | 25/09/2024 | 9:10 | NW33 | NUNAWADING | Urban | Network Business | Network Error | 2775 | 14753.8425 | 5.3167 | 1 | No
| 1839731 | 25/09/2024 | 10:17 | 25/09/2024 | 14:03 | EL24 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 226.6167 | 226.6167 | 1 | No
| 1839783 | 25/09/2024 | 11:42 | 25/09/2024 | 12:47 | GW2 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 65.1833 | 65.1833 | 1 | No
| 1839793 | 25/09/2024 | 12:02 | 25/09/2024 | 13:35 | EB32 | EAST BURWOOD | Urban | Asset Failure | Distribution substation | 65.66 | 6072.4535 | 92.4833 | 1 | No
| 1839890 | 25/09/2024 | 15:27 | 25/09/2024 | 17:53 | EB33 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 145.8167 | 145.8167 | 1 | No
| 1839962 | 25/09/2024 | 21:45 | 25/09/2024 | 23:00 | DC1 | DONCASTER | Urban | Animal | Animal impact | 67 | 4973.6311 | 74.2333 | 1 | No
| 1839981 | 26/09/2024 | 0:20 | 26/09/2024 | 2:50 | MGE13 | MULGRAVE | Urban | Third Party | Other | 26 | 3899.5658 | 149.9833 | 1 | No
| 1839995 | 26/09/2024 | 2:50 | 26/09/2024 | 5:05 | FTN25 | FRANKSTON | Urban | Animal | Animal impact | 31.49 | 4222.809 | 134.1 | 1 | No
| 1840001 | 26/09/2024 | 2:53 | 26/09/2024 | 3:37 | FSH33 | FRANKSTON SOUTH | Urban | Animal | Other | 262 | 11410.1 | 43.55 | 1 | No
| 1840001 | 26/09/2024 | 2:53 | 26/09/2024 | 3:43 | FSH33 | FRANKSTON SOUTH | Urban | Animal | Other | 348 | 17220.1884 | 49.4833 | 2 | No
| 1840029 | 26/09/2024 | 7:48 | 26/09/2024 | 10:26 | SVW42 | SPRINGVALE WEST | Urban | Third Party | Vehicle Impact | 1 | 158.0833 | 158.0833 | 1 | No
| 1840138 | 26/09/2024 | 13:57 | 26/09/2024 | 21:29 | NB25 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 452.1333 | 452.1333 | 1 | No
| 1840147 | 26/09/2024 | 14:14 | 26/09/2024 | 16:53 | BW35 | BURWOOD | Urban | Asset Failure | LV | 3.7 | 587.0668 | 158.6667 | 1 | No
| 1840190 | 26/09/2024 | 17:25 | 26/09/2024 | 22:18 | SV33 | SPRINGVALE | Urban | Animal | Animal impact | 151 | 44285.7783 | 293.2833 | 1 | No
| 1840199 | 26/09/2024 | 18:15 | 26/09/2024 | 19:44 | M35 | MENTONE | Urban | Asset Failure | Distribution substation | 158 | 13980.3614 | 88.4833 | 1 | No
| 1840197 | 26/09/2024 | 18:15 | 26/09/2024 | 20:40 | MTN24 | MORNINGTON | Rural Short | Asset Failure | LV | 3.3 | 476.1349 | 144.2833 | 1 | No
| 1840214 | 26/09/2024 | 20:05 | 26/09/2024 | 20:30 | CRM14 | CARRUM | Rural Short | Third Party | Vehicle Impact | 16 | 400 | 25 | 1 | No
| 1840228 | 26/09/2024 | 21:04 | 26/09/2024 | 22:44 | WD34 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 100.9 | 100.9 | 1 | No
| 1840260 | 27/09/2024 | 2:07 | 27/09/2024 | 3:23 | MR31 | MOORABBIN | Urban | Asset Failure | Distribution substation | 48.91 | 3673.141 | 75.1 | 1 | No
| 1840311 | 27/09/2024 | 9:53 | 27/09/2024 | 11:01 | SS12 | SPRINGVALE SOUTH | Urban | Unknown | Unknown | 4 | 270.5332 | 67.6333 | 1 | No
| 1840311 | 27/09/2024 | 9:53 | 27/09/2024 | 11:01 | SV16 | SPRINGVALE | Urban | Unknown | Unknown | 425 | 28744.1525 | 67.6333 | 1 | No
| 1840311 | 27/09/2024 | 9:53 | 27/09/2024 | 11:01 | SV33 | SPRINGVALE | Urban | Unknown | Unknown | 151 | 10212.6283 | 67.6333 | 1 | No
| 1840390 | 27/09/2024 | 17:27 | 27/09/2024 | 21:26 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 1 | 239.75 | 239.75 | 1 | No
| 1840323 | 27/09/2024 | 18:25 | 27/09/2024 | 19:24 | BH12 | BOX HILL | Urban | Asset Failure | LV | 1 | 59 | 59 | 1 | No
| 1840378 | 27/09/2024 | 19:01 | 27/09/2024 | 20:35 | CRM14 | CARRUM | Rural Short | Asset Failure | LV | 1 | 94.2167 | 94.2167 | 1 | No
| 1840400 | 27/09/2024 | 19:55 | 27/09/2024 | 20:24 | NW33 | NUNAWADING | Urban | Asset Failure | LV | 1 | 29.3333 | 29.3333 | 1 | No
| 1840408 | 27/09/2024 | 21:18 | 27/09/2024 | 22:53 | SVW53 | SPRINGVALE WEST | Urban | Third Party | Other | 77 | 7259.8141 | 94.2833 | 1 | No
| 1840432 | 28/09/2024 | 3:55 | 28/09/2024 | 10:30 | SS14 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 394.3 | 394.3 | 1 | No
| 1840456 | 28/09/2024 | 8:56 | 28/09/2024 | 9:45 | EB32 | EAST BURWOOD | Urban | Asset Failure | LV | 101 | 4898.5 | 48.5 | 1 | No
| 1840481 | 28/09/2024 | 11:45 | 28/09/2024 | 13:46 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 121.6667 | 121.6667 | 1 | No
| 1840497 | 28/09/2024 | 13:12 | 28/09/2024 | 14:26 | FSH22 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 64 | 4701.8688 | 73.4667 | 1 | No
| 1840505 | 28/09/2024 | 15:44 | 28/09/2024 | 16:55 | HGS23 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 71.5667 | 71.5667 | 1 | No
| 1840538 | 28/09/2024 | 18:51 | 28/09/2024 | 19:47 | CRM14 | CARRUM | Rural Short | Asset Failure | LV | 16 | 892.8 | 55.8 | 1 | No
| 1840549 | 28/09/2024 | 23:09 | 29/09/2024 | 0:18 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 51 | 3511.35 | 68.85 | 1 | No
| 1840575 | 29/09/2024 | 6:40 | 29/09/2024 | 15:49 | CRM15 | CARRUM | Urban | Asset Failure | HV | 62 | 34021.4646 | 548.7333 | 1 | No
| 1840598 | 29/09/2024 | 11:04 | 29/09/2024 | 12:25 | MTN35 | MORNINGTON | Rural Short | Animal | Animal impact | 5 | 403.6665 | 80.7333 | 1 | No
| 1840627 | 29/09/2024 | 14:22 | 29/09/2024 | 15:56 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 94.6667 | 94.6667 | 1 | No
| 1840651 | 29/09/2024 | 17:54 | 29/09/2024 | 19:14 | BU21 | BULLEEN | Urban | Third Party | Other | 13 | 1042.3829 | 80.1833 | 1 | No
| 1840654 | 29/09/2024 | 20:24 | 29/09/2024 | 21:01 | NW13 | NUNAWADING | Urban | Asset Failure | LV | 1 | 37.8167 | 37.8167 | 1 | No
| 1840671 | 30/09/2024 | 3:30 | 30/09/2024 | 5:47 | HGS22 | HASTINGS | Rural Short | Animal | Animal impact | 30.15 | 4133.565 | 137.1 | 1 | No
| 1840671 | 30/09/2024 | 3:30 | 30/09/2024 | 5:59 | HGS22 | HASTINGS | Rural Short | Animal | Animal impact | 6.03 | 898.2692 | 148.9667 | 2 | No
| 1840810 | 30/09/2024 | 12:41 | 30/09/2024 | 14:30 | MR23 | MOORABBIN | Urban | Asset Failure | LV | 1 | 108.6 | 108.6 | 1 | No
| 1840850 | 30/09/2024 | 14:33 | 30/09/2024 | 16:18 | EW12 | ELWOOD | Urban | Asset Failure | LV | 1 | 105 | 105 | 1 | No
| 1840854 | 30/09/2024 | 14:58 | 30/09/2024 | 17:26 | MC21 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 147.5667 | 147.5667 | 1 | No
| 1840776 | 30/09/2024 | 16:47 | 30/09/2024 | 17:45 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 1 | 58 | 58 | 1 | No
| 1841067 | 30/09/2024 | 17:40 | 30/09/2024 | 18:46 | LD33 | LYNDALE | Urban | Asset Failure | HV | 63 | 4107.6 | 65.2 | 1 | No
| 1841191 | 2024-01-10 | 9:31 | 2024-01-10 | 10:50 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 79.1333 | 79.1333 | 1 | No
| 1841239 | 2024-01-10 | 10:34 | 2024-01-10 | 12:40 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 126.2167 | 126.2167 | 1 | No
| 1841242 | 2024-01-10 | 10:40 | 2024-01-10 | 11:51 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 1 | 71.5333 | 71.5333 | 1 | No
| 1841318 | 2024-01-10 | 12:51 | 2024-01-10 | 14:50 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 7.26 | 856.9218 | 118.0333 | 1 | No
| 1841410 | 2024-01-10 | 15:55 | 2024-01-10 | 16:14 | NP12 | NOBLE PARK | Urban | Asset Failure | HV | 28.38 | 531.1799 | 18.7167 | 1 | No
| 1841432 | 2024-01-10 | 18:33 | 2024-01-10 | 21:45 | M12 | MENTONE | Urban | Asset Failure | LV | 3.28 | 629.76 | 192 | 1 | No
| 1841435 | 2024-01-10 | 20:06 | 2024-01-10 | 21:19 | MTN22 | MORNINGTON | Rural Short | Unknown | Unknown | 1 | 73.0833 | 73.0833 | 1 | No
| 1841448 | 2024-01-10 | 23:08 | 2024-02-10 | 1:20 | OR33 | ORMOND | Urban | Asset Failure | LV | 19 | 2500.7173 | 131.6167 | 1 | No
| 1841454 | 2024-02-10 | 1:56 | 2024-02-10 | 2:40 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 43.5167 | 43.5167 | 1 | No
| 1841455 | 2024-02-10 | 3:30 | 2024-02-10 | 7:49 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 259.0833 | 259.0833 | 1 | No
| 1841458 | 2024-02-10 | 4:40 | 2024-02-10 | 7:08 | MGE23 | MULGRAVE | Urban | Asset Failure | LV | 1 | 148.1833 | 148.1833 | 1 | No
| 1841465 | 2024-02-10 | 7:54 | 2024-02-10 | 9:23 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 4.29 | 381.6671 | 88.9667 | 1 | No
| 1841565 | 2024-02-10 | 11:07 | 2024-02-10 | 11:18 | NP34 | NOBLE PARK | Urban | Asset Failure | LV | 22.44 | 236.742 | 10.55 | 1 | No
| 1841638 | 2024-02-10 | 15:01 | 2024-02-10 | 15:45 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 14.19 | 622.4685 | 43.8667 | 1 | No
| 1841665 | 2024-02-10 | 19:32 | 2024-02-10 | 20:09 | EB31 | EAST BURWOOD | Urban | Asset Failure | Distribution substation | 79.06 | 2904.1347 | 36.7333 | 1 | No
| 1841752 | 2024-03-10 | 9:11 | 2024-03-10 | 10:20 | BW34 | BURWOOD | Urban | Overloads |  | 1 | 68.4 | 68.4 | 1 | No
| 1841776 | 2024-03-10 | 9:56 | 2024-03-10 | 12:20 | CFD23 | CAULFIELD | Urban | Asset Failure | LV | 1 | 143.4833 | 143.4833 | 1 | No
| 1841830 | 2024-03-10 | 12:14 | 2024-03-10 | 13:20 | K24 | GARDINER | Urban | Asset Failure | LV | 1 | 65.05 | 65.05 | 1 | No
| 1841848 | 2024-03-10 | 12:46 | 2024-03-10 | 17:52 | CFD16 | CAULFIELD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 340 | 103949.322 | 305.7333 | 1 | No
| 1841848 | 2024-03-10 | 12:46 | 2024-03-10 | 18:11 | CFD16 | CAULFIELD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 13 | 4225.2171 | 325.0167 | 2 | No
| 1841884 | 2024-03-10 | 14:06 | 2024-03-10 | 15:45 | MGE31 | MULGRAVE | Urban | Third Party | Other | 1 | 98.5833 | 98.5833 | 1 | No
| 1841919 | 2024-03-10 | 17:36 | 2024-03-10 | 22:04 | BT16 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 267.8667 | 267.8667 | 1 | No
| 1841922 | 2024-03-10 | 18:15 | 2024-03-10 | 19:39 | GW2 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 84.0333 | 84.0333 | 1 | No
| 1841936 | 2024-03-10 | 19:52 | 2024-03-10 | 23:48 | DC3 | DONCASTER | Urban | Animal | Other | 39.53 | 9330.3963 | 236.0333 | 1 | No
| 1841936 | 2024-03-10 | 19:52 | 2024-04-10 | 0:30 | DC3 | DONCASTER | Urban | Animal | Other | 47.57 | 13205.432 | 277.6 | 2 | No
| 1841954 | 2024-03-10 | 20:38 | 2024-04-10 | 0:30 | DC3 | DONCASTER | Urban | Animal | Animal impact | 17.16 | 3969.3946 | 231.3167 | 1 | No
| 1841970 | 2024-03-10 | 21:44 | 2024-03-10 | 22:42 | LWN35 | LANGWARRIN | Urban | Animal | Animal impact | 0.67 | 38.86 | 58 | 1 | No
| 1841974 | 2024-03-10 | 23:48 | 2024-04-10 | 0:56 | CRM15 | CARRUM | Urban | Asset Failure | LV | 1 | 68.3 | 68.3 | 1 | No
| 1842007 | 2024-04-10 | 7:58 | 2024-04-10 | 8:44 | M33 | MENTONE | Urban | Asset Failure | LV | 22.77 | 1057.6665 | 46.45 | 1 | No
| 1842036 | 2024-04-10 | 8:54 | 2024-04-10 | 21:06 | FTN24 | FRANKSTON | Urban | Asset Failure | LV | 1 | 731.8667 | 731.8667 | 1 | No
| 1842056 | 2024-04-10 | 9:51 | 2024-04-10 | 12:25 | NB35 | NORTH BRIGHTON | Urban | Third Party | Vehicle Impact | 19.8 | 3061.08 | 154.6 | 1 | No
| 1842064 | 2024-04-10 | 11:07 | 2024-04-10 | 13:25 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 137.7167 | 137.7167 | 1 | No
| 1841890 | 2024-04-10 | 11:33 | 2024-04-10 | 13:15 | EB12 | EAST BURWOOD | Urban | Unknown | Unknown | 1 | 102.5333 | 102.5333 | 1 | No
| 1842099 | 2024-04-10 | 12:49 | 2024-04-10 | 15:25 | KBH34 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 156.4167 | 156.4167 | 1 | No
| 1842104 | 2024-04-10 | 13:10 | 2024-04-10 | 14:15 | NW13 | NUNAWADING | Urban | Unknown | Unknown | 1 | 64.85 | 64.85 | 1 | No
| 1842133 | 2024-04-10 | 15:04 | 2024-04-10 | 18:17 | NW33 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 94 | 18052.7 | 192.05 | 1 | No
| 1842135 | 2024-04-10 | 15:06 | 2024-04-10 | 17:11 | EM5 | EAST MALVERN | Urban | Third Party | Other | 1 | 124.5333 | 124.5333 | 1 | No
| 1842159 | 2024-04-10 | 17:03 | 2024-04-10 | 18:40 | BW33 | BURWOOD | Urban | Unknown | Unknown | 1 | 96.3833 | 96.3833 | 1 | No
| 1842186 | 2024-04-10 | 17:12 | 2024-04-10 | 19:50 | STO21 | SORRENTO | Rural Short | Weather |  | 1 | 158.7833 | 158.7833 | 1 | No
| 1842167 | 2024-04-10 | 17:44 | 2024-04-10 | 23:22 | SVW55 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 338.4167 | 338.4167 | 1 | No
| 1842194 | 2024-04-10 | 18:43 | 2024-04-10 | 23:30 | NO7 | NOTTING HILL | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 19 | 5446.9827 | 286.6833 | 1 | No
| 1842183 | 2024-04-10 | 19:16 | 2024-04-10 | 21:12 | DMA15 | DROMANA | Rural Short | Weather |  | 3 | 345.15 | 115.05 | 1 | No
| 1842191 | 2024-04-10 | 20:23 | 2024-04-10 | 21:11 | STO21 | SORRENTO | Rural Short | Weather |  | 1 | 47.9333 | 47.9333 | 1 | No
| 1842195 | 2024-04-10 | 20:42 | 2024-04-10 | 22:52 | RBD14 | ROSEBUD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 130.2 | 130.2 | 1 | No
| 1842202 | 2024-04-10 | 22:39 | 2024-05-10 | 0:39 | RBD24 | ROSEBUD | Urban | Asset Failure | LV | 1 | 119.9167 | 119.9167 | 1 | No
| 1842205 | 2024-05-10 | 3:57 | 2024-05-10 | 5:24 | OR23 | ORMOND | Urban | Overloads |  | 1 | 87.0667 | 87.0667 | 1 | No
| 1842225 | 2024-05-10 | 14:12 | 2024-05-10 | 16:45 | SS13 | SPRINGVALE SOUTH | Urban | Animal | Animal impact | 73.03 | 11156.5521 | 152.7667 | 1 | No
| 1842239 | 2024-05-10 | 15:49 | 2024-05-10 | 21:20 | DMA14 | DROMANA | Urban | Asset Failure | LV | 3.96 | 1309.968 | 330.8 | 1 | No
| 1842250 | 2024-05-10 | 16:25 | 2024-05-10 | 17:31 | NW14 | NUNAWADING | Urban | Asset Failure | LV | 1 | 65.5 | 65.5 | 1 | No
| 1842261 | 2024-05-10 | 18:26 | 2024-05-10 | 18:54 | MGE34 | MULGRAVE | Urban | Asset Failure | HV | 150 | 4202.505 | 28.0167 | 1 | No
| 1842261 | 2024-05-10 | 18:26 | 2024-05-10 | 19:22 | MGE34 | MULGRAVE | Urban | Asset Failure | HV | 184 | 10322.4 | 56.1 | 2 | No
| 1842261 | 2024-05-10 | 18:26 | 2024-05-10 | 19:27 | MGE34 | MULGRAVE | Urban | Asset Failure | HV | 78 | 4689.1026 | 60.1167 | 3 | No
| 1842261 | 2024-05-10 | 18:26 | 2024-05-10 | 19:34 | MGE34 | MULGRAVE | Urban | Asset Failure | HV | 222 | 14903.5926 | 67.1333 | 4 | No
| 1842266 | 2024-05-10 | 20:11 | 2024-05-10 | 23:06 | CM13 | CHELTENHAM | Urban | Asset Failure | LV | 22 | 3850 | 175 | 1 | No
| 1842275 | 2024-05-10 | 21:53 | 2024-06-10 | 10:07 | STO22 | SORRENTO | Urban | Asset Failure | LV | 1 | 733.95 | 733.95 | 1 | No
| 1842288 | 2024-05-10 | 22:39 | 2024-05-10 | 23:54 | FSH21 | FRANKSTON SOUTH | Rural Short | Third Party | Other | 58.29 | 4347.4606 | 74.5833 | 1 | No
| 1842376 | 2024-06-10 | 19:23 | 2024-06-10 | 20:50 | EM7 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 86.2333 | 86.2333 | 1 | No
| 1842372 | 2024-06-10 | 20:39 | 2024-06-10 | 22:25 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 1 | 106 | 106 | 1 | No
| 1842408 | 2024-07-10 | 4:25 | 2024-07-10 | 7:25 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 179.2667 | 179.2667 | 1 | No
| 1842416 | 2024-07-10 | 6:35 | 2024-07-10 | 8:32 | CRM15 | CARRUM | Urban | Asset Failure | LV | 1 | 117.2 | 117.2 | 1 | No
| 1842417 | 2024-07-10 | 6:37 | 2024-07-10 | 9:30 | MGE22 | MULGRAVE | Urban | Animal | Animal impact | 3 | 517.5 | 172.5 | 1 | No
| 1842597 | 2024-07-10 | 13:08 | 2024-07-10 | 13:12 | M22 | MENTONE | Urban | Network Business | Network Error | 68 | 218.7356 | 3.2167 | 1 | No
| 1842612 | 2024-07-10 | 13:39 | 2024-07-10 | 15:15 | EB22 | EAST BURWOOD | Urban | Overloads |  | 11.55 | 1102.4475 | 95.45 | 1 | No
| 1842621 | 2024-07-10 | 13:57 | 2024-07-10 | 22:50 | NB21 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 532.5833 | 532.5833 | 1 | No
| 1842650 | 2024-07-10 | 16:33 | 2024-07-10 | 18:56 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 143.0667 | 143.0667 | 1 | No
| 1842664 | 2024-07-10 | 18:04 | 2024-08-10 | 19:07 | DN7 | DANDENONG | Urban | Third Party | Vehicle Impact | 39 | 58585.8 | 1502.2 | 1 | No
| 1842802 | 2024-07-10 | 20:20 | 2024-07-10 | 21:15 | SV16 | SPRINGVALE | Urban | Unknown | Unknown | 3 | 165 | 55 | 1 | No
| 1842795 | 2024-07-10 | 20:55 | 2024-07-10 | 21:56 | BW35 | BURWOOD | Urban | Asset Failure | LV | 46 | 2806 | 61 | 1 | No
| 1842790 | 2024-07-10 | 21:45 | 2024-07-10 | 23:11 | RWT23 | RINGWOOD | Urban | Animal | Animal impact | 6.03 | 517.5748 | 85.8333 | 1 | No
| 1842816 | 2024-08-10 | 5:56 | 2024-08-10 | 8:12 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 136.2333 | 136.2333 | 1 | No
| 1842616 | 2024-08-10 | 7:06 | 2024-08-10 | 7:47 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 41.9833 | 41.9833 | 1 | No
| 1842822 | 2024-08-10 | 7:21 | 2024-08-10 | 8:42 | RD4 | RIVERSDALE | Urban | Asset Failure | LV | 1 | 80.4 | 80.4 | 1 | No
| 1842931 | 2024-08-10 | 10:49 | 2024-09-10 | 0:15 | DN22 | DANDENONG | Urban | Third Party | Other | 1 | 805.3 | 805.3 | 1 | No
| 1842812 | 2024-08-10 | 12:31 | 2024-08-10 | 13:52 | NW32 | NUNAWADING | Urban | Asset Failure | LV | 1 | 81.8333 | 81.8333 | 1 | No
| 1842993 | 2024-08-10 | 13:18 | 2024-08-10 | 20:07 | EL23 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 408.3833 | 408.3833 | 1 | No
| 1842998 | 2024-08-10 | 13:22 | 2024-08-10 | 14:27 | KBH34 | KEYSBOROUGH | Urban | Unknown | Unknown | 18 | 1170.9 | 65.05 | 1 | No
| 1843005 | 2024-08-10 | 13:32 | 2024-08-10 | 17:00 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 207.6667 | 207.6667 | 1 | No
| 1843043 | 2024-08-10 | 16:04 | 2024-08-10 | 17:25 | MR14 | MOORABBIN | Urban | Asset Failure | LV | 1 | 80.4333 | 80.4333 | 1 | No
| 1843092 | 2024-08-10 | 20:45 | 2024-09-10 | 0:44 | NP33 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 238.2 | 238.2 | 1 | No
| 1843108 | 2024-08-10 | 23:34 | 2024-09-10 | 1:37 | LWN34 | LANGWARRIN | Urban | Asset Failure | LV | 56 | 6848.8 | 122.3 | 1 | No
| 1843116 | 2024-09-10 | 1:50 | 2024-09-10 | 3:26 | RBD12 | ROSEBUD | Rural Short | Unknown | Unknown | 15 | 1438.2495 | 95.8833 | 1 | No
| 1843116 | 2024-09-10 | 1:50 | 2024-09-10 | 4:00 | RBD12 | ROSEBUD | Rural Short | Unknown | Unknown | 20 | 2595.334 | 129.7667 | 2 | No
| 1843116 | 2024-09-10 | 1:50 | 2024-09-10 | 4:55 | RBD12 | ROSEBUD | Rural Short | Unknown | Unknown | 88 | 16306.4 | 185.3 | 3 | No
| 1843132 | 2024-09-10 | 2:18 | 2024-09-10 | 3:22 | OAK23 | OAKLEIGH | Urban | Third Party | Other | 92 | 5886.4636 | 63.9833 | 1 | No
| 1843110 | 2024-09-10 | 7:49 | 2024-09-10 | 9:14 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 85.45 | 85.45 | 1 | No
| 1843149 | 2024-09-10 | 8:51 | 2024-09-10 | 10:30 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 1 | 99 | 99 | 1 | No
| 1843211 | 2024-09-10 | 9:15 | 2024-09-10 | 10:32 | OE4 | OAKLEIGH EAST | Urban | Asset Failure | LV | 1 | 77.1167 | 77.1167 | 1 | No
| 1843255 | 2024-09-10 | 10:20 | 2024-09-10 | 11:45 | DN11 | DANDENONG | Urban | Asset Failure | LV | 8.91 | 754.2315 | 84.65 | 1 | No
| 1843210 | 2024-09-10 | 12:52 | 2024-09-10 | 13:42 | STO22 | SORRENTO | Urban | Asset Failure | LV | 3 | 150 | 50 | 1 | No
| 1843385 | 2024-09-10 | 15:09 | 2024-09-10 | 23:27 | NW21 | NUNAWADING | Urban | Asset Failure | LV | 1 | 497.1167 | 497.1167 | 1 | No
| 1843391 | 2024-09-10 | 15:50 | 2024-09-10 | 20:20 | NW23 | NUNAWADING | Urban | Unknown | Unknown | 1 | 270 | 270 | 1 | No
| 1843405 | 2024-09-10 | 17:03 | 2024-09-10 | 18:38 | MR13 | MOORABBIN | Urban | Asset Failure | LV | 1 | 94.2833 | 94.2833 | 1 | No
| 1843407 | 2024-09-10 | 17:13 | 2024-10-10 | 0:25 | OE6 | OAKLEIGH EAST | Urban | Third Party | Other | 2 | 863.6 | 431.8 | 1 | No
| 1843408 | 2024-09-10 | 17:34 | 2024-09-10 | 18:03 | RBD21 | ROSEBUD | Rural Short | Animal | Animal impact | 2 | 59.4 | 29.7 | 1 | No
| 1842941 | 2024-09-10 | 19:02 | 2024-09-10 | 21:23 | NW14 | NUNAWADING | Urban | Asset Failure | LV | 1 | 141.3167 | 141.3167 | 1 | No
| 1843422 | 2024-09-10 | 20:00 | 2024-09-10 | 22:30 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 150.1 | 150.1 | 1 | No
| 1843437 | 2024-09-10 | 23:33 | 2024-10-10 | 2:11 | DSH33 | DANDENONG SOUTH | Urban | Asset Failure | Distribution substation | 4 | 631.3332 | 157.8333 | 1 | No
| 1843443 | 2024-10-10 | 0:45 | 2024-10-10 | 2:32 | HGS21 | HASTINGS | Rural Short | Animal | Other | 1 | 106.7333 | 106.7333 | 1 | No
| 1843444 | 2024-10-10 | 2:00 | 2024-10-10 | 2:57 | HGS21 | HASTINGS | Rural Short | Unknown | Unknown | 1 | 57.35 | 57.35 | 1 | No
| 1843449 | 2024-10-10 | 2:22 | 2024-10-10 | 3:57 | FSH33 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 9.24 | 876.1063 | 94.8167 | 1 | No
| 1843458 | 2024-10-10 | 5:16 | 2024-10-10 | 6:06 | DN24 | DANDENONG | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 15 | 741.75 | 49.45 | 1 | No
| 1843458 | 2024-10-10 | 5:16 | 2024-10-10 | 6:18 | DN24 | DANDENONG | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 161 | 9904.1887 | 61.5167 | 2 | No
| 1843458 | 2024-10-10 | 5:16 | 2024-10-10 | 6:46 | DN24 | DANDENONG | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 16 | 1435.4672 | 89.7167 | 3 | No
| 1843458 | 2024-10-10 | 5:16 | 2024-10-10 | 10:05 | DN24 | DANDENONG | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 4 | 1153.5332 | 288.3833 | 4 | No
| 1843468 | 2024-10-10 | 6:31 | 2024-10-10 | 9:05 | MR15 | MOORABBIN | Urban | Asset Failure | LV | 1 | 153.8667 | 153.8667 | 1 | No
| 1843469 | 2024-10-10 | 6:35 | 2024-10-10 | 8:38 | MC31 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 122.9833 | 122.9833 | 1 | No
| 1843479 | 2024-10-10 | 9:11 | 2024-10-10 | 12:04 | SR22 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 173.35 | 173.35 | 1 | No
| 1843552 | 2024-10-10 | 9:35 | 2024-10-10 | 11:00 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 84.3333 | 84.3333 | 1 | No
| 1843669 | 2024-10-10 | 15:40 | 2024-10-10 | 17:30 | EB32 | EAST BURWOOD | Urban | Unknown | Unknown | 1 | 110 | 110 | 1 | No
| 1843700 | 2024-10-10 | 17:52 | 2024-10-10 | 22:41 | M35 | MENTONE | Urban | Asset Failure | LV | 3 | 866.55 | 288.85 | 1 | No
| 1843715 | 2024-10-10 | 23:14 | 2024-11-10 | 1:31 | SS14 | SPRINGVALE SOUTH | Urban | Third Party | Other | 13 | 1773.2 | 136.4 | 1 | No
| 1843715 | 2024-10-10 | 23:14 | 2024-11-10 | 1:31 | SS14 | SPRINGVALE SOUTH | Urban | Third Party | Other | 3 | 411.0501 | 137.0167 | 2 | No
| 1843715 | 2024-10-10 | 23:14 | 2024-11-10 | 5:38 | SS14 | SPRINGVALE SOUTH | Urban | Third Party | Other | 1 | 383.7333 | 383.7333 | 3 | No
| 1843724 | 2024-11-10 | 1:30 | 2024-11-10 | 2:48 | HGS22 | HASTINGS | Rural Short | Animal | Animal impact | 2.68 | 208.37 | 77.75 | 1 | No
| 1843723 | 2024-11-10 | 1:33 | 2024-11-10 | 5:37 | SS14 | SPRINGVALE SOUTH | Urban | Third Party | Other | 1 | 244.6 | 244.6 | 1 | No
| 1843723 | 2024-11-10 | 1:33 | 2024-11-10 | 5:37 | SS14 | SPRINGVALE SOUTH | Urban | Third Party | Other | 1 | 244.4833 | 244.4833 | 1 | No
| 1843726 | 2024-11-10 | 2:14 | 2024-11-10 | 2:35 | SV20 | SPRINGVALE | Urban | Asset Failure | HV | 13 | 279.7171 | 21.5167 | 1 | No
| 1843736 | 2024-11-10 | 6:42 | 2024-11-10 | 7:43 | LD1 | LYNDALE | Urban | Unknown | Unknown | 1 | 61.4167 | 61.4167 | 1 | No
| 1843763 | 2024-11-10 | 8:17 | 2024-11-10 | 9:00 | LWN34 | LANGWARRIN | Urban | Third Party | Other | 1 | 42.0667 | 42.0667 | 1 | No
| 1843798 | 2024-11-10 | 9:17 | 2024-11-10 | 11:16 | NW11 | NUNAWADING | Urban | Asset Failure | LV | 1 | 119.15 | 119.15 | 1 | No
| 1843774 | 2024-11-10 | 10:12 | 2024-11-10 | 12:07 | SVW55 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 115.35 | 115.35 | 1 | No
| 1843899 | 2024-11-10 | 14:44 | 2024-11-10 | 18:49 | MGE21 | MULGRAVE | Urban | Unknown | Unknown | 1 | 244.95 | 244.95 | 1 | No
| 1843904 | 2024-11-10 | 14:54 | 2024-11-10 | 18:02 | DN21 | DANDENONG | Urban | Unknown | Unknown | 1 | 188.1 | 188.1 | 1 | No
| 1843916 | 2024-11-10 | 17:10 | 2024-11-10 | 19:10 | EW8 | ELWOOD | Urban | Asset Failure | LV | 1 | 119.9833 | 119.9833 | 1 | No
| 1843928 | 2024-11-10 | 19:34 | 2024-11-10 | 20:36 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 62.15 | 62.15 | 1 | No
| 1843934 | 2024-11-10 | 19:58 | 2024-11-10 | 22:14 | DC2 | DONCASTER | Urban | Asset Failure | LV | 1 | 136.2667 | 136.2667 | 1 | No
| 1843937 | 2024-11-10 | 20:27 | 2024-11-10 | 21:45 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 1 | 77.3833 | 77.3833 | 1 | No
| 1843941 | 2024-11-10 | 21:41 | 2024-11-10 | 22:50 | DC2 | DONCASTER | Urban | Animal | Animal impact | 67 | 4588.3811 | 68.4833 | 1 | No
| 1843966 | 2024-12-10 | 6:48 | 2024-12-10 | 9:10 | FSH21 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 3 | 423.6999 | 141.2333 | 1 | No
| 1843977 | 2024-12-10 | 8:30 | 2024-12-10 | 14:47 | NP25 | NOBLE PARK | Urban | Asset Failure | LV | 126 | 47531.3958 | 377.2333 | 1 | No
| 1843979 | 2024-12-10 | 9:21 | 2024-12-10 | 10:20 | OR32 | ORMOND | Urban | Asset Failure | LV | 1 | 58.8 | 58.8 | 1 | No
| 1843984 | 2024-12-10 | 11:05 | 2024-12-10 | 14:54 | NP16 | NOBLE PARK | Urban | Asset Failure | LV | 41 | 9417.0153 | 229.6833 | 1 | No
| 1843992 | 2024-12-10 | 12:53 | 13/10/2024 | 20:00 | LD4 | LYNDALE | Urban | Unknown | Unknown | 3 | 5600.3499 | 1866.7833 | 1 | No
| 1844005 | 2024-12-10 | 17:31 | 2024-12-10 | 20:32 | MC12 | MORDIALLOC | Urban | Weather |  | 84 | 15208.2 | 181.05 | 1 | No
| 1844022 | 2024-12-10 | 23:04 | 13/10/2024 | 0:31 | HT2 | HEATHERTON | Urban | Asset Failure | LV | 1 | 87.3667 | 87.3667 | 1 | No
| 1844024 | 13/10/2024 | 7:48 | 13/10/2024 | 8:49 | NP23 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 61.8333 | 61.8333 | 1 | No
| 1844027 | 13/10/2024 | 8:03 | 13/10/2024 | 10:13 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 129.8 | 129.8 | 1 | No
| 1844038 | 13/10/2024 | 10:02 | 13/10/2024 | 11:45 | NP16 | NOBLE PARK | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 102.2167 | 102.2167 | 1 | No
| 1844041 | 13/10/2024 | 10:44 | 13/10/2024 | 13:11 | BT12 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 146.1333 | 146.1333 | 1 | No
| 1844044 | 13/10/2024 | 11:04 | 13/10/2024 | 15:55 | M31 | MENTONE | Urban | Asset Failure | LV | 1 | 290.0667 | 290.0667 | 1 | No
| 1844056 | 13/10/2024 | 14:00 | 13/10/2024 | 17:23 | OR24 | ORMOND | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 203.05 | 203.05 | 1 | No
| 1844060 | 13/10/2024 | 14:30 | 13/10/2024 | 22:05 | BW33 | BURWOOD | Urban | Asset Failure | LV | 1 | 455.1 | 455.1 | 1 | No
| 1844072 | 13/10/2024 | 17:34 | 13/10/2024 | 19:05 | BW34 | BURWOOD | Urban | Third Party |  | 90.45 | 8170.647 | 90.3333 | 1 | No
| 1844091 | 13/10/2024 | 18:45 | 13/10/2024 | 20:45 | BW21 | BURWOOD | Urban | Third Party |  | 0.67 | 81.0588 | 120.9833 | 1 | No
| 1844099 | 13/10/2024 | 22:42 | 14/10/2024 | 0:45 | MR33 | MOORABBIN | Urban | Asset Failure | LV | 1 | 123 | 123 | 1 | No
| 1844101 | 13/10/2024 | 23:21 | 14/10/2024 | 0:30 | DMA21 | DROMANA | Urban | Third Party | Vehicle Impact | 3 | 205.4499 | 68.4833 | 1 | No
| 1844104 | 14/10/2024 | 2:16 | 14/10/2024 | 4:27 | FSH22 | FRANKSTON SOUTH | Urban | Third Party | Other | 1 | 131.6833 | 131.6833 | 1 | No
| 1844111 | 14/10/2024 | 5:46 | 14/10/2024 | 8:35 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 169.5833 | 169.5833 | 1 | No
| 1844190 | 14/10/2024 | 12:38 | 14/10/2024 | 14:40 | HT11 | HEATHERTON | Urban | Unknown | Unknown | 1 | 121.6167 | 121.6167 | 1 | No
| 1844213 | 14/10/2024 | 14:49 | 14/10/2024 | 16:20 | KBH34 | KEYSBOROUGH | Urban | Unknown | Unknown | 1 | 90.3333 | 90.3333 | 1 | No
| 1844229 | 14/10/2024 | 16:47 | 14/10/2024 | 19:40 | EW1 | ELWOOD | Urban | Overloads |  | 70.95 | 12242.4225 | 172.55 | 1 | No
| 1844221 | 14/10/2024 | 17:11 | 14/10/2024 | 19:35 | HT10 | HEATHERTON | Urban | Asset Failure | LV | 5 | 720 | 144 | 1 | No
| 1844255 | 14/10/2024 | 22:23 | 15/10/2024 | 0:05 | DN22 | DANDENONG | Urban | Third Party | Other | 1 | 101.8833 | 101.8833 | 1 | No
| 1844256 | 14/10/2024 | 22:58 | 15/10/2024 | 0:12 | RWT24 | RINGWOOD | Urban | Animal | Animal impact | 2.01 | 148.74 | 74 | 1 | No
| 1844260 | 15/10/2024 | 0:03 | 15/10/2024 | 0:49 | GW3 | GLEN WAVERLEY | Urban | Animal | Animal impact | 20.1 | 916.56 | 45.6 | 1 | No
| 1844263 | 15/10/2024 | 1:21 | 15/10/2024 | 2:54 | GW3 | GLEN WAVERLEY | Urban | Animal | Animal impact | 30 | 2813.001 | 93.7667 | 1 | No
| 1844268 | 15/10/2024 | 2:31 | 15/10/2024 | 9:40 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 1 | 428.2833 | 428.2833 | 1 | No
| 1844282 | 15/10/2024 | 6:16 | 15/10/2024 | 9:45 | DC4 | DONCASTER | Urban | Unknown | Unknown | 14.07 | 2934.0635 | 208.5333 | 1 | No
| 1844284 | 15/10/2024 | 7:15 | 15/10/2024 | 11:00 | MTN24 | MORNINGTON | Rural Short | Asset Failure | Distribution substation | 0.67 | 150.616 | 224.8 | 1 | No
| 1844288 | 15/10/2024 | 7:47 | 15/10/2024 | 8:30 | RBD21 | ROSEBUD | Rural Short | Unknown | Unknown | 1 | 42.3667 | 42.3667 | 1 | No
| 1844300 | 15/10/2024 | 8:13 | 15/10/2024 | 9:50 | FTN23 | FRANKSTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 97.4667 | 97.4667 | 1 | No
| 1844449 | 15/10/2024 | 15:53 | 15/10/2024 | 19:31 | OR24 | ORMOND | Urban | Asset Failure | LV | 86.46 | 18888.6309 | 218.4667 | 1 | No
| 1844451 | 15/10/2024 | 15:59 | 15/10/2024 | 17:43 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 104.0167 | 104.0167 | 1 | No
| 1844102 | 15/10/2024 | 17:45 | 15/10/2024 | 21:00 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 195 | 195 | 1 | No
| 1844479 | 15/10/2024 | 19:15 | 15/10/2024 | 22:41 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 206.2167 | 206.2167 | 1 | No
| 1844510 | 16/10/2024 | 2:26 | 16/10/2024 | 3:58 | BH11 | BOX HILL | Urban | Animal | Animal impact | 82.41 | 7536.3945 | 91.45 | 1 | No
| 1844525 | 16/10/2024 | 5:44 | 16/10/2024 | 8:27 | EM7 | EAST MALVERN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 162.6333 | 162.6333 | 1 | No
| 1844601 | 16/10/2024 | 9:50 | 16/10/2024 | 13:48 | SS14 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 238.4167 | 238.4167 | 1 | No
| 1844634 | 16/10/2024 | 10:38 | 16/10/2024 | 12:34 | MGE21 | MULGRAVE | Urban | Asset Failure | LV | 1 | 115.3 | 115.3 | 1 | No
| 1844685 | 16/10/2024 | 12:37 | 16/10/2024 | 17:30 | HT10 | HEATHERTON | Urban | Asset Failure | LV | 20 | 5847.334 | 292.3667 | 1 | No
| 1844697 | 16/10/2024 | 13:12 | 16/10/2024 | 14:38 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 1 | 85.3833 | 85.3833 | 1 | No
| 1844708 | 16/10/2024 | 13:54 | 16/10/2024 | 19:40 | NP16 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 345.3 | 345.3 | 1 | No
| 1844733 | 16/10/2024 | 15:31 | 16/10/2024 | 20:20 | SS22 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 288.4833 | 288.4833 | 1 | No
| 1844749 | 16/10/2024 | 19:38 | 16/10/2024 | 21:32 | DMA23 | DROMANA | Rural Short | Animal | Other | 1 | 113.3 | 113.3 | 1 | No
| 1844765 | 16/10/2024 | 22:38 | 17/10/2024 | 0:40 | SS21 | SPRINGVALE SOUTH | Urban | Third Party | Vehicle Impact | 4 | 487.6668 | 121.9167 | 1 | No
| 1844766 | 16/10/2024 | 22:38 | 17/10/2024 | 0:38 | SS21 | SPRINGVALE SOUTH | Urban | Third Party | Vehicle Impact | 1 | 119.7333 | 119.7333 | 1 | No
| 1844771 | 17/10/2024 | 1:52 | 17/10/2024 | 3:05 | STO22 | SORRENTO | Urban | Unknown | Unknown | 80 | 5829.336 | 72.8667 | 1 | No
| 1844843 | 17/10/2024 | 8:31 | 17/10/2024 | 11:23 | DC2 | DONCASTER | Urban | Asset Failure | HV | 158.79 | 27258.9553 | 171.6667 | 1 | No
| 1844843 | 17/10/2024 | 8:31 | 17/10/2024 | 11:23 | DC2 | DONCASTER | Urban | Asset Failure | HV | 38.86 | 6692.341 | 172.2167 | 2 | No
| 1844778 | 17/10/2024 | 8:48 | 17/10/2024 | 10:27 | BR15 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 99.1667 | 99.1667 | 1 | No
| 1844893 | 17/10/2024 | 9:15 | 17/10/2024 | 10:36 | BR15 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 81.0333 | 81.0333 | 1 | No
| 1844923 | 17/10/2024 | 11:44 | 17/10/2024 | 17:58 | STO23 | SORRENTO | Urban | Third Party | Vehicle Impact | 1 | 373.55 | 373.55 | 1 | No
| 1844938 | 17/10/2024 | 13:44 | 17/10/2024 | 18:25 | CFD13 | CAULFIELD | Urban | Asset Failure | LV | 9 | 2529 | 281 | 1 | No
| 1844957 | 17/10/2024 | 15:48 | 17/10/2024 | 17:30 | STO23 | SORRENTO | Urban | Third Party | Vehicle Impact | 1 | 101.4667 | 101.4667 | 1 | No
| 1844959 | 17/10/2024 | 16:14 | 17/10/2024 | 18:15 | OR23 | ORMOND | Urban | Asset Failure | LV | 1 | 120.15 | 120.15 | 1 | No
| 1844979 | 17/10/2024 | 18:50 | 17/10/2024 | 20:58 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 128.0333 | 128.0333 | 1 | No
| 1844998 | 17/10/2024 | 23:46 | 18/10/2024 | 8:52 | SS22 | SPRINGVALE SOUTH | Urban | Unknown | Unknown | 1 | 546.2167 | 546.2167 | 1 | No
| 1844999 | 18/10/2024 | 1:05 | 18/10/2024 | 2:25 | RBD11 | ROSEBUD | Urban | Asset Failure | Distribution substation | 96.48 | 7703.928 | 79.85 | 1 | No
| 1845002 | 18/10/2024 | 3:49 | 18/10/2024 | 5:23 | EW1 | ELWOOD | Urban | Asset Failure | LV | 1 | 93.6167 | 93.6167 | 1 | No
| 1845050 | 18/10/2024 | 8:57 | 18/10/2024 | 11:30 | MTN35 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 152.9167 | 152.9167 | 1 | No
| 1845059 | 18/10/2024 | 9:34 | 18/10/2024 | 11:34 | BT15 | BENTLEIGH | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 141 | 16818.9453 | 119.2833 | 1 | No
| 1845092 | 18/10/2024 | 10:41 | 18/10/2024 | 15:27 | K25 | GARDINER | Urban | Asset Failure | LV | 1 | 286.2833 | 286.2833 | 1 | No
| 1845094 | 18/10/2024 | 10:42 | 18/10/2024 | 11:13 | NP36 | NOBLE PARK | Urban | Third Party | Vehicle Impact | 407 | 12840.85 | 31.55 | 1 | No
| 1845094 | 18/10/2024 | 10:42 | 18/10/2024 | 17:50 | NP36 | NOBLE PARK | Urban | Third Party | Vehicle Impact | 95 | 40718.5865 | 428.6167 | 2 | No
| 1845094 | 18/10/2024 | 10:42 | 18/10/2024 | 17:53 | NP36 | NOBLE PARK | Urban | Third Party | Vehicle Impact | 145 | 62577.1715 | 431.5667 | 3 | No
| 1845100 | 18/10/2024 | 10:46 | 18/10/2024 | 11:37 | NB26 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 51.35 | 51.35 | 1 | No
| 1845137 | 18/10/2024 | 11:45 | 18/10/2024 | 19:08 | K34 | GARDINER | Urban | Asset Failure | LV | 1 | 443.35 | 443.35 | 1 | No
| 1845148 | 18/10/2024 | 12:26 | 18/10/2024 | 18:00 | MTN31 | MORNINGTON | Urban | Overloads |  | 15 | 5008.7505 | 333.9167 | 1 | No
| 1845156 | 18/10/2024 | 13:07 | 18/10/2024 | 20:15 | CDA11 | CLARINDA | Urban | Third Party | Vehicle Impact | 60 | 25683 | 428.05 | 1 | No
| 1845156 | 18/10/2024 | 13:07 | 18/10/2024 | 20:19 | CDA11 | CLARINDA | Urban | Third Party | Vehicle Impact | 95 | 41082.75 | 432.45 | 2 | No
| 1845156 | 18/10/2024 | 13:07 | 18/10/2024 | 20:27 | CDA11 | CLARINDA | Urban | Third Party | Vehicle Impact | 1 | 440.0167 | 440.0167 | 3 | No
| 1845156 | 18/10/2024 | 13:07 | 18/10/2024 | 20:31 | CDA11 | CLARINDA | Urban | Third Party | Vehicle Impact | 74 | 32888.0642 | 444.4333 | 4 | No
| 1845171 | 18/10/2024 | 13:25 | 18/10/2024 | 16:19 | FSH11 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 1 | 173.2667 | 173.2667 | 1 | No
| 1845154 | 18/10/2024 | 13:30 | 18/10/2024 | 15:48 | MTN35 | MORNINGTON | Rural Short | Asset Failure | LV | 17.49 | 2413.62 | 138 | 1 | No
| 1845071 | 18/10/2024 | 16:43 | 18/10/2024 | 21:24 | OR32 | ORMOND | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 281.2333 | 281.2333 | 1 | No
| 1845084 | 18/10/2024 | 17:21 | 18/10/2024 | 21:00 | M13 | MENTONE | Urban | Asset Failure | LV | 1 | 219.3667 | 219.3667 | 1 | No
| 1845200 | 18/10/2024 | 17:30 | 19/10/2024 | 0:04 | CFD22 | CAULFIELD | Urban | Asset Failure | LV | 1 | 394.5833 | 394.5833 | 1 | No
| 1845208 | 18/10/2024 | 18:36 | 18/10/2024 | 20:50 | LWN21 | LANGWARRIN | Rural Short | Animal | Animal impact | 3.35 | 447.1134 | 133.4667 | 1 | No
| 1845209 | 18/10/2024 | 18:58 | 18/10/2024 | 23:14 | NP36 | NOBLE PARK | Urban | Third Party | Vehicle Impact | 4 | 1023.4668 | 255.8667 | 1 | No
| 1845211 | 18/10/2024 | 19:16 | 18/10/2024 | 23:10 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 233.6167 | 233.6167 | 1 | No
| 1845225 | 18/10/2024 | 20:41 | 18/10/2024 | 21:13 | CDA11 | CLARINDA | Urban | Unknown | Unknown | 1 | 31.6833 | 31.6833 | 1 | No
| 1845230 | 18/10/2024 | 21:19 | 18/10/2024 | 23:21 | BW34 | BURWOOD | Urban | Asset Failure | LV | 1 | 122.0667 | 122.0667 | 1 | No
| 1845233 | 18/10/2024 | 22:22 | 18/10/2024 | 23:09 | EB33 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 46.65 | 46.65 | 1 | No
| 1845229 | 18/10/2024 | 23:33 | 19/10/2024 | 2:56 | DC6 | DONCASTER | Urban | Asset Failure | LV | 1 | 203.65 | 203.65 | 1 | No
| 1845245 | 19/10/2024 | 3:18 | 19/10/2024 | 5:35 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 136.25 | 136.25 | 1 | No
| 1845261 | 19/10/2024 | 8:13 | 19/10/2024 | 16:15 | EM10 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 481.35 | 481.35 | 1 | No
| 1845250 | 19/10/2024 | 8:48 | 19/10/2024 | 14:02 | BT14 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 314.9333 | 314.9333 | 1 | No
| 1845278 | 19/10/2024 | 9:21 | 19/10/2024 | 13:39 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 257.8167 | 257.8167 | 1 | No
| 1845281 | 19/10/2024 | 9:30 | 19/10/2024 | 14:27 | BW35 | BURWOOD | Urban | Asset Failure | LV | 1 | 296.3667 | 296.3667 | 1 | No
| 1845287 | 19/10/2024 | 10:10 | 19/10/2024 | 12:00 | GW6 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 109.8333 | 109.8333 | 1 | No
| 1845293 | 19/10/2024 | 10:43 | 19/10/2024 | 14:45 | RBD12 | ROSEBUD | Rural Short | Animal | Other | 1 | 241.5333 | 241.5333 | 1 | No
| 1845294 | 19/10/2024 | 10:47 | 19/10/2024 | 12:30 | FTN13 | FRANKSTON | Urban | Asset Failure | LV | 1 | 102.05 | 102.05 | 1 | No
| 1845297 | 19/10/2024 | 11:02 | 19/10/2024 | 13:13 | OAK26 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 131.0333 | 131.0333 | 1 | No
| 1845298 | 19/10/2024 | 11:02 | 19/10/2024 | 15:23 | DC1 | DONCASTER | Urban | Asset Failure | LV | 1 | 261.25 | 261.25 | 1 | No
| 1845299 | 19/10/2024 | 11:03 | 19/10/2024 | 15:24 | LWN34 | LANGWARRIN | Urban | Third Party | Vehicle Impact | 42 | 10994.2014 | 261.7667 | 1 | No
| 1845300 | 19/10/2024 | 11:07 | 19/10/2024 | 15:24 | LWN24 | LANGWARRIN | Urban | Third Party | Vehicle Impact | 28 | 7189 | 256.75 | 1 | No
| 1845305 | 19/10/2024 | 13:07 | 19/10/2024 | 16:15 | FSH31 | FRANKSTON SOUTH | Urban | Weather |  | 1 | 187.0333 | 187.0333 | 1 | No
| 1845307 | 19/10/2024 | 13:08 | 19/10/2024 | 19:44 | BU22 | BULLEEN | Urban | Third Party | Vehicle Impact | 40 | 15871.332 | 396.7833 | 1 | No
| 1845309 | 19/10/2024 | 13:21 | 19/10/2024 | 19:44 | BU22 | BULLEEN | Urban | Third Party | Vehicle Impact | 2 | 765.5 | 382.75 | 1 | No
| 1845311 | 19/10/2024 | 13:33 | 19/10/2024 | 16:22 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 168.8333 | 168.8333 | 1 | No
| 1845325 | 19/10/2024 | 18:16 | 19/10/2024 | 20:47 | M31 | MENTONE | Urban | Asset Failure | LV | 1 | 151 | 151 | 1 | No
| 1845354 | 20/10/2024 | 6:30 | 20/10/2024 | 10:12 | DMA23 | DROMANA | Rural Short | Asset Failure | LV | 1 | 221.2167 | 221.2167 | 1 | No
| 1845367 | 20/10/2024 | 12:05 | 20/10/2024 | 16:00 | NB32 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 234.2667 | 234.2667 | 1 | No
| 1845380 | 20/10/2024 | 13:54 | 20/10/2024 | 15:15 | GW4 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 80.2167 | 80.2167 | 1 | No
| 1845386 | 20/10/2024 | 14:56 | 20/10/2024 | 16:45 | GW11 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 109 | 109 | 1 | No
| 1845396 | 20/10/2024 | 18:15 | 20/10/2024 | 19:30 | M12 | MENTONE | Urban | Asset Failure | LV | 1 | 74.9 | 74.9 | 1 | No
| 1845409 | 20/10/2024 | 22:05 | 21/10/2024 | 0:06 | MTN24 | MORNINGTON | Rural Short | Asset Failure | LV | 3 | 364.2501 | 121.4167 | 1 | No
| 1845407 | 20/10/2024 | 22:07 | 20/10/2024 | 23:58 | MGE21 | MULGRAVE | Urban | Asset Failure | LV | 1 | 111.05 | 111.05 | 1 | No
| 1845416 | 21/10/2024 | 4:10 | 21/10/2024 | 5:26 | GW12 | GLEN WAVERLEY | Urban | Animal | Other | 38.86 | 2971.496 | 76.4667 | 1 | No
| 1845456 | 21/10/2024 | 8:16 | 21/10/2024 | 10:21 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 125.5 | 125.5 | 1 | No
| 1845513 | 21/10/2024 | 10:54 | 21/10/2024 | 12:33 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 98.5333 | 98.5333 | 1 | No
| 1845518 | 21/10/2024 | 11:22 | 21/10/2024 | 12:36 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 1 | 73.2 | 73.2 | 1 | No
| 1845569 | 21/10/2024 | 14:05 | 21/10/2024 | 16:10 | LD4 | LYNDALE | Urban | Unknown | Unknown | 48 | 5973.6 | 124.45 | 1 | No
| 1845607 | 21/10/2024 | 16:28 | 21/10/2024 | 20:59 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 270.1 | 270.1 | 1 | No
| 1845588 | 21/10/2024 | 16:48 | 21/10/2024 | 19:38 | GW11 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 170.1333 | 170.1333 | 1 | No
| 1845615 | 21/10/2024 | 17:16 | 21/10/2024 | 19:00 | MTN24 | MORNINGTON | Rural Short | Third Party |  | 4 | 412.4668 | 103.1167 | 1 | No
| 1845617 | 21/10/2024 | 17:30 | 21/10/2024 | 21:32 | M13 | MENTONE | Urban | Network Business | Network Error | 1 | 242.1833 | 242.1833 | 1 | No
| 1845620 | 21/10/2024 | 18:23 | 21/10/2024 | 19:48 | GW2 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 84.5167 | 84.5167 | 1 | No
| 1845630 | 21/10/2024 | 20:43 | 21/10/2024 | 23:30 | BR10 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 166.1833 | 166.1833 | 1 | No
| 1845668 | 22/10/2024 | 5:11 | 22/10/2024 | 6:59 | K24 | GARDINER | Urban | Animal | Animal impact | 58.29 | 6264.2339 | 107.4667 | 1 | No
| 1845781 | 22/10/2024 | 10:32 | 22/10/2024 | 19:05 | OR23 | ORMOND | Urban | Third Party | Other | 14 | 7169.1662 | 512.0833 | 1 | No
| 1845788 | 22/10/2024 | 10:53 | 22/10/2024 | 11:55 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 62 | 62 | 1 | No
| 1845799 | 22/10/2024 | 11:32 | 22/10/2024 | 12:34 | GW12 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 62.8 | 62.8 | 1 | No
| 1845853 | 22/10/2024 | 13:02 | 22/10/2024 | 14:09 | EB22 | EAST BURWOOD | Urban | Asset Failure | Distribution substation | 1180.54 | 78289.517 | 66.3167 | 1 | No
| 1845862 | 22/10/2024 | 14:09 | 22/10/2024 | 15:27 | EB22 | EAST BURWOOD | Urban | Asset Failure | HV | 0 | 7641.9801 | 78.7833 | 1 | No
| 1845862 | 22/10/2024 | 14:09 | 22/10/2024 | 15:27 | EB22 | EAST BURWOOD | Urban | Asset Failure | HV | 0 | 7722.4 | 78.8 | 2 | No
| 1845862 | 22/10/2024 | 14:09 | 22/10/2024 | 15:28 | EB22 | EAST BURWOOD | Urban | Asset Failure | HV | 0 | 8908.1629 | 78.8333 | 3 | No
| 1845891 | 22/10/2024 | 15:42 | 22/10/2024 | 17:23 | OE5 | OAKLEIGH EAST | Urban | Third Party | Other | 1 | 100.8667 | 100.8667 | 1 | No
| 1845906 | 22/10/2024 | 16:51 | 22/10/2024 | 20:35 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 223.25 | 223.25 | 1 | No
| 1845947 | 22/10/2024 | 22:12 | 22/10/2024 | 22:43 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 31.0333 | 31.0333 | 1 | No
| 1845950 | 23/10/2024 | 1:36 | 23/10/2024 | 2:25 | NP16 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 49.2833 | 49.2833 | 1 | No
| 1845955 | 23/10/2024 | 1:49 | 23/10/2024 | 3:30 | GW7 | GLEN WAVERLEY | Urban | Animal | Animal impact | 43.55 | 4397.0998 | 100.9667 | 1 | No
| 1845960 | 23/10/2024 | 2:01 | 23/10/2024 | 3:30 | GW7 | GLEN WAVERLEY | Urban | Animal | Animal impact | 0.67 | 59.0382 | 88.1167 | 1 | No
| 1845962 | 23/10/2024 | 6:05 | 23/10/2024 | 6:50 | FSH22 | FRANKSTON SOUTH | Urban | Third Party | Other | 1 | 45.0167 | 45.0167 | 1 | No
| 1845964 | 23/10/2024 | 7:17 | 23/10/2024 | 10:40 | MC32 | MORDIALLOC | Urban | Third Party | Vehicle Impact | 1 | 203.25 | 203.25 | 1 | No
| 1845980 | 23/10/2024 | 9:10 | 23/10/2024 | 10:39 | LD33 | LYNDALE | Urban | Asset Failure | LV | 21 | 1884.0507 | 89.7167 | 1 | No
| 1846003 | 23/10/2024 | 9:10 | 23/10/2024 | 12:03 | GW6 | GLEN WAVERLEY | Urban | Asset Failure | LV | 2 | 347.6 | 173.8 | 1 | No
| 1846018 | 23/10/2024 | 10:53 | 23/10/2024 | 12:39 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 1 | 106.6 | 106.6 | 1 | No
| 1846063 | 23/10/2024 | 17:39 | 23/10/2024 | 18:25 | LD4 | LYNDALE | Urban | Animal | Animal impact | 32.16 | 1464.888 | 45.55 | 1 | No
| 1846087 | 23/10/2024 | 20:43 | 23/10/2024 | 22:25 | RWT35 | RINGWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 102.5333 | 102.5333 | 1 | No
| 1846093 | 23/10/2024 | 22:21 | 23/10/2024 | 23:34 | RBD21 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 93 | 6824.6469 | 73.3833 | 1 | No
| 1846093 | 23/10/2024 | 22:21 | 23/10/2024 | 23:43 | RBD21 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 8 | 661.7336 | 82.7167 | 2 | No
| 1846093 | 23/10/2024 | 22:21 | 24/10/2024 | 20:36 | RBD21 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 4006.05 | 1335.35 | 3 | No
| 1846100 | 24/10/2024 | 0:37 | 24/10/2024 | 2:05 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 88 | 88 | 1 | No
| 1846149 | 24/10/2024 | 8:42 | 24/10/2024 | 10:21 | STO22 | SORRENTO | Urban | Asset Failure | LV | 1 | 98.4333 | 98.4333 | 1 | No
| 1846170 | 24/10/2024 | 10:34 | 24/10/2024 | 11:16 | RBD23 | ROSEBUD | Urban | Asset Failure | Distribution substation | 73.03 | 3068.4796 | 42.0167 | 1 | No
| 1846185 | 24/10/2024 | 12:39 | 24/10/2024 | 14:23 | DN6 | DANDENONG | Urban | Asset Failure | LV | 1 | 103.85 | 103.85 | 1 | No
| 1846186 | 24/10/2024 | 12:46 | 24/10/2024 | 13:35 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 49 | 49 | 1 | No
| 1846204 | 24/10/2024 | 13:53 | 24/10/2024 | 17:04 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 190.3333 | 190.3333 | 1 | No
| 1846217 | 24/10/2024 | 14:20 | 24/10/2024 | 15:45 | OR33 | ORMOND | Urban | Asset Failure | LV | 25.41 | 2159.85 | 85 | 1 | No
| 1846213 | 24/10/2024 | 15:16 | 24/10/2024 | 17:30 | OR23 | ORMOND | Urban | Asset Failure | LV | 33 | 4444.0011 | 134.6667 | 1 | No
| 1846223 | 24/10/2024 | 17:39 | 24/10/2024 | 18:35 | DN11 | DANDENONG | Urban | Third Party | Vehicle Impact | 54 | 3006.0018 | 55.6667 | 1 | No
| 1846223 | 24/10/2024 | 17:39 | 24/10/2024 | 19:27 | DN11 | DANDENONG | Urban | Third Party | Vehicle Impact | 19 | 2061.1827 | 108.4833 | 2 | No
| 1846245 | 24/10/2024 | 20:32 | 24/10/2024 | 21:50 | FTN23 | FRANKSTON | Urban | Animal | Animal impact | 60.97 | 4750.5812 | 77.9167 | 1 | No
| 1846274 | 24/10/2024 | 23:06 | 25/10/2024 | 1:06 | RD2 | RIVERSDALE | Urban | Asset Failure | HV | 29 | 3480 | 120 | 1 | No
| 1846278 | 24/10/2024 | 23:15 | 25/10/2024 | 1:06 | K25 | GARDINER | Urban | Asset Failure | HV | 64 | 7104 | 111 | 1 | No
| 1846296 | 25/10/2024 | 2:35 | 25/10/2024 | 3:10 | LD2 | LYNDALE | Urban | Animal | Animal impact | 960 | 33631.968 | 35.0333 | 1 | No
| 1846296 | 25/10/2024 | 2:35 | 25/10/2024 | 3:13 | LD2 | LYNDALE | Urban | Animal | Animal impact | 350 | 13235.845 | 37.8167 | 2 | No
| 1846296 | 25/10/2024 | 2:35 | 25/10/2024 | 3:20 | LD2 | LYNDALE | Urban | Animal | Animal impact | 845 | 37968.6385 | 44.9333 | 3 | No
| 1846296 | 25/10/2024 | 2:35 | 25/10/2024 | 3:36 | LD2 | LYNDALE | Urban | Animal | Animal impact | 149 | 9126.25 | 61.25 | 4 | No
| 1846296 | 25/10/2024 | 2:35 | 25/10/2024 | 3:46 | LD2 | LYNDALE | Urban | Animal | Animal impact | 394 | 27954.3 | 70.95 | 5 | No
| 1846305 | 25/10/2024 | 4:08 | 25/10/2024 | 8:25 | SS23 | SPRINGVALE SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 257.2333 | 257.2333 | 1 | No
| 1846326 | 25/10/2024 | 5:11 | 25/10/2024 | 13:06 | LD2 | LYNDALE | Urban | Third Party | Other | 5 | 2374.1665 | 474.8333 | 1 | No
| 1846319 | 25/10/2024 | 7:34 | 25/10/2024 | 8:43 | EM10 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 69.8833 | 69.8833 | 1 | No
| 1846331 | 25/10/2024 | 8:27 | 25/10/2024 | 9:36 | BU15 | BULLEEN | Urban | Asset Failure | LV | 1 | 69.15 | 69.15 | 1 | No
| 1846372 | 25/10/2024 | 10:05 | 25/10/2024 | 11:42 | SH22 | SURREY HILLS | Urban | Asset Failure | LV | 1 | 97.0167 | 97.0167 | 1 | No
| 1846383 | 25/10/2024 | 10:14 | 25/10/2024 | 13:58 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 223.2667 | 223.2667 | 1 | No
| 1846479 | 25/10/2024 | 14:16 | 25/10/2024 | 23:51 | LD33 | LYNDALE | Urban | Asset Failure | HV | 15 | 8628.2505 | 575.2167 | 1 | No
| 1846515 | 25/10/2024 | 15:54 | 26/10/2024 | 0:38 | WD36 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 523.6833 | 523.6833 | 1 | No
| 1846464 | 25/10/2024 | 16:07 | 25/10/2024 | 21:17 | DC4 | DONCASTER | Urban | Asset Failure | LV | 1 | 310.3833 | 310.3833 | 1 | No
| 1846528 | 25/10/2024 | 16:49 | 25/10/2024 | 18:10 | HGS33 | HASTINGS | Rural Short | Third Party | Vehicle Impact | 6 | 483 | 80.5 | 1 | No
| 1846523 | 25/10/2024 | 17:35 | 26/10/2024 | 23:00 | DMA15 | DROMANA | Rural Short | Asset Failure | LV | 8 | 14120 | 1765 | 1 | No
| 1846536 | 25/10/2024 | 18:21 | 25/10/2024 | 21:30 | NP36 | NOBLE PARK | Urban | Unknown | Unknown | 1 | 188.9333 | 188.9333 | 1 | No
| 1846542 | 25/10/2024 | 19:09 | 25/10/2024 | 22:34 | NW31 | NUNAWADING | Urban | Asset Failure | LV | 1 | 204.8 | 204.8 | 1 | No
| 1846565 | 26/10/2024 | 2:05 | 26/10/2024 | 2:55 | K26 | GARDINER | Urban | Third Party | Other | 1 | 49.65 | 49.65 | 1 | No
| 1846567 | 26/10/2024 | 5:06 | 26/10/2024 | 8:25 | NW33 | NUNAWADING | Urban | Unknown | Unknown | 157 | 31229.9219 | 198.9167 | 1 | No
| 1846572 | 26/10/2024 | 6:47 | 26/10/2024 | 21:00 | WD36 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 853.0167 | 853.0167 | 1 | No
| 1846575 | 26/10/2024 | 7:10 | 26/10/2024 | 21:00 | WD36 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 829.7 | 829.7 | 1 | No
| 1846604 | 26/10/2024 | 10:34 | 26/10/2024 | 11:22 | SVW53 | SPRINGVALE WEST | Urban | Third Party | Other | 1 | 47.5333 | 47.5333 | 1 | No
| 1846634 | 26/10/2024 | 16:26 | 26/10/2024 | 18:20 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 114 | 114 | 1 | No
| 1846581 | 26/10/2024 | 16:31 | 26/10/2024 | 18:05 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 1 | 94.3167 | 94.3167 | 1 | No
| 1846675 | 26/10/2024 | 20:13 | 26/10/2024 | 21:00 | WD36 | WEST DONCASTER | Urban | Asset Failure | LV | 7 | 329 | 47 | 1 | No
| 1846681 | 26/10/2024 | 22:14 | 27/10/2024 | 13:13 | DMA15 | DROMANA | Rural Short | Overloads |  | 1 | 898.2167 | 898.2167 | 1 | No
| 1846690 | 27/10/2024 | 5:40 | 28/10/2024 | 8:39 | LD5 | LYNDALE | Urban | Third Party | Other | 5 | 8096.3335 | 1619.2667 | 1 | No
| 1846690 | 27/10/2024 | 5:40 | 28/10/2024 | 22:47 | LD5 | LYNDALE | Urban | Third Party | Other | 3 | 7401.2499 | 2467.0833 | 2 | No
| 1846695 | 27/10/2024 | 8:15 | 27/10/2024 | 17:45 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 6 | 3417.9 | 569.65 | 1 | No
| 1846698 | 27/10/2024 | 8:54 | 27/10/2024 | 11:40 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 165.2667 | 165.2667 | 1 | No
| 1846699 | 27/10/2024 | 10:02 | 27/10/2024 | 10:49 | GW3 | GLEN WAVERLEY | Urban | Unknown | Unknown | 83 | 3936.9639 | 47.4333 | 1 | No
| 1846708 | 27/10/2024 | 11:56 | 27/10/2024 | 13:05 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 68.3667 | 68.3667 | 1 | No
| 1846704 | 27/10/2024 | 12:31 | 27/10/2024 | 15:11 | CFD16 | CAULFIELD | Urban | Asset Failure | LV | 1 | 160.5833 | 160.5833 | 1 | No
| 1846715 | 27/10/2024 | 12:45 | 27/10/2024 | 14:55 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 129.7333 | 129.7333 | 1 | No
| 1846718 | 27/10/2024 | 13:46 | 27/10/2024 | 16:00 | M25 | MENTONE | Urban | Asset Failure | LV | 1 | 133.2833 | 133.2833 | 1 | No
| 1846726 | 27/10/2024 | 15:13 | 27/10/2024 | 16:48 | DN7 | DANDENONG | Urban | Third Party | Other | 1 | 95.2667 | 95.2667 | 1 | No
| 1846732 | 27/10/2024 | 16:54 | 27/10/2024 | 21:05 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 4.95 | 1238.985 | 250.3 | 1 | No
| 1846742 | 27/10/2024 | 19:10 | 27/10/2024 | 20:30 | SR25 | SANDRINGHAM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 15.51 | 1229.684 | 79.2833 | 1 | No
| 1846756 | 27/10/2024 | 19:59 | 27/10/2024 | 21:40 | M25 | MENTONE | Urban | Asset Failure | LV | 33.99 | 3406.9299 | 100.2333 | 1 | No
| 1846764 | 27/10/2024 | 21:50 | 28/10/2024 | 2:20 | EW14 | ELWOOD | Urban | Third Party | Vehicle Impact | 17 | 4602.4661 | 270.7333 | 1 | No
| 1846764 | 27/10/2024 | 21:50 | 28/10/2024 | 2:20 | EW14 | ELWOOD | Urban | Third Party | Vehicle Impact | 35 | 9478.5845 | 270.8167 | 2 | No
| 1846774 | 27/10/2024 | 22:34 | 27/10/2024 | 22:43 | RWT34 | RINGWOOD | Urban | Third Party | Other | 3491 | 33164.5 | 9.5 | 1 | No
| 1846774 | 27/10/2024 | 22:34 | 27/10/2024 | 22:40 | RWT35 | RINGWOOD | Urban | Third Party | Other | 2553 | 15828.6 | 6.2 | 1 | No
| 1846775 | 27/10/2024 | 22:54 | 28/10/2024 | 8:50 | EB12 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 595.55 | 595.55 | 1 | No
| 1846776 | 27/10/2024 | 23:25 | 28/10/2024 | 2:00 | LD5 | LYNDALE | Urban | Third Party | Other | 7 | 1082.0831 | 154.5833 | 1 | No
| 1846778 | 28/10/2024 | 2:09 | 28/10/2024 | 4:16 | RWT35 | RINGWOOD | Urban | Animal | Other | 93.13 | 11774.7332 | 126.4333 | 1 | No
| 1846782 | 28/10/2024 | 2:33 | 28/10/2024 | 3:27 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | HV | 100 | 5310 | 53.1 | 1 | No
| 1846782 | 28/10/2024 | 2:33 | 28/10/2024 | 3:43 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | HV | 54 | 3732.3018 | 69.1167 | 2 | No
| 1846782 | 28/10/2024 | 2:33 | 28/10/2024 | 3:48 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | HV | 107 | 8012.5131 | 74.8833 | 3 | No
| 1846876 | 28/10/2024 | 10:31 | 28/10/2024 | 12:00 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 1 | 88.0667 | 88.0667 | 1 | No
| 1846891 | 28/10/2024 | 11:22 | 28/10/2024 | 13:07 | RWT35 | RINGWOOD | Urban | Asset Failure | LV | 1 | 105.7167 | 105.7167 | 1 | No
| 1847009 | 28/10/2024 | 18:46 | 28/10/2024 | 22:10 | LD5 | LYNDALE | Urban | Third Party | Other | 5 | 1015.0835 | 203.0167 | 1 | No
| 1847043 | 29/10/2024 | 2:12 | 29/10/2024 | 3:40 | MR32 | MOORABBIN | Urban | Third Party | Vehicle Impact | 40 | 3518.668 | 87.9667 | 1 | No
| 1847049 | 29/10/2024 | 5:06 | 29/10/2024 | 7:40 | DC4 | DONCASTER | Urban | Asset Failure | LV | 26.73 | 4104.3915 | 153.55 | 1 | No
| 1847053 | 29/10/2024 | 7:21 | 29/10/2024 | 9:40 | SS13 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 139 | 139 | 1 | No
| 1847110 | 29/10/2024 | 9:03 | 29/10/2024 | 9:14 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 10.1 | 10.1 | 1 | No
| 1847129 | 29/10/2024 | 11:15 | 29/10/2024 | 14:07 | MR33 | MOORABBIN | Urban | Asset Failure | LV | 1 | 172.7 | 172.7 | 1 | No
| 1847217 | 29/10/2024 | 11:37 | 29/10/2024 | 14:00 | OE14 | OAKLEIGH EAST | Urban | Asset Failure | LV | 1 | 142.8 | 142.8 | 1 | No
| 1847312 | 29/10/2024 | 19:57 | 29/10/2024 | 23:28 | MR32 | MOORABBIN | Urban | Third Party | Other | 40 | 8447.332 | 211.1833 | 1 | No
| 1847316 | 29/10/2024 | 21:24 | 29/10/2024 | 22:45 | CFD24 | CAULFIELD | Urban | Asset Failure | LV | 4.95 | 400.95 | 81 | 1 | No
| 1847330 | 30/10/2024 | 0:25 | 30/10/2024 | 1:24 | OE14 | OAKLEIGH EAST | Urban | Third Party | Other | 10 | 589 | 58.9 | 1 | No
| 1847330 | 30/10/2024 | 0:25 | 30/10/2024 | 1:33 | OE14 | OAKLEIGH EAST | Urban | Third Party | Other | 36 | 2445.5988 | 67.9333 | 2 | No
| 1847330 | 30/10/2024 | 0:25 | 30/10/2024 | 4:16 | OE14 | OAKLEIGH EAST | Urban | Third Party | Other | 1 | 230.55 | 230.55 | 3 | No
| 1847359 | 30/10/2024 | 2:08 | 30/10/2024 | 20:08 | OE14 | OAKLEIGH EAST | Urban | Third Party | Other | 1 | 1079.5 | 1079.5 | 1 | No
| 1847366 | 30/10/2024 | 6:34 | 30/10/2024 | 9:15 | MR32 | MOORABBIN | Urban | Asset Failure | LV | 1 | 160.6667 | 160.6667 | 1 | No
| 1847371 | 30/10/2024 | 7:19 | 30/10/2024 | 10:16 | HT13 | HEATHERTON | Urban | Third Party | Other | 1 | 176.8 | 176.8 | 1 | No
| 1847376 | 30/10/2024 | 7:26 | 30/10/2024 | 8:35 | DC4 | DONCASTER | Urban | Animal | Animal impact | 73.03 | 4995.252 | 68.4 | 1 | No
| 1847482 | 30/10/2024 | 10:25 | 30/10/2024 | 11:32 | OR22 | ORMOND | Urban | Third Party | Other | 1 | 67.4167 | 67.4167 | 1 | No
| 1847583 | 30/10/2024 | 13:15 | 30/10/2024 | 16:05 | NP11 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 169.4 | 169.4 | 1 | No
| 1847613 | 30/10/2024 | 14:48 | 30/10/2024 | 16:45 | LD3 | LYNDALE | Urban | Asset Failure | LV | 23.76 | 2779.92 | 117 | 1 | No
| 1847617 | 30/10/2024 | 15:21 | 30/10/2024 | 16:51 | NW14 | NUNAWADING | Urban | Overloads |  | 1 | 89.7833 | 89.7833 | 1 | No
| 1847626 | 30/10/2024 | 16:46 | 30/10/2024 | 20:21 | LWN32 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 214.4667 | 214.4667 | 1 | No
| 1847655 | 30/10/2024 | 20:33 | 30/10/2024 | 21:56 | EW1 | ELWOOD | Urban | Third Party | Other | 16 | 1336 | 83.5 | 1 | No
| 1847657 | 30/10/2024 | 21:20 | 30/10/2024 | 22:27 | DMA23 | DROMANA | Rural Short | Animal | Other | 40.2 | 2690.0513 | 66.9167 | 1 | No
| 1847671 | 30/10/2024 | 23:03 | 31/10/2024 | 0:30 | HGS32 | HASTINGS | Urban | Animal | Animal impact | 53.6 | 4648.9049 | 86.7333 | 1 | No
| 1847675 | 31/10/2024 | 1:57 | 31/10/2024 | 2:12 | DMA21 | DROMANA | Urban | Asset Failure | Zone substation | 2251 | 33427.35 | 14.85 | 1 | No
| 1847675 | 31/10/2024 | 1:57 | 31/10/2024 | 2:49 | DMA21 | DROMANA | Urban | Asset Failure | Zone substation | 1041 | 53663.55 | 51.55 | 2 | No
| 1847675 | 31/10/2024 | 1:57 | 31/10/2024 | 2:16 | DMA23 | DROMANA | Rural Short | Asset Failure | Zone substation | 1725 | 31855.0575 | 18.4667 | 1 | No
| 1847675 | 31/10/2024 | 1:57 | 31/10/2024 | 2:53 | DMA23 | DROMANA | Rural Short | Asset Failure | Zone substation | 124 | 6956.4 | 56.1 | 2 | No
| 1847675 | 31/10/2024 | 1:57 | 31/10/2024 | 2:25 | DMA24 | DROMANA | Rural Short | Asset Failure | Zone substation | 1832 | 50532.6056 | 27.5833 | 1 | No
| 1847675 | 31/10/2024 | 1:57 | 31/10/2024 | 3:12 | DMA24 | DROMANA | Rural Short | Asset Failure | Zone substation | 16 | 1193.0672 | 74.5667 | 2 | No
| 1847675 | 31/10/2024 | 1:57 | 31/10/2024 | 3:14 | DMA24 | DROMANA | Rural Short | Asset Failure | Zone substation | 57 | 4340.55 | 76.15 | 3 | No
| 1847681 | 31/10/2024 | 5:44 | 31/10/2024 | 8:32 | MR13 | MOORABBIN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 167.8167 | 167.8167 | 1 | No
| 1847654 | 31/10/2024 | 7:29 | 31/10/2024 | 13:11 | MTN32 | MORNINGTON | Rural Short | Unknown | Unknown | 2 | 684.5 | 342.25 | 1 | No
| 1847732 | 31/10/2024 | 9:35 | 31/10/2024 | 10:20 | OAK33 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 44.7833 | 44.7833 | 1 | No
| 1847739 | 31/10/2024 | 10:08 | 31/10/2024 | 12:58 | DMA24 | DROMANA | Rural Short | Unknown | Unknown | 1 | 169.35 | 169.35 | 1 | No
| 1847798 | 31/10/2024 | 16:37 | 31/10/2024 | 17:30 | OR25 | ORMOND | Urban | Asset Failure | LV | 1 | 53 | 53 | 1 | No
| 1847837 | 31/10/2024 | 20:42 | 31/10/2024 | 22:45 | MR24 | MOORABBIN | Urban | Asset Failure | LV | 1 | 122.4167 | 122.4167 | 1 | No
| 1847844 | 31/10/2024 | 21:15 | 31/10/2024 | 23:35 | MTN24 | MORNINGTON | Rural Short | Asset Failure | LV | 2 | 280 | 140 | 1 | No
| 1847848 | 31/10/2024 | 23:52 | 2024-01-11 | 1:29 | LWN21 | LANGWARRIN | Rural Short | Animal | Animal impact | 15 | 1447.5 | 96.5 | 1 | No
| 1847845 | 2024-01-11 | 6:00 | 2024-01-11 | 8:09 | EW1 | ELWOOD | Urban | Asset Failure | LV | 1 | 129.0167 | 129.0167 | 1 | No
| 1847853 | 2024-01-11 | 7:06 | 2024-01-11 | 8:30 | BR9 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 84 | 84 | 1 | No
| 1847856 | 2024-01-11 | 8:35 | 2024-01-11 | 9:45 | OAK26 | OAKLEIGH | Urban | Asset Failure | LV | 4 | 280 | 70 | 1 | No
| 1847939 | 2024-01-11 | 9:26 | 2024-01-11 | 12:51 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 204.3833 | 204.3833 | 1 | No
| 1847942 | 2024-01-11 | 9:57 | 2024-01-11 | 10:34 | MGE34 | MULGRAVE | Urban | Third Party | Other | 1 | 37.9667 | 37.9667 | 1 | No
| 1847965 | 2024-01-11 | 10:27 | 2024-01-11 | 12:00 | DC2 | DONCASTER | Urban | Asset Failure | LV | 1 | 92.15 | 92.15 | 1 | No
| 1847855 | 2024-01-11 | 11:12 | 2024-01-11 | 12:41 | NP12 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 89.8667 | 89.8667 | 1 | No
| 1848034 | 2024-01-11 | 19:33 | 2024-01-11 | 20:54 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 9.24 | 748.7477 | 81.0333 | 1 | No
| 1848041 | 2024-01-11 | 20:13 | 2024-01-11 | 23:00 | NB34 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 166.95 | 166.95 | 1 | No
| 1848042 | 2024-01-11 | 20:31 | 2024-01-11 | 22:41 | HGS21 | HASTINGS | Rural Short | Unknown | Unknown | 0.67 | 86.9995 | 129.85 | 1 | No
| 1848050 | 2024-01-11 | 23:31 | 2024-02-11 | 0:28 | LWN35 | LANGWARRIN | Urban | Unknown | Unknown | 0.67 | 37.6205 | 56.15 | 1 | No
| 1848062 | 2024-02-11 | 6:21 | 2024-02-11 | 7:48 | HGS22 | HASTINGS | Rural Short | Animal | Animal impact | 2.68 | 231.9988 | 86.5667 | 1 | No
| 1848068 | 2024-02-11 | 8:59 | 2024-02-11 | 11:15 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 135.4 | 135.4 | 1 | No
| 1848083 | 2024-02-11 | 11:25 | 2024-02-11 | 12:58 | CFD12 | CAULFIELD | Urban | Asset Failure | LV | 1 | 92.8833 | 92.8833 | 1 | No
| 1848087 | 2024-02-11 | 11:56 | 2024-02-11 | 14:46 | NW32 | NUNAWADING | Urban | Asset Failure | LV | 1 | 169.4833 | 169.4833 | 1 | No
| 1848091 | 2024-02-11 | 13:35 | 2024-02-11 | 16:37 | FTN22 | FRANKSTON | Urban | Third Party | Other | 1 | 181.4833 | 181.4833 | 1 | No
| 1848110 | 2024-02-11 | 19:50 | 2024-02-11 | 21:45 | LD6 | LYNDALE | Urban | Overloads |  | 1 | 114.75 | 114.75 | 1 | No
| 1848113 | 2024-02-11 | 22:59 | 2024-03-11 | 0:15 | MTN32 | MORNINGTON | Rural Short | Animal | Animal impact | 5 | 375.9165 | 75.1833 | 1 | No
| 1848119 | 2024-03-11 | 5:34 | 2024-03-11 | 7:05 | BW35 | BURWOOD | Urban | Weather |  | 22.78 | 2056.6536 | 90.2833 | 1 | No
| 1848120 | 2024-03-11 | 7:17 | 2024-03-11 | 9:07 | HGS22 | HASTINGS | Rural Short | Unknown | Unknown | 1 | 110 | 110 | 1 | No
| 1848137 | 2024-03-11 | 9:48 | 2024-03-11 | 11:50 | K33 | GARDINER | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 41 | 4982.8653 | 121.5333 | 1 | No
| 1848141 | 2024-03-11 | 11:07 | 2024-03-11 | 13:06 | BR6 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 42 | 4977.7014 | 118.5167 | 1 | No
| 1848144 | 2024-03-11 | 12:18 | 2024-03-11 | 14:20 | BU21 | BULLEEN | Urban | Asset Failure | LV | 1 | 121.6167 | 121.6167 | 1 | No
| 1848168 | 2024-03-11 | 23:00 | 2024-04-11 | 0:06 | SS23 | SPRINGVALE SOUTH | Urban | Animal | Animal impact | 66.33 | 4439.6858 | 66.9333 | 1 | No
| 1848173 | 2024-04-11 | 4:55 | 2024-04-11 | 5:20 | BW33 | BURWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 446 | 11053.3518 | 24.7833 | 1 | No
| 1848173 | 2024-04-11 | 4:55 | 2024-04-11 | 6:05 | BW33 | BURWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 300 | 20889.99 | 69.6333 | 2 | No
| 1848183 | 2024-04-11 | 8:23 | 2024-04-11 | 10:05 | OAK23 | OAKLEIGH | Urban | Other | XXX | 1 | 102.7333 | 102.7333 | 1 | No
| 1848200 | 2024-04-11 | 9:26 | 2024-04-11 | 11:31 | DC8 | DONCASTER | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 124.45 | 124.45 | 1 | No
| 1848201 | 2024-04-11 | 9:27 | 2024-04-11 | 11:16 | SVW53 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 109.7 | 109.7 | 1 | No
| 1848202 | 2024-04-11 | 9:31 | 2024-04-11 | 11:23 | DN6 | DANDENONG | Urban | Overloads |  | 1 | 112.1333 | 112.1333 | 1 | No
| 1848220 | 2024-04-11 | 11:00 | 2024-04-11 | 11:51 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 51.2667 | 51.2667 | 1 | No
| 1848244 | 2024-04-11 | 13:31 | 2024-04-11 | 17:23 | SR36 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 231.95 | 231.95 | 1 | No
| 1848246 | 2024-04-11 | 13:38 | 2024-04-11 | 16:50 | CDA21 | CLARINDA | Urban | Asset Failure | LV | 1 | 191.5167 | 191.5167 | 1 | No
| 1848287 | 2024-05-11 | 10:59 | 2024-05-11 | 12:59 | DC2 | DONCASTER | Urban | Asset Failure | LV | 1 | 120.3 | 120.3 | 1 | No
| 1848297 | 2024-05-11 | 17:29 | 2024-05-11 | 18:44 | RBD11 | ROSEBUD | Urban | Asset Failure | LV | 1 | 74.6833 | 74.6833 | 1 | No
| 1848308 | 2024-05-11 | 20:02 | 2024-06-11 | 0:25 | NB33 | NORTH BRIGHTON | Urban | Third Party | Vehicle Impact | 19 | 4990.9827 | 262.6833 | 1 | No
| 1848395 | 2024-06-11 | 10:27 | 2024-06-11 | 12:39 | GW2 | GLEN WAVERLEY | Urban | Unknown | Unknown | 1 | 131.8167 | 131.8167 | 1 | No
| 1848417 | 2024-06-11 | 11:15 | 2024-06-11 | 12:18 | EL34 | ELSTERNWICK | Urban | Asset Failure | LV | 13.86 | 867.636 | 62.6 | 1 | No
| 1848430 | 2024-06-11 | 12:04 | 2024-06-11 | 14:35 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 1 | 150.0833 | 150.0833 | 1 | No
| 1848450 | 2024-06-11 | 12:44 | 2024-06-11 | 14:07 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 1 | 82.4667 | 82.4667 | 1 | No
| 1848479 | 2024-06-11 | 14:19 | 2024-06-11 | 19:58 | STO23 | SORRENTO | Urban | Network Business | Network Error | 1 | 338.6333 | 338.6333 | 1 | No
| 1848491 | 2024-06-11 | 15:03 | 2024-06-11 | 15:08 | LD2 | LYNDALE | Urban | Weather |  | 397 | 2044.55 | 5.15 | 1 | No
| 1848491 | 2024-06-11 | 15:03 | 2024-06-11 | 15:44 | LD2 | LYNDALE | Urban | Weather |  | 675 | 27405 | 40.6 | 2 | No
| 1848491 | 2024-06-11 | 15:03 | 2024-06-11 | 15:54 | LD2 | LYNDALE | Urban | Weather |  | 12 | 609.3996 | 50.7833 | 3 | No
| 1848491 | 2024-06-11 | 15:03 | 2024-06-11 | 19:16 | LD2 | LYNDALE | Urban | Weather |  | 1 | 253.4 | 253.4 | 4 | No
| 1848491 | 2024-06-11 | 15:03 | 2024-06-11 | 19:42 | LD2 | LYNDALE | Urban | Weather |  | 24 | 6684.7992 | 278.5333 | 5 | No
| 1848500 | 2024-06-11 | 15:48 | 2024-06-11 | 17:15 | MTN21 | MORNINGTON | Urban | Asset Failure | LV | 1 | 86.75 | 86.75 | 1 | No
| 1848507 | 2024-06-11 | 16:35 | 2024-06-11 | 18:55 | RBD11 | ROSEBUD | Urban | Third Party | Vehicle Impact | 36 | 5058 | 140.5 | 1 | No
| 1848512 | 2024-06-11 | 16:55 | 2024-06-11 | 18:34 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 30.69 | 3028.081 | 98.6667 | 1 | No
| 1848543 | 2024-06-11 | 22:22 | 2024-07-11 | 0:21 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 1.34 | 158.2764 | 118.1167 | 1 | No
| 1848576 | 2024-07-11 | 2:12 | 2024-07-11 | 5:30 | OAK35 | OAKLEIGH | Urban | Third Party | Other | 2 | 395.2666 | 197.6333 | 1 | No
| 1848585 | 2024-07-11 | 6:38 | 2024-07-11 | 8:36 | OAK35 | OAKLEIGH | Urban | Unknown | Unknown | 13 | 1539.85 | 118.45 | 1 | No
| 1848627 | 2024-07-11 | 8:28 | 2024-07-11 | 10:30 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 2 | 243.1334 | 121.5667 | 1 | No
| 1848688 | 2024-07-11 | 10:34 | 2024-07-11 | 11:25 | WD14 | WEST DONCASTER | Urban | Third Party | Other | 1 | 50.25 | 50.25 | 1 | No
| 1848702 | 2024-07-11 | 11:31 | 2024-07-11 | 13:22 | GW10 | GLEN WAVERLEY | Urban | Third Party | Other | 1 | 110.9333 | 110.9333 | 1 | No
| 1848708 | 2024-07-11 | 11:55 | 2024-07-11 | 14:31 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 155.45 | 155.45 | 1 | No
| 1848756 | 2024-07-11 | 16:57 | 2024-07-11 | 17:51 | BT13 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 54.8333 | 54.8333 | 1 | No
| 1848772 | 2024-07-11 | 19:30 | 2024-07-11 | 21:30 | CDA22 | CLARINDA | Urban | Asset Failure | LV | 1 | 119.3667 | 119.3667 | 1 | No
| 1848787 | 2024-07-11 | 22:26 | 2024-08-11 | 1:28 | SS14 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 181.5 | 181.5 | 1 | No
| 1848875 | 2024-08-11 | 9:39 | 2024-08-11 | 9:57 | LWN21 | LANGWARRIN | Rural Short | Other | XXX | 1 | 17.3667 | 17.3667 | 1 | No
| 1848906 | 2024-08-11 | 10:23 | 2024-08-11 | 11:25 | RWT34 | RINGWOOD | Urban | Asset Failure | Distribution substation | 73.7 | 4517.81 | 61.3 | 1 | No
| 1848913 | 2024-08-11 | 10:37 | 2024-08-11 | 12:45 | FSH11 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 127.3 | 127.3 | 1 | No
| 1848999 | 2024-08-11 | 14:06 | 2024-08-11 | 16:03 | WD36 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 117.5 | 117.5 | 1 | No
| 1849030 | 2024-08-11 | 16:31 | 2024-08-11 | 17:16 | NW13 | NUNAWADING | Urban | Unknown | Unknown | 1 | 44.7833 | 44.7833 | 1 | No
| 1849031 | 2024-08-11 | 17:04 | 2024-08-11 | 19:25 | WD36 | WEST DONCASTER | Urban | Asset Failure | LV | 17.49 | 2466.9645 | 141.05 | 1 | No
| 1849022 | 2024-08-11 | 17:36 | 2024-08-11 | 20:15 | SR22 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 159.4833 | 159.4833 | 1 | No
| 1849052 | 2024-09-11 | 5:46 | 2024-09-11 | 9:15 | DN11 | DANDENONG | Urban | Asset Failure | LV | 1 | 209 | 209 | 1 | No
| 1849096 | 2024-09-11 | 10:16 | 2024-09-11 | 12:55 | STO22 | SORRENTO | Urban | Asset Failure | LV | 1 | 159 | 159 | 1 | No
| 1849108 | 2024-09-11 | 11:09 | 2024-09-11 | 14:38 | RWT24 | RINGWOOD | Urban | Animal | Animal impact | 1 | 208.0167 | 208.0167 | 1 | No
| 1849162 | 2024-09-11 | 15:54 | 2024-09-11 | 17:30 | DN10 | DANDENONG | Urban | Asset Failure | LV | 1 | 95.4167 | 95.4167 | 1 | No
| 1849093 | 2024-09-11 | 18:03 | 2024-09-11 | 22:45 | NP25 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 282 | 282 | 1 | No
| 1849186 | 2024-10-11 | 3:44 | 2024-10-11 | 5:10 | HT1 | HEATHERTON | Urban | Animal | Animal impact | 18.09 | 1544.2836 | 85.3667 | 1 | No
| 1849189 | 2024-10-11 | 4:56 | 2024-10-11 | 7:05 | NW14 | NUNAWADING | Urban | Unknown | Unknown | 1.34 | 172.0114 | 128.3667 | 1 | No
| 1849182 | 2024-10-11 | 7:08 | 2024-10-11 | 8:55 | CRM23 | CARRUM | Urban | Asset Failure | LV | 2 | 214 | 107 | 1 | No
| 1849226 | 2024-10-11 | 10:22 | 2024-10-11 | 11:32 | EB32 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 70.05 | 70.05 | 1 | No
| 1849248 | 2024-10-11 | 14:49 | 2024-10-11 | 16:19 | NW22 | NUNAWADING | Urban | Asset Failure | LV | 1 | 89.65 | 89.65 | 1 | No
| 1849244 | 2024-10-11 | 15:27 | 2024-10-11 | 16:45 | CRM15 | CARRUM | Urban | Asset Failure | LV | 1 | 78 | 78 | 1 | No
| 1849265 | 2024-10-11 | 19:24 | 2024-10-11 | 21:37 | SR35 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 132.1 | 132.1 | 1 | No
| 1849266 | 2024-10-11 | 19:53 | 2024-10-11 | 21:35 | HGS31 | HASTINGS | Rural Short | Asset Failure | LV | 51.59 | 5244.9851 | 101.6667 | 1 | No
| 1849442 | 2024-11-11 | 12:15 | 2024-11-11 | 15:45 | EL34 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 209.9167 | 209.9167 | 1 | No
| 1849482 | 2024-11-11 | 13:41 | 2024-11-11 | 17:34 | MC32 | MORDIALLOC | Urban | Unknown | Unknown | 1 | 232.7667 | 232.7667 | 1 | No
| 1849519 | 2024-11-11 | 16:21 | 2024-11-11 | 19:30 | BU21 | BULLEEN | Urban | Asset Failure | LV | 52 | 9823.6684 | 188.9167 | 1 | No
| 1849528 | 2024-11-11 | 18:06 | 2024-11-11 | 21:20 | MR12 | MOORABBIN | Urban | Asset Failure | LV | 1 | 193.9 | 193.9 | 1 | No
| 1849526 | 2024-11-11 | 18:17 | 2024-11-11 | 19:57 | SVW56 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 100.7667 | 100.7667 | 1 | No
| 1849556 | 2024-11-11 | 21:56 | 2024-11-11 | 23:15 | NP34 | NOBLE PARK | Urban | Animal | Animal impact | 5.36 | 419.42 | 78.25 | 1 | No
| 1849565 | 2024-12-11 | 2:56 | 2024-12-11 | 4:02 | NW22 | NUNAWADING | Urban | Animal | Animal impact | 123.95 | 8075.3425 | 65.15 | 1 | No
| 1849713 | 2024-12-11 | 12:06 | 2024-12-11 | 13:48 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 17.49 | 1776.4016 | 101.5667 | 1 | No
| 1849799 | 2024-12-11 | 16:34 | 2024-12-11 | 18:18 | MC15 | MORDIALLOC | Urban | Unknown | Unknown | 1 | 103.9167 | 103.9167 | 1 | No
| 1849810 | 2024-12-11 | 17:46 | 2024-12-11 | 18:52 | RBD21 | ROSEBUD | Rural Short | Unknown | Unknown | 6 | 395.5002 | 65.9167 | 1 | No
| 1849809 | 2024-12-11 | 18:09 | 2024-12-11 | 18:53 | FSH13 | FRANKSTON SOUTH | Urban | Overloads |  | 1 | 44.9167 | 44.9167 | 1 | No
| 1849816 | 2024-12-11 | 18:14 | 2024-12-11 | 21:45 | BT14 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 210.1167 | 210.1167 | 1 | No
| 1849817 | 2024-12-11 | 18:18 | 2024-12-11 | 19:30 | FTN12 | FRANKSTON | Urban | Animal | Animal impact | 33 | 2373.2511 | 71.9167 | 1 | No
| 1849839 | 13/11/2024 | 0:30 | 13/11/2024 | 1:56 | K32 | GARDINER | Urban | Animal | Animal impact | 68 | 5782.2644 | 85.0333 | 1 | No
| 1849839 | 13/11/2024 | 0:30 | 13/11/2024 | 1:56 | K32 | GARDINER | Urban | Animal | Animal impact | 81 | 6967.3527 | 86.0167 | 2 | No
| 1849842 | 13/11/2024 | 1:29 | 13/11/2024 | 2:33 | M25 | MENTONE | Urban | Animal | Animal impact | 60.97 | 3852.2858 | 63.1833 | 1 | No
| 1849849 | 13/11/2024 | 1:36 | 13/11/2024 | 2:23 | MR33 | MOORABBIN | Urban | Unknown | Unknown | 521 | 24374.0993 | 46.7833 | 1 | No
| 1849849 | 13/11/2024 | 1:36 | 13/11/2024 | 2:38 | MR33 | MOORABBIN | Urban | Unknown | Unknown | 450 | 27644.985 | 61.4333 | 2 | No
| 1849849 | 13/11/2024 | 1:36 | 13/11/2024 | 2:44 | MR33 | MOORABBIN | Urban | Unknown | Unknown | 146 | 9986.4 | 68.4 | 3 | No
| 1849849 | 13/11/2024 | 1:36 | 13/11/2024 | 2:52 | MR33 | MOORABBIN | Urban | Unknown | Unknown | 51 | 3887.0517 | 76.2167 | 4 | No
| 1849849 | 13/11/2024 | 1:36 | 13/11/2024 | 3:02 | MR33 | MOORABBIN | Urban | Unknown | Unknown | 161 | 13835.2613 | 85.9333 | 5 | No
| 1849874 | 13/11/2024 | 5:27 | 13/11/2024 | 5:50 | OAK35 | OAKLEIGH | Urban | Third Party | Other | 13 | 299 | 23 | 1 | No
| 1849917 | 13/11/2024 | 7:55 | 13/11/2024 | 8:41 | EB23 | EAST BURWOOD | Urban | Animal | Animal impact | 477 | 21616.0659 | 45.3167 | 1 | No
| 1849918 | 13/11/2024 | 8:25 | 13/11/2024 | 11:30 | M12 | MENTONE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 185 | 185 | 1 | No
| 1850066 | 13/11/2024 | 11:15 | 13/11/2024 | 12:59 | DN11 | DANDENONG | Urban | Third Party | Other | 1 | 103.5667 | 103.5667 | 1 | No
| 1850081 | 13/11/2024 | 11:39 | 13/11/2024 | 14:14 | NB35 | NORTH BRIGHTON | Urban | Asset Failure | LV | 3 | 465.3501 | 155.1167 | 1 | No
| 1850097 | 13/11/2024 | 12:16 | 13/11/2024 | 12:46 | SV32 | SPRINGVALE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1148 | 35396.6284 | 30.8333 | 1 | No
| 1850103 | 13/11/2024 | 12:29 | 13/11/2024 | 14:14 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 1 | 105.3333 | 105.3333 | 1 | No
| 1849807 | 13/11/2024 | 13:05 | 13/11/2024 | 14:43 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 98.3833 | 98.3833 | 1 | No
| 1850124 | 13/11/2024 | 13:21 | 13/11/2024 | 16:50 | LD7 | LYNDALE | Urban | Third Party | Other | 1 | 209.7667 | 209.7667 | 1 | No
| 1850139 | 13/11/2024 | 14:18 | 13/11/2024 | 16:49 | CRM13 | CARRUM | Urban | Unknown | Unknown | 27 | 4068.4491 | 150.6833 | 1 | No
| 1850144 | 13/11/2024 | 14:37 | 13/11/2024 | 16:30 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 113.4333 | 113.4333 | 1 | No
| 1850152 | 13/11/2024 | 15:00 | 13/11/2024 | 17:15 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 1 | 134.9333 | 134.9333 | 1 | No
| 1850176 | 13/11/2024 | 17:02 | 13/11/2024 | 18:40 | EB31 | EAST BURWOOD | Urban | Unknown | Unknown | 1 | 98.0833 | 98.0833 | 1 | No
| 1850185 | 13/11/2024 | 18:02 | 13/11/2024 | 20:55 | CRM24 | CARRUM | Urban | Third Party | Vehicle Impact | 15 | 2595.75 | 173.05 | 1 | No
| 1850194 | 13/11/2024 | 19:06 | 13/11/2024 | 21:15 | DN11 | DANDENONG | Urban | Asset Failure | LV | 1 | 128.1167 | 128.1167 | 1 | No
| 1850248 | 14/11/2024 | 8:04 | 14/11/2024 | 10:34 | MC14 | MORDIALLOC | Urban | Asset Failure | LV | 3.4 | 511.5868 | 150.4667 | 1 | No
| 1850305 | 14/11/2024 | 9:29 | 14/11/2024 | 10:51 | EM2 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 82 | 82 | 1 | No
| 1850324 | 14/11/2024 | 9:33 | 14/11/2024 | 12:00 | EW12 | ELWOOD | Urban | Overloads |  | 1 | 146.6667 | 146.6667 | 1 | No
| 1850426 | 14/11/2024 | 13:16 | 14/11/2024 | 15:07 | DN13 | DANDENONG | Urban | Asset Failure | LV | 14.85 | 1646.3705 | 110.8667 | 1 | No
| 1850468 | 14/11/2024 | 15:42 | 14/11/2024 | 19:01 | OAK21 | OAKLEIGH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 198.5167 | 198.5167 | 1 | No
| 1850503 | 14/11/2024 | 17:05 | 14/11/2024 | 21:36 | MTN32 | MORNINGTON | Rural Short | Unknown | Unknown | 1 | 270.85 | 270.85 | 1 | No
| 1850506 | 14/11/2024 | 17:40 | 14/11/2024 | 18:28 | MGE21 | MULGRAVE | Urban | Asset Failure | LV | 2.5 | 120.625 | 48.25 | 1 | No
| 1850515 | 14/11/2024 | 18:58 | 14/11/2024 | 21:00 | NB22 | NORTH BRIGHTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 122.3667 | 122.3667 | 1 | No
| 1850520 | 14/11/2024 | 19:48 | 14/11/2024 | 21:53 | LWN33 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 124.6333 | 124.6333 | 1 | No
| 1850533 | 14/11/2024 | 22:32 | 15/11/2024 | 0:29 | SVW55 | SPRINGVALE WEST | Urban | Unknown | Unknown | 1 | 117.2333 | 117.2333 | 1 | No
| 1850675 | 15/11/2024 | 10:29 | 15/11/2024 | 12:12 | BR9 | BEAUMARIS | Urban | Asset Failure | LV | 9.9 | 1013.9253 | 102.4167 | 1 | No
| 1850706 | 15/11/2024 | 11:50 | 15/11/2024 | 14:20 | MTN35 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 149.3833 | 149.3833 | 1 | No
| 1850787 | 15/11/2024 | 17:44 | 15/11/2024 | 19:31 | SS22 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 21.45 | 2284.7832 | 106.5167 | 1 | No
| 1850785 | 15/11/2024 | 17:56 | 16/11/2024 | 2:21 | BC12 | BALACLAVA | Urban | Asset Failure | LV | 13 | 6577.7829 | 505.9833 | 1 | No
| 1850788 | 15/11/2024 | 18:14 | 15/11/2024 | 20:20 | GW3 | GLEN WAVERLEY | Urban | Third Party | Vehicle Impact | 38 | 4791.1654 | 126.0833 | 1 | No
| 1850788 | 15/11/2024 | 18:14 | 16/11/2024 | 0:02 | GW3 | GLEN WAVERLEY | Urban | Third Party | Vehicle Impact | 150 | 52122.495 | 347.4833 | 2 | No
| 1850789 | 15/11/2024 | 18:33 | 15/11/2024 | 20:42 | GW8 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 129.8667 | 129.8667 | 1 | No
| 1850760 | 15/11/2024 | 19:58 | 15/11/2024 | 23:25 | OE10 | OAKLEIGH EAST | Urban | Asset Failure | LV | 1 | 207.9667 | 207.9667 | 1 | No
| 1850803 | 15/11/2024 | 20:32 | 15/11/2024 | 22:38 | MTN22 | MORNINGTON | Rural Short | Third Party | Other | 23 | 2876.9159 | 125.0833 | 1 | No
| 1850808 | 15/11/2024 | 20:33 | 15/11/2024 | 22:38 | MTN22 | MORNINGTON | Rural Short | Third Party | Other | 25 | 3115.8325 | 124.6333 | 1 | No
| 1850811 | 15/11/2024 | 21:17 | 15/11/2024 | 22:33 | OAK35 | OAKLEIGH | Urban | Animal | Animal impact | 2.68 | 202.0272 | 75.3833 | 1 | No
| 1850812 | 15/11/2024 | 21:34 | 16/11/2024 | 1:28 | CFD13 | CAULFIELD | Urban | Asset Failure | LV | 1 | 233.5167 | 233.5167 | 1 | No
| 1850820 | 16/11/2024 | 1:06 | 16/11/2024 | 9:10 | HGS31 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 483.3167 | 483.3167 | 1 | No
| 1850822 | 16/11/2024 | 5:16 | 16/11/2024 | 7:03 | MC15 | MORDIALLOC | Urban | Animal | Animal impact | 67 | 7175.7 | 107.1 | 1 | No
| 1850879 | 16/11/2024 | 12:21 | 16/11/2024 | 15:20 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 178.3 | 178.3 | 1 | No
| 1850883 | 16/11/2024 | 13:27 | 16/11/2024 | 15:28 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 120.85 | 120.85 | 1 | No
| 1850890 | 16/11/2024 | 16:00 | 16/11/2024 | 18:55 | FSH32 | FRANKSTON SOUTH | Rural Short | Third Party | Vehicle Impact | 2 | 349 | 174.5 | 1 | No
| 1850893 | 16/11/2024 | 16:46 | 16/11/2024 | 18:47 | MGE22 | MULGRAVE | Urban | Asset Failure | LV | 1 | 120.25 | 120.25 | 1 | No
| 1850894 | 16/11/2024 | 17:03 | 16/11/2024 | 20:13 | NO7 | NOTTING HILL | Urban | Asset Failure | LV | 1 | 190.05 | 190.05 | 1 | No
| 1850939 | 16/11/2024 | 17:34 | 16/11/2024 | 18:05 | EL25 | ELSTERNWICK | Urban | Third Party | Other | 86 | 2664.5638 | 30.9833 | 1 | No
| 1850939 | 16/11/2024 | 17:34 | 16/11/2024 | 18:24 | EL25 | ELSTERNWICK | Urban | Third Party | Other | 97 | 4882.3301 | 50.3333 | 2 | No
| 1850939 | 16/11/2024 | 17:34 | 16/11/2024 | 18:38 | EL25 | ELSTERNWICK | Urban | Third Party | Other | 43 | 2741.9681 | 63.7667 | 3 | No
| 1850950 | 16/11/2024 | 18:39 | 16/11/2024 | 22:30 | SS11 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 13.2 | 3044.1404 | 230.6167 | 1 | No
| 1850968 | 16/11/2024 | 21:31 | 16/11/2024 | 22:49 | FTN21 | FRANKSTON | Urban | Animal | Animal impact | 98.49 | 7646.1037 | 77.6333 | 1 | No
| 1851011 | 17/11/2024 | 10:15 | 17/11/2024 | 11:20 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 1 | 64.1667 | 64.1667 | 1 | No
| 1851021 | 17/11/2024 | 11:23 | 17/11/2024 | 12:18 | SS11 | SPRINGVALE SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 16.83 | 917.7954 | 54.5333 | 1 | No
| 1851023 | 17/11/2024 | 11:24 | 17/11/2024 | 13:18 | NB24 | NORTH BRIGHTON | Urban | Weather |  | 38.19 | 4340.9313 | 113.6667 | 1 | No
| 1851025 | 17/11/2024 | 11:28 | 17/11/2024 | 12:33 | SR22 | SANDRINGHAM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 64.8833 | 64.8833 | 1 | No
| 1851026 | 17/11/2024 | 11:32 | 17/11/2024 | 12:40 | EM7 | EAST MALVERN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 67.95 | 67.95 | 1 | No
| 1851028 | 17/11/2024 | 11:45 | 17/11/2024 | 14:31 | BW35 | BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 165.8833 | 165.8833 | 1 | No
| 1851003 | 17/11/2024 | 11:59 | 17/11/2024 | 15:35 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 216 | 216 | 1 | No
| 1851036 | 17/11/2024 | 12:25 | 17/11/2024 | 14:15 | CRM13 | CARRUM | Urban | Asset Failure | LV | 1 | 109.3 | 109.3 | 1 | No
| 1851037 | 17/11/2024 | 12:29 | 17/11/2024 | 12:56 | DMA23 | DROMANA | Rural Short | Weather |  | 95 | 2620.4135 | 27.5833 | 1 | No
| 1851037 | 17/11/2024 | 12:29 | 17/11/2024 | 14:13 | DMA23 | DROMANA | Rural Short | Weather |  | 43 | 4493.5 | 104.5 | 2 | No
| 1851037 | 17/11/2024 | 12:29 | 17/11/2024 | 14:35 | DMA23 | DROMANA | Rural Short | Weather |  | 63 | 7987.3479 | 126.7833 | 3 | No
| 1851040 | 17/11/2024 | 12:33 | 17/11/2024 | 13:11 | NP36 | NOBLE PARK | Urban | Vegetation | Grow-in - NSP responsibility | 41 | 1568.9347 | 38.2667 | 1 | No
| 1851040 | 17/11/2024 | 12:33 | 17/11/2024 | 13:35 | NP36 | NOBLE PARK | Urban | Vegetation | Grow-in - NSP responsibility | 808 | 50378.8 | 62.35 | 2 | No
| 1851045 | 17/11/2024 | 12:46 | 17/11/2024 | 14:50 | K34 | GARDINER | Urban | Asset Failure | LV | 2 | 246.9 | 123.45 | 1 | No
| 1851051 | 17/11/2024 | 13:06 | 17/11/2024 | 13:13 | LD32 | LYNDALE | Urban | Vegetation | Grow-in - NSP responsibility | 1655 | 12605.6385 | 7.6167 | 1 | No
| 1851054 | 17/11/2024 | 13:07 | 17/11/2024 | 16:15 | NW13 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 5 | 937.25 | 187.45 | 1 | No
| 1851063 | 17/11/2024 | 13:54 | 17/11/2024 | 17:15 | GW7 | GLEN WAVERLEY | Urban | Asset Failure | HV | 23.1 | 4633.4742 | 200.5833 | 1 | No
| 1851064 | 17/11/2024 | 13:56 | 17/11/2024 | 16:10 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 133.3333 | 133.3333 | 1 | No
| 1851074 | 17/11/2024 | 16:01 | 17/11/2024 | 17:50 | DVY12 | DANDENONG VALLEY | Urban | Asset Failure | LV | 1 | 109 | 109 | 1 | No
| 1851083 | 17/11/2024 | 17:25 | 17/11/2024 | 23:44 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 2 | 758.3666 | 379.1833 | 1 | No
| 1851087 | 17/11/2024 | 18:39 | 17/11/2024 | 20:27 | EL23 | ELSTERNWICK | Urban | Asset Failure | LV | 15.84 | 1704.9115 | 107.6333 | 1 | No
| 1851113 | 18/11/2024 | 0:08 | 18/11/2024 | 1:12 | LWN21 | LANGWARRIN | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 13.4 | 855.1438 | 63.8167 | 1 | No
| 1851115 | 18/11/2024 | 0:27 | 18/11/2024 | 1:27 | MGE23 | MULGRAVE | Urban | Animal | Animal impact | 66 | 3952.2978 | 59.8833 | 1 | No
| 1851127 | 18/11/2024 | 3:17 | 18/11/2024 | 8:27 | MGE14 | MULGRAVE | Urban | Animal | Animal impact | 31.49 | 9757.7024 | 309.8667 | 1 | No
| 1851131 | 18/11/2024 | 4:10 | 18/11/2024 | 16:59 | OE13 | OAKLEIGH EAST | Urban | Third Party | Other | 48 | 36901.5984 | 768.7833 | 1 | No
| 1851131 | 18/11/2024 | 4:10 | 18/11/2024 | 17:23 | OE13 | OAKLEIGH EAST | Urban | Third Party | Other | 1 | 793.0833 | 793.0833 | 2 | No
| 1851131 | 18/11/2024 | 4:10 | 18/11/2024 | 17:28 | OE13 | OAKLEIGH EAST | Urban | Third Party | Other | 81 | 64671.7527 | 798.4167 | 3 | No
| 1851131 | 18/11/2024 | 4:10 | 18/11/2024 | 18:38 | OE13 | OAKLEIGH EAST | Urban | Third Party | Other | 19 | 16487.25 | 867.75 | 4 | No
| 1851131 | 18/11/2024 | 4:10 | 18/11/2024 | 18:38 | OE13 | OAKLEIGH EAST | Urban | Third Party | Other | 47 | 40798.35 | 868.05 | 5 | No
| 1851131 | 18/11/2024 | 4:10 | 18/11/2024 | 22:37 | OE13 | OAKLEIGH EAST | Urban | Third Party | Other | 87 | 96269.85 | 1106.55 | 6 | No
| 1851244 | 18/11/2024 | 4:41 | 18/11/2024 | 8:01 | DC2 | DONCASTER | Urban | Third Party | Other | 17.49 | 3491.004 | 199.6 | 1 | No
| 1851305 | 18/11/2024 | 6:47 | 18/11/2024 | 10:38 | MC15 | MORDIALLOC | Urban | Vegetation | Grow-in - Other responsible party | 1 | 230.3833 | 230.3833 | 1 | No
| 1851322 | 18/11/2024 | 7:59 | 18/11/2024 | 11:34 | MC34 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 215.25 | 215.25 | 1 | No
| 1851412 | 18/11/2024 | 10:36 | 18/11/2024 | 11:38 | DC10 | DONCASTER | Urban | Third Party | Other | 1 | 62 | 62 | 1 | No
| 1851364 | 18/11/2024 | 10:46 | 18/11/2024 | 17:15 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 389 | 389 | 1 | No
| 1851296 | 18/11/2024 | 12:24 | 18/11/2024 | 15:05 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 161 | 161 | 1 | No
| 1851542 | 18/11/2024 | 14:36 | 18/11/2024 | 17:30 | MTN35 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 173.7167 | 173.7167 | 1 | No
| 1851389 | 18/11/2024 | 15:06 | 18/11/2024 | 16:07 | MGE31 | MULGRAVE | Urban | Asset Failure | LV | 1 | 61 | 61 | 1 | No
| 1851559 | 18/11/2024 | 15:55 | 18/11/2024 | 18:33 | STO13 | SORRENTO | Urban | Asset Failure | LV | 13.2 | 2072.8396 | 157.0333 | 1 | No
| 1851598 | 18/11/2024 | 18:57 | 18/11/2024 | 21:25 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 147.85 | 147.85 | 1 | No
| 1851622 | 18/11/2024 | 22:37 | 19/11/2024 | 9:18 | OE13 | OAKLEIGH EAST | Urban | Third Party | Other | 1 | 640.05 | 640.05 | 1 | No
| 1851627 | 19/11/2024 | 1:00 | 19/11/2024 | 2:45 | CRM13 | CARRUM | Urban | Asset Failure | LV | 47.52 | 4964.2576 | 104.4667 | 1 | No
| 1851630 | 19/11/2024 | 2:01 | 19/11/2024 | 3:50 | HGS32 | HASTINGS | Urban | Animal | Animal impact | 57 | 6171.2019 | 108.2667 | 1 | No
| 1851634 | 19/11/2024 | 4:37 | 19/11/2024 | 7:55 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 16.75 | 3315.3828 | 197.9333 | 1 | No
| 1851717 | 19/11/2024 | 11:39 | 19/11/2024 | 13:57 | FTN12 | FRANKSTON | Urban | Animal | Animal impact | 30.15 | 4160.1965 | 137.9833 | 1 | No
| 1851752 | 19/11/2024 | 14:06 | 19/11/2024 | 17:43 | BH23 | BOX HILL | Urban | Unknown | Unknown | 1 | 217.0167 | 217.0167 | 1 | No
| 1851795 | 19/11/2024 | 19:14 | 19/11/2024 | 20:40 | BR9 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 85.9 | 85.9 | 1 | No
| 1851810 | 20/11/2024 | 3:22 | 20/11/2024 | 4:16 | BU21 | BULLEEN | Urban | Animal | Animal impact | 1184.56 | 64341.3902 | 54.3167 | 1 | No
| 1851969 | 20/11/2024 | 9:30 | 20/11/2024 | 13:36 | HT1 | HEATHERTON | Urban | Asset Failure | LV | 1 | 245.7 | 245.7 | 1 | No
| 1851479 | 20/11/2024 | 11:53 | 20/11/2024 | 14:35 | DC10 | DONCASTER | Urban | Asset Failure | LV | 2.5 | 405.1667 | 162.0667 | 1 | No
| 1851985 | 20/11/2024 | 14:23 | 20/11/2024 | 18:03 | GW2 | GLEN WAVERLEY | Urban | Third Party | Other | 1 | 219.7333 | 219.7333 | 1 | No
| 1852007 | 20/11/2024 | 15:36 | 20/11/2024 | 18:07 | GW2 | GLEN WAVERLEY | Urban | Third Party | Vehicle Impact | 1 | 151.3167 | 151.3167 | 1 | No
| 1852070 | 20/11/2024 | 23:47 | 21/11/2024 | 7:36 | GW8 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 469.0167 | 469.0167 | 1 | No
| 1852077 | 21/11/2024 | 1:37 | 21/11/2024 | 3:07 | RBD24 | ROSEBUD | Urban | Animal | Other | 91 | 8179.3803 | 89.8833 | 1 | No
| 1852183 | 21/11/2024 | 12:05 | 21/11/2024 | 13:40 | NB36 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 95.2833 | 95.2833 | 1 | No
| 1852211 | 21/11/2024 | 13:43 | 21/11/2024 | 14:31 | EM1 | EAST MALVERN | Urban | Asset Failure | HV | 625 | 30187.5 | 48.3 | 1 | No
| 1852211 | 21/11/2024 | 13:43 | 21/11/2024 | 14:33 | EM11 | EAST MALVERN | Urban | Asset Failure | HV | 1034 | 51165.7322 | 49.4833 | 1 | No
| 1852211 | 21/11/2024 | 13:43 | 21/11/2024 | 14:33 | EM2 | EAST MALVERN | Urban | Asset Failure | HV | 609 | 30135.3297 | 49.4833 | 1 | No
| 1852211 | 21/11/2024 | 13:43 | 21/11/2024 | 14:40 | EM3 | EAST MALVERN | Urban | Asset Failure | HV | 1278 | 72888.5574 | 57.0333 | 1 | No
| 1852211 | 21/11/2024 | 13:43 | 21/11/2024 | 13:50 | EM5 | EAST MALVERN | Urban | Asset Failure | HV | 1593 | 11097.9531 | 6.9667 | 1 | No
| 1852211 | 21/11/2024 | 13:43 | 21/11/2024 | 14:24 | EM5 | EAST MALVERN | Urban | Asset Failure | HV | 469 | 19330.6323 | 41.2167 | 2 | No
| 1852211 | 21/11/2024 | 13:43 | 21/11/2024 | 13:48 | EM6 | EAST MALVERN | Urban | Asset Failure | HV | 848 | 4508.5616 | 5.3167 | 1 | No
| 1852211 | 21/11/2024 | 13:43 | 21/11/2024 | 14:41 | EM6 | EAST MALVERN | Urban | Asset Failure | HV | 715 | 41219.75 | 57.65 | 2 | No
| 1852211 | 21/11/2024 | 13:43 | 21/11/2024 | 15:35 | EM6 | EAST MALVERN | Urban | Asset Failure | HV | 54 | 6032.7018 | 111.7167 | 3 | No
| 1852221 | 21/11/2024 | 13:43 | 21/11/2024 | 23:53 | EM6 | EAST MALVERN | Urban | Third Party | Vehicle Impact | 26 | 15864.7658 | 610.1833 | 1 | No
| 1852221 | 21/11/2024 | 13:47 | 21/11/2024 | 23:53 | EM6 | EAST MALVERN | Urban | Third Party | Vehicle Impact | 33 | 19995.7989 | 605.9333 | 1 | No
| 1852054 | 21/11/2024 | 18:58 | 21/11/2024 | 23:52 | EL34 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 294.4667 | 294.4667 | 1 | No
| 1852268 | 21/11/2024 | 21:20 | 22/11/2024 | 1:19 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 238.6833 | 238.6833 | 1 | No
| 1852347 | 22/11/2024 | 6:27 | 22/11/2024 | 14:02 | NW14 | NUNAWADING | Urban | Third Party | Vehicle Impact | 8 | 3636.4 | 454.55 | 1 | No
| 1852317 | 22/11/2024 | 8:21 | 22/11/2024 | 11:14 | FSH32 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 2 | 345.2 | 172.6 | 1 | No
| 1852368 | 22/11/2024 | 11:09 | 22/11/2024 | 11:50 | K21 | GARDINER | Urban | Asset Failure | LV | 1 | 41.35 | 41.35 | 1 | No
| 1852394 | 22/11/2024 | 12:45 | 22/11/2024 | 14:09 | SVW53 | SPRINGVALE WEST | Urban | Third Party | Vehicle Impact | 72 | 6050.3976 | 84.0333 | 1 | No
| 1852411 | 22/11/2024 | 14:06 | 22/11/2024 | 15:45 | MR24 | MOORABBIN | Urban | Asset Failure | LV | 1 | 98.4667 | 98.4667 | 1 | No
| 1852434 | 22/11/2024 | 15:44 | 22/11/2024 | 23:35 | DVY21 | DANDENONG VALLEY | Urban | Overloads |  | 3 | 1410.3999 | 470.1333 | 1 | No
| 1852438 | 22/11/2024 | 15:54 | 22/11/2024 | 22:10 | MC32 | MORDIALLOC | Urban | Overloads |  | 1 | 375.6167 | 375.6167 | 1 | No
| 1852437 | 22/11/2024 | 15:56 | 22/11/2024 | 16:59 | NW13 | NUNAWADING | Urban | Overloads |  | 1 | 62.9667 | 62.9667 | 1 | No
| 1852439 | 22/11/2024 | 16:05 | 22/11/2024 | 16:59 | NW13 | NUNAWADING | Urban | Overloads |  | 9 | 486 | 54 | 1 | No
| 1852441 | 22/11/2024 | 16:06 | 22/11/2024 | 16:59 | NW13 | NUNAWADING | Urban | Overloads |  | 1 | 52.45 | 52.45 | 1 | No
| 1852445 | 22/11/2024 | 16:13 | 22/11/2024 | 16:59 | NW13 | NUNAWADING | Urban | Overloads |  | 1 | 45.7833 | 45.7833 | 1 | No
| 1852448 | 22/11/2024 | 16:24 | 22/11/2024 | 18:01 | BU24 | BULLEEN | Urban | Asset Failure | LV | 7.92 | 762.696 | 96.3 | 1 | No
| 1852450 | 22/11/2024 | 16:28 | 22/11/2024 | 16:59 | NW13 | NUNAWADING | Urban | Overloads |  | 1 | 30.7333 | 30.7333 | 1 | No
| 1852454 | 22/11/2024 | 16:33 | 22/11/2024 | 23:26 | HT7 | HEATHERTON | Urban | Overloads |  | 1 | 412.9833 | 412.9833 | 1 | No
| 1852456 | 22/11/2024 | 17:11 | 22/11/2024 | 18:56 | MTN31 | MORNINGTON | Urban | Overloads |  | 1 | 105.7667 | 105.7667 | 1 | No
| 1852458 | 22/11/2024 | 17:26 | 22/11/2024 | 19:52 | CFD12 | CAULFIELD | Urban | Overloads |  | 166 | 24236 | 146 | 1 | No
| 1852466 | 22/11/2024 | 17:55 | 22/11/2024 | 20:25 | NP36 | NOBLE PARK | Urban | Overloads |  | 26.73 | 3994.3521 | 149.4333 | 1 | No
| 1852467 | 22/11/2024 | 18:05 | 22/11/2024 | 19:16 | DC1 | DONCASTER | Urban | Overloads |  | 11 | 784.6663 | 71.3333 | 1 | No
| 1852474 | 22/11/2024 | 18:44 | 22/11/2024 | 20:45 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 82 | 9909.7 | 120.85 | 1 | No
| 1852492 | 22/11/2024 | 21:14 | 23/11/2024 | 1:45 | NP34 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 271 | 271 | 1 | No
| 1852481 | 22/11/2024 | 21:59 | 23/11/2024 | 0:00 | BU25 | BULLEEN | Urban | Animal | Animal impact | 49 | 5916.75 | 120.75 | 1 | No
| 1852488 | 23/11/2024 | 0:10 | 23/11/2024 | 0:34 | NW23 | NUNAWADING | Urban | Overloads |  | 1 | 24.6833 | 24.6833 | 1 | No
| 1852519 | 23/11/2024 | 1:14 | 23/11/2024 | 2:17 | DC10 | DONCASTER | Urban | Asset Failure | LV | 60 | 3805.998 | 63.4333 | 1 | No
| 1852497 | 23/11/2024 | 1:32 | 23/11/2024 | 3:06 | EB22 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 94.45 | 94.45 | 1 | No
| 1852526 | 23/11/2024 | 3:02 | 23/11/2024 | 9:21 | GW11 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 378.1667 | 378.1667 | 1 | No
| 1852527 | 23/11/2024 | 3:22 | 23/11/2024 | 8:45 | FSH23 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 322.35 | 322.35 | 1 | No
| 1852565 | 23/11/2024 | 9:27 | 23/11/2024 | 11:10 | EB24 | EAST BURWOOD | Urban | Unknown | Unknown | 73.03 | 7473.4009 | 102.3333 | 1 | No
| 1852531 | 23/11/2024 | 9:38 | 23/11/2024 | 11:35 | LD7 | LYNDALE | Urban | Asset Failure | LV | 1 | 117.4 | 117.4 | 1 | No
| 1852545 | 23/11/2024 | 9:58 | 23/11/2024 | 10:58 | DMA21 | DROMANA | Urban | Asset Failure | LV | 1 | 60.7333 | 60.7333 | 1 | No
| 1852589 | 23/11/2024 | 11:28 | 23/11/2024 | 12:34 | CFD12 | CAULFIELD | Urban | Overloads |  | 8.91 | 582.2685 | 65.35 | 1 | No
| 1852593 | 23/11/2024 | 11:45 | 23/11/2024 | 17:20 | CM25 | CHELTENHAM | Urban | Asset Failure | LV | 1 | 334.3167 | 334.3167 | 1 | No
| 1852595 | 23/11/2024 | 11:50 | 23/11/2024 | 13:05 | MTN32 | MORNINGTON | Rural Short | Animal | Animal impact | 1 | 74.3 | 74.3 | 1 | No
| 1852616 | 23/11/2024 | 13:15 | 23/11/2024 | 14:24 | NW13 | NUNAWADING | Urban | Overloads |  | 7.92 | 545.8203 | 68.9167 | 1 | No
| 1852622 | 23/11/2024 | 13:53 | 23/11/2024 | 15:09 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 76 | 76 | 1 | No
| 1852639 | 23/11/2024 | 15:02 | 23/11/2024 | 16:23 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 1 | 80.8833 | 80.8833 | 1 | No
| 1852641 | 23/11/2024 | 15:20 | 23/11/2024 | 16:38 | CFD16 | CAULFIELD | Urban | Overloads |  | 26.73 | 2080.9305 | 77.85 | 1 | No
| 1852643 | 23/11/2024 | 15:55 | 23/11/2024 | 18:00 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | HV | 119 | 14936.4873 | 125.5167 | 1 | No
| 1852643 | 23/11/2024 | 15:55 | 23/11/2024 | 21:17 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | HV | 32 | 10301.8656 | 321.9333 | 2 | No
| 1852651 | 23/11/2024 | 16:11 | 23/11/2024 | 17:21 | MR33 | MOORABBIN | Urban | Overloads |  | 1 | 70 | 70 | 1 | No
| 1852655 | 23/11/2024 | 16:27 | 23/11/2024 | 17:24 | M11 | MENTONE | Urban | Overloads |  | 37.95 | 2153.6625 | 56.75 | 1 | No
| 1852654 | 23/11/2024 | 17:05 | 23/11/2024 | 18:22 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 77 | 77 | 1 | No
| 1852685 | 23/11/2024 | 21:21 | 23/11/2024 | 22:45 | MC21 | MORDIALLOC | Urban | Asset Failure | LV | 2 | 167.8 | 83.9 | 1 | No
| 1852687 | 23/11/2024 | 21:32 | 23/11/2024 | 22:23 | DC4 | DONCASTER | Urban | Animal | Animal impact | 37.52 | 1882.2546 | 50.1667 | 1 | No
| 1852704 | 24/11/2024 | 1:14 | 24/11/2024 | 4:00 | M22 | MENTONE | Urban | Asset Failure | LV | 1 | 165.35 | 165.35 | 1 | No
| 1852751 | 24/11/2024 | 13:59 | 24/11/2024 | 16:10 | EW2 | ELWOOD | Urban | Overloads |  | 1 | 131 | 131 | 1 | No
| 1852774 | 24/11/2024 | 23:27 | 25/11/2024 | 2:07 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 64 | 10240 | 160 | 1 | No
| 1852809 | 25/11/2024 | 3:38 | 25/11/2024 | 5:35 | OE15 | OAKLEIGH EAST | Urban | Third Party | Other | 18 | 2091.9006 | 116.2167 | 1 | No
| 1852809 | 25/11/2024 | 3:38 | 25/11/2024 | 11:10 | OE15 | OAKLEIGH EAST | Urban | Third Party | Other | 1 | 451.4333 | 451.4333 | 2 | No
| 1852908 | 25/11/2024 | 9:36 | 25/11/2024 | 10:05 | DSH32 | DANDENONG SOUTH | Urban | Third Party | Vehicle Impact | 8 | 226.6664 | 28.3333 | 1 | No
| 1852934 | 25/11/2024 | 10:24 | 25/11/2024 | 13:17 | CRM23 | CARRUM | Urban | Third Party | Other | 1 | 172.15 | 172.15 | 1 | No
| 1852931 | 25/11/2024 | 10:30 | 25/11/2024 | 14:06 | LD33 | LYNDALE | Urban | Asset Failure | LV | 1 | 216.6833 | 216.6833 | 1 | No
| 1852951 | 25/11/2024 | 11:24 | 25/11/2024 | 13:15 | GW1 | GLEN WAVERLEY | Urban | Asset Failure | LV | 9 | 995.85 | 110.65 | 1 | No
| 1853031 | 25/11/2024 | 15:46 | 25/11/2024 | 17:40 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 114.2167 | 114.2167 | 1 | No
| 1853066 | 25/11/2024 | 20:16 | 25/11/2024 | 21:15 | GW2 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 58.8667 | 58.8667 | 1 | No
| 1853080 | 25/11/2024 | 23:39 | 26/11/2024 | 3:25 | CFD12 | CAULFIELD | Urban | Overloads |  | 8.91 | 2005.9377 | 225.1333 | 1 | No
| 1853084 | 26/11/2024 | 0:56 | 26/11/2024 | 2:31 | FSH21 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 1 | 94.9833 | 94.9833 | 1 | No
| 1853090 | 26/11/2024 | 4:35 | 26/11/2024 | 7:43 | NP24 | NOBLE PARK | Urban | Weather |  | 52.93 | 9940.254 | 187.8 | 1 | No
| 1853091 | 26/11/2024 | 4:55 | 26/11/2024 | 9:00 | EL23 | ELSTERNWICK | Urban | Animal | Animal impact | 91.79 | 22402.8824 | 244.0667 | 1 | No
| 1853100 | 26/11/2024 | 7:29 | 26/11/2024 | 12:10 | EL23 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 280.0667 | 280.0667 | 1 | No
| 1853125 | 26/11/2024 | 8:31 | 26/11/2024 | 10:03 | CRM34 | CARRUM | Urban | Overloads |  | 1 | 92.05 | 92.05 | 1 | No
| 1853248 | 26/11/2024 | 14:28 | 26/11/2024 | 15:24 | DMA12 | DROMANA | Urban | Asset Failure | LV | 1 | 56.75 | 56.75 | 1 | No
| 1853285 | 26/11/2024 | 14:40 | 26/11/2024 | 17:15 | SR24 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 154.05 | 154.05 | 1 | No
| 1853283 | 26/11/2024 | 14:45 | 26/11/2024 | 16:08 | FSH23 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 5.28 | 440.7918 | 83.4833 | 1 | No
| 1853310 | 26/11/2024 | 16:13 | 26/11/2024 | 21:18 | EB24 | EAST BURWOOD | Urban | Third Party | Vehicle Impact | 19 | 5788.6673 | 304.6667 | 1 | No
| 1853324 | 26/11/2024 | 17:40 | 26/11/2024 | 21:15 | DC1 | DONCASTER | Urban | Overloads |  | 3.63 | 777.6669 | 214.2333 | 1 | No
| 1853340 | 26/11/2024 | 19:59 | 26/11/2024 | 23:50 | HT11 | HEATHERTON | Urban | Third Party | Other | 1 | 231 | 231 | 1 | No
| 1853347 | 26/11/2024 | 22:09 | 26/11/2024 | 23:20 | HT11 | HEATHERTON | Urban | Third Party | Other | 1 | 71 | 71 | 1 | No
| 1853335 | 26/11/2024 | 22:19 | 26/11/2024 | 23:23 | DC2 | DONCASTER | Urban | Animal | Animal impact | 67 | 4288 | 64 | 1 | No
| 1853333 | 26/11/2024 | 23:03 | 27/11/2024 | 1:35 | CDA21 | CLARINDA | Urban | Unknown | Unknown | 51.59 | 7841.68 | 152 | 1 | No
| 1853334 | 27/11/2024 | 1:46 | 27/11/2024 | 4:25 | BT22 | BENTLEIGH | Urban | Animal | Other | 728 | 116346.5576 | 159.8167 | 1 | No
| 1853400 | 27/11/2024 | 8:08 | 27/11/2024 | 10:36 | FSH33 | FRANKSTON SOUTH | Urban | Weather |  | 20.1 | 2956.3743 | 147.0833 | 1 | No
| 1853404 | 27/11/2024 | 8:09 | 27/11/2024 | 8:35 | EM1 | EAST MALVERN | Urban | Asset Failure | LV | 38.28 | 973.5867 | 25.4333 | 1 | No
| 1853434 | 27/11/2024 | 9:04 | 27/11/2024 | 12:10 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 1 | 186.1 | 186.1 | 1 | No
| 1853513 | 27/11/2024 | 11:55 | 27/11/2024 | 14:32 | FSH22 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 5 | 787.3335 | 157.4667 | 1 | No
| 1853539 | 27/11/2024 | 12:11 | 27/11/2024 | 14:12 | MGE12 | MULGRAVE | Urban | Asset Failure | LV | 10 | 1210.167 | 121.0167 | 1 | No
| 1853551 | 27/11/2024 | 13:02 | 27/11/2024 | 14:40 | CRM13 | CARRUM | Urban | Asset Failure | LV | 1 | 97.2667 | 97.2667 | 1 | No
| 1853552 | 27/11/2024 | 13:03 | 27/11/2024 | 16:00 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1 | 176.2167 | 176.2167 | 1 | No
| 1853564 | 27/11/2024 | 14:06 | 27/11/2024 | 18:00 | BC11 | BALACLAVA | Urban | Asset Failure | LV | 5 | 1170 | 234 | 1 | No
| 1853584 | 27/11/2024 | 14:26 | 27/11/2024 | 22:08 | SR31 | SANDRINGHAM | Urban | Unknown | Unknown | 1 | 461.6333 | 461.6333 | 1 | No
| 1853601 | 27/11/2024 | 15:00 | 27/11/2024 | 20:00 | NB31 | NORTH BRIGHTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 12 | 3590.4 | 299.2 | 1 | No
| 1853608 | 27/11/2024 | 15:09 | 27/11/2024 | 18:20 | MC21 | MORDIALLOC | Urban | Asset Failure | Distribution substation | 149 | 28334.8383 | 190.1667 | 1 | No
| 1853630 | 27/11/2024 | 16:06 | 28/11/2024 | 0:33 | HT3 | HEATHERTON | Urban | Asset Failure | LV | 1 | 506.5 | 506.5 | 1 | No
| 1853641 | 27/11/2024 | 16:14 | 27/11/2024 | 19:15 | HT1 | HEATHERTON | Urban | Asset Failure | LV | 1 | 180.1167 | 180.1167 | 1 | No
| 1853649 | 27/11/2024 | 16:32 | 27/11/2024 | 19:27 | BT12 | BENTLEIGH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 174.4167 | 174.4167 | 1 | No
| 1853655 | 27/11/2024 | 16:53 | 27/11/2024 | 20:45 | CDA23 | CLARINDA | Urban | Unknown | Unknown | 1 | 231.2333 | 231.2333 | 1 | No
| 1853562 | 27/11/2024 | 18:00 | 27/11/2024 | 20:15 | EB12 | EAST BURWOOD | Urban | Third Party | Dig-in | 1 | 135 | 135 | 1 | No
| 1853668 | 27/11/2024 | 18:06 | 27/11/2024 | 23:40 | EW9 | ELWOOD | Urban | Asset Failure | LV | 13 | 4350.2329 | 334.6333 | 1 | No
| 1853682 | 27/11/2024 | 18:22 | 28/11/2024 | 2:27 | HGS23 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 56 | 27174 | 485.25 | 1 | No
| 1853682 | 27/11/2024 | 18:25 | 27/11/2024 | 19:45 | HGS23 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 227 | 18311.3409 | 80.6667 | 1 | No
| 1853682 | 27/11/2024 | 18:25 | 27/11/2024 | 20:07 | HGS23 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 426 | 43714.7142 | 102.6167 | 2 | No
| 1853712 | 27/11/2024 | 19:01 | 27/11/2024 | 23:13 | FSH32 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 2 | 503.1 | 251.55 | 1 | No
| 1853723 | 27/11/2024 | 19:21 | 28/11/2024 | 1:17 | NB21 | NORTH BRIGHTON | Urban | Overloads |  | 2 | 711.5 | 355.75 | 1 | No
| 1853725 | 27/11/2024 | 19:26 | 27/11/2024 | 20:34 | NB22 | NORTH BRIGHTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 34 | 2298.4 | 67.6 | 1 | No
| 1853732 | 27/11/2024 | 19:58 | 27/11/2024 | 21:28 | NO7 | NOTTING HILL | Urban | Overloads |  | 1 | 89.2 | 89.2 | 1 | No
| 1853739 | 27/11/2024 | 20:38 | 28/11/2024 | 1:02 | OR24 | ORMOND | Urban | Asset Failure | LV | 1 | 263.3833 | 263.3833 | 1 | No
| 1853699 | 27/11/2024 | 20:41 | 27/11/2024 | 23:12 | BH31 | BOX HILL | Urban | Asset Failure | LV | 1 | 151.3333 | 151.3333 | 1 | No
| 1853743 | 27/11/2024 | 21:21 | 28/11/2024 | 1:49 | FSH22 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 268.6333 | 268.6333 | 1 | No
| 1853766 | 28/11/2024 | 2:31 | 28/11/2024 | 3:50 | EL23 | ELSTERNWICK | Urban | Overloads |  | 20.79 | 1636.173 | 78.7 | 1 | No
| 1853770 | 28/11/2024 | 4:33 | 28/11/2024 | 7:10 | LWN34 | LANGWARRIN | Urban | Animal | Animal impact | 61.64 | 9638.4434 | 156.3667 | 1 | No
| 1853775 | 28/11/2024 | 5:18 | 28/11/2024 | 8:01 | MC14 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 163.1833 | 163.1833 | 1 | No
| 1853783 | 28/11/2024 | 7:28 | 28/11/2024 | 15:50 | DMA24 | DROMANA | Rural Short | Weather |  | 1 | 501.15 | 501.15 | 1 | No
| 1853786 | 28/11/2024 | 7:38 | 28/11/2024 | 8:32 | FTN23 | FRANKSTON | Urban | Unknown | Unknown | 1 | 53.6333 | 53.6333 | 1 | No
| 1853798 | 28/11/2024 | 8:02 | 28/11/2024 | 11:03 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 180.25 | 180.25 | 1 | No
| 1853844 | 28/11/2024 | 9:15 | 28/11/2024 | 11:30 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 134.9833 | 134.9833 | 1 | No
| 1854058 | 28/11/2024 | 13:01 | 28/11/2024 | 15:01 | FTN11 | FRANKSTON | Urban | Third Party | Vehicle Impact | 9 | 1081.8 | 120.2 | 1 | No
| 1854075 | 28/11/2024 | 13:56 | 28/11/2024 | 14:28 | BR1 | BEAUMARIS | Urban | Overloads |  | 2.97 | 93.9016 | 31.6167 | 1 | No
| 1854123 | 28/11/2024 | 17:01 | 28/11/2024 | 17:59 | BU25 | BULLEEN | Urban | Asset Failure | HV | 499 | 28492.9 | 57.1 | 1 | No
| 1854123 | 28/11/2024 | 17:01 | 28/11/2024 | 18:29 | BU25 | BULLEEN | Urban | Asset Failure | HV | 380 | 33243.654 | 87.4833 | 2 | No
| 1854123 | 28/11/2024 | 17:01 | 28/11/2024 | 18:30 | BU25 | BULLEEN | Urban | Asset Failure | HV | 210 | 18585 | 88.5 | 3 | No
| 1854123 | 28/11/2024 | 17:01 | 28/11/2024 | 22:12 | BU25 | BULLEEN | Urban | Asset Failure | HV | 121 | 37554.3707 | 310.3667 | 4 | No
| 1854124 | 28/11/2024 | 17:02 | 28/11/2024 | 17:13 | BU21 | BULLEEN | Urban | Asset Failure | HV | 1033 | 11087.4989 | 10.7333 | 1 | No
| 1854130 | 28/11/2024 | 17:46 | 28/11/2024 | 21:30 | MC23 | MORDIALLOC | Urban | Asset Failure | LV | 2 | 446.4334 | 223.2167 | 1 | No
| 1854146 | 28/11/2024 | 19:22 | 28/11/2024 | 22:00 | MR14 | MOORABBIN | Urban | Asset Failure | LV | 1 | 157.1333 | 157.1333 | 1 | No
| 1854153 | 28/11/2024 | 20:01 | 28/11/2024 | 21:18 | FSH22 | FRANKSTON SOUTH | Urban | Asset Failure | Distribution substation | 23.43 | 1804.8902 | 77.0333 | 1 | No
| 1854164 | 28/11/2024 | 21:29 | 29/11/2024 | 0:10 | CDA11 | CLARINDA | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 160.0833 | 160.0833 | 1 | No
| 1854165 | 29/11/2024 | 7:25 | 29/11/2024 | 11:26 | HGS32 | HASTINGS | Urban | Asset Failure | LV | 1 | 241 | 241 | 1 | No
| 1854212 | 29/11/2024 | 7:50 | 29/11/2024 | 10:50 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 7 | 1260 | 180 | 1 | No
| 1854210 | 29/11/2024 | 7:54 | 29/11/2024 | 9:37 | WD23 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 102.4833 | 102.4833 | 1 | No
| 1854225 | 29/11/2024 | 8:18 | 29/11/2024 | 11:30 | SV16 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 191.5667 | 191.5667 | 1 | No
| 1854397 | 29/11/2024 | 9:15 | 29/11/2024 | 12:40 | MTN22 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 615 | 205 | 1 | No
| 1854488 | 29/11/2024 | 10:04 | 29/11/2024 | 23:10 | DN22 | DANDENONG | Urban | Asset Failure | LV | 18 | 14142.9006 | 785.7167 | 1 | No
| 1854317 | 29/11/2024 | 10:06 | 29/11/2024 | 15:09 | LWN34 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 302.7167 | 302.7167 | 1 | No
| 1854301 | 29/11/2024 | 11:52 | 29/11/2024 | 13:07 | SVW53 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 75.1667 | 75.1667 | 1 | No
| 1854385 | 29/11/2024 | 12:30 | 29/11/2024 | 14:40 | K27 | GARDINER | Urban | Asset Failure | LV | 1 | 129.2833 | 129.2833 | 1 | No
| 1854399 | 29/11/2024 | 13:44 | 29/11/2024 | 16:25 | DC3 | DONCASTER | Urban | Unknown | Unknown | 1 | 161.25 | 161.25 | 1 | No
| 1854439 | 29/11/2024 | 15:32 | 29/11/2024 | 17:15 | WD23 | WEST DONCASTER | Urban | Asset Failure | HV | 34 | 3475.3678 | 102.2167 | 1 | No
| 1854453 | 29/11/2024 | 16:52 | 29/11/2024 | 17:34 | FSH32 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 2 | 84.9666 | 42.4833 | 1 | No
| 1854468 | 29/11/2024 | 18:14 | 29/11/2024 | 19:32 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 1 | 77.4833 | 77.4833 | 1 | No
| 1854480 | 29/11/2024 | 19:09 | 30/11/2024 | 0:15 | HGS33 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 7019.6 | 305.2 | 1 | No
| 1854485 | 29/11/2024 | 19:21 | 29/11/2024 | 22:00 | EM7 | EAST MALVERN | Urban | Asset Failure | LV | 9 | 1422.1503 | 158.0167 | 1 | No
| 1854478 | 29/11/2024 | 19:46 | 30/11/2024 | 0:31 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 1 | 285.1333 | 285.1333 | 1 | No
| 1854493 | 29/11/2024 | 20:14 | 29/11/2024 | 22:29 | CFD12 | CAULFIELD | Urban | Overloads |  | 27 | 3660.7491 | 135.5833 | 1 | No
| 1854500 | 29/11/2024 | 22:24 | 29/11/2024 | 23:21 | K35 | GARDINER | Urban | Asset Failure | LV | 1 | 57 | 57 | 1 | No
| 1854501 | 29/11/2024 | 22:37 | 30/11/2024 | 0:12 | RWT35 | RINGWOOD | Urban | Overloads |  | 1 | 95.8167 | 95.8167 | 1 | No
| 1854511 | 29/11/2024 | 23:07 | 30/11/2024 | 16:21 | SS24 | SPRINGVALE SOUTH | Urban | Third Party | Other | 7 | 7236.25 | 1033.75 | 1 | No
| 1854555 | 30/11/2024 | 10:01 | 30/11/2024 | 17:23 | EB14 | EAST BURWOOD | Urban | Asset Failure | LV | 76 | 33622.4 | 442.4 | 1 | No
| 1854555 | 30/11/2024 | 14:47 | 30/11/2024 | 17:23 | EB14 | EAST BURWOOD | Urban | Asset Failure | LV | 30 | 4680.501 | 156.0167 | 1 | No
| 1854593 | 30/11/2024 | 14:52 | 30/11/2024 | 15:22 | HGS22 | HASTINGS | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 29.7333 | 29.7333 | 1 | No
| 1854555 | 30/11/2024 | 15:00 | 30/11/2024 | 17:23 | EB14 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 143.5167 | 143.5167 | 1 | No
| 1854596 | 30/11/2024 | 15:00 | 30/11/2024 | 17:23 | EB14 | EAST BURWOOD | Urban | Asset Failure | LV | 3 | 430.35 | 143.45 | 1 | No
| 1854598 | 30/11/2024 | 15:04 | 30/11/2024 | 15:25 | MR13 | MOORABBIN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 52 | 1047.8 | 20.15 | 1 | No
| 1854619 | 30/11/2024 | 18:03 | 30/11/2024 | 20:34 | DMA15 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 8.71 | 1319.7105 | 151.5167 | 1 | No
| 1854622 | 30/11/2024 | 18:26 | 30/11/2024 | 21:45 | STO14 | SORRENTO | Rural Short | Unknown | Unknown | 1 | 198.0333 | 198.0333 | 1 | No
| 1854627 | 30/11/2024 | 19:14 | 30/11/2024 | 20:48 | GW6 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 93.7667 | 93.7667 | 1 | No
| 1854647 | 2024-01-12 | 2:42 | 2024-01-12 | 8:20 | EM6 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 337.1667 | 337.1667 | 1 | No
| 1854648 | 2024-01-12 | 6:07 | 2024-01-12 | 10:37 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 270.5333 | 270.5333 | 1 | No
| 1854701 | 2024-01-12 | 11:02 | 2024-01-12 | 14:55 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 3 | 698.7 | 232.9 | 1 | No
| 1854703 | 2024-01-12 | 12:13 | 2024-01-12 | 14:18 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 22.11 | 2764.1192 | 125.0167 | 1 | No
| 1854713 | 2024-01-12 | 13:23 | 2024-01-12 | 15:22 | HT2 | HEATHERTON | Urban | Asset Failure | LV | 1 | 118.75 | 118.75 | 1 | No
| 1854716 | 2024-01-12 | 13:34 | 2024-01-12 | 16:20 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1.65 | 273.075 | 165.5 | 1 | No
| 1854738 | 2024-01-12 | 17:50 | 2024-01-12 | 20:15 | SR26 | SANDRINGHAM | Urban | Asset Failure | LV | 21.45 | 3094.1625 | 144.25 | 1 | No
| 1854751 | 2024-01-12 | 18:18 | 2024-01-12 | 20:15 | BR1 | BEAUMARIS | Urban | Overloads |  | 1 | 117 | 117 | 1 | No
| 1854741 | 2024-01-12 | 18:49 | 2024-01-12 | 20:10 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 12 | 966.6 | 80.55 | 1 | No
| 1854742 | 2024-01-12 | 19:19 | 2024-02-12 | 1:42 | DVY33 | DANDENONG VALLEY | Urban | Third Party | Other | 9 | 3441.6 | 382.4 | 1 | No
| 1854752 | 2024-01-12 | 19:46 | 2024-01-12 | 22:00 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 134 | 134 | 1 | No
| 1854774 | 2024-02-12 | 1:56 | 2024-02-12 | 17:19 | FTN24 | FRANKSTON | Urban | Asset Failure | LV | 3 | 2769.15 | 923.05 | 1 | No
| 1854944 | 2024-02-12 | 13:56 | 2024-02-12 | 19:00 | OR24 | ORMOND | Urban | Overloads |  | 1 | 303.55 | 303.55 | 1 | No
| 1854954 | 2024-02-12 | 14:25 | 2024-02-12 | 16:18 | NW33 | NUNAWADING | Urban | Unknown | Unknown | 1 | 113.3833 | 113.3833 | 1 | No
| 1854983 | 2024-02-12 | 16:56 | 2024-02-12 | 18:01 | CRM24 | CARRUM | Urban | Asset Failure | LV | 1 | 64.7833 | 64.7833 | 1 | No
| 1855000 | 2024-02-12 | 18:58 | 2024-02-12 | 20:57 | WD36 | WEST DONCASTER | Urban | Overloads |  | 21.12 | 2513.28 | 119 | 1 | No
| 1855012 | 2024-02-12 | 19:18 | 2024-02-12 | 21:12 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1 | 113.7167 | 113.7167 | 1 | No
| 1855024 | 2024-02-12 | 20:43 | 2024-03-12 | 0:18 | FSH21 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 214.95 | 214.95 | 1 | No
| 1855040 | 2024-03-12 | 2:02 | 2024-03-12 | 3:20 | DC1 | DONCASTER | Urban | Third Party | Other | 1 | 78.4 | 78.4 | 1 | No
| 1855073 | 2024-03-12 | 8:21 | 2024-03-12 | 9:39 | DC1 | DONCASTER | Urban | Third Party | Other | 1 | 77.6667 | 77.6667 | 1 | No
| 1855148 | 2024-03-12 | 10:23 | 2024-03-12 | 11:47 | DC6 | DONCASTER | Urban | Asset Failure | LV | 1 | 83.6833 | 83.6833 | 1 | No
| 1855216 | 2024-03-12 | 12:46 | 2024-03-12 | 15:18 | MR13 | MOORABBIN | Urban | Asset Failure | LV | 2.4 | 363.72 | 151.55 | 1 | No
| 1855047 | 2024-03-12 | 15:04 | 2024-03-12 | 16:13 | DC6 | DONCASTER | Urban | Asset Failure | LV | 1 | 69.5 | 69.5 | 1 | No
| 1855286 | 2024-03-12 | 17:39 | 2024-03-12 | 20:22 | KBH31 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 162.8833 | 162.8833 | 1 | No
| 1855090 | 2024-03-12 | 17:40 | 2024-03-12 | 20:59 | EL34 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 199.1 | 199.1 | 1 | No
| 1855289 | 2024-03-12 | 18:20 | 2024-03-12 | 20:02 | DVY12 | DANDENONG VALLEY | Urban | Asset Failure | LV | 1 | 102 | 102 | 1 | No
| 1855309 | 2024-03-12 | 20:07 | 2024-03-12 | 21:37 | NW13 | NUNAWADING | Urban | Asset Failure | LV | 1 | 90.6667 | 90.6667 | 1 | No
| 1855319 | 2024-03-12 | 23:39 | 2024-04-12 | 0:30 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 6.03 | 307.3292 | 50.9667 | 1 | No
| 1855321 | 2024-04-12 | 0:29 | 2024-04-12 | 0:41 | DMA23 | DROMANA | Rural Short | Animal | Other | 201 | 2405.3067 | 11.9667 | 1 | No
| 1855321 | 2024-04-12 | 0:29 | 2024-04-12 | 1:30 | DMA23 | DROMANA | Rural Short | Animal | Other | 129 | 7873.2957 | 61.0333 | 2 | No
| 1855321 | 2024-04-12 | 0:29 | 2024-04-12 | 1:35 | DMA23 | DROMANA | Rural Short | Animal | Other | 333 | 21706.0389 | 65.1833 | 3 | No
| 1855321 | 2024-04-12 | 0:29 | 2024-04-12 | 2:04 | DMA23 | DROMANA | Rural Short | Animal | Other | 32 | 3020.8 | 94.4 | 4 | No
| 1855337 | 2024-04-12 | 3:26 | 2024-04-12 | 5:29 | DN11 | DANDENONG | Urban | Animal | Animal impact | 50.25 | 6200.0108 | 123.3833 | 1 | No
| 1855369 | 2024-04-12 | 7:33 | 2024-04-12 | 10:31 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 0.66 | 117.546 | 178.1 | 1 | No
| 1855648 | 2024-04-12 | 14:21 | 2024-04-12 | 15:57 | GW2 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 96.75 | 96.75 | 1 | No
| 1855467 | 2024-04-12 | 17:33 | 2024-04-12 | 19:55 | CFD26 | CAULFIELD | Urban | Asset Failure | LV | 1 | 142 | 142 | 1 | No
| 1855695 | 2024-04-12 | 18:33 | 2024-05-12 | 0:07 | DC4 | DONCASTER | Urban | Asset Failure | LV | 35 | 11666.6655 | 333.3333 | 1 | No
| 1855700 | 2024-04-12 | 19:31 | 2024-04-12 | 22:11 | CRM35 | CARRUM | Urban | Weather |  | 1 | 160.8333 | 160.8333 | 1 | No
| 1855705 | 2024-04-12 | 20:06 | 2024-04-12 | 21:17 | DMA23 | DROMANA | Rural Short | Asset Failure | LV | 1 | 71.5167 | 71.5167 | 1 | No
| 1855714 | 2024-04-12 | 21:28 | 2024-04-12 | 23:12 | DC10 | DONCASTER | Urban | Animal | Animal impact | 71 | 7380.45 | 103.95 | 1 | No
| 1855721 | 2024-04-12 | 22:18 | 2024-04-12 | 23:10 | OAK24 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 51.8333 | 51.8333 | 1 | No
| 1855734 | 2024-04-12 | 23:03 | 2024-05-12 | 0:02 | EM5 | EAST MALVERN | Urban | Animal | Animal impact | 105.86 | 6178.6989 | 58.3667 | 1 | No
| 1855740 | 2024-04-12 | 23:21 | 2024-04-12 | 23:57 | MC15 | MORDIALLOC | Urban | Asset Failure | HV | 720 | 26208 | 36.4 | 1 | No
| 1855740 | 2024-04-12 | 23:21 | 2024-05-12 | 0:08 | MC15 | MORDIALLOC | Urban | Asset Failure | HV | 505 | 23650.8165 | 46.8333 | 2 | No
| 1855740 | 2024-04-12 | 23:21 | 2024-05-12 | 0:38 | MC15 | MORDIALLOC | Urban | Asset Failure | HV | 127 | 9776.8791 | 76.9833 | 3 | No
| 1855740 | 2024-04-12 | 23:21 | 2024-05-12 | 1:07 | MC15 | MORDIALLOC | Urban | Asset Failure | HV | 249 | 26443.8 | 106.2 | 4 | No
| 1855743 | 2024-04-12 | 23:49 | 2024-05-12 | 3:53 | MR12 | MOORABBIN | Urban | Asset Failure | LV | 4.8 | 1172.7998 | 244.3333 | 1 | No
| 1855747 | 2024-05-12 | 0:43 | 2024-05-12 | 2:20 | FSH22 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 97.05 | 97.05 | 1 | No
| 1855754 | 2024-05-12 | 3:41 | 2024-05-12 | 5:39 | MTN32 | MORNINGTON | Rural Short | Animal | Animal impact | 3 | 354.8499 | 118.2833 | 1 | No
| 1855756 | 2024-05-12 | 4:00 | 2024-05-12 | 4:25 | GW4 | GLEN WAVERLEY | Urban | Unknown | Unknown | 4 | 100 | 25 | 1 | No
| 1855746 | 2024-05-12 | 5:16 | 2024-05-12 | 7:46 | KBH35 | KEYSBOROUGH | Urban | Third Party | Other | 1 | 150.4333 | 150.4333 | 1 | No
| 1855755 | 2024-05-12 | 7:01 | 2024-05-12 | 8:25 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 84 | 84 | 1 | No
| 1855794 | 2024-05-12 | 9:08 | 2024-05-12 | 16:30 | HGS31 | HASTINGS | Rural Short | Third Party | Dig-in | 1 | 441.8333 | 441.8333 | 1 | No
| 1855817 | 2024-05-12 | 9:58 | 2024-05-12 | 11:30 | SS11 | SPRINGVALE SOUTH | Urban | Overloads |  | 1 | 91.15 | 91.15 | 1 | No
| 1855906 | 2024-05-12 | 13:26 | 2024-05-12 | 19:28 | EL34 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 361.6833 | 361.6833 | 1 | No
| 1855940 | 2024-05-12 | 15:38 | 2024-05-12 | 18:45 | STO21 | SORRENTO | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 186.6 | 186.6 | 1 | No
| 1855944 | 2024-05-12 | 16:05 | 2024-05-12 | 19:05 | RBD22 | ROSEBUD | Urban | Asset Failure | LV | 37 | 6631.0179 | 179.2167 | 1 | No
| 1855949 | 2024-05-12 | 16:29 | 2024-05-12 | 20:06 | HGS22 | HASTINGS | Rural Short | Network Business | Network Error | 1 | 216.65 | 216.65 | 1 | No
| 1855954 | 2024-05-12 | 17:54 | 2024-05-12 | 23:44 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 350.25 | 350.25 | 1 | No
| 1855960 | 2024-05-12 | 18:51 | 2024-06-12 | 1:24 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 392.7333 | 392.7333 | 1 | No
| 1855979 | 2024-05-12 | 22:45 | 2024-06-12 | 1:01 | CFD25 | CAULFIELD | Urban | Asset Failure | LV | 93 | 12640.2531 | 135.9167 | 1 | No
| 1856001 | 2024-06-12 | 5:39 | 2024-06-12 | 9:46 | SS11 | SPRINGVALE SOUTH | Urban | Animal | Animal impact | 2 | 492.9334 | 246.4667 | 1 | No
| 1856034 | 2024-06-12 | 8:32 | 2024-06-12 | 10:05 | KBH34 | KEYSBOROUGH | Urban | Overloads |  | 3.96 | 368.1481 | 92.9667 | 1 | No
| 1856052 | 2024-06-12 | 9:20 | 2024-06-12 | 16:17 | FTN24 | FRANKSTON | Urban | Third Party | Vehicle Impact | 38 | 15832.7 | 416.65 | 1 | No
| 1855981 | 2024-06-12 | 9:52 | 2024-06-12 | 10:20 | NW22 | NUNAWADING | Urban | Overloads |  | 1 | 28 | 28 | 1 | No
| 1856084 | 2024-06-12 | 11:11 | 2024-06-12 | 13:28 | SS12 | SPRINGVALE SOUTH | Urban | Overloads |  | 1 | 137.05 | 137.05 | 1 | No
| 1856103 | 2024-06-12 | 12:12 | 2024-06-12 | 15:20 | MGE23 | MULGRAVE | Urban | Asset Failure | LV | 1 | 188.4167 | 188.4167 | 1 | No
| 1856104 | 2024-06-12 | 12:12 | 2024-06-12 | 14:46 | CFD12 | CAULFIELD | Urban | Overloads |  | 54.78 | 8438.859 | 154.05 | 1 | No
| 1856107 | 2024-06-12 | 12:15 | 2024-06-12 | 16:17 | FTN24 | FRANKSTON | Urban | Third Party | Vehicle Impact | 41 | 9894.6653 | 241.3333 | 1 | No
| 1856116 | 2024-06-12 | 12:57 | 2024-06-12 | 16:52 | MC22 | MORDIALLOC | Urban | Weather |  | 1 | 235.7667 | 235.7667 | 1 | No
| 1856121 | 2024-06-12 | 13:03 | 2024-06-12 | 20:15 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | HV | 85 | 36656.25 | 431.25 | 1 | No
| 1856153 | 2024-06-12 | 15:30 | 2024-06-12 | 17:09 | EB24 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 98.9167 | 98.9167 | 1 | No
| 1856173 | 2024-06-12 | 18:11 | 2024-06-12 | 20:05 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 113.7 | 113.7 | 1 | No
| 1856176 | 2024-06-12 | 19:27 | 2024-06-12 | 22:34 | OR34 | ORMOND | Urban | Asset Failure | LV | 1 | 186.2 | 186.2 | 1 | No
| 1856185 | 2024-06-12 | 21:08 | 2024-06-12 | 22:35 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 10.89 | 944.5256 | 86.7333 | 1 | No
| 1856191 | 2024-07-12 | 2:39 | 2024-07-12 | 3:45 | NP36 | NOBLE PARK | Urban | Third Party | Other | 3.35 | 219.9275 | 65.65 | 1 | No
| 1856192 | 2024-07-12 | 9:08 | 2024-07-12 | 10:30 | GW2 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 82 | 82 | 1 | No
| 1856205 | 2024-07-12 | 10:14 | 2024-07-12 | 16:35 | DMA21 | DROMANA | Urban | Asset Failure | LV | 1 | 380.4 | 380.4 | 1 | No
| 1856208 | 2024-07-12 | 10:53 | 2024-07-12 | 15:56 | HGS21 | HASTINGS | Rural Short | Asset Failure | HV | 1 | 303.3 | 303.3 | 1 | No
| 1856218 | 2024-07-12 | 13:27 | 2024-07-12 | 20:18 | MR11 | MOORABBIN | Urban | Asset Failure | LV | 1 | 410.9667 | 410.9667 | 1 | No
| 1856224 | 2024-07-12 | 16:23 | 2024-07-12 | 19:18 | BU25 | BULLEEN | Urban | Asset Failure | LV | 21 | 3668.3493 | 174.6833 | 1 | No
| 1856247 | 2024-07-12 | 22:01 | 2024-08-12 | 0:37 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 155.1833 | 155.1833 | 1 | No
| 1856248 | 2024-07-12 | 22:46 | 2024-08-12 | 11:01 | DMA15 | DROMANA | Rural Short | Animal | Animal impact | 4.02 | 2951.5511 | 734.2167 | 1 | No
| 1856259 | 2024-08-12 | 1:11 | 2024-08-12 | 2:54 | RWT34 | RINGWOOD | Urban | Unknown | Unknown | 73.03 | 7458.7949 | 102.1333 | 1 | No
| 1856257 | 2024-08-12 | 1:14 | 2024-08-12 | 8:17 | LWN33 | LANGWARRIN | Urban | Third Party | Vehicle Impact | 254 | 107412.3582 | 422.8833 | 1 | No
| 1856265 | 2024-08-12 | 2:37 | 2024-08-12 | 9:17 | DC2 | DONCASTER | Urban | Asset Failure | LV | 1 | 399.5667 | 399.5667 | 1 | No
| 1856276 | 2024-08-12 | 8:04 | 2024-08-12 | 8:20 | DC12 | DONCASTER | Urban | Network Business | Network Error | 35 | 549.5 | 15.7 | 1 | No
| 1856298 | 2024-08-12 | 10:39 | 2024-08-12 | 12:37 | MGE12 | MULGRAVE | Urban | Asset Failure | LV | 1 | 118.0667 | 118.0667 | 1 | No
| 1856294 | 2024-08-12 | 11:38 | 2024-08-12 | 13:20 | RWT35 | RINGWOOD | Urban | Asset Failure | LV | 1 | 102 | 102 | 1 | No
| 1856314 | 2024-08-12 | 12:56 | 2024-08-12 | 14:00 | NB34 | NORTH BRIGHTON | Urban | Asset Failure | LV | 6.6 | 418.77 | 63.45 | 1 | No
| 1856325 | 2024-08-12 | 16:24 | 2024-08-12 | 16:34 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 680 | 6471.356 | 9.5167 | 1 | No
| 1856325 | 2024-08-12 | 16:24 | 2024-08-12 | 16:36 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 569 | 6723.7023 | 11.8167 | 2 | No
| 1856325 | 2024-08-12 | 16:24 | 2024-09-12 | 1:04 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 11 | 5716.3337 | 519.6667 | 3 | No
| 1856325 | 2024-08-12 | 16:24 | 2024-09-12 | 19:53 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 5 | 8244.5 | 1648.9 | 4 | No
| 1856325 | 2024-08-12 | 16:24 | 2024-09-12 | 20:01 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 7 | 11594.8 | 1656.4 | 5 | No
| 1856346 | 2024-08-12 | 20:35 | 2024-08-12 | 21:10 | BH23 | BOX HILL | Urban | Vegetation | Grow-in - NSP responsibility | 978 | 34474.5 | 35.25 | 1 | No
| 1856353 | 2024-08-12 | 21:16 | 2024-09-12 | 9:40 | BH23 | BOX HILL | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 59 | 43859.6147 | 743.3833 | 1 | No
| 1856353 | 2024-08-12 | 21:17 | 2024-08-12 | 21:33 | BH23 | BOX HILL | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 31 | 478.95 | 15.45 | 1 | No
| 1856357 | 2024-08-12 | 21:30 | 2024-08-12 | 21:38 | MC15 | MORDIALLOC | Urban | Asset Failure | HV | 250 | 1841.675 | 7.3667 | 1 | No
| 1856358 | 2024-08-12 | 21:59 | 2024-09-12 | 0:05 | EB13 | EAST BURWOOD | Urban | Animal | Animal impact | 62.31 | 7833.4076 | 125.7167 | 1 | No
| 1856378 | 2024-09-12 | 3:10 | 2024-09-12 | 4:25 | FTN25 | FRANKSTON | Urban | Unknown | Unknown | 41.54 | 3076.7307 | 74.0667 | 1 | No
| 1856384 | 2024-09-12 | 4:15 | 2024-09-12 | 7:16 | RBD14 | ROSEBUD | Urban | Animal | Animal impact | 50.16 | 9044.6857 | 180.3167 | 1 | No
| 1856474 | 2024-09-12 | 12:50 | 2024-09-12 | 17:00 | CFD15 | CAULFIELD | Urban | Third Party | Vehicle Impact | 1 | 249.6167 | 249.6167 | 1 | No
| 1856521 | 2024-09-12 | 16:01 | 2024-09-12 | 18:59 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | HV | 45 | 8017.5015 | 178.1667 | 1 | No
| 1856521 | 2024-09-12 | 16:01 | 2024-09-12 | 20:22 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | HV | 4 | 1041.5332 | 260.3833 | 2 | No
| 1856597 | 2024-10-12 | 3:36 | 2024-10-12 | 7:35 | LWN21 | LANGWARRIN | Rural Short | Animal | Animal impact | 20.1 | 4784.805 | 238.05 | 1 | No
| 1856620 | 2024-10-12 | 4:02 | 2024-10-12 | 8:08 | DMA24 | DROMANA | Rural Short | Animal | Other | 3 | 737.3499 | 245.7833 | 1 | No
| 1856586 | 2024-10-12 | 7:04 | 2024-10-12 | 8:08 | HT2 | HEATHERTON | Urban | Overloads |  | 1 | 64.7 | 64.7 | 1 | No
| 1856666 | 2024-10-12 | 8:46 | 2024-10-12 | 10:04 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 77.9667 | 77.9667 | 1 | No
| 1856751 | 2024-10-12 | 11:54 | 2024-10-12 | 13:09 | OAK21 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 75.6167 | 75.6167 | 1 | No
| 1857038 | 2024-10-12 | 14:59 | 2024-10-12 | 17:45 | M35 | MENTONE | Urban | Asset Failure | LV | 1 | 165.8667 | 165.8667 | 1 | No
| 1857059 | 2024-10-12 | 15:51 | 2024-10-12 | 19:23 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 65 | 13751.8355 | 211.5667 | 1 | No
| 1857082 | 2024-10-12 | 18:16 | 2024-10-12 | 20:14 | DVY24 | DANDENONG VALLEY | Rural Short | Asset Failure | LV | 1 | 117.7167 | 117.7167 | 1 | No
| 1857083 | 2024-10-12 | 18:16 | 2024-10-12 | 19:17 | SV20 | SPRINGVALE | Urban | Third Party | Other | 1 | 60.2667 | 60.2667 | 1 | No
| 1857093 | 2024-10-12 | 19:09 | 2024-10-12 | 23:30 | DC2 | DONCASTER | Urban | Asset Failure | LV | 31 | 8088.4177 | 260.9167 | 1 | No
| 1857095 | 2024-10-12 | 19:13 | 2024-10-12 | 23:30 | DC2 | DONCASTER | Urban | Asset Failure | LV | 41 | 10519.9153 | 256.5833 | 1 | No
| 1857108 | 2024-10-12 | 21:15 | 2024-10-12 | 23:25 | EB33 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 129.2 | 129.2 | 1 | No
| 1857113 | 2024-10-12 | 22:46 | 2024-11-12 | 0:55 | HT8 | HEATHERTON | Urban | Animal | Animal impact | 9.38 | 1203.454 | 128.3 | 1 | No
| 1857116 | 2024-11-12 | 0:24 | 2024-11-12 | 1:04 | DC2 | DONCASTER | Urban | Animal | Other | 83.08 | 3325.9666 | 40.0333 | 1 | No
| 1857261 | 2024-11-12 | 10:22 | 2024-11-12 | 11:25 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 6.27 | 392.9202 | 62.6667 | 1 | No
| 1857339 | 2024-11-12 | 13:22 | 2024-11-12 | 15:06 | GW8 | GLEN WAVERLEY | Urban | Asset Failure | LV | 16.83 | 1760.418 | 104.6 | 1 | No
| 1857341 | 2024-11-12 | 13:26 | 2024-11-12 | 15:30 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 123.8 | 123.8 | 1 | No
| 1857356 | 2024-11-12 | 15:02 | 2024-11-12 | 17:41 | RBD21 | ROSEBUD | Rural Short | Third Party | Vehicle Impact | 1 | 159.25 | 159.25 | 1 | No
| 1857368 | 2024-11-12 | 15:45 | 2024-11-12 | 17:50 | LD7 | LYNDALE | Urban | Asset Failure | LV | 1 | 125 | 125 | 1 | No
| 1857386 | 2024-11-12 | 16:12 | 2024-11-12 | 18:00 | RWT34 | RINGWOOD | Urban | Third Party | Other | 1 | 108.2667 | 108.2667 | 1 | No
| 1857412 | 2024-11-12 | 19:30 | 2024-11-12 | 21:12 | K23 | GARDINER | Urban | Asset Failure | LV | 1 | 101.5833 | 101.5833 | 1 | No
| 1857420 | 2024-11-12 | 20:49 | 2024-11-12 | 21:55 | DC5 | DONCASTER | Urban | Asset Failure | LV | 1 | 66.1167 | 66.1167 | 1 | No
| 1857485 | 2024-12-12 | 8:45 | 2024-12-12 | 11:04 | CFD13 | CAULFIELD | Urban | Asset Failure | LV | 1 | 139.6833 | 139.6833 | 1 | No
| 1857435 | 2024-12-12 | 8:57 | 2024-12-12 | 12:30 | DC4 | DONCASTER | Urban | Overloads |  | 26 | 5538 | 213 | 1 | No
| 1857534 | 2024-12-12 | 10:08 | 2024-12-12 | 11:20 | DC2 | DONCASTER | Urban | Asset Failure | Distribution substation | 140 | 10054.338 | 71.8167 | 1 | No
| 1857557 | 2024-12-12 | 10:43 | 2024-12-12 | 11:58 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 6.27 | 470.5635 | 75.05 | 1 | No
| 1857595 | 2024-12-12 | 12:14 | 2024-12-12 | 13:41 | MR22 | MOORABBIN | Urban | Asset Failure | LV | 1 | 86.7 | 86.7 | 1 | No
| 1857639 | 2024-12-12 | 14:13 | 13/12/2024 | 4:00 | LD2 | LYNDALE | Urban | Asset Failure | LV | 14 | 11578 | 827 | 1 | No
| 1857638 | 2024-12-12 | 14:16 | 2024-12-12 | 17:35 | HT11 | HEATHERTON | Urban | Third Party | Other | 1 | 198.8167 | 198.8167 | 1 | No
| 1857609 | 2024-12-12 | 15:09 | 2024-12-12 | 17:57 | MC21 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 168.5 | 168.5 | 1 | No
| 1857684 | 2024-12-12 | 16:41 | 2024-12-12 | 17:11 | K25 | GARDINER | Urban | Asset Failure | LV | 4 | 121.8 | 30.45 | 1 | No
| 1857679 | 2024-12-12 | 16:46 | 2024-12-12 | 18:45 | OR35 | ORMOND | Urban | Asset Failure | LV | 1 | 119 | 119 | 1 | No
| 1857685 | 2024-12-12 | 17:04 | 13/12/2024 | 1:15 | BU25 | BULLEEN | Urban | Third Party | Dig-in | 48.18 | 23620.245 | 490.25 | 1 | No
| 1857701 | 2024-12-12 | 21:49 | 2024-12-12 | 22:25 | LWN35 | LANGWARRIN | Urban | Animal | Animal impact | 52.93 | 1868.429 | 35.3 | 1 | No
| 1857708 | 2024-12-12 | 22:54 | 13/12/2024 | 0:05 | LWN35 | LANGWARRIN | Urban | Animal | Animal impact | 74.37 | 5231.9295 | 70.35 | 1 | No
| 1857713 | 13/12/2024 | 0:08 | 13/12/2024 | 0:46 | FTN24 | FRANKSTON | Urban | Asset Failure | LV | 1 | 37.2333 | 37.2333 | 1 | No
| 1857714 | 13/12/2024 | 0:11 | 13/12/2024 | 2:00 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 15.18 | 1652.8485 | 108.8833 | 1 | No
| 1857717 | 13/12/2024 | 0:23 | 13/12/2024 | 1:00 | NW22 | NUNAWADING | Urban | Animal | Animal impact | 66.33 | 2452.0012 | 36.9667 | 1 | No
| 1857720 | 13/12/2024 | 2:03 | 13/12/2024 | 3:10 | LWN32 | LANGWARRIN | Rural Short | Unknown | Unknown | 2.01 | 133.8996 | 66.6167 | 1 | No
| 1857729 | 13/12/2024 | 5:33 | 13/12/2024 | 7:04 | FSH21 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 9.38 | 853.58 | 91 | 1 | No
| 1857800 | 13/12/2024 | 9:37 | 13/12/2024 | 9:43 | WD26 | WEST DONCASTER | Urban | Network Business | Network Error | 21.45 | 111.54 | 5.2 | 1 | No
| 1857840 | 13/12/2024 | 11:23 | 13/12/2024 | 14:40 | LD33 | LYNDALE | Urban | Overloads |  | 1 | 197 | 197 | 1 | No
| 1857863 | 13/12/2024 | 12:21 | 13/12/2024 | 16:52 | BT23 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 270.1 | 270.1 | 1 | No
| 1857892 | 13/12/2024 | 13:56 | 13/12/2024 | 16:41 | HGS23 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 164.8667 | 164.8667 | 1 | No
| 1857936 | 13/12/2024 | 17:12 | 14/12/2024 | 2:30 | HT9 | HEATHERTON | Urban | Third Party | Vehicle Impact | 1 | 557.5333 | 557.5333 | 1 | No
| 1857946 | 13/12/2024 | 19:58 | 13/12/2024 | 21:25 | MC21 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 86.0833 | 86.0833 | 1 | No
| 1857953 | 13/12/2024 | 21:26 | 13/12/2024 | 22:25 | LD4 | LYNDALE | Urban | Third Party | Other | 1 | 59.65 | 59.65 | 1 | No
| 1857960 | 14/12/2024 | 1:40 | 14/12/2024 | 8:03 | BR6 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 42 | 16086 | 383 | 1 | No
| 1857961 | 14/12/2024 | 3:35 | 14/12/2024 | 4:48 | RWT23 | RINGWOOD | Urban | Animal | Animal impact | 75.71 | 5559.6351 | 73.4333 | 1 | No
| 1857968 | 14/12/2024 | 3:46 | 14/12/2024 | 10:23 | CDA22 | CLARINDA | Urban | Asset Failure | LV | 1 | 396.2667 | 396.2667 | 1 | No
| 1857975 | 14/12/2024 | 4:46 | 14/12/2024 | 8:41 | DVY23 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 234.9167 | 234.9167 | 1 | No
| 1857975 | 14/12/2024 | 4:46 | 14/12/2024 | 16:01 | DVY23 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 674.3 | 674.3 | 2 | No
| 1857975 | 14/12/2024 | 4:46 | 14/12/2024 | 16:09 | DVY23 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 682.1833 | 682.1833 | 3 | No
| 1857978 | 14/12/2024 | 7:54 | 14/12/2024 | 12:15 | CM25 | CHELTENHAM | Urban | Asset Failure | LV | 1 | 260.9167 | 260.9167 | 1 | No
| 1857995 | 14/12/2024 | 8:46 | 14/12/2024 | 13:00 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 1 | 254.1667 | 254.1667 | 1 | No
| 1858082 | 14/12/2024 | 20:22 | 14/12/2024 | 22:25 | STO22 | SORRENTO | Urban | Asset Failure | LV | 1 | 122.2833 | 122.2833 | 1 | No
| 1858118 | 15/12/2024 | 11:13 | 15/12/2024 | 13:00 | KBH31 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 106.8667 | 106.8667 | 1 | No
| 1858124 | 15/12/2024 | 12:01 | 15/12/2024 | 13:40 | MC21 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 98.7833 | 98.7833 | 1 | No
| 1858131 | 15/12/2024 | 14:01 | 15/12/2024 | 15:56 | DSH14 | DANDENONG SOUTH | Urban | Third Party | Other | 5 | 572.25 | 114.45 | 1 | No
| 1858131 | 15/12/2024 | 14:01 | 16/12/2024 | 2:22 | DSH14 | DANDENONG SOUTH | Urban | Third Party | Other | 8 | 5923.2 | 740.4 | 2 | No
| 1858143 | 15/12/2024 | 17:44 | 15/12/2024 | 20:00 | DMA14 | DROMANA | Urban | Third Party | Vehicle Impact | 22 | 2972.5674 | 135.1167 | 1 | No
| 1858146 | 15/12/2024 | 17:50 | 15/12/2024 | 20:00 | DMA14 | DROMANA | Urban | Third Party | Vehicle Impact | 25 | 3242.9175 | 129.7167 | 1 | No
| 1858155 | 15/12/2024 | 18:32 | 15/12/2024 | 19:30 | MTN32 | MORNINGTON | Rural Short | Vegetation | Grow-in - NSP responsibility | 48 | 2779.2 | 57.9 | 1 | No
| 1858156 | 15/12/2024 | 18:46 | 15/12/2024 | 19:20 | EM10 | EAST MALVERN | Urban | Asset Failure | Zone substation | 932 | 32138.4356 | 34.4833 | 1 | No
| 1858156 | 15/12/2024 | 18:46 | 15/12/2024 | 19:51 | EM10 | EAST MALVERN | Urban | Asset Failure | Zone substation | 1948 | 127399.2 | 65.4 | 2 | No
| 1858156 | 15/12/2024 | 18:46 | 15/12/2024 | 20:44 | EM11 | EAST MALVERN | Urban | Asset Failure | Zone substation | 476 | 56152.1492 | 117.9667 | 1 | No
| 1858156 | 15/12/2024 | 18:46 | 15/12/2024 | 20:47 | EM11 | EAST MALVERN | Urban | Asset Failure | Zone substation | 368 | 44675.2 | 121.4 | 2 | No
| 1858156 | 15/12/2024 | 18:46 | 15/12/2024 | 20:54 | EM11 | EAST MALVERN | Urban | Asset Failure | Zone substation | 192 | 24537.6 | 127.8 | 3 | No
| 1858156 | 15/12/2024 | 18:46 | 15/12/2024 | 19:00 | EM7 | EAST MALVERN | Urban | Asset Failure | Zone substation | 1370 | 19682.379 | 14.3667 | 1 | No
| 1858156 | 15/12/2024 | 18:46 | 15/12/2024 | 19:39 | EM7 | EAST MALVERN | Urban | Asset Failure | Zone substation | 183 | 9839.3061 | 53.7667 | 2 | No
| 1858156 | 15/12/2024 | 18:46 | 15/12/2024 | 19:01 | EM8 | EAST MALVERN | Urban | Asset Failure | Zone substation | 772 | 12146.1076 | 15.7333 | 1 | No
| 1858156 | 15/12/2024 | 18:46 | 15/12/2024 | 19:40 | EM8 | EAST MALVERN | Urban | Asset Failure | Zone substation | 604 | 32827.4 | 54.35 | 2 | No
| 1858156 | 15/12/2024 | 18:46 | 15/12/2024 | 18:58 | EM9 | EAST MALVERN | Urban | Asset Failure | Zone substation | 669 | 8172.9723 | 12.2167 | 1 | No
| 1858156 | 15/12/2024 | 18:46 | 15/12/2024 | 19:15 | EM9 | EAST MALVERN | Urban | Asset Failure | Zone substation | 632 | 18549.2 | 29.35 | 2 | No
| 1858158 | 15/12/2024 | 19:14 | 15/12/2024 | 20:56 | DC8 | DONCASTER | Urban | Asset Failure | LV | 1 | 102.0333 | 102.0333 | 1 | No
| 1858169 | 15/12/2024 | 20:08 | 15/12/2024 | 23:28 | LD6 | LYNDALE | Urban | Asset Failure | LV | 1 | 199.9333 | 199.9333 | 1 | No
| 1858183 | 16/12/2024 | 0:59 | 16/12/2024 | 2:09 | NW23 | NUNAWADING | Urban | Asset Failure | Distribution substation | 101.84 | 7084.6727 | 69.5667 | 1 | No
| 1858352 | 16/12/2024 | 7:41 | 16/12/2024 | 17:10 | FTN12 | FRANKSTON | Urban | Third Party | Other | 3 | 1704.8499 | 568.2833 | 1 | No
| 1858215 | 16/12/2024 | 8:17 | 16/12/2024 | 9:15 | NO7 | NOTTING HILL | Urban | Asset Failure | LV | 1 | 58.65 | 58.65 | 1 | No
| 1858236 | 16/12/2024 | 9:01 | 16/12/2024 | 10:47 | DMA23 | DROMANA | Rural Short | Weather |  | 1 | 106.0167 | 106.0167 | 1 | No
| 1858263 | 16/12/2024 | 9:24 | 16/12/2024 | 11:20 | BR9 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 16.83 | 1953.963 | 116.1 | 1 | No
| 1858292 | 16/12/2024 | 10:18 | 16/12/2024 | 11:51 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 38.61 | 3574.0003 | 92.5667 | 1 | No
| 1858333 | 16/12/2024 | 11:54 | 16/12/2024 | 15:05 | EL23 | ELSTERNWICK | Urban | Overloads |  | 16.17 | 3085.7745 | 190.8333 | 1 | No
| 1858340 | 16/12/2024 | 12:03 | 16/12/2024 | 13:15 | MC12 | MORDIALLOC | Urban | Overloads |  | 12.87 | 925.353 | 71.9 | 1 | No
| 1858341 | 16/12/2024 | 12:05 | 16/12/2024 | 13:27 | DN8 | DANDENONG | Urban | Overloads |  | 1 | 82.2667 | 82.2667 | 1 | No
| 1858350 | 16/12/2024 | 12:24 | 16/12/2024 | 17:17 | BR1 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 292.3167 | 292.3167 | 1 | No
| 1858353 | 16/12/2024 | 12:27 | 16/12/2024 | 13:45 | EB33 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 77.2 | 77.2 | 1 | No
| 1858357 | 16/12/2024 | 12:31 | 16/12/2024 | 14:35 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 123.8833 | 123.8833 | 1 | No
| 1858407 | 16/12/2024 | 13:46 | 16/12/2024 | 14:11 | MGE34 | MULGRAVE | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 936 | 22900.8312 | 24.4667 | 1 | No
| 1858437 | 16/12/2024 | 15:09 | 16/12/2024 | 16:55 | CRM23 | CARRUM | Urban | Asset Failure | LV | 9 | 951.75 | 105.75 | 1 | No
| 1858442 | 16/12/2024 | 15:15 | 16/12/2024 | 16:30 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 2 | 148.7 | 74.35 | 1 | No
| 1858445 | 16/12/2024 | 15:19 | 16/12/2024 | 17:15 | STO22 | SORRENTO | Urban | Asset Failure | LV | 1 | 115.3167 | 115.3167 | 1 | No
| 1858471 | 16/12/2024 | 16:03 | 16/12/2024 | 17:03 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.1 | 59.1 | 1 | No
| 1858481 | 16/12/2024 | 16:23 | 16/12/2024 | 17:23 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.35 | 59.35 | 1 | No
| 1858486 | 16/12/2024 | 16:30 | 16/12/2024 | 16:57 | EB22 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 26.85 | 26.85 | 1 | No
| 1858487 | 16/12/2024 | 16:33 | 16/12/2024 | 17:33 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.1333 | 59.1333 | 1 | No
| 1858489 | 16/12/2024 | 16:39 | 16/12/2024 | 17:39 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.1667 | 59.1667 | 1 | No
| 1858490 | 16/12/2024 | 16:43 | 16/12/2024 | 17:43 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.25 | 59.25 | 1 | No
| 1858493 | 16/12/2024 | 16:45 | 16/12/2024 | 18:05 | EL23 | ELSTERNWICK | Urban | Overloads |  | 16.17 | 1286.0535 | 79.5333 | 1 | No
| 1858511 | 16/12/2024 | 16:45 | 16/12/2024 | 17:44 | M11 | MENTONE | Urban | Overloads |  | 37.95 | 2202.3637 | 58.0333 | 1 | No
| 1858507 | 16/12/2024 | 16:47 | 16/12/2024 | 17:47 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.3333 | 59.3333 | 1 | No
| 1858515 | 16/12/2024 | 16:53 | 16/12/2024 | 17:53 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.3667 | 59.3667 | 1 | No
| 1858526 | 16/12/2024 | 17:02 | 16/12/2024 | 22:40 | MR21 | MOORABBIN | Urban | Overloads |  | 27.39 | 9239.5591 | 337.3333 | 1 | No
| 1858522 | 16/12/2024 | 17:03 | 16/12/2024 | 18:03 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.1667 | 59.1667 | 1 | No
| 1858529 | 16/12/2024 | 17:13 | 16/12/2024 | 18:13 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.1167 | 59.1167 | 1 | No
| 1858475 | 16/12/2024 | 17:16 | 16/12/2024 | 18:01 | MTN24 | MORNINGTON | Rural Short | Overloads |  | 1 | 45.45 | 45.45 | 1 | No
| 1858533 | 16/12/2024 | 17:17 | 16/12/2024 | 18:17 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.3667 | 59.3667 | 1 | No
| 1858534 | 16/12/2024 | 17:17 | 16/12/2024 | 18:17 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.3667 | 59.3667 | 1 | No
| 1858537 | 16/12/2024 | 17:23 | 16/12/2024 | 18:23 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.2333 | 59.2333 | 1 | No
| 1858538 | 16/12/2024 | 17:23 | 16/12/2024 | 18:23 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.2333 | 59.2333 | 1 | No
| 1858539 | 16/12/2024 | 17:29 | 17/12/2024 | 0:18 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 408.2667 | 408.2667 | 1 | No
| 1858543 | 16/12/2024 | 17:35 | 16/12/2024 | 18:35 | MR31 | MOORABBIN | Urban | Overloads |  | 1 | 59.3167 | 59.3167 | 1 | No
| 1858544 | 16/12/2024 | 17:35 | 16/12/2024 | 18:35 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.3 | 59.3 | 1 | No
| 1858546 | 16/12/2024 | 17:39 | 16/12/2024 | 18:39 | MR31 | MOORABBIN | Urban | Overloads |  | 1 | 59.2167 | 59.2167 | 1 | No
| 1858547 | 16/12/2024 | 17:43 | 16/12/2024 | 18:43 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.1333 | 59.1333 | 1 | No
| 1858271 | 16/12/2024 | 17:44 | 16/12/2024 | 23:17 | BH12 | BOX HILL | Urban | Asset Failure | LV | 1 | 333.4167 | 333.4167 | 1 | No
| 1858513 | 16/12/2024 | 17:45 | 16/12/2024 | 23:25 | DC2 | DONCASTER | Urban | Overloads |  | 1 | 340.4 | 340.4 | 1 | No
| 1858548 | 16/12/2024 | 17:45 | 16/12/2024 | 18:45 | MR31 | MOORABBIN | Urban | Overloads |  | 1 | 59.0833 | 59.0833 | 1 | No
| 1858549 | 16/12/2024 | 17:45 | 16/12/2024 | 18:45 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.0833 | 59.0833 | 1 | No
| 1858552 | 16/12/2024 | 17:47 | 16/12/2024 | 23:45 | EL23 | ELSTERNWICK | Urban | Overloads |  | 20.79 | 7423.0695 | 357.05 | 1 | No
| 1858550 | 16/12/2024 | 17:48 | 16/12/2024 | 20:45 | SR21 | SANDRINGHAM | Urban | Asset Failure | LV | 29.04 | 5142.984 | 177.1 | 1 | No
| 1858551 | 16/12/2024 | 17:49 | 16/12/2024 | 18:49 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.1667 | 59.1667 | 1 | No
| 1858554 | 16/12/2024 | 17:52 | 16/12/2024 | 21:20 | OR32 | ORMOND | Urban | Overloads |  | 24.42 | 5067.9632 | 207.5333 | 1 | No
| 1858555 | 16/12/2024 | 17:52 | 16/12/2024 | 18:45 | BR10 | BEAUMARIS | Urban | Overloads |  | 24.42 | 1277.9792 | 52.3333 | 1 | No
| 1858553 | 16/12/2024 | 17:53 | 16/12/2024 | 18:53 | MR31 | MOORABBIN | Urban | Overloads |  | 1 | 59.0833 | 59.0833 | 1 | No
| 1858558 | 16/12/2024 | 17:54 | 16/12/2024 | 22:40 | BW23 | BURWOOD | Urban | Overloads |  | 23.76 | 6788.6288 | 285.7167 | 1 | No
| 1858563 | 16/12/2024 | 18:02 | 16/12/2024 | 20:22 | OR33 | ORMOND | Urban | Asset Failure | HV | 60.72 | 8473.476 | 139.55 | 1 | No
| 1858572 | 16/12/2024 | 18:02 | 16/12/2024 | 19:58 | SS23 | SPRINGVALE SOUTH | Urban | Unknown | Unknown | 294.8 | 33975.7 | 115.25 | 1 | No
| 1858565 | 16/12/2024 | 18:05 | 16/12/2024 | 19:06 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 60.3333 | 60.3333 | 1 | No
| 1858566 | 16/12/2024 | 18:05 | 16/12/2024 | 19:05 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.3167 | 59.3167 | 1 | No
| 1858567 | 16/12/2024 | 18:05 | 16/12/2024 | 19:06 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 60.3167 | 60.3167 | 1 | No
| 1858568 | 16/12/2024 | 18:05 | 16/12/2024 | 19:05 | HT4 | HEATHERTON | Urban | Unknown | Unknown | 1 | 59.3167 | 59.3167 | 1 | No
| 1858575 | 16/12/2024 | 18:07 | 16/12/2024 | 19:07 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.2667 | 59.2667 | 1 | No
| 1858583 | 16/12/2024 | 18:08 | 16/12/2024 | 22:25 | MTN32 | MORNINGTON | Rural Short | Overloads |  | 35.64 | 9126.2172 | 256.0667 | 1 | No
| 1858579 | 16/12/2024 | 18:09 | 16/12/2024 | 19:09 | HGS31 | HASTINGS | Rural Short | Overloads |  | 1 | 59.2333 | 59.2333 | 1 | No
| 1858580 | 16/12/2024 | 18:09 | 17/12/2024 | 1:07 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 1 | 417.9167 | 417.9167 | 1 | No
| 1858586 | 16/12/2024 | 18:13 | 16/12/2024 | 19:13 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.3 | 59.3 | 1 | No
| 1858588 | 16/12/2024 | 18:15 | 16/12/2024 | 19:15 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.2667 | 59.2667 | 1 | No
| 1858589 | 16/12/2024 | 18:15 | 16/12/2024 | 19:15 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.25 | 59.25 | 1 | No
| 1858592 | 16/12/2024 | 18:16 | 16/12/2024 | 19:43 | FTN12 | FRANKSTON | Urban | Overloads |  | 27.06 | 2352.4151 | 86.9333 | 1 | No
| 1858598 | 16/12/2024 | 18:19 | 16/12/2024 | 19:19 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.1667 | 59.1667 | 1 | No
| 1858603 | 16/12/2024 | 18:20 | 16/12/2024 | 23:00 | NB21 | NORTH BRIGHTON | Urban | Overloads |  | 24.75 | 6927.525 | 279.9 | 1 | No
| 1858604 | 16/12/2024 | 18:21 | 16/12/2024 | 21:16 | FTN25 | FRANKSTON | Urban | Overloads |  | 56.76 | 9959.4899 | 175.4667 | 1 | No
| 1858599 | 16/12/2024 | 18:21 | 16/12/2024 | 19:21 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.1167 | 59.1167 | 1 | No
| 1858600 | 16/12/2024 | 18:21 | 16/12/2024 | 19:21 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.1167 | 59.1167 | 1 | No
| 1858601 | 16/12/2024 | 18:21 | 16/12/2024 | 19:21 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.1167 | 59.1167 | 1 | No
| 1858602 | 16/12/2024 | 18:21 | 16/12/2024 | 19:21 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.1167 | 59.1167 | 1 | No
| 1858607 | 16/12/2024 | 18:25 | 16/12/2024 | 19:25 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.2 | 59.2 | 1 | No
| 1858608 | 16/12/2024 | 18:25 | 16/12/2024 | 19:25 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.1833 | 59.1833 | 1 | No
| 1858609 | 16/12/2024 | 18:25 | 16/12/2024 | 19:25 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.1833 | 59.1833 | 1 | No
| 1858611 | 16/12/2024 | 18:26 | 16/12/2024 | 21:50 | HT4 | HEATHERTON | Urban | Overloads |  | 23.43 | 4762.9277 | 203.2833 | 1 | No
| 1858613 | 16/12/2024 | 18:27 | 16/12/2024 | 19:15 | M34 | MENTONE | Urban | Overloads |  | 29.04 | 1378.433 | 47.4667 | 1 | No
| 1858616 | 16/12/2024 | 18:33 | 16/12/2024 | 21:19 | OR35 | ORMOND | Urban | Asset Failure | LV | 13.53 | 2243.274 | 165.8 | 1 | No
| 1858616 | 16/12/2024 | 18:33 | 16/12/2024 | 21:32 | OR35 | ORMOND | Urban | Asset Failure | LV | 0.66 | 117.832 | 178.5333 | 2 | No
| 1858775 | 16/12/2024 | 18:33 | 16/12/2024 | 21:32 | OR35 | ORMOND | Urban | Asset Failure | LV | 75 | 13389.9975 | 178.5333 | 1 | No
| 1858619 | 16/12/2024 | 18:33 | 16/12/2024 | 20:24 | FSH11 | FRANKSTON SOUTH | Urban | Overloads |  | 10.89 | 1205.523 | 110.7 | 1 | No
| 1858615 | 16/12/2024 | 18:36 | 16/12/2024 | 19:36 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.9667 | 59.9667 | 1 | No
| 1858621 | 16/12/2024 | 18:43 | 16/12/2024 | 19:43 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.3167 | 59.3167 | 1 | No
| 1858622 | 16/12/2024 | 18:43 | 16/12/2024 | 19:43 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.3167 | 59.3167 | 1 | No
| 1858623 | 16/12/2024 | 18:43 | 16/12/2024 | 19:43 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.3 | 59.3 | 1 | No
| 1858626 | 16/12/2024 | 18:44 | 16/12/2024 | 21:06 | NW13 | NUNAWADING | Urban | Overloads |  | 18.48 | 2616.768 | 141.6 | 1 | No
| 1858630 | 16/12/2024 | 18:46 | 16/12/2024 | 20:50 | LWN24 | LANGWARRIN | Urban | Overloads |  | 34.98 | 4337.52 | 124 | 1 | No
| 1858633 | 16/12/2024 | 18:47 | 16/12/2024 | 21:50 | LWN33 | LANGWARRIN | Urban | Overloads |  | 20.46 | 3728.4933 | 182.2333 | 1 | No
| 1858638 | 16/12/2024 | 18:51 | 16/12/2024 | 22:42 | LD3 | LYNDALE | Urban | Overloads |  | 9.24 | 2141.0623 | 231.7167 | 1 | No
| 1858639 | 16/12/2024 | 18:51 | 16/12/2024 | 21:44 | MC15 | MORDIALLOC | Urban | Overloads |  | 20.46 | 3520.143 | 172.05 | 1 | No
| 1858641 | 16/12/2024 | 18:52 | 16/12/2024 | 19:05 | LWN21 | LANGWARRIN | Rural Short | Overloads |  | 33 | 405.9 | 12.3 | 1 | No
| 1858643 | 16/12/2024 | 18:56 | 16/12/2024 | 19:56 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.8833 | 59.8833 | 1 | No
| 1858644 | 16/12/2024 | 18:56 | 16/12/2024 | 19:56 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.8833 | 59.8833 | 1 | No
| 1858645 | 16/12/2024 | 18:56 | 16/12/2024 | 19:56 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.8667 | 59.8667 | 1 | No
| 1858646 | 16/12/2024 | 18:56 | 17/12/2024 | 16:20 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 1 | 1283.8667 | 1283.8667 | 1 | No
| 1858647 | 16/12/2024 | 18:56 | 16/12/2024 | 19:56 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1858648 | 16/12/2024 | 18:56 | 16/12/2024 | 23:24 | FSH21 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 1 | 267.5167 | 267.5167 | 1 | No
| 1858650 | 16/12/2024 | 18:57 | 17/12/2024 | 15:51 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 1253.1667 | 1253.1667 | 1 | No
| 1858625 | 16/12/2024 | 18:58 | 16/12/2024 | 22:26 | BU21 | BULLEEN | Urban | Overloads |  | 1 | 208.15 | 208.15 | 1 | No
| 1858652 | 16/12/2024 | 19:03 | 16/12/2024 | 20:03 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.2667 | 59.2667 | 1 | No
| 1858656 | 16/12/2024 | 19:04 | 17/12/2024 | 0:16 | OR33 | ORMOND | Urban | Overloads |  | 31.02 | 9666.865 | 311.6333 | 1 | No
| 1858664 | 16/12/2024 | 19:07 | 17/12/2024 | 0:40 | BT15 | BENTLEIGH | Urban | Overloads |  | 15.84 | 5264.6885 | 332.3667 | 1 | No
| 1858655 | 16/12/2024 | 19:07 | 16/12/2024 | 20:07 | HGS31 | HASTINGS | Rural Short | Overloads |  | 1 | 59.35 | 59.35 | 1 | No
| 1858665 | 16/12/2024 | 19:08 | 16/12/2024 | 21:39 | NP36 | NOBLE PARK | Urban | Weather |  | 55.44 | 8361.2778 | 150.8167 | 1 | No
| 1858659 | 16/12/2024 | 19:10 | 16/12/2024 | 20:10 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.9667 | 59.9667 | 1 | No
| 1858660 | 16/12/2024 | 19:10 | 16/12/2024 | 20:10 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.8 | 59.8 | 1 | No
| 1858661 | 16/12/2024 | 19:10 | 16/12/2024 | 20:10 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1858662 | 16/12/2024 | 19:10 | 16/12/2024 | 20:10 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1858663 | 16/12/2024 | 19:10 | 16/12/2024 | 20:10 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 59.6167 | 59.6167 | 1 | No
| 1858669 | 16/12/2024 | 19:13 | 16/12/2024 | 21:40 | BU15 | BULLEEN | Urban | Overloads |  | 19.47 | 2860.143 | 146.9 | 1 | No
| 1858670 | 16/12/2024 | 19:20 | 16/12/2024 | 20:20 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.9 | 59.9 | 1 | No
| 1858672 | 16/12/2024 | 19:26 | 16/12/2024 | 20:26 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1858673 | 16/12/2024 | 19:26 | 16/12/2024 | 20:26 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.5333 | 59.5333 | 1 | No
| 1858675 | 16/12/2024 | 19:27 | 16/12/2024 | 20:27 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.2833 | 59.2833 | 1 | No
| 1858676 | 16/12/2024 | 19:28 | 16/12/2024 | 22:20 | OR24 | ORMOND | Urban | Overloads |  | 32.67 | 5617.6065 | 171.95 | 1 | No
| 1858678 | 16/12/2024 | 19:28 | 16/12/2024 | 22:40 | EB14 | EAST BURWOOD | Urban | Overloads |  | 12.87 | 2462.4596 | 191.3333 | 1 | No
| 1858682 | 16/12/2024 | 19:30 | 16/12/2024 | 22:47 | LD4 | LYNDALE | Urban | Overloads |  | 85.8 | 16935.4871 | 197.3833 | 1 | No
| 1858686 | 16/12/2024 | 19:33 | 16/12/2024 | 22:14 | EB12 | EAST BURWOOD | Urban | Asset Failure | LV | 19 | 3053.3 | 160.7 | 1 | No
| 1858684 | 16/12/2024 | 19:34 | 16/12/2024 | 20:34 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.9667 | 59.9667 | 1 | No
| 1858690 | 16/12/2024 | 19:35 | 16/12/2024 | 21:41 | OAK26 | OAKLEIGH | Urban | Overloads |  | 34.32 | 4323.1771 | 125.9667 | 1 | No
| 1858685 | 16/12/2024 | 19:35 | 16/12/2024 | 20:35 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.0833 | 59.0833 | 1 | No
| 1858698 | 16/12/2024 | 19:36 | 16/12/2024 | 20:48 | NO7 | NOTTING HILL | Urban | Asset Failure | LV | 1361.44 | 98273.232 | 72.1833 | 1 | No
| 1858689 | 16/12/2024 | 19:37 | 16/12/2024 | 20:37 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.05 | 59.05 | 1 | No
| 1858691 | 16/12/2024 | 19:38 | 16/12/2024 | 20:38 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.8667 | 59.8667 | 1 | No
| 1858692 | 16/12/2024 | 19:38 | 16/12/2024 | 20:38 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.8667 | 59.8667 | 1 | No
| 1858694 | 16/12/2024 | 19:41 | 16/12/2024 | 20:41 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.1167 | 59.1167 | 1 | No
| 1858696 | 16/12/2024 | 19:43 | 16/12/2024 | 20:43 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.0667 | 59.0667 | 1 | No
| 1858697 | 16/12/2024 | 19:43 | 16/12/2024 | 20:43 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.0667 | 59.0667 | 1 | No
| 1858700 | 16/12/2024 | 19:45 | 16/12/2024 | 20:45 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.2 | 59.2 | 1 | No
| 1858703 | 16/12/2024 | 19:47 | 16/12/2024 | 22:08 | EM8 | EAST MALVERN | Urban | Overloads |  | 16.83 | 2371.6281 | 140.9167 | 1 | No
| 1858706 | 16/12/2024 | 19:49 | 16/12/2024 | 20:49 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.1 | 59.1 | 1 | No
| 1858709 | 16/12/2024 | 19:50 | 16/12/2024 | 20:50 | DN11 | DANDENONG | Urban | Overloads |  | 1 | 59.7667 | 59.7667 | 1 | No
| 1858710 | 16/12/2024 | 19:50 | 16/12/2024 | 20:50 | HT4 | HEATHERTON | Urban | Overloads |  | 1 | 59.75 | 59.75 | 1 | No
| 1858747 | 16/12/2024 | 20:04 | 16/12/2024 | 23:04 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 64 | 11557.3312 | 180.5833 | 1 | No
| 1858748 | 16/12/2024 | 20:04 | 16/12/2024 | 22:40 | LWN23 | LANGWARRIN | Urban | Overloads |  | 18.81 | 2931.2244 | 155.8333 | 1 | No
| 1858769 | 16/12/2024 | 20:47 | 16/12/2024 | 22:50 | DN11 | DANDENONG | Urban | Asset Failure | LV | 1 | 122.2333 | 122.2333 | 1 | No
| 1858808 | 16/12/2024 | 21:28 | 16/12/2024 | 22:14 | EB12 | EAST BURWOOD | Urban | Asset Failure | HV | 0 | 3039.5689 | 45.3667 | 1 | No
| 1858818 | 16/12/2024 | 21:37 | 16/12/2024 | 23:10 | BU24 | BULLEEN | Urban | Animal | Animal impact | 74.37 | 6895.341 | 92.7167 | 1 | No
| 1858845 | 16/12/2024 | 23:57 | 17/12/2024 | 11:41 | MC21 | MORDIALLOC | Urban | Overloads |  | 1 | 704.2 | 704.2 | 1 | No
| 1858848 | 17/12/2024 | 0:37 | 17/12/2024 | 2:15 | EB12 | EAST BURWOOD | Urban | Animal | Animal impact | 40.2 | 3944.2913 | 98.1167 | 1 | No
| 1858883 | 17/12/2024 | 1:28 | 17/12/2024 | 3:52 | CM25 | CHELTENHAM | Urban | Third Party | Other | 1 | 144.3333 | 144.3333 | 1 | No
| 1858658 | 17/12/2024 | 1:33 | 17/12/2024 | 2:40 | FSH22 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 67 | 67 | 1 | No
| 1858887 | 17/12/2024 | 2:11 | 17/12/2024 | 4:37 | RBD23 | ROSEBUD | Urban | Animal | Animal impact | 153 | 22281.8949 | 145.6333 | 1 | No
| 1858998 | 17/12/2024 | 6:45 | 17/12/2024 | 21:33 | CRM23 | CARRUM | Urban | Third Party | Vehicle Impact | 21 | 18628.7493 | 887.0833 | 1 | No
| 1858917 | 17/12/2024 | 7:02 | 17/12/2024 | 9:12 | HGS31 | HASTINGS | Rural Short | Animal | Animal impact | 4 | 516.7332 | 129.1833 | 1 | No
| 1859018 | 17/12/2024 | 10:15 | 17/12/2024 | 13:36 | SR26 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 200.8833 | 200.8833 | 1 | No
| 1859038 | 17/12/2024 | 10:36 | 17/12/2024 | 21:28 | CRM23 | CARRUM | Urban | Third Party | Vehicle Impact | 15 | 9778.7505 | 651.9167 | 1 | No
| 1859071 | 17/12/2024 | 11:35 | 17/12/2024 | 11:45 | HT6 | HEATHERTON | Urban | Unknown | Unknown | 1 | 9.1667 | 9.1667 | 1 | No
| 1859103 | 17/12/2024 | 12:40 | 17/12/2024 | 16:30 | NW22 | NUNAWADING | Urban | Asset Failure | LV | 1 | 229.2667 | 229.2667 | 1 | No
| 1859104 | 17/12/2024 | 12:46 | 17/12/2024 | 15:20 | DMA13 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 153.2167 | 153.2167 | 1 | No
| 1859182 | 17/12/2024 | 16:06 | 17/12/2024 | 20:29 | MGE21 | MULGRAVE | Urban | Third Party | Vehicle Impact | 41 | 10788.4653 | 263.1333 | 1 | No
| 1859189 | 17/12/2024 | 16:39 | 17/12/2024 | 20:00 | RBD24 | ROSEBUD | Urban | Asset Failure | LV | 1 | 200.9167 | 200.9167 | 1 | No
| 1859191 | 17/12/2024 | 17:19 | 17/12/2024 | 21:30 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 251 | 251 | 1 | No
| 1859203 | 17/12/2024 | 18:05 | 17/12/2024 | 20:45 | EM9 | EAST MALVERN | Urban | Third Party | Other | 1 | 160.3833 | 160.3833 | 1 | No
| 1859223 | 17/12/2024 | 19:45 | 17/12/2024 | 22:07 | BW34 | BURWOOD | Urban | Asset Failure | LV | 1 | 142.2833 | 142.2833 | 1 | No
| 1859231 | 17/12/2024 | 21:06 | 17/12/2024 | 22:08 | BW34 | BURWOOD | Urban | Asset Failure | LV | 1 | 62.0833 | 62.0833 | 1 | No
| 1859248 | 17/12/2024 | 22:04 | 17/12/2024 | 23:51 | DC8 | DONCASTER | Urban | Animal | Animal impact | 47.57 | 5070.962 | 106.6 | 1 | No
| 1859243 | 17/12/2024 | 22:35 | 17/12/2024 | 23:55 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 20.46 | 1618.386 | 79.1 | 1 | No
| 1859264 | 18/12/2024 | 4:23 | 18/12/2024 | 4:44 | FSH13 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 1407 | 28843.5 | 20.5 | 1 | No
| 1859264 | 18/12/2024 | 4:23 | 18/12/2024 | 4:47 | FSH13 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 766 | 17835.0078 | 23.2833 | 2 | No
| 1859264 | 18/12/2024 | 4:23 | 18/12/2024 | 5:16 | FSH13 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 392 | 20593.0536 | 52.5333 | 3 | No
| 1859264 | 18/12/2024 | 4:23 | 18/12/2024 | 8:19 | FSH13 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 272 | 63997.0576 | 235.2833 | 4 | No
| 1859261 | 18/12/2024 | 5:19 | 18/12/2024 | 7:17 | GW11 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 118.1333 | 118.1333 | 1 | No
| 1859267 | 18/12/2024 | 5:44 | 18/12/2024 | 9:24 | FSH13 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 41 | 8994.0347 | 219.3667 | 1 | No
| 1859271 | 18/12/2024 | 6:02 | 18/12/2024 | 8:27 | EM9 | EAST MALVERN | Urban | Network Business | Switching and protection error | 1 | 145.0833 | 145.0833 | 1 | No
| 1859276 | 18/12/2024 | 6:29 | 18/12/2024 | 8:08 | BRA21 | BORONIA | Urban | Asset Failure | LV | 1 | 99.65 | 99.65 | 1 | No
| 1859278 | 18/12/2024 | 6:48 | 18/12/2024 | 8:17 | FSH13 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 59 | 5245.1 | 88.9 | 1 | No
| 1859344 | 18/12/2024 | 9:20 | 18/12/2024 | 11:20 | DC7 | DONCASTER | Urban | Asset Failure | LV | 1 | 120.1167 | 120.1167 | 1 | No
| 1859229 | 18/12/2024 | 10:40 | 18/12/2024 | 15:37 | EW14 | ELWOOD | Urban | Asset Failure | LV | 1 | 297.35 | 297.35 | 1 | No
| 1859564 | 18/12/2024 | 13:02 | 18/12/2024 | 16:50 | BT23 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 227.8833 | 227.8833 | 1 | No
| 1859539 | 18/12/2024 | 13:17 | 18/12/2024 | 14:45 | MR12 | MOORABBIN | Urban | Asset Failure | LV | 1 | 88 | 88 | 1 | No
| 1859588 | 18/12/2024 | 15:29 | 18/12/2024 | 17:30 | CFD26 | CAULFIELD | Urban | Asset Failure | LV | 1 | 121.8667 | 121.8667 | 1 | No
| 1859643 | 18/12/2024 | 17:17 | 18/12/2024 | 19:12 | DN25 | DANDENONG | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 115.4167 | 115.4167 | 1 | No
| 1859611 | 18/12/2024 | 18:19 | 18/12/2024 | 20:30 | MR14 | MOORABBIN | Urban | Asset Failure | LV | 1 | 131.6167 | 131.6167 | 1 | No
| 1859670 | 18/12/2024 | 20:57 | 18/12/2024 | 22:45 | EM5 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 108 | 108 | 1 | No
| 1859673 | 18/12/2024 | 21:22 | 18/12/2024 | 22:44 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 1 | 81.8667 | 81.8667 | 1 | No
| 1859690 | 19/12/2024 | 0:41 | 19/12/2024 | 1:50 | NW21 | NUNAWADING | Urban | Animal | Animal impact | 265.99 | 18233.6145 | 68.55 | 1 | No
| 1859700 | 19/12/2024 | 0:52 | 19/12/2024 | 3:03 | BH11 | BOX HILL | Urban | Animal | Other | 123 | 16174.5 | 131.5 | 1 | No
| 1859709 | 19/12/2024 | 4:01 | 19/12/2024 | 7:21 | LWN32 | LANGWARRIN | Rural Short | Animal | Other | 3 | 599.0001 | 199.6667 | 1 | No
| 1859745 | 19/12/2024 | 8:05 | 19/12/2024 | 9:50 | CRM14 | CARRUM | Rural Short | Third Party | Other | 1 | 104.6833 | 104.6833 | 1 | No
| 1859834 | 19/12/2024 | 10:20 | 19/12/2024 | 15:21 | OAK33 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 300.3333 | 300.3333 | 1 | No
| 1859839 | 19/12/2024 | 10:30 | 19/12/2024 | 13:18 | DC3 | DONCASTER | Urban | Asset Failure | LV | 42 | 7062.3 | 168.15 | 1 | No
| 1859959 | 19/12/2024 | 14:15 | 19/12/2024 | 18:10 | DMA15 | DROMANA | Rural Short | Third Party | Other | 1 | 235.2333 | 235.2333 | 1 | No
| 1859729 | 19/12/2024 | 14:20 | 19/12/2024 | 17:20 | MTN21 | MORNINGTON | Urban | Asset Failure | LV | 35 | 6274.3345 | 179.2667 | 1 | No
| 1859978 | 19/12/2024 | 15:09 | 19/12/2024 | 16:21 | DSH34 | DANDENONG SOUTH | Urban | Asset Failure | LV | 1 | 72.55 | 72.55 | 1 | No
| 1859986 | 19/12/2024 | 16:02 | 19/12/2024 | 18:25 | M31 | MENTONE | Urban | Asset Failure | LV | 1 | 142.8 | 142.8 | 1 | No
| 1860014 | 19/12/2024 | 19:31 | 19/12/2024 | 22:01 | FSH22 | FRANKSTON SOUTH | Urban | Overloads |  | 1 | 149.1167 | 149.1167 | 1 | No
| 1860018 | 19/12/2024 | 20:47 | 19/12/2024 | 22:58 | BH33 | BOX HILL | Urban | Third Party | Vehicle Impact | 40 | 5230 | 130.75 | 1 | No
| 1860028 | 20/12/2024 | 1:43 | 20/12/2024 | 2:55 | EB31 | EAST BURWOOD | Urban | Animal | Animal impact | 111.89 | 8061.6745 | 72.05 | 1 | No
| 1860033 | 20/12/2024 | 3:39 | 20/12/2024 | 7:40 | DN13 | DANDENONG | Urban | Animal | Animal impact | 117.92 | 28326.3533 | 240.2167 | 1 | No
| 1860052 | 20/12/2024 | 8:16 | 20/12/2024 | 19:30 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 7 | 4715.9 | 673.7 | 1 | No
| 1860087 | 20/12/2024 | 9:44 | 20/12/2024 | 11:03 | LWN35 | LANGWARRIN | Urban | Third Party | Other | 1 | 78.1 | 78.1 | 1 | No
| 1860149 | 20/12/2024 | 13:13 | 20/12/2024 | 15:00 | EL35 | ELSTERNWICK | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 106.2667 | 106.2667 | 1 | No
| 1860162 | 20/12/2024 | 13:42 | 20/12/2024 | 15:40 | RBD22 | ROSEBUD | Urban | Asset Failure | LV | 1 | 118.0667 | 118.0667 | 1 | No
| 1860163 | 20/12/2024 | 13:52 | 20/12/2024 | 21:45 | MC21 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 472.5167 | 472.5167 | 1 | No
| 1860166 | 20/12/2024 | 13:59 | 20/12/2024 | 15:00 | KBH34 | KEYSBOROUGH | Urban | Overloads |  | 13 | 786.7171 | 60.5167 | 1 | No
| 1860134 | 20/12/2024 | 14:12 | 20/12/2024 | 16:47 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 2.08 | 322.4347 | 155.0167 | 1 | No
| 1860200 | 20/12/2024 | 16:43 | 20/12/2024 | 20:40 | OR32 | ORMOND | Urban | Asset Failure | LV | 1 | 237 | 237 | 1 | No
| 1860210 | 20/12/2024 | 16:57 | 20/12/2024 | 18:48 | NP24 | NOBLE PARK | Urban | Asset Failure | LV | 19 | 2108.3673 | 110.9667 | 1 | No
| 1860212 | 20/12/2024 | 17:02 | 20/12/2024 | 17:55 | NP36 | NOBLE PARK | Urban | Overloads |  | 76 | 3979.8692 | 52.3667 | 1 | No
| 1860238 | 20/12/2024 | 20:07 | 20/12/2024 | 22:46 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 2 | 318.1 | 159.05 | 1 | No
| 1860333 | 20/12/2024 | 22:46 | 20/12/2024 | 23:21 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 34.65 | 34.65 | 1 | No
| 1860377 | 21/12/2024 | 7:47 | 21/12/2024 | 11:00 | CRM15 | CARRUM | Urban | Asset Failure | LV | 1 | 192.6167 | 192.6167 | 1 | No
| 1860383 | 21/12/2024 | 8:23 | 21/12/2024 | 9:49 | CRM14 | CARRUM | Rural Short | Animal | Animal impact | 127 | 10919.8791 | 85.9833 | 1 | No
| 1860421 | 21/12/2024 | 10:47 | 21/12/2024 | 12:20 | MC34 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 92.0333 | 92.0333 | 1 | No
| 1860429 | 21/12/2024 | 12:01 | 21/12/2024 | 14:45 | RD10 | RIVERSDALE | Urban | Asset Failure | LV | 1 | 163.8333 | 163.8333 | 1 | No
| 1860442 | 21/12/2024 | 14:30 | 21/12/2024 | 18:00 | OAK22 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 209.15 | 209.15 | 1 | No
| 1860453 | 21/12/2024 | 15:23 | 21/12/2024 | 18:14 | DC2 | DONCASTER | Urban | Overloads |  | 1 | 170.1833 | 170.1833 | 1 | No
| 1860451 | 21/12/2024 | 17:15 | 21/12/2024 | 19:52 | EB31 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 157.9833 | 157.9833 | 1 | No
| 1860466 | 21/12/2024 | 17:52 | 21/12/2024 | 21:09 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 197 | 197 | 1 | No
| 1860469 | 21/12/2024 | 18:08 | 21/12/2024 | 19:02 | BU21 | BULLEEN | Urban | Asset Failure | LV | 1 | 53.9333 | 53.9333 | 1 | No
| 1860477 | 21/12/2024 | 19:53 | 21/12/2024 | 21:00 | OR34 | ORMOND | Urban | Asset Failure | LV | 1 | 66.25 | 66.25 | 1 | No
| 1860478 | 21/12/2024 | 19:57 | 21/12/2024 | 22:35 | SR36 | SANDRINGHAM | Urban | Overloads |  | 2 | 315.8666 | 157.9333 | 1 | No
| 1860369 | 22/12/2024 | 13:51 | 22/12/2024 | 16:05 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 134 | 134 | 1 | No
| 1860538 | 22/12/2024 | 15:38 | 22/12/2024 | 17:20 | MR12 | MOORABBIN | Urban | Asset Failure | LV | 1 | 101.9 | 101.9 | 1 | No
| 1860564 | 22/12/2024 | 20:09 | 22/12/2024 | 20:24 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 362 | 5550.6546 | 15.3333 | 1 | No
| 1860564 | 22/12/2024 | 20:09 | 22/12/2024 | 20:51 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 558 | 23808.0186 | 42.6667 | 2 | No
| 1860573 | 22/12/2024 | 21:35 | 22/12/2024 | 22:15 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 123 | 4833.9 | 39.3 | 1 | No
| 1860573 | 22/12/2024 | 21:35 | 22/12/2024 | 22:47 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 45 | 3224.25 | 71.65 | 2 | No
| 1860573 | 22/12/2024 | 21:35 | 22/12/2024 | 22:51 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 209 | 15842.2 | 75.8 | 3 | No
| 1860579 | 22/12/2024 | 21:45 | 22/12/2024 | 22:45 | LD2 | LYNDALE | Urban | Asset Failure | HV | 248 | 14979.2 | 60.4 | 1 | No
| 1860579 | 22/12/2024 | 21:45 | 22/12/2024 | 22:47 | LD2 | LYNDALE | Urban | Asset Failure | HV | 20 | 1235.334 | 61.7667 | 2 | No
| 1860579 | 22/12/2024 | 21:45 | 23/12/2024 | 3:40 | LD2 | LYNDALE | Urban | Asset Failure | HV | 129 | 45861.6543 | 355.5167 | 3 | No
| 1860582 | 22/12/2024 | 21:58 | 23/12/2024 | 0:29 | STO21 | SORRENTO | Rural Short | Asset Failure | HV | 4 | 603.4 | 150.85 | 1 | No
| 1860592 | 22/12/2024 | 23:22 | 23/12/2024 | 0:30 | HT2 | HEATHERTON | Urban | Asset Failure | LV | 1 | 67.1167 | 67.1167 | 1 | No
| 1860597 | 22/12/2024 | 23:45 | 23/12/2024 | 1:27 | HT1 | HEATHERTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 25 | 2539.5825 | 101.5833 | 1 | No
| 1860623 | 23/12/2024 | 8:13 | 23/12/2024 | 10:13 | NO7 | NOTTING HILL | Urban | Asset Failure | LV | 1 | 119.1167 | 119.1167 | 1 | No
| 1860637 | 23/12/2024 | 8:53 | 23/12/2024 | 11:55 | STO14 | SORRENTO | Rural Short | Asset Failure | Distribution substation | 60 | 10872 | 181.2 | 1 | No
| 1860576 | 23/12/2024 | 10:13 | 23/12/2024 | 13:45 | NP36 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 212.0333 | 212.0333 | 1 | No
| 1860722 | 23/12/2024 | 11:10 | 23/12/2024 | 15:09 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 238.7667 | 238.7667 | 1 | No
| 1860767 | 23/12/2024 | 13:46 | 23/12/2024 | 17:02 | MR14 | MOORABBIN | Urban | Asset Failure | LV | 1 | 195.95 | 195.95 | 1 | No
| 1860795 | 23/12/2024 | 15:13 | 23/12/2024 | 18:58 | NB35 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 224.95 | 224.95 | 1 | No
| 1860464 | 23/12/2024 | 15:49 | 23/12/2024 | 21:56 | K25 | GARDINER | Urban | Asset Failure | LV | 1 | 367.1667 | 367.1667 | 1 | No
| 1860822 | 23/12/2024 | 16:27 | 23/12/2024 | 16:33 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 703 | 4557.7599 | 6.4833 | 1 | No
| 1860822 | 23/12/2024 | 16:27 | 23/12/2024 | 17:27 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 524 | 31579.7508 | 60.2667 | 2 | No
| 1860831 | 23/12/2024 | 16:27 | 23/12/2024 | 17:38 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 0 | 3227.2515 | 71.7167 | 1 | No
| 1860831 | 23/12/2024 | 17:28 | 23/12/2024 | 17:38 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 0 | 471.5651 | 10.0333 | 1 | No
| 1860831 | 23/12/2024 | 17:28 | 23/12/2024 | 18:23 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 0 | 25967.7 | 54.9 | 2 | No
| 1860831 | 23/12/2024 | 17:28 | 23/12/2024 | 20:05 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 0 | 625.0668 | 156.2667 | 3 | No
| 1860866 | 23/12/2024 | 19:34 | 23/12/2024 | 21:45 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 1 | 130.9833 | 130.9833 | 1 | No
| 1860869 | 23/12/2024 | 20:13 | 23/12/2024 | 23:51 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 218.1333 | 218.1333 | 1 | No
| 1860884 | 23/12/2024 | 23:55 | 24/12/2024 | 0:17 | FSH34 | FRANKSTON SOUTH | Urban | Overloads |  | 45.87 | 991.558 | 21.6167 | 1 | No
| 1860887 | 24/12/2024 | 1:27 | 24/12/2024 | 2:17 | DC5 | DONCASTER | Urban | Animal | Other | 95.14 | 4777.6168 | 50.2167 | 1 | No
| 1860917 | 24/12/2024 | 8:09 | 24/12/2024 | 10:39 | CDA23 | CLARINDA | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 149.9667 | 149.9667 | 1 | No
| 1860931 | 24/12/2024 | 9:05 | 24/12/2024 | 9:48 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 42.9333 | 42.9333 | 1 | No
| 1860932 | 24/12/2024 | 9:07 | 24/12/2024 | 10:08 | GW7 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 61.25 | 61.25 | 1 | No
| 1860944 | 24/12/2024 | 9:42 | 24/12/2024 | 15:25 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 343.6 | 343.6 | 1 | No
| 1860965 | 24/12/2024 | 11:14 | 24/12/2024 | 12:09 | MGE21 | MULGRAVE | Urban | Asset Failure | LV | 1 | 55.85 | 55.85 | 1 | No
| 1860970 | 24/12/2024 | 11:29 | 24/12/2024 | 18:00 | KBH32 | KEYSBOROUGH | Urban | Third Party | Vehicle Impact | 61 | 23844.9 | 390.9 | 1 | No
| 1860969 | 24/12/2024 | 11:31 | 24/12/2024 | 12:53 | OE10 | OAKLEIGH EAST | Urban | Asset Failure | LV | 1 | 81.85 | 81.85 | 1 | No
| 1860978 | 24/12/2024 | 12:11 | 24/12/2024 | 14:45 | EW2 | ELWOOD | Urban | Asset Failure | LV | 92 | 14168 | 154 | 1 | No
| 1860985 | 24/12/2024 | 12:58 | 24/12/2024 | 13:27 | MGE34 | MULGRAVE | Urban | Asset Failure | LV | 1 | 29.55 | 29.55 | 1 | No
| 1861015 | 24/12/2024 | 17:54 | 24/12/2024 | 19:13 | RBD24 | ROSEBUD | Urban | Asset Failure | LV | 1 | 78.2833 | 78.2833 | 1 | No
| 1861016 | 24/12/2024 | 17:54 | 24/12/2024 | 20:37 | RD4 | RIVERSDALE | Urban | Asset Failure | LV | 1 | 163.1833 | 163.1833 | 1 | No
| 1861017 | 24/12/2024 | 18:14 | 24/12/2024 | 19:34 | MGE24 | MULGRAVE | Urban | Asset Failure | LV | 1 | 80.25 | 80.25 | 1 | No
| 1861033 | 24/12/2024 | 21:40 | 24/12/2024 | 22:24 | CRM35 | CARRUM | Urban | Asset Failure | HV | 65 | 2831.8355 | 43.5667 | 1 | No
| 1861033 | 24/12/2024 | 21:40 | 24/12/2024 | 22:38 | CRM35 | CARRUM | Urban | Asset Failure | HV | 699 | 40180.8267 | 57.4833 | 2 | No
| 1861033 | 24/12/2024 | 21:40 | 24/12/2024 | 23:01 | CRM35 | CARRUM | Urban | Asset Failure | HV | 403 | 32266.8801 | 80.0667 | 3 | No
| 1861033 | 24/12/2024 | 21:40 | 24/12/2024 | 23:27 | CRM35 | CARRUM | Urban | Asset Failure | HV | 834 | 88918.3278 | 106.6167 | 4 | No
| 1861033 | 24/12/2024 | 21:40 | 24/12/2024 | 23:42 | CRM35 | CARRUM | Urban | Asset Failure | HV | 296 | 35885.0568 | 121.2333 | 5 | No
| 1861033 | 24/12/2024 | 21:40 | 24/12/2024 | 23:45 | CRM35 | CARRUM | Urban | Asset Failure | HV | 102 | 12748.2966 | 124.9833 | 6 | No
| 1861033 | 24/12/2024 | 21:40 | 24/12/2024 | 23:52 | CRM35 | CARRUM | Urban | Asset Failure | HV | 579 | 76215.6807 | 131.6333 | 7 | No
| 1861033 | 24/12/2024 | 21:40 | 25/12/2024 | 0:06 | CRM35 | CARRUM | Urban | Asset Failure | HV | 160 | 23213.328 | 145.0833 | 8 | No
| 1861033 | 24/12/2024 | 21:40 | 25/12/2024 | 0:17 | CRM35 | CARRUM | Urban | Asset Failure | HV | 113 | 17735.35 | 156.95 | 9 | No
| 1861033 | 24/12/2024 | 21:40 | 25/12/2024 | 0:22 | CRM35 | CARRUM | Urban | Asset Failure | HV | 524 | 84713.3508 | 161.6667 | 10 | No
| 1861033 | 24/12/2024 | 21:40 | 25/12/2024 | 0:45 | CRM35 | CARRUM | Urban | Asset Failure | HV | 159 | 29354.0553 | 184.6167 | 11 | No
| 1861033 | 24/12/2024 | 21:40 | 25/12/2024 | 1:20 | CRM35 | CARRUM | Urban | Asset Failure | HV | 14 | 3066.4662 | 219.0333 | 12 | No
| 1861033 | 24/12/2024 | 21:40 | 25/12/2024 | 3:03 | CRM35 | CARRUM | Urban | Asset Failure | HV | 33 | 10644.15 | 322.55 | 13 | No
| 1861048 | 24/12/2024 | 23:25 | 25/12/2024 | 1:06 | EM1 | EAST MALVERN | Urban | Animal | Animal impact | 105.86 | 10644.223 | 100.55 | 1 | No
| 1861061 | 25/12/2024 | 0:12 | 25/12/2024 | 4:04 | STO22 | SORRENTO | Urban | Animal | Other | 5 | 1157.5 | 231.5 | 1 | No
| 1861072 | 25/12/2024 | 1:23 | 25/12/2024 | 2:48 | HGS23 | HASTINGS | Rural Short | Animal | Animal impact | 188 | 15970.6 | 84.95 | 1 | No
| 1861083 | 25/12/2024 | 2:51 | 25/12/2024 | 9:09 | CRM35 | CARRUM | Urban | Asset Failure | Distribution substation | 34.84 | 13146.2922 | 377.3333 | 1 | No
| 1861085 | 25/12/2024 | 3:29 | 25/12/2024 | 7:16 | NP23 | NOBLE PARK | Urban | Animal | Animal impact | 66.33 | 15014.9032 | 226.3667 | 1 | No
| 1861091 | 25/12/2024 | 4:47 | 25/12/2024 | 7:48 | RBD12 | ROSEBUD | Rural Short | Asset Failure | HV | 150 | 27122.505 | 180.8167 | 1 | No
| 1861091 | 25/12/2024 | 4:47 | 25/12/2024 | 8:50 | RBD12 | ROSEBUD | Rural Short | Asset Failure | HV | 66 | 16033.5978 | 242.9333 | 2 | No
| 1861091 | 25/12/2024 | 4:47 | 25/12/2024 | 9:01 | RBD12 | ROSEBUD | Rural Short | Asset Failure | HV | 45 | 11449.4985 | 254.4333 | 3 | No
| 1861107 | 25/12/2024 | 10:26 | 25/12/2024 | 13:34 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 187.7167 | 187.7167 | 1 | No
| 1861111 | 25/12/2024 | 11:58 | 25/12/2024 | 16:01 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 243.6167 | 243.6167 | 1 | No
| 1861121 | 25/12/2024 | 14:13 | 25/12/2024 | 16:28 | MTN24 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 135.9167 | 135.9167 | 1 | No
| 1861125 | 25/12/2024 | 15:01 | 25/12/2024 | 17:42 | CRM35 | CARRUM | Urban | Asset Failure | HV | 1 | 160.65 | 160.65 | 1 | No
| 1861128 | 25/12/2024 | 16:55 | 25/12/2024 | 17:47 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 52.2167 | 52.2167 | 1 | No
| 1861136 | 25/12/2024 | 17:48 | 25/12/2024 | 18:41 | RBD12 | ROSEBUD | Rural Short | Asset Failure | HV | 45 | 2385.7515 | 53.0167 | 1 | No
| 1861138 | 25/12/2024 | 18:16 | 25/12/2024 | 19:39 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 83.1667 | 83.1667 | 1 | No
| 1861141 | 25/12/2024 | 19:05 | 25/12/2024 | 20:54 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 109.8 | 109.8 | 1 | No
| 1861127 | 25/12/2024 | 22:50 | 26/12/2024 | 3:18 | OAK33 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 268.4833 | 268.4833 | 1 | No
| 1861155 | 26/12/2024 | 0:56 | 26/12/2024 | 4:30 | RWT24 | RINGWOOD | Urban | Animal | Other | 10 | 2132 | 213.2 | 1 | No
| 1861158 | 26/12/2024 | 1:50 | 26/12/2024 | 9:27 | GW8 | GLEN WAVERLEY | Urban | Third Party | Vehicle Impact | 14 | 6394.9662 | 456.7833 | 1 | No
| 1861162 | 26/12/2024 | 1:55 | 26/12/2024 | 3:48 | STO21 | SORRENTO | Rural Short | Animal | Animal impact | 14 | 1573.6 | 112.4 | 1 | No
| 1861163 | 26/12/2024 | 2:02 | 26/12/2024 | 9:24 | GW8 | GLEN WAVERLEY | Urban | Third Party | Vehicle Impact | 17 | 7519.6661 | 442.3333 | 1 | No
| 1861198 | 26/12/2024 | 10:57 | 26/12/2024 | 13:43 | LWN23 | LANGWARRIN | Urban | Third Party | Other | 1 | 165.0333 | 165.0333 | 1 | No
| 1861200 | 26/12/2024 | 11:10 | 26/12/2024 | 12:50 | OAK34 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 99.6333 | 99.6333 | 1 | No
| 1861219 | 26/12/2024 | 13:58 | 26/12/2024 | 15:21 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 3 | 249.3501 | 83.1167 | 1 | No
| 1861216 | 26/12/2024 | 14:23 | 26/12/2024 | 16:05 | EB31 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 102.9 | 102.9 | 1 | No
| 1861221 | 26/12/2024 | 14:33 | 26/12/2024 | 16:36 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 123.1667 | 123.1667 | 1 | No
| 1861235 | 26/12/2024 | 17:06 | 26/12/2024 | 17:44 | HGS32 | HASTINGS | Urban | Animal | Animal impact | 565 | 21300.5 | 37.7 | 1 | No
| 1861235 | 26/12/2024 | 17:06 | 26/12/2024 | 17:44 | HGS32 | HASTINGS | Urban | Animal | Animal impact | 494 | 18936.6502 | 38.3333 | 2 | No
| 1861239 | 26/12/2024 | 17:44 | 26/12/2024 | 19:20 | MR14 | MOORABBIN | Urban | Third Party | Other | 1 | 95.3 | 95.3 | 1 | No
| 1861259 | 26/12/2024 | 21:02 | 27/12/2024 | 8:39 | MR11 | MOORABBIN | Urban | Asset Failure | LV | 1 | 697.2333 | 697.2333 | 1 | No
| 1861262 | 26/12/2024 | 21:43 | 26/12/2024 | 22:40 | EB32 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 21.12 | 1189.7593 | 56.3333 | 1 | No
| 1861267 | 26/12/2024 | 22:21 | 27/12/2024 | 0:17 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 116.1833 | 116.1833 | 1 | No
| 1861268 | 26/12/2024 | 23:08 | 27/12/2024 | 7:50 | MTN34 | MORNINGTON | Urban | Animal | Other | 1 | 521.2667 | 521.2667 | 1 | No
| 1861271 | 26/12/2024 | 23:35 | 27/12/2024 | 1:01 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 85.85 | 85.85 | 1 | No
| 1861274 | 27/12/2024 | 0:36 | 27/12/2024 | 2:17 | HGS31 | HASTINGS | Rural Short | Animal | Animal impact | 0.67 | 67.3573 | 100.5333 | 1 | No
| 1861276 | 27/12/2024 | 1:26 | 27/12/2024 | 2:08 | RWT34 | RINGWOOD | Urban | Animal | Animal impact | 73.03 | 3056.3055 | 41.85 | 1 | No
| 1861281 | 27/12/2024 | 2:12 | 27/12/2024 | 2:40 | MGE31 | MULGRAVE | Urban | Third Party | Vehicle Impact | 56 | 1559.6 | 27.85 | 1 | No
| 1861290 | 27/12/2024 | 8:03 | 27/12/2024 | 9:38 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 1 | 95.4333 | 95.4333 | 1 | No
| 1861240 | 27/12/2024 | 8:06 | 27/12/2024 | 10:45 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 159 | 159 | 1 | No
| 1861300 | 27/12/2024 | 9:46 | 27/12/2024 | 14:28 | NW21 | NUNAWADING | Urban | Asset Failure | LV | 1 | 282 | 282 | 1 | No
| 1861321 | 27/12/2024 | 10:13 | 27/12/2024 | 11:52 | CFD25 | CAULFIELD | Urban | Asset Failure | LV | 1 | 98.9667 | 98.9667 | 1 | No
| 1861328 | 27/12/2024 | 10:50 | 27/12/2024 | 12:17 | CRM23 | CARRUM | Urban | Asset Failure | LV | 31 | 2683.5677 | 86.5667 | 1 | No
| 1861315 | 27/12/2024 | 11:22 | 27/12/2024 | 14:12 | OR32 | ORMOND | Urban | Asset Failure | LV | 1 | 170.8333 | 170.8333 | 1 | No
| 1861339 | 27/12/2024 | 11:48 | 27/12/2024 | 12:57 | OR23 | ORMOND | Urban | Asset Failure | LV | 1 | 68.8 | 68.8 | 1 | No
| 1861351 | 27/12/2024 | 13:12 | 27/12/2024 | 15:08 | MTN31 | MORNINGTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 2 | 232.5666 | 116.2833 | 1 | No
| 1861363 | 27/12/2024 | 14:38 | 27/12/2024 | 17:22 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 163.5833 | 163.5833 | 1 | No
| 1861387 | 27/12/2024 | 21:49 | 27/12/2024 | 23:15 | STO14 | SORRENTO | Rural Short | Animal | Animal impact | 170.18 | 14570.25 | 85.6167 | 1 | No
| 1861430 | 28/12/2024 | 11:09 | 28/12/2024 | 11:58 | SVW56 | SPRINGVALE WEST | Urban | Overloads |  | 1 | 48.9333 | 48.9333 | 1 | No
| 1861439 | 28/12/2024 | 12:00 | 28/12/2024 | 14:04 | DN4 | DANDENONG | Urban | Animal | Animal impact | 1 | 123.2 | 123.2 | 1 | No
| 1861455 | 28/12/2024 | 14:41 | 28/12/2024 | 16:48 | SR24 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 126.75 | 126.75 | 1 | No
| 1861474 | 28/12/2024 | 18:03 | 28/12/2024 | 18:28 | GW3 | GLEN WAVERLEY | Urban | Vegetation | Grow-in - Other responsible party | 807 | 20282.5731 | 25.1333 | 1 | No
| 1861474 | 28/12/2024 | 18:03 | 28/12/2024 | 19:24 | GW3 | GLEN WAVERLEY | Urban | Vegetation | Grow-in - Other responsible party | 69 | 5534.9523 | 80.2167 | 2 | No
| 1861470 | 28/12/2024 | 19:05 | 28/12/2024 | 22:04 | M33 | MENTONE | Urban | Third Party | Other | 19 | 3408.6 | 179.4 | 1 | No
| 1861470 | 28/12/2024 | 19:05 | 28/12/2024 | 22:07 | M33 | MENTONE | Urban | Third Party | Other | 2 | 364 | 182 | 2 | No
| 1861499 | 28/12/2024 | 21:14 | 29/12/2024 | 1:56 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 281.6667 | 281.6667 | 1 | No
| 1861504 | 28/12/2024 | 22:07 | 28/12/2024 | 23:20 | NP31 | NOBLE PARK | Urban | Animal | Other | 72 | 5189.9976 | 72.0833 | 1 | No
| 1861520 | 29/12/2024 | 7:27 | 29/12/2024 | 10:59 | CRM22 | CARRUM | Urban | Asset Failure | LV | 1 | 211.7667 | 211.7667 | 1 | No
| 1861558 | 29/12/2024 | 20:02 | 29/12/2024 | 22:30 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 22.11 | 3271.1745 | 147.95 | 1 | No
| 1861567 | 29/12/2024 | 23:08 | 30/12/2024 | 3:03 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 235.25 | 235.25 | 1 | No
| 1861586 | 30/12/2024 | 1:58 | 30/12/2024 | 3:30 | LD7 | LYNDALE | Urban | Animal | Animal impact | 16.75 | 1528.4375 | 91.25 | 1 | No
| 1861592 | 30/12/2024 | 5:57 | 30/12/2024 | 9:53 | DMA15 | DROMANA | Rural Short | Animal | Animal impact | 1 | 236.3333 | 236.3333 | 1 | No
| 1861606 | 30/12/2024 | 8:41 | 30/12/2024 | 10:20 | SV20 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 98.5167 | 98.5167 | 1 | No
| 1861614 | 30/12/2024 | 9:29 | 30/12/2024 | 11:42 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1 | 133 | 133 | 1 | No
| 1861626 | 30/12/2024 | 10:50 | 30/12/2024 | 11:47 | BU11 | BULLEEN | Urban | Asset Failure | LV | 1 | 57.6333 | 57.6333 | 1 | No
| 1861563 | 30/12/2024 | 12:09 | 30/12/2024 | 13:23 | GW7 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 74.35 | 74.35 | 1 | No
| 1861662 | 30/12/2024 | 14:13 | 30/12/2024 | 14:50 | MGE24 | MULGRAVE | Urban | Third Party | Other | 5 | 182.1665 | 36.4333 | 1 | No
| 1861747 | 31/12/2024 | 8:00 | 31/12/2024 | 9:35 | HT3 | HEATHERTON | Urban | Animal | Animal impact | 20 | 1899.666 | 94.9833 | 1 | No
| 1861747 | 31/12/2024 | 8:00 | 31/12/2024 | 9:36 | HT3 | HEATHERTON | Urban | Animal | Animal impact | 1 | 96.3333 | 96.3333 | 2 | No
| 1861747 | 31/12/2024 | 8:00 | 31/12/2024 | 11:25 | HT3 | HEATHERTON | Urban | Animal | Animal impact | 2 | 411.4 | 205.7 | 3 | No
| 1861753 | 31/12/2024 | 9:11 | 31/12/2024 | 10:12 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 61.3667 | 61.3667 | 1 | No
| 1861765 | 31/12/2024 | 9:56 | 31/12/2024 | 11:30 | STO21 | SORRENTO | Rural Short | Animal | Animal impact | 15.41 | 1439.5513 | 93.4167 | 1 | No
| 1861779 | 31/12/2024 | 11:29 | 31/12/2024 | 13:33 | EW1 | ELWOOD | Urban | Overloads |  | 1 | 123.1833 | 123.1833 | 1 | No
| 1861781 | 31/12/2024 | 11:52 | 31/12/2024 | 14:13 | NW23 | NUNAWADING | Urban | Third Party | Other | 1 | 140.7333 | 140.7333 | 1 | No
| 1861818 | 31/12/2024 | 15:39 | 31/12/2024 | 18:38 | K35 | GARDINER | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 178.95 | 178.95 | 1 | No
| 1861831 | 2025-01-01 | 3:20 | 2025-01-01 | 3:25 | LD4 | LYNDALE | Urban | Animal | Animal impact | 2914 | 14764.3638 | 5.0667 | 1 | No
| 1861831 | 2025-01-01 | 3:20 | 2025-01-01 | 4:16 | LD4 | LYNDALE | Urban | Animal | Animal impact | 754 | 42525.6 | 56.4 | 2 | No
| 1861847 | 2025-01-01 | 11:40 | 2025-01-01 | 12:10 | WD23 | WEST DONCASTER | Urban | Asset Failure | LV | 12.87 | 384.5981 | 29.8833 | 1 | No
| 1861859 | 2025-01-01 | 14:14 | 2025-01-01 | 14:59 | LWN21 | LANGWARRIN | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 711 | 32599.35 | 45.85 | 1 | No
| 1861859 | 2025-01-01 | 14:17 | 2025-01-01 | 15:17 | LWN21 | LANGWARRIN | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 107 | 6330.8369 | 59.1667 | 1 | No
| 1861859 | 2025-01-01 | 14:17 | 2025-01-01 | 19:50 | LWN21 | LANGWARRIN | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 2324.35 | 332.05 | 2 | No
| 1861824 | 2025-01-01 | 16:58 | 2025-01-01 | 18:30 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 92 | 92 | 1 | No
| 1861974 | 2025-01-01 | 22:13 | 2025-01-01 | 23:56 | LWN24 | LANGWARRIN | Urban | Animal | Animal impact | 166 | 17086.9278 | 102.9333 | 1 | No
| 1862041 | 2025-02-01 | 12:45 | 2025-02-01 | 13:45 | SS11 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 60 | 60 | 1 | No
| 1862080 | 2025-02-01 | 15:33 | 2025-02-01 | 17:35 | SVW42 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 122.1833 | 122.1833 | 1 | No
| 1862098 | 2025-02-01 | 18:10 | 2025-02-01 | 19:43 | HT4 | HEATHERTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 92.4667 | 92.4667 | 1 | No
| 1862117 | 2025-02-01 | 22:51 | 2025-03-01 | 1:09 | HGS21 | HASTINGS | Rural Short | Animal | Animal impact | 503 | 69103.7999 | 137.3833 | 1 | No
| 1862135 | 2025-03-01 | 1:17 | 2025-03-01 | 2:25 | EB22 | EAST BURWOOD | Urban | Animal | Animal impact | 107 | 7240.3369 | 67.6667 | 1 | No
| 1862155 | 2025-03-01 | 7:37 | 2025-03-01 | 17:33 | NP12 | NOBLE PARK | Urban | Third Party | Other | 1 | 595.3833 | 595.3833 | 1 | No
| 1862163 | 2025-03-01 | 9:03 | 2025-03-01 | 11:24 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 141 | 141 | 1 | No
| 1862195 | 2025-03-01 | 11:15 | 2025-03-01 | 13:09 | STO21 | SORRENTO | Rural Short | Third Party | Vehicle Impact | 1 | 113.4 | 113.4 | 1 | No
| 1862210 | 2025-03-01 | 12:42 | 2025-03-01 | 15:19 | BU11 | BULLEEN | Urban | Unknown | Unknown | 1 | 157.5333 | 157.5333 | 1 | No
| 1862228 | 2025-03-01 | 14:20 | 2025-03-01 | 22:00 | FTN12 | FRANKSTON | Urban | Third Party | Other | 3 | 1378.5999 | 459.5333 | 1 | No
| 1862232 | 2025-03-01 | 14:54 | 2025-03-01 | 17:13 | GW8 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 139.3667 | 139.3667 | 1 | No
| 1862235 | 2025-03-01 | 15:03 | 2025-03-01 | 19:58 | RD4 | RIVERSDALE | Urban | Asset Failure | LV | 1 | 294.3667 | 294.3667 | 1 | No
| 1862200 | 2025-03-01 | 15:04 | 2025-03-01 | 15:30 | BR15 | BEAUMARIS | Urban | Asset Failure | HV | 88 | 2358.4 | 26.8 | 1 | No
| 1862220 | 2025-03-01 | 15:47 | 2025-03-01 | 16:50 | NP31 | NOBLE PARK | Urban | Overloads |  | 1 | 63.0667 | 63.0667 | 1 | No
| 1862255 | 2025-03-01 | 18:41 | 2025-03-01 | 22:25 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 223.2667 | 223.2667 | 1 | No
| 1862261 | 2025-03-01 | 19:18 | 2025-03-01 | 22:25 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 186.7 | 186.7 | 1 | No
| 1862262 | 2025-03-01 | 20:12 | 2025-03-01 | 22:48 | CFD23 | CAULFIELD | Urban | Overloads |  | 1 | 156.4167 | 156.4167 | 1 | No
| 1862281 | 2025-04-01 | 3:26 | 2025-04-01 | 8:42 | GW10 | GLEN WAVERLEY | Urban | Unknown | Unknown | 35 | 11050.0845 | 315.7167 | 1 | No
| 1862314 | 2025-04-01 | 12:05 | 2025-04-01 | 15:47 | MTN22 | MORNINGTON | Rural Short | Unknown | Unknown | 1 | 221.8 | 221.8 | 1 | No
| 1862315 | 2025-04-01 | 12:30 | 2025-04-01 | 14:08 | NW13 | NUNAWADING | Urban | Unknown | Unknown | 1 | 97.4333 | 97.4333 | 1 | No
| 1862330 | 2025-04-01 | 14:14 | 2025-04-01 | 17:19 | MGE22 | MULGRAVE | Urban | Asset Failure | LV | 1 | 184.4667 | 184.4667 | 1 | No
| 1862332 | 2025-04-01 | 14:40 | 2025-04-01 | 16:01 | GW7 | GLEN WAVERLEY | Urban | Asset Failure | LV | 11 | 891.1837 | 81.0167 | 1 | No
| 1862333 | 2025-04-01 | 15:03 | 2025-04-01 | 16:05 | NB33 | NORTH BRIGHTON | Urban | Overloads |  | 1 | 62 | 62 | 1 | No
| 1862340 | 2025-04-01 | 16:12 | 2025-04-01 | 18:19 | EB22 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 126.9667 | 126.9667 | 1 | No
| 1862342 | 2025-04-01 | 16:51 | 2025-04-01 | 20:20 | CRM23 | CARRUM | Urban | Overloads |  | 69.01 | 14410.4405 | 208.8167 | 1 | No
| 1862344 | 2025-04-01 | 16:52 | 2025-04-01 | 18:14 | STO23 | SORRENTO | Urban | Overloads |  | 21.12 | 1726.56 | 81.75 | 1 | No
| 1862347 | 2025-04-01 | 17:32 | 2025-04-01 | 20:09 | BR4 | BEAUMARIS | Urban | Overloads |  | 33.99 | 5312.637 | 156.3 | 1 | No
| 1862353 | 2025-04-01 | 18:08 | 2025-04-01 | 20:15 | SS11 | SPRINGVALE SOUTH | Urban | Overloads |  | 5.28 | 668.0958 | 126.5333 | 1 | No
| 1862357 | 2025-04-01 | 18:22 | 2025-04-01 | 19:05 | MGE34 | MULGRAVE | Urban | Asset Failure | LV | 1 | 43.2667 | 43.2667 | 1 | No
| 1862360 | 2025-04-01 | 18:25 | 2025-04-01 | 21:04 | OR32 | ORMOND | Urban | Overloads |  | 24.42 | 3868.9412 | 158.4333 | 1 | No
| 1862361 | 2025-04-01 | 18:35 | 2025-04-01 | 21:00 | MC12 | MORDIALLOC | Urban | Weather |  | 26.07 | 3754.9481 | 144.0333 | 1 | No
| 1862365 | 2025-04-01 | 18:51 | 2025-04-01 | 19:52 | LWN24 | LANGWARRIN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 60.6667 | 60.6667 | 1 | No
| 1862371 | 2025-04-01 | 19:17 | 2025-04-01 | 21:34 | GW1 | GLEN WAVERLEY | Urban | Asset Failure | LV | 2.97 | 404.5636 | 136.2167 | 1 | No
| 1862364 | 2025-04-01 | 19:25 | 2025-04-01 | 22:50 | SR36 | SANDRINGHAM | Urban | Overloads |  | 1 | 205 | 205 | 1 | No
| 1862375 | 2025-04-01 | 20:10 | 2025-04-01 | 21:51 | STO23 | SORRENTO | Urban | Overloads |  | 1 | 100.5833 | 100.5833 | 1 | No
| 1862384 | 2025-04-01 | 21:15 | 2025-04-01 | 22:56 | RBD14 | ROSEBUD | Urban | Overloads |  | 13.2 | 1323.7396 | 100.2833 | 1 | No
| 1862383 | 2025-04-01 | 21:27 | 2025-05-01 | 0:52 | HGS33 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 204.0833 | 204.0833 | 1 | No
| 1862413 | 2025-05-01 | 7:42 | 2025-05-01 | 9:48 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 125.9167 | 125.9167 | 1 | No
| 1862417 | 2025-05-01 | 8:56 | 2025-05-01 | 9:50 | DC8 | DONCASTER | Urban | Third Party | Other | 1 | 53.4333 | 53.4333 | 1 | No
| 1862418 | 2025-05-01 | 9:04 | 2025-05-01 | 14:38 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 334.3167 | 334.3167 | 1 | No
| 1862428 | 2025-05-01 | 9:19 | 2025-05-01 | 10:32 | SVW53 | SPRINGVALE WEST | Urban | Animal | Animal impact | 0.67 | 48.5638 | 72.4833 | 1 | No
| 1862425 | 2025-05-01 | 9:44 | 2025-05-01 | 11:40 | FTN22 | FRANKSTON | Urban | Third Party | Other | 9 | 1037.25 | 115.25 | 1 | No
| 1862426 | 2025-05-01 | 10:03 | 2025-05-01 | 14:34 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 1 | 270.0833 | 270.0833 | 1 | No
| 1862433 | 2025-05-01 | 10:32 | 2025-05-01 | 13:16 | STO22 | SORRENTO | Urban | Asset Failure | LV | 16.17 | 2641.908 | 163.3833 | 1 | No
| 1862441 | 2025-05-01 | 11:36 | 2025-05-01 | 13:06 | BR13 | BEAUMARIS | Urban | Asset Failure | LV | 34.98 | 3127.212 | 89.4 | 1 | No
| 1862440 | 2025-05-01 | 11:40 | 2025-05-01 | 16:17 | FTN24 | FRANKSTON | Urban | Asset Failure | LV | 1 | 277.8 | 277.8 | 1 | No
| 1862493 | 2025-05-01 | 13:25 | 2025-05-01 | 18:39 | HGS22 | HASTINGS | Rural Short | Unknown | Unknown | 1 | 313.2333 | 313.2333 | 1 | No
| 1862452 | 2025-05-01 | 13:35 | 2025-05-01 | 17:00 | NB21 | NORTH BRIGHTON | Urban | Overloads |  | 1 | 204.6333 | 204.6333 | 1 | No
| 1862455 | 2025-05-01 | 14:42 | 2025-05-01 | 16:43 | K25 | GARDINER | Urban | Asset Failure | LV | 1 | 121.6667 | 121.6667 | 1 | No
| 1862459 | 2025-05-01 | 15:07 | 2025-05-01 | 16:03 | OAK26 | OAKLEIGH | Urban | Overloads |  | 51.48 | 2865.7217 | 55.6667 | 1 | No
| 1862463 | 2025-05-01 | 15:25 | 2025-05-01 | 19:46 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 261.7667 | 261.7667 | 1 | No
| 1862464 | 2025-05-01 | 15:27 | 2025-05-01 | 21:25 | M23 | MENTONE | Urban | Asset Failure | LV | 1 | 357.5167 | 357.5167 | 1 | No
| 1862466 | 2025-05-01 | 15:36 | 2025-05-01 | 17:23 | STO13 | SORRENTO | Urban | Asset Failure | LV | 14.85 | 1585.732 | 106.7833 | 1 | No
| 1862482 | 2025-05-01 | 16:25 | 2025-05-01 | 18:00 | STO13 | SORRENTO | Urban | Asset Failure | LV | 108 | 10170.0036 | 94.1667 | 1 | No
| 1862485 | 2025-05-01 | 16:31 | 2025-05-01 | 18:22 | FTN25 | FRANKSTON | Urban | Overloads |  | 60 | 6696 | 111.6 | 1 | No
| 1862486 | 2025-05-01 | 16:49 | 2025-05-01 | 18:25 | CFD25 | CAULFIELD | Urban | Overloads |  | 1 | 96 | 96 | 1 | No
| 1862488 | 2025-05-01 | 16:57 | 2025-05-01 | 19:50 | MC14 | MORDIALLOC | Urban | Asset Failure | LV | 149 | 25754.65 | 172.85 | 1 | No
| 1862489 | 2025-05-01 | 17:21 | 2025-05-01 | 18:23 | BU22 | BULLEEN | Urban | Asset Failure | LV | 1 | 62.1 | 62.1 | 1 | No
| 1862494 | 2025-05-01 | 17:39 | 2025-05-01 | 20:04 | FTN25 | FRANKSTON | Urban | Overloads |  | 172 | 24882.6724 | 144.6667 | 1 | No
| 1862503 | 2025-05-01 | 17:52 | 2025-05-01 | 22:40 | FTN12 | FRANKSTON | Urban | Overloads |  | 82 | 23539.4694 | 287.0667 | 1 | No
| 1862510 | 2025-05-01 | 17:55 | 2025-05-01 | 21:55 | CRM13 | CARRUM | Urban | Overloads |  | 190 | 45492.327 | 239.4333 | 1 | No
| 1862513 | 2025-05-01 | 18:00 | 2025-05-01 | 20:03 | FSH11 | FRANKSTON SOUTH | Urban | Weather |  | 115 | 14077.9205 | 122.4167 | 1 | No
| 1862517 | 2025-05-01 | 18:15 | 2025-05-01 | 19:53 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 99 | 9763.0533 | 98.6167 | 1 | No
| 1862518 | 2025-05-01 | 18:16 | 2025-05-01 | 21:06 | CRM15 | CARRUM | Urban | Overloads |  | 218 | 36914.6594 | 169.3333 | 1 | No
| 1862520 | 2025-05-01 | 18:24 | 2025-05-01 | 19:50 | NW13 | NUNAWADING | Urban | Weather |  | 56 | 4816 | 86 | 1 | No
| 1862525 | 2025-05-01 | 18:28 | 2025-05-01 | 20:15 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 106.6667 | 106.6667 | 1 | No
| 1862529 | 2025-05-01 | 18:48 | 2025-05-01 | 21:03 | WD34 | WEST DONCASTER | Urban | Overloads |  | 66 | 8889.0978 | 134.6833 | 1 | No
| 1862530 | 2025-05-01 | 18:56 | 2025-05-01 | 22:20 | FTN23 | FRANKSTON | Urban | Animal | Animal impact | 7.37 | 1497.0924 | 203.1333 | 1 | No
| 1862535 | 2025-05-01 | 19:12 | 2025-06-01 | 0:43 | DMA13 | DROMANA | Rural Short | Asset Failure | HV | 172 | 56886.1276 | 330.7333 | 1 | No
| 1862543 | 2025-05-01 | 19:38 | 2025-05-01 | 21:57 | DC2 | DONCASTER | Urban | Asset Failure | LV | 1 | 138.6 | 138.6 | 1 | No
| 1862545 | 2025-05-01 | 19:49 | 2025-05-01 | 22:15 | MGE21 | MULGRAVE | Urban | Overloads |  | 329 | 47990.1443 | 145.8667 | 1 | No
| 1862547 | 2025-05-01 | 19:55 | 2025-05-01 | 20:50 | EL23 | ELSTERNWICK | Urban | Overloads |  | 63 | 3404.0979 | 54.0333 | 1 | No
| 1862548 | 2025-05-01 | 20:57 | 2025-06-01 | 0:30 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 26 | 5540.6 | 213.1 | 1 | No
| 1862558 | 2025-05-01 | 22:37 | 2025-06-01 | 0:26 | SV16 | SPRINGVALE | Urban | Animal | Animal impact | 2.68 | 291.6732 | 108.8333 | 1 | No
| 1862559 | 2025-05-01 | 22:41 | 2025-06-01 | 0:22 | MGE34 | MULGRAVE | Urban | Animal | Animal impact | 48.24 | 4848.12 | 100.5 | 1 | No
| 1862568 | 2025-06-01 | 3:38 | 2025-06-01 | 9:10 | HGS21 | HASTINGS | Rural Short | Unknown | Unknown | 22 | 7284.5674 | 331.1167 | 1 | No
| 1862602 | 2025-06-01 | 4:21 | 2025-06-01 | 15:00 | DVY32 | DANDENONG VALLEY | Urban | Third Party | Other | 8 | 5112 | 639 | 1 | No
| 1862577 | 2025-06-01 | 6:14 | 2025-06-01 | 6:47 | DC6 | DONCASTER | Urban | Asset Failure | HV | 531 | 17478.7677 | 32.9167 | 1 | No
| 1862577 | 2025-06-01 | 6:14 | 2025-06-01 | 7:00 | DC6 | DONCASTER | Urban | Asset Failure | HV | 70 | 3174.5 | 45.35 | 2 | No
| 1862577 | 2025-06-01 | 6:14 | 2025-06-01 | 7:05 | DC6 | DONCASTER | Urban | Asset Failure | HV | 2 | 101.7334 | 50.8667 | 3 | No
| 1862577 | 2025-06-01 | 6:14 | 2025-06-01 | 11:51 | DC6 | DONCASTER | Urban | Asset Failure | HV | 17 | 5726.45 | 336.85 | 4 | No
| 1862617 | 2025-06-01 | 8:58 | 2025-06-01 | 11:53 | NB25 | NORTH BRIGHTON | Urban | Third Party | Other | 1 | 174.7333 | 174.7333 | 1 | No
| 1862619 | 2025-06-01 | 9:00 | 2025-06-01 | 12:38 | HGS23 | HASTINGS | Rural Short | Asset Failure | Distribution substation | 5 | 1090 | 218 | 1 | No
| 1862622 | 2025-06-01 | 9:05 | 2025-06-01 | 14:45 | OE4 | OAKLEIGH EAST | Urban | Asset Failure | LV | 4.56 | 1548.9558 | 339.6833 | 1 | No
| 1862574 | 2025-06-01 | 9:45 | 2025-06-01 | 15:39 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 42 | 14868 | 354 | 1 | No
| 1862666 | 2025-06-01 | 11:41 | 2025-06-01 | 12:04 | SVW55 | SPRINGVALE WEST | Urban | Asset Failure | HV | 313 | 7266.8271 | 23.2167 | 1 | No
| 1862666 | 2025-06-01 | 11:41 | 2025-06-01 | 12:48 | SVW55 | SPRINGVALE WEST | Urban | Asset Failure | HV | 111 | 7437 | 67 | 2 | No
| 1862666 | 2025-06-01 | 11:41 | 2025-06-01 | 12:54 | SVW55 | SPRINGVALE WEST | Urban | Asset Failure | HV | 168 | 12182.8056 | 72.5167 | 3 | No
| 1862666 | 2025-06-01 | 11:41 | 2025-06-01 | 13:08 | SVW55 | SPRINGVALE WEST | Urban | Asset Failure | HV | 119 | 10368.8627 | 87.1333 | 4 | No
| 1862666 | 2025-06-01 | 11:41 | 2025-06-01 | 19:31 | SVW55 | SPRINGVALE WEST | Urban | Asset Failure | HV | 55 | 25810.5815 | 469.2833 | 5 | No
| 1862682 | 2025-06-01 | 12:31 | 2025-06-01 | 14:59 | MGE24 | MULGRAVE | Urban | Unknown | Unknown | 1 | 148.5833 | 148.5833 | 1 | No
| 1862720 | 2025-06-01 | 14:25 | 2025-06-01 | 16:51 | RBD14 | ROSEBUD | Urban | Overloads |  | 23.43 | 3411.408 | 145.6 | 1 | No
| 1862726 | 2025-06-01 | 15:01 | 2025-06-01 | 16:20 | GW7 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 79 | 79 | 1 | No
| 1862739 | 2025-06-01 | 15:57 | 2025-06-01 | 18:27 | LD6 | LYNDALE | Urban | Overloads |  | 1 | 150.0833 | 150.0833 | 1 | No
| 1862752 | 2025-06-01 | 16:56 | 2025-06-01 | 21:17 | CM25 | CHELTENHAM | Urban | Asset Failure | LV | 1 | 261.1833 | 261.1833 | 1 | No
| 1862756 | 2025-06-01 | 18:42 | 2025-06-01 | 22:46 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 1 | 244.6833 | 244.6833 | 1 | No
| 1862770 | 2025-06-01 | 18:52 | 2025-06-01 | 23:50 | MC21 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 297.65 | 297.65 | 1 | No
| 1862776 | 2025-06-01 | 20:39 | 2025-06-01 | 21:07 | EB33 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 27.9333 | 27.9333 | 1 | No
| 1862780 | 2025-06-01 | 21:07 | 2025-06-01 | 22:10 | FSH22 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 63.1167 | 63.1167 | 1 | No
| 1862781 | 2025-06-01 | 21:52 | 2025-07-01 | 0:34 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 162.7833 | 162.7833 | 1 | No
| 1862792 | 2025-07-01 | 6:43 | 2025-07-01 | 7:56 | CDA11 | CLARINDA | Urban | Unknown | Unknown | 75 | 5468.7525 | 72.9167 | 1 | No
| 1862769 | 2025-07-01 | 9:29 | 2025-07-01 | 10:03 | BW21 | BURWOOD | Urban | Asset Failure | LV | 1 | 34.3667 | 34.3667 | 1 | No
| 1862857 | 2025-07-01 | 9:34 | 2025-07-01 | 13:30 | BT15 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 235.0833 | 235.0833 | 1 | No
| 1862912 | 2025-07-01 | 11:17 | 2025-07-01 | 15:50 | EW12 | ELWOOD | Urban | Asset Failure | LV | 1 | 273.1167 | 273.1167 | 1 | No
| 1862918 | 2025-07-01 | 11:38 | 2025-07-01 | 13:16 | BU12 | BULLEEN | Urban | Asset Failure | LV | 1 | 97.7 | 97.7 | 1 | No
| 1862922 | 2025-07-01 | 11:47 | 2025-07-01 | 15:58 | CDA11 | CLARINDA | Urban | Asset Failure | LV | 12.75 | 3205.35 | 251.4 | 1 | No
| 1863007 | 2025-07-01 | 14:19 | 2025-07-01 | 18:10 | MC23 | MORDIALLOC | Urban | Asset Failure | LV | 5 | 1155.3335 | 231.0667 | 1 | No
| 1862989 | 2025-07-01 | 15:28 | 2025-07-01 | 21:18 | EL22 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 350.7 | 350.7 | 1 | No
| 1863001 | 2025-07-01 | 16:28 | 2025-07-01 | 22:05 | BT16 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 337 | 337 | 1 | No
| 1863011 | 2025-07-01 | 17:08 | 2025-07-01 | 21:28 | DC1 | DONCASTER | Urban | Overloads |  | 1 | 260.9 | 260.9 | 1 | No
| 1863019 | 2025-07-01 | 17:24 | 2025-07-01 | 20:18 | NW23 | NUNAWADING | Urban | Overloads |  | 1 | 174.7 | 174.7 | 1 | No
| 1863033 | 2025-07-01 | 18:35 | 2025-07-01 | 19:21 | WD14 | WEST DONCASTER | Urban | Third Party | Vehicle Impact | 73 | 3358 | 46 | 1 | No
| 1863052 | 2025-07-01 | 20:25 | 2025-07-01 | 23:25 | SS11 | SPRINGVALE SOUTH | Urban | Overloads |  | 5.28 | 950.136 | 179.95 | 1 | No
| 1863055 | 2025-07-01 | 21:22 | 2025-07-01 | 22:17 | EB32 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 55.0167 | 55.0167 | 1 | No
| 1863062 | 2025-07-01 | 22:00 | 2025-08-01 | 0:41 | DN6 | DANDENONG | Urban | Animal | Animal impact | 170.18 | 27322.399 | 160.55 | 1 | No
| 1863069 | 2025-07-01 | 22:17 | 2025-08-01 | 14:30 | DC1 | DONCASTER | Urban | Asset Failure | LV | 1 | 972.2667 | 972.2667 | 1 | No
| 1863058 | 2025-08-01 | 1:15 | 2025-08-01 | 2:15 | MC23 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 60 | 60 | 1 | No
| 1863086 | 2025-08-01 | 4:29 | 2025-08-01 | 7:20 | DC3 | DONCASTER | Urban | Animal | Animal impact | 77 | 13134.9141 | 170.5833 | 1 | No
| 1863102 | 2025-08-01 | 6:46 | 2025-08-01 | 10:20 | NO32 | NOTTING HILL | Urban | Third Party | Other | 8 | 1707.2 | 213.4 | 1 | No
| 1863118 | 2025-08-01 | 8:02 | 2025-08-01 | 9:22 | OR25 | ORMOND | Urban | Asset Failure | LV | 1 | 79.05 | 79.05 | 1 | No
| 1863126 | 2025-08-01 | 8:31 | 2025-08-01 | 10:20 | RWT34 | RINGWOOD | Urban | Network Business | Switching and protection error | 1 | 109.9667 | 109.9667 | 1 | No
| 1863147 | 2025-08-01 | 8:45 | 2025-08-01 | 9:24 | WD26 | WEST DONCASTER | Urban | Third Party |  | 11.55 | 444.4821 | 38.4833 | 1 | No
| 1863177 | 2025-08-01 | 9:45 | 2025-08-01 | 12:21 | SK1 | ST. KILDA | Urban | Asset Failure | LV | 1 | 155.3 | 155.3 | 1 | No
| 1863211 | 2025-08-01 | 11:45 | 2025-08-01 | 11:50 | EB11 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 4.9167 | 4.9167 | 1 | No
| 1863230 | 2025-08-01 | 13:03 | 2025-08-01 | 14:00 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 5 | 285 | 57 | 1 | No
| 1863256 | 2025-08-01 | 14:11 | 2025-08-01 | 16:20 | SS11 | SPRINGVALE SOUTH | Urban | Overloads |  | 5.28 | 677.5998 | 128.3333 | 1 | No
| 1863281 | 2025-08-01 | 15:45 | 2025-08-01 | 18:00 | EL25 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 134.6167 | 134.6167 | 1 | No
| 1863094 | 2025-08-01 | 17:48 | 2025-08-01 | 19:35 | NW14 | NUNAWADING | Urban | Unknown | Unknown | 1 | 107.7 | 107.7 | 1 | No
| 1863305 | 2025-08-01 | 17:55 | 2025-08-01 | 20:31 | SV34 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 155.75 | 155.75 | 1 | No
| 1863307 | 2025-08-01 | 18:41 | 2025-08-01 | 20:40 | EL23 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 119 | 119 | 1 | No
| 1863309 | 2025-08-01 | 18:48 | 2025-08-01 | 20:10 | EW9 | ELWOOD | Urban | Overloads |  | 53.13 | 4334.5207 | 81.5833 | 1 | No
| 1863329 | 2025-08-01 | 23:02 | 2025-09-01 | 3:18 | EB11 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 255.3333 | 255.3333 | 1 | No
| 1863331 | 2025-08-01 | 23:31 | 2025-09-01 | 2:00 | NP11 | NOBLE PARK | Urban | Third Party | Other | 6 | 888.4002 | 148.0667 | 1 | No
| 1863331 | 2025-08-01 | 23:31 | 2025-09-01 | 2:13 | NP11 | NOBLE PARK | Urban | Third Party | Other | 1 | 161.1833 | 161.1833 | 2 | No
| 1863331 | 2025-08-01 | 23:31 | 2025-09-01 | 8:08 | NP11 | NOBLE PARK | Urban | Third Party | Other | 2 | 1032.3334 | 516.1667 | 3 | No
| 1863332 | 2025-08-01 | 23:59 | 2025-09-01 | 0:44 | RBD11 | ROSEBUD | Urban | Animal | Animal impact | 71.69 | 3173.4797 | 44.2667 | 1 | No
| 1863346 | 2025-09-01 | 2:02 | 2025-09-01 | 4:15 | OR33 | ORMOND | Urban | Third Party | Other | 1 | 132.1167 | 132.1167 | 1 | No
| 1863427 | 2025-09-01 | 9:39 | 2025-09-01 | 10:05 | RBD13 | ROSEBUD | Urban | Other | XXX | 1 | 25.4167 | 25.4167 | 1 | No
| 1863546 | 2025-09-01 | 10:25 | 2025-09-01 | 18:00 | HT4 | HEATHERTON | Urban | Third Party | Vehicle Impact | 3 | 1362.9501 | 454.3167 | 1 | No
| 1863509 | 2025-09-01 | 13:46 | 2025-09-01 | 18:00 | BT12 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 253.3833 | 253.3833 | 1 | No
| 1863524 | 2025-09-01 | 14:17 | 2025-09-01 | 17:33 | EM7 | EAST MALVERN | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 390.6334 | 195.3167 | 1 | No
| 1863528 | 2025-09-01 | 14:38 | 2025-09-01 | 16:58 | MC23 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 140.1667 | 140.1667 | 1 | No
| 1863566 | 2025-09-01 | 16:23 | 2025-09-01 | 19:01 | GW6 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 158.2833 | 158.2833 | 1 | No
| 1863606 | 2025-09-01 | 21:26 | 2025-09-01 | 23:20 | STO23 | SORRENTO | Urban | Overloads |  | 1 | 113.1167 | 113.1167 | 1 | No
| 1863609 | 2025-09-01 | 22:51 | 2025-09-01 | 23:30 | GW5 | GLEN WAVERLEY | Urban | Animal | Animal impact | 932 | 36316.9644 | 38.9667 | 1 | No
| 1863616 | 2025-10-01 | 0:48 | 2025-10-01 | 1:10 | SS11 | SPRINGVALE SOUTH | Urban | Unknown | Unknown | 16 | 352 | 22 | 1 | No
| 1863661 | 2025-10-01 | 9:30 | 2025-10-01 | 10:24 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 53.8833 | 53.8833 | 1 | No
| 1863717 | 2025-10-01 | 15:14 | 2025-10-01 | 18:18 | MC34 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 184.4833 | 184.4833 | 1 | No
| 1863766 | 2025-10-01 | 15:50 | 2025-10-01 | 17:31 | BT22 | BENTLEIGH | Urban | Third Party | Vehicle Impact | 1 | 101.2167 | 101.2167 | 1 | No
| 1863780 | 2025-10-01 | 18:07 | 2025-10-01 | 23:13 | SR21 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 306.35 | 306.35 | 1 | No
| 1863774 | 2025-10-01 | 18:21 | 2025-11-01 | 0:32 | NB32 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 371.4667 | 371.4667 | 1 | No
| 1863763 | 2025-10-01 | 18:34 | 2025-10-01 | 20:56 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 1 | 142.1333 | 142.1333 | 1 | No
| 1863785 | 2025-10-01 | 18:39 | 2025-10-01 | 22:35 | CFD23 | CAULFIELD | Urban | Overloads |  | 1 | 235.8167 | 235.8167 | 1 | No
| 1863789 | 2025-10-01 | 20:02 | 2025-10-01 | 21:51 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 109.1333 | 109.1333 | 1 | No
| 1863788 | 2025-10-01 | 20:27 | 2025-10-01 | 21:08 | EB11 | EAST BURWOOD | Urban | Overloads |  | 1 | 41.1 | 41.1 | 1 | No
| 1863796 | 2025-10-01 | 23:19 | 2025-11-01 | 0:59 | DN22 | DANDENONG | Urban | Animal | Animal impact | 98 | 9777.1366 | 99.7667 | 1 | No
| 1863813 | 2025-11-01 | 1:08 | 2025-11-01 | 2:09 | MGE22 | MULGRAVE | Urban | Animal | Animal impact | 48.24 | 2922.5384 | 60.5833 | 1 | No
| 1863820 | 2025-11-01 | 4:15 | 2025-11-01 | 8:39 | STO21 | SORRENTO | Rural Short | Animal | Animal impact | 11 | 2898.8663 | 263.5333 | 1 | No
| 1863825 | 2025-11-01 | 7:06 | 2025-11-01 | 8:40 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 14.19 | 1327.2375 | 93.5333 | 1 | No
| 1863843 | 2025-11-01 | 10:45 | 2025-11-01 | 12:50 | DMA14 | DROMANA | Urban | Asset Failure | LV | 4.29 | 534.8914 | 124.6833 | 1 | No
| 1863845 | 2025-11-01 | 12:03 | 2025-11-01 | 12:58 | NW21 | NUNAWADING | Urban | Overloads |  | 1 | 55.8167 | 55.8167 | 1 | No
| 1863854 | 2025-11-01 | 13:35 | 2025-11-01 | 15:27 | BT16 | BENTLEIGH | Urban | Overloads |  | 1 | 112.4333 | 112.4333 | 1 | No
| 1863858 | 2025-11-01 | 13:47 | 2025-11-01 | 14:37 | SVW55 | SPRINGVALE WEST | Urban | Animal | Animal impact | 1 | 49.6333 | 49.6333 | 1 | No
| 1863859 | 2025-11-01 | 14:00 | 2025-11-01 | 16:32 | KBH34 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 152.8 | 152.8 | 1 | No
| 1863863 | 2025-11-01 | 14:45 | 2025-11-01 | 15:55 | BH11 | BOX HILL | Urban | Overloads |  | 1 | 70.4 | 70.4 | 1 | No
| 1863864 | 2025-11-01 | 14:57 | 2025-11-01 | 16:43 | MC15 | MORDIALLOC | Urban | Asset Failure | LV | 24.75 | 2605.7617 | 105.2833 | 1 | No
| 1863867 | 2025-11-01 | 15:21 | 2025-11-01 | 16:45 | DMA21 | DROMANA | Urban | Overloads |  | 8 | 665.3336 | 83.1667 | 1 | No
| 1863870 | 2025-11-01 | 16:10 | 2025-11-01 | 17:15 | LWN35 | LANGWARRIN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 64.5167 | 64.5167 | 1 | No
| 1863871 | 2025-11-01 | 17:01 | 2025-11-01 | 17:24 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | HV | 663 | 15735.1779 | 23.7333 | 1 | No
| 1863871 | 2025-11-01 | 17:01 | 2025-11-01 | 17:39 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | HV | 766 | 29337.8 | 38.3 | 2 | No
| 1863877 | 2025-11-01 | 17:35 | 2025-11-01 | 19:16 | FSH13 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 41 | 4125.2847 | 100.6167 | 1 | No
| 1863879 | 2025-11-01 | 17:43 | 2025-11-01 | 19:50 | FSH33 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 134 | 16964.4 | 126.6 | 1 | No
| 1863874 | 2025-11-01 | 17:47 | 2025-11-01 | 19:00 | SS11 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 73 | 73 | 1 | No
| 1863885 | 2025-11-01 | 17:59 | 2025-11-01 | 19:55 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 24 | 2778 | 115.75 | 1 | No
| 1863887 | 2025-11-01 | 18:15 | 2025-11-01 | 20:15 | EL23 | ELSTERNWICK | Urban | Overloads |  | 16.17 | 1933.3935 | 119.5667 | 1 | No
| 1863894 | 2025-11-01 | 19:04 | 2025-11-01 | 20:30 | HGS23 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 86 | 86 | 1 | No
| 1863902 | 2025-11-01 | 21:34 | 2025-11-01 | 22:37 | NO5 | NOTTING HILL | Urban | Third Party | Other | 2 | 126 | 63 | 1 | No
| 1863933 | 2025-12-01 | 7:46 | 2025-12-01 | 9:32 | DN25 | DANDENONG | Urban | Asset Failure | LV | 8.91 | 940.3017 | 105.5333 | 1 | No
| 1863912 | 2025-12-01 | 9:19 | 2025-12-01 | 10:37 | OAK33 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 78.3833 | 78.3833 | 1 | No
| 1863920 | 2025-12-01 | 11:41 | 2025-12-01 | 13:26 | DN11 | DANDENONG | Urban | Asset Failure | LV | 1 | 105.3667 | 105.3667 | 1 | No
| 1864007 | 2025-12-01 | 12:23 | 2025-12-01 | 23:55 | LWN21 | LANGWARRIN | Rural Short | Overloads |  | 4 | 2765.1332 | 691.2833 | 1 | No
| 1863969 | 2025-12-01 | 12:25 | 2025-12-01 | 14:13 | FSH13 | FRANKSTON SOUTH | Urban | Weather |  | 427 | 45952.3309 | 107.6167 | 1 | No
| 1863981 | 2025-12-01 | 12:33 | 2025-12-01 | 17:32 | HT4 | HEATHERTON | Urban | Weather |  | 109.21 | 32624.6637 | 298.7333 | 1 | No
| 1864186 | 2025-12-01 | 12:33 | 2025-12-01 | 22:09 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 3 | 1727.3499 | 575.7833 | 1 | No
| 1863982 | 2025-12-01 | 12:34 | 2025-12-01 | 13:36 | EM3 | EAST MALVERN | Urban | Asset Failure | Distribution substation | 62.98 | 3880.6198 | 61.6167 | 1 | No
| 1863978 | 2025-12-01 | 12:35 | 2025-12-01 | 13:58 | OAK24 | OAKLEIGH | Urban | Weather |  | 2 | 166.2666 | 83.1333 | 1 | No
| 1863978 | 2025-12-01 | 12:35 | 2025-12-01 | 14:22 | OAK24 | OAKLEIGH | Urban | Weather |  | 433 | 46634.1 | 107.7 | 2 | No
| 1863980 | 2025-12-01 | 12:37 | 13/01/2025 | 0:01 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 11 | 7521.25 | 683.75 | 1 | No
| 1864045 | 2025-12-01 | 12:44 | 2025-12-01 | 16:45 | HGS23 | HASTINGS | Rural Short | Weather |  | 21 | 5050.5 | 240.5 | 1 | No
| 1864011 | 2025-12-01 | 12:47 | 2025-12-01 | 18:51 | EB12 | EAST BURWOOD | Urban | Weather |  | 277 | 100569.4759 | 363.0667 | 1 | No
| 1864003 | 2025-12-01 | 12:48 | 2025-12-01 | 14:08 | NW32 | NUNAWADING | Urban | Weather |  | 793 | 63849.7431 | 80.5167 | 1 | No
| 1864004 | 2025-12-01 | 12:48 | 2025-12-01 | 13:00 | NW21 | NUNAWADING | Urban | Weather |  | 2018 | 25292.1994 | 12.5333 | 1 | No
| 1864004 | 2025-12-01 | 12:48 | 2025-12-01 | 13:23 | NW21 | NUNAWADING | Urban | Weather |  | 497 | 17610.3501 | 35.4333 | 2 | No
| 1864004 | 2025-12-01 | 12:48 | 2025-12-01 | 14:08 | NW21 | NUNAWADING | Urban | Weather |  | 570 | 45561.981 | 79.9333 | 3 | No
| 1864006 | 2025-12-01 | 12:49 | 2025-12-01 | 14:22 | OAK23 | OAKLEIGH | Urban | Weather |  | 1 | 92.8167 | 92.8167 | 1 | No
| 1864015 | 2025-12-01 | 12:50 | 2025-12-01 | 16:04 | MR12 | MOORABBIN | Urban | Asset Failure | LV | 3 | 581.4501 | 193.8167 | 1 | No
| 1864021 | 2025-12-01 | 12:54 | 2025-12-01 | 20:18 | LD4 | LYNDALE | Urban | Weather |  | 11.39 | 5060.9563 | 444.3333 | 1 | No
| 1864017 | 2025-12-01 | 12:55 | 2025-12-01 | 21:52 | OAK32 | OAKLEIGH | Urban | Unknown | Unknown | 1 | 537.3 | 537.3 | 1 | No
| 1864026 | 2025-12-01 | 12:57 | 2025-12-01 | 17:43 | LD6 | LYNDALE | Urban | Weather |  | 62 | 17685.5 | 285.25 | 1 | No
| 1864030 | 2025-12-01 | 13:04 | 2025-12-01 | 17:06 | LD6 | LYNDALE | Urban | Weather |  | 25.41 | 6160.2302 | 242.4333 | 1 | No
| 1864033 | 2025-12-01 | 13:06 | 2025-12-01 | 15:30 | NW13 | NUNAWADING | Urban | Weather |  | 66 | 9484.2 | 143.7 | 1 | No
| 1864037 | 2025-12-01 | 13:11 | 2025-12-01 | 15:20 | MGE23 | MULGRAVE | Urban | Third Party | Other | 1 | 129.3333 | 129.3333 | 1 | No
| 1864201 | 2025-12-01 | 13:17 | 13/01/2025 | 2:18 | HGS23 | HASTINGS | Rural Short | Weather |  | 1 | 780.3167 | 780.3167 | 1 | No
| 1864065 | 2025-12-01 | 13:18 | 2025-12-01 | 22:15 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 4 | 2145.6668 | 536.4167 | 1 | No
| 1864029 | 2025-12-01 | 13:25 | 2025-12-01 | 15:28 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 2.01 | 248.1681 | 123.4667 | 1 | No
| 1864245 | 2025-12-01 | 13:37 | 13/01/2025 | 8:14 | HGS23 | HASTINGS | Rural Short | Weather |  | 1 | 1117 | 1117 | 1 | No
| 1864071 | 2025-12-01 | 14:02 | 2025-12-01 | 16:31 | SR24 | SANDRINGHAM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 148.4 | 148.4 | 1 | No
| 1864076 | 2025-12-01 | 14:21 | 2025-12-01 | 15:36 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 75 | 5643.75 | 75.25 | 1 | No
| 1864076 | 2025-12-01 | 14:21 | 2025-12-01 | 15:38 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 95 | 7340.3365 | 77.2667 | 2 | No
| 1864076 | 2025-12-01 | 14:21 | 2025-12-01 | 15:45 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 28 | 2362.2676 | 84.3667 | 3 | No
| 1864076 | 2025-12-01 | 14:21 | 2025-12-01 | 16:06 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 3 | 315.3999 | 105.1333 | 4 | No
| 1864076 | 2025-12-01 | 14:21 | 2025-12-01 | 16:08 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 82 | 8737.1 | 106.55 | 5 | No
| 1864076 | 2025-12-01 | 14:21 | 2025-12-01 | 16:27 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 119 | 15035.65 | 126.35 | 6 | No
| 1864076 | 2025-12-01 | 14:21 | 2025-12-01 | 16:41 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 27 | 3774.6 | 139.8 | 7 | No
| 1864076 | 2025-12-01 | 14:21 | 2025-12-01 | 16:48 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 114 | 16706.7 | 146.55 | 8 | No
| 1864076 | 2025-12-01 | 14:21 | 2025-12-01 | 22:26 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 4 | 1940.3332 | 485.0833 | 9 | No
| 1864094 | 2025-12-01 | 15:18 | 2025-12-01 | 17:25 | LD7 | LYNDALE | Urban | Third Party | Vehicle Impact | 128 | 16142.9376 | 126.1167 | 1 | No
| 1864098 | 2025-12-01 | 15:25 | 2025-12-01 | 17:11 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 53 | 5618.8851 | 106.0167 | 1 | No
| 1864125 | 2025-12-01 | 17:16 | 13/01/2025 | 2:31 | HGS23 | HASTINGS | Rural Short | Weather |  | 1 | 555.6333 | 555.6333 | 1 | No
| 1864137 | 2025-12-01 | 17:25 | 2025-12-01 | 18:05 | BH22 | BOX HILL | Urban | Weather |  | 5.36 | 209.3975 | 39.0667 | 1 | No
| 1864137 | 2025-12-01 | 17:25 | 2025-12-01 | 18:07 | BH22 | BOX HILL | Urban | Weather |  | 2.68 | 110.7288 | 41.3167 | 2 | No
| 1864137 | 2025-12-01 | 17:25 | 2025-12-01 | 18:07 | BH22 | BOX HILL | Urban | Weather |  | 18.09 | 754.9554 | 41.7333 | 3 | No
| 1864140 | 2025-12-01 | 17:27 | 2025-12-01 | 18:07 | BH22 | BOX HILL | Urban | Weather |  | 14 | 554.1662 | 39.5833 | 1 | No
| 1864145 | 2025-12-01 | 18:03 | 2025-12-01 | 22:09 | BR9 | BEAUMARIS | Urban | Weather |  | 21 | 5164.95 | 245.95 | 1 | No
| 1864151 | 2025-12-01 | 18:18 | 2025-12-01 | 22:05 | BR9 | BEAUMARIS | Urban | Weather |  | 35 | 7928.0845 | 226.5167 | 1 | No
| 1864156 | 2025-12-01 | 18:29 | 2025-12-01 | 18:36 | BR9 | BEAUMARIS | Urban | Weather |  | 454 | 3003.9818 | 6.6167 | 1 | No
| 1864159 | 2025-12-01 | 18:50 | 13/01/2025 | 1:38 | RBD24 | ROSEBUD | Urban | Asset Failure | LV | 1 | 407.25 | 407.25 | 1 | No
| 1864161 | 2025-12-01 | 18:54 | 2025-12-01 | 21:56 | BU25 | BULLEEN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 59 | 10700.6353 | 181.3667 | 1 | No
| 1864168 | 2025-12-01 | 19:30 | 2025-12-01 | 20:00 | LD4 | LYNDALE | Urban | Weather |  | 17 | 509.15 | 29.95 | 1 | No
| 1864168 | 2025-12-01 | 19:30 | 2025-12-01 | 20:05 | LD4 | LYNDALE | Urban | Weather |  | 2 | 69.9666 | 34.9833 | 2 | No
| 1864187 | 2025-12-01 | 22:07 | 13/01/2025 | 0:41 | RBD23 | ROSEBUD | Urban | Weather |  | 124 | 19071.2 | 153.8 | 1 | No
| 1864192 | 2025-12-01 | 22:21 | 2025-12-01 | 23:41 | SV34 | SPRINGVALE | Urban | Animal | Animal impact | 105 | 8413.9965 | 80.1333 | 1 | No
| 1864126 | 2025-12-01 | 22:49 | 13/01/2025 | 3:20 | HGS23 | HASTINGS | Rural Short | Weather |  | 1 | 271.6333 | 271.6333 | 1 | No
| 1864272 | 13/01/2025 | 2:41 | 13/01/2025 | 9:48 | RBD12 | ROSEBUD | Rural Short | Animal | Other | 0.67 | 285.6098 | 426.2833 | 1 | No
| 1864211 | 13/01/2025 | 4:01 | 13/01/2025 | 7:57 | BR9 | BEAUMARIS | Urban | Asset Failure | LV | 18.81 | 4439.16 | 236 | 1 | No
| 1864206 | 13/01/2025 | 4:02 | 13/01/2025 | 7:13 | FSH31 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 36.18 | 6880.8318 | 190.1833 | 1 | No
| 1864217 | 13/01/2025 | 7:16 | 13/01/2025 | 15:57 | DVY33 | DANDENONG VALLEY | Urban | Third Party | Other | 9 | 4695.3 | 521.7 | 1 | No
| 1864225 | 13/01/2025 | 7:20 | 13/01/2025 | 12:30 | LWN21 | LANGWARRIN | Rural Short | Animal | Other | 23.45 | 7267.5466 | 309.9167 | 1 | No
| 1864314 | 13/01/2025 | 9:09 | 13/01/2025 | 11:40 | CRM35 | CARRUM | Urban | Overloads |  | 1 | 150.3333 | 150.3333 | 1 | No
| 1864281 | 13/01/2025 | 11:13 | 13/01/2025 | 13:08 | RWT12 | RINGWOOD | Urban | Asset Failure | LV | 6 | 690.1998 | 115.0333 | 1 | No
| 1864313 | 13/01/2025 | 11:25 | 13/01/2025 | 15:36 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 250.6333 | 250.6333 | 1 | No
| 1864317 | 13/01/2025 | 11:35 | 13/01/2025 | 17:00 | STO22 | SORRENTO | Urban | Asset Failure | LV | 1 | 324.1167 | 324.1167 | 1 | No
| 1864342 | 13/01/2025 | 12:58 | 13/01/2025 | 15:15 | NB31 | NORTH BRIGHTON | Urban | Asset Failure | Distribution substation | 29.37 | 4001.6625 | 136.25 | 1 | No
| 1864367 | 13/01/2025 | 14:37 | 13/01/2025 | 18:15 | STO14 | SORRENTO | Rural Short | Overloads |  | 1 | 218 | 218 | 1 | No
| 1864408 | 13/01/2025 | 17:52 | 13/01/2025 | 21:18 | NW23 | NUNAWADING | Urban | Overloads |  | 1 | 206.5833 | 206.5833 | 1 | No
| 1864419 | 13/01/2025 | 18:57 | 13/01/2025 | 23:00 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 2 | 485.2334 | 242.6167 | 1 | No
| 1864413 | 13/01/2025 | 20:31 | 13/01/2025 | 21:44 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 73 | 73 | 1 | No
| 1864453 | 14/01/2025 | 7:25 | 14/01/2025 | 11:30 | MTN32 | MORNINGTON | Rural Short | Unknown | Unknown | 1 | 245 | 245 | 1 | No
| 1864470 | 14/01/2025 | 8:08 | 14/01/2025 | 9:46 | RWT35 | RINGWOOD | Urban | Asset Failure | LV | 1 | 97.0667 | 97.0667 | 1 | No
| 1864516 | 14/01/2025 | 9:17 | 14/01/2025 | 10:01 | HT1 | HEATHERTON | Urban | Asset Failure | LV | 1 | 43.0667 | 43.0667 | 1 | No
| 1864575 | 14/01/2025 | 10:57 | 14/01/2025 | 11:39 | NW11 | NUNAWADING | Urban | Third Party | Other | 1 | 42.1 | 42.1 | 1 | No
| 1864561 | 14/01/2025 | 10:58 | 14/01/2025 | 13:15 | DC5 | DONCASTER | Urban | Asset Failure | LV | 1 | 137 | 137 | 1 | No
| 1864604 | 14/01/2025 | 12:12 | 14/01/2025 | 14:50 | SVW55 | SPRINGVALE WEST | Urban | Overloads |  | 9.57 | 1503.2872 | 157.0833 | 1 | No
| 1864682 | 14/01/2025 | 16:05 | 14/01/2025 | 17:33 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 88.5167 | 88.5167 | 1 | No
| 1864672 | 14/01/2025 | 16:25 | 14/01/2025 | 16:55 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 30.1833 | 30.1833 | 1 | No
| 1864697 | 14/01/2025 | 17:05 | 14/01/2025 | 19:32 | CFD26 | CAULFIELD | Urban | Asset Failure | HV | 71 | 10412.15 | 146.65 | 1 | No
| 1864690 | 14/01/2025 | 17:11 | 14/01/2025 | 20:45 | DC10 | DONCASTER | Urban | Asset Failure | LV | 1 | 214.0333 | 214.0333 | 1 | No
| 1864707 | 14/01/2025 | 18:55 | 14/01/2025 | 20:55 | K25 | GARDINER | Urban | Overloads |  | 1 | 120.7833 | 120.7833 | 1 | No
| 1864719 | 14/01/2025 | 20:10 | 14/01/2025 | 21:45 | OR24 | ORMOND | Urban | Overloads |  | 30.03 | 2835.3335 | 94.4167 | 1 | No
| 1864726 | 14/01/2025 | 22:26 | 15/01/2025 | 0:10 | SV16 | SPRINGVALE | Urban | Animal | Animal impact | 2.68 | 276.844 | 103.3 | 1 | No
| 1864729 | 14/01/2025 | 22:44 | 15/01/2025 | 0:02 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 77.65 | 77.65 | 1 | No
| 1864732 | 14/01/2025 | 22:56 | 14/01/2025 | 23:03 | NW13 | NUNAWADING | Urban | Third Party | Other | 32 | 214.9344 | 6.7167 | 1 | No
| 1864740 | 15/01/2025 | 6:58 | 15/01/2025 | 7:05 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 267 | 2069.25 | 7.75 | 1 | No
| 1864740 | 15/01/2025 | 6:58 | 15/01/2025 | 7:26 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 693 | 19658.1231 | 28.3667 | 2 | No
| 1864740 | 15/01/2025 | 6:58 | 15/01/2025 | 7:42 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 322 | 14151.9 | 43.95 | 3 | No
| 1864740 | 15/01/2025 | 6:58 | 15/01/2025 | 9:05 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 19 | 2411.7327 | 126.9333 | 4 | No
| 1864742 | 15/01/2025 | 7:08 | 15/01/2025 | 16:19 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 550.55 | 550.55 | 1 | No
| 1864747 | 15/01/2025 | 7:24 | 15/01/2025 | 9:05 | DC3 | DONCASTER | Urban | Animal | Animal impact | 1 | 100.7 | 100.7 | 1 | No
| 1864791 | 15/01/2025 | 8:47 | 15/01/2025 | 10:01 | M35 | MENTONE | Urban | Asset Failure | LV | 1 | 73.8333 | 73.8333 | 1 | No
| 1864676 | 15/01/2025 | 8:56 | 15/01/2025 | 11:30 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 154.9167 | 154.9167 | 1 | No
| 1864815 | 15/01/2025 | 9:28 | 15/01/2025 | 12:11 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 163.2667 | 163.2667 | 1 | No
| 1864837 | 15/01/2025 | 10:58 | 15/01/2025 | 15:02 | DN22 | DANDENONG | Urban | Overloads |  | 1 | 244 | 244 | 1 | No
| 1864901 | 15/01/2025 | 12:21 | 15/01/2025 | 15:29 | NB21 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 188.5667 | 188.5667 | 1 | No
| 1864921 | 15/01/2025 | 12:47 | 15/01/2025 | 14:25 | EM3 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 98.8167 | 98.8167 | 1 | No
| 1864948 | 15/01/2025 | 13:54 | 15/01/2025 | 14:03 | HT9 | HEATHERTON | Urban | Third Party | Vehicle Impact | 7.92 | 69.9597 | 8.8333 | 1 | No
| 1864974 | 15/01/2025 | 15:37 | 15/01/2025 | 18:00 | LD7 | LYNDALE | Urban | Asset Failure | LV | 1 | 142.6167 | 142.6167 | 1 | No
| 1864883 | 15/01/2025 | 18:29 | 16/01/2025 | 0:36 | LWN32 | LANGWARRIN | Rural Short | Asset Failure | LV | 33 | 12111 | 367 | 1 | No
| 1864997 | 15/01/2025 | 19:31 | 15/01/2025 | 21:04 | SVW42 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 92.1667 | 92.1667 | 1 | No
| 1864998 | 15/01/2025 | 19:53 | 16/01/2025 | 2:36 | DMA12 | DROMANA | Urban | Asset Failure | LV | 52 | 20956 | 403 | 1 | No
| 1865022 | 15/01/2025 | 23:25 | 16/01/2025 | 0:40 | DC3 | DONCASTER | Urban | Asset Failure | HV | 0.67 | 49.8927 | 74.4667 | 1 | No
| 1865030 | 16/01/2025 | 0:37 | 16/01/2025 | 2:15 | HGS33 | HASTINGS | Rural Short | Unknown | Unknown | 138.02 | 13514.4629 | 97.9167 | 1 | No
| 1865042 | 16/01/2025 | 5:19 | 16/01/2025 | 6:46 | GW11 | GLEN WAVERLEY | Urban | Third Party | Other | 1 | 86.9 | 86.9 | 1 | No
| 1865057 | 16/01/2025 | 7:41 | 16/01/2025 | 13:30 | FSH12 | FRANKSTON SOUTH | Rural Short | Third Party | Vehicle Impact | 11 | 3836.0663 | 348.7333 | 1 | No
| 1865123 | 16/01/2025 | 9:33 | 16/01/2025 | 13:30 | FSH32 | FRANKSTON SOUTH | Rural Short | Third Party | Vehicle Impact | 4 | 946.1332 | 236.5333 | 1 | No
| 1865171 | 16/01/2025 | 11:01 | 16/01/2025 | 11:56 | LWN35 | LANGWARRIN | Urban | Unknown | Unknown | 1 | 54.0333 | 54.0333 | 1 | No
| 1865226 | 16/01/2025 | 13:18 | 16/01/2025 | 15:42 | LWN21 | LANGWARRIN | Rural Short | Unknown | Unknown | 1 | 144.25 | 144.25 | 1 | No
| 1865224 | 16/01/2025 | 13:34 | 16/01/2025 | 19:11 | NB35 | NORTH BRIGHTON | Urban | Third Party | Vehicle Impact | 1 | 337 | 337 | 1 | No
| 1865273 | 16/01/2025 | 15:41 | 16/01/2025 | 17:56 | K21 | GARDINER | Urban | Asset Failure | LV | 7 | 949.55 | 135.65 | 1 | No
| 1865277 | 16/01/2025 | 15:56 | 16/01/2025 | 16:28 | EM7 | EAST MALVERN | Urban | Asset Failure | LV | 3 | 95.6499 | 31.8833 | 1 | No
| 1865266 | 16/01/2025 | 16:40 | 16/01/2025 | 19:31 | GW4 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 171.1667 | 171.1667 | 1 | No
| 1865283 | 16/01/2025 | 16:45 | 16/01/2025 | 18:30 | HGS22 | HASTINGS | Rural Short | Other | XXX | 1 | 104.2333 | 104.2333 | 1 | No
| 1865306 | 16/01/2025 | 23:04 | 16/01/2025 | 23:52 | NP34 | NOBLE PARK | Urban | Animal | Animal impact | 81 | 3852.9027 | 47.5667 | 1 | No
| 1865306 | 16/01/2025 | 23:04 | 16/01/2025 | 23:53 | NP34 | NOBLE PARK | Urban | Animal | Animal impact | 42 | 2076.9 | 49.45 | 2 | No
| 1865312 | 17/01/2025 | 1:46 | 17/01/2025 | 1:54 | NW23 | NUNAWADING | Urban | Other | XXX | 1 | 7.2667 | 7.2667 | 1 | No
| 1865314 | 17/01/2025 | 4:22 | 17/01/2025 | 5:17 | OR24 | ORMOND | Urban | Animal | Animal impact | 116.58 | 6351.6631 | 54.4833 | 1 | No
| 1865323 | 17/01/2025 | 7:17 | 17/01/2025 | 9:32 | M13 | MENTONE | Urban | Asset Failure | LV | 1 | 134.85 | 134.85 | 1 | No
| 1865219 | 17/01/2025 | 9:09 | 17/01/2025 | 11:30 | EW1 | ELWOOD | Urban | Unknown | Unknown | 1 | 141 | 141 | 1 | No
| 1865396 | 17/01/2025 | 9:49 | 17/01/2025 | 12:04 | RBD12 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 134.3667 | 134.3667 | 1 | No
| 1865463 | 17/01/2025 | 11:28 | 17/01/2025 | 16:20 | MR33 | MOORABBIN | Urban | Asset Failure | LV | 1 | 291.55 | 291.55 | 1 | No
| 1865530 | 17/01/2025 | 13:34 | 17/01/2025 | 16:31 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 6.93 | 1222.1055 | 176.35 | 1 | No
| 1865545 | 17/01/2025 | 14:30 | 17/01/2025 | 18:14 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 1 | 223.9333 | 223.9333 | 1 | No
| 1865561 | 17/01/2025 | 16:02 | 17/01/2025 | 17:03 | DC2 | DONCASTER | Urban | Asset Failure | LV | 1 | 60.4667 | 60.4667 | 1 | No
| 1865599 | 17/01/2025 | 22:49 | 18/01/2025 | 1:46 | LWN33 | LANGWARRIN | Urban | Third Party |  | 5 | 883.6665 | 176.7333 | 1 | No
| 1865601 | 17/01/2025 | 23:04 | 17/01/2025 | 23:50 | RBD21 | ROSEBUD | Rural Short | Unknown | Unknown | 6 | 273.6 | 45.6 | 1 | No
| 1865607 | 18/01/2025 | 2:51 | 18/01/2025 | 4:56 | M22 | MENTONE | Urban | Third Party | Vehicle Impact | 33 | 4120.05 | 124.85 | 1 | No
| 1865651 | 18/01/2025 | 10:21 | 18/01/2025 | 13:23 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 13 | 2377.4829 | 182.8833 | 1 | No
| 1865598 | 18/01/2025 | 10:33 | 18/01/2025 | 16:31 | FSH32 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 1 | 358 | 358 | 1 | No
| 1865652 | 18/01/2025 | 10:50 | 18/01/2025 | 14:23 | NW21 | NUNAWADING | Urban | Asset Failure | LV | 1 | 212.5 | 212.5 | 1 | No
| 1865631 | 18/01/2025 | 11:00 | 18/01/2025 | 18:07 | MTN24 | MORNINGTON | Rural Short | Animal | Other | 1 | 427 | 427 | 1 | No
| 1865608 | 18/01/2025 | 12:38 | 18/01/2025 | 16:53 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 255.0667 | 255.0667 | 1 | No
| 1865658 | 18/01/2025 | 13:12 | 18/01/2025 | 15:40 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 147.7167 | 147.7167 | 1 | No
| 1865604 | 18/01/2025 | 14:17 | 18/01/2025 | 17:05 | CRM15 | CARRUM | Urban | Asset Failure | LV | 1 | 168 | 168 | 1 | No
| 1865660 | 18/01/2025 | 14:20 | 18/01/2025 | 16:35 | DMA21 | DROMANA | Urban | Third Party | Other | 1 | 134.95 | 134.95 | 1 | No
| 1865664 | 18/01/2025 | 16:29 | 18/01/2025 | 19:34 | OAK21 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 184.9333 | 184.9333 | 1 | No
| 1865679 | 18/01/2025 | 17:39 | 19/01/2025 | 3:53 | MGE12 | MULGRAVE | Urban | Asset Failure | LV | 18 | 11045.1006 | 613.6167 | 1 | No
| 1865694 | 18/01/2025 | 21:02 | 18/01/2025 | 22:06 | NP23 | NOBLE PARK | Urban | Asset Failure | LV | 52 | 3362.6684 | 64.6667 | 1 | No
| 1865696 | 18/01/2025 | 21:55 | 18/01/2025 | 23:15 | MTN35 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 43 | 3431.4 | 79.8 | 1 | No
| 1865703 | 18/01/2025 | 23:00 | 18/01/2025 | 23:13 | GW7 | GLEN WAVERLEY | Urban | Vegetation | Grow-in - NSP responsibility | 1013 | 12814.45 | 12.65 | 1 | No
| 1865703 | 18/01/2025 | 23:00 | 18/01/2025 | 23:17 | GW7 | GLEN WAVERLEY | Urban | Vegetation | Grow-in - NSP responsibility | 1205 | 20726 | 17.2 | 2 | No
| 1865703 | 18/01/2025 | 23:00 | 18/01/2025 | 23:32 | GW7 | GLEN WAVERLEY | Urban | Vegetation | Grow-in - NSP responsibility | 1241 | 39484.5247 | 31.8167 | 3 | No
| 1865703 | 18/01/2025 | 23:00 | 18/01/2025 | 23:56 | GW7 | GLEN WAVERLEY | Urban | Vegetation | Grow-in - NSP responsibility | 619 | 34725.9 | 56.1 | 4 | No
| 1865750 | 19/01/2025 | 11:06 | 19/01/2025 | 12:22 | SR23 | SANDRINGHAM | Urban | Asset Failure | LV | 8 | 612.1336 | 76.5167 | 1 | No
| 1865760 | 19/01/2025 | 12:08 | 19/01/2025 | 13:34 | NW14 | NUNAWADING | Urban | Asset Failure | LV | 1 | 86.2667 | 86.2667 | 1 | No
| 1865746 | 19/01/2025 | 12:16 | 19/01/2025 | 14:15 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 1 | 119 | 119 | 1 | No
| 1865765 | 19/01/2025 | 13:01 | 19/01/2025 | 13:42 | EW9 | ELWOOD | Urban | Asset Failure | LV | 51.81 | 2081.0367 | 40.1667 | 1 | No
| 1865766 | 19/01/2025 | 13:22 | 19/01/2025 | 14:48 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 85.75 | 85.75 | 1 | No
| 1865770 | 19/01/2025 | 13:51 | 19/01/2025 | 18:07 | FSH22 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 255.6 | 255.6 | 1 | No
| 1865777 | 19/01/2025 | 14:37 | 19/01/2025 | 16:45 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 25.41 | 3249.0928 | 127.8667 | 1 | No
| 1865771 | 19/01/2025 | 16:38 | 19/01/2025 | 19:04 | HGS31 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 146.2333 | 146.2333 | 1 | No
| 1865793 | 19/01/2025 | 17:11 | 19/01/2025 | 22:31 | LD2 | LYNDALE | Urban | Asset Failure | LV | 13 | 4147.65 | 319.05 | 1 | No
| 1865800 | 19/01/2025 | 18:33 | 19/01/2025 | 20:42 | NB32 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 129 | 129 | 1 | No
| 1865820 | 19/01/2025 | 19:28 | 19/01/2025 | 20:52 | RBD23 | ROSEBUD | Urban | Asset Failure | HV | 124 | 10413.9292 | 83.9833 | 1 | No
| 1865822 | 19/01/2025 | 19:37 | 19/01/2025 | 20:49 | HGS23 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 71.3833 | 71.3833 | 1 | No
| 1865829 | 19/01/2025 | 20:26 | 19/01/2025 | 21:17 | MGE24 | MULGRAVE | Urban | Asset Failure | LV | 1 | 51.8833 | 51.8833 | 1 | No
| 1865848 | 19/01/2025 | 23:49 | 20/01/2025 | 1:40 | STO21 | SORRENTO | Rural Short | Animal | Animal impact | 6 | 660.7998 | 110.1333 | 1 | No
| 1865852 | 20/01/2025 | 0:20 | 20/01/2025 | 1:45 | EW1 | ELWOOD | Urban | Overloads |  | 1 | 84.8167 | 84.8167 | 1 | No
| 1865857 | 20/01/2025 | 0:55 | 20/01/2025 | 2:43 | LWN33 | LANGWARRIN | Urban | Animal | Animal impact | 3.35 | 359.9016 | 107.4333 | 1 | No
| 1865868 | 20/01/2025 | 2:20 | 20/01/2025 | 3:14 | EB32 | EAST BURWOOD | Urban | Animal | Animal impact | 65.66 | 3510.6235 | 53.4667 | 1 | No
| 1865909 | 20/01/2025 | 7:57 | 20/01/2025 | 9:44 | NP14 | NOBLE PARK | Urban | Animal | Other | 4 | 425.9332 | 106.4833 | 1 | No
| 1865858 | 20/01/2025 | 8:33 | 20/01/2025 | 10:40 | OE15 | OAKLEIGH EAST | Urban | Asset Failure | LV | 1 | 127 | 127 | 1 | No
| 1866006 | 20/01/2025 | 10:43 | 20/01/2025 | 12:30 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 1 | 107 | 107 | 1 | No
| 1865712 | 20/01/2025 | 12:10 | 20/01/2025 | 13:34 | K37 | GARDINER | Urban | Asset Failure | LV | 89 | 7476 | 84 | 1 | No
| 1866075 | 20/01/2025 | 14:54 | 20/01/2025 | 20:29 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 335.6167 | 335.6167 | 1 | No
| 1866038 | 20/01/2025 | 15:24 | 20/01/2025 | 18:19 | BT16 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 175.45 | 175.45 | 1 | No
| 1866131 | 20/01/2025 | 15:58 | 20/01/2025 | 18:34 | CFD22 | CAULFIELD | Urban | Asset Failure | LV | 126 | 19721.1042 | 156.5167 | 1 | No
| 1866158 | 20/01/2025 | 20:11 | 20/01/2025 | 21:40 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 89.1333 | 89.1333 | 1 | No
| 1866160 | 20/01/2025 | 20:30 | 20/01/2025 | 21:19 | RWT23 | RINGWOOD | Urban | Unknown | Unknown | 1 | 48.7167 | 48.7167 | 1 | No
| 1866166 | 20/01/2025 | 21:20 | 20/01/2025 | 22:51 | RBD24 | ROSEBUD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 90.7333 | 90.7333 | 1 | No
| 1866172 | 20/01/2025 | 23:04 | 21/01/2025 | 0:31 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | Distribution substation | 15 | 1299 | 86.6 | 1 | No
| 1866182 | 21/01/2025 | 0:09 | 21/01/2025 | 0:53 | K21 | GARDINER | Urban | Overloads |  | 73 | 3142.65 | 43.05 | 1 | No
| 1866214 | 21/01/2025 | 7:40 | 21/01/2025 | 8:26 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 45.95 | 45.95 | 1 | No
| 1866265 | 21/01/2025 | 8:34 | 21/01/2025 | 9:46 | EB14 | EAST BURWOOD | Urban | Third Party | Other | 1 | 72 | 72 | 1 | No
| 1866286 | 21/01/2025 | 9:05 | 21/01/2025 | 9:55 | DC2 | DONCASTER | Urban | Asset Failure | LV | 9.9 | 488.3997 | 49.3333 | 1 | No
| 1866347 | 21/01/2025 | 10:22 | 21/01/2025 | 13:35 | DN7 | DANDENONG | Urban | Asset Failure | LV | 1 | 192.2667 | 192.2667 | 1 | No
| 1866337 | 21/01/2025 | 10:45 | 21/01/2025 | 12:52 | K33 | GARDINER | Urban | Asset Failure | LV | 1 | 127.6667 | 127.6667 | 1 | No
| 1866351 | 21/01/2025 | 10:46 | 21/01/2025 | 13:11 | BU14 | BULLEEN | Urban | Third Party | Other | 71 | 10306.8357 | 145.1667 | 1 | No
| 1866453 | 21/01/2025 | 14:03 | 21/01/2025 | 15:00 | SV20 | SPRINGVALE | Urban | Overloads |  | 1 | 56.3167 | 56.3167 | 1 | No
| 1866459 | 21/01/2025 | 14:15 | 21/01/2025 | 14:43 | KBH32 | KEYSBOROUGH | Urban | Overloads |  | 13.2 | 364.98 | 27.65 | 1 | No
| 1866433 | 21/01/2025 | 14:54 | 21/01/2025 | 15:54 | SS23 | SPRINGVALE SOUTH | Urban | Overloads |  | 1 | 60.9167 | 60.9167 | 1 | No
| 1866499 | 21/01/2025 | 17:01 | 21/01/2025 | 18:33 | STO22 | SORRENTO | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 10 | 919.5 | 91.95 | 1 | No
| 1866497 | 21/01/2025 | 17:03 | 21/01/2025 | 19:35 | STO13 | SORRENTO | Urban | Asset Failure | LV | 2 | 304.5 | 152.25 | 1 | No
| 1866530 | 21/01/2025 | 20:23 | 21/01/2025 | 20:29 | BH23 | BOX HILL | Urban | Asset Failure | HV | 124 | 723.3292 | 5.8333 | 1 | No
| 1866536 | 21/01/2025 | 20:54 | 21/01/2025 | 22:23 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 88.0833 | 88.0833 | 1 | No
| 1866551 | 21/01/2025 | 23:46 | 22/01/2025 | 8:33 | BT13 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 526.3333 | 526.3333 | 1 | No
| 1866563 | 22/01/2025 | 4:24 | 22/01/2025 | 6:20 | FSH34 | FRANKSTON SOUTH | Urban | Overloads |  | 4.95 | 569.9098 | 115.1333 | 1 | No
| 1866569 | 22/01/2025 | 5:31 | 22/01/2025 | 8:44 | NP24 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 193.25 | 193.25 | 1 | No
| 1866752 | 22/01/2025 | 12:26 | 22/01/2025 | 16:10 | CFD16 | CAULFIELD | Urban | Third Party | Other | 1 | 223.8833 | 223.8833 | 1 | No
| 1866828 | 22/01/2025 | 15:26 | 23/01/2025 | 14:00 | KBH31 | KEYSBOROUGH | Urban | Third Party | Vehicle Impact | 7 | 9476.25 | 1353.75 | 1 | No
| 1866832 | 22/01/2025 | 15:46 | 22/01/2025 | 17:31 | DN24 | DANDENONG | Urban | Asset Failure | LV | 1 | 104.4167 | 104.4167 | 1 | No
| 1866839 | 22/01/2025 | 16:48 | 22/01/2025 | 19:21 | MR12 | MOORABBIN | Urban | Third Party | Other | 1 | 152.3 | 152.3 | 1 | No
| 1866857 | 22/01/2025 | 18:47 | 22/01/2025 | 21:26 | CFD23 | CAULFIELD | Urban | Asset Failure | LV | 1 | 158.2333 | 158.2333 | 1 | No
| 1866861 | 22/01/2025 | 19:35 | 22/01/2025 | 21:06 | STO22 | SORRENTO | Urban | Asset Failure | LV | 1 | 91.75 | 91.75 | 1 | No
| 1867070 | 22/01/2025 | 21:17 | 23/01/2025 | 18:31 | MC14 | MORDIALLOC | Urban | Third Party | Other | 1 | 1274.6833 | 1274.6833 | 1 | No
| 1867070 | 22/01/2025 | 21:17 | 23/01/2025 | 18:32 | MC14 | MORDIALLOC | Urban | Third Party | Other | 1 | 1274.95 | 1274.95 | 2 | No
| 1866881 | 23/01/2025 | 1:53 | 23/01/2025 | 3:18 | STO21 | SORRENTO | Rural Short | Animal | Animal impact | 85 | 7172.5805 | 84.3833 | 1 | No
| 1866884 | 23/01/2025 | 4:56 | 23/01/2025 | 7:06 | DC3 | DONCASTER | Urban | Animal | Animal impact | 22.11 | 2887.9352 | 130.6167 | 1 | No
| 1866940 | 23/01/2025 | 8:24 | 23/01/2025 | 8:44 | RBD23 | ROSEBUD | Urban | Unknown | Unknown | 1 | 19.25 | 19.25 | 1 | No
| 1866999 | 23/01/2025 | 9:34 | 23/01/2025 | 12:22 | SR35 | SANDRINGHAM | Urban | Third Party | Other | 1 | 167.0167 | 167.0167 | 1 | No
| 1866877 | 23/01/2025 | 9:42 | 23/01/2025 | 12:13 | EM10 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 151.9667 | 151.9667 | 1 | No
| 1866963 | 23/01/2025 | 10:23 | 23/01/2025 | 14:00 | STO13 | SORRENTO | Urban | Overloads |  | 1 | 217.1667 | 217.1667 | 1 | No
| 1867040 | 23/01/2025 | 10:36 | 23/01/2025 | 15:40 | HT13 | HEATHERTON | Urban | Asset Failure | LV | 1 | 303.1 | 303.1 | 1 | No
| 1867070 | 23/01/2025 | 11:38 | 23/01/2025 | 18:31 | MC14 | MORDIALLOC | Urban | Third Party | Other | 6 | 2476.6002 | 412.7667 | 1 | No
| 1867121 | 23/01/2025 | 13:53 | 23/01/2025 | 15:31 | SR24 | SANDRINGHAM | Urban | Asset Failure | LV | 1094.11 | 106675.725 | 97.5 | 1 | No
| 1867204 | 23/01/2025 | 18:57 | 23/01/2025 | 21:00 | EW12 | ELWOOD | Urban | Vegetation | Grow-in - Other responsible party | 103 | 12596.9 | 122.3 | 1 | No
| 1867212 | 23/01/2025 | 20:38 | 23/01/2025 | 21:40 | LD6 | LYNDALE | Urban | Asset Failure | HV | 851 | 52648.5617 | 61.8667 | 1 | No
| 1867223 | 23/01/2025 | 23:18 | 24/01/2025 | 0:38 | HGS22 | HASTINGS | Rural Short | Animal | Other | 6 | 477.7998 | 79.6333 | 1 | No
| 1867228 | 24/01/2025 | 1:30 | 24/01/2025 | 8:05 | MC15 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 394.25 | 394.25 | 1 | No
| 1867243 | 24/01/2025 | 2:39 | 24/01/2025 | 15:23 | STO21 | SORRENTO | Rural Short | Asset Failure | HV | 17 | 12995.3661 | 764.4333 | 1 | No
| 1867245 | 24/01/2025 | 2:53 | 24/01/2025 | 4:00 | NO32 | NOTTING HILL | Urban | Animal | Animal impact | 599 | 39733.6467 | 66.3333 | 1 | No
| 1867261 | 24/01/2025 | 6:40 | 24/01/2025 | 8:44 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1.75 | 216.1542 | 123.5167 | 1 | No
| 1867289 | 24/01/2025 | 8:12 | 24/01/2025 | 10:28 | K21 | GARDINER | Urban | Unknown | Unknown | 1 | 136.3833 | 136.3833 | 1 | No
| 1867374 | 24/01/2025 | 10:32 | 24/01/2025 | 16:01 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 328.7667 | 328.7667 | 1 | No
| 1867435 | 24/01/2025 | 12:30 | 24/01/2025 | 15:35 | OAK21 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 184.3167 | 184.3167 | 1 | No
| 1867446 | 24/01/2025 | 12:49 | 24/01/2025 | 14:31 | FTN14 | FRANKSTON | Urban | Third Party | Other | 1 | 102.2833 | 102.2833 | 1 | No
| 1867464 | 24/01/2025 | 13:33 | 24/01/2025 | 17:07 | MTN35 | MORNINGTON | Rural Short | Asset Failure | LV | 13.53 | 2882.7925 | 213.0667 | 1 | No
| 1867327 | 24/01/2025 | 16:00 | 24/01/2025 | 19:50 | DVY14 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 230 | 230 | 1 | No
| 1867605 | 25/01/2025 | 3:10 | 25/01/2025 | 3:54 | NB26 | NORTH BRIGHTON | Urban | Asset Failure | HV | 410.71 | 18071.24 | 44 | 1 | No
| 1867542 | 25/01/2025 | 3:54 | 25/01/2025 | 4:51 | NB26 | NORTH BRIGHTON | Urban | Asset Failure | HV | 228 | 13011.2076 | 57.0667 | 1 | No
| 1867542 | 25/01/2025 | 3:54 | 25/01/2025 | 5:13 | NB26 | NORTH BRIGHTON | Urban | Asset Failure | HV | 385 | 30639.5705 | 79.5833 | 2 | No
| 1867542 | 25/01/2025 | 3:54 | 25/01/2025 | 9:40 | NB26 | NORTH BRIGHTON | Urban | Asset Failure | HV | 61 | 21155.8187 | 346.8167 | 3 | No
| 1867542 | 25/01/2025 | 3:54 | 25/01/2025 | 9:50 | NB26 | NORTH BRIGHTON | Urban | Asset Failure | HV | 19 | 6769.0673 | 356.2667 | 4 | No
| 1867542 | 25/01/2025 | 3:54 | 25/01/2025 | 9:59 | NB26 | NORTH BRIGHTON | Urban | Asset Failure | HV | 86 | 31395.7362 | 365.0667 | 5 | No
| 1867542 | 25/01/2025 | 3:54 | 25/01/2025 | 10:34 | NB26 | NORTH BRIGHTON | Urban | Asset Failure | HV | 112 | 44893.3296 | 400.8333 | 6 | No
| 1867628 | 25/01/2025 | 14:06 | 25/01/2025 | 15:05 | DC10 | DONCASTER | Urban | Asset Failure | LV | 1 | 58.9167 | 58.9167 | 1 | No
| 1867636 | 25/01/2025 | 15:43 | 25/01/2025 | 22:50 | LD5 | LYNDALE | Urban | Third Party | Other | 8 | 3410.5336 | 426.3167 | 1 | No
| 1867665 | 25/01/2025 | 19:31 | 25/01/2025 | 22:19 | RWT34 | RINGWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 167.9667 | 167.9667 | 1 | No
| 1867667 | 25/01/2025 | 19:37 | 25/01/2025 | 22:32 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 174.9667 | 174.9667 | 1 | No
| 1867673 | 25/01/2025 | 22:33 | 25/01/2025 | 23:22 | EB21 | EAST BURWOOD | Urban | Animal | Animal impact | 58.29 | 2829.0061 | 48.5333 | 1 | No
| 1867682 | 26/01/2025 | 5:15 | 26/01/2025 | 8:22 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 186.75 | 186.75 | 1 | No
| 1867710 | 26/01/2025 | 13:50 | 26/01/2025 | 16:00 | CRM23 | CARRUM | Urban | Asset Failure | HV | 19 | 2470 | 130 | 1 | No
| 1867714 | 26/01/2025 | 14:11 | 26/01/2025 | 14:54 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 43.0167 | 43.0167 | 1 | No
| 1867708 | 26/01/2025 | 15:36 | 26/01/2025 | 18:44 | DN10 | DANDENONG | Urban | Asset Failure | LV | 1 | 188.2333 | 188.2333 | 1 | No
| 1867721 | 26/01/2025 | 16:20 | 26/01/2025 | 20:08 | EW1 | ELWOOD | Urban | Asset Failure | LV | 1 | 228.1 | 228.1 | 1 | No
| 1867702 | 26/01/2025 | 18:58 | 26/01/2025 | 19:52 | OAK26 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 54.1 | 54.1 | 1 | No
| 1867737 | 26/01/2025 | 20:47 | 26/01/2025 | 22:53 | MGE24 | MULGRAVE | Urban | Third Party | Other | 13 | 1637.1329 | 125.9333 | 1 | No
| 1867779 | 27/01/2025 | 11:26 | 27/01/2025 | 14:23 | DN13 | DANDENONG | Urban | Asset Failure | LV | 1 | 177.6 | 177.6 | 1 | No
| 1867765 | 27/01/2025 | 11:56 | 27/01/2025 | 15:38 | DN6 | DANDENONG | Urban | Asset Failure | LV | 1 | 222.9333 | 222.9333 | 1 | No
| 1867828 | 27/01/2025 | 14:42 | 27/01/2025 | 16:52 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 110 | 14267 | 129.7 | 1 | No
| 1867835 | 27/01/2025 | 16:16 | 27/01/2025 | 20:10 | MC15 | MORDIALLOC | Urban | Asset Failure | LV | 76 | 17784 | 234 | 1 | No
| 1867843 | 27/01/2025 | 16:35 | 27/01/2025 | 17:30 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 665 | 37040.5 | 55.7 | 1 | No
| 1867843 | 27/01/2025 | 16:35 | 27/01/2025 | 18:22 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 39 | 4173 | 107 | 2 | No
| 1867843 | 27/01/2025 | 16:35 | 27/01/2025 | 18:49 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 156 | 20969.0052 | 134.4167 | 3 | No
| 1867843 | 27/01/2025 | 16:35 | 27/01/2025 | 19:16 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 169 | 27206.1777 | 160.9833 | 4 | No
| 1867843 | 27/01/2025 | 16:35 | 27/01/2025 | 19:39 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 437 | 80386.15 | 183.95 | 5 | No
| 1867844 | 27/01/2025 | 16:38 | 27/01/2025 | 18:20 | OR32 | ORMOND | Urban | Asset Failure | LV | 48.18 | 4891.8744 | 101.5333 | 1 | No
| 1867847 | 27/01/2025 | 16:47 | 27/01/2025 | 17:53 | NW23 | NUNAWADING | Urban | Overloads |  | 17.49 | 1142.097 | 65.3 | 1 | No
| 1867846 | 27/01/2025 | 16:48 | 27/01/2025 | 21:06 | DVY24 | DANDENONG VALLEY | Rural Short | Asset Failure | LV | 1 | 258.4 | 258.4 | 1 | No
| 1867857 | 27/01/2025 | 16:52 | 27/01/2025 | 19:35 | DMA14 | DROMANA | Urban | Weather |  | 42 | 6824.2986 | 162.4833 | 1 | No
| 1867861 | 27/01/2025 | 17:31 | 27/01/2025 | 18:03 | LWN24 | LANGWARRIN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 788 | 24716.9596 | 31.3667 | 1 | No
| 1867861 | 27/01/2025 | 17:31 | 27/01/2025 | 18:20 | LWN24 | LANGWARRIN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 801 | 39395.8233 | 49.1833 | 2 | No
| 1867865 | 27/01/2025 | 17:51 | 27/01/2025 | 19:14 | MGE32 | MULGRAVE | Urban | Asset Failure | LV | 92 | 7718.8 | 83.9 | 1 | No
| 1867884 | 27/01/2025 | 18:41 | 27/01/2025 | 21:16 | EM9 | EAST MALVERN | Urban | Asset Failure | LV | 90 | 13911.003 | 154.5667 | 1 | No
| 1867886 | 27/01/2025 | 18:44 | 27/01/2025 | 19:17 | K31 | GARDINER | Urban | Overloads |  | 17.82 | 572.022 | 32.1 | 1 | No
| 1867902 | 27/01/2025 | 21:11 | 27/01/2025 | 21:53 | EM5 | EAST MALVERN | Urban | Animal | Animal impact | 41 | 1719.95 | 41.95 | 1 | No
| 1867916 | 27/01/2025 | 21:54 | 27/01/2025 | 23:30 | DMA13 | DROMANA | Rural Short | Vegetation | Grow-in - Other responsible party | 29 | 2762.7343 | 95.2667 | 1 | No
| 1867915 | 27/01/2025 | 22:03 | 28/01/2025 | 0:34 | M11 | MENTONE | Urban | Asset Failure | LV | 1 | 151.2167 | 151.2167 | 1 | No
| 1867932 | 28/01/2025 | 0:44 | 28/01/2025 | 2:32 | DC1 | DONCASTER | Urban | Asset Failure | HV | 39 | 4207.4487 | 107.8833 | 1 | No
| 1867938 | 28/01/2025 | 0:54 | 28/01/2025 | 1:57 | NP25 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 62.1667 | 62.1667 | 1 | No
| 1867942 | 28/01/2025 | 1:10 | 28/01/2025 | 1:28 | EM10 | EAST MALVERN | Urban | Weather |  | 46 | 856.3682 | 18.6167 | 1 | No
| 1867959 | 28/01/2025 | 1:52 | 28/01/2025 | 2:56 | CRM13 | CARRUM | Urban | Weather |  | 1 | 63.95 | 63.95 | 1 | No
| 1867960 | 28/01/2025 | 2:03 | 28/01/2025 | 3:46 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 1 | 103 | 103 | 1 | No
| 1867971 | 28/01/2025 | 7:03 | 28/01/2025 | 16:22 | NO6 | NOTTING HILL | Urban | Third Party | Vehicle Impact | 24 | 13432.0008 | 559.6667 | 1 | No
| 1868057 | 28/01/2025 | 7:36 | 28/01/2025 | 10:20 | MTN24 | MORNINGTON | Rural Short | Weather |  | 0.66 | 107.591 | 163.0167 | 1 | No
| 1868000 | 28/01/2025 | 8:23 | 28/01/2025 | 10:15 | SS11 | SPRINGVALE SOUTH | Urban | Animal | Other | 1.34 | 149.745 | 111.75 | 1 | No
| 1868132 | 28/01/2025 | 13:07 | 28/01/2025 | 15:31 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | Distribution substation | 45.54 | 6514.497 | 143.05 | 1 | No
| 1868146 | 28/01/2025 | 13:41 | 28/01/2025 | 14:06 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 78 | 1891.5 | 24.25 | 1 | No
| 1868146 | 28/01/2025 | 13:41 | 28/01/2025 | 14:22 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 46 | 1859.1682 | 40.4167 | 2 | No
| 1868146 | 28/01/2025 | 13:41 | 28/01/2025 | 14:35 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 33 | 1780.9011 | 53.9667 | 3 | No
| 1868146 | 28/01/2025 | 13:41 | 28/01/2025 | 15:14 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 56 | 5166 | 92.25 | 4 | No
| 1868146 | 28/01/2025 | 13:41 | 28/01/2025 | 15:48 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 29 | 3679.1343 | 126.8667 | 5 | No
| 1868146 | 28/01/2025 | 13:41 | 28/01/2025 | 16:44 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 21 | 3825.5007 | 182.1667 | 6 | No
| 1868146 | 28/01/2025 | 13:41 | 28/01/2025 | 17:45 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 37 | 9001.4821 | 243.2833 | 7 | No
| 1868146 | 28/01/2025 | 13:41 | 28/01/2025 | 21:12 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 29 | 13079 | 451 | 8 | No
| 1868146 | 28/01/2025 | 13:41 | 28/01/2025 | 21:47 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 49 | 23778.8817 | 485.2833 | 9 | No
| 1868146 | 28/01/2025 | 13:41 | 28/01/2025 | 21:48 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 24 | 11681.5992 | 486.7333 | 10 | No
| 1868156 | 28/01/2025 | 14:19 | 28/01/2025 | 21:45 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 62 | 27636.5 | 445.75 | 1 | No
| 1868163 | 28/01/2025 | 15:23 | 28/01/2025 | 16:41 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 1 | 78.0667 | 78.0667 | 1 | No
| 1868173 | 28/01/2025 | 16:32 | 28/01/2025 | 18:05 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 18 | 1674.9 | 93.05 | 1 | No
| 1868160 | 28/01/2025 | 17:16 | 28/01/2025 | 19:40 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 144.2167 | 144.2167 | 1 | No
| 1868236 | 28/01/2025 | 20:12 | 29/01/2025 | 0:45 | NW13 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 55 | 15013.1685 | 272.9667 | 1 | No
| 1868245 | 28/01/2025 | 23:00 | 29/01/2025 | 0:08 | SR34 | SANDRINGHAM | Urban | Asset Failure | LV | 59 | 4053.3 | 68.7 | 1 | No
| 1868261 | 29/01/2025 | 2:05 | 29/01/2025 | 3:30 | OR25 | ORMOND | Urban | Asset Failure | Distribution substation | 87 | 7393.5471 | 84.9833 | 1 | No
| 1868272 | 29/01/2025 | 4:25 | 29/01/2025 | 5:15 | LD3 | LYNDALE | Urban | Animal | Animal impact | 115 | 5705.9205 | 49.6167 | 1 | No
| 1868283 | 29/01/2025 | 7:17 | 29/01/2025 | 11:00 | DN25 | DANDENONG | Urban | Asset Failure | LV | 5.61 | 1248.225 | 222.5 | 1 | No
| 1868296 | 29/01/2025 | 7:57 | 29/01/2025 | 9:33 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 95.8833 | 95.8833 | 1 | No
| 1868471 | 29/01/2025 | 13:29 | 29/01/2025 | 15:19 | OAK21 | OAKLEIGH | Urban | Asset Failure | HV | 46.86 | 5127.2666 | 109.4167 | 1 | No
| 1868476 | 29/01/2025 | 13:33 | 29/01/2025 | 15:15 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 101.5 | 101.5 | 1 | No
| 1868518 | 29/01/2025 | 15:42 | 29/01/2025 | 20:20 | EW12 | ELWOOD | Urban | Asset Failure | LV | 1 | 277.75 | 277.75 | 1 | No
| 1868537 | 29/01/2025 | 17:43 | 30/01/2025 | 17:53 | DVY12 | DANDENONG VALLEY | Urban | Asset Failure | HV | 1 | 1450.5333 | 1450.5333 | 1 | No
| 1868537 | 29/01/2025 | 17:43 | 30/01/2025 | 17:53 | DVY12 | DANDENONG VALLEY | Urban | Asset Failure | HV | 1 | 1450.7833 | 1450.7833 | 2 | No
| 1868517 | 29/01/2025 | 21:35 | 30/01/2025 | 0:30 | LD7 | LYNDALE | Urban | Asset Failure | LV | 1 | 175.8833 | 175.8833 | 1 | No
| 1868596 | 30/01/2025 | 7:02 | 30/01/2025 | 8:25 | HGS23 | HASTINGS | Rural Short | Animal | Animal impact | 55.61 | 4601.7275 | 82.75 | 1 | No
| 1868629 | 30/01/2025 | 8:14 | 30/01/2025 | 10:04 | KBH35 | KEYSBOROUGH | Urban | Overloads |  | 13 | 1436.7171 | 110.5167 | 1 | No
| 1868685 | 30/01/2025 | 9:52 | 30/01/2025 | 11:31 | HGS23 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 99.2167 | 99.2167 | 1 | No
| 1868877 | 31/01/2025 | 1:40 | 31/01/2025 | 3:00 | HGS23 | HASTINGS | Rural Short | Animal | Animal impact | 1.34 | 106.664 | 79.6 | 1 | No
| 1868880 | 31/01/2025 | 3:25 | 31/01/2025 | 3:59 | DC1 | DONCASTER | Urban | Third Party | Other | 3.63 | 123.42 | 34 | 1 | No
| 1868909 | 31/01/2025 | 8:12 | 31/01/2025 | 9:35 | RBD21 | ROSEBUD | Rural Short | Animal | Other | 2.01 | 166.2606 | 82.7167 | 1 | No
| 1868914 | 31/01/2025 | 8:19 | 31/01/2025 | 10:59 | DN6 | DANDENONG | Urban | Asset Failure | LV | 1 | 159.8167 | 159.8167 | 1 | No
| 1868965 | 31/01/2025 | 9:40 | 31/01/2025 | 10:18 | MR22 | MOORABBIN | Urban | Third Party | Vehicle Impact | 2 | 74.5666 | 37.2833 | 1 | No
| 1869131 | 31/01/2025 | 16:03 | 31/01/2025 | 17:55 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 4.15 | 464.0393 | 111.8167 | 1 | No
| 1869135 | 31/01/2025 | 16:26 | 31/01/2025 | 18:34 | SS11 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 128.6667 | 128.6667 | 1 | No
| 1869161 | 31/01/2025 | 19:58 | 31/01/2025 | 21:55 | EW14 | ELWOOD | Urban | Third Party | Other | 1 | 117.5667 | 117.5667 | 1 | No
| 1869234 | 2025-01-02 | 13:38 | 2025-01-02 | 17:22 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1 | 224.3 | 224.3 | 1 | No
| 1869240 | 2025-01-02 | 15:36 | 2025-01-02 | 17:40 | FSH12 | FRANKSTON SOUTH | Rural Short | Third Party | Vehicle Impact | 1 | 123.8167 | 123.8167 | 1 | No
| 1869241 | 2025-01-02 | 15:41 | 2025-01-02 | 18:01 | SH24 | SURREY HILLS | Urban | Overloads |  | 1 | 139.85 | 139.85 | 1 | No
| 1869242 | 2025-01-02 | 15:49 | 2025-01-02 | 17:30 | BU21 | BULLEEN | Urban | Asset Failure | LV | 1 | 100.85 | 100.85 | 1 | No
| 1869243 | 2025-01-02 | 16:19 | 2025-01-02 | 20:25 | SV33 | SPRINGVALE | Urban | Third Party | Vehicle Impact | 3.3 | 810.8651 | 245.7167 | 1 | No
| 1869248 | 2025-01-02 | 18:00 | 2025-01-02 | 18:47 | EM9 | EAST MALVERN | Urban | Asset Failure | HV | 496 | 22931.7168 | 46.2333 | 1 | No
| 1869248 | 2025-01-02 | 18:00 | 2025-01-02 | 19:35 | EM9 | EAST MALVERN | Urban | Asset Failure | HV | 64 | 6076.8 | 94.95 | 2 | No
| 1869248 | 2025-01-02 | 18:00 | 2025-01-02 | 19:35 | EM9 | EAST MALVERN | Urban | Asset Failure | HV | 72 | 6850.8 | 95.15 | 3 | No
| 1869261 | 2025-01-02 | 19:01 | 2025-01-02 | 20:45 | LD7 | LYNDALE | Urban | Asset Failure | LV | 1 | 103.2167 | 103.2167 | 1 | No
| 1869260 | 2025-01-02 | 19:44 | 2025-01-02 | 20:52 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 68.7833 | 68.7833 | 1 | No
| 1869258 | 2025-01-02 | 19:45 | 2025-01-02 | 22:09 | BH31 | BOX HILL | Urban | Asset Failure | LV | 1 | 144.25 | 144.25 | 1 | No
| 1869268 | 2025-01-02 | 19:56 | 2025-01-02 | 22:32 | MC12 | MORDIALLOC | Urban | Overloads |  | 26.4 | 4104.3209 | 155.4667 | 1 | No
| 1869273 | 2025-01-02 | 20:36 | 2025-01-02 | 22:25 | WD23 | WEST DONCASTER | Urban | Overloads |  | 11.22 | 1222.2316 | 108.9333 | 1 | No
| 1869276 | 2025-01-02 | 20:45 | 2025-01-02 | 23:50 | BW34 | BURWOOD | Urban | Overloads |  | 28.71 | 5300.822 | 184.6333 | 1 | No
| 1869281 | 2025-01-02 | 21:36 | 2025-01-02 | 21:40 | RWT35 | RINGWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1215 | 5001.7905 | 4.1167 | 1 | No
| 1869281 | 2025-01-02 | 21:36 | 2025-01-02 | 22:43 | RWT35 | RINGWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1334 | 89311.3 | 66.95 | 2 | No
| 1869283 | 2025-01-02 | 21:48 | 2025-02-02 | 2:00 | BT14 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 251.75 | 251.75 | 1 | No
| 1869285 | 2025-01-02 | 22:16 | 2025-01-02 | 23:15 | HGS32 | HASTINGS | Urban | Animal | Animal impact | 30.82 | 1805.5373 | 58.5833 | 1 | No
| 1869288 | 2025-01-02 | 23:05 | 2025-02-02 | 0:07 | DC6 | DONCASTER | Urban | Overloads |  | 1 | 62.1167 | 62.1167 | 1 | No
| 1869295 | 2025-02-02 | 2:05 | 2025-02-02 | 3:13 | RBD13 | ROSEBUD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 67.6167 | 67.6167 | 1 | No
| 1869297 | 2025-02-02 | 2:12 | 2025-02-02 | 3:23 | DN11 | DANDENONG | Urban | Animal | Other | 209.04 | 14803.523 | 70.8167 | 1 | No
| 1869301 | 2025-02-02 | 2:50 | 2025-02-02 | 4:08 | DN7 | DANDENONG | Urban | Asset Failure | LV | 1 | 77.9167 | 77.9167 | 1 | No
| 1869302 | 2025-02-02 | 4:51 | 2025-02-02 | 7:49 | STO14 | SORRENTO | Rural Short | Animal | Animal impact | 7.37 | 1310.7545 | 177.85 | 1 | No
| 1869308 | 2025-02-02 | 8:08 | 2025-02-02 | 10:00 | SS14 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 111.3333 | 111.3333 | 1 | No
| 1869316 | 2025-02-02 | 9:08 | 2025-02-02 | 10:57 | BH34 | BOX HILL | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 108.9333 | 108.9333 | 1 | No
| 1869326 | 2025-02-02 | 10:48 | 2025-02-02 | 14:02 | DC10 | DONCASTER | Urban | Overloads |  | 4.29 | 832.6174 | 194.0833 | 1 | No
| 1869328 | 2025-02-02 | 11:25 | 2025-02-02 | 12:44 | K21 | GARDINER | Urban | Overloads |  | 1 | 79 | 79 | 1 | No
| 1869333 | 2025-02-02 | 12:38 | 2025-02-02 | 14:37 | DMA24 | DROMANA | Rural Short | Overloads |  | 1 | 119.25 | 119.25 | 1 | No
| 1869335 | 2025-02-02 | 12:54 | 2025-02-02 | 15:27 | DMA21 | DROMANA | Urban | Overloads |  | 2.64 | 405.636 | 153.65 | 1 | No
| 1869337 | 2025-02-02 | 12:58 | 2025-02-02 | 15:10 | NW13 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 131.8167 | 131.8167 | 1 | No
| 1869338 | 2025-02-02 | 13:14 | 2025-02-02 | 14:23 | MGE33 | MULGRAVE | Urban | Overloads |  | 1 | 69.25 | 69.25 | 1 | No
| 1869343 | 2025-02-02 | 13:52 | 2025-02-02 | 15:35 | CDA23 | CLARINDA | Urban | Overloads |  | 41.91 | 4279.011 | 102.1 | 1 | No
| 1869347 | 2025-02-02 | 14:06 | 2025-02-02 | 18:16 | STO23 | SORRENTO | Urban | Weather |  | 97 | 24193.4199 | 249.4167 | 1 | No
| 1869347 | 2025-02-02 | 14:06 | 2025-02-02 | 18:12 | STO23 | SORRENTO | Urban | Weather |  | 73 | 17959.2191 | 246.0167 | 1 | No
| 1869347 | 2025-02-02 | 14:06 | 2025-03-02 | 0:41 | STO23 | SORRENTO | Urban | Weather |  | 70 | 44452.331 | 635.0333 | 2 | No
| 1869353 | 2025-02-02 | 14:42 | 2025-02-02 | 16:55 | OR35 | ORMOND | Urban | Asset Failure | LV | 11.88 | 1580.04 | 133 | 1 | No
| 1869367 | 2025-02-02 | 15:18 | 2025-02-02 | 17:13 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 115.65 | 115.65 | 1 | No
| 1869373 | 2025-02-02 | 15:44 | 2025-03-02 | 7:47 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 1 | 962.3667 | 962.3667 | 1 | No
| 1869375 | 2025-02-02 | 15:44 | 2025-02-02 | 16:23 | EM11 | EAST MALVERN | Urban | Asset Failure | HV | 560 | 21392 | 38.2 | 1 | No
| 1869375 | 2025-02-02 | 15:44 | 2025-02-02 | 16:35 | EM11 | EAST MALVERN | Urban | Asset Failure | HV | 15 | 762.2505 | 50.8167 | 2 | No
| 1869375 | 2025-02-02 | 15:44 | 2025-02-02 | 16:36 | EM11 | EAST MALVERN | Urban | Asset Failure | HV | 461 | 23864.4487 | 51.7667 | 3 | No
| 1869378 | 2025-02-02 | 15:55 | 2025-02-02 | 19:55 | EL31 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 239.9167 | 239.9167 | 1 | No
| 1869379 | 2025-02-02 | 15:57 | 2025-02-02 | 16:37 | K34 | GARDINER | Urban | Overloads |  | 15.18 | 600.1155 | 39.5333 | 1 | No
| 1869377 | 2025-02-02 | 16:09 | 2025-02-02 | 20:30 | BU22 | BULLEEN | Urban | Asset Failure | LV | 2 | 522.4666 | 261.2333 | 1 | No
| 1869381 | 2025-02-02 | 16:10 | 2025-02-02 | 17:09 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 59.5 | 59.5 | 1 | No
| 1869382 | 2025-02-02 | 16:10 | 2025-02-02 | 20:47 | CFD14 | CAULFIELD | Urban | Overloads |  | 19.14 | 5294.4436 | 276.6167 | 1 | No
| 1869383 | 2025-02-02 | 16:13 | 2025-02-02 | 17:25 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 71.75 | 71.75 | 1 | No
| 1869384 | 2025-02-02 | 16:13 | 2025-02-02 | 17:25 | OR24 | ORMOND | Urban | Overloads |  | 1 | 71.7333 | 71.7333 | 1 | No
| 1869386 | 2025-02-02 | 16:16 | 2025-03-02 | 8:27 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 971.2167 | 971.2167 | 1 | No
| 1869389 | 2025-02-02 | 16:19 | 2025-02-02 | 18:13 | LD1 | LYNDALE | Urban | Overloads |  | 32.67 | 3718.9339 | 113.8333 | 1 | No
| 1869388 | 2025-02-02 | 16:19 | 2025-02-02 | 17:25 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 65.7833 | 65.7833 | 1 | No
| 1869393 | 2025-02-02 | 16:23 | 2025-02-02 | 17:25 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 61.6833 | 61.6833 | 1 | No
| 1869394 | 2025-02-02 | 16:27 | 2025-02-02 | 17:29 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 61.7667 | 61.7667 | 1 | No
| 1869397 | 2025-02-02 | 16:51 | 2025-02-02 | 18:00 | BT16 | BENTLEIGH | Urban | Asset Failure | LV | 14.85 | 1021.432 | 68.7833 | 1 | No
| 1869398 | 2025-02-02 | 17:03 | 2025-02-02 | 18:09 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 65.6833 | 65.6833 | 1 | No
| 1869399 | 2025-02-02 | 17:07 | 2025-03-02 | 4:25 | MR12 | MOORABBIN | Urban | Overloads |  | 18.81 | 12735.9369 | 677.0833 | 1 | No
| 1869400 | 2025-02-02 | 17:10 | 2025-02-02 | 19:50 | MTN31 | MORNINGTON | Urban | Overloads |  | 70.62 | 11252.1176 | 159.3333 | 1 | No
| 1869405 | 2025-02-02 | 17:15 | 2025-02-02 | 19:16 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 30.69 | 3725.766 | 121.4 | 1 | No
| 1869404 | 2025-02-02 | 17:15 | 2025-02-02 | 18:37 | NW13 | NUNAWADING | Urban | Overloads |  | 36.96 | 2999.304 | 81.15 | 1 | No
| 1869409 | 2025-02-02 | 17:22 | 2025-02-02 | 18:38 | BU11 | BULLEEN | Urban | Overloads |  | 21.12 | 1612.8647 | 76.3667 | 1 | No
| 1869411 | 2025-02-02 | 17:24 | 2025-02-02 | 18:50 | BT15 | BENTLEIGH | Urban | Asset Failure | LV | 65 | 5548.8355 | 85.3667 | 1 | No
| 1869414 | 2025-02-02 | 17:26 | 2025-02-02 | 19:10 | HT4 | HEATHERTON | Urban | Overloads |  | 35.97 | 3730.6897 | 103.7167 | 1 | No
| 1869415 | 2025-02-02 | 17:29 | 2025-02-02 | 19:05 | K34 | GARDINER | Urban | Overloads |  | 30.36 | 2901.405 | 95.5667 | 1 | No
| 1869418 | 2025-02-02 | 17:37 | 2025-02-02 | 20:00 | CFD16 | CAULFIELD | Urban | Asset Failure | LV | 26.73 | 3804.5691 | 142.3333 | 1 | No
| 1869420 | 2025-02-02 | 17:38 | 2025-02-02 | 19:41 | WD34 | WEST DONCASTER | Urban | Overloads |  | 24.09 | 2957.0475 | 122.75 | 1 | No
| 1869417 | 2025-02-02 | 17:39 | 2025-02-02 | 18:41 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 61.7833 | 61.7833 | 1 | No
| 1869425 | 2025-02-02 | 17:46 | 2025-02-02 | 18:43 | OR24 | ORMOND | Urban | Overloads |  | 1 | 57.4667 | 57.4667 | 1 | No
| 1869430 | 2025-02-02 | 17:47 | 2025-02-02 | 21:30 | OR33 | ORMOND | Urban | Overloads |  | 29.37 | 6548.532 | 222.9667 | 1 | No
| 1869431 | 2025-02-02 | 17:47 | 2025-02-02 | 19:00 | KBH35 | KEYSBOROUGH | Urban | Overloads |  | 16.5 | 1199.55 | 72.7 | 1 | No
| 1869426 | 2025-02-02 | 17:47 | 2025-02-02 | 18:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.7667 | 61.7667 | 1 | No
| 1869427 | 2025-02-02 | 17:49 | 2025-02-02 | 18:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 60 | 60 | 1 | No
| 1869428 | 2025-02-02 | 17:49 | 2025-02-02 | 18:49 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1869429 | 2025-02-02 | 17:49 | 2025-02-02 | 18:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1869436 | 2025-02-02 | 17:52 | 2025-02-02 | 22:30 | OR24 | ORMOND | Urban | Overloads |  | 9.9 | 2746.0947 | 277.3833 | 1 | No
| 1869435 | 2025-02-02 | 17:53 | 2025-02-02 | 23:40 | RBD24 | ROSEBUD | Urban | Overloads |  | 27.72 | 9604.5171 | 346.4833 | 1 | No
| 1869433 | 2025-02-02 | 17:53 | 2025-02-02 | 18:53 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 59.8167 | 59.8167 | 1 | No
| 1869439 | 2025-02-02 | 17:59 | 2025-02-02 | 18:59 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.8333 | 59.8333 | 1 | No
| 1869440 | 2025-02-02 | 17:59 | 2025-02-02 | 18:59 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 59.6667 | 59.6667 | 1 | No
| 1869445 | 2025-02-02 | 18:05 | 2025-02-02 | 22:35 | SH32 | SURREY HILLS | Urban | Overloads |  | 31.68 | 8540.928 | 269.6 | 1 | No
| 1869444 | 2025-02-02 | 18:06 | 2025-02-02 | 22:45 | MTN34 | MORNINGTON | Urban | Overloads |  | 33 | 9191.5989 | 278.5333 | 1 | No
| 1869451 | 2025-02-02 | 18:07 | 2025-02-02 | 20:19 | EB24 | EAST BURWOOD | Urban | Overloads |  | 27.72 | 3636.864 | 131.2 | 1 | No
| 1869448 | 2025-02-02 | 18:09 | 2025-02-02 | 19:11 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.6167 | 61.6167 | 1 | No
| 1869449 | 2025-02-02 | 18:09 | 2025-02-02 | 19:11 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 61.6167 | 61.6167 | 1 | No
| 1869455 | 2025-02-02 | 18:13 | 2025-02-02 | 19:19 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 65.7 | 65.7 | 1 | No
| 1869459 | 2025-02-02 | 18:19 | 2025-02-02 | 21:07 | SR25 | SANDRINGHAM | Urban | Overloads |  | 27.06 | 4540.668 | 167.8 | 1 | No
| 1869456 | 2025-02-02 | 18:20 | 2025-02-02 | 19:19 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 59.4 | 59.4 | 1 | No
| 1869457 | 2025-02-02 | 18:20 | 2025-02-02 | 19:19 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.3833 | 59.3833 | 1 | No
| 1869458 | 2025-02-02 | 18:20 | 2025-02-02 | 19:19 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.3833 | 59.3833 | 1 | No
| 1869460 | 2025-02-02 | 18:23 | 2025-02-02 | 19:23 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6333 | 59.6333 | 1 | No
| 1869461 | 2025-02-02 | 18:23 | 2025-02-02 | 19:23 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 59.6333 | 59.6333 | 1 | No
| 1869462 | 2025-02-02 | 18:23 | 2025-02-02 | 19:23 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.6333 | 59.6333 | 1 | No
| 1869464 | 2025-02-02 | 18:26 | 2025-02-02 | 23:41 | K31 | GARDINER | Urban | Overloads |  | 11.88 | 3739.23 | 314.75 | 1 | No
| 1869468 | 2025-02-02 | 18:27 | 2025-02-02 | 20:43 | SR21 | SANDRINGHAM | Urban | Asset Failure | Distribution substation | 58.74 | 7944.585 | 135.25 | 1 | No
| 1869463 | 2025-02-02 | 18:27 | 2025-02-02 | 19:29 | EM8 | EAST MALVERN | Urban | Overloads |  | 1 | 61.7167 | 61.7167 | 1 | No
| 1869465 | 2025-02-02 | 18:29 | 2025-02-02 | 19:29 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.8333 | 59.8333 | 1 | No
| 1869466 | 2025-02-02 | 18:29 | 2025-02-02 | 19:29 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.8333 | 59.8333 | 1 | No
| 1869472 | 2025-02-02 | 18:31 | 2025-02-02 | 22:04 | MGE32 | MULGRAVE | Urban | Overloads |  | 30.36 | 6467.187 | 213.0167 | 1 | No
| 1869475 | 2025-02-02 | 18:35 | 2025-02-02 | 23:45 | DMA14 | DROMANA | Urban | Overloads |  | 15.51 | 4805.257 | 309.8167 | 1 | No
| 1869476 | 2025-02-02 | 18:35 | 2025-02-02 | 21:45 | M34 | MENTONE | Urban | Overloads |  | 30.36 | 5750.691 | 189.4167 | 1 | No
| 1869477 | 2025-02-02 | 18:36 | 2025-02-02 | 21:15 | MTN23 | MORNINGTON | Urban | Overloads |  | 48.18 | 7640.5434 | 158.5833 | 1 | No
| 1869474 | 2025-02-02 | 18:37 | 2025-02-02 | 19:39 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.6667 | 61.6667 | 1 | No
| 1869481 | 2025-02-02 | 18:40 | 2025-03-02 | 2:55 | M25 | MENTONE | Urban | Overloads |  | 38.94 | 19268.8087 | 494.8333 | 1 | No
| 1869483 | 2025-02-02 | 18:42 | 2025-02-02 | 21:56 | SH22 | SURREY HILLS | Urban | Overloads |  | 31.35 | 6079.809 | 193.9333 | 1 | No
| 1869482 | 2025-02-02 | 18:44 | 2025-02-02 | 19:43 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.35 | 59.35 | 1 | No
| 1869484 | 2025-02-02 | 18:44 | 2025-02-02 | 19:41 | BU21 | BULLEEN | Urban | Overloads |  | 27.06 | 1528.89 | 56.5 | 1 | No
| 1869485 | 2025-02-02 | 18:47 | 2025-02-02 | 20:45 | CRM23 | CARRUM | Urban | Overloads |  | 56.43 | 6670.026 | 118.2 | 1 | No
| 1869489 | 2025-02-02 | 18:49 | 2025-02-02 | 19:58 | K23 | GARDINER | Urban | Overloads |  | 26.4 | 1841.8409 | 69.7667 | 1 | No
| 1869486 | 2025-02-02 | 18:50 | 2025-02-02 | 19:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.4 | 59.4 | 1 | No
| 1869487 | 2025-02-02 | 18:50 | 2025-02-02 | 19:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.05 | 59.05 | 1 | No
| 1869488 | 2025-02-02 | 18:50 | 2025-02-02 | 23:45 | DC6 | DONCASTER | Urban | Asset Failure | LV | 2.97 | 875.853 | 294.9 | 1 | No
| 1869490 | 2025-02-02 | 18:54 | 2025-02-02 | 19:53 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 59.4667 | 59.4667 | 1 | No
| 1869492 | 2025-02-02 | 18:54 | 2025-02-02 | 21:15 | CRM13 | CARRUM | Urban | Overloads |  | 118.8 | 16780.5 | 141.25 | 1 | No
| 1869495 | 2025-02-02 | 18:55 | 2025-02-02 | 21:23 | OR33 | ORMOND | Urban | Overloads |  | 31.02 | 4569.246 | 147.3 | 1 | No
| 1869491 | 2025-02-02 | 18:56 | 2025-03-02 | 7:54 | GW4 | GLEN WAVERLEY | Urban | Weather |  | 1 | 778.3833 | 778.3833 | 1 | No
| 1869494 | 2025-02-02 | 18:57 | 2025-02-02 | 19:59 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.55 | 61.55 | 1 | No
| 1869496 | 2025-02-02 | 18:59 | 2025-02-02 | 19:59 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 59.5167 | 59.5167 | 1 | No
| 1869497 | 2025-02-02 | 19:00 | 2025-02-02 | 19:59 | EM8 | EAST MALVERN | Urban | Overloads |  | 1 | 59.3333 | 59.3333 | 1 | No
| 1869499 | 2025-02-02 | 19:03 | 2025-02-02 | 20:03 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 59.7667 | 59.7667 | 1 | No
| 1869500 | 2025-02-02 | 19:03 | 2025-02-02 | 20:03 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.75 | 59.75 | 1 | No
| 1869510 | 2025-02-02 | 19:06 | 2025-02-02 | 21:00 | OAK26 | OAKLEIGH | Urban | Overloads |  | 51.48 | 5832.684 | 113.3 | 1 | No
| 1869513 | 2025-02-02 | 19:08 | 2025-02-02 | 22:55 | EW12 | ELWOOD | Urban | Overloads |  | 24.09 | 5462.0052 | 226.7333 | 1 | No
| 1869517 | 2025-02-02 | 19:09 | 2025-02-02 | 20:13 | BU11 | BULLEEN | Urban | Overloads |  | 21.12 | 1343.232 | 63.6 | 1 | No
| 1869511 | 2025-02-02 | 19:10 | 2025-03-02 | 13:49 | BR4 | BEAUMARIS | Urban | Unknown | Unknown | 1 | 1119.2667 | 1119.2667 | 1 | No
| 1869514 | 2025-02-02 | 19:11 | 2025-02-02 | 20:09 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 57.5833 | 57.5833 | 1 | No
| 1869520 | 2025-02-02 | 19:12 | 2025-02-02 | 20:34 | OAK26 | OAKLEIGH | Urban | Overloads |  | 34.32 | 2845.7011 | 82.9167 | 1 | No
| 1869521 | 2025-02-02 | 19:12 | 2025-02-02 | 23:13 | CM22 | CHELTENHAM | Urban | Overloads |  | 23.43 | 5636.4778 | 240.5667 | 1 | No
| 1869522 | 2025-02-02 | 19:12 | 2025-03-02 | 1:22 | LWN35 | LANGWARRIN | Urban | Overloads |  | 24.75 | 9164.5117 | 370.2833 | 1 | No
| 1869531 | 2025-02-02 | 19:14 | 2025-03-02 | 0:24 | CRM23 | CARRUM | Urban | Overloads |  | 33.66 | 10459.845 | 310.75 | 1 | No
| 1869528 | 2025-02-02 | 19:14 | 2025-03-02 | 3:09 | RWT12 | RINGWOOD | Urban | Overloads |  | 184 | 87326.4 | 474.6 | 1 | No
| 1869519 | 2025-02-02 | 19:15 | 2025-02-02 | 19:55 | EL31 | ELSTERNWICK | Urban | Asset Failure | LV | 44 | 1759.2652 | 39.9833 | 1 | No
| 1869536 | 2025-02-02 | 19:18 | 2025-02-02 | 21:05 | NW31 | NUNAWADING | Urban | Asset Failure | LV | 37.62 | 4022.8307 | 106.9333 | 1 | No
| 1869537 | 2025-02-02 | 19:18 | 2025-03-02 | 1:39 | LWN35 | LANGWARRIN | Urban | Overloads |  | 29.04 | 11074.889 | 381.3667 | 1 | No
| 1869533 | 2025-02-02 | 19:20 | 2025-02-02 | 20:19 | EM8 | EAST MALVERN | Urban | Overloads |  | 1 | 59.4167 | 59.4167 | 1 | No
| 1869534 | 2025-02-02 | 19:20 | 2025-02-02 | 20:19 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.4167 | 59.4167 | 1 | No
| 1869535 | 2025-02-02 | 19:20 | 2025-02-02 | 20:19 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.4 | 59.4 | 1 | No
| 1869539 | 2025-02-02 | 19:20 | 2025-02-02 | 23:00 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 43.56 | 9565.0485 | 219.5833 | 1 | No
| 1869541 | 2025-02-02 | 19:21 | 2025-02-02 | 20:10 | OR33 | ORMOND | Urban | Overloads |  | 115.17 | 5597.262 | 48.6 | 1 | No
| 1869540 | 2025-02-02 | 19:23 | 2025-02-02 | 20:29 | OR24 | ORMOND | Urban | Overloads |  | 1 | 65.6667 | 65.6667 | 1 | No
| 1869544 | 2025-02-02 | 19:25 | 2025-03-02 | 1:58 | BR1 | BEAUMARIS | Urban | Overloads |  | 18.48 | 7258.6354 | 392.7833 | 1 | No
| 1869550 | 2025-02-02 | 19:25 | 2025-02-02 | 20:51 | STO13 | SORRENTO | Urban | Weather |  | 267 | 22850.7411 | 85.5833 | 1 | No
| 1869569 | 2025-02-02 | 19:29 | 2025-02-02 | 22:30 | SR34 | SANDRINGHAM | Urban | Overloads |  | 22.77 | 4117.9545 | 180.85 | 1 | No
| 1869571 | 2025-02-02 | 19:29 | 2025-02-02 | 20:29 | SS23 | SPRINGVALE SOUTH | Urban | Overloads |  | 26.73 | 1606.473 | 60.1 | 1 | No
| 1869572 | 2025-02-02 | 19:33 | 2025-02-02 | 20:33 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.6 | 59.6 | 1 | No
| 1869577 | 2025-02-02 | 19:37 | 2025-02-02 | 22:48 | DC3 | DONCASTER | Urban | Overloads |  | 11.55 | 2203.1625 | 190.75 | 1 | No
| 1869582 | 2025-02-02 | 19:38 | 2025-02-02 | 21:58 | GW8 | GLEN WAVERLEY | Urban | Overloads |  | 27.06 | 3791.5579 | 140.1167 | 1 | No
| 1869584 | 2025-02-02 | 19:39 | 2025-02-02 | 22:59 | K21 | GARDINER | Urban | Overloads |  | 48.91 | 9799.1185 | 200.35 | 1 | No
| 1869586 | 2025-02-02 | 19:43 | 2025-02-02 | 20:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 65.7167 | 65.7167 | 1 | No
| 1869587 | 2025-02-02 | 19:43 | 2025-02-02 | 20:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 65.55 | 65.55 | 1 | No
| 1869594 | 2025-02-02 | 19:48 | 2025-02-02 | 21:32 | MGE21 | MULGRAVE | Urban | Overloads |  | 108.57 | 11267.7529 | 103.7833 | 1 | No
| 1869595 | 2025-02-02 | 19:49 | 2025-02-02 | 21:04 | BW32 | BURWOOD | Urban | Overloads |  | 39.93 | 2967.4658 | 74.3167 | 1 | No
| 1869590 | 2025-02-02 | 19:49 | 2025-02-02 | 20:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.5833 | 59.5833 | 1 | No
| 1869591 | 2025-02-02 | 19:50 | 2025-02-02 | 20:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.2333 | 59.2333 | 1 | No
| 1869592 | 2025-02-02 | 19:50 | 2025-02-02 | 20:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.2333 | 59.2333 | 1 | No
| 1869598 | 2025-02-02 | 20:04 | 2025-03-02 | 2:09 | LWN33 | LANGWARRIN | Urban | Overloads |  | 18.15 | 6627.4725 | 365.15 | 1 | No
| 1869602 | 2025-02-02 | 20:10 | 2025-03-02 | 1:31 | MC12 | MORDIALLOC | Urban | Overloads |  | 26.4 | 8476.5991 | 321.0833 | 1 | No
| 1869604 | 2025-02-02 | 20:11 | 2025-03-02 | 4:50 | FSH21 | FRANKSTON SOUTH | Rural Short | Overloads |  | 7.59 | 3934.1497 | 518.3333 | 1 | No
| 1869608 | 2025-02-02 | 20:16 | 2025-03-02 | 0:00 | OAK26 | OAKLEIGH | Urban | Overloads |  | 25.08 | 5614.9932 | 223.8833 | 1 | No
| 1869612 | 2025-02-02 | 20:22 | 2025-03-02 | 0:05 | AR12 | ARMADALE | Urban | Overloads |  | 23.76 | 5297.292 | 222.95 | 1 | No
| 1869617 | 2025-02-02 | 20:26 | 2025-03-02 | 2:15 | EM7 | EAST MALVERN | Urban | Overloads |  | 14.52 | 5055.6215 | 348.1833 | 1 | No
| 1869623 | 2025-02-02 | 20:37 | 2025-02-02 | 22:01 | BU11 | BULLEEN | Urban | Overloads |  | 21.12 | 1768.8 | 83.75 | 1 | No
| 1869473 | 2025-02-02 | 20:54 | 2025-03-02 | 0:48 | EB33 | EAST BURWOOD | Urban | Overloads |  | 1 | 234.5833 | 234.5833 | 1 | No
| 1869601 | 2025-02-02 | 21:09 | 2025-03-02 | 5:28 | RWT23 | RINGWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 499.4167 | 499.4167 | 1 | No
| 1869622 | 2025-02-02 | 21:25 | 2025-03-02 | 5:50 | MR21 | MOORABBIN | Urban | Asset Failure | LV | 1 | 505 | 505 | 1 | No
| 1869634 | 2025-02-02 | 21:26 | 2025-03-02 | 2:04 | EM5 | EAST MALVERN | Urban | Overloads |  | 1 | 277.4167 | 277.4167 | 1 | No
| 1869642 | 2025-02-02 | 21:26 | 2025-03-02 | 0:45 | SS23 | SPRINGVALE SOUTH | Urban | Overloads |  | 49.17 | 9738.9396 | 198.0667 | 1 | No
| 1869646 | 2025-02-02 | 21:41 | 2025-02-02 | 22:45 | RBD22 | ROSEBUD | Urban | Weather |  | 1 | 63.9333 | 63.9333 | 1 | No
| 1869644 | 2025-02-02 | 21:43 | 2025-03-02 | 12:39 | M31 | MENTONE | Urban | Asset Failure | LV | 1 | 896.1667 | 896.1667 | 1 | No
| 1869651 | 2025-02-02 | 21:57 | 2025-03-02 | 0:06 | MGE21 | MULGRAVE | Urban | Overloads |  | 217.14 | 27873.5452 | 128.3667 | 1 | No
| 1869653 | 2025-02-02 | 22:02 | 2025-03-02 | 1:54 | DMA15 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 232.4333 | 232.4333 | 1 | No
| 1869656 | 2025-02-02 | 22:09 | 2025-03-02 | 0:45 | RWT35 | RINGWOOD | Urban | Overloads |  | 4.62 | 722.8762 | 156.4667 | 1 | No
| 1869669 | 2025-02-02 | 23:00 | 2025-02-02 | 23:36 | MC23 | MORDIALLOC | Urban | Asset Failure | HV | 169 | 6126.25 | 36.25 | 1 | No
| 1869669 | 2025-02-02 | 23:00 | 2025-02-02 | 23:56 | MC23 | MORDIALLOC | Urban | Asset Failure | HV | 25 | 1413.75 | 56.55 | 2 | No
| 1869669 | 2025-02-02 | 23:00 | 2025-03-02 | 0:25 | MC23 | MORDIALLOC | Urban | Asset Failure | HV | 24 | 2035.6008 | 84.8167 | 3 | No
| 1869781 | 2025-02-02 | 23:48 | 2025-03-02 | 10:55 | LD4 | LYNDALE | Urban | Weather |  | 17 | 11331.35 | 666.55 | 1 | No
| 1869781 | 2025-02-02 | 23:48 | 2025-03-02 | 12:11 | LD4 | LYNDALE | Urban | Weather |  | 2 | 1486.1666 | 743.0833 | 2 | No
| 1869697 | 2025-03-02 | 0:45 | 2025-03-02 | 5:05 | EW1 | ELWOOD | Urban | Weather |  | 7 | 1818.1331 | 259.7333 | 1 | No
| 1869712 | 2025-03-02 | 1:42 | 2025-03-02 | 2:09 | DC10 | DONCASTER | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 585 | 15638.9805 | 26.7333 | 1 | No
| 1869720 | 2025-03-02 | 1:59 | 2025-03-02 | 10:05 | HGS33 | HASTINGS | Rural Short | Weather |  | 2 | 970.7666 | 485.3833 | 1 | No
| 1869729 | 2025-03-02 | 3:23 | 2025-03-02 | 4:20 | DC3 | DONCASTER | Urban | Asset Failure | Distribution substation | 32.83 | 1857.6297 | 56.5833 | 1 | No
| 1869816 | 2025-03-02 | 3:34 | 2025-03-02 | 9:25 | HGS33 | HASTINGS | Rural Short | Weather |  | 6 | 2100.4998 | 350.0833 | 1 | No
| 1869686 | 2025-03-02 | 5:46 | 2025-04-02 | 0:12 | HT1 | HEATHERTON | Urban | Overloads |  | 1 | 1106.3667 | 1106.3667 | 1 | No
| 1869815 | 2025-03-02 | 5:47 | 2025-03-02 | 9:15 | HGS33 | HASTINGS | Rural Short | Weather |  | 6 | 1245.6 | 207.6 | 1 | No
| 1869732 | 2025-03-02 | 6:35 | 2025-03-02 | 12:45 | OE4 | OAKLEIGH EAST | Urban | Asset Failure | LV | 1 | 370 | 370 | 1 | No
| 1869752 | 2025-03-02 | 6:50 | 2025-03-02 | 15:19 | SH22 | SURREY HILLS | Urban | Overloads |  | 1 | 508.35 | 508.35 | 1 | No
| 1869933 | 2025-03-02 | 7:12 | 2025-03-02 | 13:12 | OE4 | OAKLEIGH EAST | Urban | Overloads |  | 1 | 359.95 | 359.95 | 1 | No
| 1869763 | 2025-03-02 | 7:36 | 2025-03-02 | 9:35 | HGS33 | HASTINGS | Rural Short | Weather |  | 7 | 829.5 | 118.5 | 1 | No
| 1869800 | 2025-03-02 | 8:35 | 2025-03-02 | 12:31 | MTN34 | MORNINGTON | Urban | Weather |  | 1 | 235.4667 | 235.4667 | 1 | No
| 1869817 | 2025-03-02 | 9:01 | 2025-03-02 | 9:50 | HGS33 | HASTINGS | Rural Short | Weather |  | 4 | 195.4668 | 48.8667 | 1 | No
| 1869840 | 2025-03-02 | 9:47 | 2025-03-02 | 11:29 | EM8 | EAST MALVERN | Urban | Asset Failure | LV | 2 | 202.5334 | 101.2667 | 1 | No
| 1869839 | 2025-03-02 | 9:49 | 2025-03-02 | 20:14 | CFD26 | CAULFIELD | Urban | Asset Failure | LV | 1 | 625.9833 | 625.9833 | 1 | No
| 1869467 | 2025-03-02 | 10:08 | 2025-03-02 | 15:35 | K35 | GARDINER | Urban | Overloads |  | 1 | 327 | 327 | 1 | No
| 1869851 | 2025-03-02 | 10:18 | 2025-03-02 | 16:25 | RBD21 | ROSEBUD | Rural Short | Weather |  | 1 | 366.7667 | 366.7667 | 1 | No
| 1869852 | 2025-03-02 | 10:19 | 2025-03-02 | 12:32 | HGS23 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 132.4167 | 132.4167 | 1 | No
| 1869883 | 2025-03-02 | 11:25 | 2025-03-02 | 17:13 | DC6 | DONCASTER | Urban | Overloads |  | 1 | 347.7333 | 347.7333 | 1 | No
| 1869896 | 2025-03-02 | 11:45 | 2025-03-02 | 18:08 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 1 | 383.2833 | 383.2833 | 1 | No
| 1869898 | 2025-03-02 | 11:46 | 2025-03-02 | 18:00 | NB31 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 374 | 374 | 1 | No
| 1869832 | 2025-03-02 | 12:46 | 2025-03-02 | 15:47 | LWN21 | LANGWARRIN | Rural Short | Overloads |  | 1 | 181 | 181 | 1 | No
| 1869943 | 2025-03-02 | 13:04 | 2025-03-02 | 23:30 | DN6 | DANDENONG | Urban | Overloads |  | 1 | 625.5667 | 625.5667 | 1 | No
| 1869958 | 2025-03-02 | 13:31 | 2025-03-02 | 17:23 | EB31 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 232.1833 | 232.1833 | 1 | No
| 1869967 | 2025-03-02 | 13:49 | 2025-03-02 | 17:09 | FSH31 | FRANKSTON SOUTH | Urban | Overloads |  | 1 | 199.85 | 199.85 | 1 | No
| 1869982 | 2025-03-02 | 15:01 | 2025-03-02 | 18:55 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 234 | 234 | 1 | No
| 1869985 | 2025-03-02 | 15:33 | 2025-04-02 | 0:58 | BR10 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 565 | 565 | 1 | No
| 1869998 | 2025-03-02 | 16:02 | 2025-03-02 | 18:19 | BU14 | BULLEEN | Urban | Asset Failure | LV | 50.25 | 6862.4767 | 136.5667 | 1 | No
| 1870006 | 2025-03-02 | 16:36 | 2025-03-02 | 18:09 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | Distribution substation | 36.63 | 3377.8977 | 92.2167 | 1 | No
| 1870009 | 2025-03-02 | 16:47 | 2025-03-02 | 17:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.8167 | 61.8167 | 1 | No
| 1870011 | 2025-03-02 | 16:50 | 2025-03-02 | 19:12 | NB34 | NORTH BRIGHTON | Urban | Overloads |  | 15.84 | 2241.6245 | 141.5167 | 1 | No
| 1870013 | 2025-03-02 | 16:53 | 2025-03-02 | 17:53 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6833 | 59.6833 | 1 | No
| 1870014 | 2025-03-02 | 16:59 | 2025-03-02 | 17:59 | M34 | MENTONE | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1870015 | 2025-03-02 | 16:59 | 2025-03-02 | 18:05 | OR24 | ORMOND | Urban | Overloads |  | 1 | 65.7167 | 65.7167 | 1 | No
| 1870017 | 2025-03-02 | 17:09 | 2025-03-02 | 18:09 | M34 | MENTONE | Urban | Overloads |  | 1 | 59.6833 | 59.6833 | 1 | No
| 1870018 | 2025-03-02 | 17:13 | 2025-03-02 | 18:13 | M34 | MENTONE | Urban | Overloads |  | 1 | 59.75 | 59.75 | 1 | No
| 1870019 | 2025-03-02 | 17:13 | 2025-03-02 | 18:19 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 65.75 | 65.75 | 1 | No
| 1870027 | 2025-03-02 | 17:18 | 2025-03-02 | 18:12 | EB32 | EAST BURWOOD | Urban | Asset Failure | LV | 23.43 | 1258.9712 | 53.7333 | 1 | No
| 1870024 | 2025-03-02 | 17:19 | 2025-03-02 | 18:19 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.8 | 59.8 | 1 | No
| 1870025 | 2025-03-02 | 17:19 | 2025-03-02 | 18:19 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.8 | 59.8 | 1 | No
| 1870026 | 2025-03-02 | 17:19 | 2025-03-02 | 18:19 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1870033 | 2025-03-02 | 17:23 | 2025-03-02 | 19:15 | EL23 | ELSTERNWICK | Urban | Asset Failure | LV | 16.17 | 1802.4165 | 111.4667 | 1 | No
| 1870029 | 2025-03-02 | 17:23 | 2025-03-02 | 18:23 | M34 | MENTONE | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1870030 | 2025-03-02 | 17:23 | 2025-03-02 | 18:23 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1870031 | 2025-03-02 | 17:23 | 2025-03-02 | 18:25 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 61.7 | 61.7 | 1 | No
| 1870032 | 2025-03-02 | 17:25 | 2025-03-02 | 23:09 | RVE12 | ROWVILLE | Rural Short | Unknown | Unknown | 1 | 344.35 | 344.35 | 1 | No
| 1870037 | 2025-03-02 | 17:27 | 2025-03-02 | 18:29 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 61.7667 | 61.7667 | 1 | No
| 1870038 | 2025-03-02 | 17:27 | 2025-03-02 | 18:29 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.7667 | 61.7667 | 1 | No
| 1870041 | 2025-03-02 | 17:28 | 2025-03-02 | 19:35 | EM8 | EAST MALVERN | Urban | Asset Failure | LV | 24.75 | 3136.2383 | 126.7167 | 1 | No
| 1870039 | 2025-03-02 | 17:29 | 2025-03-02 | 18:29 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1870040 | 2025-03-02 | 17:29 | 2025-03-02 | 18:29 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1870043 | 2025-03-02 | 17:33 | 2025-03-02 | 18:35 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.8 | 61.8 | 1 | No
| 1870045 | 2025-03-02 | 17:33 | 2025-03-02 | 19:08 | M11 | MENTONE | Urban | Overloads |  | 37.95 | 3578.685 | 94.3 | 1 | No
| 1870044 | 2025-03-02 | 17:35 | 2025-03-02 | 18:33 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 57.75 | 57.75 | 1 | No
| 1870046 | 2025-03-02 | 17:39 | 2025-03-02 | 18:39 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.6667 | 59.6667 | 1 | No
| 1870047 | 2025-03-02 | 17:43 | 2025-03-02 | 18:43 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7333 | 59.7333 | 1 | No
| 1870049 | 2025-03-02 | 17:47 | 2025-03-02 | 18:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.8167 | 61.8167 | 1 | No
| 1870050 | 2025-03-02 | 17:47 | 2025-03-02 | 18:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.8167 | 61.8167 | 1 | No
| 1870052 | 2025-03-02 | 17:49 | 2025-03-02 | 18:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7667 | 59.7667 | 1 | No
| 1870055 | 2025-03-02 | 17:50 | 2025-03-02 | 22:56 | MR12 | MOORABBIN | Urban | Overloads |  | 18.81 | 5737.9905 | 305.05 | 1 | No
| 1870010 | 2025-03-02 | 17:52 | 2025-03-02 | 19:30 | NW13 | NUNAWADING | Urban | Asset Failure | LV | 1 | 98 | 98 | 1 | No
| 1870061 | 2025-03-02 | 17:58 | 2025-03-02 | 19:10 | K25 | GARDINER | Urban | Asset Failure | LV | 10.89 | 775.7306 | 71.2333 | 1 | No
| 1870062 | 2025-03-02 | 17:58 | 2025-03-02 | 19:10 | K34 | GARDINER | Urban | Overloads |  | 38 | 2706.8654 | 71.2333 | 1 | No
| 1870059 | 2025-03-02 | 18:01 | 2025-04-02 | 0:19 | HGS22 | HASTINGS | Rural Short | Overloads |  | 1 | 378.95 | 378.95 | 1 | No
| 1870060 | 2025-03-02 | 18:01 | 2025-04-02 | 0:05 | OR25 | ORMOND | Urban | Overloads |  | 1 | 364 | 364 | 1 | No
| 1870063 | 2025-03-02 | 18:06 | 2025-03-02 | 19:20 | FSH11 | FRANKSTON SOUTH | Urban | Overloads |  | 37.95 | 2802.6075 | 73.85 | 1 | No
| 1870068 | 2025-03-02 | 18:23 | 2025-03-02 | 21:47 | SS23 | SPRINGVALE SOUTH | Urban | Overloads |  | 26.73 | 5446.6839 | 203.7667 | 1 | No
| 1870066 | 2025-03-02 | 18:23 | 2025-03-02 | 19:23 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1870067 | 2025-03-02 | 18:23 | 2025-03-02 | 19:31 | K34 | GARDINER | Urban | Overloads |  | 1 | 67.7167 | 67.7167 | 1 | No
| 1870069 | 2025-03-02 | 18:27 | 2025-03-02 | 19:29 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.8 | 61.8 | 1 | No
| 1870070 | 2025-03-02 | 18:29 | 2025-03-02 | 19:29 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 59.75 | 59.75 | 1 | No
| 1870071 | 2025-03-02 | 18:29 | 2025-03-02 | 19:29 | M34 | MENTONE | Urban | Overloads |  | 1 | 59.75 | 59.75 | 1 | No
| 1870072 | 2025-03-02 | 18:29 | 2025-03-02 | 19:29 | K34 | GARDINER | Urban | Overloads |  | 1 | 59.75 | 59.75 | 1 | No
| 1870074 | 2025-03-02 | 18:33 | 2025-03-02 | 19:33 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6667 | 59.6667 | 1 | No
| 1870075 | 2025-03-02 | 18:33 | 2025-03-02 | 19:33 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.65 | 59.65 | 1 | No
| 1870076 | 2025-03-02 | 18:35 | 2025-03-02 | 19:39 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 63.7833 | 63.7833 | 1 | No
| 1870079 | 2025-03-02 | 18:36 | 2025-03-02 | 20:45 | MTN35 | MORNINGTON | Rural Short | Weather |  | 72.27 | 9311.9895 | 128.85 | 1 | No
| 1870077 | 2025-03-02 | 18:37 | 2025-03-02 | 19:39 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 61.7333 | 61.7333 | 1 | No
| 1870078 | 2025-03-02 | 18:37 | 2025-03-02 | 20:58 | CRM23 | CARRUM | Urban | Overloads |  | 56.43 | 7944.4016 | 140.7833 | 1 | No
| 1870082 | 2025-03-02 | 18:39 | 2025-03-02 | 19:39 | OAK26 | OAKLEIGH | Urban | Overloads |  | 1 | 59.6833 | 59.6833 | 1 | No
| 1870083 | 2025-03-02 | 18:39 | 2025-03-02 | 19:39 | SH22 | SURREY HILLS | Urban | Overloads |  | 1 | 59.6833 | 59.6833 | 1 | No
| 1870084 | 2025-03-02 | 18:43 | 2025-03-02 | 19:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 65.7667 | 65.7667 | 1 | No
| 1870085 | 2025-03-02 | 18:43 | 2025-03-02 | 19:49 | SH22 | SURREY HILLS | Urban | Overloads |  | 1 | 65.7667 | 65.7667 | 1 | No
| 1870086 | 2025-03-02 | 18:43 | 2025-03-02 | 19:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 65.7667 | 65.7667 | 1 | No
| 1870087 | 2025-03-02 | 18:44 | 2025-03-02 | 21:55 | MTN34 | MORNINGTON | Urban | Weather |  | 33 | 6275.5011 | 190.1667 | 1 | No
| 1870088 | 2025-03-02 | 18:47 | 2025-03-02 | 19:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.6667 | 61.6667 | 1 | No
| 1870089 | 2025-03-02 | 18:47 | 2025-03-02 | 19:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.6667 | 61.6667 | 1 | No
| 1870090 | 2025-03-02 | 18:47 | 2025-03-02 | 19:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.6667 | 61.6667 | 1 | No
| 1870091 | 2025-03-02 | 18:47 | 2025-03-02 | 19:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.6667 | 61.6667 | 1 | No
| 1870096 | 2025-03-02 | 18:48 | 2025-03-02 | 21:39 | CRM13 | CARRUM | Urban | Asset Failure | LV | 62.7 | 10700.8021 | 170.6667 | 1 | No
| 1870092 | 2025-03-02 | 18:49 | 2025-03-02 | 19:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1870093 | 2025-03-02 | 18:49 | 2025-03-02 | 19:49 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1870099 | 2025-03-02 | 18:53 | 2025-03-02 | 19:53 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1870100 | 2025-03-02 | 18:53 | 2025-03-02 | 19:53 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1870101 | 2025-03-02 | 18:54 | 2025-04-02 | 0:15 | MC21 | MORDIALLOC | Urban | Overloads |  | 18.15 | 5828.2681 | 321.1167 | 1 | No
| 1870102 | 2025-03-02 | 18:56 | 2025-03-02 | 20:43 | RWT34 | RINGWOOD | Urban | Overloads |  | 42.24 | 4533.0574 | 107.3167 | 1 | No
| 1870103 | 2025-03-02 | 18:59 | 2025-03-02 | 19:59 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.7333 | 59.7333 | 1 | No
| 1870104 | 2025-03-02 | 18:59 | 2025-03-02 | 19:59 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 59.2333 | 59.2333 | 1 | No
| 1870113 | 2025-03-02 | 19:01 | 2025-03-02 | 23:12 | MR24 | MOORABBIN | Urban | Overloads |  | 18.81 | 4715.3529 | 250.6833 | 1 | No
| 1870124 | 2025-03-02 | 19:01 | 2025-03-02 | 20:46 | MGE21 | MULGRAVE | Urban | Overloads |  | 108.57 | 11398.0369 | 104.9833 | 1 | No
| 1870116 | 2025-03-02 | 19:02 | 2025-04-02 | 2:21 | LWN22 | LANGWARRIN | Urban | Overloads |  | 25.08 | 10992.9828 | 438.3167 | 1 | No
| 1870110 | 2025-03-02 | 19:03 | 2025-03-02 | 20:03 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 59.6333 | 59.6333 | 1 | No
| 1870111 | 2025-03-02 | 19:03 | 2025-03-02 | 20:03 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.6333 | 59.6333 | 1 | No
| 1870112 | 2025-03-02 | 19:03 | 2025-03-02 | 20:03 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.1333 | 59.1333 | 1 | No
| 1870120 | 2025-03-02 | 19:04 | 2025-03-02 | 23:45 | RBD24 | ROSEBUD | Urban | Asset Failure | LV | 21.12 | 5918.1767 | 280.2167 | 1 | No
| 1870118 | 2025-03-02 | 19:07 | 2025-03-02 | 20:09 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.7167 | 61.7167 | 1 | No
| 1870119 | 2025-03-02 | 19:07 | 2025-03-02 | 20:09 | BW32 | BURWOOD | Urban | Overloads |  | 1 | 61.7167 | 61.7167 | 1 | No
| 1870125 | 2025-03-02 | 19:08 | 2025-03-02 | 21:18 | SR23 | SANDRINGHAM | Urban | Overloads |  | 24.09 | 3127.2843 | 129.8167 | 1 | No
| 1870126 | 2025-03-02 | 19:08 | 2025-03-02 | 20:00 | OR35 | ORMOND | Urban | Overloads |  | 70 | 3600.331 | 51.4333 | 1 | No
| 1870122 | 2025-03-02 | 19:09 | 2025-03-02 | 20:09 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.6667 | 59.6667 | 1 | No
| 1870123 | 2025-03-02 | 19:09 | 2025-03-02 | 20:09 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 59.6667 | 59.6667 | 1 | No
| 1870133 | 2025-03-02 | 19:12 | 2025-03-02 | 20:21 | MTN24 | MORNINGTON | Rural Short | Overloads |  | 29.7 | 2051.281 | 69.0667 | 1 | No
| 1870130 | 2025-03-02 | 19:13 | 2025-03-02 | 22:19 | BT15 | BENTLEIGH | Urban | Overloads |  | 1 | 185.7333 | 185.7333 | 1 | No
| 1870131 | 2025-03-02 | 19:13 | 2025-03-02 | 20:15 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.7333 | 61.7333 | 1 | No
| 1870132 | 2025-03-02 | 19:13 | 2025-03-02 | 20:13 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.7333 | 59.7333 | 1 | No
| 1870137 | 2025-03-02 | 19:16 | 2025-03-02 | 20:05 | FTN14 | FRANKSTON | Urban | Overloads |  | 28.05 | 1373.0475 | 48.95 | 1 | No
| 1870138 | 2025-03-02 | 19:16 | 2025-04-02 | 1:10 | FSH11 | FRANKSTON SOUTH | Urban | Overloads |  | 27.39 | 9685.5614 | 353.6167 | 1 | No
| 1870135 | 2025-03-02 | 19:17 | 2025-03-02 | 21:43 | OR33 | ORMOND | Urban | Overloads |  | 29.37 | 4274.313 | 145.5333 | 1 | No
| 1870144 | 2025-03-02 | 19:18 | 2025-03-02 | 22:10 | HT11 | HEATHERTON | Urban | Overloads |  | 12.21 | 2091.9796 | 171.3333 | 1 | No
| 1870145 | 2025-03-02 | 19:18 | 2025-03-02 | 22:00 | OAK21 | OAKLEIGH | Urban | Overloads |  | 16.83 | 2711.5941 | 161.1167 | 1 | No
| 1870136 | 2025-03-02 | 19:19 | 2025-03-02 | 23:00 | DMA14 | DROMANA | Urban | Overloads |  | 15.51 | 3426.6755 | 220.9333 | 1 | No
| 1870141 | 2025-03-02 | 19:19 | 2025-03-02 | 20:19 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.2667 | 59.2667 | 1 | No
| 1870147 | 2025-03-02 | 19:22 | 2025-03-02 | 22:40 | M25 | MENTONE | Urban | Overloads |  | 19.47 | 3841.1059 | 197.2833 | 1 | No
| 1870148 | 2025-03-02 | 19:23 | 2025-03-02 | 20:23 | BW32 | BURWOOD | Urban | Overloads |  | 1 | 59.85 | 59.85 | 1 | No
| 1870149 | 2025-03-02 | 19:23 | 2025-03-02 | 20:23 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.85 | 59.85 | 1 | No
| 1870150 | 2025-03-02 | 19:23 | 2025-03-02 | 20:23 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.85 | 59.85 | 1 | No
| 1870151 | 2025-03-02 | 19:23 | 2025-03-02 | 21:49 | OAK26 | OAKLEIGH | Urban | Overloads |  | 1 | 145.85 | 145.85 | 1 | No
| 1870154 | 2025-03-02 | 19:23 | 2025-03-02 | 21:17 | LWN23 | LANGWARRIN | Urban | Overloads |  | 46.86 | 5307.6776 | 113.2667 | 1 | No
| 1870152 | 2025-03-02 | 19:24 | 2025-03-02 | 20:53 | EM11 | EAST MALVERN | Urban | Overloads |  | 47.52 | 4215.8176 | 88.7167 | 1 | No
| 1870162 | 2025-03-02 | 19:25 | 2025-03-02 | 23:56 | CRM23 | CARRUM | Urban | Overloads |  | 33.66 | 9105.03 | 270.5 | 1 | No
| 1870167 | 2025-03-02 | 19:26 | 2025-03-02 | 21:15 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 107 | 11625.55 | 108.65 | 1 | No
| 1870169 | 2025-03-02 | 19:26 | 2025-03-02 | 20:48 | SR36 | SANDRINGHAM | Urban | Overloads |  | 12.21 | 989.4166 | 81.0333 | 1 | No
| 1870170 | 2025-03-02 | 19:29 | 2025-03-02 | 20:54 | GW10 | GLEN WAVERLEY | Urban | Overloads |  | 29.7 | 2496.781 | 84.0667 | 1 | No
| 1870176 | 2025-03-02 | 19:33 | 2025-03-02 | 23:00 | LWN35 | LANGWARRIN | Urban | Overloads |  | 24.75 | 5111.2883 | 206.5167 | 1 | No
| 1870172 | 2025-03-02 | 19:33 | 2025-03-02 | 20:33 | SH22 | SURREY HILLS | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1870173 | 2025-03-02 | 19:33 | 2025-03-02 | 20:35 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.7833 | 61.7833 | 1 | No
| 1870174 | 2025-03-02 | 19:34 | 2025-03-02 | 22:20 | LWN35 | LANGWARRIN | Urban | Overloads |  | 29.04 | 4809.991 | 165.6333 | 1 | No
| 1870177 | 2025-03-02 | 19:37 | 2025-03-02 | 20:39 | SH22 | SURREY HILLS | Urban | Overloads |  | 1 | 61.6833 | 61.6833 | 1 | No
| 1870178 | 2025-03-02 | 19:39 | 2025-03-02 | 20:39 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6333 | 59.6333 | 1 | No
| 1870179 | 2025-03-02 | 19:40 | 2025-03-02 | 21:48 | OR33 | ORMOND | Urban | Overloads |  | 31.02 | 3970.56 | 128 | 1 | No
| 1870189 | 2025-03-02 | 19:42 | 2025-03-02 | 21:50 | BT15 | BENTLEIGH | Urban | Overloads |  | 16.83 | 2145.825 | 127.5 | 1 | No
| 1870192 | 2025-03-02 | 19:49 | 2025-03-02 | 20:49 | BW32 | BURWOOD | Urban | Overloads |  | 1 | 59.5667 | 59.5667 | 1 | No
| 1870193 | 2025-03-02 | 19:50 | 2025-03-02 | 20:49 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 59.3833 | 59.3833 | 1 | No
| 1870194 | 2025-03-02 | 19:50 | 2025-03-02 | 20:49 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 59.3667 | 59.3667 | 1 | No
| 1870196 | 2025-03-02 | 19:53 | 2025-03-02 | 20:53 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.5667 | 59.5667 | 1 | No
| 1870197 | 2025-03-02 | 19:54 | 2025-03-02 | 20:53 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.4 | 59.4 | 1 | No
| 1870203 | 2025-03-02 | 19:54 | 2025-03-02 | 21:05 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 25.41 | 1801.1447 | 70.8833 | 1 | No
| 1870198 | 2025-03-02 | 19:54 | 2025-03-02 | 20:53 | M34 | MENTONE | Urban | Overloads |  | 1 | 59.2333 | 59.2333 | 1 | No
| 1870202 | 2025-03-02 | 19:56 | 2025-03-02 | 22:20 | LWN35 | LANGWARRIN | Urban | Overloads |  | 1 | 143.35 | 143.35 | 1 | No
| 1870205 | 2025-03-02 | 19:57 | 2025-03-02 | 20:59 | M34 | MENTONE | Urban | Overloads |  | 1 | 61.65 | 61.65 | 1 | No
| 1870206 | 2025-03-02 | 19:58 | 2025-03-02 | 20:59 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.4833 | 61.4833 | 1 | No
| 1870208 | 2025-03-02 | 19:59 | 2025-03-02 | 20:59 | BW32 | BURWOOD | Urban | Overloads |  | 1 | 59.7333 | 59.7333 | 1 | No
| 1870212 | 2025-03-02 | 20:00 | 2025-04-02 | 0:01 | MC23 | MORDIALLOC | Urban | Overloads |  | 22.77 | 5487.1897 | 240.9833 | 1 | No
| 1870213 | 2025-03-02 | 20:00 | 2025-03-02 | 22:45 | FSH34 | FRANKSTON SOUTH | Urban | Weather |  | 55.77 | 9198.3301 | 164.9333 | 1 | No
| 1870209 | 2025-03-02 | 20:03 | 2025-03-02 | 23:00 | RD14 | RIVERSDALE | Urban | Unknown | Unknown | 1 | 177.0667 | 177.0667 | 1 | No
| 1870210 | 2025-03-02 | 20:04 | 2025-03-02 | 21:03 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 59.45 | 59.45 | 1 | No
| 1870211 | 2025-03-02 | 20:04 | 2025-03-02 | 21:03 | BW32 | BURWOOD | Urban | Overloads |  | 1 | 59.45 | 59.45 | 1 | No
| 1870223 | 2025-03-02 | 20:09 | 2025-04-02 | 1:21 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 107 | 33353.6869 | 311.7167 | 1 | No
| 1870220 | 2025-03-02 | 20:10 | 2025-03-02 | 21:09 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.4833 | 59.4833 | 1 | No
| 1870221 | 2025-03-02 | 20:10 | 2025-03-02 | 21:09 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.1333 | 59.1333 | 1 | No
| 1870225 | 2025-03-02 | 20:13 | 2025-03-02 | 21:19 | OR24 | ORMOND | Urban | Overloads |  | 1 | 65.7333 | 65.7333 | 1 | No
| 1870226 | 2025-03-02 | 20:13 | 2025-03-02 | 21:13 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.2333 | 59.2333 | 1 | No
| 1870227 | 2025-03-02 | 20:13 | 2025-03-02 | 21:19 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 65.55 | 65.55 | 1 | No
| 1870228 | 2025-03-02 | 20:14 | 2025-03-02 | 21:10 | OAK26 | OAKLEIGH | Urban | Overloads |  | 34.65 | 1908.6363 | 55.0833 | 1 | No
| 1870230 | 2025-03-02 | 20:15 | 2025-03-02 | 21:07 | DC1 | DONCASTER | Urban | Overloads |  | 1 | 52.2167 | 52.2167 | 1 | No
| 1870236 | 2025-03-02 | 20:19 | 2025-03-02 | 21:19 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 59.6 | 59.6 | 1 | No
| 1870237 | 2025-03-02 | 20:20 | 2025-03-02 | 21:19 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.4167 | 59.4167 | 1 | No
| 1870241 | 2025-03-02 | 20:22 | 2025-03-02 | 22:31 | CRM15 | CARRUM | Urban | Overloads |  | 71.94 | 9255.081 | 128.65 | 1 | No
| 1870242 | 2025-03-02 | 20:24 | 2025-03-02 | 21:23 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.3333 | 59.3333 | 1 | No
| 1870244 | 2025-03-02 | 20:33 | 2025-03-02 | 21:33 | OAK26 | OAKLEIGH | Urban | Overloads |  | 1 | 59.6333 | 59.6333 | 1 | No
| 1870245 | 2025-03-02 | 20:34 | 2025-03-02 | 21:33 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.45 | 59.45 | 1 | No
| 1870246 | 2025-03-02 | 20:40 | 2025-03-02 | 21:39 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.5 | 59.5 | 1 | No
| 1870251 | 2025-03-02 | 20:43 | 2025-03-02 | 21:43 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.7333 | 59.7333 | 1 | No
| 1870253 | 2025-03-02 | 20:45 | 2025-03-02 | 22:30 | NW31 | NUNAWADING | Urban | Overloads |  | 28.05 | 2923.7441 | 104.2333 | 1 | No
| 1870252 | 2025-03-02 | 20:47 | 2025-03-02 | 21:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.65 | 61.65 | 1 | No
| 1870255 | 2025-03-02 | 20:49 | 2025-03-02 | 21:49 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.6 | 59.6 | 1 | No
| 1870256 | 2025-03-02 | 20:49 | 2025-03-02 | 21:57 | BW32 | BURWOOD | Urban | Overloads |  | 1 | 67.6 | 67.6 | 1 | No
| 1870258 | 2025-03-02 | 20:53 | 2025-03-02 | 21:53 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.6833 | 59.6833 | 1 | No
| 1870260 | 2025-03-02 | 20:54 | 2025-03-02 | 21:28 | MGE32 | MULGRAVE | Urban | Overloads |  | 30.36 | 1053.492 | 34.7 | 1 | No
| 1870261 | 2025-03-02 | 20:55 | 2025-03-02 | 22:03 | MTN22 | MORNINGTON | Rural Short | Overloads |  | 35 | 2367.75 | 67.65 | 1 | No
| 1870261 | 2025-03-02 | 20:55 | 2025-03-02 | 22:03 | MTN22 | MORNINGTON | Rural Short | Overloads |  | 978 | 66976.6674 | 68.4833 | 2 | No
| 1870261 | 2025-03-02 | 20:55 | 2025-03-02 | 22:09 | MTN22 | MORNINGTON | Rural Short | Overloads |  | 57 | 4210.4019 | 73.8667 | 3 | No
| 1870261 | 2025-03-02 | 20:55 | 2025-03-02 | 22:19 | MTN22 | MORNINGTON | Rural Short | Overloads |  | 295 | 24642.3235 | 83.5333 | 4 | No
| 1870261 | 2025-03-02 | 20:55 | 2025-03-02 | 22:30 | MTN22 | MORNINGTON | Rural Short | Overloads |  | 766 | 72604.0078 | 94.7833 | 5 | No
| 1870261 | 2025-03-02 | 20:55 | 2025-03-02 | 22:32 | MTN22 | MORNINGTON | Rural Short | Overloads |  | 100 | 9728.33 | 97.2833 | 6 | No
| 1870261 | 2025-03-02 | 20:55 | 2025-03-02 | 22:43 | MTN22 | MORNINGTON | Rural Short | Overloads |  | 458 | 49318.9514 | 107.6833 | 7 | No
| 1870261 | 2025-03-02 | 20:55 | 2025-03-02 | 23:01 | MTN22 | MORNINGTON | Rural Short | Overloads |  | 627 | 78949.7709 | 125.9167 | 8 | No
| 1870263 | 2025-03-02 | 21:01 | 2025-03-02 | 22:38 | MGE21 | MULGRAVE | Urban | Overloads |  | 108.57 | 10614.5306 | 97.7667 | 1 | No
| 1870267 | 2025-03-02 | 21:12 | 2025-03-02 | 22:08 | MR12 | MOORABBIN | Urban | Overloads |  | 23.1 | 1272.0408 | 55.0667 | 1 | No
| 1870271 | 2025-03-02 | 21:18 | 2025-03-02 | 22:58 | CRM23 | CARRUM | Urban | Overloads |  | 171 | 17071.4943 | 99.8333 | 1 | No
| 1870272 | 2025-03-02 | 21:23 | 2025-03-02 | 22:29 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 65.7167 | 65.7167 | 1 | No
| 1870280 | 2025-03-02 | 21:43 | 2025-03-02 | 22:43 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.6167 | 59.6167 | 1 | No
| 1870284 | 2025-03-02 | 22:07 | 2025-03-02 | 23:07 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 59.2833 | 59.2833 | 1 | No
| 1870286 | 2025-03-02 | 22:16 | 2025-04-02 | 0:11 | FTN12 | FRANKSTON | Urban | Overloads |  | 1 | 114.9333 | 114.9333 | 1 | No
| 1870293 | 2025-03-02 | 22:32 | 2025-04-02 | 11:40 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 6 | 4726.9002 | 787.8167 | 1 | No
| 1870302 | 2025-03-02 | 22:41 | 2025-04-02 | 1:35 | MTN22 | MORNINGTON | Rural Short | Unknown | Unknown | 15 | 2596.2495 | 173.0833 | 1 | No
| 1870287 | 2025-03-02 | 22:54 | 2025-04-02 | 0:21 | MGE11 | MULGRAVE | Urban | Asset Failure | HV | 1 | 87 | 87 | 1 | No
| 1870300 | 2025-03-02 | 22:57 | 2025-04-02 | 0:18 | MTN22 | MORNINGTON | Rural Short | Asset Failure | Distribution substation | 30 | 2412.999 | 80.4333 | 1 | No
| 1870301 | 2025-03-02 | 22:57 | 2025-03-02 | 23:26 | CRM15 | CARRUM | Urban | Overloads |  | 71.94 | 2039.499 | 28.35 | 1 | No
| 1870308 | 2025-03-02 | 23:19 | 2025-04-02 | 1:03 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 38.94 | 4046.5163 | 103.9167 | 1 | No
| 1870288 | 2025-03-02 | 23:22 | 2025-04-02 | 15:22 | MGE11 | MULGRAVE | Urban | Third Party | Other | 1 | 960 | 960 | 1 | No
| 1870310 | 2025-03-02 | 23:38 | 2025-04-02 | 8:29 | GW4 | GLEN WAVERLEY | Urban | Third Party | Other | 1 | 531.0833 | 531.0833 | 1 | No
| 1870311 | 2025-03-02 | 23:38 | 2025-04-02 | 7:41 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 483.1 | 483.1 | 1 | No
| 1870313 | 2025-03-02 | 23:51 | 2025-04-02 | 0:08 | MTN22 | MORNINGTON | Rural Short | Asset Failure | HV | 1194 | 20576.5602 | 17.2333 | 1 | No
| 1870322 | 2025-04-02 | 0:57 | 2025-04-02 | 2:10 | FSH34 | FRANKSTON SOUTH | Urban | Overloads |  | 4.95 | 359.5348 | 72.6333 | 1 | No
| 1870331 | 2025-04-02 | 3:49 | 2025-04-02 | 4:40 | RBD24 | ROSEBUD | Urban | Overloads |  | 21.12 | 1067.2633 | 50.5333 | 1 | No
| 1870337 | 2025-04-02 | 6:30 | 2025-04-02 | 10:57 | RD4 | RIVERSDALE | Urban | Third Party | Other | 1 | 266.95 | 266.95 | 1 | No
| 1870350 | 2025-04-02 | 7:35 | 2025-04-02 | 8:28 | CRM13 | CARRUM | Urban | Asset Failure | LV | 1 | 53.15 | 53.15 | 1 | No
| 1870366 | 2025-04-02 | 8:13 | 2025-04-02 | 9:40 | NB24 | NORTH BRIGHTON | Urban | Overloads |  | 1 | 87.0333 | 87.0333 | 1 | No
| 1870426 | 2025-04-02 | 10:16 | 2025-04-02 | 11:25 | MTN24 | MORNINGTON | Rural Short | Weather |  | 2 | 137.9334 | 68.9667 | 1 | No
| 1870439 | 2025-04-02 | 10:41 | 2025-04-02 | 14:02 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 201.0333 | 201.0333 | 1 | No
| 1870428 | 2025-04-02 | 10:57 | 2025-04-02 | 12:43 | OR32 | ORMOND | Urban | Asset Failure | LV | 1 | 106.0833 | 106.0833 | 1 | No
| 1870458 | 2025-04-02 | 11:18 | 2025-04-02 | 15:34 | MGE11 | MULGRAVE | Urban | Unknown | Unknown | 33 | 8460.6489 | 256.3833 | 1 | No
| 1870510 | 2025-04-02 | 13:33 | 2025-04-02 | 15:25 | M22 | MENTONE | Urban | Overloads |  | 64 | 7213.8688 | 112.7167 | 1 | No
| 1870514 | 2025-04-02 | 13:46 | 2025-04-02 | 15:00 | KBH32 | KEYSBOROUGH | Urban | Overloads |  | 13.2 | 969.7604 | 73.4667 | 1 | No
| 1870528 | 2025-04-02 | 14:19 | 2025-04-02 | 15:35 | K35 | GARDINER | Urban | Overloads |  | 18.15 | 1377.585 | 75.9 | 1 | No
| 1870529 | 2025-04-02 | 14:22 | 2025-04-02 | 16:33 | M11 | MENTONE | Urban | Asset Failure | LV | 1 | 130.6833 | 130.6833 | 1 | No
| 1870531 | 2025-04-02 | 14:23 | 2025-04-02 | 16:54 | NW31 | NUNAWADING | Urban | Asset Failure | LV | 1 | 150.2833 | 150.2833 | 1 | No
| 1870537 | 2025-04-02 | 14:43 | 2025-04-02 | 17:05 | RBD12 | ROSEBUD | Rural Short | Overloads |  | 26.4 | 3725.9191 | 141.1333 | 1 | No
| 1870542 | 2025-04-02 | 14:49 | 2025-04-02 | 16:34 | K21 | GARDINER | Urban | Asset Failure | LV | 1 | 104.9 | 104.9 | 1 | No
| 1870549 | 2025-04-02 | 15:12 | 2025-04-02 | 17:13 | CM22 | CHELTENHAM | Urban | Vegetation | Grow-in - Other responsible party | 58 | 6966.7686 | 120.1167 | 1 | No
| 1870560 | 2025-04-02 | 15:50 | 2025-04-02 | 17:30 | LD7 | LYNDALE | Urban | Asset Failure | LV | 1 | 99.8833 | 99.8833 | 1 | No
| 1870526 | 2025-04-02 | 17:24 | 2025-04-02 | 18:50 | NP36 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 86 | 86 | 1 | No
| 1869688 | 2025-04-02 | 19:08 | 2025-04-02 | 21:45 | SVW41 | SPRINGVALE WEST | Urban | Overloads |  | 1 | 157 | 157 | 1 | No
| 1870611 | 2025-04-02 | 20:44 | 2025-04-02 | 21:39 | SS13 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 55.05 | 55.05 | 1 | No
| 1870618 | 2025-04-02 | 20:49 | 2025-04-02 | 22:05 | OR24 | ORMOND | Urban | Overloads |  | 30.03 | 2256.7545 | 75.15 | 1 | No
| 1870626 | 2025-04-02 | 21:46 | 2025-04-02 | 23:14 | LD6 | LYNDALE | Urban | Asset Failure | LV | 27.06 | 2379.927 | 87.95 | 1 | No
| 1870634 | 2025-05-02 | 1:57 | 2025-05-02 | 3:05 | RBD12 | ROSEBUD | Rural Short | Unknown | Unknown | 24.79 | 1662.995 | 67.0833 | 1 | No
| 1870679 | 2025-05-02 | 8:15 | 2025-05-02 | 8:30 | MGE23 | MULGRAVE | Urban | Network Business | Switching and protection error | 1 | 14.4333 | 14.4333 | 1 | No
| 1870696 | 2025-05-02 | 9:03 | 2025-05-02 | 11:37 | DMA14 | DROMANA | Urban | Asset Failure | LV | 12.54 | 1936.803 | 154.45 | 1 | No
| 1870720 | 2025-05-02 | 9:07 | 2025-05-02 | 10:11 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 267 | 16976.7411 | 63.5833 | 1 | No
| 1870879 | 2025-05-02 | 14:08 | 2025-05-02 | 16:45 | MR11 | MOORABBIN | Urban | Asset Failure | LV | 1 | 156.9167 | 156.9167 | 1 | No
| 1870931 | 2025-05-02 | 17:21 | 2025-05-02 | 18:13 | RBD23 | ROSEBUD | Urban | Unknown | Unknown | 1 | 52.2833 | 52.2833 | 1 | No
| 1870934 | 2025-05-02 | 18:35 | 2025-05-02 | 21:48 | BC23 | BALACLAVA | Urban | Asset Failure | LV | 1 | 193.05 | 193.05 | 1 | No
| 1870942 | 2025-05-02 | 19:05 | 2025-06-02 | 3:22 | CDA22 | CLARINDA | Urban | Network Business | Switching and protection error | 2 | 993.6 | 496.8 | 1 | No
| 1870947 | 2025-05-02 | 20:29 | 2025-05-02 | 21:18 | M23 | MENTONE | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 308 | 15143.3436 | 49.1667 | 1 | No
| 1870947 | 2025-05-02 | 20:29 | 2025-06-02 | 1:02 | M23 | MENTONE | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 325 | 88762.9275 | 273.1167 | 2 | No
| 1870948 | 2025-05-02 | 20:29 | 2025-05-02 | 21:20 | M11 | MENTONE | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1137 | 58005.9879 | 51.0167 | 1 | No
| 1870948 | 2025-05-02 | 20:29 | 2025-06-02 | 1:02 | M11 | MENTONE | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 437 | 119155.3479 | 272.6667 | 2 | No
| 1870958 | 2025-05-02 | 21:10 | 2025-06-02 | 1:18 | M34 | MENTONE | Urban | Asset Failure | LV | 101 | 25002.55 | 247.55 | 1 | No
| 1870983 | 2025-06-02 | 1:35 | 2025-06-02 | 2:30 | STO21 | SORRENTO | Rural Short | Animal | Animal impact | 67.67 | 3721.85 | 55 | 1 | No
| 1870989 | 2025-06-02 | 4:52 | 2025-06-02 | 6:58 | NW21 | NUNAWADING | Urban | Animal | Animal impact | 8.04 | 1005.2677 | 125.0333 | 1 | No
| 1871005 | 2025-06-02 | 7:51 | 2025-06-02 | 9:25 | MTN24 | MORNINGTON | Rural Short | Weather |  | 2 | 186.8334 | 93.4167 | 1 | No
| 1871037 | 2025-06-02 | 8:38 | 2025-06-02 | 10:20 | FTN14 | FRANKSTON | Urban | Asset Failure | LV | 1 | 102.2833 | 102.2833 | 1 | No
| 1871149 | 2025-06-02 | 12:49 | 2025-06-02 | 15:36 | RBD24 | ROSEBUD | Urban | Asset Failure | HV | 115 | 19162.8295 | 166.6333 | 1 | No
| 1871150 | 2025-06-02 | 12:56 | 2025-06-02 | 15:41 | RBD24 | ROSEBUD | Urban | Asset Failure | HV | 26 | 4304.3 | 165.55 | 1 | No
| 1871208 | 2025-06-02 | 16:28 | 2025-06-02 | 17:47 | BT23 | BENTLEIGH | Urban | Asset Failure | LV | 20.13 | 1572.153 | 78.1 | 1 | No
| 1871244 | 2025-06-02 | 16:55 | 2025-06-02 | 18:33 | SVW53 | SPRINGVALE WEST | Urban | Asset Failure | Distribution substation | 40.26 | 3919.311 | 97.35 | 1 | No
| 1871242 | 2025-06-02 | 17:50 | 2025-06-02 | 18:45 | MTN35 | MORNINGTON | Rural Short | Overloads |  | 72.27 | 3950.7624 | 54.6667 | 1 | No
| 1871264 | 2025-06-02 | 19:26 | 2025-06-02 | 20:32 | WD23 | WEST DONCASTER | Urban | Asset Failure | LV | 11.22 | 732.8534 | 65.3167 | 1 | No
| 1871265 | 2025-06-02 | 19:30 | 2025-06-02 | 20:29 | LD6 | LYNDALE | Urban | Asset Failure | HV | 25.6 | 1533.44 | 59.9 | 1 | No
| 1871290 | 2025-06-02 | 20:59 | 2025-06-02 | 22:13 | WD34 | WEST DONCASTER | Urban | Asset Failure | LV | 3 | 224.7 | 74.9 | 1 | No
| 1871296 | 2025-06-02 | 21:02 | 2025-06-02 | 22:41 | WD34 | WEST DONCASTER | Urban | Overloads |  | 16.83 | 1657.1946 | 98.4667 | 1 | No
| 1871318 | 2025-07-02 | 1:58 | 2025-07-02 | 3:06 | EM8 | EAST MALVERN | Urban | Overloads |  | 52 | 3586.2684 | 68.9667 | 1 | No
| 1871320 | 2025-07-02 | 5:21 | 2025-07-02 | 7:13 | LWN35 | LANGWARRIN | Urban | Animal | Animal impact | 1 | 111.7667 | 111.7667 | 1 | No
| 1871334 | 2025-07-02 | 7:06 | 2025-07-02 | 9:31 | NP11 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 144.9167 | 144.9167 | 1 | No
| 1871521 | 2025-07-02 | 13:59 | 2025-07-02 | 18:20 | FSH21 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 1 | 260.2667 | 260.2667 | 1 | No
| 1871538 | 2025-07-02 | 15:37 | 2025-07-02 | 18:15 | HT2 | HEATHERTON | Urban | Third Party | Other | 49 | 7704.4317 | 157.2333 | 1 | No
| 1871540 | 2025-07-02 | 15:50 | 2025-07-02 | 17:10 | DN22 | DANDENONG | Urban | Asset Failure | LV | 49 | 3893.05 | 79.45 | 1 | No
| 1871183 | 2025-07-02 | 16:01 | 2025-07-02 | 17:30 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 1 | 89 | 89 | 1 | No
| 1871568 | 2025-07-02 | 18:05 | 2025-07-02 | 19:07 | DC4 | DONCASTER | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 405 | 25082.9865 | 61.9333 | 1 | No
| 1871568 | 2025-07-02 | 18:05 | 2025-07-02 | 19:28 | DC4 | DONCASTER | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 204 | 16860.6 | 82.65 | 2 | No
| 1871568 | 2025-07-02 | 18:05 | 2025-07-02 | 19:32 | DC4 | DONCASTER | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 209 | 18043.6597 | 86.3333 | 3 | No
| 1871590 | 2025-07-02 | 22:31 | 2025-07-02 | 23:43 | RWT23 | RINGWOOD | Urban | Asset Failure | LV | 1 | 72.2667 | 72.2667 | 1 | No
| 1871592 | 2025-07-02 | 23:10 | 2025-08-02 | 0:14 | LD33 | LYNDALE | Urban | Asset Failure | HV | 424 | 26902.8 | 63.45 | 1 | No
| 1871613 | 2025-07-02 | 23:12 | 2025-08-02 | 1:41 | CDA11 | CLARINDA | Urban | Asset Failure | HV | 165 | 24582.2445 | 148.9833 | 1 | No
| 1871593 | 2025-08-02 | 0:00 | 2025-08-02 | 0:08 | CDA11 | CLARINDA | Urban | Asset Failure | HV | 126 | 1020.6 | 8.1 | 1 | No
| 1871604 | 2025-08-02 | 0:35 | 2025-08-02 | 2:48 | LD33 | LYNDALE | Urban | Overloads |  | 50.16 | 6668.772 | 132.95 | 1 | No
| 1871621 | 2025-08-02 | 2:44 | 2025-08-02 | 4:33 | LWN21 | LANGWARRIN | Rural Short | Animal | Animal impact | 18.76 | 2030.1453 | 108.2167 | 1 | No
| 1871685 | 2025-08-02 | 12:11 | 2025-08-02 | 15:09 | NP14 | NOBLE PARK | Urban | Third Party | Other | 1 | 178.5333 | 178.5333 | 1 | No
| 1871692 | 2025-08-02 | 12:55 | 2025-08-02 | 18:10 | STO23 | SORRENTO | Urban | Weather |  | 10 | 3150 | 315 | 1 | No
| 1871708 | 2025-08-02 | 17:15 | 2025-08-02 | 18:27 | NW31 | NUNAWADING | Urban | Asset Failure | LV | 53 | 3806.2851 | 71.8167 | 1 | No
| 1871713 | 2025-08-02 | 17:47 | 2025-08-02 | 20:24 | M12 | MENTONE | Urban | Asset Failure | LV | 1 | 156.3 | 156.3 | 1 | No
| 1871739 | 2025-08-02 | 20:49 | 2025-08-02 | 21:34 | HT9 | HEATHERTON | Urban | Asset Failure | HV | 144 | 6398.3952 | 44.4333 | 1 | No
| 1871739 | 2025-08-02 | 20:49 | 2025-08-02 | 21:45 | HT9 | HEATHERTON | Urban | Asset Failure | HV | 185 | 10329.1605 | 55.8333 | 2 | No
| 1871739 | 2025-08-02 | 20:49 | 2025-08-02 | 21:58 | HT9 | HEATHERTON | Urban | Asset Failure | HV | 34 | 2352.8 | 69.2 | 3 | No
| 1871739 | 2025-08-02 | 20:49 | 2025-08-02 | 22:07 | HT9 | HEATHERTON | Urban | Asset Failure | HV | 1 | 77.6 | 77.6 | 4 | No
| 1871739 | 2025-08-02 | 20:49 | 2025-08-02 | 23:26 | HT9 | HEATHERTON | Urban | Asset Failure | HV | 1 | 156.5833 | 156.5833 | 5 | No
| 1871744 | 2025-08-02 | 22:15 | 2025-09-02 | 1:12 | LD32 | LYNDALE | Urban | Asset Failure | LV | 1 | 176.8167 | 176.8167 | 1 | No
| 1871745 | 2025-08-02 | 22:31 | 2025-09-02 | 2:34 | LD4 | LYNDALE | Urban | Asset Failure | LV | 24.75 | 6006.4117 | 242.6833 | 1 | No
| 1871749 | 2025-09-02 | 1:09 | 2025-09-02 | 3:09 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 36 | 4344.0012 | 120.6667 | 1 | No
| 1871765 | 2025-09-02 | 1:49 | 2025-09-02 | 4:20 | FTN11 | FRANKSTON | Urban | Animal | Animal impact | 111.22 | 16755.293 | 150.65 | 1 | No
| 1871767 | 2025-09-02 | 1:52 | 2025-09-02 | 2:19 | SS11 | SPRINGVALE SOUTH | Urban | Weather |  | 51 | 1374.45 | 26.95 | 1 | No
| 1871780 | 2025-09-02 | 5:49 | 2025-09-02 | 9:30 | HGS22 | HASTINGS | Rural Short | Animal | Other | 7 | 1541.9831 | 220.2833 | 1 | No
| 1871784 | 2025-09-02 | 6:21 | 2025-09-02 | 9:00 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 158.8833 | 158.8833 | 1 | No
| 1871820 | 2025-09-02 | 10:27 | 2025-09-02 | 13:05 | SVW53 | SPRINGVALE WEST | Urban | Third Party | Other | 1 | 157.9333 | 157.9333 | 1 | No
| 1871827 | 2025-09-02 | 10:54 | 2025-09-02 | 13:30 | BR9 | BEAUMARIS | Urban | Asset Failure | HV | 82.5 | 12805.3777 | 155.2167 | 1 | No
| 1871814 | 2025-09-02 | 13:29 | 2025-09-02 | 16:46 | SS14 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 197.5167 | 197.5167 | 1 | No
| 1871844 | 2025-09-02 | 14:43 | 2025-09-02 | 17:20 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 157.6167 | 157.6167 | 1 | No
| 1871875 | 2025-09-02 | 15:22 | 2025-09-02 | 17:49 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 147 | 147 | 1 | No
| 1871876 | 2025-09-02 | 15:29 | 2025-09-02 | 18:50 | M22 | MENTONE | Urban | Weather |  | 1 | 201.1 | 201.1 | 1 | No
| 1871879 | 2025-09-02 | 15:39 | 2025-09-02 | 16:12 | MTN34 | MORNINGTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 126 | 4078.2042 | 32.3667 | 1 | No
| 1871879 | 2025-09-02 | 15:39 | 2025-09-02 | 16:37 | MTN34 | MORNINGTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1040 | 59956 | 57.65 | 2 | No
| 1871894 | 2025-09-02 | 16:30 | 2025-09-02 | 17:30 | SS11 | SPRINGVALE SOUTH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 51 | 3032.8017 | 59.4667 | 1 | No
| 1871909 | 2025-09-02 | 17:12 | 2025-09-02 | 17:38 | MC23 | MORDIALLOC | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 3 | 75.0501 | 25.0167 | 1 | No
| 1871912 | 2025-09-02 | 17:16 | 2025-09-02 | 17:56 | CRM15 | CARRUM | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 550 | 21972.5 | 39.95 | 1 | No
| 1871912 | 2025-09-02 | 17:16 | 2025-09-02 | 18:16 | CRM15 | CARRUM | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 629 | 37635.1457 | 59.8333 | 2 | No
| 1871918 | 2025-09-02 | 17:29 | 2025-09-02 | 18:57 | K34 | GARDINER | Urban | Asset Failure | LV | 36 | 3159 | 87.75 | 1 | No
| 1871925 | 2025-09-02 | 18:15 | 2025-09-02 | 19:45 | GW5 | GLEN WAVERLEY | Urban | Asset Failure | LV | 81 | 7235.9973 | 89.3333 | 1 | No
| 1871927 | 2025-09-02 | 18:19 | 2025-09-02 | 18:43 | DSH21 | DANDENONG SOUTH | Urban | Third Party |  | 21 | 500.4993 | 23.8333 | 1 | No
| 1871927 | 2025-09-02 | 18:19 | 2025-09-02 | 19:00 | DSH21 | DANDENONG SOUTH | Urban | Third Party |  | 164 | 6773.2 | 41.3 | 2 | No
| 1871931 | 2025-09-02 | 18:58 | 2025-09-02 | 21:45 | BR4 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 167 | 167 | 1 | No
| 1871943 | 2025-09-02 | 19:38 | 2025-09-02 | 22:55 | BU25 | BULLEEN | Urban | Overloads |  | 170 | 33427.661 | 196.6333 | 1 | No
| 1871944 | 2025-09-02 | 19:38 | 2025-09-02 | 20:42 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 64.0167 | 64.0167 | 1 | No
| 1871954 | 2025-09-02 | 20:16 | 2025-09-02 | 20:22 | NW33 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1237 | 7195.2579 | 5.8167 | 1 | No
| 1871954 | 2025-09-02 | 20:16 | 2025-09-02 | 21:43 | NW33 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 582 | 50925 | 87.5 | 2 | No
| 1871963 | 2025-09-02 | 20:32 | 2025-10-02 | 0:50 | DN25 | DANDENONG | Urban | Asset Failure | Distribution substation | 41 | 10540.4153 | 257.0833 | 1 | No
| 1871980 | 2025-09-02 | 20:57 | 2025-09-02 | 22:45 | MTN31 | MORNINGTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 107.8667 | 107.8667 | 1 | No
| 1871985 | 2025-09-02 | 21:13 | 2025-09-02 | 22:55 | MR13 | MOORABBIN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 16 | 1618.4 | 101.15 | 1 | No
| 1871987 | 2025-09-02 | 21:22 | 2025-10-02 | 18:08 | BC22 | BALACLAVA | Urban | Asset Failure | LV | 1 | 1245.2167 | 1245.2167 | 1 | No
| 1871989 | 2025-09-02 | 21:27 | 2025-10-02 | 1:00 | RBD12 | ROSEBUD | Rural Short | Weather |  | 1 | 212.8833 | 212.8833 | 1 | No
| 1871992 | 2025-09-02 | 21:41 | 2025-09-02 | 21:58 | EL35 | ELSTERNWICK | Urban | Weather |  | 41 | 694.2653 | 16.9333 | 1 | No
| 1871998 | 2025-09-02 | 22:01 | 2025-10-02 | 0:28 | BU14 | BULLEEN | Urban | Asset Failure | LV | 1 | 146.8833 | 146.8833 | 1 | No
| 1872009 | 2025-09-02 | 22:18 | 2025-10-02 | 2:16 | NP12 | NOBLE PARK | Urban | Overloads |  | 1 | 238.0333 | 238.0333 | 1 | No
| 1872014 | 2025-09-02 | 23:47 | 2025-10-02 | 0:05 | NB25 | NORTH BRIGHTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 27.39 | 477.0434 | 17.4167 | 1 | No
| 1872016 | 2025-10-02 | 0:05 | 2025-10-02 | 1:14 | DC3 | DONCASTER | Urban | Animal | Animal impact | 149.41 | 10264.467 | 68.7 | 1 | No
| 1872027 | 2025-10-02 | 3:24 | 2025-10-02 | 4:30 | NW13 | NUNAWADING | Urban | Animal | Animal impact | 82 | 5350.5 | 65.25 | 1 | No
| 1872015 | 2025-10-02 | 6:00 | 2025-10-02 | 7:30 | DSH14 | DANDENONG SOUTH | Urban | Third Party | Other | 1 | 90 | 90 | 1 | No
| 1872032 | 2025-10-02 | 6:10 | 2025-10-02 | 8:45 | HT9 | HEATHERTON | Urban | Asset Failure | LV | 8.58 | 1329.9 | 155 | 1 | No
| 1872206 | 2025-10-02 | 6:15 | 2025-10-02 | 10:40 | CRM15 | CARRUM | Urban | Animal | Animal impact | 2 | 528.9 | 264.45 | 1 | No
| 1872140 | 2025-10-02 | 8:28 | 2025-10-02 | 17:40 | NB33 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 551.6667 | 551.6667 | 1 | No
| 1871737 | 2025-10-02 | 11:50 | 2025-10-02 | 21:30 | BC11 | BALACLAVA | Urban | Asset Failure | LV | 1 | 580 | 580 | 1 | No
| 1872267 | 2025-10-02 | 12:05 | 2025-10-02 | 13:55 | SS11 | SPRINGVALE SOUTH | Urban | Animal | Animal impact | 62.31 | 6876.9491 | 110.3667 | 1 | No
| 1872293 | 2025-10-02 | 13:13 | 2025-10-02 | 18:54 | EL35 | ELSTERNWICK | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 340.2167 | 340.2167 | 1 | No
| 1872097 | 2025-10-02 | 13:52 | 2025-10-02 | 19:37 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 1.77 | 611.4169 | 345.4333 | 1 | No
| 1872212 | 2025-10-02 | 14:04 | 2025-10-02 | 18:15 | M13 | MENTONE | Urban | Overloads |  | 1 | 251 | 251 | 1 | No
| 1872331 | 2025-10-02 | 14:56 | 2025-10-02 | 17:29 | EB11 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 152.6833 | 152.6833 | 1 | No
| 1872348 | 2025-10-02 | 15:58 | 2025-10-02 | 20:20 | CDA23 | CLARINDA | Urban | Overloads |  | 1 | 261.8167 | 261.8167 | 1 | No
| 1872358 | 2025-10-02 | 16:10 | 2025-10-02 | 19:12 | BT23 | BENTLEIGH | Urban | Asset Failure | LV | 98 | 17857.2366 | 182.2167 | 1 | No
| 1872369 | 2025-10-02 | 17:32 | 2025-10-02 | 18:00 | SH22 | SURREY HILLS | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1032 | 28775.5656 | 27.8833 | 1 | No
| 1872369 | 2025-10-02 | 17:32 | 2025-10-02 | 18:00 | SH24 | SURREY HILLS | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 577 | 16088.6641 | 27.8833 | 1 | No
| 1872369 | 2025-10-02 | 17:32 | 2025-10-02 | 18:00 | SH32 | SURREY HILLS | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 454 | 12659.0182 | 27.8833 | 1 | No
| 1872369 | 2025-10-02 | 17:32 | 2025-10-02 | 18:00 | SH34 | SURREY HILLS | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1064 | 29667.8312 | 27.8833 | 1 | No
| 1872401 | 2025-10-02 | 19:08 | 2025-10-02 | 20:40 | M34 | MENTONE | Urban | Asset Failure | LV | 6 | 548.8998 | 91.4833 | 1 | No
| 1872410 | 2025-10-02 | 20:07 | 2025-10-02 | 22:13 | DC5 | DONCASTER | Urban | Asset Failure | LV | 1 | 125.95 | 125.95 | 1 | No
| 1872431 | 2025-10-02 | 21:54 | 2025-10-02 | 23:42 | MTN22 | MORNINGTON | Rural Short | Animal | Animal impact | 1 | 107.8333 | 107.8333 | 1 | No
| 1872433 | 2025-11-02 | 0:21 | 2025-11-02 | 1:25 | SV14 | SPRINGVALE | Urban | Third Party | Other | 4 | 255.3332 | 63.8333 | 1 | No
| 1872442 | 2025-11-02 | 1:42 | 2025-11-02 | 3:31 | EW1 | ELWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 108.6667 | 108.6667 | 1 | No
| 1872451 | 2025-11-02 | 4:46 | 2025-11-02 | 7:25 | LWN21 | LANGWARRIN | Rural Short | Animal | Animal impact | 11 | 1745.15 | 158.65 | 1 | No
| 1872429 | 2025-11-02 | 5:44 | 2025-11-02 | 8:36 | OR32 | ORMOND | Urban | Asset Failure | LV | 1 | 172.3167 | 172.3167 | 1 | No
| 1872471 | 2025-11-02 | 6:41 | 2025-11-02 | 8:05 | HGS31 | HASTINGS | Rural Short | Overloads |  | 3 | 250.5999 | 83.5333 | 1 | No
| 1872552 | 2025-11-02 | 10:29 | 2025-11-02 | 12:32 | M32 | MENTONE | Urban | Asset Failure | LV | 1 | 122.6833 | 122.6833 | 1 | No
| 1872334 | 2025-11-02 | 11:48 | 2025-11-02 | 16:27 | CFD23 | CAULFIELD | Urban | Third Party | Other | 1 | 279.8833 | 279.8833 | 1 | No
| 1872697 | 2025-11-02 | 18:45 | 2025-11-02 | 22:37 | DC1 | DONCASTER | Urban | Asset Failure | LV | 1 | 232.8 | 232.8 | 1 | No
| 1872716 | 2025-11-02 | 19:02 | 2025-11-02 | 23:33 | LD7 | LYNDALE | Urban | Asset Failure | LV | 1 | 271.0833 | 271.0833 | 1 | No
| 1872739 | 2025-12-02 | 1:24 | 2025-12-02 | 2:24 | RWT34 | RINGWOOD | Urban | Unknown | Unknown | 42.24 | 2492.8654 | 59.0167 | 1 | No
| 1872742 | 2025-12-02 | 5:41 | 2025-12-02 | 6:52 | DC4 | DONCASTER | Urban | Animal | Animal impact | 89.78 | 6295.0773 | 70.1167 | 1 | No
| 1872795 | 2025-12-02 | 8:38 | 2025-12-02 | 9:42 | LD32 | LYNDALE | Urban | Asset Failure | LV | 1 | 63.95 | 63.95 | 1 | No
| 1872856 | 2025-12-02 | 10:36 | 2025-12-02 | 15:15 | DN24 | DANDENONG | Urban | Unknown | Unknown | 0.67 | 186.4722 | 278.3167 | 1 | No
| 1872915 | 2025-12-02 | 13:46 | 2025-12-02 | 15:44 | KBH32 | KEYSBOROUGH | Urban | Overloads |  | 13.2 | 1554.96 | 117.8 | 1 | No
| 1872937 | 2025-12-02 | 15:17 | 2025-12-02 | 19:10 | EB11 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 233 | 233 | 1 | No
| 1872899 | 2025-12-02 | 15:37 | 2025-12-02 | 17:28 | NW21 | NUNAWADING | Urban | Asset Failure | LV | 1 | 111 | 111 | 1 | No
| 1872953 | 2025-12-02 | 15:42 | 2025-12-02 | 17:15 | K21 | GARDINER | Urban | Overloads |  | 18.15 | 1672.8256 | 92.1667 | 1 | No
| 1872964 | 2025-12-02 | 16:16 | 2025-12-02 | 20:37 | LWN21 | LANGWARRIN | Rural Short | Overloads |  | 1.65 | 430.32 | 260.8 | 1 | No
| 1872967 | 2025-12-02 | 16:23 | 2025-12-02 | 18:55 | CRM33 | CARRUM | Urban | Third Party | Vehicle Impact | 211 | 32054.4237 | 151.9167 | 1 | No
| 1872960 | 2025-12-02 | 16:24 | 2025-12-02 | 21:20 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 1 | 296 | 296 | 1 | No
| 1872983 | 2025-12-02 | 17:36 | 2025-12-02 | 21:15 | K21 | GARDINER | Urban | Overloads |  | 18.15 | 3960.0269 | 218.1833 | 1 | No
| 1872984 | 2025-12-02 | 17:40 | 2025-12-02 | 19:25 | K21 | GARDINER | Urban | Overloads |  | 16.17 | 1688.418 | 104.4167 | 1 | No
| 1872987 | 2025-12-02 | 17:55 | 2025-12-02 | 20:35 | LWN21 | LANGWARRIN | Rural Short | Overloads |  | 3 | 478.7499 | 159.5833 | 1 | No
| 1872993 | 2025-12-02 | 18:32 | 2025-12-02 | 21:30 | CRM23 | CARRUM | Urban | Overloads |  | 9.57 | 1702.9815 | 177.95 | 1 | No
| 1872998 | 2025-12-02 | 18:50 | 2025-12-02 | 22:30 | HGS22 | HASTINGS | Rural Short | Asset Failure | Distribution substation | 1 | 219.0167 | 219.0167 | 1 | No
| 1873001 | 2025-12-02 | 18:53 | 2025-12-02 | 20:26 | CFD14 | CAULFIELD | Urban | Overloads |  | 19.14 | 1771.407 | 92.55 | 1 | No
| 1873006 | 2025-12-02 | 19:35 | 2025-12-02 | 21:16 | K21 | GARDINER | Urban | Weather |  | 24.09 | 2418.636 | 100.4 | 1 | No
| 1873008 | 2025-12-02 | 19:43 | 2025-12-02 | 20:30 | K21 | GARDINER | Urban | Asset Failure | LV | 16.17 | 753.792 | 46.6167 | 1 | No
| 1873017 | 2025-12-02 | 21:17 | 2025-12-02 | 22:23 | GW10 | GLEN WAVERLEY | Urban | Overloads |  | 29.7 | 1960.696 | 66.0167 | 1 | No
| 1873026 | 2025-12-02 | 22:10 | 13/02/2025 | 0:54 | DMA24 | DROMANA | Rural Short | Other | XXX | 1 | 163.45 | 163.45 | 1 | No
| 1873034 | 2025-12-02 | 22:46 | 13/02/2025 | 0:45 | OAK34 | OAKLEIGH | Urban | Third Party | Vehicle Impact | 5.36 | 632.748 | 118.05 | 1 | No
| 1873045 | 13/02/2025 | 1:33 | 13/02/2025 | 8:06 | NB25 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 392.2833 | 392.2833 | 1 | No
| 1873046 | 13/02/2025 | 2:46 | 13/02/2025 | 13:52 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 665.7 | 665.7 | 1 | No
| 1873049 | 13/02/2025 | 4:40 | 13/02/2025 | 8:25 | SH32 | SURREY HILLS | Urban | Asset Failure | LV | 1 | 225.3667 | 225.3667 | 1 | No
| 1873057 | 13/02/2025 | 5:18 | 13/02/2025 | 12:30 | SVW45 | SPRINGVALE WEST | Urban | Third Party | Other | 2 | 863.8 | 431.9 | 1 | No
| 1873072 | 13/02/2025 | 7:17 | 13/02/2025 | 9:34 | BR15 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 136.75 | 136.75 | 1 | No
| 1873148 | 13/02/2025 | 7:53 | 13/02/2025 | 9:42 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 108.7833 | 108.7833 | 1 | No
| 1873052 | 13/02/2025 | 8:00 | 13/02/2025 | 8:53 | BH22 | BOX HILL | Urban | Asset Failure | LV | 1 | 53 | 53 | 1 | No
| 1873107 | 13/02/2025 | 8:17 | 13/02/2025 | 13:58 | SS12 | SPRINGVALE SOUTH | Urban | Overloads |  | 1 | 340.7167 | 340.7167 | 1 | No
| 1873137 | 13/02/2025 | 9:00 | 13/02/2025 | 9:47 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 215 | 10019 | 46.6 | 1 | No
| 1873137 | 13/02/2025 | 9:00 | 13/02/2025 | 9:48 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1456 | 69354.0848 | 47.6333 | 2 | No
| 1873137 | 13/02/2025 | 9:00 | 13/02/2025 | 9:52 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 617 | 31826.8961 | 51.5833 | 3 | No
| 1873137 | 13/02/2025 | 9:00 | 13/02/2025 | 9:53 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 113 | 6024.7871 | 53.3167 | 4 | No
| 1873137 | 13/02/2025 | 9:00 | 13/02/2025 | 10:19 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 247 | 19467.7249 | 78.8167 | 5 | No
| 1873137 | 13/02/2025 | 9:00 | 13/02/2025 | 11:12 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 177 | 23396.4441 | 132.1833 | 6 | No
| 1873137 | 13/02/2025 | 9:00 | 13/02/2025 | 11:32 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 34 | 5156.1 | 151.65 | 7 | No
| 1873137 | 13/02/2025 | 9:00 | 13/02/2025 | 11:34 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 34 | 5235.4322 | 153.9833 | 8 | No
| 1873137 | 13/02/2025 | 9:00 | 13/02/2025 | 15:03 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 40 | 14523.332 | 363.0833 | 9 | No
| 1873137 | 13/02/2025 | 9:00 | 13/02/2025 | 15:06 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 138 | 50418.3 | 365.35 | 10 | No
| 1873137 | 13/02/2025 | 9:00 | 13/02/2025 | 15:11 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 7425.334 | 371.2667 | 11 | No
| 1873168 | 13/02/2025 | 9:57 | 13/02/2025 | 12:15 | HGS22 | HASTINGS | Rural Short | Unknown | Unknown | 44.89 | 6221.754 | 138.6 | 1 | No
| 1873190 | 13/02/2025 | 10:26 | 13/02/2025 | 12:48 | HGS22 | HASTINGS | Rural Short | Unknown | Unknown | 7.92 | 1118.4363 | 141.2167 | 1 | No
| 1873201 | 13/02/2025 | 10:45 | 13/02/2025 | 12:05 | EW9 | ELWOOD | Urban | Asset Failure | HV | 90.42 | 7207.984 | 79.7167 | 1 | No
| 1873222 | 13/02/2025 | 11:23 | 13/02/2025 | 16:08 | K21 | GARDINER | Urban | Asset Failure | LV | 1 | 285.0667 | 285.0667 | 1 | No
| 1873271 | 13/02/2025 | 12:49 | 13/02/2025 | 14:40 | NW21 | NUNAWADING | Urban | Overloads |  | 7.92 | 872.5203 | 110.1667 | 1 | No
| 1873259 | 13/02/2025 | 13:06 | 13/02/2025 | 14:06 | NW11 | NUNAWADING | Urban | Overloads |  | 1 | 60.8333 | 60.8333 | 1 | No
| 1873276 | 13/02/2025 | 13:28 | 13/02/2025 | 16:45 | CFD22 | CAULFIELD | Urban | Asset Failure | LV | 19.14 | 3752.0774 | 196.0333 | 1 | No
| 1873307 | 13/02/2025 | 14:46 | 13/02/2025 | 19:15 | SS11 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 268.7833 | 268.7833 | 1 | No
| 1873303 | 13/02/2025 | 15:24 | 13/02/2025 | 17:15 | RBD12 | ROSEBUD | Rural Short | Overloads |  | 1 | 111 | 111 | 1 | No
| 1873320 | 13/02/2025 | 15:30 | 13/02/2025 | 17:46 | MTN34 | MORNINGTON | Urban | Overloads |  | 1 | 136.5833 | 136.5833 | 1 | No
| 1873321 | 13/02/2025 | 15:32 | 13/02/2025 | 17:09 | KBH32 | KEYSBOROUGH | Urban | Third Party | Other | 1 | 96.5667 | 96.5667 | 1 | No
| 1873322 | 13/02/2025 | 15:32 | 13/02/2025 | 17:20 | HGS22 | HASTINGS | Rural Short | Unknown | Unknown | 1 | 107.3333 | 107.3333 | 1 | No
| 1873330 | 13/02/2025 | 16:05 | 13/02/2025 | 21:30 | GW8 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 324.2167 | 324.2167 | 1 | No
| 1873336 | 13/02/2025 | 16:13 | 13/02/2025 | 17:13 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6667 | 59.6667 | 1 | No
| 1873339 | 13/02/2025 | 16:15 | 13/02/2025 | 17:13 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 57.6167 | 57.6167 | 1 | No
| 1873340 | 13/02/2025 | 16:19 | 13/02/2025 | 17:19 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1873341 | 13/02/2025 | 16:19 | 13/02/2025 | 17:25 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 65.6833 | 65.6833 | 1 | No
| 1873343 | 13/02/2025 | 16:23 | 13/02/2025 | 17:23 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7667 | 59.7667 | 1 | No
| 1873344 | 13/02/2025 | 16:23 | 13/02/2025 | 17:23 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7667 | 59.7667 | 1 | No
| 1873346 | 13/02/2025 | 16:27 | 13/02/2025 | 17:29 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.6833 | 61.6833 | 1 | No
| 1873347 | 13/02/2025 | 16:27 | 13/02/2025 | 17:29 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.6667 | 61.6667 | 1 | No
| 1873350 | 13/02/2025 | 16:33 | 13/02/2025 | 17:33 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1873351 | 13/02/2025 | 16:33 | 13/02/2025 | 17:33 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1873352 | 13/02/2025 | 16:37 | 13/02/2025 | 17:39 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.7 | 61.7 | 1 | No
| 1873353 | 13/02/2025 | 16:39 | 13/02/2025 | 17:39 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.65 | 59.65 | 1 | No
| 1873354 | 13/02/2025 | 16:43 | 13/02/2025 | 17:43 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7333 | 59.7333 | 1 | No
| 1873356 | 13/02/2025 | 16:49 | 13/02/2025 | 17:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7667 | 59.7667 | 1 | No
| 1873357 | 13/02/2025 | 16:49 | 13/02/2025 | 17:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7667 | 59.7667 | 1 | No
| 1873329 | 13/02/2025 | 16:52 | 13/02/2025 | 21:35 | BR9 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 283.6833 | 283.6833 | 1 | No
| 1873358 | 13/02/2025 | 16:53 | 13/02/2025 | 17:53 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.5167 | 59.5167 | 1 | No
| 1873359 | 13/02/2025 | 16:54 | 13/02/2025 | 17:20 | HGS22 | HASTINGS | Rural Short | Unknown | Unknown | 1 | 25.6667 | 25.6667 | 1 | No
| 1873361 | 13/02/2025 | 16:57 | 13/02/2025 | 17:59 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.7667 | 61.7667 | 1 | No
| 1873362 | 13/02/2025 | 17:03 | 13/02/2025 | 18:03 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.65 | 59.65 | 1 | No
| 1873363 | 13/02/2025 | 17:03 | 13/02/2025 | 18:03 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6333 | 59.6333 | 1 | No
| 1873366 | 13/02/2025 | 17:07 | 13/02/2025 | 18:07 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1873367 | 13/02/2025 | 17:09 | 13/02/2025 | 18:09 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6667 | 59.6667 | 1 | No
| 1873368 | 13/02/2025 | 17:13 | 13/02/2025 | 18:13 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.75 | 59.75 | 1 | No
| 1873369 | 13/02/2025 | 17:13 | 13/02/2025 | 18:13 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.75 | 59.75 | 1 | No
| 1873370 | 13/02/2025 | 17:13 | 13/02/2025 | 18:15 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.75 | 61.75 | 1 | No
| 1873371 | 13/02/2025 | 17:15 | 13/02/2025 | 18:21 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 65.7 | 65.7 | 1 | No
| 1873373 | 13/02/2025 | 17:17 | 13/02/2025 | 18:17 | OR24 | ORMOND | Urban | Network Business | Network Error | 1 | 59.1833 | 59.1833 | 1 | No
| 1873377 | 13/02/2025 | 17:33 | 13/02/2025 | 18:33 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.65 | 59.65 | 1 | No
| 1873378 | 13/02/2025 | 17:37 | 13/02/2025 | 18:39 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.7333 | 61.7333 | 1 | No
| 1873380 | 13/02/2025 | 17:47 | 13/02/2025 | 18:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.6833 | 61.6833 | 1 | No
| 1873263 | 13/02/2025 | 17:48 | 13/02/2025 | 19:55 | STO22 | SORRENTO | Urban | Overloads |  | 1 | 127 | 127 | 1 | No
| 1873381 | 13/02/2025 | 17:53 | 13/02/2025 | 18:57 | OR24 | ORMOND | Urban | Overloads |  | 1 | 63.7167 | 63.7167 | 1 | No
| 1873382 | 13/02/2025 | 17:57 | 13/02/2025 | 18:59 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.8 | 61.8 | 1 | No
| 1873389 | 13/02/2025 | 18:24 | 13/02/2025 | 19:09 | EB14 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 681 | 30656.3727 | 45.0167 | 1 | No
| 1873389 | 13/02/2025 | 18:24 | 13/02/2025 | 19:21 | EB14 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 80 | 4590.664 | 57.3833 | 2 | No
| 1873389 | 13/02/2025 | 18:24 | 13/02/2025 | 19:30 | EB14 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 76 | 5000.8 | 65.8 | 3 | No
| 1873386 | 13/02/2025 | 18:35 | 13/02/2025 | 19:39 | NP24 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 64.0667 | 64.0667 | 1 | No
| 1873385 | 13/02/2025 | 19:40 | 13/02/2025 | 20:30 | MC34 | MORDIALLOC | Urban | Third Party | Other | 1 | 50 | 50 | 1 | No
| 1873402 | 13/02/2025 | 20:14 | 14/02/2025 | 0:43 | LD33 | LYNDALE | Urban | Weather |  | 76 | 20376.8692 | 268.1167 | 1 | No
| 1873405 | 13/02/2025 | 20:17 | 13/02/2025 | 21:30 | FTN14 | FRANKSTON | Urban | Weather |  | 62.31 | 4507.0879 | 72.3333 | 1 | No
| 1873414 | 13/02/2025 | 21:04 | 13/02/2025 | 22:44 | SH32 | SURREY HILLS | Urban | Unknown | Unknown | 1 | 100.2833 | 100.2833 | 1 | No
| 1873423 | 13/02/2025 | 21:26 | 13/02/2025 | 21:36 | DSH32 | DANDENONG SOUTH | Urban | Weather |  | 25 | 267.5 | 10.7 | 1 | No
| 1873423 | 13/02/2025 | 21:26 | 13/02/2025 | 21:42 | DSH32 | DANDENONG SOUTH | Urban | Weather |  | 81 | 1333.8027 | 16.4667 | 2 | No
| 1873423 | 13/02/2025 | 21:26 | 13/02/2025 | 22:32 | DSH32 | DANDENONG SOUTH | Urban | Weather |  | 2 | 131.4334 | 65.7167 | 3 | No
| 1873423 | 13/02/2025 | 21:26 | 14/02/2025 | 1:10 | DSH32 | DANDENONG SOUTH | Urban | Weather |  | 21 | 4698.0507 | 223.7167 | 4 | No
| 1873428 | 13/02/2025 | 23:32 | 14/02/2025 | 2:10 | MGE21 | MULGRAVE | Urban | Weather |  | 12.06 | 1896.0334 | 157.2167 | 1 | No
| 1873431 | 14/02/2025 | 1:01 | 14/02/2025 | 11:15 | RWT24 | RINGWOOD | Urban | Third Party | Other | 2 | 1229.4 | 614.7 | 1 | No
| 1873436 | 14/02/2025 | 2:21 | 14/02/2025 | 3:27 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 1.34 | 87.167 | 65.05 | 1 | No
| 1873442 | 14/02/2025 | 3:09 | 14/02/2025 | 4:40 | HT10 | HEATHERTON | Urban | Animal | Animal impact | 75.71 | 6836.613 | 90.3 | 1 | No
| 1873517 | 14/02/2025 | 8:46 | 14/02/2025 | 12:21 | DC2 | DONCASTER | Urban | Overloads |  | 1 | 214.5833 | 214.5833 | 1 | No
| 1873429 | 14/02/2025 | 9:13 | 14/02/2025 | 12:35 | K34 | GARDINER | Urban | Asset Failure | LV | 1 | 202.8167 | 202.8167 | 1 | No
| 1873360 | 14/02/2025 | 9:22 | 14/02/2025 | 10:23 | MC21 | MORDIALLOC | Urban | Third Party | Other | 1 | 61.4 | 61.4 | 1 | No
| 1873587 | 14/02/2025 | 10:59 | 14/02/2025 | 13:12 | DN6 | DANDENONG | Urban | Unknown | Unknown | 1 | 132.6333 | 132.6333 | 1 | No
| 1873605 | 14/02/2025 | 11:54 | 14/02/2025 | 15:35 | CRM15 | CARRUM | Urban | Third Party | Other | 1 | 221.1667 | 221.1667 | 1 | No
| 1873619 | 14/02/2025 | 12:20 | 14/02/2025 | 15:30 | NB21 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 189.3333 | 189.3333 | 1 | No
| 1873678 | 14/02/2025 | 15:02 | 14/02/2025 | 20:18 | EM2 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 315.2833 | 315.2833 | 1 | No
| 1873711 | 14/02/2025 | 21:44 | 14/02/2025 | 22:46 | RWT34 | RINGWOOD | Urban | Unknown | Unknown | 72.36 | 4419.9876 | 61.0833 | 1 | No
| 1873715 | 15/02/2025 | 0:24 | 15/02/2025 | 1:23 | STO14 | SORRENTO | Rural Short | Unknown | Unknown | 40.2 | 2342.9887 | 58.2833 | 1 | No
| 1873720 | 15/02/2025 | 3:17 | 15/02/2025 | 4:55 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 6 | 585.9 | 97.65 | 1 | No
| 1873723 | 15/02/2025 | 3:20 | 15/02/2025 | 8:51 | CRM15 | CARRUM | Urban | Animal | Animal impact | 1 | 330.2667 | 330.2667 | 1 | No
| 1873728 | 15/02/2025 | 5:18 | 15/02/2025 | 6:23 | STO14 | SORRENTO | Rural Short | Asset Failure | Distribution substation | 60 | 3921 | 65.35 | 1 | No
| 1873710 | 15/02/2025 | 7:07 | 15/02/2025 | 9:34 | DC7 | DONCASTER | Urban | Asset Failure | LV | 1 | 147.25 | 147.25 | 1 | No
| 1873756 | 15/02/2025 | 7:56 | 15/02/2025 | 9:50 | HGS22 | HASTINGS | Rural Short | Asset Failure | Distribution substation | 24 | 2734.8 | 113.95 | 1 | No
| 1873782 | 15/02/2025 | 11:27 | 15/02/2025 | 14:31 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 2 | 367.8334 | 183.9167 | 1 | No
| 1873783 | 15/02/2025 | 11:32 | 15/02/2025 | 14:29 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 177.3667 | 177.3667 | 1 | No
| 1873784 | 15/02/2025 | 11:35 | 15/02/2025 | 14:41 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 186.5167 | 186.5167 | 1 | No
| 1873786 | 15/02/2025 | 11:38 | 15/02/2025 | 14:41 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 4 | 734.6668 | 183.6667 | 1 | No
| 1873794 | 15/02/2025 | 12:30 | 15/02/2025 | 16:46 | DSH33 | DANDENONG SOUTH | Urban | Third Party | Other | 1 | 256.8833 | 256.8833 | 1 | No
| 1873801 | 15/02/2025 | 13:51 | 15/02/2025 | 15:25 | RBD23 | ROSEBUD | Urban | Asset Failure | HV | 343 | 32219.1219 | 93.9333 | 1 | No
| 1873814 | 15/02/2025 | 14:53 | 15/02/2025 | 16:15 | DC12 | DONCASTER | Urban | Asset Failure | LV | 38.08 | 3129.5401 | 82.1833 | 1 | No
| 1873820 | 15/02/2025 | 15:56 | 15/02/2025 | 17:44 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 107.6 | 107.6 | 1 | No
| 1873823 | 15/02/2025 | 16:21 | 15/02/2025 | 17:37 | CDA22 | CLARINDA | Urban | Weather |  | 20 | 1510 | 75.5 | 1 | No
| 1873840 | 15/02/2025 | 17:36 | 15/02/2025 | 18:35 | WD26 | WEST DONCASTER | Urban | Weather |  | 72.36 | 4265.622 | 58.95 | 1 | No
| 1873839 | 15/02/2025 | 17:37 | 15/02/2025 | 18:24 | SVW45 | SPRINGVALE WEST | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 18.76 | 873.9027 | 46.5833 | 1 | No
| 1873849 | 15/02/2025 | 18:25 | 15/02/2025 | 20:40 | CRM33 | CARRUM | Urban | Unknown | Unknown | 369 | 49765.8123 | 134.8667 | 1 | No
| 1873867 | 15/02/2025 | 19:14 | 15/02/2025 | 21:13 | LWN34 | LANGWARRIN | Urban | Animal | Animal impact | 1.34 | 159.1474 | 118.7667 | 1 | No
| 1873868 | 15/02/2025 | 21:03 | 15/02/2025 | 23:06 | M33 | MENTONE | Urban | Asset Failure | LV | 1 | 122.1 | 122.1 | 1 | No
| 1873876 | 15/02/2025 | 22:08 | 15/02/2025 | 23:45 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 477 | 46467.7659 | 97.4167 | 1 | No
| 1873876 | 15/02/2025 | 22:08 | 15/02/2025 | 23:46 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 20 | 1972 | 98.6 | 2 | No
| 1873879 | 15/02/2025 | 22:23 | 16/02/2025 | 0:45 | BW32 | BURWOOD | Urban | Animal | Animal impact | 64 | 9076.2688 | 141.8167 | 1 | No
| 1873885 | 15/02/2025 | 22:26 | 16/02/2025 | 0:14 | LWN21 | LANGWARRIN | Rural Short | Animal | Animal impact | 20.1 | 2159.0757 | 107.4167 | 1 | No
| 1873896 | 16/02/2025 | 7:28 | 16/02/2025 | 9:46 | DN7 | DANDENONG | Urban | Asset Failure | LV | 1 | 138 | 138 | 1 | No
| 1873909 | 16/02/2025 | 11:52 | 16/02/2025 | 13:00 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 1 | 68.0667 | 68.0667 | 1 | No
| 1873925 | 16/02/2025 | 12:38 | 16/02/2025 | 14:34 | SS11 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 115.05 | 115.05 | 1 | No
| 1873926 | 16/02/2025 | 13:48 | 16/02/2025 | 16:07 | RD4 | RIVERSDALE | Urban | Asset Failure | LV | 1 | 139.2167 | 139.2167 | 1 | No
| 1873935 | 16/02/2025 | 15:13 | 16/02/2025 | 16:41 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 87.6833 | 87.6833 | 1 | No
| 1873977 | 16/02/2025 | 20:21 | 16/02/2025 | 21:46 | DN11 | DANDENONG | Urban | Asset Failure | Distribution substation | 44.55 | 3786.75 | 85 | 1 | No
| 1873979 | 16/02/2025 | 21:32 | 16/02/2025 | 22:41 | GW7 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 69.1167 | 69.1167 | 1 | No
| 1873982 | 17/02/2025 | 3:02 | 17/02/2025 | 4:40 | STO22 | SORRENTO | Urban | Animal | Animal impact | 80 | 7802.664 | 97.5333 | 1 | No
| 1874007 | 17/02/2025 | 4:55 | 17/02/2025 | 8:21 | RBD12 | ROSEBUD | Rural Short | Animal | Animal impact | 24.79 | 5084.843 | 205.1167 | 1 | No
| 1873996 | 17/02/2025 | 7:15 | 17/02/2025 | 9:56 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 161.6833 | 161.6833 | 1 | No
| 1874271 | 17/02/2025 | 8:58 | 17/02/2025 | 16:55 | DN9 | DANDENONG | Urban | Asset Failure | Distribution substation | 3 | 1428.8499 | 476.2833 | 1 | No
| 1874073 | 17/02/2025 | 9:29 | 17/02/2025 | 12:08 | NB25 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 158.8667 | 158.8667 | 1 | No
| 1874060 | 17/02/2025 | 10:49 | 17/02/2025 | 13:03 | CFD24 | CAULFIELD | Urban | Asset Failure | LV | 1 | 134.5 | 134.5 | 1 | No
| 1874163 | 17/02/2025 | 12:03 | 17/02/2025 | 14:25 | BU21 | BULLEEN | Urban | Asset Failure | LV | 1 | 141.25 | 141.25 | 1 | No
| 1874181 | 17/02/2025 | 12:46 | 17/02/2025 | 13:50 | LWN35 | LANGWARRIN | Urban | Weather |  | 1 | 63.5167 | 63.5167 | 1 | No
| 1874259 | 17/02/2025 | 15:59 | 17/02/2025 | 17:24 | HGS22 | HASTINGS | Rural Short | Weather |  | 3 | 255.3 | 85.1 | 1 | No
| 1874273 | 17/02/2025 | 16:22 | 17/02/2025 | 16:28 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | HV | 953 | 5146.2 | 5.4 | 1 | No
| 1874281 | 17/02/2025 | 18:15 | 18/02/2025 | 0:40 | MGE31 | MULGRAVE | Urban | Asset Failure | LV | 1 | 384.4333 | 384.4333 | 1 | No
| 1874287 | 17/02/2025 | 19:59 | 17/02/2025 | 20:20 | GW7 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 21.2 | 21.2 | 1 | No
| 1874299 | 17/02/2025 | 21:54 | 17/02/2025 | 22:55 | LD32 | LYNDALE | Urban | Network Business | Switching and protection error | 1 | 60.8 | 60.8 | 1 | No
| 1874309 | 18/02/2025 | 1:24 | 18/02/2025 | 2:57 | MTN35 | MORNINGTON | Rural Short | Third Party | Other | 25 | 2322.0825 | 92.8833 | 1 | No
| 1874313 | 18/02/2025 | 6:49 | 18/02/2025 | 8:51 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 1 | 121.7833 | 121.7833 | 1 | No
| 1874352 | 18/02/2025 | 8:55 | 18/02/2025 | 9:15 | K34 | GARDINER | Urban | Asset Failure | LV | 3 | 58.95 | 19.65 | 1 | No
| 1874519 | 18/02/2025 | 15:23 | 18/02/2025 | 16:44 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 1 | 80.4667 | 80.4667 | 1 | No
| 1874521 | 18/02/2025 | 15:27 | 18/02/2025 | 18:03 | DMA14 | DROMANA | Urban | Asset Failure | LV | 140 | 21856.338 | 156.1167 | 1 | No
| 1874529 | 18/02/2025 | 15:49 | 18/02/2025 | 20:58 | MC21 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 308.05 | 308.05 | 1 | No
| 1874539 | 18/02/2025 | 17:19 | 18/02/2025 | 18:45 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 1 | 86.7 | 86.7 | 1 | No
| 1874588 | 19/02/2025 | 1:58 | 19/02/2025 | 2:55 | NW31 | NUNAWADING | Urban | Animal | Animal impact | 189 | 10653.3063 | 56.3667 | 1 | No
| 1874592 | 19/02/2025 | 3:06 | 19/02/2025 | 4:10 | NW22 | NUNAWADING | Urban | Animal | Other | 71 | 4501.4 | 63.4 | 1 | No
| 1874601 | 19/02/2025 | 3:42 | 19/02/2025 | 4:37 | STO14 | SORRENTO | Rural Short | Animal | Animal impact | 129 | 7060.5957 | 54.7333 | 1 | No
| 1874603 | 19/02/2025 | 5:47 | 19/02/2025 | 7:06 | OR35 | ORMOND | Urban | Animal | Animal impact | 72.36 | 5670.6144 | 78.3667 | 1 | No
| 1874607 | 19/02/2025 | 5:59 | 19/02/2025 | 7:10 | EM9 | EAST MALVERN | Urban | Third Party | Vehicle Impact | 251 | 17967.4083 | 71.5833 | 1 | No
| 1874607 | 19/02/2025 | 5:59 | 19/02/2025 | 7:53 | EM9 | EAST MALVERN | Urban | Third Party | Vehicle Impact | 35 | 3994.0845 | 114.1167 | 2 | No
| 1874607 | 19/02/2025 | 5:59 | 19/02/2025 | 7:56 | EM9 | EAST MALVERN | Urban | Third Party | Vehicle Impact | 49 | 5720.75 | 116.75 | 3 | No
| 1874607 | 19/02/2025 | 5:59 | 19/02/2025 | 7:56 | EM9 | EAST MALVERN | Urban | Third Party | Vehicle Impact | 37 | 4325.9179 | 116.9167 | 4 | No
| 1874607 | 19/02/2025 | 5:59 | 19/02/2025 | 8:14 | EM9 | EAST MALVERN | Urban | Third Party | Vehicle Impact | 41 | 5546.6153 | 135.2833 | 5 | No
| 1874607 | 19/02/2025 | 5:59 | 19/02/2025 | 8:16 | EM9 | EAST MALVERN | Urban | Third Party | Vehicle Impact | 82 | 11232.6306 | 136.9833 | 6 | No
| 1874607 | 19/02/2025 | 5:59 | 19/02/2025 | 16:48 | EM9 | EAST MALVERN | Urban | Third Party | Vehicle Impact | 138 | 89596.5 | 649.25 | 7 | No
| 1874678 | 19/02/2025 | 9:01 | 19/02/2025 | 11:02 | EB32 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 121.7167 | 121.7167 | 1 | No
| 1874765 | 19/02/2025 | 9:50 | 19/02/2025 | 11:06 | NP23 | NOBLE PARK | Urban | Unknown | Unknown | 66.33 | 5083.0868 | 76.6333 | 1 | No
| 1874742 | 19/02/2025 | 10:19 | 19/02/2025 | 13:17 | DN13 | DANDENONG | Urban | Unknown | Unknown | 1 | 178.4833 | 178.4833 | 1 | No
| 1874754 | 19/02/2025 | 10:38 | 19/02/2025 | 12:25 | MTN22 | MORNINGTON | Rural Short | Asset Failure | Distribution substation | 3.35 | 357.11 | 106.6 | 1 | No
| 1874772 | 19/02/2025 | 11:30 | 19/02/2025 | 17:19 | DN24 | DANDENONG | Urban | Asset Failure | LV | 1 | 349.4 | 349.4 | 1 | No
| 1874794 | 19/02/2025 | 12:15 | 19/02/2025 | 15:00 | DC2 | DONCASTER | Urban | Third Party | Other | 1 | 164.95 | 164.95 | 1 | No
| 1874889 | 19/02/2025 | 16:37 | 19/02/2025 | 18:10 | MTN21 | MORNINGTON | Urban | Unknown | Unknown | 1 | 92.15 | 92.15 | 1 | No
| 1874886 | 19/02/2025 | 17:26 | 19/02/2025 | 20:38 | RBD13 | ROSEBUD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 3 | 577.4499 | 192.4833 | 1 | No
| 1874912 | 19/02/2025 | 18:59 | 20/02/2025 | 0:53 | RWT12 | RINGWOOD | Urban | Asset Failure | LV | 8 | 2828.1336 | 353.5167 | 1 | No
| 1874921 | 19/02/2025 | 19:42 | 19/02/2025 | 21:11 | NP16 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 89.8 | 89.8 | 1 | No
| 1874958 | 20/02/2025 | 8:01 | 20/02/2025 | 10:35 | BU25 | BULLEEN | Urban | Asset Failure | LV | 1 | 154 | 154 | 1 | No
| 1874986 | 20/02/2025 | 8:28 | 20/02/2025 | 11:30 | EM7 | EAST MALVERN | Urban | Third Party | Other | 1 | 181.8667 | 181.8667 | 1 | No
| 1875028 | 20/02/2025 | 9:33 | 20/02/2025 | 12:00 | RWT35 | RINGWOOD | Urban | Asset Failure | LV | 1 | 147 | 147 | 1 | No
| 1875046 | 20/02/2025 | 9:59 | 20/02/2025 | 11:30 | DVY21 | DANDENONG VALLEY | Urban | Asset Failure | LV | 1 | 90.8 | 90.8 | 1 | No
| 1875047 | 20/02/2025 | 9:59 | 20/02/2025 | 11:30 | FTN25 | FRANKSTON | Urban | Animal | Animal impact | 41.54 | 3768.3717 | 90.7167 | 1 | No
| 1875068 | 20/02/2025 | 10:46 | 20/02/2025 | 12:48 | BU25 | BULLEEN | Urban | Asset Failure | LV | 1 | 121.5667 | 121.5667 | 1 | No
| 1875115 | 20/02/2025 | 12:39 | 20/02/2025 | 14:08 | WD34 | WEST DONCASTER | Urban | Third Party | Other | 4.95 | 440.7148 | 89.0333 | 1 | No
| 1875126 | 20/02/2025 | 13:05 | 20/02/2025 | 15:56 | FTN14 | FRANKSTON | Urban | Third Party | Other | 1 | 171.4167 | 171.4167 | 1 | No
| 1875131 | 20/02/2025 | 13:14 | 20/02/2025 | 15:46 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 151.85 | 151.85 | 1 | No
| 1875153 | 20/02/2025 | 14:22 | 20/02/2025 | 15:20 | MGE23 | MULGRAVE | Urban | Third Party | Other | 1 | 58.0833 | 58.0833 | 1 | No
| 1875171 | 20/02/2025 | 14:52 | 20/02/2025 | 18:06 | BH33 | BOX HILL | Urban | Asset Failure | LV | 1 | 193.3 | 193.3 | 1 | No
| 1875184 | 20/02/2025 | 17:09 | 20/02/2025 | 20:10 | DC2 | DONCASTER | Urban | Asset Failure | LV | 1 | 181.5333 | 181.5333 | 1 | No
| 1875221 | 20/02/2025 | 18:52 | 20/02/2025 | 21:11 | BR13 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 138.8833 | 138.8833 | 1 | No
| 1875227 | 20/02/2025 | 20:17 | 20/02/2025 | 21:19 | SV33 | SPRINGVALE | Urban | Asset Failure | HV | 25.41 | 1574.1495 | 61.95 | 1 | No
| 1874660 | 20/02/2025 | 21:26 | 21/02/2025 | 0:19 | SS13 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 173.6 | 173.6 | 1 | No
| 1875402 | 21/02/2025 | 12:37 | 21/02/2025 | 14:26 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 109.5 | 109.5 | 1 | No
| 1875461 | 21/02/2025 | 15:16 | 21/02/2025 | 20:20 | DMA14 | DROMANA | Urban | Third Party | Other | 1 | 303.3333 | 303.3333 | 1 | No
| 1875470 | 21/02/2025 | 16:22 | 21/02/2025 | 21:30 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 307.2833 | 307.2833 | 1 | No
| 1875484 | 21/02/2025 | 21:26 | 21/02/2025 | 22:32 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 66 | 66 | 1 | No
| 1875498 | 21/02/2025 | 21:29 | 21/02/2025 | 22:54 | RBD23 | ROSEBUD | Urban | Animal | Animal impact | 1 | 84.9833 | 84.9833 | 1 | No
| 1875501 | 21/02/2025 | 22:11 | 22/02/2025 | 0:30 | CDA11 | CLARINDA | Urban | Animal | Animal impact | 2.68 | 370.5548 | 138.2667 | 1 | No
| 1875508 | 22/02/2025 | 0:47 | 22/02/2025 | 2:00 | CRM13 | CARRUM | Urban | Animal | Animal impact | 60.3 | 4398.885 | 72.95 | 1 | No
| 1875524 | 22/02/2025 | 1:29 | 22/02/2025 | 3:18 | NP23 | NOBLE PARK | Urban | Animal | Animal impact | 65.66 | 7143.808 | 108.8 | 1 | No
| 1875539 | 22/02/2025 | 8:21 | 22/02/2025 | 10:42 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 141.05 | 141.05 | 1 | No
| 1875553 | 22/02/2025 | 10:02 | 22/02/2025 | 13:03 | NP14 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 181.25 | 181.25 | 1 | No
| 1875585 | 22/02/2025 | 13:20 | 22/02/2025 | 15:11 | BT16 | BENTLEIGH | Urban | Asset Failure | Distribution substation | 111 | 12243.3 | 110.3 | 1 | No
| 1875587 | 22/02/2025 | 13:22 | 22/02/2025 | 16:14 | M22 | MENTONE | Urban | Asset Failure | LV | 35.64 | 6113.4468 | 171.5333 | 1 | No
| 1875591 | 22/02/2025 | 13:40 | 22/02/2025 | 16:44 | SR35 | SANDRINGHAM | Urban | Asset Failure | LV | 18.48 | 3408.636 | 184.45 | 1 | No
| 1875595 | 22/02/2025 | 14:12 | 23/02/2025 | 0:48 | CFD14 | CAULFIELD | Urban | Asset Failure | LV | 1 | 636.6833 | 636.6833 | 1 | No
| 1875618 | 22/02/2025 | 17:03 | 22/02/2025 | 18:09 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 65.85 | 65.85 | 1 | No
| 1875622 | 22/02/2025 | 17:13 | 22/02/2025 | 18:13 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6167 | 59.6167 | 1 | No
| 1875623 | 22/02/2025 | 17:13 | 22/02/2025 | 18:13 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.6167 | 59.6167 | 1 | No
| 1875626 | 22/02/2025 | 17:19 | 22/02/2025 | 18:19 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.8333 | 59.8333 | 1 | No
| 1875634 | 22/02/2025 | 17:22 | 22/02/2025 | 19:55 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 152.5833 | 152.5833 | 1 | No
| 1875628 | 22/02/2025 | 17:23 | 22/02/2025 | 18:25 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.7333 | 61.7333 | 1 | No
| 1875629 | 22/02/2025 | 17:23 | 22/02/2025 | 18:25 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.7333 | 61.7333 | 1 | No
| 1875631 | 22/02/2025 | 17:24 | 22/02/2025 | 18:45 | FSH11 | FRANKSTON SOUTH | Urban | Overloads |  | 37.95 | 3067.6237 | 80.8333 | 1 | No
| 1875630 | 22/02/2025 | 17:27 | 22/02/2025 | 18:27 | OR24 | ORMOND | Urban | Overloads |  | 1 | 60.0167 | 60.0167 | 1 | No
| 1875639 | 22/02/2025 | 17:39 | 22/02/2025 | 18:39 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1875642 | 22/02/2025 | 17:47 | 22/02/2025 | 18:55 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 67.5333 | 67.5333 | 1 | No
| 1875645 | 22/02/2025 | 17:49 | 22/02/2025 | 20:12 | NW31 | NUNAWADING | Urban | Asset Failure | LV | 1 | 143.9 | 143.9 | 1 | No
| 1875646 | 22/02/2025 | 17:53 | 22/02/2025 | 18:55 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.75 | 61.75 | 1 | No
| 1875647 | 22/02/2025 | 17:53 | 22/02/2025 | 18:55 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 61.75 | 61.75 | 1 | No
| 1875649 | 22/02/2025 | 17:57 | 22/02/2025 | 18:59 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.8333 | 61.8333 | 1 | No
| 1875650 | 22/02/2025 | 17:59 | 22/02/2025 | 18:59 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1875651 | 22/02/2025 | 17:59 | 22/02/2025 | 18:59 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1875652 | 22/02/2025 | 17:59 | 22/02/2025 | 19:01 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 61.7833 | 61.7833 | 1 | No
| 1875653 | 22/02/2025 | 18:03 | 22/02/2025 | 19:09 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 65.6833 | 65.6833 | 1 | No
| 1875654 | 22/02/2025 | 18:03 | 22/02/2025 | 19:09 | OR24 | ORMOND | Urban | Overloads |  | 1 | 65.6833 | 65.6833 | 1 | No
| 1875657 | 22/02/2025 | 18:05 | 22/02/2025 | 19:09 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 63.8167 | 63.8167 | 1 | No
| 1875658 | 22/02/2025 | 18:07 | 22/02/2025 | 19:09 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 61.7667 | 61.7667 | 1 | No
| 1875661 | 22/02/2025 | 18:08 | 22/02/2025 | 19:40 | BU25 | BULLEEN | Urban | Overloads |  | 18.48 | 1694.9246 | 91.7167 | 1 | No
| 1875659 | 22/02/2025 | 18:09 | 22/02/2025 | 19:09 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1875660 | 22/02/2025 | 18:09 | 22/02/2025 | 19:09 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1875663 | 22/02/2025 | 18:13 | 22/02/2025 | 19:13 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.8 | 59.8 | 1 | No
| 1875664 | 22/02/2025 | 18:13 | 22/02/2025 | 19:13 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 59.8 | 59.8 | 1 | No
| 1875665 | 22/02/2025 | 18:13 | 22/02/2025 | 19:13 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1875666 | 22/02/2025 | 18:13 | 22/02/2025 | 19:13 | CRM23 | CARRUM | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1875669 | 22/02/2025 | 18:19 | 22/02/2025 | 19:23 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 63.8167 | 63.8167 | 1 | No
| 1875670 | 22/02/2025 | 18:19 | 22/02/2025 | 19:25 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 65.8167 | 65.8167 | 1 | No
| 1875671 | 22/02/2025 | 18:19 | 22/02/2025 | 19:23 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 63.8167 | 63.8167 | 1 | No
| 1875673 | 22/02/2025 | 18:20 | 22/02/2025 | 19:11 | NW31 | NUNAWADING | Urban | Overloads |  | 38.28 | 1938.882 | 50.65 | 1 | No
| 1875675 | 22/02/2025 | 18:25 | 22/02/2025 | 19:25 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 59.6833 | 59.6833 | 1 | No
| 1875676 | 22/02/2025 | 18:25 | 22/02/2025 | 19:23 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 57.6833 | 57.6833 | 1 | No
| 1875677 | 22/02/2025 | 18:25 | 22/02/2025 | 19:25 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6833 | 59.6833 | 1 | No
| 1875678 | 22/02/2025 | 18:25 | 22/02/2025 | 19:29 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 63.6667 | 63.6667 | 1 | No
| 1875684 | 22/02/2025 | 18:33 | 22/02/2025 | 19:39 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 65.8333 | 65.8333 | 1 | No
| 1875685 | 22/02/2025 | 18:33 | 22/02/2025 | 19:39 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 65.8333 | 65.8333 | 1 | No
| 1875686 | 22/02/2025 | 18:33 | 22/02/2025 | 19:39 | OR24 | ORMOND | Urban | Overloads |  | 1 | 65.8333 | 65.8333 | 1 | No
| 1875687 | 22/02/2025 | 18:33 | 22/02/2025 | 19:39 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 65.8333 | 65.8333 | 1 | No
| 1875691 | 22/02/2025 | 18:39 | 22/02/2025 | 19:39 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1875692 | 22/02/2025 | 18:39 | 22/02/2025 | 19:39 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1875693 | 22/02/2025 | 18:39 | 22/02/2025 | 19:39 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 59.6833 | 59.6833 | 1 | No
| 1875694 | 22/02/2025 | 18:39 | 22/02/2025 | 19:45 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 65.6833 | 65.6833 | 1 | No
| 1875698 | 22/02/2025 | 18:47 | 22/02/2025 | 19:49 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.6833 | 61.6833 | 1 | No
| 1875701 | 22/02/2025 | 18:53 | 22/02/2025 | 19:53 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1875703 | 22/02/2025 | 18:57 | 22/02/2025 | 20:13 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 75.8 | 75.8 | 1 | No
| 1875704 | 22/02/2025 | 18:57 | 22/02/2025 | 20:05 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 67.8 | 67.8 | 1 | No
| 1875705 | 22/02/2025 | 18:59 | 22/02/2025 | 19:59 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.75 | 59.75 | 1 | No
| 1875707 | 22/02/2025 | 19:03 | 22/02/2025 | 20:03 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.8333 | 59.8333 | 1 | No
| 1875709 | 22/02/2025 | 19:09 | 22/02/2025 | 20:09 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1875711 | 22/02/2025 | 19:13 | 22/02/2025 | 20:13 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1875712 | 22/02/2025 | 19:17 | 22/02/2025 | 20:19 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.6833 | 61.6833 | 1 | No
| 1875713 | 22/02/2025 | 19:23 | 22/02/2025 | 20:25 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.7333 | 61.7333 | 1 | No
| 1875714 | 22/02/2025 | 19:27 | 22/02/2025 | 20:29 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.8 | 61.8 | 1 | No
| 1875718 | 22/02/2025 | 19:33 | 22/02/2025 | 20:33 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6667 | 59.6667 | 1 | No
| 1875719 | 22/02/2025 | 19:33 | 22/02/2025 | 20:33 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6667 | 59.6667 | 1 | No
| 1875722 | 22/02/2025 | 19:39 | 22/02/2025 | 20:45 | OAK26 | OAKLEIGH | Urban | Overloads |  | 51.48 | 3361.644 | 65.3 | 1 | No
| 1875721 | 22/02/2025 | 19:42 | 22/02/2025 | 21:17 | FTN11 | FRANKSTON | Urban | Overloads |  | 42.24 | 3996.6094 | 94.6167 | 1 | No
| 1875720 | 22/02/2025 | 19:42 | 22/02/2025 | 20:42 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6333 | 59.6333 | 1 | No
| 1875723 | 22/02/2025 | 19:43 | 22/02/2025 | 20:43 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.6167 | 59.6167 | 1 | No
| 1875727 | 22/02/2025 | 19:47 | 22/02/2025 | 20:49 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 61.6833 | 61.6833 | 1 | No
| 1875729 | 22/02/2025 | 19:49 | 22/02/2025 | 22:03 | CRM23 | CARRUM | Urban | Overloads |  | 56.43 | 7535.2841 | 133.5333 | 1 | No
| 1875730 | 22/02/2025 | 19:49 | 22/02/2025 | 20:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.8167 | 59.8167 | 1 | No
| 1875734 | 22/02/2025 | 19:49 | 22/02/2025 | 21:08 | OAK26 | OAKLEIGH | Urban | Overloads |  | 25.08 | 1961.6748 | 78.2167 | 1 | No
| 1875736 | 22/02/2025 | 19:52 | 22/02/2025 | 22:15 | FSH11 | FRANKSTON SOUTH | Urban | Overloads |  | 23 | 3301.2659 | 143.5333 | 1 | No
| 1875731 | 22/02/2025 | 19:53 | 22/02/2025 | 20:55 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.7333 | 61.7333 | 1 | No
| 1875732 | 22/02/2025 | 19:53 | 22/02/2025 | 20:55 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.7333 | 61.7333 | 1 | No
| 1875733 | 22/02/2025 | 19:53 | 22/02/2025 | 20:53 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 59.7167 | 59.7167 | 1 | No
| 1875738 | 22/02/2025 | 19:57 | 22/02/2025 | 20:57 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 60 | 60 | 1 | No
| 1875739 | 22/02/2025 | 19:59 | 22/02/2025 | 20:59 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 59.9333 | 59.9333 | 1 | No
| 1875740 | 22/02/2025 | 20:03 | 22/02/2025 | 21:04 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.35 | 61.35 | 1 | No
| 1875741 | 22/02/2025 | 20:03 | 22/02/2025 | 21:03 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 59.6667 | 59.6667 | 1 | No
| 1875742 | 22/02/2025 | 20:04 | 22/02/2025 | 21:04 | CRM13 | CARRUM | Urban | Overloads |  | 1 | 60.15 | 60.15 | 1 | No
| 1875743 | 22/02/2025 | 20:09 | 22/02/2025 | 21:09 | BR4 | BEAUMARIS | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1875748 | 22/02/2025 | 20:19 | 22/02/2025 | 21:19 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.65 | 59.65 | 1 | No
| 1875751 | 22/02/2025 | 20:27 | 22/02/2025 | 21:29 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.65 | 61.65 | 1 | No
| 1875754 | 22/02/2025 | 20:39 | 22/02/2025 | 21:39 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7333 | 59.7333 | 1 | No
| 1875757 | 22/02/2025 | 20:43 | 22/02/2025 | 21:43 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.65 | 59.65 | 1 | No
| 1875759 | 22/02/2025 | 20:49 | 22/02/2025 | 21:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.6833 | 59.6833 | 1 | No
| 1875760 | 22/02/2025 | 20:49 | 22/02/2025 | 21:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.6833 | 59.6833 | 1 | No
| 1875764 | 22/02/2025 | 20:53 | 22/02/2025 | 21:53 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 59.7667 | 59.7667 | 1 | No
| 1875765 | 22/02/2025 | 20:55 | 22/02/2025 | 21:53 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 57.7167 | 57.7167 | 1 | No
| 1875768 | 22/02/2025 | 21:23 | 22/02/2025 | 22:29 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 65.8 | 65.8 | 1 | No
| 1875769 | 22/02/2025 | 21:26 | 22/02/2025 | 23:20 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 113.6167 | 113.6167 | 1 | No
| 1875770 | 22/02/2025 | 21:27 | 22/02/2025 | 22:29 | CRM15 | CARRUM | Urban | Overloads |  | 1 | 61.7167 | 61.7167 | 1 | No
| 1875771 | 22/02/2025 | 21:29 | 22/02/2025 | 22:29 | RBD24 | ROSEBUD | Urban | Overloads |  | 1 | 59.6667 | 59.6667 | 1 | No
| 1875783 | 23/02/2025 | 2:16 | 23/02/2025 | 2:26 | BU25 | BULLEEN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 831 | 7852.95 | 9.45 | 1 | No
| 1875783 | 23/02/2025 | 2:16 | 23/02/2025 | 2:29 | BU25 | BULLEEN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 379 | 4813.3 | 12.7 | 2 | No
| 1875783 | 23/02/2025 | 2:16 | 23/02/2025 | 3:32 | BU25 | BULLEEN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 583 | 44298.2639 | 75.9833 | 3 | No
| 1875791 | 23/02/2025 | 3:08 | 23/02/2025 | 6:23 | OR24 | ORMOND | Urban | Overloads |  | 29.7 | 5787.541 | 194.8667 | 1 | No
| 1875818 | 23/02/2025 | 3:42 | 23/02/2025 | 5:29 | HGS33 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 96 | 10206.4032 | 106.3167 | 1 | No
| 1875844 | 23/02/2025 | 4:18 | 23/02/2025 | 8:43 | LD2 | LYNDALE | Urban | Weather |  | 24 | 6362.4 | 265.1 | 1 | No
| 1875809 | 23/02/2025 | 4:21 | 23/02/2025 | 5:19 | MGE34 | MULGRAVE | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 636 | 36622.9788 | 57.5833 | 1 | No
| 1875809 | 23/02/2025 | 4:21 | 23/02/2025 | 5:19 | MGE34 | MULGRAVE | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 938 | 54497.8 | 58.1 | 2 | No
| 1875822 | 23/02/2025 | 6:59 | 23/02/2025 | 9:55 | LWN21 | LANGWARRIN | Rural Short | Weather |  | 4 | 702.8 | 175.7 | 1 | No
| 1875843 | 23/02/2025 | 8:38 | 23/02/2025 | 14:54 | LWN34 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 376.5 | 376.5 | 1 | No
| 1875846 | 23/02/2025 | 8:49 | 23/02/2025 | 11:01 | FSH23 | FRANKSTON SOUTH | Rural Short | Overloads |  | 1 | 132.2667 | 132.2667 | 1 | No
| 1875855 | 23/02/2025 | 9:28 | 23/02/2025 | 17:00 | BH31 | BOX HILL | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 1355.7 | 451.9 | 1 | No
| 1875866 | 23/02/2025 | 10:20 | 23/02/2025 | 14:30 | BR9 | BEAUMARIS | Urban | Asset Failure | LV | 67 | 16725.4311 | 249.6333 | 1 | No
| 1875881 | 23/02/2025 | 11:03 | 23/02/2025 | 14:58 | SS14 | SPRINGVALE SOUTH | Urban | Network Business | Switching and protection error | 23 | 5411.5159 | 235.2833 | 1 | No
| 1875905 | 23/02/2025 | 13:30 | 23/02/2025 | 17:04 | LWN23 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 214.1167 | 214.1167 | 1 | No
| 1875925 | 23/02/2025 | 15:24 | 23/02/2025 | 19:15 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 231 | 231 | 1 | No
| 1875863 | 23/02/2025 | 17:47 | 23/02/2025 | 20:18 | HT2 | HEATHERTON | Urban | Third Party | Other | 2 | 302 | 151 | 1 | No
| 1875940 | 23/02/2025 | 18:10 | 23/02/2025 | 19:54 | EM8 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 103.0167 | 103.0167 | 1 | No
| 1875960 | 23/02/2025 | 21:09 | 23/02/2025 | 22:19 | FTN12 | FRANKSTON | Urban | Animal | Animal impact | 67 | 4708.9811 | 70.2833 | 1 | No
| 1875962 | 23/02/2025 | 21:24 | 24/02/2025 | 0:07 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 1 | 162.9167 | 162.9167 | 1 | No
| 1875964 | 23/02/2025 | 21:52 | 24/02/2025 | 10:56 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 783.85 | 783.85 | 1 | No
| 1875968 | 23/02/2025 | 23:46 | 24/02/2025 | 1:24 | FTN25 | FRANKSTON | Urban | Animal | Other | 41.54 | 4084.7653 | 98.3333 | 1 | No
| 1875976 | 24/02/2025 | 5:05 | 24/02/2025 | 8:02 | HGS21 | HASTINGS | Rural Short | Unknown | Unknown | 503 | 89399.8499 | 177.7333 | 1 | No
| 1876010 | 24/02/2025 | 7:42 | 24/02/2025 | 8:33 | MGE34 | MULGRAVE | Urban | Animal | Other | 1 | 50.7333 | 50.7333 | 1 | No
| 1876028 | 24/02/2025 | 8:27 | 24/02/2025 | 8:32 | NP11 | NOBLE PARK | Urban | Network Business | Switching and protection error | 1 | 4.9667 | 4.9667 | 1 | No
| 1876068 | 24/02/2025 | 10:02 | 24/02/2025 | 12:50 | STO22 | SORRENTO | Urban | Asset Failure | LV | 1 | 167.3833 | 167.3833 | 1 | No
| 1876096 | 24/02/2025 | 11:30 | 24/02/2025 | 13:00 | WD36 | WEST DONCASTER | Urban | Third Party | Other | 46 | 4142.3 | 90.05 | 1 | No
| 1876165 | 24/02/2025 | 14:04 | 24/02/2025 | 18:30 | EM8 | EAST MALVERN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 265.05 | 265.05 | 1 | No
| 1876200 | 24/02/2025 | 16:42 | 24/02/2025 | 17:42 | DC10 | DONCASTER | Urban | Asset Failure | LV | 1 | 60.55 | 60.55 | 1 | No
| 1876218 | 24/02/2025 | 19:03 | 24/02/2025 | 20:00 | CDA21 | CLARINDA | Urban | Animal | Animal impact | 105 | 5948.25 | 56.65 | 1 | No
| 1876258 | 25/02/2025 | 7:46 | 25/02/2025 | 9:00 | NO3 | NOTTING HILL | Urban | Third Party | Other | 6 | 441.1998 | 73.5333 | 1 | No
| 1876314 | 25/02/2025 | 8:56 | 25/02/2025 | 10:30 | EB14 | EAST BURWOOD | Urban | Animal | Animal impact | 74.37 | 6951.1185 | 93.4667 | 1 | No
| 1876376 | 25/02/2025 | 11:05 | 25/02/2025 | 12:40 | M23 | MENTONE | Urban | Asset Failure | LV | 1 | 95.6167 | 95.6167 | 1 | No
| 1876367 | 25/02/2025 | 11:21 | 25/02/2025 | 12:08 | DC5 | DONCASTER | Urban | Asset Failure | LV | 1 | 47.5833 | 47.5833 | 1 | No
| 1876434 | 25/02/2025 | 13:13 | 25/02/2025 | 14:14 | MTN23 | MORNINGTON | Urban | Asset Failure | LV | 1 | 60.7167 | 60.7167 | 1 | No
| 1876512 | 25/02/2025 | 15:47 | 25/02/2025 | 18:20 | MTN35 | MORNINGTON | Rural Short | Animal | Animal impact | 4 | 611.6668 | 152.9167 | 1 | No
| 1876484 | 25/02/2025 | 15:47 | 25/02/2025 | 19:32 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 25 | 5619.5825 | 224.7833 | 1 | No
| 1876484 | 25/02/2025 | 16:19 | 25/02/2025 | 21:01 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 5 | 1414.3335 | 282.8667 | 1 | No
| 1876455 | 25/02/2025 | 16:45 | 25/02/2025 | 17:00 | DC5 | DONCASTER | Urban | Asset Failure | LV | 32 | 480 | 15 | 1 | No
| 1876553 | 25/02/2025 | 19:01 | 25/02/2025 | 22:35 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 4 | 853.6668 | 213.4167 | 1 | No
| 1876526 | 25/02/2025 | 19:59 | 25/02/2025 | 20:14 | LD2 | LYNDALE | Urban | Asset Failure | HV | 24 | 356.4 | 14.85 | 1 | No
| 1876560 | 25/02/2025 | 23:46 | 26/02/2025 | 13:17 | NO6 | NOTTING HILL | Urban | Third Party | Other | 1 | 811.0333 | 811.0333 | 1 | No
| 1876445 | 26/02/2025 | 8:03 | 26/02/2025 | 9:49 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 106 | 106 | 1 | No
| 1876675 | 26/02/2025 | 10:12 | 26/02/2025 | 11:52 | MGE11 | MULGRAVE | Urban | Asset Failure | LV | 1 | 100.5167 | 100.5167 | 1 | No
| 1876799 | 26/02/2025 | 15:13 | 26/02/2025 | 16:00 | DVY13 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 46.9 | 46.9 | 1 | No
| 1876801 | 26/02/2025 | 15:14 | 26/02/2025 | 17:13 | NB35 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 118.2167 | 118.2167 | 1 | No
| 1876820 | 26/02/2025 | 16:54 | 26/02/2025 | 20:25 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 211 | 211 | 1 | No
| 1876832 | 26/02/2025 | 17:05 | 26/02/2025 | 17:36 | BR15 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 703 | 21710.9599 | 30.8833 | 1 | No
| 1876835 | 26/02/2025 | 17:12 | 26/02/2025 | 17:36 | BR1 | BEAUMARIS | Urban | Unknown | Unknown | 28 | 668.7324 | 23.8833 | 1 | No
| 1876858 | 26/02/2025 | 18:44 | 26/02/2025 | 20:20 | STO13 | SORRENTO | Urban | Asset Failure | LV | 2 | 191.0666 | 95.5333 | 1 | No
| 1876879 | 26/02/2025 | 20:36 | 26/02/2025 | 21:50 | LWN21 | LANGWARRIN | Rural Short | Unknown | Unknown | 15.18 | 1113.1995 | 73.3333 | 1 | No
| 1876891 | 27/02/2025 | 1:41 | 27/02/2025 | 3:08 | LWN21 | LANGWARRIN | Rural Short | Unknown | Unknown | 15 | 1294.2495 | 86.2833 | 1 | No
| 1876919 | 27/02/2025 | 8:16 | 27/02/2025 | 14:30 | STO13 | SORRENTO | Urban | Asset Failure | HV | 1 | 373.0833 | 373.0833 | 1 | No
| 1876938 | 27/02/2025 | 8:41 | 27/02/2025 | 13:27 | LD1 | LYNDALE | Urban | Third Party | Other | 3 | 858.3501 | 286.1167 | 1 | No
| 1877100 | 27/02/2025 | 16:22 | 27/02/2025 | 20:00 | DC5 | DONCASTER | Urban | Overloads |  | 1 | 218 | 218 | 1 | No
| 1877102 | 27/02/2025 | 17:02 | 27/02/2025 | 17:43 | RBD23 | ROSEBUD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 101 | 4071.9867 | 40.3167 | 1 | No
| 1877112 | 27/02/2025 | 17:59 | 27/02/2025 | 20:45 | LWN33 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 165.5167 | 165.5167 | 1 | No
| 1877130 | 27/02/2025 | 20:38 | 27/02/2025 | 22:27 | BU25 | BULLEEN | Urban | Asset Failure | LV | 1 | 109 | 109 | 1 | No
| 1877137 | 27/02/2025 | 21:39 | 27/02/2025 | 23:31 | BU21 | BULLEEN | Urban | Asset Failure | LV | 1 | 112 | 112 | 1 | No
| 1877048 | 27/02/2025 | 22:36 | 28/02/2025 | 0:09 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 93 | 93 | 1 | No
| 1877147 | 28/02/2025 | 3:24 | 28/02/2025 | 4:03 | EM6 | EAST MALVERN | Urban | Unknown | Unknown | 110.55 | 4311.45 | 39 | 1 | No
| 1877151 | 28/02/2025 | 3:49 | 28/02/2025 | 5:40 | HGS33 | HASTINGS | Rural Short | Animal | Other | 1 | 111.4167 | 111.4167 | 1 | No
| 1877191 | 28/02/2025 | 9:02 | 28/02/2025 | 10:40 | SS22 | SPRINGVALE SOUTH | Urban | Third Party | Other | 1 | 98.2833 | 98.2833 | 1 | No
| 1877375 | 28/02/2025 | 13:54 | 28/02/2025 | 15:25 | BH31 | BOX HILL | Urban | Asset Failure | LV | 1 | 91.0833 | 91.0833 | 1 | No
| 1877396 | 28/02/2025 | 15:38 | 28/02/2025 | 17:40 | LWN33 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 121.1667 | 121.1667 | 1 | No
| 1877426 | 28/02/2025 | 18:38 | 28/02/2025 | 19:00 | SS21 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 3 | 63.5499 | 21.1833 | 1 | No
| 1877428 | 28/02/2025 | 19:12 | 28/02/2025 | 20:23 | DC6 | DONCASTER | Urban | Overloads |  | 9 | 644.85 | 71.65 | 1 | No
| 1877429 | 28/02/2025 | 19:18 | 28/02/2025 | 20:35 | SR25 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 77.0167 | 77.0167 | 1 | No
| 1877432 | 28/02/2025 | 19:40 | 28/02/2025 | 22:17 | HT1 | HEATHERTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 157.7333 | 157.7333 | 1 | No
| 1877446 | 28/02/2025 | 21:35 | 2025-01-03 | 3:30 | DN2 | DANDENONG | Urban | Third Party | Other | 1 | 354.3667 | 354.3667 | 1 | No
| 1877444 | 28/02/2025 | 22:28 | 2025-01-03 | 1:50 | DC2 | DONCASTER | Urban | Asset Failure | HV | 45 | 9075.0015 | 201.6667 | 1 | No
| 1877451 | 2025-01-03 | 4:02 | 2025-01-03 | 6:18 | STO14 | SORRENTO | Rural Short | Animal | Animal impact | 35.51 | 4810.4225 | 135.4667 | 1 | No
| 1877492 | 2025-01-03 | 10:31 | 2025-01-03 | 12:01 | BT25 | BENTLEIGH | Urban | Weather |  | 1 | 89.3833 | 89.3833 | 1 | No
| 1877480 | 2025-01-03 | 11:01 | 2025-01-03 | 13:15 | GW7 | GLEN WAVERLEY | Urban | Unknown | Unknown | 1 | 134 | 134 | 1 | No
| 1877545 | 2025-01-03 | 17:58 | 2025-01-03 | 20:02 | MR33 | MOORABBIN | Urban | Asset Failure | LV | 1 | 124.95 | 124.95 | 1 | No
| 1877557 | 2025-01-03 | 20:14 | 2025-01-03 | 21:00 | BW34 | BURWOOD | Urban | Asset Failure | LV | 1 | 45.1167 | 45.1167 | 1 | No
| 1877561 | 2025-01-03 | 20:19 | 2025-01-03 | 22:25 | CRM35 | CARRUM | Urban | Third Party | Vehicle Impact | 17 | 2134.9161 | 125.5833 | 1 | No
| 1877583 | 2025-01-03 | 23:18 | 2025-01-03 | 23:26 | GW7 | GLEN WAVERLEY | Urban | Animal | Other | 1207 | 10440.55 | 8.65 | 1 | No
| 1877583 | 2025-01-03 | 23:18 | 2025-01-03 | 23:33 | GW7 | GLEN WAVERLEY | Urban | Animal | Other | 1010 | 15789.633 | 15.6333 | 2 | No
| 1877583 | 2025-01-03 | 23:18 | 2025-01-03 | 23:52 | GW7 | GLEN WAVERLEY | Urban | Animal | Other | 1495 | 50979.5 | 34.1 | 3 | No
| 1877583 | 2025-01-03 | 23:18 | 2025-02-03 | 0:08 | GW7 | GLEN WAVERLEY | Urban | Animal | Other | 305 | 15265.25 | 50.05 | 4 | No
| 1877583 | 2025-01-03 | 23:18 | 2025-02-03 | 0:21 | GW7 | GLEN WAVERLEY | Urban | Animal | Other | 31 | 1955.0677 | 63.0667 | 5 | No
| 1877583 | 2025-01-03 | 23:18 | 2025-02-03 | 0:21 | GW7 | GLEN WAVERLEY | Urban | Animal | Other | 32 | 2019.7344 | 63.1167 | 6 | No
| 1877591 | 2025-02-03 | 3:50 | 2025-02-03 | 4:50 | LWN33 | LANGWARRIN | Urban | Unknown | Unknown | 71.02 | 4231.606 | 59.5833 | 1 | No
| 1877596 | 2025-02-03 | 4:55 | 2025-02-03 | 6:10 | LWN33 | LANGWARRIN | Urban | Unknown | Unknown | 115.24 | 8548.8835 | 74.1833 | 1 | No
| 1877613 | 2025-02-03 | 8:36 | 2025-02-03 | 14:25 | LWN21 | LANGWARRIN | Rural Short | Third Party | Other | 1 | 348.8667 | 348.8667 | 1 | No
| 1877625 | 2025-02-03 | 11:31 | 2025-02-03 | 12:35 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 2 | 126.3 | 63.15 | 1 | No
| 1877632 | 2025-02-03 | 12:25 | 2025-02-03 | 14:35 | CDA24 | CLARINDA | Urban | Asset Failure | LV | 1 | 130.5333 | 130.5333 | 1 | No
| 1877656 | 2025-02-03 | 18:45 | 2025-02-03 | 20:00 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 21.45 | 1592.3043 | 74.2333 | 1 | No
| 1877781 | 2025-03-03 | 7:53 | 2025-03-03 | 10:59 | BU24 | BULLEEN | Urban | Third Party | Other | 1 | 186 | 186 | 1 | No
| 1877708 | 2025-03-03 | 8:43 | 2025-03-03 | 10:06 | BH23 | BOX HILL | Urban | Asset Failure | LV | 1 | 83.5833 | 83.5833 | 1 | No
| 1877674 | 2025-03-03 | 9:06 | 2025-03-03 | 11:42 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 156.55 | 156.55 | 1 | No
| 1877817 | 2025-03-03 | 12:55 | 2025-03-03 | 14:00 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 64.3 | 64.3 | 1 | No
| 1877804 | 2025-03-03 | 12:58 | 2025-03-03 | 14:10 | DMA12 | DROMANA | Urban | Asset Failure | LV | 2 | 144.4334 | 72.2167 | 1 | No
| 1877822 | 2025-03-03 | 13:23 | 2025-03-03 | 14:00 | HGS31 | HASTINGS | Rural Short | Third Party | Other | 83 | 2994.9139 | 36.0833 | 1 | No
| 1877888 | 2025-03-03 | 22:29 | 2025-03-03 | 23:05 | HGS22 | HASTINGS | Rural Short | Animal | Animal impact | 3 | 105.75 | 35.25 | 1 | No
| 1877901 | 2025-04-03 | 3:19 | 2025-04-03 | 3:27 | DC10 | DONCASTER | Urban | Unknown | Unknown | 3306 | 24189.0102 | 7.3167 | 1 | No
| 1877901 | 2025-04-03 | 3:19 | 2025-04-03 | 4:15 | DC10 | DONCASTER | Urban | Unknown | Unknown | 968 | 53401.3656 | 55.1667 | 2 | No
| 1877901 | 2025-04-03 | 3:19 | 2025-04-03 | 4:04 | DC12 | DONCASTER | Urban | Unknown | Unknown | 1539 | 68126.4513 | 44.2667 | 1 | No
| 1877901 | 2025-04-03 | 3:19 | 2025-04-03 | 4:15 | DC12 | DONCASTER | Urban | Unknown | Unknown | 2 | 110.3334 | 55.1667 | 2 | No
| 1877901 | 2025-04-03 | 3:19 | 2025-04-03 | 3:30 | DC8 | DONCASTER | Urban | Unknown | Unknown | 2801 | 30624.1733 | 10.9333 | 1 | No
| 1877907 | 2025-04-03 | 5:48 | 2025-04-03 | 5:51 | DC8 | DONCASTER | Urban | Overloads |  | 20 | 61.666 | 3.0833 | 1 | No
| 1877906 | 2025-04-03 | 7:05 | 2025-04-03 | 9:05 | DC8 | DONCASTER | Urban | Unknown | Unknown | 50.25 | 6006.5483 | 119.5333 | 1 | No
| 1877921 | 2025-04-03 | 7:46 | 2025-04-03 | 9:05 | DC8 | DONCASTER | Urban | Unknown | Unknown | 1 | 78.2333 | 78.2333 | 1 | No
| 1878019 | 2025-04-03 | 10:25 | 2025-04-03 | 11:22 | DC4 | DONCASTER | Urban | Third Party | Other | 1 | 56.15 | 56.15 | 1 | No
| 1878025 | 2025-04-03 | 10:37 | 2025-04-03 | 11:06 | NP12 | NOBLE PARK | Urban | Animal | Other | 350 | 10319.155 | 29.4833 | 1 | No
| 1878025 | 2025-04-03 | 10:37 | 2025-04-03 | 11:26 | NP12 | NOBLE PARK | Urban | Animal | Other | 250 | 12275 | 49.1 | 2 | No
| 1878025 | 2025-04-03 | 10:37 | 2025-04-03 | 11:39 | NP12 | NOBLE PARK | Urban | Animal | Other | 540 | 33470.982 | 61.9833 | 3 | No
| 1878026 | 2025-04-03 | 10:37 | 2025-04-03 | 12:47 | EB24 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 129.95 | 129.95 | 1 | No
| 1878090 | 2025-04-03 | 12:07 | 2025-04-03 | 14:30 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 142.3333 | 142.3333 | 1 | No
| 1878106 | 2025-04-03 | 12:46 | 2025-04-03 | 18:36 | NP16 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 349.6333 | 349.6333 | 1 | No
| 1878117 | 2025-04-03 | 13:26 | 2025-04-03 | 15:05 | DC10 | DONCASTER | Urban | Asset Failure | LV | 60 | 5907 | 98.45 | 1 | No
| 1878122 | 2025-04-03 | 13:36 | 2025-04-03 | 17:35 | SS11 | SPRINGVALE SOUTH | Urban | Animal | Animal impact | 1 | 238.25 | 238.25 | 1 | No
| 1878137 | 2025-04-03 | 13:55 | 2025-04-03 | 21:55 | HT7 | HEATHERTON | Urban | Asset Failure | LV | 1 | 479.9167 | 479.9167 | 1 | No
| 1878148 | 2025-04-03 | 14:22 | 2025-04-03 | 20:35 | NP23 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 372.1 | 372.1 | 1 | No
| 1878165 | 2025-04-03 | 15:20 | 2025-04-03 | 17:59 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 158.8167 | 158.8167 | 1 | No
| 1878168 | 2025-04-03 | 15:30 | 2025-04-03 | 18:51 | BH33 | BOX HILL | Urban | Asset Failure | LV | 1 | 200.65 | 200.65 | 1 | No
| 1878170 | 2025-04-03 | 15:40 | 2025-04-03 | 21:40 | BT25 | BENTLEIGH | Urban | Overloads |  | 17.82 | 6407.7744 | 359.5833 | 1 | No
| 1878183 | 2025-04-03 | 16:19 | 2025-04-03 | 18:41 | MC31 | MORDIALLOC | Urban | Unknown | Unknown | 36 | 5084.3988 | 141.2333 | 1 | No
| 1878156 | 2025-04-03 | 16:25 | 2025-04-03 | 21:30 | SV34 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 305 | 305 | 1 | No
| 1878211 | 2025-04-03 | 19:52 | 2025-04-03 | 22:03 | SS12 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 131.5667 | 131.5667 | 1 | No
| 1878213 | 2025-04-03 | 20:06 | 2025-04-03 | 22:26 | M13 | MENTONE | Urban | Asset Failure | Distribution substation | 29.37 | 4138.7235 | 140.9167 | 1 | No
| 1878245 | 2025-04-03 | 23:24 | 2025-04-03 | 23:43 | SR25 | SANDRINGHAM | Urban | Vegetation | Grow-in - Other responsible party | 81 | 1467.4527 | 18.1167 | 1 | No
| 1878252 | 2025-05-03 | 4:40 | 2025-05-03 | 7:02 | HGS33 | HASTINGS | Rural Short | Animal | Other | 4.69 | 661.6807 | 141.0833 | 1 | No
| 1878320 | 2025-05-03 | 7:27 | 2025-05-03 | 9:21 | SS12 | SPRINGVALE SOUTH | Urban | Third Party | Other | 3 | 342.0999 | 114.0333 | 1 | No
| 1878269 | 2025-05-03 | 7:52 | 2025-05-03 | 10:48 | MTN35 | MORNINGTON | Rural Short | Asset Failure | LV | 12.87 | 2264.9051 | 175.9833 | 1 | No
| 1878394 | 2025-05-03 | 11:51 | 2025-05-03 | 14:29 | FTN12 | FRANKSTON | Urban | Overloads |  | 1 | 158.2833 | 158.2833 | 1 | No
| 1878460 | 2025-05-03 | 15:41 | 2025-05-03 | 17:30 | SVW53 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 108.7833 | 108.7833 | 1 | No
| 1878461 | 2025-05-03 | 15:44 | 2025-05-03 | 16:46 | MTN32 | MORNINGTON | Rural Short | Animal | Animal impact | 1 | 62.0333 | 62.0333 | 1 | No
| 1878474 | 2025-05-03 | 16:55 | 2025-05-03 | 18:18 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 82.5167 | 82.5167 | 1 | No
| 1878475 | 2025-05-03 | 16:58 | 2025-05-03 | 17:30 | WD26 | WEST DONCASTER | Urban | Weather |  | 50 | 1572.5 | 31.45 | 1 | No
| 1878478 | 2025-05-03 | 17:05 | 2025-05-03 | 17:30 | SVW45 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 24.5167 | 24.5167 | 1 | No
| 1878481 | 2025-05-03 | 17:26 | 2025-05-03 | 17:37 | BR15 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 68 | 693.6 | 10.2 | 1 | No
| 1878484 | 2025-05-03 | 18:29 | 2025-05-03 | 22:22 | M23 | MENTONE | Urban | Asset Failure | HV | 2 | 466 | 233 | 1 | No
| 1878496 | 2025-05-03 | 19:48 | 2025-05-03 | 23:20 | EB31 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 212.3833 | 212.3833 | 1 | No
| 1878515 | 2025-05-03 | 22:20 | 2025-06-03 | 0:13 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 1 | 113.8167 | 113.8167 | 1 | No
| 1878521 | 2025-05-03 | 23:34 | 2025-06-03 | 0:57 | LD2 | LYNDALE | Urban | Overloads |  | 1.32 | 109.56 | 83 | 1 | No
| 1878540 | 2025-06-03 | 4:36 | 2025-06-03 | 8:47 | DSH33 | DANDENONG SOUTH | Urban | Animal | Animal impact | 1.34 | 335.5806 | 250.4333 | 1 | No
| 1878527 | 2025-06-03 | 6:05 | 2025-06-03 | 7:50 | DMA23 | DROMANA | Rural Short | Asset Failure | LV | 1 | 104.8167 | 104.8167 | 1 | No
| 1878661 | 2025-06-03 | 11:32 | 2025-06-03 | 13:24 | HGS23 | HASTINGS | Rural Short | Other | XXX | 1 | 111.9667 | 111.9667 | 1 | No
| 1878704 | 2025-06-03 | 13:30 | 2025-06-03 | 14:11 | BU22 | BULLEEN | Urban | Overloads |  | 1 | 41.7 | 41.7 | 1 | No
| 1878703 | 2025-06-03 | 13:41 | 2025-06-03 | 15:41 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 120.05 | 120.05 | 1 | No
| 1878738 | 2025-06-03 | 15:12 | 2025-06-03 | 17:16 | LWN24 | LANGWARRIN | Urban | Unknown | Unknown | 1 | 123.2667 | 123.2667 | 1 | No
| 1878752 | 2025-06-03 | 16:44 | 2025-06-03 | 18:10 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 2 | 170.5334 | 85.2667 | 1 | No
| 1878765 | 2025-06-03 | 19:21 | 2025-06-03 | 23:50 | WD34 | WEST DONCASTER | Urban | Asset Failure | LV | 8 | 2149.3336 | 268.6667 | 1 | No
| 1878781 | 2025-06-03 | 21:58 | 2025-06-03 | 22:56 | KBH32 | KEYSBOROUGH | Urban | Animal | Animal impact | 23 | 1339.75 | 58.25 | 1 | No
| 1878792 | 2025-07-03 | 0:03 | 2025-07-03 | 13:00 | LD2 | LYNDALE | Urban | Unknown | Unknown | 9 | 6985.1997 | 776.1333 | 1 | No
| 1878794 | 2025-07-03 | 1:24 | 2025-07-03 | 2:34 | FTN24 | FRANKSTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 70.0833 | 70.0833 | 1 | No
| 1878796 | 2025-07-03 | 2:40 | 2025-07-03 | 3:51 | EB22 | EAST BURWOOD | Urban | Animal | Animal impact | 110.22 | 7853.175 | 71.25 | 1 | No
| 1878805 | 2025-07-03 | 5:59 | 2025-07-03 | 7:12 | OAK33 | OAKLEIGH | Urban | Asset Failure | LV | 15 | 1090.0005 | 72.6667 | 1 | No
| 1878900 | 2025-07-03 | 10:46 | 2025-07-03 | 12:05 | BU11 | BULLEEN | Urban | Asset Failure | LV | 1 | 79.1333 | 79.1333 | 1 | No
| 1878975 | 2025-07-03 | 13:44 | 2025-07-03 | 18:52 | SS11 | SPRINGVALE SOUTH | Urban | Overloads |  | 1 | 308.6167 | 308.6167 | 1 | No
| 1879029 | 2025-07-03 | 14:50 | 2025-07-03 | 22:54 | FTN24 | FRANKSTON | Urban | Asset Failure | LV | 13 | 6300.8829 | 484.6833 | 1 | No
| 1878995 | 2025-07-03 | 15:37 | 2025-07-03 | 17:43 | WD34 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 126.0833 | 126.0833 | 1 | No
| 1879009 | 2025-07-03 | 17:12 | 2025-07-03 | 18:24 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 24.09 | 1732.8732 | 71.9333 | 1 | No
| 1879022 | 2025-07-03 | 18:41 | 2025-08-03 | 0:28 | SR21 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 346.9 | 346.9 | 1 | No
| 1879032 | 2025-07-03 | 20:44 | 2025-07-03 | 22:24 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 17.16 | 1710.5654 | 99.6833 | 1 | No
| 1879061 | 2025-08-03 | 9:59 | 2025-08-03 | 17:09 | DVY12 | DANDENONG VALLEY | Urban | Asset Failure | HV | 11 | 4724.8663 | 429.5333 | 1 | No
| 1879062 | 2025-08-03 | 10:01 | 2025-08-03 | 17:14 | DVY24 | DANDENONG VALLEY | Rural Short | Asset Failure | HV | 26 | 11263.6342 | 433.2167 | 1 | No
| 1879064 | 2025-08-03 | 10:08 | 2025-08-03 | 17:00 | DVY24 | DANDENONG VALLEY | Rural Short | Asset Failure | HV | 7 | 2879.8 | 411.4 | 1 | No
| 1879078 | 2025-08-03 | 12:32 | 2025-08-03 | 13:56 | FSH23 | FRANKSTON SOUTH | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 83.5167 | 83.5167 | 1 | No
| 1879082 | 2025-08-03 | 12:56 | 2025-08-03 | 13:45 | DVY22 | DANDENONG VALLEY | Urban | Asset Failure | LV | 3 | 144.6501 | 48.2167 | 1 | No
| 1879093 | 2025-08-03 | 14:18 | 2025-08-03 | 15:30 | HGS31 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 71.1833 | 71.1833 | 1 | No
| 1879102 | 2025-08-03 | 17:19 | 2025-08-03 | 18:56 | MTN35 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 96.8167 | 96.8167 | 1 | No
| 1879107 | 2025-08-03 | 18:47 | 2025-08-03 | 20:45 | MGE12 | MULGRAVE | Urban | Asset Failure | LV | 1 | 117.9333 | 117.9333 | 1 | No
| 1879105 | 2025-08-03 | 18:52 | 2025-08-03 | 20:48 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 1 | 116 | 116 | 1 | No
| 1879118 | 2025-08-03 | 21:38 | 2025-08-03 | 22:31 | OR24 | ORMOND | Urban | Asset Failure | LV | 1 | 52.7833 | 52.7833 | 1 | No
| 1879125 | 2025-08-03 | 23:34 | 2025-09-03 | 0:58 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 83.7 | 83.7 | 1 | No
| 1879139 | 2025-09-03 | 8:30 | 2025-09-03 | 18:12 | RD4 | RIVERSDALE | Urban | Vegetation | Grow-in - Other responsible party | 30 | 17466.999 | 582.2333 | 1 | No
| 1879143 | 2025-09-03 | 9:25 | 2025-09-03 | 12:09 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 163.95 | 163.95 | 1 | No
| 1879157 | 2025-09-03 | 12:46 | 2025-09-03 | 15:15 | NW33 | NUNAWADING | Urban | Asset Failure | LV | 1 | 149.3833 | 149.3833 | 1 | No
| 1879158 | 2025-09-03 | 12:54 | 2025-09-03 | 17:34 | OR34 | ORMOND | Urban | Asset Failure | LV | 1 | 279.9 | 279.9 | 1 | No
| 1879167 | 2025-09-03 | 14:57 | 2025-09-03 | 18:21 | HT9 | HEATHERTON | Urban | Asset Failure | LV | 6.03 | 1231.326 | 204.2 | 1 | No
| 1879169 | 2025-09-03 | 15:26 | 2025-09-03 | 17:00 | FTN24 | FRANKSTON | Urban | Asset Failure | LV | 1 | 94 | 94 | 1 | No
| 1879173 | 2025-09-03 | 16:37 | 2025-09-03 | 17:56 | NB26 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 78.5 | 78.5 | 1 | No
| 1879180 | 2025-09-03 | 17:49 | 2025-09-03 | 19:11 | NW22 | NUNAWADING | Urban | Asset Failure | LV | 73 | 5966.5309 | 81.7333 | 1 | No
| 1879180 | 2025-09-03 | 17:49 | 2025-09-03 | 19:18 | NW22 | NUNAWADING | Urban | Asset Failure | LV | 61 | 5419.85 | 88.85 | 2 | No
| 1879180 | 2025-09-03 | 17:49 | 2025-09-03 | 23:06 | NW22 | NUNAWADING | Urban | Asset Failure | LV | 2 | 633.4 | 316.7 | 3 | No
| 1879185 | 2025-09-03 | 17:53 | 2025-09-03 | 18:48 | BT23 | BENTLEIGH | Urban | Overloads |  | 61 | 3327.55 | 54.55 | 1 | No
| 1879198 | 2025-09-03 | 17:53 | 2025-09-03 | 19:15 | BT23 | BENTLEIGH | Urban | Asset Failure | LV | 62 | 5069.5354 | 81.7667 | 1 | No
| 1879192 | 2025-09-03 | 18:19 | 2025-09-03 | 19:45 | RBD13 | ROSEBUD | Urban | Overloads |  | 37.43 | 3218.98 | 86 | 1 | No
| 1879200 | 2025-09-03 | 18:44 | 2025-09-03 | 19:15 | BT23 | BENTLEIGH | Urban | Asset Failure | LV | 48 | 1495.2 | 31.15 | 1 | No
| 1879205 | 2025-09-03 | 19:26 | 2025-09-03 | 21:06 | RBD24 | ROSEBUD | Urban | Overloads |  | 41.37 | 4101.8355 | 99.15 | 1 | No
| 1879214 | 2025-09-03 | 20:43 | 2025-09-03 | 23:54 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 190.0167 | 190.0167 | 1 | No
| 1879217 | 2025-09-03 | 21:01 | 2025-10-03 | 1:14 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 252.2833 | 252.2833 | 1 | No
| 1879219 | 2025-09-03 | 21:20 | 2025-10-03 | 0:40 | NO3 | NOTTING HILL | Urban | Third Party | Other | 22 | 4412.8326 | 200.5833 | 1 | No
| 1879222 | 2025-09-03 | 21:38 | 2025-10-03 | 2:02 | HGS33 | HASTINGS | Rural Short | Third Party | Vehicle Impact | 14 | 3698.3338 | 264.1667 | 1 | No
| 1879224 | 2025-09-03 | 22:18 | 2025-09-03 | 22:36 | NO4 | NOTTING HILL | Urban | Unknown | Unknown | 195 | 3454.7565 | 17.7167 | 1 | No
| 1879224 | 2025-09-03 | 22:18 | 2025-09-03 | 23:34 | NO4 | NOTTING HILL | Urban | Unknown | Unknown | 53 | 4012.9851 | 75.7167 | 2 | No
| 1879224 | 2025-09-03 | 22:18 | 2025-09-03 | 23:46 | NO4 | NOTTING HILL | Urban | Unknown | Unknown | 51 | 4500.75 | 88.25 | 3 | No
| 1879224 | 2025-09-03 | 22:18 | 2025-10-03 | 0:02 | NO4 | NOTTING HILL | Urban | Unknown | Unknown | 46 | 4798.5682 | 104.3167 | 4 | No
| 1879229 | 2025-09-03 | 22:51 | 2025-10-03 | 0:38 | LD7 | LYNDALE | Urban | Asset Failure | LV | 9.9 | 1054.5153 | 106.5167 | 1 | No
| 1879225 | 2025-09-03 | 23:07 | 2025-10-03 | 1:03 | DC10 | DONCASTER | Urban | Asset Failure | LV | 1 | 116.8833 | 116.8833 | 1 | No
| 1879226 | 2025-10-03 | 0:24 | 2025-10-03 | 3:20 | EW14 | ELWOOD | Urban | Asset Failure | LV | 8 | 1411.7336 | 176.4667 | 1 | No
| 1879236 | 2025-10-03 | 2:07 | 2025-10-03 | 12:42 | MGE34 | MULGRAVE | Urban | Animal | Animal impact | 4 | 2539.8668 | 634.9667 | 1 | No
| 1879238 | 2025-10-03 | 2:27 | 2025-10-03 | 4:01 | BT13 | BENTLEIGH | Urban | Asset Failure | LV | 57.34 | 5425.3216 | 94.6167 | 1 | No
| 1879246 | 2025-10-03 | 5:24 | 2025-10-03 | 12:27 | SH22 | SURREY HILLS | Urban | Overloads |  | 31.35 | 13275.1575 | 423.45 | 1 | No
| 1879248 | 2025-10-03 | 6:38 | 2025-10-03 | 8:30 | MR31 | MOORABBIN | Urban | Asset Failure | LV | 48.91 | 5442.8662 | 111.2833 | 1 | No
| 1879255 | 2025-10-03 | 7:12 | 2025-10-03 | 11:46 | HT4 | HEATHERTON | Urban | Unknown | Unknown | 81.07 | 22205.073 | 273.9 | 1 | No
| 1879260 | 2025-10-03 | 7:55 | 2025-10-03 | 11:07 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 8.58 | 1639.209 | 191.05 | 1 | No
| 1879261 | 2025-10-03 | 8:19 | 2025-10-03 | 12:54 | LWN24 | LANGWARRIN | Urban | Asset Failure | Distribution substation | 50.92 | 13994.5116 | 274.8333 | 1 | No
| 1879269 | 2025-10-03 | 9:18 | 2025-10-03 | 13:32 | EB14 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 253.2 | 253.2 | 1 | No
| 1879271 | 2025-10-03 | 9:23 | 2025-10-03 | 14:57 | NW21 | NUNAWADING | Urban | Asset Failure | LV | 1 | 334.0167 | 334.0167 | 1 | No
| 1879282 | 2025-10-03 | 11:20 | 2025-10-03 | 14:28 | BC22 | BALACLAVA | Urban | Asset Failure | LV | 1 | 187.5 | 187.5 | 1 | No
| 1879245 | 2025-10-03 | 11:48 | 2025-10-03 | 13:35 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 107 | 107 | 1 | No
| 1879291 | 2025-10-03 | 14:59 | 2025-10-03 | 15:50 | HGS33 | HASTINGS | Rural Short | Overloads |  | 1 | 51 | 51 | 1 | No
| 1879292 | 2025-10-03 | 15:11 | 2025-10-03 | 16:50 | FSH13 | FRANKSTON SOUTH | Urban | Overloads |  | 1 | 99 | 99 | 1 | No
| 1879296 | 2025-10-03 | 15:36 | 2025-11-03 | 3:14 | FSH23 | FRANKSTON SOUTH | Rural Short | Asset Failure | HV | 1 | 698.05 | 698.05 | 1 | No
| 1879298 | 2025-10-03 | 15:46 | 2025-10-03 | 23:31 | BR10 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 464.5167 | 464.5167 | 1 | No
| 1879299 | 2025-10-03 | 15:49 | 2025-10-03 | 16:15 | OAK35 | OAKLEIGH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 36 | 904.7988 | 25.1333 | 1 | No
| 1879307 | 2025-10-03 | 16:40 | 2025-10-03 | 18:15 | EW1 | ELWOOD | Urban | Asset Failure | LV | 1 | 94.3333 | 94.3333 | 1 | No
| 1879310 | 2025-10-03 | 16:58 | 2025-10-03 | 18:55 | MR13 | MOORABBIN | Urban | Asset Failure | LV | 1 | 117.1167 | 117.1167 | 1 | No
| 1879330 | 2025-10-03 | 19:20 | 2025-10-03 | 21:26 | BU21 | BULLEEN | Urban | Overloads |  | 1 | 126.6167 | 126.6167 | 1 | No
| 1879333 | 2025-10-03 | 19:35 | 2025-10-03 | 21:04 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 103 | 9136.1 | 88.7 | 1 | No
| 1879297 | 2025-10-03 | 20:12 | 2025-11-03 | 3:00 | FSH23 | FRANKSTON SOUTH | Rural Short | Asset Failure | HV | 1 | 408 | 408 | 1 | No
| 1879341 | 2025-10-03 | 22:12 | 2025-11-03 | 0:30 | MC15 | MORDIALLOC | Urban | Animal | Animal impact | 49 | 6751.3817 | 137.7833 | 1 | No
| 1879343 | 2025-10-03 | 22:45 | 2025-10-03 | 23:17 | M32 | MENTONE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 643 | 20661.7119 | 32.1333 | 1 | No
| 1879343 | 2025-10-03 | 22:45 | 2025-10-03 | 23:28 | M32 | MENTONE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 287 | 12561.0429 | 43.7667 | 2 | No
| 1879343 | 2025-10-03 | 22:45 | 2025-10-03 | 23:49 | M32 | MENTONE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 435 | 28108.2645 | 64.6167 | 3 | No
| 1879348 | 2025-10-03 | 23:21 | 2025-11-03 | 0:44 | M32 | MENTONE | Urban | Asset Failure | LV | 138 | 11463.2046 | 83.0667 | 1 | No
| 1879427 | 2025-11-03 | 7:02 | 2025-11-03 | 8:49 | DC3 | DONCASTER | Urban | Asset Failure | LV | 19.14 | 2037.453 | 106.45 | 1 | No
| 1879442 | 2025-11-03 | 7:27 | 2025-11-03 | 8:40 | FSH34 | FRANKSTON SOUTH | Urban | Overloads |  | 9.9 | 722.0397 | 72.9333 | 1 | No
| 1879476 | 2025-11-03 | 8:36 | 2025-11-03 | 10:55 | CRM14 | CARRUM | Rural Short | Asset Failure | LV | 1 | 138.5667 | 138.5667 | 1 | No
| 1879433 | 2025-11-03 | 9:16 | 2025-11-03 | 11:55 | M32 | MENTONE | Urban | Asset Failure | LV | 1 | 159 | 159 | 1 | No
| 1879521 | 2025-11-03 | 9:56 | 2025-11-03 | 11:15 | NW32 | NUNAWADING | Urban | Asset Failure | LV | 1 | 78.55 | 78.55 | 1 | No
| 1879563 | 2025-11-03 | 11:21 | 2025-11-03 | 12:30 | LWN21 | LANGWARRIN | Rural Short | Third Party | Other | 1 | 68.4 | 68.4 | 1 | No
| 1879631 | 2025-11-03 | 14:00 | 2025-11-03 | 15:20 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 79.5833 | 79.5833 | 1 | No
| 1879799 | 2025-11-03 | 16:08 | 2025-11-03 | 22:47 | DC10 | DONCASTER | Urban | Asset Failure | LV | 64 | 25522.1312 | 398.7833 | 1 | No
| 1879811 | 2025-11-03 | 17:12 | 2025-11-03 | 17:41 | NW23 | NUNAWADING | Urban | Asset Failure | HV | 194 | 5596.9 | 28.85 | 1 | No
| 1879811 | 2025-11-03 | 17:12 | 2025-11-03 | 17:52 | NW23 | NUNAWADING | Urban | Asset Failure | HV | 476 | 18825.8 | 39.55 | 2 | No
| 1879811 | 2025-11-03 | 17:12 | 2025-11-03 | 20:10 | NW23 | NUNAWADING | Urban | Asset Failure | HV | 36 | 6388.2 | 177.45 | 3 | No
| 1879811 | 2025-11-03 | 17:12 | 2025-11-03 | 20:10 | NW23 | NUNAWADING | Urban | Asset Failure | HV | 188 | 33382.5396 | 177.5667 | 4 | No
| 1879811 | 2025-11-03 | 17:12 | 2025-11-03 | 20:10 | NW23 | NUNAWADING | Urban | Asset Failure | HV | 172 | 30550.0724 | 177.6167 | 5 | No
| 1879811 | 2025-11-03 | 17:12 | 2025-11-03 | 20:10 | NW23 | NUNAWADING | Urban | Asset Failure | HV | 10 | 1776.833 | 177.6833 | 6 | No
| 1879815 | 2025-11-03 | 17:24 | 2025-11-03 | 20:54 | MR21 | MOORABBIN | Urban | Asset Failure | LV | 1 | 210.75 | 210.75 | 1 | No
| 1879825 | 2025-11-03 | 17:41 | 2025-11-03 | 21:35 | LWN21 | LANGWARRIN | Rural Short | Overloads |  | 1 | 233.1667 | 233.1667 | 1 | No
| 1879827 | 2025-11-03 | 17:56 | 2025-11-03 | 23:21 | RD4 | RIVERSDALE | Urban | Overloads |  | 1 | 324.4667 | 324.4667 | 1 | No
| 1879838 | 2025-11-03 | 19:00 | 2025-11-03 | 21:48 | NP12 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 168 | 168 | 1 | No
| 1879839 | 2025-11-03 | 19:37 | 2025-12-03 | 0:55 | NP36 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 318.0667 | 318.0667 | 1 | No
| 1879856 | 2025-11-03 | 20:18 | 2025-11-03 | 21:58 | SR34 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 99.85 | 99.85 | 1 | No
| 1879859 | 2025-11-03 | 21:40 | 2025-12-03 | 1:38 | NB21 | NORTH BRIGHTON | Urban | Overloads |  | 1 | 238.2167 | 238.2167 | 1 | No
| 1879865 | 2025-11-03 | 22:38 | 2025-11-03 | 22:45 | BT23 | BENTLEIGH | Urban | Overloads |  | 58 | 387.6314 | 6.6833 | 1 | No
| 1879874 | 2025-12-03 | 2:59 | 2025-12-03 | 7:19 | NW13 | NUNAWADING | Urban | Asset Failure | LV | 1 | 260.4667 | 260.4667 | 1 | No
| 1879875 | 2025-12-03 | 3:39 | 2025-12-03 | 11:55 | MC21 | MORDIALLOC | Urban | Unknown | Unknown | 1.34 | 663.568 | 495.2 | 1 | No
| 1879910 | 2025-12-03 | 8:10 | 2025-12-03 | 8:50 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 570 | 22904.481 | 40.1833 | 1 | No
| 1879941 | 2025-12-03 | 11:04 | 2025-12-03 | 12:22 | BU22 | BULLEEN | Urban | Asset Failure | LV | 1 | 78.0167 | 78.0167 | 1 | No
| 1880044 | 2025-12-03 | 11:52 | 2025-12-03 | 11:55 | MC21 | MORDIALLOC | Urban | Asset Failure | HV | 315 | 955.4895 | 3.0333 | 1 | No
| 1880064 | 2025-12-03 | 12:44 | 2025-12-03 | 14:58 | LD4 | LYNDALE | Urban | Third Party | Other | 1 | 133.8833 | 133.8833 | 1 | No
| 1880082 | 2025-12-03 | 13:50 | 2025-12-03 | 17:50 | MC32 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 239.6 | 239.6 | 1 | No
| 1880107 | 2025-12-03 | 15:06 | 2025-12-03 | 17:00 | DVY21 | DANDENONG VALLEY | Urban | Overloads |  | 1 | 113.1667 | 113.1667 | 1 | No
| 1880108 | 2025-12-03 | 15:09 | 13/03/2025 | 0:58 | CRM13 | CARRUM | Urban | Asset Failure | LV | 1 | 589.3833 | 589.3833 | 1 | No
| 1880090 | 2025-12-03 | 15:12 | 2025-12-03 | 16:45 | CRM15 | CARRUM | Urban | Asset Failure | LV | 1 | 93 | 93 | 1 | No
| 1880109 | 2025-12-03 | 15:18 | 2025-12-03 | 16:40 | MR23 | MOORABBIN | Urban | Asset Failure | LV | 1 | 81.8333 | 81.8333 | 1 | No
| 1880118 | 2025-12-03 | 15:25 | 2025-12-03 | 17:32 | EM3 | EAST MALVERN | Urban | Weather |  | 94 | 11934.8698 | 126.9667 | 1 | No
| 1880120 | 2025-12-03 | 15:48 | 2025-12-03 | 17:05 | K35 | GARDINER | Urban | Asset Failure | LV | 18.15 | 1397.2469 | 76.9833 | 1 | No
| 1880149 | 2025-12-03 | 16:54 | 2025-12-03 | 16:59 | EM1 | EAST MALVERN | Urban | Weather |  | 631 | 3481.0377 | 5.5167 | 1 | No
| 1880143 | 2025-12-03 | 16:58 | 13/03/2025 | 12:42 | HGS33 | HASTINGS | Rural Short | Third Party | Other | 1 | 1184 | 1184 | 1 | No
| 1880156 | 2025-12-03 | 17:23 | 2025-12-03 | 19:30 | HGS32 | HASTINGS | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 14.85 | 1881.0005 | 126.6667 | 1 | No
| 1880171 | 2025-12-03 | 19:10 | 2025-12-03 | 22:08 | HT4 | HEATHERTON | Urban | Unknown | Unknown | 1 | 177.9167 | 177.9167 | 1 | No
| 1880189 | 2025-12-03 | 21:14 | 2025-12-03 | 23:38 | HGS32 | HASTINGS | Urban | Animal | Animal impact | 1 | 143.0333 | 143.0333 | 1 | No
| 1880199 | 13/03/2025 | 0:09 | 13/03/2025 | 2:24 | BC23 | BALACLAVA | Urban | Asset Failure | LV | 7 | 939.2831 | 134.1833 | 1 | No
| 1880200 | 13/03/2025 | 0:16 | 13/03/2025 | 2:52 | NW22 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 155.2833 | 155.2833 | 1 | No
| 1880237 | 13/03/2025 | 7:32 | 13/03/2025 | 8:35 | FTN14 | FRANKSTON | Urban | Animal | Other | 1 | 62.4833 | 62.4833 | 1 | No
| 1880296 | 13/03/2025 | 8:16 | 13/03/2025 | 9:23 | DVY31 | DANDENONG VALLEY | Urban | Asset Failure | LV | 0.99 | 65.9175 | 66.5833 | 1 | No
| 1880260 | 13/03/2025 | 8:40 | 13/03/2025 | 10:43 | SR35 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 122.8167 | 122.8167 | 1 | No
| 1880330 | 13/03/2025 | 10:47 | 13/03/2025 | 12:03 | MR15 | MOORABBIN | Urban | Asset Failure | LV | 1 | 75.4 | 75.4 | 1 | No
| 1880360 | 13/03/2025 | 11:26 | 13/03/2025 | 12:24 | GW3 | GLEN WAVERLEY | Urban | Asset Failure | LV | 40.59 | 2346.7799 | 57.8167 | 1 | No
| 1880432 | 13/03/2025 | 14:06 | 13/03/2025 | 20:15 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 2 | 737.9 | 368.95 | 1 | No
| 1880499 | 13/03/2025 | 20:42 | 13/03/2025 | 21:37 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 7.2 | 395.0402 | 54.8667 | 1 | No
| 1880507 | 13/03/2025 | 23:15 | 13/03/2025 | 23:33 | DC1 | DONCASTER | Urban | Asset Failure | LV | 107 | 2018.7369 | 18.8667 | 1 | No
| 1880515 | 14/03/2025 | 3:30 | 14/03/2025 | 5:00 | WD14 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 89.1167 | 89.1167 | 1 | No
| 1880519 | 14/03/2025 | 5:35 | 14/03/2025 | 5:39 | LD4 | LYNDALE | Urban | Animal | Animal impact | 1484 | 6059.6172 | 4.0833 | 1 | No
| 1880519 | 14/03/2025 | 5:35 | 14/03/2025 | 6:40 | LD4 | LYNDALE | Urban | Animal | Animal impact | 861 | 55979.3787 | 65.0167 | 2 | No
| 1880519 | 14/03/2025 | 5:35 | 14/03/2025 | 7:45 | LD4 | LYNDALE | Urban | Animal | Animal impact | 73 | 9516.7691 | 130.3667 | 3 | No
| 1880519 | 14/03/2025 | 5:35 | 14/03/2025 | 7:46 | LD4 | LYNDALE | Urban | Animal | Animal impact | 90 | 11788.497 | 130.9833 | 4 | No
| 1880519 | 14/03/2025 | 5:35 | 14/03/2025 | 7:58 | LD4 | LYNDALE | Urban | Animal | Animal impact | 55 | 7859.5 | 142.9 | 5 | No
| 1880519 | 14/03/2025 | 5:35 | 14/03/2025 | 9:07 | LD4 | LYNDALE | Urban | Animal | Animal impact | 118 | 24966.8294 | 211.5833 | 6 | No
| 1880519 | 14/03/2025 | 5:35 | 14/03/2025 | 9:25 | LD4 | LYNDALE | Urban | Animal | Animal impact | 1 | 230.2333 | 230.2333 | 7 | No
| 1880522 | 14/03/2025 | 6:14 | 14/03/2025 | 9:02 | CFD24 | CAULFIELD | Urban | Overloads |  | 1 | 167.5167 | 167.5167 | 1 | No
| 1880523 | 14/03/2025 | 6:30 | 14/03/2025 | 8:14 | CDA21 | CLARINDA | Urban | Asset Failure | LV | 1 | 103.5833 | 103.5833 | 1 | No
| 1880527 | 14/03/2025 | 6:43 | 14/03/2025 | 9:06 | STO21 | SORRENTO | Rural Short | Unknown | Unknown | 23 | 3272.9 | 142.3 | 1 | No
| 1880539 | 14/03/2025 | 7:29 | 14/03/2025 | 18:17 | DC6 | DONCASTER | Urban | Third Party | Other | 2 | 1295.4334 | 647.7167 | 1 | No
| 1880552 | 14/03/2025 | 7:59 | 14/03/2025 | 9:25 | LD4 | LYNDALE | Urban | Animal | Animal impact | 18 | 1554.6006 | 86.3667 | 1 | No
| 1880607 | 14/03/2025 | 9:28 | 14/03/2025 | 11:30 | EW12 | ELWOOD | Urban | Asset Failure | LV | 1 | 121.2667 | 121.2667 | 1 | No
| 1880614 | 14/03/2025 | 9:38 | 14/03/2025 | 10:10 | NP11 | NOBLE PARK | Urban | Third Party | Vehicle Impact | 674 | 21848.8558 | 32.4167 | 1 | No
| 1880626 | 14/03/2025 | 10:01 | 14/03/2025 | 10:41 | NP11 | NOBLE PARK | Urban | Third Party | Other | 1 | 40.0833 | 40.0833 | 1 | No
| 1880654 | 14/03/2025 | 11:21 | 14/03/2025 | 18:45 | DC6 | DONCASTER | Urban | Third Party | Other | 3 | 1332.9501 | 444.3167 | 1 | No
| 1880654 | 14/03/2025 | 11:21 | 14/03/2025 | 18:46 | DC6 | DONCASTER | Urban | Third Party | Other | 4 | 1777.5332 | 444.3833 | 2 | No
| 1880671 | 14/03/2025 | 12:17 | 14/03/2025 | 14:09 | KBH34 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 111.6333 | 111.6333 | 1 | No
| 1880738 | 14/03/2025 | 17:03 | 14/03/2025 | 18:47 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 0.7 | 72.6833 | 103.8333 | 1 | No
| 1880748 | 14/03/2025 | 20:15 | 14/03/2025 | 21:12 | CFD14 | CAULFIELD | Urban | Asset Failure | LV | 1 | 56.6333 | 56.6333 | 1 | No
| 1880754 | 14/03/2025 | 21:45 | 15/03/2025 | 3:30 | MGE12 | MULGRAVE | Urban | Asset Failure | LV | 6.93 | 2385.5368 | 344.2333 | 1 | No
| 1880754 | 14/03/2025 | 21:45 | 15/03/2025 | 3:38 | MGE12 | MULGRAVE | Urban | Asset Failure | LV | 1.32 | 465.278 | 352.4833 | 2 | No
| 1880758 | 14/03/2025 | 22:33 | 15/03/2025 | 4:21 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 1 | 348.6833 | 348.6833 | 1 | No
| 1880763 | 15/03/2025 | 1:30 | 15/03/2025 | 9:46 | RWT34 | RINGWOOD | Urban | Third Party | Other | 1 | 495.9 | 495.9 | 1 | No
| 1880778 | 15/03/2025 | 7:12 | 15/03/2025 | 9:10 | HGS33 | HASTINGS | Rural Short | Animal | Other | 4 | 470.8668 | 117.7167 | 1 | No
| 1880789 | 15/03/2025 | 8:30 | 15/03/2025 | 9:45 | DN21 | DANDENONG | Urban | Animal | Animal impact | 1 | 74.3833 | 74.3833 | 1 | No
| 1880791 | 15/03/2025 | 8:35 | 15/03/2025 | 10:53 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 137.9333 | 137.9333 | 1 | No
| 1880794 | 15/03/2025 | 8:54 | 15/03/2025 | 14:10 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 1 | 316.1333 | 316.1333 | 1 | No
| 1880780 | 15/03/2025 | 9:49 | 15/03/2025 | 14:00 | CFD14 | CAULFIELD | Urban | Asset Failure | LV | 1 | 251 | 251 | 1 | No
| 1880825 | 15/03/2025 | 12:54 | 15/03/2025 | 15:35 | EW9 | ELWOOD | Urban | Asset Failure | LV | 1 | 160.3833 | 160.3833 | 1 | No
| 1880844 | 15/03/2025 | 15:22 | 15/03/2025 | 16:23 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 497 | 30341.85 | 61.05 | 1 | No
| 1880844 | 15/03/2025 | 15:22 | 15/03/2025 | 16:42 | NW21 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 744 | 59334 | 79.75 | 2 | No
| 1880850 | 15/03/2025 | 15:37 | 15/03/2025 | 16:55 | OAK23 | OAKLEIGH | Urban | Asset Failure | Distribution substation | 95.7 | 7483.74 | 78.2 | 1 | No
| 1880793 | 15/03/2025 | 15:56 | 15/03/2025 | 17:42 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 105.9833 | 105.9833 | 1 | No
| 1880879 | 15/03/2025 | 16:39 | 15/03/2025 | 19:30 | MTN23 | MORNINGTON | Urban | Asset Failure | LV | 1 | 170.3333 | 170.3333 | 1 | No
| 1880862 | 15/03/2025 | 17:03 | 15/03/2025 | 18:03 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.7 | 59.7 | 1 | No
| 1880866 | 15/03/2025 | 17:23 | 15/03/2025 | 18:23 | OR24 | ORMOND | Urban | Overloads |  | 1 | 59.7833 | 59.7833 | 1 | No
| 1880867 | 15/03/2025 | 17:27 | 15/03/2025 | 18:29 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.7 | 61.7 | 1 | No
| 1880869 | 15/03/2025 | 17:47 | 15/03/2025 | 18:49 | OR24 | ORMOND | Urban | Overloads |  | 1 | 61.7667 | 61.7667 | 1 | No
| 1880875 | 15/03/2025 | 17:51 | 15/03/2025 | 21:18 | GW3 | GLEN WAVERLEY | Urban | Asset Failure | Distribution substation | 38.94 | 8022.2903 | 206.0167 | 1 | No
| 1880887 | 15/03/2025 | 20:39 | 15/03/2025 | 22:37 | EW1 | ELWOOD | Urban | Overloads |  | 18.81 | 2215.5039 | 117.7833 | 1 | No
| 1880884 | 15/03/2025 | 20:49 | 15/03/2025 | 21:28 | BH31 | BOX HILL | Urban | Animal | Animal impact | 808.69 | 32091.4879 | 39.6833 | 1 | No
| 1880915 | 15/03/2025 | 23:15 | 16/03/2025 | 11:49 | NB34 | NORTH BRIGHTON | Urban | Unknown | Unknown | 1 | 754.1167 | 754.1167 | 1 | No
| 1880930 | 15/03/2025 | 23:49 | 16/03/2025 | 4:02 | BW21 | BURWOOD | Urban | Asset Failure | LV | 45 | 11381.2515 | 252.9167 | 1 | No
| 1880926 | 15/03/2025 | 23:56 | 16/03/2025 | 3:32 | MGE31 | MULGRAVE | Urban | Animal | Animal impact | 7.37 | 1586.8841 | 215.3167 | 1 | No
| 1880935 | 16/03/2025 | 7:03 | 16/03/2025 | 8:15 | FTN24 | FRANKSTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 97 | 6937.1199 | 71.5167 | 1 | No
| 1880946 | 16/03/2025 | 7:58 | 16/03/2025 | 10:31 | SR25 | SANDRINGHAM | Urban | Overloads |  | 12.54 | 1912.35 | 152.5 | 1 | No
| 1880959 | 16/03/2025 | 9:13 | 16/03/2025 | 20:40 | FTN24 | FRANKSTON | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 13 | 8922.1171 | 686.3167 | 1 | No
| 1880951 | 16/03/2025 | 9:16 | 16/03/2025 | 12:31 | CFD22 | CAULFIELD | Urban | Asset Failure | LV | 10.89 | 2123.55 | 195 | 1 | No
| 1880964 | 16/03/2025 | 9:45 | 16/03/2025 | 11:35 | FTN25 | FRANKSTON | Urban | Unknown | Unknown | 1 | 109.7833 | 109.7833 | 1 | No
| 1880973 | 16/03/2025 | 10:48 | 16/03/2025 | 12:48 | HGS23 | HASTINGS | Rural Short | Unknown | Unknown | 476.37 | 57053.2629 | 119.7667 | 1 | No
| 1880968 | 16/03/2025 | 10:49 | 16/03/2025 | 14:42 | FSH34 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 10.05 | 2345.5022 | 233.3833 | 1 | No
| 1881093 | 16/03/2025 | 11:06 | 17/03/2025 | 2:05 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 1 | 898.3 | 898.3 | 1 | No
| 1881012 | 16/03/2025 | 11:22 | 16/03/2025 | 17:16 | HGS31 | HASTINGS | Rural Short | Asset Failure | LV | 6 | 2126.5998 | 354.4333 | 1 | No
| 1881039 | 16/03/2025 | 12:23 | 16/03/2025 | 15:10 | RBD12 | ROSEBUD | Rural Short | Unknown | Unknown | 6.03 | 1006.9093 | 166.9833 | 1 | No
| 1881045 | 16/03/2025 | 13:02 | 16/03/2025 | 14:39 | FTN23 | FRANKSTON | Urban | Asset Failure | LV | 1 | 96.8167 | 96.8167 | 1 | No
| 1881051 | 16/03/2025 | 13:50 | 16/03/2025 | 20:43 | SV32 | SPRINGVALE | Urban | Asset Failure | LV | 78 | 32158.0974 | 412.2833 | 1 | No
| 1881053 | 16/03/2025 | 13:55 | 16/03/2025 | 15:31 | EB14 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 96.4333 | 96.4333 | 1 | No
| 1881073 | 16/03/2025 | 15:22 | 16/03/2025 | 20:44 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 15 | 4834.2495 | 322.2833 | 1 | No
| 1881072 | 16/03/2025 | 15:30 | 17/03/2025 | 17:50 | CRM22 | CARRUM | Urban | Asset Failure | LV | 23 | 36317.3841 | 1579.0167 | 1 | No
| 1881069 | 16/03/2025 | 15:38 | 16/03/2025 | 19:20 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 1 | 221.7833 | 221.7833 | 1 | No
| 1881078 | 16/03/2025 | 16:07 | 16/03/2025 | 18:25 | NB33 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 137.6 | 137.6 | 1 | No
| 1881081 | 16/03/2025 | 16:32 | 16/03/2025 | 18:10 | CFD23 | CAULFIELD | Urban | Asset Failure | LV | 1 | 97.8 | 97.8 | 1 | No
| 1881080 | 16/03/2025 | 16:41 | 16/03/2025 | 23:29 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 408.3167 | 408.3167 | 1 | No
| 1881112 | 16/03/2025 | 18:37 | 16/03/2025 | 19:15 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 1 | 37.7 | 37.7 | 1 | No
| 1881120 | 16/03/2025 | 18:52 | 16/03/2025 | 20:03 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 71.7167 | 71.7167 | 1 | No
| 1881061 | 16/03/2025 | 19:37 | 16/03/2025 | 20:40 | FTN24 | FRANKSTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 63 | 63 | 1 | No
| 1881128 | 16/03/2025 | 19:53 | 16/03/2025 | 21:32 | STO23 | SORRENTO | Urban | Third Party | Other | 1 | 99.5333 | 99.5333 | 1 | No
| 1881137 | 16/03/2025 | 20:43 | 17/03/2025 | 2:19 | RWT12 | RINGWOOD | Urban | Asset Failure | LV | 21.12 | 7104.4153 | 336.3833 | 1 | No
| 1881139 | 16/03/2025 | 20:57 | 16/03/2025 | 21:32 | DN25 | DANDENONG | Urban | Asset Failure | HV | 174 | 6075.5058 | 34.9167 | 1 | No
| 1881139 | 16/03/2025 | 20:57 | 16/03/2025 | 22:13 | DN25 | DANDENONG | Urban | Asset Failure | HV | 60 | 4555.998 | 75.9333 | 2 | No
| 1881141 | 16/03/2025 | 21:05 | 16/03/2025 | 22:00 | FSH34 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 1 | 54.95 | 54.95 | 1 | No
| 1881143 | 16/03/2025 | 21:11 | 16/03/2025 | 23:51 | GW7 | GLEN WAVERLEY | Urban | Overloads |  | 10.23 | 1633.2195 | 159.65 | 1 | No
| 1881142 | 16/03/2025 | 21:14 | 17/03/2025 | 12:20 | FTN24 | FRANKSTON | Urban | Asset Failure | LV | 1 | 905.9167 | 905.9167 | 1 | No
| 1881157 | 17/03/2025 | 2:41 | 17/03/2025 | 8:40 | HGS23 | HASTINGS | Rural Short | Weather |  | 16 | 5735.4672 | 358.4667 | 1 | No
| 1881167 | 17/03/2025 | 6:19 | 17/03/2025 | 10:07 | BT16 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 227.6833 | 227.6833 | 1 | No
| 1881188 | 17/03/2025 | 8:17 | 17/03/2025 | 10:54 | KBH31 | KEYSBOROUGH | Urban | Overloads |  | 5.6 | 876.2135 | 156.4667 | 1 | No
| 1881191 | 17/03/2025 | 8:23 | 17/03/2025 | 11:26 | EB24 | EAST BURWOOD | Urban | Third Party | Other | 1 | 182.6833 | 182.6833 | 1 | No
| 1881209 | 17/03/2025 | 8:47 | 17/03/2025 | 11:30 | NB22 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 162.35 | 162.35 | 1 | No
| 1881236 | 17/03/2025 | 9:35 | 17/03/2025 | 12:28 | CRM34 | CARRUM | Urban | Third Party | Dig-in | 1 | 172.3833 | 172.3833 | 1 | No
| 1881247 | 17/03/2025 | 10:00 | 17/03/2025 | 12:15 | M25 | MENTONE | Urban | Asset Failure | LV | 15.18 | 2040.192 | 134.4 | 1 | No
| 1881254 | 17/03/2025 | 10:14 | 17/03/2025 | 14:52 | BR13 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 277.75 | 277.75 | 1 | No
| 1881308 | 17/03/2025 | 11:51 | 17/03/2025 | 15:15 | DN11 | DANDENONG | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 203.1333 | 203.1333 | 1 | No
| 1881348 | 17/03/2025 | 13:21 | 17/03/2025 | 15:15 | HT6 | HEATHERTON | Urban | Asset Failure | LV | 1 | 113.5667 | 113.5667 | 1 | No
| 1881351 | 17/03/2025 | 13:35 | 17/03/2025 | 17:43 | NB33 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 247.9333 | 247.9333 | 1 | No
| 1881379 | 17/03/2025 | 16:25 | 17/03/2025 | 20:49 | CRM34 | CARRUM | Urban | Asset Failure | LV | 1 | 263.7833 | 263.7833 | 1 | No
| 1881396 | 17/03/2025 | 17:33 | 17/03/2025 | 18:05 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 70 | 2230.669 | 31.8667 | 1 | No
| 1881400 | 17/03/2025 | 18:03 | 17/03/2025 | 20:25 | LD7 | LYNDALE | Urban | Unknown | Unknown | 11 | 1562 | 142 | 1 | No
| 1881419 | 17/03/2025 | 20:20 | 17/03/2025 | 22:25 | EM5 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 125.9833 | 125.9833 | 1 | No
| 1881425 | 17/03/2025 | 20:30 | 17/03/2025 | 20:40 | MC32 | MORDIALLOC | Urban | Animal | Animal impact | 1 | 10.1833 | 10.1833 | 1 | No
| 1881434 | 18/03/2025 | 4:04 | 18/03/2025 | 5:24 | MTN32 | MORNINGTON | Rural Short | Unknown | Unknown | 136 | 10816.5288 | 79.5333 | 1 | No
| 1881461 | 18/03/2025 | 7:56 | 18/03/2025 | 16:34 | OR23 | ORMOND | Urban | Third Party | Vehicle Impact | 46 | 23801.9318 | 517.4333 | 1 | No
| 1881675 | 18/03/2025 | 19:05 | 18/03/2025 | 22:32 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | HV | 15 | 3102 | 206.8 | 1 | No
| 1881679 | 18/03/2025 | 20:26 | 18/03/2025 | 21:30 | HGS32 | HASTINGS | Urban | Animal | Animal impact | 3.35 | 211.8875 | 63.25 | 1 | No
| 1881698 | 19/03/2025 | 3:44 | 19/03/2025 | 4:57 | HGS23 | HASTINGS | Rural Short | Unknown | Unknown | 13.4 | 970.6062 | 72.4333 | 1 | No
| 1881710 | 19/03/2025 | 4:52 | 19/03/2025 | 5:34 | NW14 | NUNAWADING | Urban | Animal | Animal impact | 56.95 | 2341.5961 | 41.1167 | 1 | No
| 1881788 | 19/03/2025 | 9:47 | 19/03/2025 | 11:16 | BU25 | BULLEEN | Urban | Asset Failure | LV | 1 | 88.3333 | 88.3333 | 1 | No
| 1881901 | 19/03/2025 | 11:17 | 19/03/2025 | 15:03 | LD1 | LYNDALE | Urban | Unknown | Unknown | 0.67 | 151.1297 | 225.5667 | 1 | No
| 1881831 | 19/03/2025 | 11:26 | 19/03/2025 | 12:34 | CFD16 | CAULFIELD | Urban | Third Party | Other | 1 | 67.2 | 67.2 | 1 | No
| 1881883 | 19/03/2025 | 13:29 | 19/03/2025 | 15:21 | SV34 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 111.4167 | 111.4167 | 1 | No
| 1881897 | 19/03/2025 | 14:07 | 19/03/2025 | 16:45 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 157.8167 | 157.8167 | 1 | No
| 1881931 | 19/03/2025 | 17:27 | 20/03/2025 | 1:06 | KBH32 | KEYSBOROUGH | Urban | Animal | Animal impact | 31 | 14252.25 | 459.75 | 1 | No
| 1881934 | 19/03/2025 | 17:40 | 19/03/2025 | 20:27 | MC21 | MORDIALLOC | Urban | Network Business | Network Error | 1 | 166.3333 | 166.3333 | 1 | No
| 1881939 | 19/03/2025 | 18:33 | 19/03/2025 | 19:54 | SV16 | SPRINGVALE | Urban | Animal | Animal impact | 113.23 | 9147.0931 | 80.7833 | 1 | No
| 1881944 | 19/03/2025 | 18:43 | 19/03/2025 | 20:08 | OR32 | ORMOND | Urban | Asset Failure | Distribution substation | 50.49 | 4291.65 | 85 | 1 | No
| 1881948 | 19/03/2025 | 19:02 | 19/03/2025 | 19:57 | CRM23 | CARRUM | Urban | Overloads |  | 19.92 | 1093.608 | 54.9 | 1 | No
| 1881977 | 20/03/2025 | 0:49 | 20/03/2025 | 2:06 | BR15 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 76.9667 | 76.9667 | 1 | No
| 1881980 | 20/03/2025 | 2:33 | 20/03/2025 | 3:13 | BH12 | BOX HILL | Urban | Animal | Animal impact | 64.32 | 2543.856 | 39.55 | 1 | No
| 1881988 | 20/03/2025 | 7:10 | 20/03/2025 | 7:56 | EB14 | EAST BURWOOD | Urban | Third Party | Other | 1 | 46.1333 | 46.1333 | 1 | No
| 1882035 | 20/03/2025 | 8:23 | 20/03/2025 | 9:21 | SVW41 | SPRINGVALE WEST | Urban | Third Party | Other | 1 | 57.9167 | 57.9167 | 1 | No
| 1882094 | 20/03/2025 | 10:08 | 20/03/2025 | 12:00 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 111.7667 | 111.7667 | 1 | No
| 1882122 | 20/03/2025 | 11:10 | 20/03/2025 | 17:24 | HT2 | HEATHERTON | Urban | Third Party | Other | 1 | 374.0833 | 374.0833 | 1 | No
| 1882153 | 20/03/2025 | 12:38 | 20/03/2025 | 13:28 | GW7 | GLEN WAVERLEY | Urban | Weather |  | 10.23 | 503.9983 | 49.2667 | 1 | No
| 1882156 | 20/03/2025 | 12:40 | 20/03/2025 | 14:44 | LD3 | LYNDALE | Urban | Asset Failure | Distribution substation | 70.35 | 8683.5327 | 123.4333 | 1 | No
| 1882314 | 20/03/2025 | 14:51 | 20/03/2025 | 23:15 | CRM23 | CARRUM | Urban | Asset Failure | LV | 16 | 8051.2 | 503.2 | 1 | No
| 1882318 | 20/03/2025 | 14:59 | 20/03/2025 | 18:30 | EB22 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 34 | 7164.3678 | 210.7167 | 1 | No
| 1882322 | 20/03/2025 | 15:16 | 20/03/2025 | 19:07 | MTN32 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 48 | 11067.2016 | 230.5667 | 1 | No
| 1882339 | 20/03/2025 | 17:24 | 20/03/2025 | 18:50 | GW11 | GLEN WAVERLEY | Urban | Asset Failure | LV | 19.5 | 1676.6744 | 85.9833 | 1 | No
| 1882338 | 20/03/2025 | 17:25 | 20/03/2025 | 20:00 | EW3 | ELWOOD | Urban | Asset Failure | LV | 1 | 154.4667 | 154.4667 | 1 | No
| 1882345 | 20/03/2025 | 17:46 | 20/03/2025 | 19:11 | CRM35 | CARRUM | Urban | Asset Failure | HV | 17 | 1429.4161 | 84.0833 | 1 | No
| 1882142 | 20/03/2025 | 18:25 | 20/03/2025 | 21:06 | LD32 | LYNDALE | Urban | Overloads |  | 1 | 161 | 161 | 1 | No
| 1882376 | 20/03/2025 | 20:30 | 20/03/2025 | 22:48 | MTN31 | MORNINGTON | Urban | Asset Failure | HV | 61.64 | 8458.0374 | 137.2167 | 1 | No
| 1882380 | 20/03/2025 | 20:56 | 21/03/2025 | 1:06 | MTN23 | MORNINGTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 250.7167 | 250.7167 | 1 | No
| 1882399 | 21/03/2025 | 2:48 | 21/03/2025 | 3:03 | MTN32 | MORNINGTON | Rural Short | Weather |  | 48 | 740.0016 | 15.4167 | 1 | No
| 1882408 | 21/03/2025 | 7:17 | 21/03/2025 | 10:40 | DN21 | DANDENONG | Urban | Third Party | Other | 8 | 1619.8664 | 202.4833 | 1 | No
| 1882428 | 21/03/2025 | 8:46 | 21/03/2025 | 10:32 | MR31 | MOORABBIN | Urban | Asset Failure | LV | 1 | 105.5333 | 105.5333 | 1 | No
| 1882464 | 21/03/2025 | 10:14 | 21/03/2025 | 12:02 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 29.04 | 3118.411 | 107.3833 | 1 | No
| 1882486 | 21/03/2025 | 10:54 | 21/03/2025 | 13:39 | GW3 | GLEN WAVERLEY | Urban | Third Party | Other | 1 | 164.3667 | 164.3667 | 1 | No
| 1882493 | 21/03/2025 | 11:35 | 21/03/2025 | 15:12 | BT12 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 217.0833 | 217.0833 | 1 | No
| 1882504 | 21/03/2025 | 12:32 | 21/03/2025 | 14:42 | NW23 | NUNAWADING | Urban | Third Party |  | 20.46 | 2675.4867 | 130.7667 | 1 | No
| 1882519 | 21/03/2025 | 13:39 | 21/03/2025 | 17:41 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 1 | 242.1167 | 242.1167 | 1 | No
| 1882541 | 21/03/2025 | 15:55 | 21/03/2025 | 17:38 | MC32 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 103.4 | 103.4 | 1 | No
| 1882549 | 21/03/2025 | 18:07 | 21/03/2025 | 20:29 | CFD23 | CAULFIELD | Urban | Overloads |  | 1.55 | 220.3325 | 142.15 | 1 | No
| 1882580 | 22/03/2025 | 9:14 | 22/03/2025 | 11:36 | MTN22 | MORNINGTON | Rural Short | Weather |  | 1 | 141.8 | 141.8 | 1 | No
| 1882585 | 22/03/2025 | 9:30 | 22/03/2025 | 9:45 | GW7 | GLEN WAVERLEY | Urban | Unknown | Unknown | 1 | 14.95 | 14.95 | 1 | No
| 1882591 | 22/03/2025 | 10:37 | 22/03/2025 | 12:49 | RBD11 | ROSEBUD | Urban | Asset Failure | LV | 1 | 132.8 | 132.8 | 1 | No
| 1882595 | 22/03/2025 | 11:30 | 22/03/2025 | 14:52 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 1 | 202.35 | 202.35 | 1 | No
| 1882599 | 22/03/2025 | 13:40 | 22/03/2025 | 15:05 | NB25 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 84.5167 | 84.5167 | 1 | No
| 1882602 | 22/03/2025 | 16:32 | 22/03/2025 | 18:07 | GW4 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 95.5667 | 95.5667 | 1 | No
| 1882621 | 22/03/2025 | 18:57 | 22/03/2025 | 20:24 | LWN34 | LANGWARRIN | Urban | Asset Failure | LV | 13.86 | 1192.1915 | 86.0167 | 1 | No
| 1882638 | 22/03/2025 | 23:26 | 23/03/2025 | 0:37 | GW3 | GLEN WAVERLEY | Urban | Animal | Animal impact | 99.66 | 7109.0767 | 71.3333 | 1 | No
| 1882623 | 22/03/2025 | 23:40 | 23/03/2025 | 0:58 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 1 | 78 | 78 | 1 | No
| 1882690 | 23/03/2025 | 9:58 | 23/03/2025 | 14:51 | DVY33 | DANDENONG VALLEY | Urban | Third Party | Other | 14 | 4101.5338 | 292.9667 | 1 | No
| 1882705 | 23/03/2025 | 12:38 | 23/03/2025 | 14:00 | DN10 | DANDENONG | Urban | Asset Failure | LV | 2 | 163.3334 | 81.6667 | 1 | No
| 1882712 | 23/03/2025 | 13:01 | 23/03/2025 | 14:10 | MC15 | MORDIALLOC | Urban | Animal | Animal impact | 24.79 | 1694.8105 | 68.3667 | 1 | No
| 1882716 | 23/03/2025 | 13:17 | 23/03/2025 | 16:23 | HGS21 | HASTINGS | Rural Short | Animal | Animal impact | 10.05 | 1870.9753 | 186.1667 | 1 | No
| 1882719 | 23/03/2025 | 13:54 | 23/03/2025 | 16:44 | MR21 | MOORABBIN | Urban | Asset Failure | LV | 1 | 169.3333 | 169.3333 | 1 | No
| 1882728 | 23/03/2025 | 15:02 | 23/03/2025 | 16:41 | HGS21 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 98.8167 | 98.8167 | 1 | No
| 1882757 | 23/03/2025 | 15:53 | 23/03/2025 | 20:26 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 1.98 | 539.9791 | 272.7167 | 1 | No
| 1882741 | 23/03/2025 | 16:55 | 23/03/2025 | 18:12 | RWT12 | RINGWOOD | Urban | Asset Failure | LV | 1 | 76.8833 | 76.8833 | 1 | No
| 1882743 | 23/03/2025 | 17:04 | 23/03/2025 | 17:26 | HGS21 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 22.1833 | 22.1833 | 1 | No
| 1882762 | 23/03/2025 | 21:12 | 23/03/2025 | 21:46 | NW14 | NUNAWADING | Urban | Asset Failure | LV | 1 | 34.35 | 34.35 | 1 | No
| 1882766 | 23/03/2025 | 22:57 | 24/03/2025 | 0:11 | LWN33 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 73.95 | 73.95 | 1 | No
| 1882808 | 24/03/2025 | 8:22 | 24/03/2025 | 10:20 | SVW53 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 117.5833 | 117.5833 | 1 | No
| 1882816 | 24/03/2025 | 8:41 | 24/03/2025 | 11:20 | RBD12 | ROSEBUD | Rural Short | Animal | Animal impact | 0.67 | 106.1727 | 158.4667 | 1 | No
| 1883058 | 24/03/2025 | 18:28 | 24/03/2025 | 23:30 | SR34 | SANDRINGHAM | Urban | Unknown | Unknown | 1 | 301.35 | 301.35 | 1 | No
| 1883048 | 24/03/2025 | 20:45 | 25/03/2025 | 1:13 | CDA22 | CLARINDA | Urban | Third Party | Vehicle Impact | 65 | 17408.0855 | 267.8167 | 1 | No
| 1883076 | 25/03/2025 | 4:06 | 25/03/2025 | 5:29 | M34 | MENTONE | Urban | Animal | Animal impact | 10 | 826.667 | 82.6667 | 1 | No
| 1883223 | 25/03/2025 | 10:35 | 25/03/2025 | 13:23 | MGE32 | MULGRAVE | Urban | Asset Failure | LV | 1 | 168.0667 | 168.0667 | 1 | No
| 1883393 | 25/03/2025 | 17:45 | 25/03/2025 | 19:00 | FTN24 | FRANKSTON | Urban | Animal | Animal impact | 55.61 | 4160.5567 | 74.8167 | 1 | No
| 1883407 | 25/03/2025 | 18:32 | 25/03/2025 | 21:38 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 10.89 | 2022.8175 | 185.75 | 1 | No
| 1883423 | 25/03/2025 | 19:21 | 25/03/2025 | 21:18 | HGS32 | HASTINGS | Urban | Unknown | Unknown | 1 | 117.2167 | 117.2167 | 1 | No
| 1883438 | 25/03/2025 | 20:54 | 25/03/2025 | 22:04 | GW4 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 69.95 | 69.95 | 1 | No
| 1883466 | 26/03/2025 | 1:26 | 26/03/2025 | 2:41 | DC3 | DONCASTER | Urban | Animal | Other | 113.9 | 8519.72 | 74.8 | 1 | No
| 1883452 | 26/03/2025 | 1:30 | 26/03/2025 | 2:55 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 0 | 925.65 | 85 | 1 | No
| 1883469 | 26/03/2025 | 1:35 | 26/03/2025 | 2:50 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 139 | 10290.6287 | 74.0333 | 1 | No
| 1883489 | 26/03/2025 | 6:01 | 26/03/2025 | 7:18 | DC8 | DONCASTER | Urban | Asset Failure | Distribution substation | 56.28 | 4331.6859 | 76.9667 | 1 | No
| 1883561 | 26/03/2025 | 9:08 | 26/03/2025 | 12:24 | TK6 | TOORAK | Urban | Third Party | Other | 33 | 6465.2511 | 195.9167 | 1 | No
| 1883562 | 26/03/2025 | 9:08 | 26/03/2025 | 12:15 | TK6 | TOORAK | Urban | Third Party | Other | 1 | 186.9167 | 186.9167 | 1 | No
| 1883596 | 26/03/2025 | 10:12 | 26/03/2025 | 10:55 | DMA21 | DROMANA | Urban | Asset Failure | LV | 1 | 43.6 | 43.6 | 1 | No
| 1883651 | 26/03/2025 | 11:52 | 26/03/2025 | 15:39 | SR24 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 226.0667 | 226.0667 | 1 | No
| 1883675 | 26/03/2025 | 12:26 | 26/03/2025 | 15:53 | BH23 | BOX HILL | Urban | Third Party | Other | 1 | 206.0833 | 206.0833 | 1 | No
| 1883753 | 26/03/2025 | 12:37 | 26/03/2025 | 17:30 | K24 | GARDINER | Urban | Third Party | Other | 30 | 8805.999 | 293.5333 | 1 | No
| 1883718 | 26/03/2025 | 15:04 | 26/03/2025 | 19:28 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 264.5167 | 264.5167 | 1 | No
| 1883777 | 26/03/2025 | 17:27 | 26/03/2025 | 21:15 | GW8 | GLEN WAVERLEY | Urban | Asset Failure | LV | 30 | 6819.999 | 227.3333 | 1 | No
| 1883486 | 26/03/2025 | 18:22 | 26/03/2025 | 20:07 | LD6 | LYNDALE | Urban | Asset Failure | HV | 1 | 105 | 105 | 1 | No
| 1883814 | 27/03/2025 | 4:16 | 27/03/2025 | 5:50 | HGS31 | HASTINGS | Rural Short | Animal | Animal impact | 157.08 | 14741.958 | 93.85 | 1 | No
| 1883827 | 27/03/2025 | 5:02 | 27/03/2025 | 7:35 | HGS21 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 152.9167 | 152.9167 | 1 | No
| 1883857 | 27/03/2025 | 8:23 | 27/03/2025 | 8:28 | STO21 | SORRENTO | Rural Short | Other | XXX | 1 | 4.4667 | 4.4667 | 1 | No
| 1883923 | 27/03/2025 | 9:52 | 28/03/2025 | 0:30 | DC3 | DONCASTER | Urban | Third Party | Dig-in | 31 | 27188.0323 | 877.0333 | 1 | No
| 1884077 | 27/03/2025 | 16:28 | 27/03/2025 | 22:32 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 19 | 6920.75 | 364.25 | 1 | No
| 1884078 | 27/03/2025 | 16:31 | 28/03/2025 | 4:15 | DC3 | DONCASTER | Urban | Third Party | Dig-in | 51 | 35904 | 704 | 1 | No
| 1884091 | 27/03/2025 | 19:06 | 27/03/2025 | 20:56 | RWT35 | RINGWOOD | Urban | Asset Failure | LV | 1 | 109.55 | 109.55 | 1 | No
| 1884107 | 27/03/2025 | 20:05 | 27/03/2025 | 22:05 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 119.5833 | 119.5833 | 1 | No
| 1884117 | 27/03/2025 | 22:46 | 27/03/2025 | 23:38 | SS11 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 52.2667 | 52.2667 | 1 | No
| 1884126 | 28/03/2025 | 3:19 | 28/03/2025 | 4:38 | HGS31 | HASTINGS | Rural Short | Animal | Animal impact | 50 | 3948.335 | 78.9667 | 1 | No
| 1884145 | 28/03/2025 | 7:47 | 28/03/2025 | 8:00 | EB31 | EAST BURWOOD | Urban | Third Party | Other | 1 | 13.75 | 13.75 | 1 | No
| 1884196 | 28/03/2025 | 9:07 | 28/03/2025 | 10:59 | KBH31 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 111.9 | 111.9 | 1 | No
| 1884255 | 28/03/2025 | 11:00 | 28/03/2025 | 11:59 | RWT23 | RINGWOOD | Urban | Asset Failure | LV | 1 | 58.4 | 58.4 | 1 | No
| 1884295 | 28/03/2025 | 13:20 | 28/03/2025 | 16:17 | BH23 | BOX HILL | Urban | Asset Failure | LV | 1 | 177.7 | 177.7 | 1 | No
| 1884338 | 28/03/2025 | 14:10 | 28/03/2025 | 14:30 | DVY31 | DANDENONG VALLEY | Urban | Third Party | Vehicle Impact | 3.96 | 77.6821 | 19.6167 | 1 | No
| 1884354 | 28/03/2025 | 14:30 | 28/03/2025 | 16:50 | DVY31 | DANDENONG VALLEY | Urban | Third Party | Vehicle Impact | 1 | 140 | 140 | 1 | No
| 1884362 | 28/03/2025 | 15:31 | 28/03/2025 | 17:50 | CDA22 | CLARINDA | Urban | Unknown | Unknown | 1 | 138.5833 | 138.5833 | 1 | No
| 1884393 | 28/03/2025 | 16:04 | 28/03/2025 | 18:50 | DSH32 | DANDENONG SOUTH | Urban | Animal | Animal impact | 3 | 497.4501 | 165.8167 | 1 | No
| 1884406 | 28/03/2025 | 17:22 | 28/03/2025 | 20:15 | NB34 | NORTH BRIGHTON | Urban | Asset Failure | LV | 17 | 2926.2661 | 172.1333 | 1 | No
| 1884420 | 28/03/2025 | 17:44 | 28/03/2025 | 19:45 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 25 | 3015.8325 | 120.6333 | 1 | No
| 1884462 | 28/03/2025 | 21:52 | 28/03/2025 | 22:13 | HGS31 | HASTINGS | Rural Short | Animal | Animal impact | 4 | 84.6 | 21.15 | 1 | No
| 1884506 | 29/03/2025 | 0:27 | 29/03/2025 | 1:24 | MGE23 | MULGRAVE | Urban | Animal | Animal impact | 38.19 | 2177.4678 | 57.0167 | 1 | No
| 1884517 | 29/03/2025 | 1:48 | 29/03/2025 | 13:47 | SR35 | SANDRINGHAM | Urban | Animal | Other | 1 | 718.4667 | 718.4667 | 1 | No
| 1884521 | 29/03/2025 | 3:10 | 29/03/2025 | 4:08 | EW12 | ELWOOD | Urban | Unknown | Unknown | 691 | 40193.1897 | 58.1667 | 1 | No
| 1884521 | 29/03/2025 | 3:10 | 29/03/2025 | 4:08 | EW12 | ELWOOD | Urban | Unknown | Unknown | 744 | 43585.9752 | 58.5833 | 2 | No
| 1884521 | 29/03/2025 | 3:10 | 29/03/2025 | 4:20 | EW12 | ELWOOD | Urban | Unknown | Unknown | 1110 | 78144 | 70.4 | 3 | No
| 1884521 | 29/03/2025 | 3:10 | 29/03/2025 | 5:03 | EW12 | ELWOOD | Urban | Unknown | Unknown | 337 | 38271.9779 | 113.5667 | 4 | No
| 1884524 | 29/03/2025 | 3:40 | 29/03/2025 | 4:37 | FSH23 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 75.71 | 4251.1165 | 56.15 | 1 | No
| 1884532 | 29/03/2025 | 5:15 | 29/03/2025 | 11:18 | EW14 | ELWOOD | Urban | Asset Failure | LV | 1 | 362.1333 | 362.1333 | 1 | No
| 1884533 | 29/03/2025 | 5:24 | 29/03/2025 | 7:57 | OR25 | ORMOND | Urban | Overloads |  | 147 | 22471.4049 | 152.8667 | 1 | No
| 1884535 | 29/03/2025 | 6:06 | 29/03/2025 | 8:55 | BH11 | BOX HILL | Urban | Asset Failure | HV | 123 | 20756.25 | 168.75 | 1 | No
| 1884609 | 29/03/2025 | 15:06 | 29/03/2025 | 16:52 | MR15 | MOORABBIN | Urban | Asset Failure | LV | 1 | 106 | 106 | 1 | No
| 1884610 | 29/03/2025 | 15:06 | 29/03/2025 | 16:23 | LD7 | LYNDALE | Urban | Third Party | Other | 17 | 1316.9339 | 77.4667 | 1 | No
| 1884611 | 29/03/2025 | 15:15 | 29/03/2025 | 17:40 | MC23 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 144.3 | 144.3 | 1 | No
| 1884614 | 29/03/2025 | 16:28 | 29/03/2025 | 17:16 | EB22 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 48.1333 | 48.1333 | 1 | No
| 1884620 | 29/03/2025 | 17:37 | 29/03/2025 | 18:40 | DN11 | DANDENONG | Urban | Asset Failure | LV | 14.52 | 911.6135 | 62.7833 | 1 | No
| 1884623 | 29/03/2025 | 18:59 | 29/03/2025 | 22:27 | STO13 | SORRENTO | Urban | Asset Failure | LV | 18 | 3730.8006 | 207.2667 | 1 | No
| 1884630 | 29/03/2025 | 21:01 | 29/03/2025 | 21:58 | BH33 | BOX HILL | Urban | Asset Failure | HV | 34.98 | 1993.2758 | 56.9833 | 1 | No
| 1884636 | 29/03/2025 | 22:34 | 29/03/2025 | 23:14 | DC3 | DONCASTER | Urban | Animal | Animal impact | 0.67 | 26.5655 | 39.65 | 1 | No
| 1884639 | 29/03/2025 | 22:50 | 30/03/2025 | 0:05 | LD5 | LYNDALE | Urban | Third Party | Other | 8 | 597.7336 | 74.7167 | 1 | No
| 1884644 | 30/03/2025 | 1:02 | 30/03/2025 | 3:11 | STO14 | SORRENTO | Rural Short | Animal | Animal impact | 60 | 7756.998 | 129.2833 | 1 | No
| 1884655 | 30/03/2025 | 1:28 | 30/03/2025 | 4:32 | HGS32 | HASTINGS | Urban | Asset Failure | LV | 1 | 183.4333 | 183.4333 | 1 | No
| 1884657 | 30/03/2025 | 3:23 | 30/03/2025 | 5:55 | LWN35 | LANGWARRIN | Urban | Animal | Animal impact | 52.93 | 8034.774 | 151.8 | 1 | No
| 1884661 | 30/03/2025 | 6:01 | 30/03/2025 | 7:38 | FSH33 | FRANKSTON SOUTH | Urban | Animal | Animal impact | 40 | 3874 | 96.85 | 1 | No
| 1884670 | 30/03/2025 | 7:37 | 30/03/2025 | 8:00 | LD33 | LYNDALE | Urban | Third Party | Other | 61 | 1433.5 | 23.5 | 1 | No
| 1884670 | 30/03/2025 | 7:37 | 30/03/2025 | 8:54 | LD33 | LYNDALE | Urban | Third Party | Other | 1888 | 146382.8704 | 77.5333 | 2 | No
| 1884670 | 30/03/2025 | 7:37 | 30/03/2025 | 9:10 | LD33 | LYNDALE | Urban | Third Party | Other | 285 | 26652.2595 | 93.5167 | 3 | No
| 1884670 | 30/03/2025 | 7:37 | 30/03/2025 | 18:29 | LD33 | LYNDALE | Urban | Third Party | Other | 17 | 11095.05 | 652.65 | 4 | No
| 1884670 | 30/03/2025 | 7:37 | 30/03/2025 | 18:38 | LD33 | LYNDALE | Urban | Third Party | Other | 2 | 1322.8666 | 661.4333 | 5 | No
| 1884670 | 30/03/2025 | 7:37 | 30/03/2025 | 18:44 | LD33 | LYNDALE | Urban | Third Party | Other | 36 | 24024.6 | 667.35 | 6 | No
| 1884670 | 30/03/2025 | 7:37 | 30/03/2025 | 18:47 | LD33 | LYNDALE | Urban | Third Party | Other | 31 | 20777.75 | 670.25 | 7 | No
| 1884672 | 30/03/2025 | 7:37 | 30/03/2025 | 8:37 | LD7 | LYNDALE | Urban | Asset Failure | HV | 97 | 5805.45 | 59.85 | 1 | No
| 1884672 | 30/03/2025 | 7:37 | 30/03/2025 | 8:52 | LD7 | LYNDALE | Urban | Asset Failure | HV | 1094 | 82122.9698 | 75.0667 | 2 | No
| 1884672 | 30/03/2025 | 7:37 | 30/03/2025 | 9:41 | LD7 | LYNDALE | Urban | Asset Failure | HV | 147 | 18328.4451 | 124.6833 | 3 | No
| 1884672 | 30/03/2025 | 7:37 | 30/03/2025 | 10:01 | LD7 | LYNDALE | Urban | Asset Failure | HV | 5 | 720.25 | 144.05 | 4 | No
| 1884672 | 30/03/2025 | 7:37 | 30/03/2025 | 10:23 | LD7 | LYNDALE | Urban | Asset Failure | HV | 386 | 64166.0538 | 166.2333 | 5 | No
| 1884716 | 30/03/2025 | 9:23 | 30/03/2025 | 12:21 | M21 | MENTONE | Urban | Asset Failure | LV | 1 | 178.4333 | 178.4333 | 1 | No
| 1884721 | 30/03/2025 | 9:38 | 30/03/2025 | 11:05 | MGE23 | MULGRAVE | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 7 | 604.1 | 86.3 | 1 | No
| 1884722 | 30/03/2025 | 9:49 | 30/03/2025 | 12:33 | OAK34 | OAKLEIGH | Urban | Asset Failure | LV | 2.31 | 378.1084 | 163.6833 | 1 | No
| 1884734 | 30/03/2025 | 11:40 | 30/03/2025 | 14:00 | NP23 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 139.35 | 139.35 | 1 | No
| 1884743 | 30/03/2025 | 12:28 | 30/03/2025 | 13:23 | FTN25 | FRANKSTON | Urban | Vegetation | Grow-in - Other responsible party | 206 | 11213.2598 | 54.4333 | 1 | No
| 1884743 | 30/03/2025 | 12:28 | 30/03/2025 | 13:24 | FTN25 | FRANKSTON | Urban | Vegetation | Grow-in - Other responsible party | 3627 | 200754.45 | 55.35 | 2 | No
| 1884791 | 30/03/2025 | 23:00 | 30/03/2025 | 23:57 | MGE31 | MULGRAVE | Urban | Animal | Animal impact | 113 | 6392.0371 | 56.5667 | 1 | No
| 1884802 | 31/03/2025 | 2:57 | 31/03/2025 | 3:51 | NW14 | NUNAWADING | Urban | Animal | Animal impact | 50.25 | 2728.575 | 54.3 | 1 | No
| 1884808 | 31/03/2025 | 3:05 | 31/03/2025 | 3:50 | NW14 | NUNAWADING | Urban | Animal | Animal impact | 1 | 45.4 | 45.4 | 1 | No
| 1884800 | 31/03/2025 | 6:38 | 31/03/2025 | 7:38 | BH12 | BOX HILL | Urban | Asset Failure | LV | 1 | 60.4 | 60.4 | 1 | No
| 1884816 | 31/03/2025 | 6:51 | 31/03/2025 | 8:25 | STO14 | SORRENTO | Rural Short | Asset Failure | Distribution substation | 60 | 5668.998 | 94.4833 | 1 | No
| 1884811 | 31/03/2025 | 8:21 | 31/03/2025 | 9:54 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 93 | 93 | 1 | No
| 1884879 | 31/03/2025 | 9:08 | 31/03/2025 | 12:53 | MGE11 | MULGRAVE | Urban | Other | XXX | 1 | 224.3 | 224.3 | 1 | No
| 1884955 | 31/03/2025 | 11:26 | 31/03/2025 | 14:55 | LWN33 | LANGWARRIN | Urban | Third Party | Other | 1 | 208.4667 | 208.4667 | 1 | No
| 1884875 | 31/03/2025 | 12:27 | 31/03/2025 | 13:58 | RBD12 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 91 | 91 | 1 | No
| 1885011 | 31/03/2025 | 13:28 | 31/03/2025 | 15:41 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 133.45 | 133.45 | 1 | No
| 1885057 | 31/03/2025 | 17:01 | 31/03/2025 | 18:15 | LWN32 | LANGWARRIN | Rural Short | Asset Failure | LV | 4 | 293.5332 | 73.3833 | 1 | No
| 1885095 | 31/03/2025 | 21:09 | 31/03/2025 | 21:51 | RWT24 | RINGWOOD | Urban | Unknown | Unknown | 1 | 42 | 42 | 1 | No
| 1885111 | 31/03/2025 | 21:55 | 31/03/2025 | 23:59 | BC22 | BALACLAVA | Urban | Asset Failure | LV | 1 | 123.4 | 123.4 | 1 | No
| 1885113 | 31/03/2025 | 22:19 | 31/03/2025 | 23:45 | FSH22 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 85.2333 | 85.2333 | 1 | No
| 1885116 | 31/03/2025 | 22:46 | 2025-01-04 | 0:09 | BC22 | BALACLAVA | Urban | Asset Failure | LV | 1 | 83.3333 | 83.3333 | 1 | No
| 1885158 | 2025-01-04 | 8:32 | 2025-01-04 | 10:54 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 142.5667 | 142.5667 | 1 | No
| 1885179 | 2025-01-04 | 8:54 | 2025-01-04 | 9:11 | MTN34 | MORNINGTON | Urban | Weather |  | 20.46 | 347.4783 | 16.9833 | 1 | No
| 1885251 | 2025-01-04 | 10:56 | 2025-01-04 | 13:34 | BT15 | BENTLEIGH | Urban | Unknown | Unknown | 1 | 158.3333 | 158.3333 | 1 | No
| 1885374 | 2025-01-04 | 14:55 | 2025-01-04 | 16:10 | LD4 | LYNDALE | Urban | Third Party | Other | 1 | 74.1 | 74.1 | 1 | No
| 1885394 | 2025-01-04 | 16:46 | 2025-01-04 | 18:18 | BH21 | BOX HILL | Urban | Third Party | Other | 1 | 92.0833 | 92.0833 | 1 | No
| 1885399 | 2025-01-04 | 16:59 | 2025-01-04 | 18:50 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 110.75 | 110.75 | 1 | No
| 1885430 | 2025-01-04 | 20:09 | 2025-01-04 | 22:03 | CFD13 | CAULFIELD | Urban | Asset Failure | LV | 1 | 114 | 114 | 1 | No
| 1885451 | 2025-01-04 | 21:08 | 2025-01-04 | 21:42 | CFD23 | CAULFIELD | Urban | Asset Failure | LV | 3 | 103.7499 | 34.5833 | 1 | No
| 1885468 | 2025-02-04 | 2:45 | 2025-02-04 | 3:50 | STO21 | SORRENTO | Rural Short | Animal | Animal impact | 16.75 | 1082.3297 | 64.6167 | 1 | No
| 1885498 | 2025-02-04 | 7:56 | 2025-02-04 | 10:05 | DC3 | DONCASTER | Urban | Asset Failure | HV | 20.77 | 2665.1379 | 128.3167 | 1 | No
| 1885629 | 2025-02-04 | 10:50 | 2025-02-04 | 11:57 | EL22 | ELSTERNWICK | Urban | Asset Failure | LV | 9 | 608.4 | 67.6 | 1 | No
| 1885385 | 2025-02-04 | 11:52 | 2025-02-04 | 14:00 | EM7 | EAST MALVERN | Urban | Third Party | Vehicle Impact | 1 | 128.4333 | 128.4333 | 1 | No
| 1885746 | 2025-02-04 | 13:25 | 2025-02-04 | 20:47 | MGE23 | MULGRAVE | Urban | Third Party | Dig-in | 25 | 11067.5 | 442.7 | 1 | No
| 1885698 | 2025-02-04 | 13:42 | 2025-02-04 | 16:39 | NW23 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 177 | 177 | 1 | No
| 1885813 | 2025-02-04 | 15:20 | 2025-02-04 | 16:22 | LD4 | LYNDALE | Urban | Animal | Animal impact | 33.5 | 2055.7845 | 61.3667 | 1 | No
| 1885818 | 2025-02-04 | 15:36 | 2025-02-04 | 18:40 | BT13 | BENTLEIGH | Urban | Third Party | Vehicle Impact | 1 | 184 | 184 | 1 | No
| 1885823 | 2025-02-04 | 15:48 | 2025-02-04 | 17:33 | DMA15 | DROMANA | Rural Short | Third Party | Other | 1 | 104.9667 | 104.9667 | 1 | No
| 1885502 | 2025-02-04 | 16:19 | 2025-02-04 | 19:18 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 179 | 179 | 1 | No
| 1885837 | 2025-02-04 | 18:55 | 2025-02-04 | 21:25 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 6 | 900 | 150 | 1 | No
| 1885884 | 2025-02-04 | 20:13 | 2025-02-04 | 22:18 | DC2 | DONCASTER | Urban | Overloads |  | 67 | 8319.1689 | 124.1667 | 1 | No
| 1885920 | 2025-03-04 | 0:34 | 2025-03-04 | 4:22 | NW22 | NUNAWADING | Urban | Third Party | Vehicle Impact | 45 | 10215.7515 | 227.0167 | 1 | No
| 1885930 | 2025-03-04 | 3:56 | 2025-03-04 | 7:09 | HGS31 | HASTINGS | Rural Short | Animal | Animal impact | 4 | 770.2 | 192.55 | 1 | No
| 1885968 | 2025-03-04 | 8:29 | 2025-03-04 | 9:30 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 18.15 | 1093.5375 | 60.25 | 1 | No
| 1886195 | 2025-03-04 | 17:00 | 2025-03-04 | 17:33 | FSH31 | FRANKSTON SOUTH | Urban | Third Party |  | 712 | 23163.7096 | 32.5333 | 1 | No
| 1886195 | 2025-03-04 | 17:00 | 2025-03-04 | 17:37 | FSH31 | FRANKSTON SOUTH | Urban | Third Party |  | 480 | 17432.016 | 36.3167 | 2 | No
| 1886195 | 2025-03-04 | 17:00 | 2025-03-04 | 18:28 | FSH31 | FRANKSTON SOUTH | Urban | Third Party |  | 711 | 61987.3263 | 87.1833 | 3 | No
| 1886202 | 2025-03-04 | 18:27 | 2025-03-04 | 20:16 | M33 | MENTONE | Urban | Asset Failure | LV | 1 | 109.7333 | 109.7333 | 1 | No
| 1886220 | 2025-03-04 | 20:02 | 2025-03-04 | 22:00 | NP16 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 117.8667 | 117.8667 | 1 | No
| 1886222 | 2025-03-04 | 20:58 | 2025-03-04 | 21:54 | BH34 | BOX HILL | Urban | Overloads |  | 60.97 | 3468.1748 | 56.8833 | 1 | No
| 1886229 | 2025-03-04 | 21:39 | 2025-03-04 | 23:23 | MGE23 | MULGRAVE | Urban | Asset Failure | LV | 23 | 2403.8841 | 104.5167 | 1 | No
| 1886237 | 2025-04-04 | 1:35 | 2025-04-04 | 2:50 | GW4 | GLEN WAVERLEY | Urban | Animal | Other | 1 | 74.2833 | 74.2833 | 1 | No
| 1886240 | 2025-04-04 | 3:48 | 2025-04-04 | 5:07 | STO13 | SORRENTO | Urban | Asset Failure | Distribution substation | 42.88 | 3387.52 | 79 | 1 | No
| 1886244 | 2025-04-04 | 4:10 | 2025-04-04 | 6:49 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 29 | 4593.6 | 158.4 | 1 | No
| 1886250 | 2025-04-04 | 4:48 | 2025-04-04 | 5:02 | FSH32 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 483 | 6826.3839 | 14.1333 | 1 | No
| 1886250 | 2025-04-04 | 4:48 | 2025-04-04 | 5:04 | FSH32 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 315 | 5218.5105 | 16.5667 | 2 | No
| 1886250 | 2025-04-04 | 4:48 | 2025-04-04 | 5:56 | FSH32 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 296 | 20147.7432 | 68.0667 | 3 | No
| 1886250 | 2025-04-04 | 4:48 | 2025-04-04 | 6:06 | FSH32 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 197 | 15543.3 | 78.9 | 4 | No
| 1886250 | 2025-04-04 | 4:48 | 2025-04-04 | 6:12 | FSH32 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 207 | 17567.4069 | 84.8667 | 5 | No
| 1886252 | 2025-04-04 | 4:59 | 2025-04-04 | 7:15 | LWN21 | LANGWARRIN | Rural Short | Animal | Other | 6.03 | 815.1553 | 135.1833 | 1 | No
| 1886338 | 2025-04-04 | 9:16 | 2025-04-04 | 13:14 | DC5 | DONCASTER | Urban | Asset Failure | LV | 1 | 237.5333 | 237.5333 | 1 | No
| 1886364 | 2025-04-04 | 10:21 | 2025-04-04 | 11:47 | CRM23 | CARRUM | Urban | Network Business | Switching and protection error | 67 | 5748.6 | 85.8 | 1 | No
| 1886455 | 2025-04-04 | 12:25 | 2025-04-04 | 15:25 | SS22 | SPRINGVALE SOUTH | Urban | Animal | Animal impact | 17.42 | 3133.858 | 179.9 | 1 | No
| 1886473 | 2025-04-04 | 13:38 | 2025-04-04 | 15:37 | SVW53 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 118.4 | 118.4 | 1 | No
| 1886494 | 2025-04-04 | 14:52 | 2025-04-04 | 15:32 | OAK22 | OAKLEIGH | Urban | Asset Failure | HV | 630 | 25588.521 | 40.6167 | 1 | No
| 1886512 | 2025-04-04 | 15:38 | 2025-04-04 | 15:45 | FSH13 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 1 | 6.3833 | 6.3833 | 1 | No
| 1886515 | 2025-04-04 | 15:38 | 2025-04-04 | 15:54 | FSH13 | FRANKSTON SOUTH | Urban | Unknown | Unknown | 1 | 15.3667 | 15.3667 | 1 | No
| 1886203 | 2025-04-04 | 17:12 | 2025-04-04 | 20:52 | EW3 | ELWOOD | Urban | Asset Failure | LV | 1 | 220.35 | 220.35 | 1 | No
| 1886571 | 2025-04-04 | 19:30 | 2025-04-04 | 22:35 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 185 | 185 | 1 | No
| 1886587 | 2025-04-04 | 21:15 | 2025-04-04 | 22:53 | SR26 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 97.3333 | 97.3333 | 1 | No
| 1886613 | 2025-05-04 | 1:20 | 2025-05-04 | 2:35 | HT4 | HEATHERTON | Urban | Animal | Animal impact | 91 | 6752.2 | 74.2 | 1 | No
| 1886613 | 2025-05-04 | 1:20 | 2025-05-04 | 2:37 | HT4 | HEATHERTON | Urban | Animal | Animal impact | 38 | 2923.4654 | 76.9333 | 2 | No
| 1886627 | 2025-05-04 | 3:29 | 2025-05-04 | 4:10 | LD33 | LYNDALE | Urban | Asset Failure | HV | 78 | 3217.5 | 41.25 | 1 | No
| 1886627 | 2025-05-04 | 3:29 | 2025-05-04 | 5:23 | LD33 | LYNDALE | Urban | Asset Failure | HV | 560 | 64353.352 | 114.9167 | 2 | No
| 1886627 | 2025-05-04 | 3:29 | 2025-05-04 | 5:32 | LD33 | LYNDALE | Urban | Asset Failure | HV | 1397 | 172319.95 | 123.35 | 3 | No
| 1886627 | 2025-05-04 | 3:29 | 2025-05-04 | 5:39 | LD33 | LYNDALE | Urban | Asset Failure | HV | 191 | 24938.2397 | 130.5667 | 4 | No
| 1886627 | 2025-05-04 | 3:29 | 2025-05-04 | 5:59 | LD33 | LYNDALE | Urban | Asset Failure | HV | 6 | 903.4998 | 150.5833 | 5 | No
| 1886627 | 2025-05-04 | 3:29 | 2025-05-04 | 6:18 | LD33 | LYNDALE | Urban | Asset Failure | HV | 38 | 6456.8346 | 169.9167 | 6 | No
| 1886627 | 2025-05-04 | 3:29 | 2025-05-04 | 6:18 | LD33 | LYNDALE | Urban | Asset Failure | HV | 50 | 8497.5 | 169.95 | 7 | No
| 1886629 | 2025-05-04 | 4:17 | 2025-05-04 | 9:10 | NP36 | NOBLE PARK | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 36.18 | 10567.5738 | 292.0833 | 1 | No
| 1886643 | 2025-05-04 | 8:07 | 2025-05-04 | 11:48 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 220.7833 | 220.7833 | 1 | No
| 1886762 | 2025-05-04 | 8:27 | 2025-05-04 | 17:39 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 551.6833 | 551.6833 | 1 | No
| 1886761 | 2025-05-04 | 9:15 | 2025-05-04 | 17:39 | CRM23 | CARRUM | Urban | Asset Failure | LV | 0 | 503.1 | 503.1 | 1 | No
| 1886697 | 2025-05-04 | 12:16 | 2025-05-04 | 13:30 | BR6 | BEAUMARIS | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 73.9667 | 73.9667 | 1 | No
| 1886708 | 2025-05-04 | 13:10 | 2025-05-04 | 13:35 | CRM35 | CARRUM | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 53 | 1325 | 25 | 1 | No
| 1886754 | 2025-05-04 | 17:02 | 2025-05-04 | 19:33 | NW22 | NUNAWADING | Urban | Asset Failure | LV | 1 | 151.2167 | 151.2167 | 1 | No
| 1886756 | 2025-05-04 | 17:06 | 2025-05-04 | 21:19 | FTN12 | FRANKSTON | Urban | Animal | Animal impact | 4 | 1012.0668 | 253.0167 | 1 | No
| 1886648 | 2025-05-04 | 17:39 | 2025-05-04 | 18:05 | CRM23 | CARRUM | Urban | Asset Failure | HV | 37 | 962 | 26 | 1 | No
| 1886772 | 2025-05-04 | 19:01 | 2025-05-04 | 20:56 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 114.5667 | 114.5667 | 1 | No
| 1886789 | 2025-05-04 | 20:47 | 2025-05-04 | 21:53 | CRM33 | CARRUM | Urban | Overloads |  | 56.95 | 3794.7664 | 66.6333 | 1 | No
| 1886795 | 2025-05-04 | 22:06 | 2025-05-04 | 23:23 | MGE21 | MULGRAVE | Urban | Animal | Animal impact | 6 | 461.5002 | 76.9167 | 1 | No
| 1886796 | 2025-05-04 | 22:18 | 2025-05-04 | 23:34 | CFD26 | CAULFIELD | Urban | Asset Failure | LV | 1 | 76.8833 | 76.8833 | 1 | No
| 1886797 | 2025-05-04 | 22:30 | 2025-05-04 | 23:39 | NP14 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 69.4333 | 69.4333 | 1 | No
| 1886801 | 2025-05-04 | 23:31 | 2025-06-04 | 1:36 | DC8 | DONCASTER | Urban | Animal | Animal impact | 71 | 8844.2357 | 124.5667 | 1 | No
| 1886799 | 2025-05-04 | 23:40 | 2025-06-04 | 0:42 | OAK26 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 62.3833 | 62.3833 | 1 | No
| 1886812 | 2025-06-04 | 0:50 | 2025-06-04 | 2:50 | GW3 | GLEN WAVERLEY | Urban | Animal | Animal impact | 139 | 16596.6 | 119.4 | 1 | No
| 1886816 | 2025-06-04 | 2:05 | 2025-06-04 | 9:55 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 469.9167 | 469.9167 | 1 | No
| 1886809 | 2025-06-04 | 6:10 | 2025-06-04 | 7:58 | RWT24 | RINGWOOD | Urban | Asset Failure | LV | 1 | 108.1333 | 108.1333 | 1 | No
| 1886828 | 2025-06-04 | 6:25 | 2025-06-04 | 8:17 | LD3 | LYNDALE | Urban | Animal | Other | 69.01 | 7718.7685 | 111.85 | 1 | No
| 1886910 | 2025-06-04 | 17:21 | 2025-06-04 | 23:15 | MTN23 | MORNINGTON | Urban | Asset Failure | LV | 4 | 1415.5332 | 353.8833 | 1 | No
| 1886932 | 2025-06-04 | 21:52 | 2025-06-04 | 23:15 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 83.0667 | 83.0667 | 1 | No
| 1886940 | 2025-06-04 | 23:39 | 2025-07-04 | 0:24 | BR4 | BEAUMARIS | Urban | Animal | Animal impact | 211 | 9322.6763 | 44.1833 | 1 | No
| 1886940 | 2025-06-04 | 23:39 | 2025-07-04 | 0:37 | BR4 | BEAUMARIS | Urban | Animal | Animal impact | 99 | 5717.25 | 57.75 | 2 | No
| 1886940 | 2025-06-04 | 23:39 | 2025-07-04 | 0:41 | BR4 | BEAUMARIS | Urban | Animal | Animal impact | 220 | 13647.326 | 62.0333 | 3 | No
| 1886940 | 2025-06-04 | 23:39 | 2025-07-04 | 3:35 | BR4 | BEAUMARIS | Urban | Animal | Animal impact | 237 | 55718.7 | 235.1 | 4 | No
| 1886951 | 2025-07-04 | 6:21 | 2025-07-04 | 9:00 | GW6 | GLEN WAVERLEY | Urban | Third Party | Other | 5 | 794.75 | 158.95 | 1 | No
| 1886974 | 2025-07-04 | 8:41 | 2025-07-04 | 9:38 | DVY13 | DANDENONG VALLEY | Urban | Third Party | Other | 3 | 168.2499 | 56.0833 | 1 | No
| 1887034 | 2025-07-04 | 10:54 | 2025-07-04 | 13:34 | DMA15 | DROMANA | Rural Short | Asset Failure | LV | 1 | 159.7667 | 159.7667 | 1 | No
| 1887182 | 2025-07-04 | 17:18 | 2025-07-04 | 23:35 | LD1 | LYNDALE | Urban | Third Party | Other | 3 | 1128.0501 | 376.0167 | 1 | No
| 1887214 | 2025-07-04 | 20:24 | 2025-07-04 | 22:21 | DC8 | DONCASTER | Urban | Animal | Animal impact | 47.57 | 5557.7601 | 116.8333 | 1 | No
| 1887231 | 2025-07-04 | 20:49 | 2025-07-04 | 23:45 | DC5 | DONCASTER | Urban | Animal | Animal impact | 38.19 | 6716.9832 | 175.8833 | 1 | No
| 1887244 | 2025-07-04 | 23:04 | 2025-08-04 | 0:06 | LD2 | LYNDALE | Urban | Asset Failure | LV | 1 | 62.1833 | 62.1833 | 1 | No
| 1887247 | 2025-07-04 | 23:20 | 2025-08-04 | 0:43 | MGE23 | MULGRAVE | Urban | Animal | Animal impact | 24.79 | 2051.7865 | 82.7667 | 1 | No
| 1887262 | 2025-08-04 | 4:07 | 2025-08-04 | 5:24 | SV34 | SPRINGVALE | Urban | Animal | Animal impact | 79.73 | 6133.892 | 76.9333 | 1 | No
| 1887346 | 2025-08-04 | 9:42 | 2025-08-04 | 11:15 | EW3 | ELWOOD | Urban | Asset Failure | LV | 1 | 92.8333 | 92.8333 | 1 | No
| 1887462 | 2025-08-04 | 11:10 | 2025-08-04 | 13:30 | HGS21 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 139.2333 | 139.2333 | 1 | No
| 1887422 | 2025-08-04 | 12:08 | 2025-08-04 | 15:45 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 217 | 217 | 1 | No
| 1887437 | 2025-08-04 | 12:11 | 2025-08-04 | 12:48 | RWT34 | RINGWOOD | Urban | Asset Failure | LV | 1 | 36.7833 | 36.7833 | 1 | No
| 1887452 | 2025-08-04 | 12:28 | 2025-08-04 | 13:33 | CM15 | CHELTENHAM | Urban | Asset Failure | LV | 1 | 64.5833 | 64.5833 | 1 | No
| 1887516 | 2025-08-04 | 15:08 | 2025-08-04 | 19:38 | STO21 | SORRENTO | Rural Short | Unknown | Unknown | 1 | 270.1333 | 270.1333 | 1 | No
| 1887603 | 2025-08-04 | 16:38 | 2025-09-04 | 0:00 | DMA23 | DROMANA | Rural Short | Asset Failure | HV | 4 | 1765.2 | 441.3 | 1 | No
| 1887540 | 2025-08-04 | 17:32 | 2025-08-04 | 19:31 | BR9 | BEAUMARIS | Urban | Asset Failure | LV | 55 | 6567 | 119.4 | 1 | No
| 1887558 | 2025-08-04 | 18:56 | 2025-08-04 | 21:20 | RBD21 | ROSEBUD | Rural Short | Unknown | Unknown | 88.44 | 12720.6171 | 143.8333 | 1 | No
| 1887604 | 2025-08-04 | 22:06 | 2025-09-04 | 1:50 | BR4 | BEAUMARIS | Urban | Third Party | Vehicle Impact | 9 | 2017.35 | 224.15 | 1 | No
| 1887614 | 2025-08-04 | 23:11 | 2025-09-04 | 2:00 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 5 | 848.4165 | 169.6833 | 1 | No
| 1887622 | 2025-09-04 | 5:02 | 2025-09-04 | 6:50 | LD4 | LYNDALE | Urban | Animal | Animal impact | 69.01 | 7420.873 | 107.5333 | 1 | No
| 1887625 | 2025-09-04 | 5:31 | 2025-09-04 | 9:16 | SVW53 | SPRINGVALE WEST | Urban | Third Party | Other | 34 | 7647.7322 | 224.9333 | 1 | No
| 1887625 | 2025-09-04 | 5:31 | 2025-09-04 | 10:05 | SVW53 | SPRINGVALE WEST | Urban | Third Party | Other | 1 | 273.3833 | 273.3833 | 2 | No
| 1887631 | 2025-09-04 | 6:32 | 2025-09-04 | 7:58 | DVY14 | DANDENONG VALLEY | Urban | Animal | Animal impact | 4.62 | 395.241 | 85.55 | 1 | No
| 1887677 | 2025-09-04 | 7:01 | 2025-09-04 | 16:19 | DN21 | DANDENONG | Urban | Third Party | Other | 2 | 1115.9334 | 557.9667 | 1 | No
| 1887698 | 2025-09-04 | 9:02 | 2025-09-04 | 11:04 | BT22 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 121.85 | 121.85 | 1 | No
| 1887695 | 2025-09-04 | 10:44 | 2025-09-04 | 12:11 | NB34 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 87.9167 | 87.9167 | 1 | No
| 1887793 | 2025-09-04 | 11:59 | 2025-09-04 | 13:27 | KBH34 | KEYSBOROUGH | Urban | Third Party | Other | 1 | 88.9667 | 88.9667 | 1 | No
| 1887806 | 2025-09-04 | 12:37 | 2025-09-04 | 14:17 | MR12 | MOORABBIN | Urban | Unknown | Unknown | 1 | 99.2333 | 99.2333 | 1 | No
| 1887852 | 2025-09-04 | 15:22 | 2025-09-04 | 17:25 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 122.5333 | 122.5333 | 1 | No
| 1887866 | 2025-09-04 | 16:29 | 2025-09-04 | 16:50 | CFD16 | CAULFIELD | Urban | Asset Failure | LV | 1 | 21.1667 | 21.1667 | 1 | No
| 1887882 | 2025-09-04 | 18:39 | 2025-09-04 | 20:07 | DN21 | DANDENONG | Urban | Third Party | Other | 2 | 175.2 | 87.6 | 1 | No
| 1887915 | 2025-10-04 | 2:49 | 2025-10-04 | 4:07 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 1 | 77.9333 | 77.9333 | 1 | No
| 1887922 | 2025-10-04 | 4:46 | 2025-10-04 | 7:04 | HGS31 | HASTINGS | Rural Short | Animal | Animal impact | 2.68 | 367.7852 | 137.2333 | 1 | No
| 1887965 | 2025-10-04 | 8:55 | 2025-10-04 | 10:26 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 30.36 | 2744.037 | 90.3833 | 1 | No
| 1888083 | 2025-10-04 | 10:56 | 2025-10-04 | 13:43 | LD4 | LYNDALE | Urban | Unknown | Unknown | 0.67 | 111.555 | 166.5 | 1 | No
| 1888068 | 2025-10-04 | 12:37 | 2025-10-04 | 13:40 | DN7 | DANDENONG | Urban | Network Business | Network Error | 1 | 62.2333 | 62.2333 | 1 | No
| 1888143 | 2025-10-04 | 17:01 | 2025-10-04 | 17:42 | CM25 | CHELTENHAM | Urban | Asset Failure | LV | 1 | 40.1 | 40.1 | 1 | No
| 1888150 | 2025-10-04 | 17:45 | 2025-10-04 | 21:22 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 216.75 | 216.75 | 1 | No
| 1888148 | 2025-10-04 | 18:34 | 2025-10-04 | 21:28 | MC21 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 174 | 174 | 1 | No
| 1888165 | 2025-10-04 | 18:36 | 2025-10-04 | 22:08 | OE14 | OAKLEIGH EAST | Urban | Third Party | Other | 1 | 212.0833 | 212.0833 | 1 | No
| 1888171 | 2025-10-04 | 19:14 | 2025-10-04 | 19:40 | DC2 | DONCASTER | Urban | Animal | Animal impact | 93.8 | 2418.4735 | 25.7833 | 1 | No
| 1888184 | 2025-10-04 | 20:28 | 2025-10-04 | 21:17 | LWN24 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 48.7167 | 48.7167 | 1 | No
| 1888200 | 2025-11-04 | 1:22 | 2025-11-04 | 2:46 | FTN11 | FRANKSTON | Urban | Unknown | Unknown | 74.37 | 6245.838 | 83.9833 | 1 | No
| 1888204 | 2025-11-04 | 6:00 | 2025-11-04 | 7:49 | CFD16 | CAULFIELD | Urban | Asset Failure | LV | 1 | 109.5833 | 109.5833 | 1 | No
| 1888337 | 2025-11-04 | 10:51 | 2025-11-04 | 11:15 | STO21 | SORRENTO | Rural Short | Unknown | Unknown | 1 | 23.1 | 23.1 | 1 | No
| 1888443 | 2025-11-04 | 13:46 | 2025-11-04 | 21:08 | CRM23 | CARRUM | Urban | Asset Failure | LV | 3.6 | 1588.9799 | 441.3833 | 1 | No
| 1888403 | 2025-11-04 | 14:22 | 2025-11-04 | 15:50 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 1 | 87.3 | 87.3 | 1 | No
| 1888404 | 2025-11-04 | 16:21 | 2025-11-04 | 18:45 | SVW53 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 144 | 144 | 1 | No
| 1888437 | 2025-11-04 | 17:13 | 2025-11-04 | 21:47 | HGS22 | HASTINGS | Rural Short | Third Party | Vehicle Impact | 1 | 274.2833 | 274.2833 | 1 | No
| 1888467 | 2025-11-04 | 19:15 | 2025-11-04 | 21:40 | BR9 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 144.1167 | 144.1167 | 1 | No
| 1888469 | 2025-11-04 | 20:03 | 2025-11-04 | 21:00 | SS14 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 35.31 | 1980.3013 | 56.0833 | 1 | No
| 1888471 | 2025-11-04 | 20:21 | 2025-11-04 | 22:15 | EM6 | EAST MALVERN | Urban | Asset Failure | LV | 19.8 | 2256.5407 | 113.9667 | 1 | No
| 1888473 | 2025-11-04 | 20:32 | 2025-11-04 | 22:50 | LWN21 | LANGWARRIN | Rural Short | Third Party | Other | 2 | 274.5 | 137.25 | 1 | No
| 1888476 | 2025-11-04 | 20:34 | 2025-11-04 | 22:50 | LWN21 | LANGWARRIN | Rural Short | Third Party | Other | 35 | 4726.1655 | 135.0333 | 1 | No
| 1888487 | 2025-11-04 | 22:55 | 2025-12-04 | 0:14 | RBD11 | ROSEBUD | Urban | Asset Failure | HV | 42.21 | 3349.3635 | 79.35 | 1 | No
| 1888487 | 2025-11-04 | 22:55 | 2025-12-04 | 0:21 | RBD11 | ROSEBUD | Urban | Asset Failure | HV | 25.46 | 2197.198 | 86.3 | 2 | No
| 1888503 | 2025-12-04 | 3:15 | 2025-12-04 | 8:29 | MGE32 | MULGRAVE | Urban | Asset Failure | LV | 1 | 314.2167 | 314.2167 | 1 | No
| 1888566 | 2025-12-04 | 11:43 | 2025-12-04 | 12:56 | LWN33 | LANGWARRIN | Urban | Asset Failure | LV | 2 | 145.9 | 72.95 | 1 | No
| 1888574 | 2025-12-04 | 14:31 | 2025-12-04 | 16:24 | FSH21 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 113.35 | 113.35 | 1 | No
| 1888596 | 2025-12-04 | 18:16 | 2025-12-04 | 19:25 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 68.5167 | 68.5167 | 1 | No
| 1888599 | 2025-12-04 | 18:34 | 2025-12-04 | 19:25 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 50.2333 | 50.2333 | 1 | No
| 1888602 | 2025-12-04 | 18:51 | 2025-12-04 | 19:25 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 33.3 | 33.3 | 1 | No
| 1888548 | 2025-12-04 | 20:12 | 2025-12-04 | 21:30 | K34 | GARDINER | Urban | Asset Failure | LV | 1 | 78 | 78 | 1 | No
| 1888647 | 13/04/2025 | 11:07 | 13/04/2025 | 12:48 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 101.2833 | 101.2833 | 1 | No
| 1888615 | 13/04/2025 | 11:12 | 13/04/2025 | 13:06 | DN25 | DANDENONG | Urban | Asset Failure | LV | 1 | 114 | 114 | 1 | No
| 1888660 | 13/04/2025 | 13:38 | 13/04/2025 | 14:44 | BU22 | BULLEEN | Urban | Asset Failure | LV | 1 | 65.35 | 65.35 | 1 | No
| 1888682 | 13/04/2025 | 17:33 | 13/04/2025 | 21:15 | BT21 | BENTLEIGH | Urban | Asset Failure | LV | 3 | 664.8 | 221.6 | 1 | No
| 1888691 | 13/04/2025 | 19:16 | 13/04/2025 | 21:32 | NW13 | NUNAWADING | Urban | Asset Failure | LV | 1 | 136.25 | 136.25 | 1 | No
| 1888692 | 13/04/2025 | 19:26 | 13/04/2025 | 20:45 | CDA11 | CLARINDA | Urban | Asset Failure | LV | 1 | 79 | 79 | 1 | No
| 1888693 | 13/04/2025 | 20:09 | 13/04/2025 | 21:45 | K24 | GARDINER | Urban | Asset Failure | LV | 1 | 96 | 96 | 1 | No
| 1888701 | 13/04/2025 | 23:08 | 14/04/2025 | 0:20 | RBD12 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 71.8333 | 71.8333 | 1 | No
| 1888712 | 13/04/2025 | 23:59 | 14/04/2025 | 11:45 | MGE23 | MULGRAVE | Urban | Asset Failure | LV | 2 | 1410.3666 | 705.1833 | 1 | No
| 1888705 | 14/04/2025 | 2:24 | 14/04/2025 | 3:43 | MGE23 | MULGRAVE | Urban | Unknown | Unknown | 13 | 1022.0171 | 78.6167 | 1 | No
| 1888717 | 14/04/2025 | 5:36 | 14/04/2025 | 7:38 | LWN33 | LANGWARRIN | Urban | Asset Failure | Distribution substation | 3.35 | 405.685 | 121.1 | 1 | No
| 1888718 | 14/04/2025 | 6:03 | 14/04/2025 | 7:55 | BU14 | BULLEEN | Urban | Asset Failure | LV | 49.5 | 5526.675 | 111.65 | 1 | No
| 1888728 | 14/04/2025 | 7:59 | 14/04/2025 | 10:01 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 121.9 | 121.9 | 1 | No
| 1888817 | 14/04/2025 | 10:29 | 14/04/2025 | 11:18 | SVW45 | SPRINGVALE WEST | Urban | Asset Failure | LV | 5 | 245.8335 | 49.1667 | 1 | No
| 1888863 | 14/04/2025 | 12:14 | 14/04/2025 | 15:00 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 165.3333 | 165.3333 | 1 | No
| 1888713 | 14/04/2025 | 13:05 | 14/04/2025 | 14:17 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 1 | 72.85 | 72.85 | 1 | No
| 1888928 | 14/04/2025 | 17:03 | 14/04/2025 | 18:08 | DC5 | DONCASTER | Urban | Asset Failure | LV | 1 | 64.0667 | 64.0667 | 1 | No
| 1888943 | 14/04/2025 | 20:51 | 14/04/2025 | 22:09 | MTN32 | MORNINGTON | Rural Short | Asset Failure | HV | 4 | 312.0668 | 78.0167 | 1 | No
| 1888945 | 14/04/2025 | 21:32 | 14/04/2025 | 22:16 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 43.9333 | 43.9333 | 1 | No
| 1888953 | 15/04/2025 | 6:06 | 15/04/2025 | 8:30 | DMA15 | DROMANA | Rural Short | Animal | Animal impact | 18 | 2592 | 144 | 1 | No
| 1889012 | 15/04/2025 | 8:29 | 15/04/2025 | 11:09 | MC31 | MORDIALLOC | Urban | Animal | Animal impact | 1 | 159.8667 | 159.8667 | 1 | No
| 1889026 | 15/04/2025 | 8:36 | 15/04/2025 | 8:48 | OAK23 | OAKLEIGH | Urban | Other | XXX | 1 | 11.0667 | 11.0667 | 1 | No
| 1889046 | 15/04/2025 | 9:02 | 15/04/2025 | 11:25 | NB34 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 142.8833 | 142.8833 | 1 | No
| 1889113 | 15/04/2025 | 10:19 | 15/04/2025 | 12:30 | MTN32 | MORNINGTON | Rural Short | Network Business | Switching and protection error | 1 | 130.2167 | 130.2167 | 1 | No
| 1889124 | 15/04/2025 | 10:37 | 15/04/2025 | 11:25 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 47.3833 | 47.3833 | 1 | No
| 1889187 | 15/04/2025 | 12:11 | 15/04/2025 | 18:13 | DN21 | DANDENONG | Urban | Third Party | Vehicle Impact | 1 | 361.95 | 361.95 | 1 | No
| 1889181 | 15/04/2025 | 12:13 | 15/04/2025 | 14:49 | LD2 | LYNDALE | Urban | Asset Failure | LV | 1 | 156.7 | 156.7 | 1 | No
| 1889199 | 15/04/2025 | 12:44 | 15/04/2025 | 14:37 | FTN22 | FRANKSTON | Urban | Asset Failure | LV | 1 | 112.2667 | 112.2667 | 1 | No
| 1889225 | 15/04/2025 | 13:57 | 15/04/2025 | 15:20 | SR31 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 83 | 83 | 1 | No
| 1889235 | 15/04/2025 | 14:17 | 15/04/2025 | 14:38 | CRM22 | CARRUM | Urban | Unknown | Unknown | 1 | 20.9167 | 20.9167 | 1 | No
| 1889250 | 15/04/2025 | 15:37 | 15/04/2025 | 18:29 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 1.98 | 341.5169 | 172.4833 | 1 | No
| 1889274 | 15/04/2025 | 16:34 | 15/04/2025 | 18:27 | HGS33 | HASTINGS | Rural Short | Unknown | Unknown | 1 | 112.7167 | 112.7167 | 1 | No
| 1889289 | 15/04/2025 | 17:37 | 15/04/2025 | 19:04 | DN25 | DANDENONG | Urban | Asset Failure | LV | 1 | 87 | 87 | 1 | No
| 1889121 | 15/04/2025 | 18:50 | 15/04/2025 | 21:00 | CDA23 | CLARINDA | Urban | Overloads |  | 1 | 130 | 130 | 1 | No
| 1889304 | 15/04/2025 | 19:08 | 15/04/2025 | 20:09 | NP34 | NOBLE PARK | Urban | Asset Failure | LV | 42 | 2573.2014 | 61.2667 | 1 | No
| 1889317 | 15/04/2025 | 20:33 | 15/04/2025 | 20:39 | MTN35 | MORNINGTON | Rural Short | Asset Failure | HV | 54 | 324 | 6 | 1 | No
| 1889123 | 15/04/2025 | 20:34 | 15/04/2025 | 22:10 | MR13 | MOORABBIN | Urban | Asset Failure | LV | 1 | 96 | 96 | 1 | No
| 1889320 | 15/04/2025 | 21:41 | 16/04/2025 | 0:30 | EW12 | ELWOOD | Urban | Asset Failure | LV | 1 | 168.1667 | 168.1667 | 1 | No
| 1889325 | 16/04/2025 | 0:56 | 16/04/2025 | 10:35 | DN6 | DANDENONG | Urban | Animal | Animal impact | 1 | 578.3833 | 578.3833 | 1 | No
| 1889333 | 16/04/2025 | 3:50 | 16/04/2025 | 5:53 | NP23 | NOBLE PARK | Urban | Animal | Animal impact | 34.17 | 4184.1165 | 122.45 | 1 | No
| 1889356 | 16/04/2025 | 7:21 | 16/04/2025 | 11:49 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 60 | 16063.998 | 267.7333 | 1 | No
| 1889393 | 16/04/2025 | 8:14 | 16/04/2025 | 9:40 | DN11 | DANDENONG | Urban | Asset Failure | LV | 38.94 | 3333.264 | 85.6 | 1 | No
| 1889331 | 16/04/2025 | 9:23 | 16/04/2025 | 10:49 | NB33 | NORTH BRIGHTON | Urban | Third Party | Other | 1 | 86 | 86 | 1 | No
| 1889453 | 16/04/2025 | 9:38 | 16/04/2025 | 10:05 | RWT35 | RINGWOOD | Urban | Asset Failure | LV | 10.56 | 285.12 | 27 | 1 | No
| 1889524 | 16/04/2025 | 12:07 | 16/04/2025 | 14:25 | NP25 | NOBLE PARK | Urban | Third Party | Other | 1 | 138.2333 | 138.2333 | 1 | No
| 1889528 | 16/04/2025 | 12:13 | 16/04/2025 | 15:04 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 171.2333 | 171.2333 | 1 | No
| 1889531 | 16/04/2025 | 12:19 | 16/04/2025 | 12:51 | STO22 | SORRENTO | Urban | Third Party | Other | 4 | 128 | 32 | 1 | No
| 1889628 | 16/04/2025 | 19:44 | 16/04/2025 | 21:05 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 1 | 81 | 81 | 1 | No
| 1889632 | 16/04/2025 | 23:50 | 17/04/2025 | 0:35 | NB24 | NORTH BRIGHTON | Urban | Third Party | Other | 1 | 45 | 45 | 1 | No
| 1889789 | 17/04/2025 | 13:10 | 17/04/2025 | 15:26 | LD1 | LYNDALE | Urban | Asset Failure | LV | 1 | 136 | 136 | 1 | No
| 1889946 | 17/04/2025 | 19:17 | 17/04/2025 | 21:05 | RBD14 | ROSEBUD | Urban | Asset Failure | LV | 51 | 5499.4983 | 107.8333 | 1 | No
| 1889947 | 17/04/2025 | 19:20 | 17/04/2025 | 20:57 | RBD14 | ROSEBUD | Urban | Asset Failure | LV | 97 | 9404.15 | 96.95 | 1 | No
| 1889949 | 17/04/2025 | 19:27 | 17/04/2025 | 20:19 | NB24 | NORTH BRIGHTON | Urban | Third Party | Other | 1 | 52.2667 | 52.2667 | 1 | No
| 1889975 | 18/04/2025 | 0:13 | 18/04/2025 | 1:35 | STO21 | SORRENTO | Rural Short | Weather |  | 3 | 246 | 82 | 1 | No
| 1889976 | 18/04/2025 | 0:13 | 18/04/2025 | 2:08 | STO21 | SORRENTO | Rural Short | Weather |  | 1 | 115 | 115 | 1 | No
| 1889977 | 18/04/2025 | 1:32 | 18/04/2025 | 2:30 | MC32 | MORDIALLOC | Urban | Animal | Animal impact | 16.75 | 975.9672 | 58.2667 | 1 | No
| 1889984 | 18/04/2025 | 7:14 | 18/04/2025 | 9:05 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 110.35 | 110.35 | 1 | No
| 1890048 | 18/04/2025 | 8:54 | 18/04/2025 | 9:07 | MTN35 | MORNINGTON | Rural Short | Other | XXX | 1 | 12.9 | 12.9 | 1 | No
| 1890052 | 18/04/2025 | 9:33 | 18/04/2025 | 12:13 | STO13 | SORRENTO | Urban | Asset Failure | LV | 15.84 | 2526.7445 | 159.5167 | 1 | No
| 1889979 | 18/04/2025 | 10:13 | 18/04/2025 | 12:24 | DC12 | DONCASTER | Urban | Asset Failure | LV | 1 | 131.1667 | 131.1667 | 1 | No
| 1890071 | 18/04/2025 | 11:20 | 18/04/2025 | 14:47 | RBD21 | ROSEBUD | Rural Short | Third Party | Vehicle Impact | 165 | 34163.25 | 207.05 | 1 | No
| 1890071 | 18/04/2025 | 11:20 | 18/04/2025 | 14:47 | RBD21 | ROSEBUD | Rural Short | Third Party | Vehicle Impact | 2 | 414.1666 | 207.0833 | 2 | No
| 1890071 | 18/04/2025 | 11:20 | 18/04/2025 | 14:10 | RBD21 | ROSEBUD | Rural Short | Third Party | Vehicle Impact | 121 | 20642.6 | 170.6 | 1 | No
| 1890071 | 18/04/2025 | 11:20 | 18/04/2025 | 17:28 | RBD21 | ROSEBUD | Rural Short | Third Party | Vehicle Impact | 25 | 9196.6675 | 367.8667 | 2 | No
| 1890082 | 18/04/2025 | 12:08 | 18/04/2025 | 13:57 | EW1 | ELWOOD | Urban | Asset Failure | LV | 3.96 | 430.3201 | 108.6667 | 1 | No
| 1890086 | 18/04/2025 | 12:38 | 18/04/2025 | 14:56 | EM2 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 137.6167 | 137.6167 | 1 | No
| 1890097 | 18/04/2025 | 14:07 | 18/04/2025 | 15:52 | EM9 | EAST MALVERN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 104.7 | 104.7 | 1 | No
| 1890107 | 18/04/2025 | 16:20 | 18/04/2025 | 18:55 | MR33 | MOORABBIN | Urban | Asset Failure | LV | 1 | 155 | 155 | 1 | No
| 1890122 | 18/04/2025 | 18:47 | 18/04/2025 | 21:30 | STO14 | SORRENTO | Rural Short | Third Party | Other | 1 | 162.8833 | 162.8833 | 1 | No
| 1890129 | 18/04/2025 | 21:09 | 18/04/2025 | 21:45 | MGE23 | MULGRAVE | Urban | Unknown | Unknown | 41.54 | 1494.7463 | 35.9833 | 1 | No
| 1890149 | 19/04/2025 | 9:47 | 19/04/2025 | 11:42 | FSH32 | FRANKSTON SOUTH | Rural Short | Animal | Other | 2 | 229.5666 | 114.7833 | 1 | No
| 1890136 | 19/04/2025 | 13:11 | 19/04/2025 | 14:40 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 89 | 89 | 1 | No
| 1890193 | 19/04/2025 | 19:57 | 19/04/2025 | 23:05 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 187.6833 | 187.6833 | 1 | No
| 1890134 | 19/04/2025 | 21:24 | 19/04/2025 | 22:16 | OAK33 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 52.0167 | 52.0167 | 1 | No
| 1890194 | 20/04/2025 | 7:29 | 20/04/2025 | 9:00 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 91 | 91 | 1 | No
| 1890203 | 20/04/2025 | 9:39 | 20/04/2025 | 11:45 | HGS23 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 126 | 126 | 1 | No
| 1890207 | 20/04/2025 | 10:58 | 20/04/2025 | 12:15 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 1 | 77 | 77 | 1 | No
| 1890214 | 20/04/2025 | 11:10 | 20/04/2025 | 12:17 | EL24 | ELSTERNWICK | Urban | Asset Failure | LV | 5 | 335 | 67 | 1 | No
| 1890224 | 20/04/2025 | 15:46 | 20/04/2025 | 18:38 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 172.4167 | 172.4167 | 1 | No
| 1890228 | 20/04/2025 | 19:18 | 20/04/2025 | 21:03 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 105.9667 | 105.9667 | 1 | No
| 1890231 | 20/04/2025 | 20:36 | 20/04/2025 | 22:00 | RBD13 | ROSEBUD | Urban | Animal | Animal impact | 148.5 | 12347.775 | 83.15 | 1 | No
| 1890240 | 20/04/2025 | 21:30 | 20/04/2025 | 23:19 | CDA11 | CLARINDA | Urban | Asset Failure | LV | 1 | 109.3167 | 109.3167 | 1 | No
| 1890242 | 20/04/2025 | 22:36 | 21/04/2025 | 11:25 | DN24 | DANDENONG | Urban | Third Party | Other | 27 | 20751.3009 | 768.5667 | 1 | No
| 1890264 | 21/04/2025 | 8:02 | 21/04/2025 | 13:24 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 321.3333 | 321.3333 | 1 | No
| 1890271 | 21/04/2025 | 10:48 | 21/04/2025 | 12:40 | NB35 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 112 | 112 | 1 | No
| 1890270 | 21/04/2025 | 10:53 | 21/04/2025 | 13:50 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 177.75 | 177.75 | 1 | No
| 1890275 | 21/04/2025 | 11:28 | 21/04/2025 | 14:20 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 17.16 | 2951.2334 | 171.9833 | 1 | No
| 1890286 | 21/04/2025 | 12:54 | 21/04/2025 | 15:22 | OAK26 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 147.0667 | 147.0667 | 1 | No
| 1890309 | 21/04/2025 | 19:31 | 21/04/2025 | 21:04 | LWN21 | LANGWARRIN | Rural Short | Animal | Other | 20.1 | 1864.275 | 92.75 | 1 | No
| 1890312 | 21/04/2025 | 19:45 | 21/04/2025 | 20:48 | NP23 | NOBLE PARK | Urban | Animal | Animal impact | 20.77 | 1307.8184 | 62.9667 | 1 | No
| 1890322 | 22/04/2025 | 0:41 | 22/04/2025 | 1:57 | CRM15 | CARRUM | Urban | Asset Failure | LV | 1 | 75.1833 | 75.1833 | 1 | No
| 1890335 | 22/04/2025 | 1:31 | 22/04/2025 | 3:17 | DN4 | DANDENONG | Urban | Third Party | Other | 1 | 105.3167 | 105.3167 | 1 | No
| 1890332 | 22/04/2025 | 2:30 | 22/04/2025 | 11:22 | WD14 | WEST DONCASTER | Urban | Asset Failure | LV | 44 | 23394.8 | 531.7 | 1 | No
| 1890337 | 22/04/2025 | 3:35 | 22/04/2025 | 5:05 | SV21 | SPRINGVALE | Urban | Asset Failure | HV | 15 | 1348.5 | 89.9 | 1 | No
| 1890337 | 22/04/2025 | 3:35 | 22/04/2025 | 5:28 | SV21 | SPRINGVALE | Urban | Asset Failure | HV | 58 | 6594.6 | 113.7 | 2 | No
| 1890339 | 22/04/2025 | 3:58 | 22/04/2025 | 7:41 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 22.44 | 5005.242 | 223.05 | 1 | No
| 1890345 | 22/04/2025 | 6:08 | 22/04/2025 | 11:10 | SV34 | SPRINGVALE | Urban | Asset Failure | LV | 46 | 13865.9318 | 301.4333 | 1 | No
| 1890518 | 22/04/2025 | 15:38 | 22/04/2025 | 21:35 | DN4 | DANDENONG | Urban | Third Party | Other | 1 | 356.6167 | 356.6167 | 1 | No
| 1890530 | 22/04/2025 | 16:49 | 22/04/2025 | 18:40 | KBH31 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 110.75 | 110.75 | 1 | No
| 1890603 | 23/04/2025 | 6:21 | 23/04/2025 | 7:50 | DC4 | DONCASTER | Urban | Asset Failure | HV | 23.45 | 2085.4859 | 88.9333 | 1 | No
| 1890603 | 23/04/2025 | 6:21 | 23/04/2025 | 7:51 | DC4 | DONCASTER | Urban | Asset Failure | HV | 26.8 | 2406.1924 | 89.7833 | 2 | No
| 1890612 | 23/04/2025 | 7:15 | 23/04/2025 | 8:25 | DN24 | DANDENONG | Urban | Third Party | Other | 1 | 70.2 | 70.2 | 1 | No
| 1890639 | 23/04/2025 | 8:22 | 23/04/2025 | 11:55 | EB12 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 212.4333 | 212.4333 | 1 | No
| 1890686 | 23/04/2025 | 9:04 | 23/04/2025 | 13:04 | MR21 | MOORABBIN | Urban | Asset Failure | HV | 34 | 8147.5322 | 239.6333 | 1 | No
| 1890804 | 23/04/2025 | 13:15 | 23/04/2025 | 17:39 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 264.35 | 264.35 | 1 | No
| 1890820 | 23/04/2025 | 13:50 | 23/04/2025 | 14:09 | MTN21 | MORNINGTON | Urban | Other | XXX | 1 | 18.7333 | 18.7333 | 1 | No
| 1890873 | 23/04/2025 | 17:50 | 23/04/2025 | 23:47 | HGS21 | HASTINGS | Rural Short | Third Party | Vehicle Impact | 33 | 11755.1511 | 356.2167 | 1 | No
| 1890874 | 23/04/2025 | 17:51 | 23/04/2025 | 23:47 | HGS21 | HASTINGS | Rural Short | Third Party | Vehicle Impact | 36 | 12811.2012 | 355.8667 | 1 | No
| 1890893 | 23/04/2025 | 19:38 | 23/04/2025 | 22:15 | CRM14 | CARRUM | Rural Short | Asset Failure | LV | 1 | 157.4167 | 157.4167 | 1 | No
| 1890907 | 24/04/2025 | 6:47 | 24/04/2025 | 8:45 | MR21 | MOORABBIN | Urban | Third Party | Other | 1 | 118.0333 | 118.0333 | 1 | No
| 1890923 | 24/04/2025 | 7:06 | 24/04/2025 | 9:15 | BT25 | BENTLEIGH | Urban | Asset Failure | Distribution substation | 14.07 | 1807.0565 | 128.4333 | 1 | No
| 1890903 | 24/04/2025 | 7:41 | 24/04/2025 | 9:54 | MR22 | MOORABBIN | Urban | Asset Failure | LV | 1 | 133.5667 | 133.5667 | 1 | No
| 1890993 | 24/04/2025 | 9:21 | 24/04/2025 | 10:03 | LD6 | LYNDALE | Urban | Asset Failure | LV | 3 | 127.1001 | 42.3667 | 1 | No
| 1891043 | 24/04/2025 | 11:19 | 24/04/2025 | 12:46 | DMA13 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 86.85 | 86.85 | 1 | No
| 1891076 | 24/04/2025 | 12:30 | 24/04/2025 | 14:10 | NW22 | NUNAWADING | Urban | Animal | Animal impact | 1 | 99.7833 | 99.7833 | 1 | No
| 1891143 | 24/04/2025 | 17:13 | 24/04/2025 | 18:44 | FTN23 | FRANKSTON | Urban | Asset Failure | LV | 25.41 | 2325.015 | 91.5 | 1 | No
| 1891171 | 24/04/2025 | 22:39 | 25/04/2025 | 2:24 | M34 | MENTONE | Urban | Asset Failure | LV | 1 | 224.8667 | 224.8667 | 1 | No
| 1891174 | 25/04/2025 | 0:35 | 25/04/2025 | 1:23 | K23 | GARDINER | Urban | Animal | Animal impact | 671 | 32409.3 | 48.3 | 1 | No
| 1891174 | 25/04/2025 | 0:35 | 25/04/2025 | 1:44 | K23 | GARDINER | Urban | Animal | Animal impact | 73 | 5067.4191 | 69.4167 | 2 | No
| 1891188 | 25/04/2025 | 4:41 | 25/04/2025 | 6:50 | MTN34 | MORNINGTON | Urban | Unknown | Unknown | 20 | 2576.334 | 128.8167 | 1 | No
| 1891192 | 25/04/2025 | 5:35 | 25/04/2025 | 9:03 | SVW53 | SPRINGVALE WEST | Urban | Third Party | Other | 2.55 | 531.2499 | 208.3333 | 1 | No
| 1891172 | 25/04/2025 | 8:37 | 25/04/2025 | 10:20 | SR23 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 103 | 103 | 1 | No
| 1891193 | 25/04/2025 | 12:29 | 25/04/2025 | 13:13 | DN11 | DANDENONG | Urban | Asset Failure | LV | 1 | 44.3333 | 44.3333 | 1 | No
| 1891256 | 25/04/2025 | 18:57 | 25/04/2025 | 20:32 | NP33 | NOBLE PARK | Urban | Animal | Animal impact | 55.61 | 5254.2163 | 94.4833 | 1 | No
| 1891262 | 25/04/2025 | 20:25 | 25/04/2025 | 21:04 | EB11 | EAST BURWOOD | Urban | Asset Failure | LV | 25.74 | 1012.4391 | 39.3333 | 1 | No
| 1891281 | 26/04/2025 | 1:46 | 26/04/2025 | 9:20 | EL34 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 453.1833 | 453.1833 | 1 | No
| 1891296 | 26/04/2025 | 3:30 | 26/04/2025 | 5:34 | LWN23 | LANGWARRIN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 124.35 | 124.35 | 1 | No
| 1891307 | 26/04/2025 | 4:38 | 26/04/2025 | 6:31 | NP25 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 113.0333 | 113.0333 | 1 | No
| 1891337 | 26/04/2025 | 8:58 | 26/04/2025 | 10:45 | MR24 | MOORABBIN | Urban | Asset Failure | LV | 1 | 106.55 | 106.55 | 1 | No
| 1891345 | 26/04/2025 | 9:46 | 26/04/2025 | 13:40 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 233.05 | 233.05 | 1 | No
| 1891426 | 27/04/2025 | 8:11 | 27/04/2025 | 9:50 | M11 | MENTONE | Urban | Asset Failure | HV | 170 | 16773.339 | 98.6667 | 1 | No
| 1891458 | 27/04/2025 | 11:05 | 27/04/2025 | 15:27 | GW6 | GLEN WAVERLEY | Urban | Asset Failure | LV | 4 | 1047.0668 | 261.7667 | 1 | No
| 1891466 | 27/04/2025 | 13:01 | 27/04/2025 | 14:40 | CRM35 | CARRUM | Urban | Asset Failure | LV | 1 | 98.1833 | 98.1833 | 1 | No
| 1891488 | 27/04/2025 | 15:45 | 27/04/2025 | 16:15 | HGS31 | HASTINGS | Rural Short | Third Party | Other | 1 | 30 | 30 | 1 | No
| 1891496 | 27/04/2025 | 17:13 | 27/04/2025 | 18:27 | BU11 | BULLEEN | Urban | Asset Failure | LV | 1 | 73.2 | 73.2 | 1 | No
| 1891423 | 27/04/2025 | 18:48 | 27/04/2025 | 20:30 | SS11 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 102 | 102 | 1 | No
| 1891504 | 27/04/2025 | 20:06 | 27/04/2025 | 21:22 | EM2 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 76.75 | 76.75 | 1 | No
| 1891515 | 27/04/2025 | 21:23 | 27/04/2025 | 22:50 | CRM23 | CARRUM | Urban | Asset Failure | LV | 34 | 2947.8 | 86.7 | 1 | No
| 1891609 | 28/04/2025 | 10:02 | 28/04/2025 | 10:46 | BW21 | BURWOOD | Urban | Asset Failure | LV | 1 | 44.0667 | 44.0667 | 1 | No
| 1891625 | 28/04/2025 | 10:41 | 28/04/2025 | 12:15 | SV32 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 93.5833 | 93.5833 | 1 | No
| 1891631 | 28/04/2025 | 11:06 | 28/04/2025 | 13:24 | RWT35 | RINGWOOD | Urban | Animal | Animal impact | 4 | 553.1332 | 138.2833 | 1 | No
| 1891670 | 28/04/2025 | 12:07 | 28/04/2025 | 13:41 | MR31 | MOORABBIN | Urban | Asset Failure | LV | 1 | 93.7 | 93.7 | 1 | No
| 1891673 | 28/04/2025 | 12:16 | 28/04/2025 | 12:35 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 19.1333 | 19.1333 | 1 | No
| 1891787 | 28/04/2025 | 20:23 | 28/04/2025 | 21:30 | SS11 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 66.3 | 66.3 | 1 | No
| 1891791 | 28/04/2025 | 20:43 | 28/04/2025 | 21:59 | MGE31 | MULGRAVE | Urban | Unknown | Unknown | 12 | 912.2004 | 76.0167 | 1 | No
| 1891794 | 28/04/2025 | 20:46 | 28/04/2025 | 22:29 | SVW53 | SPRINGVALE WEST | Urban | Third Party | Vehicle Impact | 38 | 3919.0654 | 103.1333 | 1 | No
| 1891811 | 28/04/2025 | 23:22 | 29/04/2025 | 2:25 | MR12 | MOORABBIN | Urban | Asset Failure | LV | 1 | 182.6 | 182.6 | 1 | No
| 1891823 | 29/04/2025 | 0:08 | 29/04/2025 | 0:48 | WD15 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 40.25 | 40.25 | 1 | No
| 1891826 | 29/04/2025 | 0:13 | 29/04/2025 | 1:16 | CRM23 | CARRUM | Urban | Asset Failure | HV | 549 | 34715.0817 | 63.2333 | 1 | No
| 1891826 | 29/04/2025 | 0:13 | 29/04/2025 | 1:40 | CRM23 | CARRUM | Urban | Asset Failure | HV | 387 | 33694.8129 | 87.0667 | 2 | No
| 1891826 | 29/04/2025 | 0:13 | 29/04/2025 | 1:45 | CRM23 | CARRUM | Urban | Asset Failure | HV | 655 | 60041.6885 | 91.6667 | 3 | No
| 1891826 | 29/04/2025 | 0:13 | 29/04/2025 | 3:49 | CRM23 | CARRUM | Urban | Asset Failure | HV | 427 | 92039.85 | 215.55 | 4 | No
| 1891835 | 29/04/2025 | 1:36 | 29/04/2025 | 3:15 | DMA15 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 47 | 4629.5 | 98.5 | 1 | No
| 1891860 | 29/04/2025 | 2:22 | 29/04/2025 | 3:15 | DC2 | DONCASTER | Urban | Animal | Animal impact | 50.92 | 2679.2424 | 52.6167 | 1 | No
| 1891873 | 29/04/2025 | 3:10 | 29/04/2025 | 5:25 | HGS21 | HASTINGS | Rural Short | Weather |  | 230 | 30950.341 | 134.5667 | 1 | No
| 1891873 | 29/04/2025 | 3:10 | 29/04/2025 | 5:20 | HGS21 | HASTINGS | Rural Short | Weather |  | 274 | 35441.9 | 129.35 | 1 | No
| 1891909 | 29/04/2025 | 5:46 | 29/04/2025 | 6:12 | HGS21 | HASTINGS | Rural Short | Animal | Animal impact | 123 | 3218.5041 | 26.1667 | 1 | No
| 1891909 | 29/04/2025 | 5:46 | 29/04/2025 | 6:22 | HGS21 | HASTINGS | Rural Short | Animal | Animal impact | 107 | 3878.75 | 36.25 | 2 | No
| 1891868 | 29/04/2025 | 6:45 | 29/04/2025 | 8:09 | SV32 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 84.9333 | 84.9333 | 1 | No
| 1891916 | 29/04/2025 | 6:45 | 29/04/2025 | 8:10 | DN8 | DANDENONG | Urban | Asset Failure | LV | 1 | 85.05 | 85.05 | 1 | No
| 1891948 | 29/04/2025 | 8:39 | 29/04/2025 | 9:00 | DMA15 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 126 | 21 | 1 | No
| 1892103 | 29/04/2025 | 12:07 | 29/04/2025 | 18:19 | CRM23 | CARRUM | Urban | Asset Failure | HV | 58 | 21548.9314 | 371.5333 | 1 | No
| 1892139 | 29/04/2025 | 12:16 | 29/04/2025 | 13:38 | MC32 | MORDIALLOC | Urban | Asset Failure | HV | 2 | 163.2334 | 81.6167 | 1 | No
| 1892136 | 29/04/2025 | 13:07 | 29/04/2025 | 15:15 | CDA24 | CLARINDA | Urban | Asset Failure | LV | 1 | 127.9333 | 127.9333 | 1 | No
| 1892171 | 29/04/2025 | 14:20 | 29/04/2025 | 15:48 | MGE21 | MULGRAVE | Urban | Asset Failure | LV | 1 | 87.2667 | 87.2667 | 1 | No
| 1891917 | 29/04/2025 | 15:54 | 29/04/2025 | 17:31 | SR31 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 97.3333 | 97.3333 | 1 | No
| 1892194 | 29/04/2025 | 16:24 | 29/04/2025 | 22:10 | BH11 | BOX HILL | Urban | Asset Failure | LV | 1 | 345.8667 | 345.8667 | 1 | No
| 1892076 | 29/04/2025 | 17:19 | 29/04/2025 | 20:00 | CFD26 | CAULFIELD | Urban | Third Party | Other | 1 | 161 | 161 | 1 | No
| 1892220 | 29/04/2025 | 19:05 | 29/04/2025 | 20:25 | LWN34 | LANGWARRIN | Urban | Asset Failure | Distribution substation | 88.44 | 7001.5029 | 79.1667 | 1 | No
| 1892222 | 29/04/2025 | 19:19 | 29/04/2025 | 20:24 | EB11 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 65.45 | 65.45 | 1 | No
| 1892244 | 29/04/2025 | 23:02 | 29/04/2025 | 23:45 | SR26 | SANDRINGHAM | Urban | Animal | Animal impact | 39 | 1640.6013 | 42.0667 | 1 | No
| 1892243 | 29/04/2025 | 23:03 | 30/04/2025 | 1:27 | SVW56 | SPRINGVALE WEST | Urban | Unknown | Unknown | 1 | 144.25 | 144.25 | 1 | No
| 1892245 | 29/04/2025 | 23:04 | 30/04/2025 | 1:24 | STO13 | SORRENTO | Urban | Asset Failure | LV | 41 | 5714.7153 | 139.3833 | 1 | No
| 1892241 | 30/04/2025 | 7:27 | 30/04/2025 | 10:01 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 154.9833 | 154.9833 | 1 | No
| 1892309 | 30/04/2025 | 8:16 | 30/04/2025 | 10:20 | DC8 | DONCASTER | Urban | Asset Failure | HV | 9 | 1119.4497 | 124.3833 | 1 | No
| 1892253 | 30/04/2025 | 8:21 | 30/04/2025 | 10:00 | DC2 | DONCASTER | Urban | Asset Failure | LV | 1 | 99 | 99 | 1 | No
| 1892400 | 30/04/2025 | 10:08 | 30/04/2025 | 10:17 | DC8 | DONCASTER | Urban | Asset Failure | HV | 20 | 174 | 8.7 | 1 | No
| 1891830 | 30/04/2025 | 10:51 | 30/04/2025 | 13:30 | CFD13 | CAULFIELD | Urban | Asset Failure | LV | 1 | 159 | 159 | 1 | No
| 1892452 | 30/04/2025 | 11:37 | 30/04/2025 | 14:37 | EW9 | ELWOOD | Urban | Asset Failure | LV | 8 | 1439.2 | 179.9 | 1 | No
| 1892457 | 30/04/2025 | 11:45 | 30/04/2025 | 13:23 | FTN21 | FRANKSTON | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 98.1 | 98.1 | 1 | No
| 1892546 | 30/04/2025 | 15:23 | 30/04/2025 | 17:52 | EB31 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 148.3167 | 148.3167 | 1 | No
| 1892565 | 30/04/2025 | 17:02 | 30/04/2025 | 21:40 | CRM14 | CARRUM | Rural Short | Asset Failure | LV | 7 | 1946 | 278 | 1 | No
| 1892567 | 30/04/2025 | 17:30 | 30/04/2025 | 19:08 | BH31 | BOX HILL | Urban | Asset Failure | LV | 1 | 97.25 | 97.25 | 1 | No
| 1892576 | 30/04/2025 | 18:40 | 30/04/2025 | 18:45 | DC8 | DONCASTER | Urban | Asset Failure | HV | 7 | 35 | 5 | 1 | No
| 1892582 | 30/04/2025 | 20:09 | 30/04/2025 | 21:21 | EM7 | EAST MALVERN | Urban | Asset Failure | LV | 11.55 | 821.9754 | 71.1667 | 1 | No
| 1892600 | 30/04/2025 | 23:11 | 2025-01-05 | 0:20 | CDA21 | CLARINDA | Urban | Animal | Animal impact | 1 | 68.2 | 68.2 | 1 | No
| 1892624 | 2025-01-05 | 5:58 | 2025-01-05 | 7:07 | CRM13 | CARRUM | Urban | Animal | Animal impact | 33.5 | 2308.7094 | 68.9167 | 1 | No
| 1892655 | 2025-01-05 | 8:48 | 2025-01-05 | 11:39 | DN13 | DANDENONG | Urban | Asset Failure | LV | 1 | 171.55 | 171.55 | 1 | No
| 1892671 | 2025-01-05 | 10:02 | 2025-01-05 | 12:15 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 133 | 133 | 1 | No
| 1892784 | 2025-01-05 | 11:30 | 2025-01-05 | 13:31 | M34 | MENTONE | Urban | Asset Failure | LV | 1 | 120.4833 | 120.4833 | 1 | No
| 1892799 | 2025-01-05 | 12:01 | 2025-01-05 | 13:35 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 0.66 | 62.04 | 94 | 1 | No
| 1892625 | 2025-01-05 | 12:35 | 2025-01-05 | 14:56 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 141.9167 | 141.9167 | 1 | No
| 1892864 | 2025-01-05 | 14:07 | 2025-01-05 | 20:32 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 24 | 9259.9992 | 385.8333 | 1 | No
| 1892866 | 2025-01-05 | 14:09 | 2025-01-05 | 16:25 | MGE33 | MULGRAVE | Urban | Asset Failure | LV | 1 | 135.7833 | 135.7833 | 1 | No
| 1892867 | 2025-01-05 | 14:12 | 2025-01-05 | 20:21 | RBD21 | ROSEBUD | Rural Short | Asset Failure | HV | 35 | 12904.5 | 368.7 | 1 | No
| 1892894 | 2025-01-05 | 15:41 | 2025-01-05 | 16:20 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 38.2667 | 38.2667 | 1 | No
| 1892925 | 2025-01-05 | 19:39 | 2025-01-05 | 22:04 | GW3 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 145.05 | 145.05 | 1 | No
| 1892937 | 2025-01-05 | 23:01 | 2025-02-05 | 1:11 | RBD12 | ROSEBUD | Rural Short | Animal | Other | 74.37 | 9670.5765 | 130.0333 | 1 | No
| 1893009 | 2025-02-05 | 6:49 | 2025-02-05 | 7:20 | HGS33 | HASTINGS | Rural Short | Animal | Other | 2.01 | 60.5679 | 30.1333 | 1 | No
| 1893125 | 2025-02-05 | 11:02 | 2025-03-05 | 15:05 | NP14 | NOBLE PARK | Urban | Asset Failure | LV | 12 | 20194.2 | 1682.85 | 1 | No
| 1893145 | 2025-02-05 | 11:57 | 2025-02-05 | 15:56 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 238.2333 | 238.2333 | 1 | No
| 1893096 | 2025-02-05 | 12:53 | 2025-02-05 | 16:13 | LD3 | LYNDALE | Urban | Overloads |  | 1 | 200.5167 | 200.5167 | 1 | No
| 1893189 | 2025-02-05 | 14:04 | 2025-02-05 | 16:10 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 126.5667 | 126.5667 | 1 | No
| 1893125 | 2025-02-05 | 17:10 | 2025-02-05 | 22:44 | NP14 | NOBLE PARK | Urban | Asset Failure | LV | 8 | 2679.8664 | 334.9833 | 1 | No
| 1893253 | 2025-02-05 | 20:04 | 2025-02-05 | 21:45 | BR10 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 100.3 | 100.3 | 1 | No
| 1893269 | 2025-03-05 | 8:30 | 2025-03-05 | 12:00 | DC8 | DONCASTER | Urban | Asset Failure | LV | 1 | 210.7 | 210.7 | 1 | No
| 1893302 | 2025-03-05 | 9:51 | 2025-03-05 | 11:00 | KBH31 | KEYSBOROUGH | Urban | Asset Failure | LV | 17 | 1170.45 | 68.85 | 1 | No
| 1893298 | 2025-03-05 | 9:51 | 2025-03-05 | 14:31 | HT3 | HEATHERTON | Urban | Unknown | Unknown | 2 | 558.1 | 279.05 | 1 | No
| 1893319 | 2025-03-05 | 12:06 | 2025-03-05 | 14:19 | DMA15 | DROMANA | Rural Short | Overloads |  | 1 | 132.2667 | 132.2667 | 1 | No
| 1893299 | 2025-03-05 | 16:14 | 2025-03-05 | 18:44 | CRM33 | CARRUM | Urban | Asset Failure | LV | 1 | 150.2333 | 150.2333 | 1 | No
| 1893358 | 2025-03-05 | 19:35 | 2025-03-05 | 21:15 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 99.8833 | 99.8833 | 1 | No
| 1893365 | 2025-03-05 | 22:11 | 2025-03-05 | 23:37 | RBD12 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 86.95 | 86.95 | 1 | No
| 1893371 | 2025-04-05 | 0:16 | 2025-04-05 | 2:23 | STO14 | SORRENTO | Rural Short | Animal | Animal impact | 5 | 632.4165 | 126.4833 | 1 | No
| 1893373 | 2025-04-05 | 2:00 | 2025-04-05 | 4:40 | CDA21 | CLARINDA | Urban | Animal | Animal impact | 71.69 | 11423.8015 | 159.35 | 1 | No
| 1893378 | 2025-04-05 | 6:45 | 2025-04-05 | 9:14 | BT22 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 149 | 149 | 1 | No
| 1893443 | 2025-04-05 | 20:21 | 2025-04-05 | 22:04 | BW35 | BURWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 35 | 3593.9155 | 102.6833 | 1 | No
| 1893457 | 2025-05-05 | 3:00 | 2025-05-05 | 4:23 | RBD24 | ROSEBUD | Urban | Animal | Animal impact | 71 | 5878.8 | 82.8 | 1 | No
| 1893487 | 2025-05-05 | 8:28 | 2025-05-05 | 12:05 | HT13 | HEATHERTON | Urban | Asset Failure | LV | 3 | 649.4001 | 216.4667 | 1 | No
| 1893511 | 2025-05-05 | 9:10 | 2025-05-05 | 12:40 | DMA23 | DROMANA | Rural Short | Asset Failure | LV | 1 | 209.4667 | 209.4667 | 1 | No
| 1893552 | 2025-05-05 | 10:07 | 2025-05-05 | 12:07 | BR10 | BEAUMARIS | Urban | Asset Failure | LV | 0.78 | 93.561 | 119.95 | 1 | No
| 1893601 | 2025-05-05 | 11:26 | 2025-05-05 | 11:32 | MGE13 | MULGRAVE | Urban | Network Business | Switching and protection error | 1 | 5.6833 | 5.6833 | 1 | No
| 1893616 | 2025-05-05 | 12:05 | 2025-05-05 | 13:00 | CFD13 | CAULFIELD | Urban | Asset Failure | LV | 19.14 | 1052.7 | 55 | 1 | No
| 1893662 | 2025-05-05 | 13:39 | 2025-05-05 | 14:47 | NW14 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 13 | 891.5829 | 68.5833 | 1 | No
| 1893662 | 2025-05-05 | 13:39 | 2025-05-05 | 14:48 | NW14 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 855 | 58909.5 | 68.9 | 2 | No
| 1893662 | 2025-05-05 | 13:39 | 2025-05-05 | 14:58 | NW14 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 217 | 17132.15 | 78.95 | 3 | No
| 1893663 | 2025-05-05 | 13:39 | 2025-05-05 | 14:33 | NW14 | NUNAWADING | Urban | Asset Failure | HV | 1588 | 85566.6804 | 53.8833 | 1 | No
| 1893671 | 2025-05-05 | 13:49 | 2025-05-05 | 14:36 | NW14 | NUNAWADING | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 46.4667 | 46.4667 | 1 | No
| 1893716 | 2025-05-05 | 16:23 | 2025-05-05 | 19:00 | NW21 | NUNAWADING | Urban | Asset Failure | HV | 0.67 | 104.9555 | 156.65 | 1 | No
| 1893490 | 2025-05-05 | 17:02 | 2025-05-05 | 19:00 | BU12 | BULLEEN | Urban | Asset Failure | LV | 1 | 118 | 118 | 1 | No
| 1893751 | 2025-05-05 | 19:24 | 2025-05-05 | 20:50 | STO14 | SORRENTO | Rural Short | Animal | Animal impact | 18.09 | 1547.9016 | 85.5667 | 1 | No
| 1893753 | 2025-05-05 | 19:28 | 2025-05-05 | 20:50 | OAK21 | OAKLEIGH | Urban | Animal | Animal impact | 95.14 | 7787.209 | 81.85 | 1 | No
| 1893802 | 2025-06-05 | 8:22 | 2025-06-05 | 9:33 | DC1 | DONCASTER | Urban | Network Business | Switching and protection error | 1 | 70.85 | 70.85 | 1 | No
| 1893893 | 2025-06-05 | 10:45 | 2025-06-05 | 13:05 | SH22 | SURREY HILLS | Urban | Asset Failure | LV | 1 | 140 | 140 | 1 | No
| 1893909 | 2025-06-05 | 11:17 | 2025-06-05 | 13:37 | DN10 | DANDENONG | Urban | Animal | Animal impact | 86.43 | 12100.2 | 140 | 1 | No
| 1893978 | 2025-06-05 | 13:24 | 2025-06-05 | 13:31 | BU14 | BULLEEN | Urban | Network Business | Switching and protection error | 1 | 6.2167 | 6.2167 | 1 | No
| 1893986 | 2025-06-05 | 13:37 | 2025-06-05 | 17:20 | K25 | GARDINER | Urban | Asset Failure | LV | 2 | 445.6334 | 222.8167 | 1 | No
| 1893990 | 2025-06-05 | 14:04 | 2025-06-05 | 15:20 | GW7 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 76.0167 | 76.0167 | 1 | No
| 1894045 | 2025-06-05 | 18:22 | 2025-06-05 | 21:29 | MC23 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 187 | 187 | 1 | No
| 1894048 | 2025-06-05 | 18:47 | 2025-06-05 | 21:02 | DN21 | DANDENONG | Urban | Third Party | Other | 4 | 541.4668 | 135.3667 | 1 | No
| 1894076 | 2025-07-05 | 2:33 | 2025-07-05 | 4:29 | LD7 | LYNDALE | Urban | Asset Failure | LV | 20 | 2311.666 | 115.5833 | 1 | No
| 1894082 | 2025-07-05 | 4:36 | 2025-07-05 | 6:58 | CFD11 | CAULFIELD | Urban | Third Party | Other | 57 | 8086.4019 | 141.8667 | 1 | No
| 1894090 | 2025-07-05 | 5:40 | 2025-07-05 | 7:48 | CRM13 | CARRUM | Urban | Asset Failure | LV | 1 | 127.8167 | 127.8167 | 1 | No
| 1894092 | 2025-07-05 | 5:58 | 2025-07-05 | 6:06 | RBD12 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 151 | 1240.7217 | 8.2167 | 1 | No
| 1894092 | 2025-07-05 | 5:58 | 2025-07-05 | 6:07 | RBD12 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 111 | 969.3963 | 8.7333 | 2 | No
| 1894092 | 2025-07-05 | 5:58 | 2025-07-05 | 8:21 | RBD12 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 11 | 1566.5837 | 142.4167 | 3 | No
| 1894092 | 2025-07-05 | 5:58 | 2025-07-05 | 8:21 | RBD12 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 46 | 6565.7318 | 142.7333 | 4 | No
| 1894175 | 2025-07-05 | 9:50 | 2025-07-05 | 12:37 | EW9 | ELWOOD | Urban | Asset Failure | LV | 1 | 166.6 | 166.6 | 1 | No
| 1894185 | 2025-07-05 | 10:11 | 2025-07-05 | 10:45 | CDA22 | CLARINDA | Urban | Asset Failure | LV | 1 | 34.2667 | 34.2667 | 1 | No
| 1894253 | 2025-07-05 | 11:59 | 2025-07-05 | 12:28 | HGS22 | HASTINGS | Rural Short | Asset Failure | HV | 66 | 1926.0978 | 29.1833 | 1 | No
| 1894292 | 2025-07-05 | 13:36 | 2025-07-05 | 20:03 | DN6 | DANDENONG | Urban | Overloads |  | 1 | 386.5333 | 386.5333 | 1 | No
| 1894305 | 2025-07-05 | 14:18 | 2025-07-05 | 19:31 | BT16 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 312.8167 | 312.8167 | 1 | No
| 1894311 | 2025-07-05 | 15:21 | 2025-07-05 | 18:30 | NW33 | NUNAWADING | Urban | Asset Failure | LV | 3.8 | 721.8735 | 189.9667 | 1 | No
| 1894342 | 2025-07-05 | 16:31 | 2025-07-05 | 16:34 | SVW53 | SPRINGVALE WEST | Urban | Asset Failure | HV | 1359 | 4190.2047 | 3.0833 | 1 | No
| 1894345 | 2025-07-05 | 16:43 | 2025-07-05 | 21:40 | BW21 | BURWOOD | Urban | Asset Failure | LV | 1 | 296.9167 | 296.9167 | 1 | No
| 1894378 | 2025-07-05 | 18:48 | 2025-07-05 | 20:04 | STO14 | SORRENTO | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1130 | 86219 | 76.3 | 1 | No
| 1894378 | 2025-07-05 | 18:48 | 2025-07-05 | 20:42 | STO14 | SORRENTO | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 217 | 24770.55 | 114.15 | 2 | No
| 1894378 | 2025-07-05 | 18:48 | 2025-07-05 | 22:00 | STO14 | SORRENTO | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 71 | 13628.45 | 191.95 | 3 | No
| 1894378 | 2025-07-05 | 18:48 | 2025-08-05 | 7:13 | STO14 | SORRENTO | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 61 | 45501.9313 | 745.9333 | 4 | No
| 1894400 | 2025-07-05 | 18:52 | 2025-08-05 | 0:55 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 19.47 | 7064.3644 | 362.8333 | 1 | No
| 1894389 | 2025-07-05 | 19:10 | 2025-07-05 | 21:08 | SS21 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 3.63 | 428.34 | 118 | 1 | No
| 1894398 | 2025-07-05 | 19:19 | 2025-07-05 | 21:08 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 108.6333 | 108.6333 | 1 | No
| 1894406 | 2025-07-05 | 19:51 | 2025-08-05 | 0:06 | HGS33 | HASTINGS | Rural Short | Asset Failure | Distribution substation | 1.34 | 341.5884 | 254.9167 | 1 | No
| 1894407 | 2025-07-05 | 19:51 | 2025-07-05 | 22:00 | HGS23 | HASTINGS | Rural Short | Animal | Animal impact | 13.4 | 1727.4838 | 128.9167 | 1 | No
| 1894409 | 2025-07-05 | 19:51 | 2025-07-05 | 22:53 | HGS21 | HASTINGS | Rural Short | Asset Failure | HV | 1.34 | 243.746 | 181.9 | 1 | No
| 1894410 | 2025-07-05 | 19:51 | 2025-08-05 | 1:05 | HGS32 | HASTINGS | Urban | Asset Failure | Distribution substation | 3.35 | 1051.565 | 313.9 | 1 | No
| 1894428 | 2025-07-05 | 19:55 | 2025-07-05 | 23:05 | HGS33 | HASTINGS | Rural Short | Animal | Other | 1.34 | 254.6224 | 190.0167 | 1 | No
| 1894429 | 2025-07-05 | 19:55 | 2025-07-05 | 21:22 | HGS22 | HASTINGS | Rural Short | Asset Failure | Distribution substation | 4 | 347 | 86.75 | 1 | No
| 1894423 | 2025-07-05 | 20:21 | 2025-07-05 | 21:19 | HGS22 | HASTINGS | Rural Short | Unknown | Unknown | 1 | 57.6 | 57.6 | 1 | No
| 1894424 | 2025-07-05 | 20:23 | 2025-07-05 | 21:19 | HGS22 | HASTINGS | Rural Short | Asset Failure | HV | 0.67 | 37.2743 | 55.6333 | 1 | No
| 1894430 | 2025-07-05 | 21:29 | 2025-07-05 | 22:05 | BT16 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 36.6667 | 36.6667 | 1 | No
| 1894447 | 2025-07-05 | 23:02 | 2025-08-05 | 0:04 | FTN24 | FRANKSTON | Urban | Animal | Animal impact | 85.76 | 5245.6562 | 61.1667 | 1 | No
| 1894454 | 2025-08-05 | 0:31 | 2025-08-05 | 1:53 | SV16 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 82.8667 | 82.8667 | 1 | No
| 1894458 | 2025-08-05 | 4:05 | 2025-08-05 | 5:00 | MGE23 | MULGRAVE | Urban | Unknown | Unknown | 14.52 | 797.874 | 54.95 | 1 | No
| 1894460 | 2025-08-05 | 5:26 | 2025-08-05 | 12:40 | MGE23 | MULGRAVE | Urban | Asset Failure | LV | 20 | 8691.666 | 434.5833 | 1 | No
| 1894461 | 2025-08-05 | 5:28 | 2025-08-05 | 7:08 | RBD12 | ROSEBUD | Rural Short | Animal | Animal impact | 6 | 597.9 | 99.65 | 1 | No
| 1894460 | 2025-08-05 | 5:40 | 2025-08-05 | 6:29 | MGE23 | MULGRAVE | Urban | Asset Failure | LV | 24 | 1187.5992 | 49.4833 | 1 | No
| 1894480 | 2025-08-05 | 7:52 | 2025-08-05 | 9:30 | CFD23 | CAULFIELD | Urban | Network Business | Network Error | 1 | 97.4833 | 97.4833 | 1 | No
| 1894543 | 2025-08-05 | 8:44 | 2025-08-05 | 10:10 | CRM23 | CARRUM | Urban | Network Business | Switching and protection error | 28 | 2397.7324 | 85.6333 | 1 | No
| 1894531 | 2025-08-05 | 9:33 | 2025-08-05 | 10:37 | CFD25 | CAULFIELD | Urban | Asset Failure | LV | 1 | 64.15 | 64.15 | 1 | No
| 1894579 | 2025-08-05 | 9:56 | 2025-08-05 | 12:10 | OR24 | ORMOND | Urban | Asset Failure | LV | 1 | 134.2667 | 134.2667 | 1 | No
| 1894623 | 2025-08-05 | 10:52 | 2025-08-05 | 13:44 | LD1 | LYNDALE | Urban | Asset Failure | Distribution substation | 38.28 | 6590.5413 | 172.1667 | 1 | No
| 1894630 | 2025-08-05 | 11:02 | 2025-08-05 | 11:37 | DMA15 | DROMANA | Rural Short | Unknown | Unknown | 96 | 3395.2032 | 35.3667 | 1 | No
| 1894630 | 2025-08-05 | 11:02 | 2025-08-05 | 11:39 | DMA15 | DROMANA | Rural Short | Unknown | Unknown | 126 | 4752.3042 | 37.7167 | 2 | No
| 1894630 | 2025-08-05 | 11:02 | 2025-08-05 | 11:41 | DMA15 | DROMANA | Rural Short | Unknown | Unknown | 264 | 10282.8 | 38.95 | 3 | No
| 1894630 | 2025-08-05 | 11:02 | 2025-08-05 | 11:50 | DMA15 | DROMANA | Rural Short | Unknown | Unknown | 317 | 15184.3 | 47.9 | 4 | No
| 1894630 | 2025-08-05 | 11:02 | 2025-08-05 | 12:06 | DMA15 | DROMANA | Rural Short | Unknown | Unknown | 114 | 7326.4038 | 64.2667 | 5 | No
| 1894630 | 2025-08-05 | 11:02 | 2025-08-05 | 12:12 | DMA15 | DROMANA | Rural Short | Unknown | Unknown | 18 | 1274.0994 | 70.7833 | 6 | No
| 1894630 | 2025-08-05 | 11:02 | 2025-08-05 | 12:56 | DMA15 | DROMANA | Rural Short | Unknown | Unknown | 131 | 15001.6877 | 114.5167 | 7 | No
| 1894683 | 2025-08-05 | 12:34 | 2025-08-05 | 15:16 | RBD24 | ROSEBUD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 3 | 486.2499 | 162.0833 | 1 | No
| 1894780 | 2025-08-05 | 19:56 | 2025-08-05 | 21:47 | CRM13 | CARRUM | Urban | Asset Failure | LV | 1 | 111 | 111 | 1 | No
| 1894789 | 2025-09-05 | 3:03 | 2025-09-05 | 4:22 | DC4 | DONCASTER | Urban | Third Party | Vehicle Impact | 4.62 | 362.5928 | 78.4833 | 1 | No
| 1894790 | 2025-09-05 | 3:24 | 2025-09-05 | 5:10 | EB31 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 106 | 106 | 1 | No
| 1894815 | 2025-09-05 | 7:10 | 2025-09-05 | 8:40 | BU21 | BULLEEN | Urban | Network Business | Network Error | 62.98 | 5641.9562 | 89.5833 | 1 | No
| 1894819 | 2025-09-05 | 7:27 | 2025-09-05 | 9:29 | LD33 | LYNDALE | Urban | Third Party | Other | 1 | 122.1167 | 122.1167 | 1 | No
| 1894964 | 2025-09-05 | 10:33 | 2025-09-05 | 12:15 | OE4 | OAKLEIGH EAST | Urban | Asset Failure | LV | 1 | 101.9833 | 101.9833 | 1 | No
| 1894983 | 2025-09-05 | 11:34 | 2025-09-05 | 13:10 | NP36 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 96.5167 | 96.5167 | 1 | No
| 1895098 | 2025-09-05 | 16:58 | 2025-09-05 | 18:11 | MGE23 | MULGRAVE | Urban | Asset Failure | LV | 20 | 1459 | 72.95 | 1 | No
| 1895133 | 2025-09-05 | 19:55 | 2025-09-05 | 21:14 | DC2 | DONCASTER | Urban | Asset Failure | LV | 1 | 79.15 | 79.15 | 1 | No
| 1895135 | 2025-09-05 | 20:10 | 2025-09-05 | 20:24 | NW33 | NUNAWADING | Urban | Asset Failure | Distribution substation | 28.81 | 415.3451 | 14.4167 | 1 | No
| 1895139 | 2025-09-05 | 20:47 | 2025-09-05 | 21:45 | NB25 | NORTH BRIGHTON | Urban | Asset Failure | LV | 30 | 1728 | 57.6 | 1 | No
| 1895167 | 2025-09-05 | 23:47 | 2025-10-05 | 9:30 | MGE14 | MULGRAVE | Urban | Asset Failure | LV | 1 | 582.2 | 582.2 | 1 | No
| 1895165 | 2025-10-05 | 5:43 | 2025-10-05 | 9:00 | HT11 | HEATHERTON | Urban | Asset Failure | LV | 1 | 197 | 197 | 1 | No
| 1895191 | 2025-10-05 | 6:27 | 2025-10-05 | 9:08 | DMA15 | DROMANA | Rural Short | Animal | Animal impact | 18.09 | 2912.49 | 161 | 1 | No
| 1895193 | 2025-10-05 | 8:04 | 2025-10-05 | 10:43 | RBD22 | ROSEBUD | Urban | Third Party | Other | 1 | 159.1833 | 159.1833 | 1 | No
| 1895300 | 2025-10-05 | 16:56 | 2025-10-05 | 18:00 | HT13 | HEATHERTON | Urban | Animal | Animal impact | 8.71 | 549.891 | 63.1333 | 1 | No
| 1895314 | 2025-10-05 | 18:39 | 2025-10-05 | 21:04 | MC21 | MORDIALLOC | Urban | Asset Failure | LV | 19 | 2742.3327 | 144.3333 | 1 | No
| 1895351 | 2025-11-05 | 0:57 | 2025-11-05 | 2:07 | OAK23 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 70.6833 | 70.6833 | 1 | No
| 1895387 | 2025-11-05 | 7:22 | 2025-11-05 | 9:38 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 135.5167 | 135.5167 | 1 | No
| 1895388 | 2025-11-05 | 7:33 | 2025-11-05 | 8:51 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 1 | 78.5333 | 78.5333 | 1 | No
| 1895347 | 2025-11-05 | 8:30 | 2025-11-05 | 12:13 | EB32 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 223.2833 | 223.2833 | 1 | No
| 1895399 | 2025-11-05 | 9:30 | 2025-11-05 | 10:41 | LWN34 | LANGWARRIN | Urban | Third Party | Other | 1 | 70.8833 | 70.8833 | 1 | No
| 1895433 | 2025-11-05 | 14:15 | 2025-11-05 | 14:54 | LWN34 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 39.05 | 39.05 | 1 | No
| 1895454 | 2025-11-05 | 18:51 | 2025-11-05 | 19:57 | NW13 | NUNAWADING | Urban | Animal | Animal impact | 56.28 | 3714.48 | 66 | 1 | No
| 1895603 | 2025-12-05 | 10:01 | 2025-12-05 | 10:16 | DVY13 | DANDENONG VALLEY | Urban | Asset Failure | HV | 25 | 350.4175 | 14.0167 | 1 | No
| 1895603 | 2025-12-05 | 10:01 | 2025-12-05 | 10:42 | DVY13 | DANDENONG VALLEY | Urban | Asset Failure | HV | 57 | 2306.6019 | 40.4667 | 2 | No
| 1895603 | 2025-12-05 | 10:01 | 2025-12-05 | 22:11 | DVY13 | DANDENONG VALLEY | Urban | Asset Failure | HV | 1 | 729.8833 | 729.8833 | 3 | No
| 1895604 | 2025-12-05 | 10:02 | 2025-12-05 | 11:18 | RBD22 | ROSEBUD | Urban | Third Party | Other | 1 | 75.7333 | 75.7333 | 1 | No
| 1895633 | 2025-12-05 | 10:57 | 2025-12-05 | 13:30 | DC8 | DONCASTER | Urban | Asset Failure | LV | 1 | 153 | 153 | 1 | No
| 1895893 | 13/05/2025 | 2:53 | 13/05/2025 | 4:01 | NW31 | NUNAWADING | Urban | Animal | Animal impact | 152.09 | 10319.3065 | 67.85 | 1 | No
| 1895861 | 13/05/2025 | 7:25 | 13/05/2025 | 8:09 | BH22 | BOX HILL | Urban | Asset Failure | LV | 1 | 44.2667 | 44.2667 | 1 | No
| 1895921 | 13/05/2025 | 7:41 | 13/05/2025 | 9:38 | DMA15 | DROMANA | Rural Short | Animal | Animal impact | 7 | 815.3831 | 116.4833 | 1 | No
| 1896060 | 13/05/2025 | 11:49 | 13/05/2025 | 12:39 | MGE23 | MULGRAVE | Urban | Animal | Other | 1.34 | 66.8884 | 49.9167 | 1 | No
| 1896136 | 13/05/2025 | 15:54 | 13/05/2025 | 18:43 | STO13 | SORRENTO | Urban | Weather |  | 2 | 336.3 | 168.15 | 1 | No
| 1896162 | 13/05/2025 | 18:55 | 13/05/2025 | 19:48 | CRM15 | CARRUM | Urban | Asset Failure | LV | 1 | 53.7833 | 53.7833 | 1 | No
| 1896178 | 13/05/2025 | 22:59 | 14/05/2025 | 8:35 | STO13 | SORRENTO | Urban | Asset Failure | LV | 1 | 575.8333 | 575.8333 | 1 | No
| 1896179 | 13/05/2025 | 23:43 | 14/05/2025 | 0:39 | FTN23 | FRANKSTON | Urban | Asset Failure | LV | 17.49 | 964.5735 | 55.15 | 1 | No
| 1896201 | 14/05/2025 | 7:59 | 14/05/2025 | 10:22 | SVW56 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 143.4167 | 143.4167 | 1 | No
| 1896197 | 14/05/2025 | 8:03 | 14/05/2025 | 9:54 | NW23 | NUNAWADING | Urban | Overloads |  | 1 | 111.85 | 111.85 | 1 | No
| 1896211 | 14/05/2025 | 8:16 | 14/05/2025 | 11:46 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 210.2167 | 210.2167 | 1 | No
| 1896219 | 14/05/2025 | 8:34 | 14/05/2025 | 10:39 | FTN23 | FRANKSTON | Urban | Asset Failure | LV | 1 | 125.7667 | 125.7667 | 1 | No
| 1896248 | 14/05/2025 | 9:31 | 14/05/2025 | 12:31 | LWN24 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 179.4167 | 179.4167 | 1 | No
| 1896388 | 14/05/2025 | 16:21 | 14/05/2025 | 17:50 | MTN33 | MORNINGTON | Urban | Asset Failure | LV | 1 | 88.5667 | 88.5667 | 1 | No
| 1896422 | 14/05/2025 | 22:31 | 15/05/2025 | 0:11 | WD15 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 99.6667 | 99.6667 | 1 | No
| 1896443 | 15/05/2025 | 7:23 | 15/05/2025 | 9:41 | K34 | GARDINER | Urban | Asset Failure | LV | 1 | 138.25 | 138.25 | 1 | No
| 1896473 | 15/05/2025 | 7:33 | 15/05/2025 | 8:45 | DMA13 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 2 | 143.3 | 71.65 | 1 | No
| 1896452 | 15/05/2025 | 7:53 | 15/05/2025 | 8:52 | LD2 | LYNDALE | Urban | Animal | Animal impact | 58.29 | 3466.3139 | 59.4667 | 1 | No
| 1896570 | 15/05/2025 | 11:15 | 15/05/2025 | 11:56 | DC8 | DONCASTER | Urban | Third Party | Other | 1 | 40.0333 | 40.0333 | 1 | No
| 1896601 | 15/05/2025 | 12:21 | 15/05/2025 | 13:56 | NO5 | NOTTING HILL | Urban | Asset Failure | LV | 2 | 189.9 | 94.95 | 1 | No
| 1896662 | 15/05/2025 | 15:36 | 15/05/2025 | 17:56 | OR33 | ORMOND | Urban | Third Party | Other | 1 | 140.5333 | 140.5333 | 1 | No
| 1896665 | 15/05/2025 | 15:40 | 15/05/2025 | 16:11 | RD10 | RIVERSDALE | Urban | Asset Failure | LV | 78 | 2436.1974 | 31.2333 | 1 | No
| 1896681 | 15/05/2025 | 17:58 | 15/05/2025 | 23:41 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 48 | 16424.7984 | 342.1833 | 1 | No
| 1896691 | 15/05/2025 | 18:54 | 15/05/2025 | 20:43 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 6.72 | 729.0078 | 108.4833 | 1 | No
| 1896721 | 16/05/2025 | 4:51 | 16/05/2025 | 10:44 | HGS21 | HASTINGS | Rural Short | Unknown | Unknown | 2 | 706.6666 | 353.3333 | 1 | No
| 1896721 | 16/05/2025 | 4:51 | 16/05/2025 | 10:45 | HGS21 | HASTINGS | Rural Short | Unknown | Unknown | 5 | 1768.9165 | 353.7833 | 2 | No
| 1896721 | 16/05/2025 | 4:51 | 16/05/2025 | 10:45 | HGS21 | HASTINGS | Rural Short | Unknown | Unknown | 3 | 1062.3999 | 354.1333 | 3 | No
| 1896721 | 16/05/2025 | 4:51 | 16/05/2025 | 10:46 | HGS21 | HASTINGS | Rural Short | Unknown | Unknown | 3 | 1063.8501 | 354.6167 | 4 | No
| 1896721 | 16/05/2025 | 4:51 | 16/05/2025 | 10:46 | HGS21 | HASTINGS | Rural Short | Unknown | Unknown | 5 | 1774.5 | 354.9 | 5 | No
| 1896721 | 16/05/2025 | 4:51 | 16/05/2025 | 10:46 | HGS21 | HASTINGS | Rural Short | Unknown | Unknown | 4 | 1420.5332 | 355.1333 | 6 | No
| 1896715 | 16/05/2025 | 5:31 | 16/05/2025 | 8:36 | NB22 | NORTH BRIGHTON | Urban | Asset Failure | LV | 5 | 929.0835 | 185.8167 | 1 | No
| 1896731 | 16/05/2025 | 6:42 | 16/05/2025 | 8:10 | DC6 | DONCASTER | Urban | Animal | Animal impact | 190 | 16707.327 | 87.9333 | 1 | No
| 1896749 | 16/05/2025 | 7:59 | 16/05/2025 | 9:50 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 16.5 | 1816.3745 | 110.0833 | 1 | No
| 1896948 | 16/05/2025 | 14:39 | 16/05/2025 | 16:03 | HGS23 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 83.35 | 83.35 | 1 | No
| 1897018 | 16/05/2025 | 20:52 | 16/05/2025 | 21:09 | DMA23 | DROMANA | Rural Short | Asset Failure | LV | 1 | 17.3333 | 17.3333 | 1 | No
| 1897027 | 17/05/2025 | 3:27 | 17/05/2025 | 9:35 | SV32 | SPRINGVALE | Urban | Asset Failure | LV | 5.28 | 1941.1038 | 367.6333 | 1 | No
| 1897028 | 17/05/2025 | 3:40 | 17/05/2025 | 5:03 | EB31 | EAST BURWOOD | Urban | Animal | Animal impact | 111.89 | 9273.8124 | 82.8833 | 1 | No
| 1897031 | 17/05/2025 | 3:42 | 17/05/2025 | 12:33 | DN24 | DANDENONG | Urban | Third Party | Other | 5 | 2651.5835 | 530.3167 | 1 | No
| 1897033 | 17/05/2025 | 4:23 | 17/05/2025 | 5:36 | MGE24 | MULGRAVE | Urban | Animal | Animal impact | 68.34 | 4976.2933 | 72.8167 | 1 | No
| 1897053 | 17/05/2025 | 7:47 | 17/05/2025 | 11:10 | FSH23 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 63.65 | 12859.4195 | 202.0333 | 1 | No
| 1897030 | 17/05/2025 | 8:29 | 17/05/2025 | 12:00 | NB32 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 211 | 211 | 1 | No
| 1897103 | 17/05/2025 | 12:55 | 17/05/2025 | 14:00 | MR12 | MOORABBIN | Urban | Third Party | Other | 1 | 64.1 | 64.1 | 1 | No
| 1897099 | 17/05/2025 | 13:03 | 17/05/2025 | 14:08 | K34 | GARDINER | Urban | Overloads |  | 1 | 65.25 | 65.25 | 1 | No
| 1897105 | 17/05/2025 | 13:58 | 17/05/2025 | 15:29 | RWT23 | RINGWOOD | Urban | Overloads |  | 1 | 91.3333 | 91.3333 | 1 | No
| 1897108 | 17/05/2025 | 16:14 | 17/05/2025 | 17:31 | DMA15 | DROMANA | Rural Short | Overloads |  | 1 | 76.1833 | 76.1833 | 1 | No
| 1897109 | 17/05/2025 | 16:18 | 17/05/2025 | 18:56 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 157.6833 | 157.6833 | 1 | No
| 1897110 | 17/05/2025 | 16:57 | 17/05/2025 | 17:43 | NO7 | NOTTING HILL | Urban | Asset Failure | LV | 1 | 45.0667 | 45.0667 | 1 | No
| 1897111 | 17/05/2025 | 17:07 | 17/05/2025 | 20:00 | HT2 | HEATHERTON | Urban | Asset Failure | LV | 3.8 | 656.07 | 172.65 | 1 | No
| 1897116 | 17/05/2025 | 18:02 | 17/05/2025 | 19:36 | OR24 | ORMOND | Urban | Overloads |  | 1 | 93.9167 | 93.9167 | 1 | No
| 1897117 | 17/05/2025 | 18:16 | 17/05/2025 | 21:14 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 177.8667 | 177.8667 | 1 | No
| 1897135 | 17/05/2025 | 19:28 | 17/05/2025 | 23:53 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 264.3833 | 264.3833 | 1 | No
| 1897137 | 17/05/2025 | 20:54 | 17/05/2025 | 21:36 | MR21 | MOORABBIN | Urban | Asset Failure | LV | 1 | 41.8667 | 41.8667 | 1 | No
| 1897139 | 17/05/2025 | 21:29 | 17/05/2025 | 22:45 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 75.85 | 75.85 | 1 | No
| 1897145 | 17/05/2025 | 23:24 | 18/05/2025 | 6:07 | MGE23 | MULGRAVE | Urban | Asset Failure | LV | 25 | 10075 | 403 | 1 | No
| 1897202 | 18/05/2025 | 7:37 | 18/05/2025 | 10:47 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 27.47 | 5215.6382 | 189.8667 | 1 | No
| 1897187 | 18/05/2025 | 9:02 | 18/05/2025 | 13:57 | K35 | GARDINER | Urban | Asset Failure | LV | 1 | 294.8667 | 294.8667 | 1 | No
| 1897205 | 18/05/2025 | 10:49 | 18/05/2025 | 14:58 | BW21 | BURWOOD | Urban | Asset Failure | LV | 1 | 248.9333 | 248.9333 | 1 | No
| 1897209 | 18/05/2025 | 11:21 | 18/05/2025 | 11:37 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 0 | 423.9528 | 15.4333 | 1 | No
| 1897213 | 18/05/2025 | 12:08 | 18/05/2025 | 14:34 | WD36 | WEST DONCASTER | Urban | Third Party | Other | 64 | 9333.3312 | 145.8333 | 1 | No
| 1897243 | 18/05/2025 | 14:47 | 19/05/2025 | 17:11 | DVY11 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 1584.6167 | 1584.6167 | 1 | No
| 1897243 | 18/05/2025 | 14:47 | 19/05/2025 | 17:17 | DVY11 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 1590.2333 | 1590.2333 | 2 | No
| 1897243 | 18/05/2025 | 14:47 | 19/05/2025 | 17:27 | DVY11 | DANDENONG VALLEY | Urban | Third Party | Other | 3 | 4801.4499 | 1600.4833 | 3 | No
| 1897243 | 18/05/2025 | 14:47 | 19/05/2025 | 17:27 | DVY11 | DANDENONG VALLEY | Urban | Third Party | Other | 3 | 4802.9001 | 1600.9667 | 4 | No
| 1897243 | 18/05/2025 | 14:47 | 19/05/2025 | 17:46 | DVY11 | DANDENONG VALLEY | Urban | Third Party | Other | 2 | 3238 | 1619 | 5 | No
| 1897249 | 18/05/2025 | 16:48 | 18/05/2025 | 21:44 | SR36 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 296.2167 | 296.2167 | 1 | No
| 1897252 | 18/05/2025 | 17:28 | 18/05/2025 | 19:18 | NW21 | NUNAWADING | Urban | Asset Failure | LV | 1 | 110.4333 | 110.4333 | 1 | No
| 1897253 | 18/05/2025 | 17:32 | 18/05/2025 | 19:31 | HGS33 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 119.6833 | 119.6833 | 1 | No
| 1897254 | 18/05/2025 | 17:37 | 18/05/2025 | 20:20 | NP36 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 162.4 | 162.4 | 1 | No
| 1897263 | 18/05/2025 | 18:44 | 18/05/2025 | 21:05 | DMA14 | DROMANA | Urban | Asset Failure | HV | 32.67 | 4602.1151 | 140.8667 | 1 | No
| 1897270 | 18/05/2025 | 19:10 | 18/05/2025 | 20:07 | DN11 | DANDENONG | Urban | Overloads |  | 38.94 | 2242.944 | 57.6 | 1 | No
| 1897273 | 18/05/2025 | 20:15 | 18/05/2025 | 23:51 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 216.0333 | 216.0333 | 1 | No
| 1897292 | 18/05/2025 | 21:25 | 18/05/2025 | 23:49 | NW33 | NUNAWADING | Urban | Overloads |  | 4 | 574.2668 | 143.5667 | 1 | No
| 1897283 | 18/05/2025 | 21:33 | 18/05/2025 | 22:27 | BR4 | BEAUMARIS | Urban | Asset Failure | LV | 10.08 | 546.1677 | 54.1833 | 1 | No
| 1897302 | 19/05/2025 | 4:23 | 19/05/2025 | 5:30 | DVY13 | DANDENONG VALLEY | Urban | Third Party | Other | 2 | 132.1334 | 66.0667 | 1 | No
| 1897308 | 19/05/2025 | 7:07 | 19/05/2025 | 8:34 | NW11 | NUNAWADING | Urban | Asset Failure | LV | 33 | 2871 | 87 | 1 | No
| 1897297 | 19/05/2025 | 7:11 | 19/05/2025 | 9:24 | GW7 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 133.2333 | 133.2333 | 1 | No
| 1897316 | 19/05/2025 | 7:23 | 19/05/2025 | 8:36 | BH11 | BOX HILL | Urban | Asset Failure | LV | 97 | 7064.8301 | 72.8333 | 1 | No
| 1897304 | 19/05/2025 | 8:05 | 19/05/2025 | 9:55 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 110 | 110 | 1 | No
| 1897398 | 19/05/2025 | 8:24 | 19/05/2025 | 8:48 | HT11 | HEATHERTON | Urban | Overloads |  | 110 | 2640 | 24 | 1 | No
| 1897417 | 19/05/2025 | 8:43 | 19/05/2025 | 11:45 | MC15 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 181.65 | 181.65 | 1 | No
| 1897428 | 19/05/2025 | 8:55 | 19/05/2025 | 13:38 | BW33 | BURWOOD | Urban | Third Party | Other | 1 | 282.6333 | 282.6333 | 1 | No
| 1897293 | 19/05/2025 | 8:57 | 19/05/2025 | 10:39 | BH11 | BOX HILL | Urban | Asset Failure | LV | 1 | 102.0667 | 102.0667 | 1 | No
| 1897312 | 19/05/2025 | 9:34 | 19/05/2025 | 11:47 | SV32 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 133.7833 | 133.7833 | 1 | No
| 1897457 | 19/05/2025 | 9:45 | 19/05/2025 | 10:30 | NP14 | NOBLE PARK | Urban | Asset Failure | LV | 5.94 | 262.845 | 44.25 | 1 | No
| 1897455 | 19/05/2025 | 9:47 | 19/05/2025 | 12:03 | EW9 | ELWOOD | Urban | Asset Failure | LV | 1 | 135.4167 | 135.4167 | 1 | No
| 1897493 | 19/05/2025 | 11:31 | 19/05/2025 | 13:23 | MC32 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 111.25 | 111.25 | 1 | No
| 1897518 | 19/05/2025 | 12:03 | 19/05/2025 | 13:23 | OAK26 | OAKLEIGH | Urban | Asset Failure | Distribution substation | 95 | 7619 | 80.2 | 1 | No
| 1897518 | 19/05/2025 | 12:03 | 19/05/2025 | 14:59 | OAK26 | OAKLEIGH | Urban | Asset Failure | Distribution substation | 2 | 352.2666 | 176.1333 | 2 | No
| 1897452 | 19/05/2025 | 12:06 | 19/05/2025 | 14:20 | K25 | GARDINER | Urban | Asset Failure | LV | 1 | 134.9167 | 134.9167 | 1 | No
| 1897543 | 19/05/2025 | 12:54 | 19/05/2025 | 15:15 | MC12 | MORDIALLOC | Urban | Overloads |  | 1 | 141.0333 | 141.0333 | 1 | No
| 1897554 | 19/05/2025 | 13:05 | 19/05/2025 | 16:01 | EW3 | ELWOOD | Urban | Third Party | Other | 1 | 175.9167 | 175.9167 | 1 | No
| 1897579 | 19/05/2025 | 14:00 | 19/05/2025 | 16:00 | MC22 | MORDIALLOC | Urban | Asset Failure | LV | 28 | 3353 | 119.75 | 1 | No
| 1897613 | 19/05/2025 | 16:28 | 19/05/2025 | 18:36 | HGS22 | HASTINGS | Rural Short | Third Party | Vehicle Impact | 42 | 5406.1014 | 128.7167 | 1 | No
| 1897595 | 19/05/2025 | 16:35 | 19/05/2025 | 19:10 | MTN32 | MORNINGTON | Rural Short | Unknown | Unknown | 4 | 620 | 155 | 1 | No
| 1897643 | 19/05/2025 | 18:38 | 19/05/2025 | 20:55 | EW1 | ELWOOD | Urban | Asset Failure | LV | 175 | 23902.0775 | 136.5833 | 1 | No
| 1897645 | 19/05/2025 | 18:50 | 19/05/2025 | 21:31 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 31.35 | 5054.664 | 161.2333 | 1 | No
| 1897655 | 19/05/2025 | 19:49 | 19/05/2025 | 21:37 | DN11 | DANDENONG | Urban | Overloads |  | 118 | 12698.7706 | 107.6167 | 1 | No
| 1897657 | 19/05/2025 | 19:52 | 19/05/2025 | 21:15 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 78 | 6437.5974 | 82.5333 | 1 | No
| 1897661 | 19/05/2025 | 20:02 | 19/05/2025 | 20:28 | BT13 | BENTLEIGH | Urban | Asset Failure | LV | 93.06 | 2419.56 | 26 | 1 | No
| 1897691 | 19/05/2025 | 22:31 | 19/05/2025 | 23:21 | CFD14 | CAULFIELD | Urban | Overloads |  | 90 | 4470.003 | 49.6667 | 1 | No
| 1897694 | 20/05/2025 | 0:59 | 20/05/2025 | 1:38 | BH11 | BOX HILL | Urban | Asset Failure | LV | 1 | 39 | 39 | 1 | No
| 1897700 | 20/05/2025 | 3:30 | 20/05/2025 | 11:52 | NP25 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 502.1 | 502.1 | 1 | No
| 1897702 | 20/05/2025 | 5:20 | 20/05/2025 | 15:57 | DVY11 | DANDENONG VALLEY | Urban | Asset Failure | LV | 3 | 1910.6499 | 636.8833 | 1 | No
| 1897788 | 20/05/2025 | 7:05 | 21/05/2025 | 22:44 | LD1 | LYNDALE | Urban | Third Party | Other | 1 | 2378.55 | 2378.55 | 1 | No
| 1897713 | 20/05/2025 | 7:10 | 20/05/2025 | 11:20 | CDA22 | CLARINDA | Urban | Asset Failure | LV | 9 | 2243.5497 | 249.2833 | 1 | No
| 1897730 | 20/05/2025 | 7:47 | 20/05/2025 | 9:30 | M12 | MENTONE | Urban | Asset Failure | LV | 1 | 102.1833 | 102.1833 | 1 | No
| 1897735 | 20/05/2025 | 8:26 | 20/05/2025 | 9:40 | NW11 | NUNAWADING | Urban | Asset Failure | LV | 1 | 74.2 | 74.2 | 1 | No
| 1897332 | 20/05/2025 | 8:48 | 20/05/2025 | 10:38 | DC8 | DONCASTER | Urban | Asset Failure | LV | 1 | 110.3833 | 110.3833 | 1 | No
| 1897774 | 20/05/2025 | 8:50 | 20/05/2025 | 9:51 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 61.8667 | 61.8667 | 1 | No
| 1897867 | 20/05/2025 | 8:58 | 20/05/2025 | 11:35 | CRM33 | CARRUM | Urban | Asset Failure | LV | 4.44 | 696.414 | 156.85 | 1 | No
| 1897720 | 20/05/2025 | 9:00 | 20/05/2025 | 10:11 | BH23 | BOX HILL | Urban | Asset Failure | LV | 1 | 71.8333 | 71.8333 | 1 | No
| 1897839 | 20/05/2025 | 9:12 | 20/05/2025 | 10:56 | BU25 | BULLEEN | Urban | Network Business | Switching and protection error | 1 | 103.65 | 103.65 | 1 | No
| 1897804 | 20/05/2025 | 9:14 | 20/05/2025 | 11:03 | SV33 | SPRINGVALE | Urban | Third Party | Other | 1 | 109.5 | 109.5 | 1 | No
| 1897826 | 20/05/2025 | 9:30 | 20/05/2025 | 13:21 | NP33 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 230.3833 | 230.3833 | 1 | No
| 1897838 | 20/05/2025 | 9:53 | 20/05/2025 | 10:56 | BU25 | BULLEEN | Urban | Network Business | Switching and protection error | 1 | 62.9167 | 62.9167 | 1 | No
| 1897681 | 20/05/2025 | 10:53 | 20/05/2025 | 15:02 | NP16 | NOBLE PARK | Urban | Third Party | Other | 1 | 249.5333 | 249.5333 | 1 | No
| 1897902 | 20/05/2025 | 12:04 | 20/05/2025 | 12:22 | BU14 | BULLEEN | Urban | Network Business | Network Error | 57 | 984.2019 | 17.2667 | 1 | No
| 1897935 | 20/05/2025 | 13:00 | 20/05/2025 | 14:08 | GW11 | GLEN WAVERLEY | Urban | Overloads |  | 20.79 | 1400.8988 | 67.3833 | 1 | No
| 1897974 | 20/05/2025 | 15:31 | 20/05/2025 | 17:47 | BH22 | BOX HILL | Urban | Asset Failure | LV | 1 | 135.55 | 135.55 | 1 | No
| 1897999 | 20/05/2025 | 17:10 | 20/05/2025 | 18:20 | K25 | GARDINER | Urban | Overloads |  | 73 | 5073.5 | 69.5 | 1 | No
| 1898002 | 20/05/2025 | 17:40 | 21/05/2025 | 1:07 | STO13 | SORRENTO | Urban | Asset Failure | LV | 10.56 | 4721.5524 | 447.1167 | 1 | No
| 1898014 | 20/05/2025 | 18:59 | 20/05/2025 | 21:52 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 172.5667 | 172.5667 | 1 | No
| 1898018 | 20/05/2025 | 19:13 | 20/05/2025 | 21:23 | EW1 | ELWOOD | Urban | Overloads |  | 175 | 22787.9225 | 130.2167 | 1 | No
| 1898023 | 20/05/2025 | 19:40 | 20/05/2025 | 22:30 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 43.23 | 7341.1759 | 169.8167 | 1 | No
| 1898042 | 20/05/2025 | 23:17 | 21/05/2025 | 0:06 | RWT24 | RINGWOOD | Urban | Animal | Animal impact | 79.73 | 3846.9725 | 48.25 | 1 | No
| 1898048 | 21/05/2025 | 1:03 | 21/05/2025 | 3:27 | CFD15 | CAULFIELD | Urban | Third Party | Other | 1 | 144.3833 | 144.3833 | 1 | No
| 1898076 | 21/05/2025 | 7:35 | 21/05/2025 | 9:35 | EW14 | ELWOOD | Urban | Asset Failure | LV | 1 | 119.9 | 119.9 | 1 | No
| 1898085 | 21/05/2025 | 8:03 | 21/05/2025 | 11:23 | MC12 | MORDIALLOC | Urban | Asset Failure | Distribution substation | 75.24 | 15083.1145 | 200.4667 | 1 | No
| 1898117 | 21/05/2025 | 8:47 | 21/05/2025 | 9:39 | DC8 | DONCASTER | Urban | Overloads |  | 1 | 52.95 | 52.95 | 1 | No
| 1898181 | 21/05/2025 | 10:02 | 21/05/2025 | 13:43 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 220.1 | 220.1 | 1 | No
| 1898191 | 21/05/2025 | 10:40 | 21/05/2025 | 11:41 | CFD21 | CAULFIELD | Urban | Asset Failure | LV | 1 | 61.6833 | 61.6833 | 1 | No
| 1898194 | 21/05/2025 | 10:46 | 21/05/2025 | 12:38 | RBD12 | ROSEBUD | Rural Short | Asset Failure | LV | 2 | 223.5334 | 111.7667 | 1 | No
| 1898054 | 21/05/2025 | 10:50 | 21/05/2025 | 11:40 | DC10 | DONCASTER | Urban | Overloads |  | 1 | 50.8167 | 50.8167 | 1 | No
| 1898244 | 21/05/2025 | 12:30 | 21/05/2025 | 15:52 | RBD11 | ROSEBUD | Urban | Asset Failure | LV | 1 | 201.9833 | 201.9833 | 1 | No
| 1898259 | 21/05/2025 | 13:07 | 21/05/2025 | 16:18 | DMA24 | DROMANA | Rural Short | Asset Failure | LV | 1 | 190.8 | 190.8 | 1 | No
| 1898302 | 21/05/2025 | 14:59 | 21/05/2025 | 17:20 | DN6 | DANDENONG | Urban | Asset Failure | LV | 1 | 140.9667 | 140.9667 | 1 | No
| 1898303 | 21/05/2025 | 15:02 | 21/05/2025 | 19:10 | CRM22 | CARRUM | Urban | Asset Failure | LV | 1 | 247.2833 | 247.2833 | 1 | No
| 1898320 | 21/05/2025 | 16:26 | 21/05/2025 | 18:40 | DN11 | DANDENONG | Urban | Asset Failure | LV | 1 | 134 | 134 | 1 | No
| 1898286 | 21/05/2025 | 16:48 | 21/05/2025 | 19:56 | DMA23 | DROMANA | Rural Short | Asset Failure | LV | 1 | 188 | 188 | 1 | No
| 1898324 | 21/05/2025 | 17:23 | 21/05/2025 | 19:42 | DN22 | DANDENONG | Urban | Asset Failure | LV | 1 | 139.9333 | 139.9333 | 1 | No
| 1898365 | 21/05/2025 | 19:53 | 21/05/2025 | 21:58 | EW1 | ELWOOD | Urban | Asset Failure | LV | 57.75 | 7179.2894 | 124.3167 | 1 | No
| 1898366 | 21/05/2025 | 20:06 | 21/05/2025 | 20:44 | SVW54 | SPRINGVALE WEST | Urban | Overloads |  | 1 | 38.1 | 38.1 | 1 | No
| 1898369 | 21/05/2025 | 22:22 | 22/05/2025 | 0:51 | EL23 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 148.6833 | 148.6833 | 1 | No
| 1898373 | 22/05/2025 | 0:40 | 22/05/2025 | 1:45 | LWN21 | LANGWARRIN | Rural Short | Animal | Animal impact | 9.38 | 609.7 | 65 | 1 | No
| 1898423 | 22/05/2025 | 8:15 | 22/05/2025 | 8:50 | HGS33 | HASTINGS | Rural Short | Network Business | Switching and protection error | 2.8 | 96.8332 | 34.5833 | 1 | No
| 1898449 | 22/05/2025 | 8:41 | 22/05/2025 | 9:49 | MTN32 | MORNINGTON | Rural Short | Third Party | Vehicle Impact | 30 | 2049 | 68.3 | 1 | No
| 1898449 | 22/05/2025 | 8:41 | 22/05/2025 | 16:08 | MTN32 | MORNINGTON | Rural Short | Third Party | Vehicle Impact | 3 | 1340.6499 | 446.8833 | 2 | No
| 1898449 | 22/05/2025 | 8:41 | 22/05/2025 | 16:08 | MTN32 | MORNINGTON | Rural Short | Third Party | Vehicle Impact | 5 | 2234.6665 | 446.9333 | 3 | No
| 1898461 | 22/05/2025 | 9:01 | 22/05/2025 | 15:43 | MTN32 | MORNINGTON | Rural Short | Third Party | Vehicle Impact | 5 | 2011.25 | 402.25 | 1 | No
| 1898402 | 22/05/2025 | 9:41 | 22/05/2025 | 10:58 | NW23 | NUNAWADING | Urban | Overloads |  | 1 | 77.2 | 77.2 | 1 | No
| 1898521 | 22/05/2025 | 10:32 | 22/05/2025 | 11:01 | OR35 | ORMOND | Urban | Network Business | Switching and protection error | 75 | 2161.2525 | 28.8167 | 1 | No
| 1898597 | 22/05/2025 | 13:26 | 22/05/2025 | 14:09 | EM6 | EAST MALVERN | Urban | Overloads |  | 1 | 43.1167 | 43.1167 | 1 | No
| 1898619 | 22/05/2025 | 14:12 | 22/05/2025 | 15:51 | DN6 | DANDENONG | Urban | Overloads |  | 1 | 98.2833 | 98.2833 | 1 | No
| 1898624 | 22/05/2025 | 15:39 | 22/05/2025 | 16:36 | M21 | MENTONE | Urban | Asset Failure | LV | 1 | 57.4333 | 57.4333 | 1 | No
| 1898654 | 22/05/2025 | 16:22 | 22/05/2025 | 17:33 | BT12 | BENTLEIGH | Urban | Asset Failure | LV | 10.23 | 728.2052 | 71.1833 | 1 | No
| 1898672 | 22/05/2025 | 18:23 | 22/05/2025 | 20:15 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 112.5333 | 112.5333 | 1 | No
| 1898681 | 22/05/2025 | 19:27 | 22/05/2025 | 22:16 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 1 | 169.9 | 169.9 | 1 | No
| 1898690 | 22/05/2025 | 21:14 | 22/05/2025 | 22:30 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 7.2 | 540.4802 | 75.0667 | 1 | No
| 1898694 | 22/05/2025 | 22:07 | 22/05/2025 | 22:41 | NO6 | NOTTING HILL | Urban | Animal | Other | 88 | 2953.8696 | 33.5667 | 1 | No
| 1898694 | 22/05/2025 | 22:07 | 22/05/2025 | 23:11 | NO6 | NOTTING HILL | Urban | Animal | Other | 636 | 40269.4212 | 63.3167 | 2 | No
| 1898697 | 22/05/2025 | 22:33 | 23/05/2025 | 0:00 | RBD24 | ROSEBUD | Urban | Animal | Animal impact | 92.46 | 8017.8261 | 86.7167 | 1 | No
| 1898705 | 23/05/2025 | 1:02 | 23/05/2025 | 2:00 | MGE12 | MULGRAVE | Urban | Asset Failure | LV | 1 | 58.15 | 58.15 | 1 | No
| 1898755 | 23/05/2025 | 8:34 | 23/05/2025 | 10:44 | DN21 | DANDENONG | Urban | Asset Failure | LV | 1 | 129.8 | 129.8 | 1 | No
| 1898823 | 23/05/2025 | 10:07 | 23/05/2025 | 11:03 | DC2 | DONCASTER | Urban | Asset Failure | HV | 36.85 | 2062.9846 | 55.9833 | 1 | No
| 1898821 | 23/05/2025 | 10:16 | 23/05/2025 | 10:50 | RWT24 | RINGWOOD | Urban | Other | XXX | 1 | 33.6333 | 33.6333 | 1 | No
| 1898908 | 23/05/2025 | 13:09 | 23/05/2025 | 15:17 | SR34 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 128.5833 | 128.5833 | 1 | No
| 1898934 | 23/05/2025 | 14:07 | 23/05/2025 | 14:28 | SS21 | SPRINGVALE SOUTH | Urban | Asset Failure | HV | 9 | 188.55 | 20.95 | 1 | No
| 1898934 | 23/05/2025 | 14:09 | 23/05/2025 | 14:28 | SS21 | SPRINGVALE SOUTH | Urban | Asset Failure | HV | 1 | 18.7 | 18.7 | 1 | No
| 1898958 | 23/05/2025 | 16:41 | 23/05/2025 | 17:09 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 28.8833 | 28.8833 | 1 | No
| 1898975 | 23/05/2025 | 17:18 | 23/05/2025 | 21:59 | SR21 | SANDRINGHAM | Urban | Third Party | Vehicle Impact | 2 | 562 | 281 | 1 | No
| 1898976 | 23/05/2025 | 17:39 | 23/05/2025 | 20:10 | CFD16 | CAULFIELD | Urban | Asset Failure | LV | 1 | 150.3167 | 150.3167 | 1 | No
| 1898978 | 23/05/2025 | 18:03 | 23/05/2025 | 18:54 | LD4 | LYNDALE | Urban | Overloads |  | 1 | 50.9833 | 50.9833 | 1 | No
| 1898981 | 23/05/2025 | 18:19 | 23/05/2025 | 22:00 | GW8 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 220.5 | 220.5 | 1 | No
| 1898982 | 23/05/2025 | 18:59 | 23/05/2025 | 21:49 | MR15 | MOORABBIN | Urban | Asset Failure | LV | 1 | 170.0167 | 170.0167 | 1 | No
| 1898993 | 23/05/2025 | 21:01 | 23/05/2025 | 22:38 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 1 | 97.25 | 97.25 | 1 | No
| 1898994 | 23/05/2025 | 21:20 | 23/05/2025 | 23:40 | LWN21 | LANGWARRIN | Rural Short | Animal | Animal impact | 6.03 | 841.788 | 139.6 | 1 | No
| 1899003 | 23/05/2025 | 23:09 | 24/05/2025 | 0:38 | MGE23 | MULGRAVE | Urban | Animal | Animal impact | 54.94 | 4880.5015 | 88.8333 | 1 | No
| 1899023 | 24/05/2025 | 6:08 | 24/05/2025 | 6:35 | GW2 | GLEN WAVERLEY | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 90 | 2430 | 27 | 1 | No
| 1899027 | 24/05/2025 | 8:42 | 24/05/2025 | 10:43 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 121 | 121 | 1 | No
| 1899055 | 24/05/2025 | 9:09 | 24/05/2025 | 12:03 | GW2 | GLEN WAVERLEY | Urban | Unknown | Unknown | 1 | 173.8167 | 173.8167 | 1 | No
| 1899071 | 24/05/2025 | 11:10 | 24/05/2025 | 14:02 | M35 | MENTONE | Urban | Asset Failure | LV | 1 | 172 | 172 | 1 | No
| 1899101 | 24/05/2025 | 14:56 | 24/05/2025 | 17:43 | CRM22 | CARRUM | Urban | Asset Failure | LV | 1 | 166.4167 | 166.4167 | 1 | No
| 1899106 | 24/05/2025 | 15:25 | 24/05/2025 | 19:29 | FTN24 | FRANKSTON | Urban | Third Party | Vehicle Impact | 21 | 5130.9993 | 244.3333 | 1 | No
| 1899107 | 24/05/2025 | 15:28 | 24/05/2025 | 19:29 | FTN24 | FRANKSTON | Urban | Third Party | Vehicle Impact | 38 | 9159.9 | 241.05 | 1 | No
| 1899126 | 24/05/2025 | 18:11 | 24/05/2025 | 21:03 | DC10 | DONCASTER | Urban | Asset Failure | LV | 1 | 172.3333 | 172.3333 | 1 | No
| 1899147 | 24/05/2025 | 21:51 | 25/05/2025 | 0:10 | HT1 | HEATHERTON | Urban | Asset Failure | LV | 1 | 138.3667 | 138.3667 | 1 | No
| 1899179 | 25/05/2025 | 8:14 | 25/05/2025 | 12:55 | MC15 | MORDIALLOC | Urban | Overloads |  | 1 | 280.1167 | 280.1167 | 1 | No
| 1899197 | 25/05/2025 | 10:21 | 25/05/2025 | 13:10 | SS11 | SPRINGVALE SOUTH | Urban | Animal | Animal impact | 1 | 168.3 | 168.3 | 1 | No
| 1899236 | 25/05/2025 | 14:54 | 25/05/2025 | 16:30 | M22 | MENTONE | Urban | Asset Failure | LV | 1 | 95.2 | 95.2 | 1 | No
| 1899257 | 25/05/2025 | 20:10 | 25/05/2025 | 21:20 | FTN21 | FRANKSTON | Urban | Animal | Animal impact | 23.1 | 1621.62 | 70.2 | 1 | No
| 1899265 | 25/05/2025 | 23:47 | 26/05/2025 | 1:10 | MR22 | MOORABBIN | Urban | Asset Failure | LV | 20 | 1640.666 | 82.0333 | 1 | No
| 1899287 | 26/05/2025 | 3:34 | 26/05/2025 | 4:51 | K24 | GARDINER | Urban | Third Party | Other | 58 | 4436.0314 | 76.4833 | 1 | No
| 1899290 | 26/05/2025 | 3:35 | 26/05/2025 | 4:48 | K24 | GARDINER | Urban | Third Party | Other | 66 | 4811.4 | 72.9 | 1 | No
| 1899292 | 26/05/2025 | 6:49 | 26/05/2025 | 8:28 | RBD12 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 74.37 | 7298.1735 | 98.1333 | 1 | No
| 1899308 | 26/05/2025 | 7:32 | 26/05/2025 | 8:21 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 1 | 48.6167 | 48.6167 | 1 | No
| 1899285 | 26/05/2025 | 9:37 | 26/05/2025 | 11:58 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 141.4667 | 141.4667 | 1 | No
| 1899367 | 26/05/2025 | 9:48 | 26/05/2025 | 11:30 | SS23 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 102 | 102 | 1 | No
| 1899381 | 26/05/2025 | 10:06 | 26/05/2025 | 14:49 | FSH23 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 282.9833 | 282.9833 | 1 | No
| 1899389 | 26/05/2025 | 10:20 | 26/05/2025 | 12:55 | MR22 | MOORABBIN | Urban | Asset Failure | LV | 2 | 309.1334 | 154.5667 | 1 | No
| 1899398 | 26/05/2025 | 10:30 | 26/05/2025 | 12:02 | NW23 | NUNAWADING | Urban | Asset Failure | LV | 1 | 92.0167 | 92.0167 | 1 | No
| 1899451 | 26/05/2025 | 12:03 | 26/05/2025 | 12:23 | FSH13 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 271 | 5261.9257 | 19.4167 | 1 | No
| 1899470 | 26/05/2025 | 12:27 | 26/05/2025 | 13:44 | LD7 | LYNDALE | Urban | Network Business | Network Error | 1 | 77.3167 | 77.3167 | 1 | No
| 1899525 | 26/05/2025 | 14:06 | 26/05/2025 | 16:03 | AR6 | ARMADALE | Urban | Asset Failure | LV | 1 | 116.7667 | 116.7667 | 1 | No
| 1899565 | 26/05/2025 | 18:18 | 26/05/2025 | 18:45 | STO23 | SORRENTO | Urban | Asset Failure | LV | 65 | 1743.0855 | 26.8167 | 1 | No
| 1899563 | 26/05/2025 | 18:20 | 26/05/2025 | 19:09 | SR34 | SANDRINGHAM | Urban | Asset Failure | LV | 63 | 3087 | 49 | 1 | No
| 1899566 | 26/05/2025 | 18:30 | 26/05/2025 | 19:45 | NB33 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 74.7333 | 74.7333 | 1 | No
| 1899572 | 26/05/2025 | 19:10 | 26/05/2025 | 19:39 | K24 | GARDINER | Urban | Network Business | Network Error | 804 | 23208.8268 | 28.8667 | 1 | No
| 1899600 | 26/05/2025 | 19:37 | 26/05/2025 | 20:59 | MR31 | MOORABBIN | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 10.56 | 865.92 | 82 | 1 | No
| 1899606 | 26/05/2025 | 20:19 | 26/05/2025 | 21:30 | HGS22 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 70.15 | 70.15 | 1 | No
| 1899609 | 26/05/2025 | 20:25 | 26/05/2025 | 20:39 | DC8 | DONCASTER | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 184 | 2655.7272 | 14.4333 | 1 | No
| 1899617 | 26/05/2025 | 20:55 | 26/05/2025 | 22:29 | CRM23 | CARRUM | Urban | Asset Failure | LV | 9 | 837.7497 | 93.0833 | 1 | No
| 1899612 | 26/05/2025 | 21:12 | 26/05/2025 | 22:29 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 77 | 77 | 1 | No
| 1899618 | 26/05/2025 | 21:20 | 26/05/2025 | 21:34 | HGS22 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 13.6 | 13.6 | 1 | No
| 1899645 | 27/05/2025 | 7:02 | 27/05/2025 | 8:49 | OE4 | OAKLEIGH EAST | Urban | Asset Failure | LV | 1 | 107.2333 | 107.2333 | 1 | No
| 1899647 | 27/05/2025 | 7:26 | 27/05/2025 | 11:10 | FSH23 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 224 | 224 | 1 | No
| 1899627 | 27/05/2025 | 7:29 | 27/05/2025 | 11:55 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 266.4833 | 266.4833 | 1 | No
| 1899650 | 27/05/2025 | 7:31 | 27/05/2025 | 9:56 | HGS33 | HASTINGS | Rural Short | Animal | Other | 29 | 4177.45 | 144.05 | 1 | No
| 1899637 | 27/05/2025 | 7:35 | 27/05/2025 | 22:15 | SS24 | SPRINGVALE SOUTH | Urban | Third Party | Other | 8 | 7036.4 | 879.55 | 1 | No
| 1899655 | 27/05/2025 | 7:53 | 27/05/2025 | 10:05 | EW1 | ELWOOD | Urban | Asset Failure | LV | 1 | 132.4667 | 132.4667 | 1 | No
| 1899680 | 27/05/2025 | 8:56 | 27/05/2025 | 11:05 | NW22 | NUNAWADING | Urban | Overloads |  | 1 | 128.75 | 128.75 | 1 | No
| 1899681 | 27/05/2025 | 8:59 | 27/05/2025 | 22:22 | SS24 | SPRINGVALE SOUTH | Urban | Third Party | Other | 1 | 802.6667 | 802.6667 | 1 | No
| 1899700 | 27/05/2025 | 11:04 | 27/05/2025 | 22:18 | OAK34 | OAKLEIGH | Urban | Third Party | Other | 4 | 2695.2668 | 673.8167 | 1 | No
| 1899705 | 27/05/2025 | 11:07 | 27/05/2025 | 22:18 | OAK34 | OAKLEIGH | Urban | Third Party | Other | 5 | 3350.6665 | 670.1333 | 1 | No
| 1899735 | 27/05/2025 | 14:17 | 27/05/2025 | 15:33 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 75.9833 | 75.9833 | 1 | No
| 1899739 | 27/05/2025 | 15:02 | 27/05/2025 | 17:20 | BH21 | BOX HILL | Urban | Asset Failure | LV | 1 | 137.6167 | 137.6167 | 1 | No
| 1899750 | 27/05/2025 | 15:30 | 27/05/2025 | 16:53 | DVY23 | DANDENONG VALLEY | Urban | Unknown | Unknown | 5.28 | 437.6238 | 82.8833 | 1 | No
| 1899758 | 27/05/2025 | 16:43 | 27/05/2025 | 21:05 | KBH32 | KEYSBOROUGH | Urban | Asset Failure | LV | 1 | 262 | 262 | 1 | No
| 1899774 | 27/05/2025 | 17:36 | 28/05/2025 | 14:15 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 2 | 2477.5666 | 1238.7833 | 1 | No
| 1899774 | 27/05/2025 | 17:41 | 27/05/2025 | 23:03 | FTN25 | FRANKSTON | Urban | Asset Failure | LV | 60 | 19294.998 | 321.5833 | 1 | No
| 1899780 | 27/05/2025 | 17:59 | 27/05/2025 | 19:40 | DN11 | DANDENONG | Urban | Asset Failure | LV | 4 | 403 | 100.75 | 1 | No
| 1899784 | 27/05/2025 | 18:43 | 27/05/2025 | 23:05 | DN22 | DANDENONG | Urban | Asset Failure | LV | 1 | 261.05 | 261.05 | 1 | No
| 1899761 | 27/05/2025 | 19:37 | 28/05/2025 | 0:01 | SV16 | SPRINGVALE | Urban | Third Party | Other | 1 | 264.2 | 264.2 | 1 | No
| 1899802 | 27/05/2025 | 20:50 | 27/05/2025 | 21:00 | EB33 | EAST BURWOOD | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 40 | 381.332 | 9.5333 | 1 | No
| 1899852 | 28/05/2025 | 5:51 | 28/05/2025 | 19:00 | MC31 | MORDIALLOC | Urban | Third Party | Other | 37 | 29181.9 | 788.7 | 1 | No
| 1899811 | 28/05/2025 | 5:56 | 28/05/2025 | 7:29 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 93.6 | 93.6 | 1 | No
| 1899851 | 28/05/2025 | 7:17 | 28/05/2025 | 8:57 | FTN14 | FRANKSTON | Urban | Weather |  | 0.67 | 66.5868 | 99.3833 | 1 | No
| 1899880 | 28/05/2025 | 8:13 | 28/05/2025 | 11:23 | NB36 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 189.7 | 189.7 | 1 | No
| 1899929 | 28/05/2025 | 10:07 | 28/05/2025 | 11:53 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 1 | 106.0333 | 106.0333 | 1 | No
| 1899964 | 28/05/2025 | 12:42 | 28/05/2025 | 13:41 | FTN11 | FRANKSTON | Urban | Unknown | Unknown | 1 | 59.5167 | 59.5167 | 1 | No
| 1899908 | 28/05/2025 | 13:38 | 28/05/2025 | 16:15 | DN7 | DANDENONG | Urban | Asset Failure | LV | 1 | 157 | 157 | 1 | No
| 1900023 | 28/05/2025 | 15:37 | 28/05/2025 | 17:20 | EB13 | EAST BURWOOD | Urban | Asset Failure | LV | 15 | 1540.7505 | 102.7167 | 1 | No
| 1900034 | 28/05/2025 | 19:36 | 28/05/2025 | 20:58 | DC2 | DONCASTER | Urban | Asset Failure | LV | 1 | 82.1167 | 82.1167 | 1 | No
| 1900033 | 28/05/2025 | 19:37 | 28/05/2025 | 22:20 | OAK33 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 163.0167 | 163.0167 | 1 | No
| 1900049 | 28/05/2025 | 20:50 | 28/05/2025 | 23:40 | SVW41 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 169.7333 | 169.7333 | 1 | No
| 1900067 | 29/05/2025 | 6:23 | 29/05/2025 | 8:04 | DVY11 | DANDENONG VALLEY | Urban | Animal | Other | 0.67 | 67.3573 | 100.5333 | 1 | No
| 1900078 | 29/05/2025 | 8:13 | 29/05/2025 | 11:00 | OR34 | ORMOND | Urban | Asset Failure | LV | 1 | 166.45 | 166.45 | 1 | No
| 1900131 | 29/05/2025 | 9:55 | 29/05/2025 | 12:22 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 1 | 147.4833 | 147.4833 | 1 | No
| 1900184 | 29/05/2025 | 12:46 | 29/05/2025 | 14:32 | KBH31 | KEYSBOROUGH | Urban | Animal | Animal impact | 19 | 2016.85 | 106.15 | 1 | No
| 1900242 | 29/05/2025 | 15:43 | 29/05/2025 | 17:27 | GW7 | GLEN WAVERLEY | Urban | Third Party | Other | 3 | 312.0501 | 104.0167 | 1 | No
| 1900247 | 29/05/2025 | 16:26 | 29/05/2025 | 18:16 | MR13 | MOORABBIN | Urban | Third Party | Other | 1 | 110.1333 | 110.1333 | 1 | No
| 1900251 | 29/05/2025 | 17:42 | 29/05/2025 | 19:35 | RBD12 | ROSEBUD | Rural Short | Overloads |  | 1 | 112.6333 | 112.6333 | 1 | No
| 1900252 | 29/05/2025 | 18:11 | 29/05/2025 | 19:30 | GW4 | GLEN WAVERLEY | Urban | Asset Failure | LV | 60 | 4714.998 | 78.5833 | 1 | No
| 1900257 | 29/05/2025 | 18:18 | 29/05/2025 | 20:32 | OR24 | ORMOND | Urban | Unknown | Unknown | 1 | 133.8 | 133.8 | 1 | No
| 1900264 | 29/05/2025 | 19:09 | 29/05/2025 | 21:00 | STO21 | SORRENTO | Rural Short | Overloads |  | 1 | 110.7667 | 110.7667 | 1 | No
| 1900276 | 29/05/2025 | 20:46 | 29/05/2025 | 22:30 | BC11 | BALACLAVA | Urban | Asset Failure | LV | 1 | 103.6 | 103.6 | 1 | No
| 1900282 | 29/05/2025 | 22:46 | 29/05/2025 | 23:45 | CDA22 | CLARINDA | Urban | Asset Failure | LV | 1 | 58.2667 | 58.2667 | 1 | No
| 1900306 | 30/05/2025 | 1:45 | 30/05/2025 | 2:26 | SS14 | SPRINGVALE SOUTH | Urban | Third Party | Other | 17 | 695.3 | 40.9 | 1 | No
| 1900322 | 30/05/2025 | 5:35 | 30/05/2025 | 10:20 | DVY22 | DANDENONG VALLEY | Urban | Third Party | Other | 12 | 3419.7996 | 284.9833 | 1 | No
| 1900322 | 30/05/2025 | 5:35 | 30/05/2025 | 19:30 | DVY22 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 834.4333 | 834.4333 | 2 | No
| 1900322 | 30/05/2025 | 5:35 | 30/05/2025 | 21:00 | DVY22 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 924.9333 | 924.9333 | 3 | No
| 1900324 | 30/05/2025 | 5:43 | 30/05/2025 | 14:27 | MC22 | MORDIALLOC | Urban | Third Party | Other | 1 | 523.3167 | 523.3167 | 1 | No
| 1900333 | 30/05/2025 | 7:01 | 30/05/2025 | 9:30 | LWN21 | LANGWARRIN | Rural Short | Animal | Animal impact | 9 | 1341 | 149 | 1 | No
| 1900337 | 30/05/2025 | 7:33 | 30/05/2025 | 10:59 | HGS22 | HASTINGS | Rural Short | Animal | Animal impact | 3 | 616.2999 | 205.4333 | 1 | No
| 1900448 | 30/05/2025 | 11:00 | 30/05/2025 | 12:19 | MGE21 | MULGRAVE | Urban | Third Party | Other | 1 | 78.5833 | 78.5833 | 1 | No
| 1900450 | 30/05/2025 | 11:06 | 30/05/2025 | 13:45 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 12 | 1899.6 | 158.3 | 1 | No
| 1900456 | 30/05/2025 | 11:36 | 30/05/2025 | 16:39 | MC22 | MORDIALLOC | Urban | Third Party | Other | 11 | 3328.4163 | 302.5833 | 1 | No
| 1900460 | 30/05/2025 | 12:13 | 30/05/2025 | 14:35 | NO4 | NOTTING HILL | Urban | Third Party | Other | 1 | 142.15 | 142.15 | 1 | No
| 1900461 | 30/05/2025 | 12:20 | 30/05/2025 | 15:15 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 174.4 | 174.4 | 1 | No
| 1900466 | 30/05/2025 | 12:44 | 30/05/2025 | 15:38 | EM5 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 173.5167 | 173.5167 | 1 | No
| 1900471 | 30/05/2025 | 13:21 | 30/05/2025 | 14:51 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 89.75 | 89.75 | 1 | No
| 1900489 | 30/05/2025 | 17:57 | 30/05/2025 | 20:09 | BH34 | BOX HILL | Urban | Asset Failure | LV | 1 | 132.2167 | 132.2167 | 1 | No
| 1900496 | 30/05/2025 | 18:43 | 30/05/2025 | 21:25 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 162 | 162 | 1 | No
| 1900505 | 30/05/2025 | 21:45 | 30/05/2025 | 23:36 | HT4 | HEATHERTON | Urban | Asset Failure | LV | 1 | 111.3833 | 111.3833 | 1 | No
| 1900522 | 31/05/2025 | 1:29 | 31/05/2025 | 2:11 | KBH33 | KEYSBOROUGH | Urban | Third Party | Other | 14 | 593.6 | 42.4 | 1 | No
| 1900535 | 31/05/2025 | 8:12 | 31/05/2025 | 9:55 | NP23 | NOBLE PARK | Urban | Animal | Animal impact | 66.33 | 6825.357 | 102.9 | 1 | No
| 1900577 | 31/05/2025 | 12:15 | 31/05/2025 | 18:30 | LD2 | LYNDALE | Urban | Asset Failure | LV | 1 | 374.3833 | 374.3833 | 1 | No
| 1900586 | 31/05/2025 | 13:13 | 31/05/2025 | 15:52 | BT21 | BENTLEIGH | Urban | Asset Failure | LV | 4 | 636.6668 | 159.1667 | 1 | No
| 1900594 | 31/05/2025 | 16:06 | 31/05/2025 | 17:50 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 103.45 | 103.45 | 1 | No
| 1900595 | 31/05/2025 | 16:19 | 31/05/2025 | 17:47 | NO6 | NOTTING HILL | Urban | Third Party | Other | 1 | 88.1833 | 88.1833 | 1 | No
| 1900596 | 31/05/2025 | 16:41 | 31/05/2025 | 18:58 | SVW41 | SPRINGVALE WEST | Urban | Asset Failure | LV | 4.62 | 630.7838 | 136.5333 | 1 | No
| 1900606 | 31/05/2025 | 18:38 | 31/05/2025 | 20:05 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 87 | 87 | 1 | No
| 1900611 | 31/05/2025 | 19:16 | 31/05/2025 | 20:02 | RWT23 | RINGWOOD | Urban | Asset Failure | LV | 1 | 46.5167 | 46.5167 | 1 | No
| 1900615 | 31/05/2025 | 20:20 | 31/05/2025 | 21:14 | NW14 | NUNAWADING | Urban | Asset Failure | LV | 7.92 | 421.74 | 53.25 | 1 | No
| 1900626 | 31/05/2025 | 23:46 | 2025-01-06 | 1:26 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 2.31 | 230.8076 | 99.9167 | 1 | No
| 1900625 | 31/05/2025 | 23:48 | 2025-01-06 | 0:20 | CFD14 | CAULFIELD | Urban | Asset Failure | HV | 124 | 4067.2 | 32.8 | 1 | No
| 1900625 | 31/05/2025 | 23:48 | 2025-01-06 | 0:27 | CFD14 | CAULFIELD | Urban | Asset Failure | HV | 185 | 7338.3395 | 39.6667 | 2 | No
| 1900625 | 31/05/2025 | 23:48 | 2025-01-06 | 0:30 | CFD14 | CAULFIELD | Urban | Asset Failure | HV | 217 | 9236.9739 | 42.5667 | 3 | No
| 1900625 | 31/05/2025 | 23:48 | 2025-01-06 | 0:34 | CFD14 | CAULFIELD | Urban | Asset Failure | HV | 298 | 13752.7 | 46.15 | 4 | No
| 1900651 | 2025-01-06 | 9:46 | 2025-01-06 | 11:20 | MTN32 | MORNINGTON | Rural Short | Overloads |  | 8 | 745.6 | 93.2 | 1 | No
| 1900704 | 2025-01-06 | 16:55 | 2025-01-06 | 19:50 | LWN24 | LANGWARRIN | Urban | Overloads |  | 1 | 175 | 175 | 1 | No
| 1900693 | 2025-01-06 | 17:07 | 2025-01-06 | 17:36 | EB11 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 29.95 | 29.95 | 1 | No
| 1900705 | 2025-01-06 | 17:16 | 2025-01-06 | 18:25 | EB32 | EAST BURWOOD | Urban | Asset Failure | LV | 34.32 | 2346.3451 | 68.3667 | 1 | No
| 1900708 | 2025-01-06 | 17:32 | 2025-01-06 | 19:44 | DC10 | DONCASTER | Urban | Asset Failure | LV | 1 | 132.2333 | 132.2333 | 1 | No
| 1900710 | 2025-01-06 | 17:54 | 2025-01-06 | 19:12 | EB11 | EAST BURWOOD | Urban | Third Party | Other | 1 | 78.6833 | 78.6833 | 1 | No
| 1900709 | 2025-01-06 | 18:47 | 2025-01-06 | 21:38 | FTN13 | FRANKSTON | Urban | Asset Failure | LV | 1 | 171 | 171 | 1 | No
| 1900723 | 2025-01-06 | 20:23 | 2025-01-06 | 21:25 | LD32 | LYNDALE | Urban | Asset Failure | Distribution substation | 48.18 | 2954.2386 | 61.3167 | 1 | No
| 1900738 | 2025-02-06 | 7:33 | 2025-02-06 | 8:19 | BW35 | BURWOOD | Urban | Asset Failure | LV | 18.48 | 846.9994 | 45.8333 | 1 | No
| 1900736 | 2025-02-06 | 7:34 | 2025-02-06 | 9:37 | NW22 | NUNAWADING | Urban | Overloads |  | 1 | 122.9333 | 122.9333 | 1 | No
| 1900743 | 2025-02-06 | 8:16 | 2025-02-06 | 10:18 | MC22 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 122.6333 | 122.6333 | 1 | No
| 1900764 | 2025-02-06 | 9:25 | 2025-02-06 | 12:40 | EW2 | ELWOOD | Urban | Asset Failure | LV | 8.91 | 1731.3618 | 194.3167 | 1 | No
| 1900766 | 2025-02-06 | 9:44 | 2025-02-06 | 10:04 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 2 | 40.8334 | 20.4167 | 1 | No
| 1900774 | 2025-02-06 | 10:05 | 2025-02-06 | 12:30 | CDA23 | CLARINDA | Urban | Unknown | Unknown | 1 | 144.7167 | 144.7167 | 1 | No
| 1900786 | 2025-02-06 | 11:25 | 2025-02-06 | 14:05 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 159.35 | 159.35 | 1 | No
| 1900791 | 2025-02-06 | 11:55 | 2025-02-06 | 14:11 | DC8 | DONCASTER | Urban | Asset Failure | LV | 1 | 136.0333 | 136.0333 | 1 | No
| 1900812 | 2025-02-06 | 14:03 | 2025-02-06 | 17:15 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 191.7667 | 191.7667 | 1 | No
| 1900820 | 2025-02-06 | 14:39 | 2025-02-06 | 22:22 | DVY14 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 463.0167 | 463.0167 | 1 | No
| 1900837 | 2025-02-06 | 17:38 | 2025-02-06 | 20:30 | DMA23 | DROMANA | Rural Short | Asset Failure | LV | 1 | 171.9167 | 171.9167 | 1 | No
| 1900838 | 2025-02-06 | 17:39 | 2025-02-06 | 19:19 | DMA21 | DROMANA | Urban | Asset Failure | LV | 1 | 100.7333 | 100.7333 | 1 | No
| 1900844 | 2025-02-06 | 18:51 | 2025-02-06 | 20:15 | GW5 | GLEN WAVERLEY | Urban | Animal | Other | 69.68 | 5807.828 | 83.35 | 1 | No
| 1900848 | 2025-02-06 | 19:41 | 2025-02-06 | 20:48 | NO6 | NOTTING HILL | Urban | Third Party | Other | 1 | 67.0667 | 67.0667 | 1 | No
| 1900893 | 2025-03-06 | 5:44 | 2025-03-06 | 7:54 | HGS23 | HASTINGS | Rural Short | Asset Failure | Distribution substation | 2 | 258.0666 | 129.0333 | 1 | No
| 1900887 | 2025-03-06 | 6:35 | 2025-03-06 | 8:14 | BW21 | BURWOOD | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 99.3667 | 99.3667 | 1 | No
| 1900945 | 2025-03-06 | 9:32 | 2025-03-06 | 12:09 | WD26 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 156.3667 | 156.3667 | 1 | No
| 1900960 | 2025-03-06 | 10:20 | 2025-03-06 | 11:30 | EW14 | ELWOOD | Urban | Asset Failure | LV | 1 | 69.3667 | 69.3667 | 1 | No
| 1900973 | 2025-03-06 | 10:41 | 2025-03-06 | 11:40 | EB12 | EAST BURWOOD | Urban | Third Party | Other | 1 | 58.7667 | 58.7667 | 1 | No
| 1900977 | 2025-03-06 | 10:42 | 2025-03-06 | 12:29 | DVY23 | DANDENONG VALLEY | Urban | Asset Failure | LV | 10.56 | 1130.976 | 107.1 | 1 | No
| 1900978 | 2025-03-06 | 10:42 | 2025-03-06 | 12:55 | NO6 | NOTTING HILL | Urban | Asset Failure | LV | 1 | 132.5 | 132.5 | 1 | No
| 1900983 | 2025-03-06 | 10:51 | 2025-03-06 | 11:10 | LWN34 | LANGWARRIN | Urban | Asset Failure | LV | 23 | 422.05 | 18.35 | 1 | No
| 1900900 | 2025-03-06 | 12:27 | 2025-03-06 | 13:40 | EL23 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 73.45 | 73.45 | 1 | No
| 1901032 | 2025-03-06 | 13:14 | 2025-03-06 | 14:45 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 11.55 | 1050.0879 | 90.9167 | 1 | No
| 1901036 | 2025-03-06 | 14:03 | 2025-03-06 | 15:22 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 79 | 79 | 1 | No
| 1901061 | 2025-03-06 | 17:38 | 2025-03-06 | 20:30 | FSH32 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 1 | 171.2333 | 171.2333 | 1 | No
| 1901063 | 2025-03-06 | 18:22 | 2025-03-06 | 19:06 | EM6 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 43.9833 | 43.9833 | 1 | No
| 1901069 | 2025-03-06 | 19:02 | 2025-03-06 | 20:34 | SS12 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 91.3 | 91.3 | 1 | No
| 1901072 | 2025-03-06 | 19:16 | 2025-03-06 | 20:31 | LD4 | LYNDALE | Urban | Unknown | Unknown | 152 | 11359.4616 | 74.7333 | 1 | No
| 1901072 | 2025-03-06 | 20:19 | 2025-03-06 | 20:31 | LD4 | LYNDALE | Urban | Unknown | Unknown | 106 | 1332.0702 | 12.5667 | 1 | No
| 1901086 | 2025-03-06 | 20:21 | 2025-03-06 | 21:19 | FTN11 | FRANKSTON | Urban | Asset Failure | HV | 330 | 19239 | 58.3 | 1 | No
| 1901091 | 2025-03-06 | 20:21 | 2025-03-06 | 21:38 | FTN11 | FRANKSTON | Urban | Unknown | Unknown | 851 | 65697.2 | 77.2 | 1 | No
| 1901087 | 2025-03-06 | 20:31 | 2025-03-06 | 23:26 | NB36 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 174.9833 | 174.9833 | 1 | No
| 1901105 | 2025-04-06 | 3:04 | 2025-04-06 | 4:06 | GW1 | GLEN WAVERLEY | Urban | Unknown | Unknown | 64 | 3956.2688 | 61.8167 | 1 | No
| 1901105 | 2025-04-06 | 3:04 | 2025-04-06 | 4:31 | GW1 | GLEN WAVERLEY | Urban | Unknown | Unknown | 229 | 19888.65 | 86.85 | 2 | No
| 1901105 | 2025-04-06 | 3:04 | 2025-04-06 | 4:38 | GW1 | GLEN WAVERLEY | Urban | Unknown | Unknown | 34 | 3189.2 | 93.8 | 3 | No
| 1901105 | 2025-04-06 | 3:04 | 2025-04-06 | 5:15 | GW1 | GLEN WAVERLEY | Urban | Unknown | Unknown | 160 | 20957.328 | 130.9833 | 4 | No
| 1901122 | 2025-04-06 | 6:49 | 2025-04-06 | 8:15 | DVY13 | DANDENONG VALLEY | Urban | Third Party | Other | 1 | 85.05 | 85.05 | 1 | No
| 1900870 | 2025-04-06 | 8:32 | 2025-04-06 | 9:55 | LD4 | LYNDALE | Urban | Overloads |  | 1 | 83.8833 | 83.8833 | 1 | No
| 1901250 | 2025-04-06 | 10:38 | 2025-04-06 | 10:44 | EB31 | EAST BURWOOD | Urban | Asset Failure | HV | 43 | 258 | 6 | 1 | No
| 1901250 | 2025-04-06 | 10:38 | 2025-04-06 | 10:44 | NW14 | NUNAWADING | Urban | Asset Failure | HV | 12 | 72 | 6 | 1 | No
| 1901296 | 2025-04-06 | 12:37 | 2025-04-06 | 13:45 | DC10 | DONCASTER | Urban | Asset Failure | LV | 13.53 | 916.4315 | 67.7333 | 1 | No
| 1901017 | 2025-04-06 | 13:49 | 2025-04-06 | 15:32 | BW33 | BURWOOD | Urban | Asset Failure | LV | 1 | 103.4333 | 103.4333 | 1 | No
| 1901329 | 2025-04-06 | 13:55 | 2025-04-06 | 17:34 | MC32 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 218.6833 | 218.6833 | 1 | No
| 1901353 | 2025-04-06 | 14:57 | 2025-04-06 | 16:28 | OR32 | ORMOND | Urban | Asset Failure | HV | 37 | 3354.6679 | 90.6667 | 1 | No
| 1901353 | 2025-04-06 | 14:57 | 2025-04-06 | 16:33 | OR32 | ORMOND | Urban | Asset Failure | HV | 37 | 3543.9821 | 95.7833 | 2 | No
| 1901353 | 2025-04-06 | 14:57 | 2025-04-06 | 16:40 | OR32 | ORMOND | Urban | Asset Failure | HV | 46 | 4751.0318 | 103.2833 | 3 | No
| 1901369 | 2025-04-06 | 16:35 | 2025-04-06 | 17:58 | BW21 | BURWOOD | Urban | Asset Failure | LV | 1 | 83.0833 | 83.0833 | 1 | No
| 1901136 | 2025-04-06 | 16:49 | 2025-04-06 | 18:58 | M11 | MENTONE | Urban | Asset Failure | LV | 1 | 129.6333 | 129.6333 | 1 | No
| 1901392 | 2025-04-06 | 19:58 | 2025-04-06 | 21:15 | DC10 | DONCASTER | Urban | Asset Failure | LV | 1 | 77.2833 | 77.2833 | 1 | No
| 1901404 | 2025-05-06 | 2:47 | 2025-05-06 | 5:00 | DVY23 | DANDENONG VALLEY | Urban | Overloads |  | 16 | 2126.1328 | 132.8833 | 1 | No
| 1901406 | 2025-05-06 | 3:01 | 2025-05-06 | 3:08 | CFD14 | CAULFIELD | Urban | Asset Failure | HV | 1106 | 7465.5 | 6.75 | 1 | No
| 1901406 | 2025-05-06 | 3:01 | 2025-05-06 | 3:15 | CFD14 | CAULFIELD | Urban | Asset Failure | HV | 712 | 10276.5096 | 14.4333 | 2 | No
| 1901406 | 2025-05-06 | 3:01 | 2025-05-06 | 3:57 | CFD14 | CAULFIELD | Urban | Asset Failure | HV | 772 | 42910.3076 | 55.5833 | 3 | No
| 1901406 | 2025-05-06 | 3:01 | 2025-05-06 | 3:57 | CFD14 | CAULFIELD | Urban | Asset Failure | HV | 90 | 5083.497 | 56.4833 | 4 | No
| 1901428 | 2025-05-06 | 8:30 | 2025-05-06 | 10:00 | GW3 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 89.7 | 89.7 | 1 | No
| 1901433 | 2025-05-06 | 8:42 | 2025-05-06 | 11:13 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 150.8 | 150.8 | 1 | No
| 1901436 | 2025-05-06 | 8:53 | 2025-05-06 | 9:38 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 1 | 44.2333 | 44.2333 | 1 | No
| 1901448 | 2025-05-06 | 9:13 | 2025-05-06 | 10:42 | NP33 | NOBLE PARK | Urban | Overloads |  | 1 | 89.8167 | 89.8167 | 1 | No
| 1901481 | 2025-05-06 | 10:46 | 2025-05-06 | 11:21 | RWT12 | RINGWOOD | Urban | Asset Failure | LV | 1 | 35.4 | 35.4 | 1 | No
| 1901655 | 2025-05-06 | 15:21 | 2025-05-06 | 17:30 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 128.05 | 128.05 | 1 | No
| 1901666 | 2025-05-06 | 16:52 | 2025-05-06 | 22:40 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 1 | 347.3167 | 347.3167 | 1 | No
| 1901678 | 2025-05-06 | 17:51 | 2025-05-06 | 20:58 | CRM35 | CARRUM | Urban | Asset Failure | LV | 11.88 | 2214.0364 | 186.3667 | 1 | No
| 1901679 | 2025-05-06 | 17:57 | 2025-05-06 | 20:56 | DN11 | DANDENONG | Urban | Asset Failure | LV | 1 | 179.1833 | 179.1833 | 1 | No
| 1901684 | 2025-05-06 | 18:44 | 2025-05-06 | 20:30 | STO21 | SORRENTO | Rural Short | Overloads |  | 24.09 | 2544.3063 | 105.6167 | 1 | No
| 1901695 | 2025-05-06 | 19:30 | 2025-05-06 | 21:59 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 149.5833 | 149.5833 | 1 | No
| 1901697 | 2025-05-06 | 19:45 | 2025-05-06 | 23:05 | RBD12 | ROSEBUD | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 199.4167 | 199.4167 | 1 | No
| 1901705 | 2025-05-06 | 21:06 | 2025-05-06 | 22:28 | EW8 | ELWOOD | Urban | Overloads |  | 1 | 82.7667 | 82.7667 | 1 | No
| 1901709 | 2025-05-06 | 21:21 | 2025-06-06 | 0:02 | NP14 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 160.7667 | 160.7667 | 1 | No
| 1901711 | 2025-05-06 | 22:13 | 2025-05-06 | 22:50 | EW1 | ELWOOD | Urban | Network Business | Switching and protection error | 84 | 3084.2028 | 36.7167 | 1 | No
| 1901711 | 2025-05-06 | 22:13 | 2025-05-06 | 22:50 | SK1 | ST. KILDA | Urban | Network Business | Switching and protection error | 38 | 1395.2346 | 36.7167 | 1 | No
| 1901719 | 2025-06-06 | 1:39 | 2025-06-06 | 7:58 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 378.4167 | 378.4167 | 1 | No
| 1901722 | 2025-06-06 | 3:36 | 2025-06-06 | 5:00 | RBD24 | ROSEBUD | Urban | Animal | Animal impact | 48.24 | 4009.5496 | 83.1167 | 1 | No
| 1901814 | 2025-06-06 | 9:50 | 2025-06-06 | 11:34 | RWT35 | RINGWOOD | Urban | Animal | Animal impact | 2.68 | 276.3528 | 103.1167 | 1 | No
| 1901818 | 2025-06-06 | 9:59 | 2025-06-06 | 16:30 | LD33 | LYNDALE | Urban | Third Party | Other | 2 | 783.2666 | 391.6333 | 1 | No
| 1901839 | 2025-06-06 | 10:44 | 2025-06-06 | 12:25 | DVY23 | DANDENONG VALLEY | Urban | Unknown | Unknown | 5.28 | 529.2318 | 100.2333 | 1 | No
| 1901844 | 2025-06-06 | 10:49 | 2025-06-06 | 16:39 | LD33 | LYNDALE | Urban | Third Party | Vehicle Impact | 1 | 349.9833 | 349.9833 | 1 | No
| 1901861 | 2025-06-06 | 11:19 | 2025-06-06 | 13:20 | HGS22 | HASTINGS | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 120.5167 | 120.5167 | 1 | No
| 1901865 | 2025-06-06 | 11:24 | 2025-06-06 | 12:54 | DC8 | DONCASTER | Urban | Other | XXX | 1 | 89.8833 | 89.8833 | 1 | No
| 1901989 | 2025-06-06 | 19:09 | 2025-06-06 | 20:10 | BU25 | BULLEEN | Urban | Overloads |  | 23.8 | 1446.2475 | 60.7667 | 1 | No
| 1902010 | 2025-07-06 | 5:19 | 2025-07-06 | 6:35 | DSH34 | DANDENONG SOUTH | Urban | Asset Failure | LV | 21.12 | 1585.4087 | 75.0667 | 1 | No
| 1902044 | 2025-07-06 | 9:26 | 2025-07-06 | 13:18 | DVY23 | DANDENONG VALLEY | Urban | Overloads |  | 7 | 1626.45 | 232.35 | 1 | No
| 1902044 | 2025-07-06 | 9:26 | 2025-07-06 | 13:18 | DVY23 | DANDENONG VALLEY | Urban | Overloads |  | 9 | 2091.8997 | 232.4333 | 2 | No
| 1902042 | 2025-07-06 | 9:28 | 2025-07-06 | 10:04 | FSH32 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 5 | 180.5835 | 36.1167 | 1 | No
| 1902042 | 2025-07-06 | 9:28 | 2025-07-06 | 10:17 | FSH32 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 298 | 14592.0766 | 48.9667 | 2 | No
| 1902042 | 2025-07-06 | 9:28 | 2025-07-06 | 10:29 | FSH32 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 207 | 12727.0431 | 61.4833 | 3 | No
| 1902042 | 2025-07-06 | 9:28 | 2025-07-06 | 10:34 | FSH32 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 199 | 13140.6267 | 66.0333 | 4 | No
| 1902042 | 2025-07-06 | 9:28 | 2025-07-06 | 10:35 | FSH32 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 484 | 32637.7172 | 67.4333 | 5 | No
| 1902042 | 2025-07-06 | 9:28 | 2025-07-06 | 10:39 | FSH32 | FRANKSTON SOUTH | Rural Short | Unknown | Unknown | 315 | 22328.2395 | 70.8833 | 6 | No
| 1902059 | 2025-07-06 | 10:25 | 2025-07-06 | 13:33 | DMA14 | DROMANA | Urban | Asset Failure | LV | 41 | 7703.9 | 187.9 | 1 | No
| 1902093 | 2025-07-06 | 13:46 | 2025-07-06 | 15:27 | DMA23 | DROMANA | Rural Short | Asset Failure | LV | 1 | 100.3 | 100.3 | 1 | No
| 1902106 | 2025-07-06 | 15:23 | 2025-07-06 | 17:52 | CRM24 | CARRUM | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 148.8167 | 148.8167 | 1 | No
| 1902068 | 2025-07-06 | 16:48 | 2025-07-06 | 17:51 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 63 | 63 | 1 | No
| 1902132 | 2025-07-06 | 19:22 | 2025-08-06 | 2:40 | DSH21 | DANDENONG SOUTH | Urban | Third Party | Other | 16 | 7001.3328 | 437.5833 | 1 | No
| 1902138 | 2025-07-06 | 20:16 | 2025-07-06 | 21:29 | M23 | MENTONE | Urban | Asset Failure | LV | 1 | 72.25 | 72.25 | 1 | No
| 1902139 | 2025-07-06 | 20:55 | 2025-07-06 | 22:00 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 65 | 65 | 1 | No
| 1902152 | 2025-08-06 | 6:17 | 2025-08-06 | 9:01 | STO14 | SORRENTO | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 163.5 | 163.5 | 1 | No
| 1902165 | 2025-08-06 | 8:36 | 2025-08-06 | 10:30 | DVY13 | DANDENONG VALLEY | Urban | Third Party | Other | 2 | 226.8 | 113.4 | 1 | No
| 1902181 | 2025-08-06 | 11:47 | 2025-08-06 | 13:56 | FTN13 | FRANKSTON | Urban | Third Party | Vehicle Impact | 1 | 129.75 | 129.75 | 1 | No
| 1902183 | 2025-08-06 | 12:15 | 2025-08-06 | 15:00 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 164.6667 | 164.6667 | 1 | No
| 1902175 | 2025-08-06 | 12:31 | 2025-08-06 | 16:24 | STO14 | SORRENTO | Rural Short | Unknown | Unknown | 1 | 233.4833 | 233.4833 | 1 | No
| 1902200 | 2025-08-06 | 13:14 | 2025-08-06 | 15:35 | HGS23 | HASTINGS | Rural Short | Asset Failure | HV | 2 | 281.0334 | 140.5167 | 1 | No
| 1902213 | 2025-08-06 | 18:08 | 2025-08-06 | 21:43 | SV33 | SPRINGVALE | Urban | Overloads |  | 1 | 215.45 | 215.45 | 1 | No
| 1902214 | 2025-08-06 | 18:32 | 2025-08-06 | 19:36 | RBD13 | ROSEBUD | Urban | Asset Failure | LV | 1 | 64.0833 | 64.0833 | 1 | No
| 1902220 | 2025-08-06 | 22:13 | 2025-08-06 | 23:45 | OAK22 | OAKLEIGH | Urban | Third Party | Vehicle Impact | 93 | 8490.9 | 91.3 | 1 | No
| 1902221 | 2025-08-06 | 22:42 | 2025-08-06 | 23:45 | CRM22 | CARRUM | Urban | Animal | Animal impact | 103 | 6458.1 | 62.7 | 1 | No
| 1902228 | 2025-09-06 | 1:12 | 2025-09-06 | 1:26 | OAK22 | OAKLEIGH | Urban | Third Party | Vehicle Impact | 22 | 301.7674 | 13.7167 | 1 | No
| 1902238 | 2025-09-06 | 7:22 | 2025-09-06 | 10:55 | STO22 | SORRENTO | Urban | Asset Failure | LV | 1 | 212.85 | 212.85 | 1 | No
| 1902226 | 2025-09-06 | 8:20 | 2025-09-06 | 11:15 | EW2 | ELWOOD | Urban | Asset Failure | LV | 1 | 175 | 175 | 1 | No
| 1902262 | 2025-09-06 | 10:18 | 2025-09-06 | 13:15 | MTN21 | MORNINGTON | Urban | Asset Failure | LV | 1 | 176.7833 | 176.7833 | 1 | No
| 1902291 | 2025-09-06 | 11:18 | 2025-09-06 | 14:37 | DC1 | DONCASTER | Urban | Asset Failure | LV | 2 | 396.4334 | 198.2167 | 1 | No
| 1902241 | 2025-09-06 | 11:22 | 2025-09-06 | 13:15 | DMA21 | DROMANA | Urban | Asset Failure | LV | 1 | 113 | 113 | 1 | No
| 1902258 | 2025-09-06 | 12:34 | 2025-09-06 | 16:19 | DC12 | DONCASTER | Urban | Asset Failure | LV | 1 | 225.7167 | 225.7167 | 1 | No
| 1902303 | 2025-09-06 | 15:15 | 2025-09-06 | 17:15 | KBH34 | KEYSBOROUGH | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 120 | 120 | 1 | No
| 1902322 | 2025-09-06 | 18:00 | 2025-09-06 | 18:54 | MR15 | MOORABBIN | Urban | Asset Failure | HV | 49.17 | 2614.2066 | 53.1667 | 1 | No
| 1902325 | 2025-09-06 | 18:02 | 2025-09-06 | 20:04 | OR23 | ORMOND | Urban | Unknown | Unknown | 78 | 9480.9 | 121.55 | 1 | No
| 1902318 | 2025-09-06 | 18:07 | 2025-09-06 | 18:41 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 1 | 34.15 | 34.15 | 1 | No
| 1902341 | 2025-09-06 | 19:08 | 2025-09-06 | 20:28 | SS24 | SPRINGVALE SOUTH | Urban | Third Party | Other | 9 | 711.6003 | 79.0667 | 1 | No
| 1902351 | 2025-09-06 | 22:29 | 2025-09-06 | 22:55 | BW32 | BURWOOD | Urban | Asset Failure | LV | 1 | 26 | 26 | 1 | No
| 1902353 | 2025-09-06 | 22:51 | 2025-10-06 | 0:13 | CRM14 | CARRUM | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 82.1 | 82.1 | 1 | No
| 1902356 | 2025-10-06 | 0:30 | 2025-10-06 | 1:06 | DMA21 | DROMANA | Urban | Asset Failure | LV | 1 | 36.9833 | 36.9833 | 1 | No
| 1902365 | 2025-10-06 | 1:53 | 2025-10-06 | 2:55 | NP14 | NOBLE PARK | Urban | Animal | Animal impact | 64.99 | 3966.5542 | 61.0333 | 1 | No
| 1902394 | 2025-10-06 | 8:02 | 2025-10-06 | 10:15 | FSH21 | FRANKSTON SOUTH | Rural Short | Animal | Animal impact | 12.06 | 1592.3216 | 132.0333 | 1 | No
| 1902397 | 2025-10-06 | 8:11 | 2025-10-06 | 10:58 | NW22 | NUNAWADING | Urban | Third Party | Other | 1 | 167.5333 | 167.5333 | 1 | No
| 1902431 | 2025-10-06 | 9:03 | 2025-10-06 | 12:09 | SV16 | SPRINGVALE | Urban | Asset Failure | LV | 5 | 932.3335 | 186.4667 | 1 | No
| 1902468 | 2025-10-06 | 10:10 | 2025-10-06 | 14:17 | BH23 | BOX HILL | Urban | Asset Failure | LV | 5 | 1233.25 | 246.65 | 1 | No
| 1902377 | 2025-10-06 | 10:44 | 2025-10-06 | 12:24 | MTN22 | MORNINGTON | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 100.1 | 100.1 | 1 | No
| 1902518 | 2025-10-06 | 11:22 | 2025-10-06 | 13:45 | SR26 | SANDRINGHAM | Urban | Unknown | Unknown | 1 | 142.6333 | 142.6333 | 1 | No
| 1902551 | 2025-10-06 | 14:00 | 2025-10-06 | 17:10 | MR13 | MOORABBIN | Urban | Asset Failure | LV | 1 | 190 | 190 | 1 | No
| 1902589 | 2025-10-06 | 14:03 | 2025-11-06 | 1:34 | NB35 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 690.5 | 690.5 | 1 | No
| 1902637 | 2025-10-06 | 16:59 | 2025-10-06 | 18:35 | MC21 | MORDIALLOC | Urban | Asset Failure | LV | 10.56 | 1011.9996 | 95.8333 | 1 | No
| 1902633 | 2025-10-06 | 17:21 | 2025-10-06 | 20:21 | RWT34 | RINGWOOD | Urban | Overloads |  | 1 | 180 | 180 | 1 | No
| 1902640 | 2025-10-06 | 17:21 | 2025-10-06 | 18:28 | NW11 | NUNAWADING | Urban | Unknown | Unknown | 1 | 66.1333 | 66.1333 | 1 | No
| 1902647 | 2025-10-06 | 17:54 | 2025-10-06 | 19:54 | OR24 | ORMOND | Urban | Asset Failure | LV | 32.67 | 3915.4995 | 119.85 | 1 | No
| 1902655 | 2025-10-06 | 18:15 | 2025-10-06 | 20:07 | DN10 | DANDENONG | Urban | Overloads |  | 53.46 | 5975.9352 | 111.7833 | 1 | No
| 1902681 | 2025-10-06 | 20:04 | 2025-10-06 | 20:51 | FSH22 | FRANKSTON SOUTH | Urban | Overloads |  | 45.54 | 2135.0655 | 46.8833 | 1 | No
| 1902688 | 2025-10-06 | 21:08 | 2025-10-06 | 21:16 | NP16 | NOBLE PARK | Urban | Asset Failure | Distribution substation | 65.34 | 484.6072 | 7.4167 | 1 | No
| 1902687 | 2025-10-06 | 21:22 | 2025-10-06 | 22:33 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 1 | 71.0667 | 71.0667 | 1 | No
| 1902700 | 2025-11-06 | 5:00 | 2025-11-06 | 8:07 | LWN24 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 187.7 | 187.7 | 1 | No
| 1902701 | 2025-11-06 | 6:00 | 2025-11-06 | 7:03 | GW11 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 63.8 | 63.8 | 1 | No
| 1902712 | 2025-11-06 | 7:14 | 2025-11-06 | 8:13 | HT9 | HEATHERTON | Urban | Third Party | Other | 145 | 8535.6715 | 58.8667 | 1 | No
| 1902712 | 2025-11-06 | 7:14 | 2025-11-06 | 8:17 | HT9 | HEATHERTON | Urban | Third Party | Other | 126 | 7919.1 | 62.85 | 2 | No
| 1902712 | 2025-11-06 | 7:14 | 2025-11-06 | 8:23 | HT9 | HEATHERTON | Urban | Third Party | Other | 34 | 2355.6322 | 69.2833 | 3 | No
| 1902712 | 2025-11-06 | 7:14 | 2025-11-06 | 9:30 | HT9 | HEATHERTON | Urban | Third Party | Other | 56 | 7618.8 | 136.05 | 4 | No
| 1902712 | 2025-11-06 | 7:14 | 2025-11-06 | 9:34 | HT9 | HEATHERTON | Urban | Third Party | Other | 1 | 139.9 | 139.9 | 5 | No
| 1902719 | 2025-11-06 | 7:46 | 2025-11-06 | 8:57 | DC8 | DONCASTER | Urban | Overloads |  | 1 | 71.5667 | 71.5667 | 1 | No
| 1902812 | 2025-11-06 | 9:53 | 2025-11-06 | 10:29 | BC11 | BALACLAVA | Urban | Asset Failure | LV | 1 | 36.55 | 36.55 | 1 | No
| 1902825 | 2025-11-06 | 10:27 | 2025-11-06 | 11:11 | BW22 | BURWOOD | Urban | Third Party | Other | 1 | 44.2 | 44.2 | 1 | No
| 1902863 | 2025-11-06 | 11:18 | 2025-11-06 | 14:10 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 95 | 16317.8365 | 171.7667 | 1 | No
| 1902874 | 2025-11-06 | 11:29 | 2025-11-06 | 14:10 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 20 | 3210 | 160.5 | 1 | No
| 1902924 | 2025-11-06 | 12:48 | 2025-11-06 | 14:16 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 88.05 | 88.05 | 1 | No
| 1902737 | 2025-11-06 | 12:51 | 2025-11-06 | 14:30 | NP16 | NOBLE PARK | Urban | Overloads |  | 1 | 99 | 99 | 1 | No
| 1902988 | 2025-11-06 | 17:03 | 2025-11-06 | 17:20 | NP36 | NOBLE PARK | Urban | Asset Failure | LV | 3.63 | 61.71 | 17 | 1 | No
| 1903008 | 2025-11-06 | 17:38 | 2025-11-06 | 20:03 | MGE31 | MULGRAVE | Urban | Overloads |  | 15.18 | 2191.233 | 144.35 | 1 | No
| 1902703 | 2025-11-06 | 17:59 | 2025-11-06 | 19:08 | HGS31 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 69.7833 | 69.7833 | 1 | No
| 1903026 | 2025-11-06 | 18:52 | 2025-11-06 | 21:36 | EW12 | ELWOOD | Urban | Overloads |  | 1 | 164.4167 | 164.4167 | 1 | No
| 1903035 | 2025-11-06 | 19:29 | 2025-11-06 | 20:39 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 2.4 | 169.1599 | 70.4833 | 1 | No
| 1903061 | 2025-11-06 | 20:12 | 2025-11-06 | 21:08 | HGS33 | HASTINGS | Rural Short | Third Party | Other | 1 | 55.9167 | 55.9167 | 1 | No
| 1903060 | 2025-11-06 | 20:15 | 2025-11-06 | 22:07 | EM11 | EAST MALVERN | Urban | Overloads |  | 1 | 112 | 112 | 1 | No
| 1903077 | 2025-12-06 | 3:54 | 2025-12-06 | 8:31 | DC10 | DONCASTER | Urban | Unknown | Unknown | 1 | 276.6167 | 276.6167 | 1 | No
| 1903089 | 2025-12-06 | 7:14 | 2025-12-06 | 8:01 | EB11 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 47.2 | 47.2 | 1 | No
| 1903110 | 2025-12-06 | 8:23 | 2025-12-06 | 9:21 | GW11 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 58.5 | 58.5 | 1 | No
| 1903136 | 2025-12-06 | 8:43 | 2025-12-06 | 10:14 | DC4 | DONCASTER | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 90.8667 | 90.8667 | 1 | No
| 1903202 | 2025-12-06 | 10:33 | 2025-12-06 | 11:53 | RWT12 | RINGWOOD | Urban | Asset Failure | LV | 1 | 80.3667 | 80.3667 | 1 | No
| 1903197 | 2025-12-06 | 11:14 | 2025-12-06 | 12:33 | EM7 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 79.7667 | 79.7667 | 1 | No
| 1903284 | 2025-12-06 | 12:25 | 2025-12-06 | 13:12 | EM6 | EAST MALVERN | Urban | Network Business | Switching and protection error | 1 | 46.8 | 46.8 | 1 | No
| 1903288 | 2025-12-06 | 12:32 | 2025-12-06 | 13:50 | M32 | MENTONE | Urban | Asset Failure | LV | 1 | 77.75 | 77.75 | 1 | No
| 1903296 | 2025-12-06 | 12:58 | 2025-12-06 | 17:54 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 107 | 31725.5 | 296.5 | 1 | No
| 1903071 | 2025-12-06 | 16:22 | 2025-12-06 | 17:39 | OAK23 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 77.0167 | 77.0167 | 1 | No
| 1903376 | 2025-12-06 | 16:55 | 2025-12-06 | 18:09 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 73.0667 | 73.0667 | 1 | No
| 1903387 | 2025-12-06 | 17:46 | 2025-12-06 | 18:49 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 2 | 125.9334 | 62.9667 | 1 | No
| 1903394 | 2025-12-06 | 19:31 | 2025-12-06 | 20:09 | BU25 | BULLEEN | Urban | Overloads |  | 15.3 | 575.28 | 37.6 | 1 | No
| 1903404 | 2025-12-06 | 20:15 | 2025-12-06 | 22:09 | LD7 | LYNDALE | Urban | Overloads |  | 40.26 | 4602.3903 | 114.3167 | 1 | No
| 1903406 | 2025-12-06 | 20:32 | 2025-12-06 | 21:20 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 34.98 | 1665.6322 | 47.6167 | 1 | No
| 1903417 | 2025-12-06 | 21:26 | 13/06/2025 | 9:38 | NB34 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 732.0667 | 732.0667 | 1 | No
| 1903440 | 2025-12-06 | 23:37 | 13/06/2025 | 0:58 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 3 | 240.6 | 80.2 | 1 | No
| 1903474 | 13/06/2025 | 6:01 | 13/06/2025 | 6:59 | MGE32 | MULGRAVE | Urban | Animal | Animal impact | 46.23 | 2668.243 | 57.7167 | 1 | No
| 1903483 | 13/06/2025 | 7:29 | 13/06/2025 | 8:21 | OR25 | ORMOND | Urban | Asset Failure | LV | 1 | 52.1167 | 52.1167 | 1 | No
| 1903593 | 13/06/2025 | 9:37 | 13/06/2025 | 13:29 | CM13 | CHELTENHAM | Urban | Overloads |  | 4.95 | 1147.8223 | 231.8833 | 1 | No
| 1903607 | 13/06/2025 | 10:07 | 13/06/2025 | 11:22 | EW8 | ELWOOD | Urban | Asset Failure | LV | 1 | 75.5833 | 75.5833 | 1 | No
| 1903614 | 13/06/2025 | 10:26 | 13/06/2025 | 12:20 | OAK33 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 113.8667 | 113.8667 | 1 | No
| 1903645 | 13/06/2025 | 11:12 | 13/06/2025 | 13:15 | GW6 | GLEN WAVERLEY | Urban | Unknown | Unknown | 1 | 122.3333 | 122.3333 | 1 | No
| 1903670 | 13/06/2025 | 12:03 | 13/06/2025 | 21:10 | RBD13 | ROSEBUD | Urban | Asset Failure | HV | 16 | 8744 | 546.5 | 1 | No
| 1903712 | 13/06/2025 | 13:21 | 13/06/2025 | 16:10 | CFD13 | CAULFIELD | Urban | Asset Failure | LV | 10.23 | 1720.1745 | 168.15 | 1 | No
| 1903723 | 13/06/2025 | 13:44 | 13/06/2025 | 15:30 | NP12 | NOBLE PARK | Urban | Animal | Animal impact | 24.12 | 2547.8752 | 105.6333 | 1 | No
| 1903723 | 13/06/2025 | 13:44 | 13/06/2025 | 15:35 | NP12 | NOBLE PARK | Urban | Animal | Animal impact | 40.87 | 4515.4525 | 110.4833 | 2 | No
| 1903758 | 13/06/2025 | 15:14 | 13/06/2025 | 16:52 | DC3 | DONCASTER | Urban | Asset Failure | LV | 1 | 98.3167 | 98.3167 | 1 | No
| 1903771 | 13/06/2025 | 16:03 | 13/06/2025 | 21:00 | SR35 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 296.75 | 296.75 | 1 | No
| 1903743 | 13/06/2025 | 18:05 | 13/06/2025 | 22:50 | EL33 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 285.1833 | 285.1833 | 1 | No
| 1903797 | 13/06/2025 | 18:20 | 13/06/2025 | 23:23 | STO22 | SORRENTO | Urban | Asset Failure | LV | 2 | 606.7334 | 303.3667 | 1 | No
| 1903804 | 13/06/2025 | 18:57 | 13/06/2025 | 20:23 | BU25 | BULLEEN | Urban | Overloads |  | 15.64 | 1332.528 | 85.2 | 1 | No
| 1903812 | 13/06/2025 | 19:33 | 13/06/2025 | 20:45 | SV32 | SPRINGVALE | Urban | Asset Failure | LV | 24.75 | 1762.6133 | 71.2167 | 1 | No
| 1903515 | 13/06/2025 | 19:45 | 13/06/2025 | 23:59 | MTN34 | MORNINGTON | Urban | Asset Failure | LV | 1 | 254.5833 | 254.5833 | 1 | No
| 1903817 | 13/06/2025 | 20:28 | 14/06/2025 | 0:35 | STO21 | SORRENTO | Rural Short | Asset Failure | LV | 1.95 | 481.065 | 246.7 | 1 | No
| 1903822 | 13/06/2025 | 21:21 | 14/06/2025 | 0:40 | FSH31 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 199.9 | 199.9 | 1 | No
| 1903827 | 13/06/2025 | 21:38 | 13/06/2025 | 22:53 | GW3 | GLEN WAVERLEY | Urban | Asset Failure | LV | 29.37 | 2194.4295 | 74.7167 | 1 | No
| 1903831 | 13/06/2025 | 22:08 | 14/06/2025 | 1:35 | MC12 | MORDIALLOC | Urban | Overloads |  | 4 | 828 | 207 | 1 | No
| 1903833 | 13/06/2025 | 22:33 | 14/06/2025 | 0:53 | SV32 | SPRINGVALE | Urban | Overloads |  | 24.75 | 3453.8625 | 139.55 | 1 | No
| 1903840 | 14/06/2025 | 0:19 | 14/06/2025 | 2:54 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 5 | 773.4165 | 154.6833 | 1 | No
| 1903864 | 14/06/2025 | 8:26 | 14/06/2025 | 10:03 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 97.3333 | 97.3333 | 1 | No
| 1903848 | 14/06/2025 | 9:12 | 14/06/2025 | 10:46 | EB32 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 94.3 | 94.3 | 1 | No
| 1903920 | 14/06/2025 | 12:31 | 14/06/2025 | 16:30 | STO21 | SORRENTO | Rural Short | Network Business | Network Error | 1 | 238.4 | 238.4 | 1 | No
| 1903816 | 14/06/2025 | 12:43 | 14/06/2025 | 16:10 | NP36 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 207.0333 | 207.0333 | 1 | No
| 1903943 | 14/06/2025 | 14:05 | 14/06/2025 | 15:18 | DN22 | DANDENONG | Urban | Animal | Animal impact | 109.21 | 7955.9485 | 72.85 | 1 | No
| 1903953 | 14/06/2025 | 15:15 | 14/06/2025 | 18:42 | BW34 | BURWOOD | Urban | Third Party | Vehicle Impact | 91 | 18833.9697 | 206.9667 | 1 | No
| 1903946 | 14/06/2025 | 17:06 | 14/06/2025 | 18:37 | DC3 | DONCASTER | Urban | Overloads |  | 1 | 91.8167 | 91.8167 | 1 | No
| 1903975 | 14/06/2025 | 17:27 | 14/06/2025 | 19:15 | RBD12 | ROSEBUD | Rural Short | Asset Failure | LV | 49 | 5293.6317 | 108.0333 | 1 | No
| 1903962 | 14/06/2025 | 17:52 | 15/06/2025 | 0:45 | FTN25 | FRANKSTON | Urban | Overloads |  | 1 | 413.1667 | 413.1667 | 1 | No
| 1903981 | 14/06/2025 | 18:34 | 14/06/2025 | 23:48 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 313.1833 | 313.1833 | 1 | No
| 1903987 | 14/06/2025 | 19:10 | 14/06/2025 | 20:20 | CDA11 | CLARINDA | Urban | Asset Failure | LV | 1 | 70 | 70 | 1 | No
| 1903988 | 14/06/2025 | 20:26 | 15/06/2025 | 1:42 | CFD15 | CAULFIELD | Urban | Asset Failure | LV | 1 | 316.85 | 316.85 | 1 | No
| 1903998 | 15/06/2025 | 0:02 | 15/06/2025 | 8:44 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 521.4667 | 521.4667 | 1 | No
| 1904002 | 15/06/2025 | 0:07 | 15/06/2025 | 2:38 | DC2 | DONCASTER | Urban | Animal | Animal impact | 38.86 | 5859.439 | 150.7833 | 1 | No
| 1904021 | 15/06/2025 | 6:57 | 15/06/2025 | 8:31 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 8 | 749.6 | 93.7 | 1 | No
| 1904034 | 15/06/2025 | 8:25 | 15/06/2025 | 9:38 | STO22 | SORRENTO | Urban | Asset Failure | LV | 10.89 | 793.1546 | 72.8333 | 1 | No
| 1904010 | 15/06/2025 | 8:42 | 15/06/2025 | 9:43 | OR32 | ORMOND | Urban | Asset Failure | LV | 1 | 61 | 61 | 1 | No
| 1904041 | 15/06/2025 | 8:55 | 15/06/2025 | 12:51 | DC1 | DONCASTER | Urban | Asset Failure | Distribution substation | 7.4 | 1744.3036 | 235.7167 | 1 | No
| 1904049 | 15/06/2025 | 10:30 | 15/06/2025 | 13:20 | NB23 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 169.2 | 169.2 | 1 | No
| 1904040 | 15/06/2025 | 11:55 | 15/06/2025 | 15:40 | OR33 | ORMOND | Urban | Asset Failure | LV | 1 | 225 | 225 | 1 | No
| 1904062 | 15/06/2025 | 12:22 | 15/06/2025 | 14:26 | EM5 | EAST MALVERN | Urban | Asset Failure | LV | 1 | 123.7 | 123.7 | 1 | No
| 1904082 | 15/06/2025 | 17:12 | 15/06/2025 | 19:50 | DN22 | DANDENONG | Urban | Asset Failure | LV | 2 | 315.4334 | 157.7167 | 1 | No
| 1904089 | 15/06/2025 | 19:12 | 15/06/2025 | 21:22 | LWN24 | LANGWARRIN | Urban | Asset Failure | LV | 28.71 | 3745.2195 | 130.45 | 1 | No
| 1904129 | 15/06/2025 | 21:03 | 16/06/2025 | 7:28 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 17 | 10625.2839 | 625.0167 | 1 | No
| 1904129 | 15/06/2025 | 21:03 | 16/06/2025 | 7:28 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 61 | 38134.15 | 625.15 | 2 | No
| 1904129 | 15/06/2025 | 21:03 | 16/06/2025 | 10:00 | SV33 | SPRINGVALE | Urban | Asset Failure | LV | 85 | 66018.0805 | 776.6833 | 3 | No
| 1904171 | 15/06/2025 | 22:23 | 16/06/2025 | 8:04 | MTN24 | MORNINGTON | Rural Short | Weather |  | 1 | 580.4833 | 580.4833 | 1 | No
| 1904188 | 16/06/2025 | 9:04 | 16/06/2025 | 10:35 | OR34 | ORMOND | Urban | Asset Failure | LV | 1 | 91.6333 | 91.6333 | 1 | No
| 1904286 | 16/06/2025 | 9:52 | 16/06/2025 | 11:25 | RBD21 | ROSEBUD | Rural Short | Asset Failure | LV | 1 | 93.1167 | 93.1167 | 1 | No
| 1904305 | 16/06/2025 | 10:25 | 16/06/2025 | 11:30 | OAK35 | OAKLEIGH | Urban | Asset Failure | LV | 1 | 64.3333 | 64.3333 | 1 | No
| 1904557 | 16/06/2025 | 13:07 | 16/06/2025 | 14:09 | GW7 | GLEN WAVERLEY | Urban | Asset Failure | LV | 10.56 | 644.688 | 61.05 | 1 | No
| 1904567 | 16/06/2025 | 13:22 | 16/06/2025 | 15:23 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 27 | 3250.3491 | 120.3833 | 1 | No
| 1904567 | 16/06/2025 | 13:22 | 16/06/2025 | 15:38 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 50 | 6770 | 135.4 | 2 | No
| 1904567 | 16/06/2025 | 13:22 | 16/06/2025 | 16:00 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 8 | 1264.8 | 158.1 | 3 | No
| 1904567 | 16/06/2025 | 13:22 | 16/06/2025 | 16:29 | MTN31 | MORNINGTON | Urban | Asset Failure | LV | 44 | 8205.2652 | 186.4833 | 4 | No
| 1904613 | 16/06/2025 | 14:57 | 16/06/2025 | 17:13 | FSH23 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 19.47 | 2636.5631 | 135.4167 | 1 | No
| 1904618 | 16/06/2025 | 15:11 | 16/06/2025 | 16:58 | DC6 | DONCASTER | Urban | Asset Failure | LV | 1 | 106.55 | 106.55 | 1 | No
| 1904573 | 16/06/2025 | 16:16 | 16/06/2025 | 19:14 | NP11 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 178.4333 | 178.4333 | 1 | No
| 1904639 | 16/06/2025 | 16:19 | 16/06/2025 | 23:00 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 1 | 401.0333 | 401.0333 | 1 | No
| 1904674 | 16/06/2025 | 16:30 | 16/06/2025 | 21:35 | M35 | MENTONE | Urban | Asset Failure | LV | 1 | 304.4667 | 304.4667 | 1 | No
| 1904646 | 16/06/2025 | 16:40 | 16/06/2025 | 23:57 | DMA13 | DROMANA | Rural Short | Asset Failure | LV | 1 | 436.5833 | 436.5833 | 1 | No
| 1904628 | 16/06/2025 | 18:33 | 16/06/2025 | 20:05 | MGE33 | MULGRAVE | Urban | Asset Failure | LV | 1 | 92.35 | 92.35 | 1 | No
| 1904693 | 16/06/2025 | 18:45 | 16/06/2025 | 22:44 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 239.3 | 239.3 | 1 | No
| 1904694 | 16/06/2025 | 18:45 | 16/06/2025 | 19:24 | DMA24 | DROMANA | Rural Short | Asset Failure | HV | 58 | 2255.2314 | 38.8833 | 1 | No
| 1904705 | 16/06/2025 | 19:39 | 16/06/2025 | 22:36 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 176.1833 | 176.1833 | 1 | No
| 1904721 | 16/06/2025 | 21:23 | 16/06/2025 | 22:11 | MC23 | MORDIALLOC | Urban | Asset Failure | Distribution substation | 241.87 | 11629.9078 | 48.0833 | 1 | No
| 1904719 | 16/06/2025 | 21:23 | 16/06/2025 | 23:22 | MGE21 | MULGRAVE | Urban | Asset Failure | LV | 1 | 119.2167 | 119.2167 | 1 | No
| 1904728 | 16/06/2025 | 21:56 | 16/06/2025 | 23:43 | HGS33 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 107 | 107 | 1 | No
| 1904736 | 16/06/2025 | 22:39 | 17/06/2025 | 0:55 | SS13 | SPRINGVALE SOUTH | Urban | Asset Failure | LV | 1 | 135.9167 | 135.9167 | 1 | No
| 1904760 | 17/06/2025 | 6:03 | 17/06/2025 | 10:18 | NP24 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 255.7167 | 255.7167 | 1 | No
| 1904884 | 17/06/2025 | 9:12 | 17/06/2025 | 9:35 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 6 | 138 | 23 | 1 | No
| 1904895 | 17/06/2025 | 9:22 | 17/06/2025 | 11:17 | DMA15 | DROMANA | Rural Short | Asset Failure | LV | 6 | 688.9002 | 114.8167 | 1 | No
| 1904958 | 17/06/2025 | 11:56 | 17/06/2025 | 14:25 | FTN24 | FRANKSTON | Urban | Asset Failure | LV | 1 | 149 | 149 | 1 | No
| 1905051 | 17/06/2025 | 13:24 | 17/06/2025 | 19:17 | MGE21 | MULGRAVE | Urban | Asset Failure | LV | 2.08 | 732.992 | 352.4 | 1 | No
| 1905086 | 17/06/2025 | 14:33 | 17/06/2025 | 15:39 | FTN12 | FRANKSTON | Urban | Asset Failure | LV | 1 | 66.3 | 66.3 | 1 | No
| 1905108 | 17/06/2025 | 15:11 | 17/06/2025 | 15:28 | HGS21 | HASTINGS | Rural Short | Asset Failure | LV | 3 | 48.2001 | 16.0667 | 1 | No
| 1905123 | 17/06/2025 | 16:16 | 17/06/2025 | 19:08 | FSH12 | FRANKSTON SOUTH | Rural Short | Asset Failure | LV | 1 | 172.8667 | 172.8667 | 1 | No
| 1905145 | 17/06/2025 | 17:45 | 17/06/2025 | 18:41 | LD7 | LYNDALE | Urban | Asset Failure | LV | 29.37 | 1644.72 | 56 | 1 | No
| 1905138 | 17/06/2025 | 17:56 | 17/06/2025 | 21:49 | LWN32 | LANGWARRIN | Rural Short | Asset Failure | LV | 1 | 233 | 233 | 1 | No
| 1905157 | 17/06/2025 | 19:11 | 17/06/2025 | 21:00 | MR11 | MOORABBIN | Urban | Asset Failure | LV | 59.73 | 6509.5725 | 108.9833 | 1 | No
| 1905165 | 17/06/2025 | 20:24 | 17/06/2025 | 21:21 | GW3 | GLEN WAVERLEY | Urban | Overloads |  | 29.37 | 1674.09 | 57 | 1 | No
| 1905208 | 18/06/2025 | 0:57 | 18/06/2025 | 2:10 | BU25 | BULLEEN | Urban | Unknown | Unknown | 1 | 73 | 73 | 1 | No
| 1905218 | 18/06/2025 | 5:46 | 18/06/2025 | 8:33 | SVW56 | SPRINGVALE WEST | Urban | Asset Failure | LV | 1 | 166.45 | 166.45 | 1 | No
| 1905228 | 18/06/2025 | 6:42 | 18/06/2025 | 7:34 | FSH13 | FRANKSTON SOUTH | Urban | Asset Failure | HV | 1176.52 | 61924.1301 | 52.6333 | 1 | No
| 1905372 | 18/06/2025 | 8:33 | 18/06/2025 | 9:13 | CRM15 | CARRUM | Urban | Asset Failure | LV | 1 | 39.3333 | 39.3333 | 1 | No
| 1905425 | 18/06/2025 | 9:44 | 18/06/2025 | 11:20 | K21 | GARDINER | Urban | Asset Failure | LV | 6 | 574.8 | 95.8 | 1 | No
| 1905217 | 18/06/2025 | 9:49 | 18/06/2025 | 12:37 | HGS21 | HASTINGS | Rural Short | Animal | Animal impact | 1 | 168.45 | 168.45 | 1 | No
| 1905514 | 18/06/2025 | 11:36 | 18/06/2025 | 11:53 | NW22 | NUNAWADING | Urban | Asset Failure | LV | 76 | 1354.0692 | 17.8167 | 1 | No
| 1905514 | 18/06/2025 | 11:36 | 18/06/2025 | 15:43 | NW22 | NUNAWADING | Urban | Asset Failure | LV | 109 | 26972.05 | 247.45 | 2 | No
| 1905576 | 18/06/2025 | 13:32 | 18/06/2025 | 17:56 | HT3 | HEATHERTON | Urban | Asset Failure | LV | 1 | 263.1833 | 263.1833 | 1 | No
| 1905590 | 18/06/2025 | 14:00 | 18/06/2025 | 16:18 | SH34 | SURREY HILLS | Urban | Overloads |  | 1 | 137.85 | 137.85 | 1 | No
| 1905611 | 18/06/2025 | 14:57 | 18/06/2025 | 19:15 | BT14 | BENTLEIGH | Urban | Overloads |  | 1 | 257.15 | 257.15 | 1 | No
| 1905647 | 18/06/2025 | 18:49 | 18/06/2025 | 19:29 | EW12 | ELWOOD | Urban | Asset Failure | Distribution substation | 1930.27 | 76342.1785 | 39.55 | 1 | No
| 1905723 | 18/06/2025 | 22:21 | 18/06/2025 | 23:50 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 89 | 89 | 1 | No
| 1905737 | 18/06/2025 | 23:53 | 19/06/2025 | 1:04 | BH11 | BOX HILL | Urban | Overloads |  | 1 | 71.7333 | 71.7333 | 1 | No
| 1905738 | 19/06/2025 | 1:10 | 19/06/2025 | 1:37 | NP23 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 27.1667 | 27.1667 | 1 | No
| 1905922 | 19/06/2025 | 12:24 | 19/06/2025 | 13:38 | M25 | MENTONE | Urban | Asset Failure | LV | 1 | 73.5833 | 73.5833 | 1 | No
| 1905875 | 19/06/2025 | 13:13 | 19/06/2025 | 15:00 | NP23 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 107.5667 | 107.5667 | 1 | No
| 1905943 | 19/06/2025 | 13:14 | 19/06/2025 | 15:10 | CFD12 | CAULFIELD | Urban | Asset Failure | LV | 1 | 115.1833 | 115.1833 | 1 | No
| 1905949 | 19/06/2025 | 13:33 | 19/06/2025 | 17:05 | MC12 | MORDIALLOC | Urban | Asset Failure | LV | 1 | 211.8667 | 211.8667 | 1 | No
| 1905955 | 19/06/2025 | 13:53 | 19/06/2025 | 16:36 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 162.7333 | 162.7333 | 1 | No
| 1905990 | 19/06/2025 | 15:15 | 19/06/2025 | 16:29 | MTN23 | MORNINGTON | Urban | Asset Failure | LV | 1 | 74.2833 | 74.2833 | 1 | No
| 1905996 | 19/06/2025 | 16:00 | 19/06/2025 | 20:26 | RD2 | RIVERSDALE | Urban | Third Party | Vehicle Impact | 50 | 13288.335 | 265.7667 | 1 | No
| 1905997 | 19/06/2025 | 16:07 | 19/06/2025 | 17:12 | MTN21 | MORNINGTON | Urban | Third Party | Other | 1 | 64.4333 | 64.4333 | 1 | No
| 1906000 | 19/06/2025 | 16:31 | 19/06/2025 | 18:43 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 131.25 | 131.25 | 1 | No
| 1906005 | 19/06/2025 | 16:50 | 19/06/2025 | 19:10 | OAK23 | OAKLEIGH | Urban | Overloads |  | 123 | 17193.3459 | 139.7833 | 1 | No
| 1906004 | 19/06/2025 | 16:52 | 19/06/2025 | 22:24 | FSH22 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 332.35 | 332.35 | 1 | No
| 1906007 | 19/06/2025 | 17:29 | 19/06/2025 | 19:15 | LD4 | LYNDALE | Urban | Asset Failure | LV | 1 | 106.0167 | 106.0167 | 1 | No
| 1906055 | 19/06/2025 | 22:00 | 20/06/2025 | 3:28 | MC15 | MORDIALLOC | Urban | Asset Failure | LV | 36 | 11829.6 | 328.6 | 1 | No
| 1906069 | 20/06/2025 | 6:05 | 20/06/2025 | 8:09 | LD6 | LYNDALE | Urban | Asset Failure | LV | 1 | 124.8833 | 124.8833 | 1 | No
| 1906074 | 20/06/2025 | 9:33 | 20/06/2025 | 10:55 | LWN21 | LANGWARRIN | Rural Short | Asset Failure | LV | 4.95 | 405.9 | 82 | 1 | No
| 1906285 | 20/06/2025 | 13:43 | 20/06/2025 | 15:25 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 39.93 | 4057.5548 | 101.6167 | 1 | No
| 1906286 | 20/06/2025 | 13:56 | 20/06/2025 | 16:35 | STO23 | SORRENTO | Urban | Asset Failure | LV | 1 | 158.4 | 158.4 | 1 | No
| 1906329 | 20/06/2025 | 16:15 | 20/06/2025 | 18:00 | RBD23 | ROSEBUD | Urban | Asset Failure | LV | 39 | 4056.6513 | 104.0167 | 1 | No
| 1906346 | 20/06/2025 | 18:01 | 20/06/2025 | 18:55 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 54.2833 | 54.2833 | 1 | No
| 1906347 | 20/06/2025 | 18:05 | 20/06/2025 | 19:30 | NW14 | NUNAWADING | Urban | Asset Failure | LV | 55.77 | 4726.5075 | 84.75 | 1 | No
| 1906374 | 20/06/2025 | 20:42 | 20/06/2025 | 21:46 | STO13 | SORRENTO | Urban | Overloads |  | 1 | 64.1667 | 64.1667 | 1 | No
| 1906378 | 20/06/2025 | 21:00 | 20/06/2025 | 21:55 | OAK23 | OAKLEIGH | Urban | Asset Failure | HV | 95.04 | 5135.3248 | 54.0333 | 1 | No
| 1906389 | 21/06/2025 | 2:31 | 21/06/2025 | 4:35 | BR15 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 124 | 124 | 1 | No
| 1906457 | 21/06/2025 | 12:34 | 21/06/2025 | 15:18 | BT16 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 164.1 | 164.1 | 1 | No
| 1906461 | 21/06/2025 | 12:44 | 21/06/2025 | 14:50 | DMA15 | DROMANA | Rural Short | Asset Failure | LV | 1 | 125.9333 | 125.9333 | 1 | No
| 1906467 | 21/06/2025 | 13:28 | 21/06/2025 | 14:29 | NO7 | NOTTING HILL | Urban | Third Party | Vehicle Impact | 1 | 61 | 61 | 1 | No
| 1906354 | 21/06/2025 | 13:45 | 21/06/2025 | 14:58 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 73.3667 | 73.3667 | 1 | No
| 1906506 | 21/06/2025 | 20:50 | 21/06/2025 | 23:15 | NW31 | NUNAWADING | Urban | Asset Failure | LV | 2 | 289.3334 | 144.6667 | 1 | No
| 1906539 | 22/06/2025 | 8:14 | 22/06/2025 | 9:40 | RBD22 | ROSEBUD | Urban | Asset Failure | LV | 1 | 86 | 86 | 1 | No
| 1906566 | 22/06/2025 | 8:53 | 22/06/2025 | 12:28 | BW34 | BURWOOD | Urban | Asset Failure | LV | 37 | 7945.75 | 214.75 | 1 | No
| 1906582 | 22/06/2025 | 12:32 | 22/06/2025 | 13:34 | MTN22 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 62.3 | 62.3 | 1 | No
| 1906597 | 22/06/2025 | 13:16 | 22/06/2025 | 15:00 | DC10 | DONCASTER | Urban | Overloads |  | 30 | 3093.999 | 103.1333 | 1 | No
| 1906607 | 22/06/2025 | 14:50 | 22/06/2025 | 16:30 | NP23 | NOBLE PARK | Urban | Asset Failure | LV | 52 | 5197.4 | 99.95 | 1 | No
| 1906631 | 22/06/2025 | 19:44 | 22/06/2025 | 21:26 | NP16 | NOBLE PARK | Urban | Overloads |  | 89.1 | 9054.048 | 101.6167 | 1 | No
| 1906644 | 22/06/2025 | 22:17 | 22/06/2025 | 23:55 | DC10 | DONCASTER | Urban | Asset Failure | LV | 17 | 1650.4161 | 97.0833 | 1 | No
| 1906647 | 22/06/2025 | 23:11 | 22/06/2025 | 23:35 | DC10 | DONCASTER | Urban | Unknown | Unknown | 13 | 317.85 | 24.45 | 1 | No
| 1906666 | 23/06/2025 | 7:16 | 23/06/2025 | 8:30 | CRM15 | CARRUM | Urban | Third Party | Other | 1 | 73.8 | 73.8 | 1 | No
| 1906667 | 23/06/2025 | 7:25 | 23/06/2025 | 9:25 | HGS22 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 119.5167 | 119.5167 | 1 | No
| 1906707 | 23/06/2025 | 9:04 | 23/06/2025 | 10:25 | RWT23 | RINGWOOD | Urban | Third Party | Other | 1 | 81.6 | 81.6 | 1 | No
| 1906711 | 23/06/2025 | 9:06 | 23/06/2025 | 11:58 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 1 | 172.3167 | 172.3167 | 1 | No
| 1906742 | 23/06/2025 | 12:15 | 23/06/2025 | 15:04 | CRM13 | CARRUM | Urban | Asset Failure | LV | 1 | 169.1 | 169.1 | 1 | No
| 1906828 | 23/06/2025 | 13:21 | 23/06/2025 | 19:21 | NP11 | NOBLE PARK | Urban | Asset Failure | LV | 1 | 359.9667 | 359.9667 | 1 | No
| 1906857 | 23/06/2025 | 14:57 | 23/06/2025 | 16:18 | DC10 | DONCASTER | Urban | Asset Failure | LV | 44 | 3555.2 | 80.8 | 1 | No
| 1906898 | 23/06/2025 | 15:49 | 23/06/2025 | 19:28 | GW5 | GLEN WAVERLEY | Urban | Asset Failure | LV | 1 | 218.95 | 218.95 | 1 | No
| 1906907 | 23/06/2025 | 16:28 | 23/06/2025 | 21:10 | STO13 | SORRENTO | Urban | Weather |  | 38 | 10703.9654 | 281.6833 | 1 | No
| 1906921 | 23/06/2025 | 17:46 | 23/06/2025 | 18:15 | M12 | MENTONE | Urban | Asset Failure | LV | 4.3 | 122.335 | 28.45 | 1 | No
| 1906933 | 23/06/2025 | 20:35 | 24/06/2025 | 0:12 | K24 | GARDINER | Urban | Asset Failure | LV | 58 | 12580.2 | 216.9 | 1 | No
| 1906935 | 23/06/2025 | 20:36 | 24/06/2025 | 0:12 | K24 | GARDINER | Urban | Asset Failure | LV | 35 | 7539.5845 | 215.4167 | 1 | No
| 1906937 | 23/06/2025 | 20:36 | 23/06/2025 | 22:05 | NP23 | NOBLE PARK | Urban | Animal | Animal impact | 69.68 | 6153.9077 | 88.3167 | 1 | No
| 1906963 | 24/06/2025 | 2:57 | 24/06/2025 | 3:56 | NW31 | NUNAWADING | Urban | Asset Failure | LV | 1 | 59.0333 | 59.0333 | 1 | No
| 1906966 | 24/06/2025 | 3:55 | 24/06/2025 | 5:00 | LWN21 | LANGWARRIN | Rural Short | Animal | Animal impact | 10.05 | 651.4078 | 64.8167 | 1 | No
| 1907029 | 24/06/2025 | 5:58 | 24/06/2025 | 10:05 | HGS21 | HASTINGS | Rural Short | Asset Failure | HV | 1 | 246.65 | 246.65 | 1 | No
| 1906973 | 24/06/2025 | 6:39 | 24/06/2025 | 10:04 | MGE21 | MULGRAVE | Urban | Asset Failure | HV | 26 | 5330 | 205 | 1 | No
| 1907061 | 24/06/2025 | 9:23 | 24/06/2025 | 12:50 | NP36 | NOBLE PARK | Urban | Third Party | Vehicle Impact | 2 | 414 | 207 | 1 | No
| 1907056 | 24/06/2025 | 9:24 | 24/06/2025 | 12:50 | NP36 | NOBLE PARK | Urban | Third Party | Vehicle Impact | 23 | 4724.2 | 205.4 | 1 | No
| 1907068 | 24/06/2025 | 9:44 | 24/06/2025 | 11:05 | EL32 | ELSTERNWICK | Urban | Asset Failure | LV | 1 | 80.3167 | 80.3167 | 1 | No
| 1907097 | 24/06/2025 | 10:31 | 24/06/2025 | 12:51 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 15.51 | 2160.802 | 139.3167 | 1 | No
| 1907126 | 24/06/2025 | 11:02 | 24/06/2025 | 12:57 | NW33 | NUNAWADING | Urban | Third Party | Other | 1 | 115.3333 | 115.3333 | 1 | No
| 1907166 | 24/06/2025 | 11:49 | 24/06/2025 | 12:48 | NW13 | NUNAWADING | Urban | Animal | Other | 18.09 | 1073.9436 | 59.3667 | 1 | No
| 1907211 | 24/06/2025 | 13:41 | 24/06/2025 | 15:36 | K25 | GARDINER | Urban | Asset Failure | LV | 1 | 115.9667 | 115.9667 | 1 | No
| 1907223 | 24/06/2025 | 13:46 | 24/06/2025 | 15:54 | FSH22 | FRANKSTON SOUTH | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 128.2667 | 128.2667 | 1 | No
| 1907246 | 24/06/2025 | 14:55 | 24/06/2025 | 16:51 | SVW53 | SPRINGVALE WEST | Urban | Asset Failure | LV | 6.6 | 765.1598 | 115.9333 | 1 | No
| 1907256 | 24/06/2025 | 15:19 | 24/06/2025 | 18:00 | FSH32 | FRANKSTON SOUTH | Rural Short | Asset Failure | HV | 1 | 160.9167 | 160.9167 | 1 | No
| 1907257 | 24/06/2025 | 15:22 | 24/06/2025 | 18:53 | CDA23 | CLARINDA | Urban | Asset Failure | LV | 6 | 1269.4002 | 211.5667 | 1 | No
| 1907263 | 24/06/2025 | 15:33 | 24/06/2025 | 17:32 | CDA11 | CLARINDA | Urban | Asset Failure | LV | 1 | 119.2333 | 119.2333 | 1 | No
| 1907277 | 24/06/2025 | 16:14 | 24/06/2025 | 21:30 | DC3 | DONCASTER | Urban | Unknown | Unknown | 1 | 315.0333 | 315.0333 | 1 | No
| 1907285 | 24/06/2025 | 16:51 | 24/06/2025 | 18:35 | MR31 | MOORABBIN | Urban | Asset Failure | LV | 1 | 104 | 104 | 1 | No
| 1907290 | 24/06/2025 | 16:51 | 24/06/2025 | 18:50 | M34 | MENTONE | Urban | Asset Failure | LV | 1 | 118.1167 | 118.1167 | 1 | No
| 1907286 | 24/06/2025 | 17:02 | 24/06/2025 | 18:30 | DC4 | DONCASTER | Urban | Overloads |  | 1 | 88 | 88 | 1 | No
| 1907298 | 24/06/2025 | 17:30 | 24/06/2025 | 17:34 | STO13 | SORRENTO | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 858 | 2888.6286 | 3.3667 | 1 | No
| 1907298 | 24/06/2025 | 17:30 | 24/06/2025 | 18:30 | STO13 | SORRENTO | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 502 | 29810.4166 | 59.3833 | 2 | No
| 1907298 | 24/06/2025 | 17:30 | 24/06/2025 | 18:39 | STO13 | SORRENTO | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 44 | 3014 | 68.5 | 3 | No
| 1907298 | 24/06/2025 | 17:30 | 24/06/2025 | 19:00 | STO13 | SORRENTO | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 161 | 14420.2387 | 89.5667 | 4 | No
| 1907298 | 24/06/2025 | 17:30 | 25/06/2025 | 16:42 | STO13 | SORRENTO | Urban | Vegetation | Blow-in/Fall-in - Other responsible party | 36 | 50089.2012 | 1391.3667 | 5 | No
| 1907305 | 24/06/2025 | 17:53 | 24/06/2025 | 20:20 | LWN35 | LANGWARRIN | Urban | Asset Failure | HV | 52.93 | 7750.7146 | 146.4333 | 1 | No
| 1907314 | 24/06/2025 | 18:34 | 24/06/2025 | 23:55 | DMA23 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 320.2667 | 320.2667 | 1 | No
| 1907318 | 24/06/2025 | 18:48 | 24/06/2025 | 21:00 | BR1 | BEAUMARIS | Urban | Asset Failure | LV | 1 | 132 | 132 | 1 | No
| 1907319 | 24/06/2025 | 18:53 | 24/06/2025 | 22:07 | DMA15 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 18 | 3494.7 | 194.15 | 1 | No
| 1907330 | 24/06/2025 | 19:38 | 24/06/2025 | 20:55 | MR11 | MOORABBIN | Urban | Asset Failure | LV | 1 | 77.5333 | 77.5333 | 1 | No
| 1907329 | 24/06/2025 | 20:24 | 24/06/2025 | 21:32 | CDA23 | CLARINDA | Urban | Overloads |  | 1 | 68.7167 | 68.7167 | 1 | No
| 1907335 | 24/06/2025 | 20:43 | 24/06/2025 | 23:55 | MR22 | MOORABBIN | Urban | Asset Failure | LV | 1 | 191.1667 | 191.1667 | 1 | No
| 1907344 | 24/06/2025 | 21:42 | 24/06/2025 | 23:05 | EW1 | ELWOOD | Urban | Third Party | Other | 1 | 82.9667 | 82.9667 | 1 | No
| 1907354 | 25/06/2025 | 0:24 | 25/06/2025 | 1:18 | DMA14 | DROMANA | Urban | Asset Failure | HV | 38.19 | 2068.6263 | 54.1667 | 1 | No
| 1907383 | 25/06/2025 | 6:14 | 25/06/2025 | 10:47 | STO21 | SORRENTO | Rural Short | Weather |  | 1 | 272.8333 | 272.8333 | 1 | No
| 1907417 | 25/06/2025 | 7:01 | 25/06/2025 | 9:01 | DMA23 | DROMANA | Rural Short | Animal | Animal impact | 2 | 240 | 120 | 1 | No
| 1907398 | 25/06/2025 | 8:14 | 25/06/2025 | 11:11 | STO23 | SORRENTO | Urban | Unknown | Unknown | 1 | 177.6167 | 177.6167 | 1 | No
| 1907432 | 25/06/2025 | 8:49 | 25/06/2025 | 11:18 | DVY33 | DANDENONG VALLEY | Urban | Asset Failure | LV | 1 | 149.1 | 149.1 | 1 | No
| 1907451 | 25/06/2025 | 9:16 | 25/06/2025 | 14:45 | MTN21 | MORNINGTON | Urban | Asset Failure | LV | 1 | 328.6 | 328.6 | 1 | No
| 1907511 | 25/06/2025 | 9:46 | 25/06/2025 | 11:55 | LWN32 | LANGWARRIN | Rural Short | Asset Failure | HV | 2 | 256.6666 | 128.3333 | 1 | No
| 1907495 | 25/06/2025 | 12:31 | 25/06/2025 | 14:29 | CM13 | CHELTENHAM | Urban | Asset Failure | LV | 1 | 118 | 118 | 1 | No
| 1907546 | 25/06/2025 | 12:32 | 25/06/2025 | 13:22 | FSH11 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 2.96 | 145.5826 | 49.1833 | 1 | No
| 1907572 | 25/06/2025 | 13:12 | 25/06/2025 | 15:40 | SR21 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 147.3333 | 147.3333 | 1 | No
| 1907599 | 25/06/2025 | 13:53 | 25/06/2025 | 15:14 | NW33 | NUNAWADING | Urban | Asset Failure | HV | 55.77 | 4547.1121 | 81.5333 | 1 | No
| 1907615 | 25/06/2025 | 14:41 | 25/06/2025 | 15:16 | K26 | GARDINER | Urban | Third Party | Other | 1 | 35 | 35 | 1 | No
| 1907628 | 25/06/2025 | 15:56 | 25/06/2025 | 16:34 | HT3 | HEATHERTON | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 443 | 16789.7 | 37.9 | 1 | No
| 1907628 | 25/06/2025 | 15:56 | 25/06/2025 | 16:34 | HT9 | HEATHERTON | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 126 | 4775.4 | 37.9 | 1 | No
| 1907628 | 25/06/2025 | 15:56 | 25/06/2025 | 17:19 | HT9 | HEATHERTON | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 55 | 4587.9185 | 83.4167 | 2 | No
| 1907633 | 25/06/2025 | 16:25 | 25/06/2025 | 18:43 | OE9 | OAKLEIGH EAST | Urban | Third Party | Vehicle Impact | 29 | 4002 | 138 | 1 | No
| 1907635 | 25/06/2025 | 16:27 | 25/06/2025 | 18:08 | HT6 | HEATHERTON | Urban | Overloads |  | 1 | 100.5 | 100.5 | 1 | No
| 1907642 | 25/06/2025 | 16:45 | 25/06/2025 | 20:49 | MC21 | MORDIALLOC | Urban | Weather |  | 1 | 243.65 | 243.65 | 1 | No
| 1907645 | 25/06/2025 | 16:56 | 25/06/2025 | 18:10 | HT9 | HEATHERTON | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 26 | 1900.6 | 73.1 | 1 | No
| 1907650 | 25/06/2025 | 17:16 | 25/06/2025 | 19:10 | FTN21 | FRANKSTON | Urban | Asset Failure | LV | 1 | 114.1333 | 114.1333 | 1 | No
| 1907670 | 25/06/2025 | 18:49 | 25/06/2025 | 20:35 | MR24 | MOORABBIN | Urban | Weather |  | 105 | 11037.2535 | 105.1167 | 1 | No
| 1907688 | 25/06/2025 | 19:30 | 25/06/2025 | 20:05 | OR35 | ORMOND | Urban | Overloads |  | 1 | 35.1 | 35.1 | 1 | No
| 1907694 | 25/06/2025 | 20:34 | 25/06/2025 | 23:30 | DMA24 | DROMANA | Rural Short | Vegetation | Blow-in/Fall-in - Other responsible party | 1 | 176.4167 | 176.4167 | 1 | No
| 1907704 | 25/06/2025 | 22:15 | 25/06/2025 | 22:57 | OAK33 | OAKLEIGH | Urban | Overloads |  | 1 | 42 | 42 | 1 | No
| 1907700 | 26/06/2025 | 0:05 | 26/06/2025 | 2:04 | SR25 | SANDRINGHAM | Urban | Asset Failure | LV | 1 | 119 | 119 | 1 | No
| 1907752 | 26/06/2025 | 7:02 | 26/06/2025 | 7:31 | NW21 | NUNAWADING | Urban | Animal | Other | 2 | 56.3666 | 28.1833 | 1 | No
| 1907767 | 26/06/2025 | 7:55 | 26/06/2025 | 11:13 | LWN23 | LANGWARRIN | Urban | Asset Failure | LV | 2 | 397.3 | 198.65 | 1 | No
| 1907812 | 26/06/2025 | 9:39 | 26/06/2025 | 12:00 | SV34 | SPRINGVALE | Urban | Asset Failure | LV | 1 | 141 | 141 | 1 | No
| 1907872 | 26/06/2025 | 10:41 | 26/06/2025 | 12:44 | BH33 | BOX HILL | Urban | Other | XXX | 1 | 123.1667 | 123.1667 | 1 | No
| 1907719 | 26/06/2025 | 12:19 | 26/06/2025 | 14:27 | LD32 | LYNDALE | Urban | Asset Failure | LV | 1 | 128 | 128 | 1 | No
| 1907955 | 26/06/2025 | 13:56 | 26/06/2025 | 16:23 | DN6 | DANDENONG | Urban | Unknown | Unknown | 1 | 147.5 | 147.5 | 1 | No
| 1907947 | 26/06/2025 | 14:11 | 26/06/2025 | 17:49 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 218 | 218 | 1 | No
| 1908013 | 26/06/2025 | 16:55 | 26/06/2025 | 18:20 | CM22 | CHELTENHAM | Urban | Asset Failure | LV | 1 | 84.6833 | 84.6833 | 1 | No
| 1908025 | 26/06/2025 | 18:12 | 26/06/2025 | 22:15 | FSH33 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 243.2167 | 243.2167 | 1 | No
| 1908092 | 26/06/2025 | 18:20 | 26/06/2025 | 19:08 | NP16 | NOBLE PARK | Urban | Overloads |  | 89.1 | 4276.8 | 48 | 1 | No
| 1908097 | 26/06/2025 | 19:33 | 26/06/2025 | 22:35 | CRM23 | CARRUM | Urban | Asset Failure | LV | 1 | 181.3333 | 181.3333 | 1 | No
| 1908099 | 26/06/2025 | 19:44 | 26/06/2025 | 20:40 | NP16 | NOBLE PARK | Urban | Overloads |  | 89.1 | 5032.662 | 56.4833 | 1 | No
| 1908102 | 26/06/2025 | 20:11 | 26/06/2025 | 21:04 | SVW54 | SPRINGVALE WEST | Urban | Overloads |  | 31.68 | 1677.9851 | 52.9667 | 1 | No
| 1908124 | 27/06/2025 | 1:44 | 27/06/2025 | 2:39 | OR35 | ORMOND | Urban | Third Party | Other | 1 | 55 | 55 | 1 | No
| 1908133 | 27/06/2025 | 6:15 | 27/06/2025 | 7:41 | STO13 | SORRENTO | Urban | Asset Failure | LV | 11.22 | 964.7326 | 85.9833 | 1 | No
| 1908151 | 27/06/2025 | 7:50 | 27/06/2025 | 9:18 | RWT24 | RINGWOOD | Urban | Asset Failure | LV | 1 | 88.05 | 88.05 | 1 | No
| 1908169 | 27/06/2025 | 8:23 | 27/06/2025 | 10:54 | BU24 | BULLEEN | Urban | Unknown | Unknown | 2 | 301.8334 | 150.9167 | 1 | No
| 1908227 | 27/06/2025 | 9:41 | 27/06/2025 | 11:54 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 133.0333 | 133.0333 | 1 | No
| 1908286 | 27/06/2025 | 11:10 | 27/06/2025 | 11:43 | STO14 | SORRENTO | Rural Short | Asset Failure | LV | 1 | 32.9833 | 32.9833 | 1 | No
| 1908289 | 27/06/2025 | 11:17 | 27/06/2025 | 13:34 | BU24 | BULLEEN | Urban | Asset Failure | LV | 1 | 137.0333 | 137.0333 | 1 | No
| 1908353 | 27/06/2025 | 13:54 | 27/06/2025 | 16:55 | EL35 | ELSTERNWICK | Urban | Unknown | Unknown | 1 | 180.9333 | 180.9333 | 1 | No
| 1908401 | 27/06/2025 | 17:40 | 27/06/2025 | 18:45 | MTN32 | MORNINGTON | Rural Short | Asset Failure | LV | 2 | 130 | 65 | 1 | No
| 1908407 | 27/06/2025 | 18:03 | 27/06/2025 | 19:20 | FTN11 | FRANKSTON | Urban | Asset Failure | LV | 18.81 | 1443.0411 | 76.7167 | 1 | No
| 1908422 | 27/06/2025 | 20:27 | 27/06/2025 | 21:32 | KBH32 | KEYSBOROUGH | Urban | Asset Failure | LV | 20.13 | 1308.45 | 65 | 1 | No
| 1908424 | 27/06/2025 | 22:33 | 27/06/2025 | 23:05 | FSH34 | FRANKSTON SOUTH | Urban | Asset Failure | LV | 1 | 32.2667 | 32.2667 | 1 | No
| 1908457 | 28/06/2025 | 8:33 | 28/06/2025 | 12:58 | MR33 | MOORABBIN | Urban | Third Party | Other | 1 | 265.3333 | 265.3333 | 1 | No
| 1908458 | 28/06/2025 | 8:33 | 28/06/2025 | 8:52 | NP16 | NOBLE PARK | Urban | Overloads |  | 22 | 406.2674 | 18.4667 | 1 | No
| 1908468 | 28/06/2025 | 9:07 | 28/06/2025 | 15:10 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 107 | 38791.0631 | 362.5333 | 1 | No
| 1908444 | 28/06/2025 | 9:40 | 28/06/2025 | 12:00 | SH22 | SURREY HILLS | Urban | Third Party | Other | 5 | 702.25 | 140.45 | 1 | No
| 1908514 | 28/06/2025 | 12:44 | 28/06/2025 | 16:40 | BU24 | BULLEEN | Urban | Unknown | Unknown | 1 | 236.3667 | 236.3667 | 1 | No
| 1908517 | 28/06/2025 | 13:02 | 28/06/2025 | 15:03 | LWN35 | LANGWARRIN | Urban | Asset Failure | LV | 2 | 243.5 | 121.75 | 1 | No
| 1908576 | 29/06/2025 | 0:29 | 29/06/2025 | 10:56 | NB36 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 627.2667 | 627.2667 | 1 | No
| 1908602 | 29/06/2025 | 10:44 | 29/06/2025 | 12:24 | CM25 | CHELTENHAM | Urban | Asset Failure | LV | 1 | 99.8167 | 99.8167 | 1 | No
| 1908587 | 29/06/2025 | 11:35 | 29/06/2025 | 13:10 | HGS23 | HASTINGS | Rural Short | Asset Failure | LV | 1 | 95 | 95 | 1 | No
| 1908606 | 29/06/2025 | 12:44 | 29/06/2025 | 14:28 | DMA14 | DROMANA | Urban | Asset Failure | LV | 1 | 104 | 104 | 1 | No
| 1908580 | 29/06/2025 | 13:32 | 29/06/2025 | 16:10 | NW21 | NUNAWADING | Urban | Asset Failure | LV | 1 | 158.1167 | 158.1167 | 1 | No
| 1908624 | 29/06/2025 | 14:59 | 29/06/2025 | 19:01 | SV31 | SPRINGVALE | Urban | Third Party | Vehicle Impact | 3 | 724.5 | 241.5 | 1 | No
| 1908625 | 29/06/2025 | 15:27 | 29/06/2025 | 17:35 | DMA23 | DROMANA | Rural Short | Asset Failure | LV | 1 | 128 | 128 | 1 | No
| 1908634 | 29/06/2025 | 17:14 | 29/06/2025 | 19:40 | HGS33 | HASTINGS | Rural Short | Asset Failure | Distribution substation | 4 | 584 | 146 | 1 | No
| 1908638 | 29/06/2025 | 17:45 | 29/06/2025 | 18:55 | MTN33 | MORNINGTON | Urban | Unknown | Unknown | 1 | 70 | 70 | 1 | No
| 1908645 | 29/06/2025 | 18:15 | 29/06/2025 | 21:15 | LWN23 | LANGWARRIN | Urban | Asset Failure | LV | 1 | 179.35 | 179.35 | 1 | No
| 1908656 | 30/06/2025 | 0:20 | 30/06/2025 | 1:07 | WD23 | WEST DONCASTER | Urban | Overloads |  | 32.34 | 1526.9881 | 47.2167 | 1 | No
| 1908713 | 30/06/2025 | 7:46 | 30/06/2025 | 10:02 | NB23 | NORTH BRIGHTON | Urban | Asset Failure | LV | 1 | 136.1 | 136.1 | 1 | No
| 1908742 | 30/06/2025 | 8:03 | 30/06/2025 | 9:27 | CRM35 | CARRUM | Urban | Unknown | Unknown | 91.12 | 7641.9337 | 83.8667 | 1 | No
| 1908698 | 30/06/2025 | 11:02 | 30/06/2025 | 13:25 | EB21 | EAST BURWOOD | Urban | Asset Failure | LV | 1 | 143.1 | 143.1 | 1 | No
| 1908897 | 30/06/2025 | 12:54 | 30/06/2025 | 18:11 | WD14 | WEST DONCASTER | Urban | Asset Failure | LV | 1 | 316.1833 | 316.1833 | 1 | No
| 1908916 | 30/06/2025 | 13:31 | 30/06/2025 | 18:51 | EW1 | ELWOOD | Urban | Asset Failure | LV | 4 | 1276.7332 | 319.1833 | 1 | No
| 1908918 | 30/06/2025 | 13:46 | 30/06/2025 | 15:55 | BW35 | BURWOOD | Urban | Network Business | Network Error | 1 | 129.0333 | 129.0333 | 1 | No
| 1908958 | 30/06/2025 | 15:44 | 30/06/2025 | 19:18 | CDA22 | CLARINDA | Urban | Third Party | Vehicle Impact | 1 | 214.05 | 214.05 | 1 | No
| 1909002 | 30/06/2025 | 19:21 | 30/06/2025 | 20:44 | EL23 | ELSTERNWICK | Urban | Overloads |  | 65 | 5379.8355 | 82.7667 | 1 | No
| 1909027 | 30/06/2025 | 19:21 | 30/06/2025 | 20:55 | EL23 | ELSTERNWICK | Urban | Overloads |  | 85 | 8001.3305 | 94.1333 | 1 | No
| 1909013 | 30/06/2025 | 19:50 | 30/06/2025 | 23:00 | EW9 | ELWOOD | Urban | Asset Failure | LV | 99 | 18773.6967 | 189.6333 | 1 | No
| 1909015 | 30/06/2025 | 20:00 | 30/06/2025 | 20:29 | NW33 | NUNAWADING | Urban | Asset Failure | Distribution substation | 30.69 | 893.079 | 29.1 | 1 | No
| 1909032 | 30/06/2025 | 20:55 | 2025-01-07 | 0:21 | BT15 | BENTLEIGH | Urban | Asset Failure | LV | 1 | 206.3333 | 206.3333 | 1 | No
| 1909033 | 30/06/2025 | 21:08 | 30/06/2025 | 23:52 | SVW56 | SPRINGVALE WEST | Urban | Overloads |  | 51.81 | 8486.478 | 163.8 | 1 | No
| 1909039 | 30/06/2025 | 22:15 | 2025-01-07 | 1:00 | SVW53 | SPRINGVALE WEST | Urban | Unknown | Unknown | 1 | 165 | 165 | 1 | No
| 1909040 | 30/06/2025 | 22:27 | 30/06/2025 | 23:51 | BH11 | BOX HILL | Urban | Overloads |  | 1 | 84.4167 | 84.4167 | 1 | No
| 1909044 | 30/06/2025 | 22:57 | 2025-01-07 | 0:44 | K25 | GARDINER | Urban | Asset Failure | LV | 24.09 | 2562.7737 | 106.3833 | 1 | No
| 145906 | 14/07/2024 | 8:01 | 14/07/2024 | 12:16 | KBH33 | KEYSBOROUGH | Urban | Planned |  | 30 | 7662.501 | 255.4167 | 1 | No
| 145932 | 14/07/2024 | 6:30 | 14/07/2024 | 14:48 | GW4 | GLEN WAVERLEY | Urban | Planned |  | 5 | 2490 | 498 | 1 | No
| 146276 | 2024-04-07 | 10:01 | 2024-04-07 | 14:49 | RBD12 | ROSEBUD | Rural Short | Planned |  | 103 | 29664 | 288 | 1 | No
| 146328 | 2024-05-07 | 8:00 | 2024-05-07 | 16:30 | HGS33 | HASTINGS | Rural Short | Planned |  | 3 | 1530 | 510 | 1 | No
| 146328 | 2024-05-07 | 8:06 | 2024-05-07 | 14:58 | HGS33 | HASTINGS | Rural Short | Planned |  | 182 | 74984 | 412 | 1 | No
| 146377 | 14/07/2024 | 8:02 | 14/07/2024 | 15:28 | FTN14 | FRANKSTON | Urban | Planned |  | 62 | 27652 | 446 | 1 | No
| 146377 | 14/07/2024 | 8:02 | 14/07/2024 | 15:28 | FTN21 | FRANKSTON | Urban | Planned |  | 9 | 4014 | 446 | 1 | No
| 146472 | 2024-02-07 | 9:50 | 2024-02-07 | 13:48 | NW33 | NUNAWADING | Urban | Planned |  | 79 | 18802 | 238 | 1 | No
| 146515 | 2024-03-07 | 8:22 | 2024-03-07 | 12:27 | DMA23 | DROMANA | Rural Short | Planned |  | 23 | 5635 | 245 | 1 | No
| 146515 | 2024-03-07 | 8:22 | 2024-03-07 | 12:27 | RBD21 | ROSEBUD | Rural Short | Planned |  | 18 | 4410 | 245 | 1 | No
| 146655 | 2024-04-07 | 9:17 | 2024-04-07 | 17:30 | FTN25 | FRANKSTON | Urban | Planned |  | 183 | 90219 | 493 | 1 | No
| 146821 | 2024-07-07 | 8:09 | 2024-07-07 | 13:56 | DVY23 | DANDENONG VALLEY | Urban | Planned |  | 56 | 19432 | 347 | 1 | No
| 146870 | 2024-04-07 | 8:35 | 2024-04-07 | 11:23 | NW13 | NUNAWADING | Urban | Planned |  | 32 | 5376 | 168 | 1 | No
| 146980 | 2024-07-07 | 8:11 | 2024-07-07 | 13:51 | MC23 | MORDIALLOC | Urban | Planned |  | 44 | 14960 | 340 | 1 | No
| 146983 | 2024-05-07 | 8:15 | 2024-05-07 | 10:48 | DMA14 | DROMANA | Urban | Planned |  | 72 | 11016 | 153 | 1 | No
| 147005 | 2024-04-08 | 8:00 | 2024-04-08 | 15:44 | NP11 | NOBLE PARK | Urban | Planned |  | 80 | 37120 | 464 | 1 | No
| 147047 | 2024-05-07 | 8:49 | 2024-05-07 | 13:14 | GW12 | GLEN WAVERLEY | Urban | Planned |  | 24 | 6360 | 265 | 1 | No
| 147068 | 2024-08-07 | 9:36 | 2024-08-07 | 12:54 | DN13 | DANDENONG | Urban | Planned |  | 6 | 1188 | 198 | 1 | No
| 147129 | 28/07/2024 | 8:00 | 28/07/2024 | 15:30 | MC23 | MORDIALLOC | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 147129 | 28/07/2024 | 8:02 | 28/07/2024 | 13:03 | MC23 | MORDIALLOC | Urban | Planned |  | 248 | 74648 | 301 | 1 | No
| 147136 | 2024-03-07 | 8:02 | 2024-03-07 | 14:40 | FTN14 | FRANKSTON | Urban | Planned |  | 240 | 95520 | 398 | 1 | No
| 147164 | 2024-10-07 | 8:31 | 2024-10-07 | 12:50 | FSH34 | FRANKSTON SOUTH | Urban | Planned |  | 21 | 5439 | 259 | 1 | No
| 147249 | 2024-02-07 | 10:33 | 2024-02-07 | 12:03 | RBD24 | ROSEBUD | Urban | Planned |  | 2 | 180 | 90 | 1 | No
| 147261 | 14/08/2024 | 8:01 | 14/08/2024 | 16:01 | NW23 | NUNAWADING | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 147261 | 14/08/2024 | 9:10 | 14/08/2024 | 16:26 | NW23 | NUNAWADING | Urban | Planned |  | 165 | 71940 | 436 | 1 | No
| 147307 | 24/07/2024 | 8:10 | 24/07/2024 | 14:23 | GW8 | GLEN WAVERLEY | Urban | Planned |  | 55 | 20515 | 373 | 1 | No
| 147318 | 2024-02-07 | 8:38 | 2024-02-07 | 13:40 | MTN31 | MORNINGTON | Urban | Planned |  | 136 | 41072 | 302 | 1 | No
| 147338 | 2024-07-07 | 7:30 | 2024-07-07 | 17:35 | CDA24 | CLARINDA | Urban | Planned |  | 150 | 90750 | 605 | 1 | No
| 147343 | 20/07/2024 | 7:59 | 20/07/2024 | 14:04 | DN7 | DANDENONG | Urban | Planned |  | 13 | 4745 | 365 | 1 | No
| 147348 | 17/07/2024 | 8:55 | 17/07/2024 | 12:05 | MGE23 | MULGRAVE | Urban | Planned |  | 30 | 5700 | 190 | 1 | No
| 147352 | 2024-03-07 | 9:35 | 2024-03-07 | 14:24 | RBD21 | ROSEBUD | Rural Short | Planned |  | 97 | 28033 | 289 | 1 | No
| 147376 | 25/07/2024 | 8:45 | 25/07/2024 | 12:50 | MTN23 | MORNINGTON | Urban | Planned |  | 18 | 4410 | 245 | 1 | No
| 147390 | 2024-09-07 | 8:00 | 2024-09-07 | 15:14 | HGS33 | HASTINGS | Rural Short | Planned |  | 28 | 12145.4676 | 433.7667 | 1 | No
| 147392 | 2024-07-07 | 8:17 | 2024-07-07 | 13:25 | MTN23 | MORNINGTON | Urban | Planned |  | 135 | 41580 | 308 | 1 | No
| 147408 | 21/07/2024 | 0:56 | 21/07/2024 | 7:13 | SR26 | SANDRINGHAM | Urban | Planned |  | 28 | 10556 | 377 | 1 | No
| 147429 | 2024-05-07 | 9:23 | 2024-05-07 | 14:02 | RWT34 | RINGWOOD | Urban | Planned |  | 65 | 18135 | 279 | 1 | No
| 147431 | 2024-04-07 | 8:00 | 2024-04-07 | 11:37 | CRM35 | CARRUM | Urban | Planned |  | 58 | 12586 | 217 | 1 | No
| 147444 | 2024-02-07 | 8:00 | 2024-02-07 | 8:01 | RBD11 | ROSEBUD | Urban | Planned |  | 282 | 282 | 1 | 1 | No
| 147451 | 28/07/2024 | 8:25 | 28/07/2024 | 14:23 | EM2 | EAST MALVERN | Urban | Planned |  | 44 | 15752 | 358 | 1 | No
| 147470 | 2024-04-08 | 8:15 | 2024-04-08 | 16:22 | HT3 | HEATHERTON | Urban | Planned |  | 37 | 18019 | 487 | 1 | No
| 147470 | 2024-04-08 | 8:15 | 2024-04-08 | 16:22 | HT9 | HEATHERTON | Urban | Planned |  | 10 | 4870 | 487 | 1 | No
| 147474 | 2024-01-07 | 8:25 | 2024-01-07 | 11:19 | CRM35 | CARRUM | Urban | Planned |  | 29 | 5046 | 174 | 1 | No
| 147486 | 23/07/2024 | 8:51 | 23/07/2024 | 15:24 | AR6 | ARMADALE | Urban | Planned |  | 56 | 22008 | 393 | 1 | No
| 147495 | 2024-02-07 | 9:10 | 2024-02-07 | 16:13 | BR1 | BEAUMARIS | Urban | Planned |  | 253 | 107019 | 423 | 1 | No
| 147504 | 2024-02-07 | 9:03 | 2024-02-07 | 14:18 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 109 | 34335 | 315 | 1 | No
| 147536 | 2024-08-07 | 8:08 | 2024-08-07 | 17:06 | GW5 | GLEN WAVERLEY | Urban | Planned |  | 6 | 3228 | 538 | 1 | No
| 147536 | 2024-08-07 | 8:08 | 2024-08-07 | 17:06 | NO32 | NOTTING HILL | Urban | Planned |  | 79 | 42502 | 538 | 1 | No
| 147559 | 2024-07-07 | 9:09 | 2024-07-07 | 16:35 | HGS32 | HASTINGS | Urban | Planned |  | 150 | 66900 | 446 | 1 | No
| 147565 | 2024-07-07 | 8:00 | 2024-07-07 | 17:18 | RD2 | RIVERSDALE | Urban | Planned |  | 60 | 33480 | 558 | 1 | No
| 147567 | 2024-04-07 | 9:31 | 2024-04-07 | 16:25 | NW13 | NUNAWADING | Urban | Planned |  | 183 | 75762 | 414 | 1 | No
| 147583 | 14/07/2024 | 9:10 | 14/07/2024 | 13:12 | CDA23 | CLARINDA | Urban | Planned |  | 24 | 5808 | 242 | 1 | No
| 147583 | 14/07/2024 | 9:10 | 14/07/2024 | 13:12 | NO31 | NOTTING HILL | Urban | Planned |  | 125 | 30250 | 242 | 1 | No
| 147598 | 2024-02-08 | 8:00 | 2024-02-08 | 10:08 | MR11 | MOORABBIN | Urban | Planned |  | 184 | 23552 | 128 | 2 | No
| 147598 | 2024-02-08 | 8:00 | 2024-02-08 | 16:00 | MR11 | MOORABBIN | Urban | Planned |  | 2 | 960 | 480 | 1 | No
| 147600 | 17/07/2024 | 8:09 | 17/07/2024 | 15:00 | RBD21 | ROSEBUD | Rural Short | Planned |  | 35 | 14385 | 411 | 1 | No
| 147621 | 2024-12-07 | 8:45 | 2024-12-07 | 12:07 | SR31 | SANDRINGHAM | Urban | Planned |  | 33 | 6666 | 202 | 1 | No
| 147644 | 2024-10-07 | 8:35 | 2024-10-07 | 13:40 | MTN34 | MORNINGTON | Urban | Planned |  | 56 | 17080 | 305 | 1 | No
| 147652 | 2024-07-07 | 8:05 | 2024-07-07 | 11:58 | LD5 | LYNDALE | Urban | Planned |  | 12 | 2796 | 233 | 1 | No
| 147653 | 14/07/2024 | 7:17 | 14/07/2024 | 7:18 | DN7 | DANDENONG | Urban | Planned |  | 19 | 19 | 1 | 1 | No
| 147656 | 2024-12-07 | 8:04 | 2024-12-07 | 14:35 | HGS33 | HASTINGS | Rural Short | Planned |  | 5 | 1955 | 391 | 1 | No
| 147657 | 2024-09-07 | 2:31 | 2024-09-07 | 3:38 | NP25 | NOBLE PARK | Urban | Planned |  | 68 | 4556 | 67 | 1 | No
| 147660 | 21/07/2024 | 7:50 | 21/07/2024 | 16:40 | DN7 | DANDENONG | Urban | Planned |  | 19 | 10070 | 530 | 1 | No
| 147667 | 2024-09-07 | 9:15 | 2024-09-07 | 10:29 | STO21 | SORRENTO | Rural Short | Planned |  | 124 | 9176 | 74 | 1 | No
| 147672 | 2024-04-08 | 8:00 | 2024-04-08 | 16:00 | NW23 | NUNAWADING | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 147672 | 2024-04-08 | 9:23 | 2024-04-08 | 17:39 | NW23 | NUNAWADING | Urban | Planned |  | 119 | 59024 | 496 | 1 | No
| 147673 | 2024-11-07 | 8:13 | 2024-11-07 | 11:15 | MTN31 | MORNINGTON | Urban | Planned |  | 21 | 3822 | 182 | 1 | No
| 147675 | 2024-04-07 | 11:35 | 2024-04-07 | 14:52 | MGE32 | MULGRAVE | Urban | Planned |  | 8 | 1576 | 197 | 1 | No
| 147679 | 2024-02-07 | 9:29 | 2024-02-07 | 12:14 | EM11 | EAST MALVERN | Urban | Planned |  | 32 | 5280 | 165 | 1 | No
| 147694 | 2024-08-07 | 8:40 | 2024-08-07 | 11:36 | STO14 | SORRENTO | Rural Short | Planned |  | 251 | 44176 | 176 | 1 | No
| 147697 | 19/07/2024 | 8:01 | 19/07/2024 | 11:20 | DC3 | DONCASTER | Urban | Planned |  | 50 | 9950 | 199 | 1 | No
| 147698 | 19/07/2024 | 12:09 | 19/07/2024 | 14:32 | DC7 | DONCASTER | Urban | Planned |  | 17 | 2431 | 143 | 1 | No
| 147702 | 2024-05-07 | 9:09 | 2024-05-07 | 13:55 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 171 | 48906 | 286 | 1 | No
| 147703 | 2024-08-07 | 8:01 | 2024-08-07 | 10:10 | FTN24 | FRANKSTON | Urban | Planned |  | 58 | 7491.6686 | 129.1667 | 1 | No
| 147712 | 19/07/2024 | 8:00 | 19/07/2024 | 16:00 | HGS31 | HASTINGS | Rural Short | Planned |  | 3 | 1440 | 480 | 1 | No
| 147712 | 19/07/2024 | 8:18 | 19/07/2024 | 11:51 | HGS31 | HASTINGS | Rural Short | Planned |  | 119 | 25347 | 213 | 1 | No
| 147713 | 19/07/2024 | 8:02 | 19/07/2024 | 10:35 | DN22 | DANDENONG | Urban | Planned |  | 60 | 9180 | 153 | 1 | No
| 147721 | 16/07/2024 | 8:26 | 16/07/2024 | 11:01 | RBD12 | ROSEBUD | Rural Short | Planned |  | 51 | 7905 | 155 | 1 | No
| 147745 | 2024-04-07 | 9:20 | 2024-04-07 | 12:30 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 17 | 3230 | 190 | 1 | No
| 147753 | 2024-10-07 | 8:20 | 2024-10-07 | 13:54 | STO14 | SORRENTO | Rural Short | Planned |  | 39 | 13026 | 334 | 1 | No
| 147755 | 19/07/2024 | 8:16 | 19/07/2024 | 10:21 | RWT24 | RINGWOOD | Urban | Planned |  | 37 | 4625 | 125 | 1 | No
| 147762 | 15/07/2024 | 9:00 | 15/07/2024 | 11:15 | RWT35 | RINGWOOD | Urban | Planned |  | 18 | 2430 | 135 | 1 | No
| 147763 | 15/07/2024 | 11:24 | 15/07/2024 | 13:04 | RWT35 | RINGWOOD | Urban | Planned |  | 51 | 5100 | 100 | 1 | No
| 147765 | 17/07/2024 | 8:00 | 17/07/2024 | 8:01 | RWT34 | RINGWOOD | Urban | Planned |  | 3 | 3 | 1 | 1 | No
| 147766 | 18/07/2024 | 8:10 | 18/07/2024 | 9:55 | RWT34 | RINGWOOD | Urban | Planned |  | 24 | 2520 | 105 | 1 | No
| 147767 | 18/07/2024 | 8:25 | 18/07/2024 | 15:33 | RWT34 | RINGWOOD | Urban | Planned |  | 55 | 23540 | 428 | 1 | No
| 147780 | 19/07/2024 | 8:18 | 19/07/2024 | 11:55 | RWT34 | RINGWOOD | Urban | Planned |  | 48 | 10416 | 217 | 1 | No
| 147809 | 2024-03-07 | 5:10 | 2024-03-07 | 6:10 | NW23 | NUNAWADING | Urban | Planned |  | 17 | 1020 | 60 | 1 | No
| 147812 | 16/07/2024 | 9:12 | 16/07/2024 | 12:42 | MTN24 | MORNINGTON | Rural Short | Planned |  | 46 | 9660 | 210 | 1 | No
| 147813 | 2025-05-02 | 19:00 | 2025-06-02 | 3:25 | CDA22 | CLARINDA | Urban | Planned |  | 23 | 11615 | 505 | 1 | No
| 147816 | 23/07/2024 | 8:26 | 23/07/2024 | 14:31 | STO14 | SORRENTO | Rural Short | Planned |  | 607 | 221555 | 365 | 1 | No
| 147818 | 28/08/2024 | 8:01 | 28/08/2024 | 14:37 | SR31 | SANDRINGHAM | Urban | Planned |  | 88 | 34848 | 396 | 1 | Yes
| 147819 | 2024-02-07 | 8:01 | 2024-02-07 | 11:06 | DN25 | DANDENONG | Urban | Planned |  | 42 | 7770 | 185 | 1 | No
| 147828 | 22/07/2024 | 8:44 | 22/07/2024 | 12:00 | DMA15 | DROMANA | Rural Short | Planned |  | 46 | 9016 | 196 | 1 | No
| 147840 | 2024-08-08 | 9:13 | 2024-08-08 | 11:25 | SR25 | SANDRINGHAM | Urban | Planned |  | 109 | 14388 | 132 | 1 | No
| 147843 | 2024-02-07 | 9:10 | 2024-02-07 | 14:45 | GW8 | GLEN WAVERLEY | Urban | Planned |  | 93 | 31155 | 335 | 1 | No
| 147849 | 2024-08-08 | 11:31 | 2024-08-08 | 16:01 | CM22 | CHELTENHAM | Urban | Planned |  | 2 | 540 | 270 | 1 | No
| 147849 | 2024-08-08 | 12:39 | 2024-08-08 | 13:41 | CM22 | CHELTENHAM | Urban | Planned |  | 58 | 3596 | 62 | 1 | No
| 147850 | 2024-07-07 | 13:31 | 2024-07-07 | 16:31 | KBH34 | KEYSBOROUGH | Urban | Planned |  | 3 | 540 | 180 | 1 | No
| 147856 | 2024-02-07 | 8:30 | 2024-02-07 | 17:47 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 89 | 49573 | 557 | 1 | No
| 147857 | 23/07/2024 | 9:10 | 23/07/2024 | 13:45 | MTN31 | MORNINGTON | Urban | Planned |  | 42 | 11550 | 275 | 1 | No
| 147866 | 24/10/2024 | 8:00 | 24/10/2024 | 16:00 | SR31 | SANDRINGHAM | Urban | Planned |  | 2 | 960 | 480 | 1 | No
| 147866 | 24/10/2024 | 8:07 | 24/10/2024 | 11:41 | SR31 | SANDRINGHAM | Urban | Planned |  | 88 | 18832 | 214 | 1 | No
| 147871 | 2024-11-07 | 8:00 | 2024-11-07 | 8:01 | EL22 | ELSTERNWICK | Urban | Planned |  | 2 | 1.3 | 0.65 | 1 | No
| 147878 | 2024-02-08 | 9:02 | 2024-02-08 | 14:26 | KBH32 | KEYSBOROUGH | Urban | Planned |  | 82 | 26568 | 324 | 1 | No
| 147880 | 2024-08-07 | 8:31 | 2024-08-07 | 15:31 | NW31 | NUNAWADING | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 147880 | 2024-08-07 | 9:43 | 2024-08-07 | 13:32 | NW31 | NUNAWADING | Urban | Planned |  | 120 | 27480 | 229 | 1 | No
| 147884 | 2024-08-07 | 9:41 | 2024-08-07 | 13:36 | DC7 | DONCASTER | Urban | Planned |  | 23 | 5405 | 235 | 1 | No
| 147886 | 2024-04-07 | 5:10 | 2024-04-07 | 5:25 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 1 | 15 | 15 | 1 | No
| 147888 | 2024-10-07 | 9:47 | 2024-10-07 | 14:02 | DC10 | DONCASTER | Urban | Planned |  | 43 | 10965 | 255 | 1 | No
| 147891 | 2024-12-07 | 8:00 | 2024-12-07 | 12:30 | SV32 | SPRINGVALE | Urban | Planned |  | 1 | 270 | 270 | 1 | No
| 147891 | 2024-12-07 | 8:03 | 2024-12-07 | 12:32 | SV32 | SPRINGVALE | Urban | Planned |  | 58 | 15602 | 269 | 1 | No
| 147893 | 2024-12-07 | 9:38 | 2024-12-07 | 13:07 | BU15 | BULLEEN | Urban | Planned |  | 290 | 60610 | 209 | 1 | No
| 147901 | 2024-01-07 | 7:01 | 2024-01-07 | 7:10 | RWT34 | RINGWOOD | Urban | Planned |  | 1 | 9 | 9 | 1 | No
| 147903 | 30/07/2024 | 8:15 | 30/07/2024 | 14:08 | STO21 | SORRENTO | Rural Short | Planned |  | 53 | 18709 | 353 | 1 | No
| 147906 | 2024-09-07 | 8:45 | 2024-09-07 | 13:50 | GW2 | GLEN WAVERLEY | Urban | Planned |  | 24 | 7320 | 305 | 1 | No
| 147907 | 23/07/2024 | 8:31 | 23/07/2024 | 18:39 | DN13 | DANDENONG | Urban | Planned |  | 116 | 70529.9372 | 608.0167 | 1 | No
| 147909 | 2024-10-07 | 8:31 | 2024-10-07 | 12:05 | DC10 | DONCASTER | Urban | Planned |  | 110 | 23540 | 214 | 1 | No
| 147911 | 2024-01-07 | 12:55 | 2024-02-07 | 14:35 | SVW41 | SPRINGVALE WEST | Urban | Planned |  | 1 | 1540 | 1540 | 1 | No
| 147918 | 16/07/2024 | 8:00 | 16/07/2024 | 16:00 | EW2 | ELWOOD | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 147918 | 16/07/2024 | 8:05 | 16/07/2024 | 11:32 | EW2 | ELWOOD | Urban | Planned |  | 142 | 29394 | 207 | 1 | No
| 147921 | 2024-11-07 | 8:13 | 2024-11-07 | 13:34 | STO21 | SORRENTO | Rural Short | Planned |  | 27 | 8667 | 321 | 1 | No
| 147922 | 2024-11-07 | 21:30 | 2024-11-07 | 23:48 | DVY34 | DANDENONG VALLEY | Urban | Planned |  | 1 | 138 | 138 | 1 | No
| 147924 | 2024-03-07 | 9:29 | 2024-03-07 | 15:12 | EB22 | EAST BURWOOD | Urban | Planned |  | 209 | 71687 | 343 | 1 | No
| 147925 | 14/07/2024 | 8:00 | 14/07/2024 | 16:00 | HGS23 | HASTINGS | Rural Short | Planned |  | 41 | 19680 | 480 | 1 | No
| 147926 | 2024-07-07 | 8:51 | 2024-07-07 | 14:20 | GW2 | GLEN WAVERLEY | Urban | Planned |  | 123 | 40467 | 329 | 1 | No
| 147931 | 2024-06-07 | 9:41 | 2024-06-07 | 15:21 | HT2 | HEATHERTON | Urban | Planned |  | 133 | 45220 | 340 | 1 | No
| 147934 | 2024-08-10 | 11:05 | 2024-08-10 | 12:40 | SS13 | SPRINGVALE SOUTH | Urban | Planned |  | 64 | 6080 | 95 | 1 | No
| 147941 | 14/07/2024 | 8:30 | 14/07/2024 | 13:00 | HT11 | HEATHERTON | Urban | Planned |  | 11 | 2970 | 270 | 1 | No
| 147941 | 14/07/2024 | 8:30 | 14/07/2024 | 13:00 | M11 | MENTONE | Urban | Planned |  | 4 | 1080 | 270 | 1 | No
| 147942 | 2024-10-07 | 8:07 | 2024-10-07 | 15:43 | LD5 | LYNDALE | Urban | Planned |  | 54 | 24624 | 456 | 1 | No
| 147956 | 24/07/2024 | 9:58 | 24/07/2024 | 12:29 | RBD21 | ROSEBUD | Rural Short | Planned |  | 2 | 302 | 151 | 1 | No
| 147963 | 30/07/2024 | 8:25 | 30/07/2024 | 10:49 | BU14 | BULLEEN | Urban | Planned |  | 40 | 5760 | 144 | 1 | No
| 147968 | 2024-11-07 | 8:03 | 2024-11-07 | 13:05 | NB31 | NORTH BRIGHTON | Urban | Planned |  | 133 | 40166 | 302 | 1 | No
| 147968 | 2024-11-07 | 8:03 | 2024-11-07 | 13:05 | NB33 | NORTH BRIGHTON | Urban | Planned |  | 3 | 906 | 302 | 1 | No
| 147971 | 2024-12-07 | 8:07 | 2024-12-07 | 17:00 | FTN25 | FRANKSTON | Urban | Planned |  | 110 | 58630 | 533 | 1 | No
| 147972 | 2024-08-07 | 23:32 | 2024-09-07 | 0:25 | EM11 | EAST MALVERN | Urban | Planned |  | 24 | 1272 | 53 | 1 | No
| 147985 | 2024-03-07 | 8:09 | 2024-03-07 | 14:00 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 48 | 16848 | 351 | 1 | No
| 147989 | 2024-04-07 | 8:34 | 2024-04-07 | 13:10 | NB32 | NORTH BRIGHTON | Urban | Planned |  | 39 | 10764 | 276 | 1 | No
| 147999 | 2024-12-07 | 8:17 | 2024-12-07 | 13:14 | FSH11 | FRANKSTON SOUTH | Urban | Planned |  | 31 | 9207 | 297 | 1 | No
| 148018 | 17/07/2024 | 9:46 | 17/07/2024 | 15:16 | DC10 | DONCASTER | Urban | Planned |  | 128 | 42240 | 330 | 1 | No
| 148024 | 2024-08-07 | 8:30 | 2024-08-07 | 13:05 | OAK26 | OAKLEIGH | Urban | Planned |  | 97 | 26675 | 275 | 1 | No
| 148025 | 13/07/2024 | 8:04 | 13/07/2024 | 15:43 | OAK32 | OAKLEIGH | Urban | Planned |  | 87 | 39933 | 459 | 1 | No
| 148025 | 13/07/2024 | 8:04 | 13/07/2024 | 15:43 | OE14 | OAKLEIGH EAST | Urban | Planned |  | 18 | 8262 | 459 | 1 | No
| 148028 | 13/07/2024 | 8:09 | 13/07/2024 | 16:34 | SS13 | SPRINGVALE SOUTH | Urban | Planned |  | 66 | 33330 | 505 | 1 | No
| 148035 | 16/07/2024 | 12:18 | 16/07/2024 | 14:21 | DMA14 | DROMANA | Urban | Planned |  | 49 | 6027 | 123 | 1 | No
| 148036 | 15/08/2024 | 8:06 | 15/08/2024 | 14:39 | M22 | MENTONE | Urban | Planned |  | 77 | 30261 | 393 | 1 | No
| 148038 | 2024-06-07 | 7:41 | 2024-06-07 | 9:16 | SVW53 | SPRINGVALE WEST | Urban | Planned |  | 2 | 190 | 95 | 1 | No
| 148041 | 2024-05-07 | 10:55 | 2024-05-07 | 15:38 | GW12 | GLEN WAVERLEY | Urban | Planned |  | 73 | 20659 | 283 | 1 | No
| 148041 | 2024-05-07 | 10:55 | 2024-05-07 | 15:38 | MGE23 | MULGRAVE | Urban | Planned |  | 17 | 4811 | 283 | 1 | No
| 148042 | 21/07/2024 | 8:05 | 21/07/2024 | 9:50 | RBD21 | ROSEBUD | Rural Short | Planned |  | 19 | 1995 | 105 | 1 | No
| 148049 | 25/07/2024 | 8:00 | 25/07/2024 | 13:30 | FTN13 | FRANKSTON | Urban | Planned |  | 402 | 132660 | 330 | 1 | No
| 148051 | 2024-12-07 | 10:16 | 2024-12-07 | 11:42 | RWT35 | RINGWOOD | Urban | Planned |  | 60 | 5160 | 86 | 1 | No
| 148053 | 17/07/2024 | 8:33 | 17/07/2024 | 15:51 | NW23 | NUNAWADING | Urban | Planned |  | 109 | 47742 | 438 | 1 | No
| 148056 | 22/07/2024 | 8:35 | 22/07/2024 | 11:47 | NW22 | NUNAWADING | Urban | Planned |  | 122 | 23424 | 192 | 1 | No
| 148059 | 15/07/2024 | 8:42 | 15/07/2024 | 8:43 | BH11 | BOX HILL | Urban | Planned |  | 39 | 39 | 1 | 1 | No
| 148060 | 14/08/2024 | 10:43 | 14/08/2024 | 13:20 | M25 | MENTONE | Urban | Planned |  | 8 | 1256 | 157 | 1 | No
| 148061 | 17/07/2024 | 8:37 | 17/07/2024 | 13:19 | DC5 | DONCASTER | Urban | Planned |  | 61 | 17202 | 282 | 1 | No
| 148066 | 19/07/2024 | 8:35 | 19/07/2024 | 16:09 | NW14 | NUNAWADING | Urban | Planned |  | 141 | 64014 | 454 | 1 | No
| 148066 | 19/07/2024 | 8:35 | 19/07/2024 | 16:09 | NW21 | NUNAWADING | Urban | Planned |  | 58 | 26332 | 454 | 1 | No
| 148067 | 19/07/2024 | 8:37 | 19/07/2024 | 13:27 | NW33 | NUNAWADING | Urban | Planned |  | 92 | 26680 | 290 | 1 | No
| 148068 | 19/07/2024 | 13:56 | 19/07/2024 | 15:03 | NW22 | NUNAWADING | Urban | Planned |  | 11 | 737 | 67 | 1 | No
| 148069 | 31/07/2024 | 8:30 | 31/07/2024 | 13:43 | LD2 | LYNDALE | Urban | Planned |  | 20 | 6260 | 313 | 1 | No
| 148071 | 13/07/2024 | 7:30 | 13/07/2024 | 16:30 | NP12 | NOBLE PARK | Urban | Planned |  | 8 | 4320 | 540 | 1 | No
| 148073 | 19/07/2024 | 8:32 | 19/07/2024 | 11:42 | NW31 | NUNAWADING | Urban | Planned |  | 83 | 15770 | 190 | 1 | No
| 148075 | 19/07/2024 | 12:11 | 19/07/2024 | 13:41 | NW22 | NUNAWADING | Urban | Planned |  | 44 | 3960 | 90 | 1 | No
| 148079 | 2024-11-07 | 8:20 | 2024-11-07 | 15:20 | HT11 | HEATHERTON | Urban | Planned |  | 123 | 51660 | 420 | 1 | No
| 148079 | 2024-11-07 | 8:20 | 2024-11-07 | 15:20 | HT2 | HEATHERTON | Urban | Planned |  | 60 | 25200 | 420 | 1 | No
| 148085 | 2024-07-08 | 9:31 | 2024-07-08 | 14:58 | DN10 | DANDENONG | Urban | Planned |  | 23 | 7521 | 327 | 1 | No
| 148093 | 18/07/2024 | 12:30 | 18/07/2024 | 12:31 | DVY12 | DANDENONG VALLEY | Urban | Planned |  | 27 | 27 | 1 | 1 | No
| 148094 | 16/07/2024 | 8:03 | 16/07/2024 | 14:50 | MTN32 | MORNINGTON | Rural Short | Planned |  | 63 | 25641 | 407 | 1 | No
| 148095 | 19/07/2024 | 8:15 | 19/07/2024 | 11:56 | NP24 | NOBLE PARK | Urban | Planned |  | 21 | 4641 | 221 | 1 | No
| 148097 | 2024-08-08 | 21:00 | 2024-09-08 | 2:59 | FSH24 | FRANKSTON SOUTH | Urban | Planned |  | 4 | 1436 | 359 | 1 | No
| 148099 | 2024-07-08 | 8:35 | 2024-07-08 | 11:40 | DN21 | DANDENONG | Urban | Planned |  | 11 | 2035 | 185 | 1 | No
| 148103 | 2024-09-07 | 8:35 | 2024-09-07 | 8:36 | NB36 | NORTH BRIGHTON | Urban | Planned |  | 2 | 2 | 1 | 1 | No
| 148104 | 2024-09-08 | 9:31 | 2024-09-08 | 13:43 | DN10 | DANDENONG | Urban | Planned |  | 21 | 5292 | 252 | 1 | No
| 148105 | 22/07/2024 | 8:30 | 22/07/2024 | 14:30 | DC10 | DONCASTER | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 148105 | 22/07/2024 | 8:31 | 22/07/2024 | 11:31 | DC10 | DONCASTER | Urban | Planned |  | 89 | 16020 | 180 | 1 | No
| 148106 | 22/07/2024 | 12:32 | 22/07/2024 | 13:42 | DC6 | DONCASTER | Urban | Planned |  | 20 | 1400 | 70 | 1 | No
| 148107 | 2024-04-07 | 7:31 | 2024-04-07 | 15:48 | MC15 | MORDIALLOC | Urban | Planned |  | 1 | 497.4667 | 497.4667 | 1 | No
| 148109 | 16/07/2024 | 9:15 | 16/07/2024 | 10:41 | DC1 | DONCASTER | Urban | Planned |  | 15 | 1290 | 86 | 1 | No
| 148109 | 16/07/2024 | 9:15 | 16/07/2024 | 10:41 | DC2 | DONCASTER | Urban | Planned |  | 26 | 2236 | 86 | 1 | No
| 148110 | 16/07/2024 | 12:04 | 16/07/2024 | 13:11 | DC2 | DONCASTER | Urban | Planned |  | 9 | 603 | 67 | 1 | No
| 148122 | 2024-11-07 | 9:20 | 2024-11-07 | 11:26 | RBD23 | ROSEBUD | Urban | Planned |  | 17 | 2142 | 126 | 1 | No
| 148123 | 14/08/2024 | 8:32 | 14/08/2024 | 12:14 | MGE12 | MULGRAVE | Urban | Planned |  | 32 | 7104 | 222 | 1 | No
| 148124 | 22/07/2024 | 10:00 | 22/07/2024 | 11:55 | WD36 | WEST DONCASTER | Urban | Planned |  | 43 | 4945 | 115 | 1 | No
| 148126 | 21/07/2024 | 8:00 | 21/07/2024 | 15:30 | DN22 | DANDENONG | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 148126 | 21/07/2024 | 8:30 | 21/07/2024 | 11:35 | DN21 | DANDENONG | Urban | Planned |  | 15 | 2775 | 185 | 1 | No
| 148126 | 21/07/2024 | 8:30 | 21/07/2024 | 11:35 | DN22 | DANDENONG | Urban | Planned |  | 104 | 19240 | 185 | 1 | No
| 148126 | 21/07/2024 | 8:30 | 21/07/2024 | 11:35 | DN4 | DANDENONG | Urban | Planned |  | 23 | 4255 | 185 | 1 | No
| 148129 | 14/07/2024 | 8:00 | 14/07/2024 | 12:34 | NO5 | NOTTING HILL | Urban | Planned |  | 28 | 7672 | 274 | 1 | No
| 148130 | 2024-09-07 | 1:34 | 2024-09-07 | 2:06 | K21 | GARDINER | Urban | Planned |  | 18 | 576 | 32 | 1 | No
| 148133 | 24/09/2024 | 8:15 | 24/09/2024 | 13:08 | MTN32 | MORNINGTON | Rural Short | Planned |  | 34 | 9962 | 293 | 1 | No
| 148134 | 21/08/2024 | 9:09 | 21/08/2024 | 12:55 | DN22 | DANDENONG | Urban | Planned |  | 18 | 4068 | 226 | 1 | No
| 148136 | 2024-12-07 | 8:46 | 2024-12-07 | 11:49 | MTN32 | MORNINGTON | Rural Short | Planned |  | 18 | 3294 | 183 | 1 | No
| 148137 | 20/08/2024 | 8:30 | 20/08/2024 | 11:42 | FTN12 | FRANKSTON | Urban | Planned |  | 23 | 4416 | 192 | 1 | No
| 148140 | 16/07/2024 | 8:47 | 16/07/2024 | 14:05 | MTN22 | MORNINGTON | Rural Short | Planned |  | 35 | 11130 | 318 | 1 | No
| 148142 | 2024-11-07 | 8:10 | 2024-11-07 | 14:30 | NW21 | NUNAWADING | Urban | Planned |  | 305 | 115900 | 380 | 1 | No
| 148143 | 22/08/2024 | 8:30 | 22/08/2024 | 11:05 | FTN12 | FRANKSTON | Urban | Planned |  | 8 | 1240 | 155 | 1 | No
| 148151 | 2024-10-07 | 9:38 | 2024-10-07 | 13:59 | EB32 | EAST BURWOOD | Urban | Planned |  | 15 | 3915 | 261 | 1 | No
| 148152 | 2024-09-07 | 9:35 | 2024-09-07 | 12:48 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 97 | 18721 | 193 | 1 | No
| 148153 | 2024-09-07 | 9:10 | 2024-09-07 | 13:55 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 148 | 42180 | 285 | 1 | No
| 148153 | 2024-09-07 | 9:10 | 2024-09-07 | 13:55 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 46 | 13110 | 285 | 1 | No
| 148156 | 24/07/2024 | 8:07 | 24/07/2024 | 13:06 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 17 | 5083 | 299 | 1 | No
| 148156 | 24/07/2024 | 8:07 | 24/07/2024 | 13:06 | LWN32 | LANGWARRIN | Rural Short | Planned |  | 190 | 56810 | 299 | 1 | No
| 148157 | 25/07/2024 | 8:09 | 25/07/2024 | 10:37 | K24 | GARDINER | Urban | Planned |  | 8 | 1184 | 148 | 1 | No
| 148161 | 21/07/2024 | 8:11 | 21/07/2024 | 13:06 | DN25 | DANDENONG | Urban | Planned |  | 97 | 28615 | 295 | 1 | No
| 148162 | 26/07/2024 | 9:14 | 26/07/2024 | 13:30 | RWT35 | RINGWOOD | Urban | Planned |  | 39 | 9984 | 256 | 1 | No
| 148164 | 2024-10-07 | 8:41 | 2024-10-07 | 15:19 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 575 | 228850 | 398 | 1 | No
| 148167 | 25/07/2024 | 9:20 | 25/07/2024 | 16:12 | DN13 | DANDENONG | Urban | Planned |  | 145 | 59740 | 412 | 1 | No
| 148174 | 15/07/2024 | 8:26 | 15/07/2024 | 10:32 | NP25 | NOBLE PARK | Urban | Planned |  | 54 | 6804 | 126 | 1 | No
| 148190 | 23/07/2024 | 8:11 | 23/07/2024 | 15:54 | K31 | GARDINER | Urban | Planned |  | 29 | 13427 | 463 | 1 | No
| 148194 | 2024-04-07 | 16:38 | 2024-04-07 | 18:21 | CRM13 | CARRUM | Urban | Planned |  | 1 | 103 | 103 | 1 | No
| 148196 | 2024-11-07 | 9:17 | 2024-11-07 | 13:10 | RWT34 | RINGWOOD | Urban | Planned |  | 46 | 10718 | 233 | 1 | No
| 148196 | 2024-11-07 | 9:17 | 2024-11-07 | 13:10 | RWT35 | RINGWOOD | Urban | Planned |  | 86 | 20038 | 233 | 1 | No
| 148198 | 23/08/2024 | 8:15 | 23/08/2024 | 11:45 | LD7 | LYNDALE | Urban | Planned |  | 4 | 840 | 210 | 1 | No
| 148201 | 31/07/2024 | 8:00 | 31/07/2024 | 16:30 | RBD12 | ROSEBUD | Rural Short | Planned |  | 1 | 510 | 510 | 1 | No
| 148201 | 31/07/2024 | 8:50 | 31/07/2024 | 16:15 | RBD12 | ROSEBUD | Rural Short | Planned |  | 37 | 16465 | 445 | 1 | No
| 148203 | 26/07/2024 | 8:03 | 26/07/2024 | 12:32 | FSH11 | FRANKSTON SOUTH | Urban | Planned |  | 95 | 25555 | 269 | 1 | No
| 148204 | 14/08/2024 | 9:01 | 14/08/2024 | 16:20 | MTN32 | MORNINGTON | Rural Short | Planned |  | 24 | 10536 | 439 | 1 | No
| 148207 | 13/07/2024 | 9:30 | 13/07/2024 | 18:05 | OAK23 | OAKLEIGH | Urban | Planned |  | 60 | 30900 | 515 | 1 | No
| 148210 | 26/07/2024 | 8:10 | 26/07/2024 | 12:43 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 66 | 18018 | 273 | 1 | No
| 148210 | 26/07/2024 | 8:10 | 26/07/2024 | 12:43 | NB36 | NORTH BRIGHTON | Urban | Planned |  | 3 | 819 | 273 | 1 | No
| 148214 | 29/08/2024 | 8:31 | 29/08/2024 | 12:13 | DN10 | DANDENONG | Urban | Planned |  | 22 | 4884 | 222 | 1 | No
| 148217 | 22/07/2024 | 7:30 | 22/07/2024 | 12:30 | FTN14 | FRANKSTON | Urban | Planned |  | 1 | 300 | 300 | 1 | No
| 148219 | 19/07/2024 | 7:33 | 19/07/2024 | 8:54 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 3 | 243 | 81 | 1 | No
| 148220 | 21/07/2024 | 8:02 | 21/07/2024 | 15:36 | MC22 | MORDIALLOC | Urban | Planned |  | 1 | 454 | 454 | 1 | No
| 148221 | 26/07/2024 | 8:52 | 26/07/2024 | 12:44 | MTN32 | MORNINGTON | Rural Short | Planned |  | 8 | 1856 | 232 | 1 | No
| 148222 | 2024-08-07 | 8:03 | 2024-08-07 | 13:04 | CDA22 | CLARINDA | Urban | Planned |  | 38 | 11438 | 301 | 1 | No
| 148223 | 24/07/2024 | 9:30 | 24/07/2024 | 13:21 | RBD13 | ROSEBUD | Urban | Planned |  | 380 | 87780 | 231 | 1 | No
| 148225 | 2024-01-08 | 22:03 | 2024-02-08 | 3:08 | BW22 | BURWOOD | Urban | Planned |  | 58 | 17690 | 305 | 1 | No
| 148227 | 2024-12-07 | 8:50 | 2024-12-07 | 13:30 | EB32 | EAST BURWOOD | Urban | Planned |  | 153 | 42840 | 280 | 1 | No
| 148230 | 2024-12-07 | 9:26 | 2024-12-07 | 18:10 | HGS31 | HASTINGS | Rural Short | Planned |  | 280 | 146720 | 524 | 1 | No
| 148231 | 25/07/2024 | 8:40 | 25/07/2024 | 11:03 | WD36 | WEST DONCASTER | Urban | Planned |  | 62 | 8866 | 143 | 1 | No
| 148232 | 19/07/2024 | 12:24 | 19/07/2024 | 13:55 | OE2 | OAKLEIGH EAST | Urban | Planned |  | 38 | 3458 | 91 | 1 | No
| 148240 | 26/07/2024 | 9:29 | 26/07/2024 | 15:50 | MTN32 | MORNINGTON | Rural Short | Planned |  | 17 | 6477 | 381 | 1 | No
| 148242 | 26/07/2024 | 8:30 | 26/07/2024 | 11:30 | STO21 | SORRENTO | Rural Short | Planned |  | 20 | 3600 | 180 | 1 | No
| 148248 | 25/07/2024 | 22:36 | 26/07/2024 | 23:40 | DSH32 | DANDENONG SOUTH | Urban | Planned |  | 1 | 1504 | 1504 | 1 | No
| 148251 | 16/07/2024 | 10:10 | 16/07/2024 | 13:30 | BC11 | BALACLAVA | Urban | Planned |  | 70 | 14000 | 200 | 1 | No
| 148252 | 17/07/2024 | 8:58 | 17/07/2024 | 11:59 | HGS33 | HASTINGS | Rural Short | Planned |  | 19 | 3439 | 181 | 1 | No
| 148264 | 18/07/2024 | 8:11 | 18/07/2024 | 15:13 | MGE34 | MULGRAVE | Urban | Planned |  | 42 | 17724 | 422 | 1 | No
| 148265 | 17/07/2024 | 9:08 | 17/07/2024 | 15:23 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 200 | 75000 | 375 | 1 | No
| 148268 | 18/07/2024 | 8:31 | 18/07/2024 | 15:03 | GW2 | GLEN WAVERLEY | Urban | Planned |  | 7 | 2744 | 392 | 1 | No
| 148269 | 2024-02-08 | 9:21 | 2024-02-08 | 12:00 | STO21 | SORRENTO | Rural Short | Planned |  | 6 | 954 | 159 | 1 | No
| 148270 | 16/07/2024 | 8:00 | 16/07/2024 | 8:01 | RBD24 | ROSEBUD | Urban | Planned |  | 49 | 49 | 1 | 1 | No
| 148271 | 17/07/2024 | 8:31 | 17/07/2024 | 15:19 | CFD15 | CAULFIELD | Urban | Planned |  | 43 | 17544 | 408 | 1 | No
| 148275 | 2024-12-07 | 9:50 | 2024-12-07 | 12:20 | BR4 | BEAUMARIS | Urban | Planned |  | 6 | 900 | 150 | 1 | No
| 148276 | 14/07/2024 | 5:00 | 14/07/2024 | 10:45 | OE5 | OAKLEIGH EAST | Urban | Planned |  | 97 | 33465 | 345 | 1 | No
| 148279 | 18/07/2024 | 9:30 | 18/07/2024 | 16:05 | STO14 | SORRENTO | Rural Short | Planned |  | 117 | 46215 | 395 | 1 | No
| 148280 | 2024-07-08 | 13:53 | 2024-07-08 | 15:16 | MTN35 | MORNINGTON | Rural Short | Planned |  | 76 | 6308 | 83 | 1 | No
| 148284 | 2024-11-08 | 7:30 | 2024-11-08 | 15:30 | M34 | MENTONE | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 148284 | 2024-11-08 | 7:37 | 2024-11-08 | 11:55 | M21 | MENTONE | Urban | Planned |  | 11 | 2838 | 258 | 1 | No
| 148284 | 2024-11-08 | 7:37 | 2024-11-08 | 11:55 | M34 | MENTONE | Urban | Planned |  | 195 | 50310 | 258 | 1 | No
| 148285 | 19/07/2024 | 8:32 | 19/07/2024 | 13:55 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 17 | 5491 | 323 | 1 | No
| 148286 | 17/07/2024 | 8:15 | 17/07/2024 | 11:58 | EM10 | EAST MALVERN | Urban | Planned |  | 55 | 12265 | 223 | 1 | No
| 148286 | 17/07/2024 | 8:15 | 17/07/2024 | 11:58 | EM3 | EAST MALVERN | Urban | Planned |  | 65 | 14495 | 223 | 1 | No
| 148291 | 2024-11-07 | 12:17 | 2024-11-07 | 12:52 | STO13 | SORRENTO | Urban | Planned |  | 36 | 1260 | 35 | 1 | No
| 148292 | 18/07/2024 | 9:32 | 18/07/2024 | 13:02 | NW14 | NUNAWADING | Urban | Planned |  | 122 | 25620 | 210 | 1 | No
| 148310 | 22/07/2024 | 8:01 | 22/07/2024 | 12:24 | HGS31 | HASTINGS | Rural Short | Planned |  | 53 | 13939 | 263 | 1 | No
| 148313 | 2024-11-08 | 9:29 | 2024-11-08 | 16:06 | DN25 | DANDENONG | Urban | Planned |  | 235 | 93295 | 397 | 1 | No
| 148315 | 30/07/2024 | 8:35 | 30/07/2024 | 10:50 | HGS22 | HASTINGS | Rural Short | Planned |  | 5 | 675 | 135 | 1 | No
| 148317 | 22/07/2024 | 8:03 | 22/07/2024 | 13:46 | OAK31 | OAKLEIGH | Urban | Planned |  | 37 | 12691 | 343 | 1 | No
| 148317 | 22/07/2024 | 8:03 | 22/07/2024 | 13:46 | OAK34 | OAKLEIGH | Urban | Planned |  | 31 | 10633 | 343 | 1 | No
| 148319 | 22/07/2024 | 8:00 | 22/07/2024 | 8:01 | HGS33 | HASTINGS | Rural Short | Planned |  | 1 | 1 | 1 | 1 | No
| 148320 | 25/07/2024 | 9:07 | 25/07/2024 | 9:53 | OR24 | ORMOND | Urban | Planned |  | 128 | 5888 | 46 | 1 | No
| 148322 | 17/07/2024 | 8:00 | 17/07/2024 | 15:00 | OAK22 | OAKLEIGH | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 148322 | 17/07/2024 | 8:28 | 17/07/2024 | 15:27 | OAK22 | OAKLEIGH | Urban | Planned |  | 66 | 27654 | 419 | 1 | No
| 148322 | 17/07/2024 | 8:28 | 17/07/2024 | 15:27 | OAK32 | OAKLEIGH | Urban | Planned |  | 1 | 419 | 419 | 1 | No
| 148323 | 18/07/2024 | 0:41 | 18/07/2024 | 1:13 | NO7 | NOTTING HILL | Urban | Planned |  | 32 | 1024 | 32 | 1 | No
| 148324 | 18/07/2024 | 2:34 | 18/07/2024 | 3:32 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 15 | 870 | 58 | 1 | No
| 148330 | 18/07/2024 | 9:16 | 18/07/2024 | 13:52 | SVW56 | SPRINGVALE WEST | Urban | Planned |  | 85 | 23460 | 276 | 1 | No
| 148337 | 28/07/2024 | 6:30 | 28/07/2024 | 14:40 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 13 | 6370 | 490 | 1 | No
| 148351 | 23/07/2024 | 8:08 | 23/07/2024 | 12:18 | HGS21 | HASTINGS | Rural Short | Planned |  | 58 | 14500 | 250 | 1 | No
| 148353 | 25/07/2024 | 8:00 | 25/07/2024 | 16:00 | HGS22 | HASTINGS | Rural Short | Planned |  | 1 | 480 | 480 | 1 | No
| 148353 | 25/07/2024 | 8:04 | 25/07/2024 | 15:37 | HGS22 | HASTINGS | Rural Short | Planned |  | 52 | 23556 | 453 | 1 | No
| 148354 | 28/07/2024 | 8:04 | 28/07/2024 | 10:24 | HGS32 | HASTINGS | Urban | Planned |  | 36 | 5040 | 140 | 1 | No
| 148355 | 30/07/2024 | 7:41 | 30/07/2024 | 14:00 | DMA14 | DROMANA | Urban | Planned |  | 145 | 54955 | 379 | 1 | No
| 148364 | 31/07/2024 | 10:36 | 31/07/2024 | 14:45 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 43 | 10707 | 249 | 1 | No
| 148365 | 19/07/2024 | 13:15 | 19/07/2024 | 15:48 | BH34 | BOX HILL | Urban | Planned |  | 114 | 17442 | 153 | 1 | No
| 148366 | 19/07/2024 | 8:00 | 19/07/2024 | 14:00 | EB32 | EAST BURWOOD | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 148366 | 19/07/2024 | 8:27 | 19/07/2024 | 11:38 | EB32 | EAST BURWOOD | Urban | Planned |  | 117 | 22347 | 191 | 1 | No
| 148371 | 21/07/2024 | 7:31 | 21/07/2024 | 15:31 | CRM35 | CARRUM | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 148371 | 21/07/2024 | 10:24 | 21/07/2024 | 16:12 | CRM35 | CARRUM | Urban | Planned |  | 156 | 54288 | 348 | 1 | No
| 148376 | 22/07/2024 | 8:30 | 22/07/2024 | 8:31 | BH21 | BOX HILL | Urban | Planned |  | 37 | 37 | 1 | 1 | No
| 148381 | 20/07/2024 | 7:30 | 20/07/2024 | 7:31 | NW21 | NUNAWADING | Urban | Planned |  | 204 | 204 | 1 | 1 | No
| 148385 | 25/07/2024 | 8:10 | 25/07/2024 | 13:19 | WD36 | WEST DONCASTER | Urban | Planned |  | 39 | 12051 | 309 | 1 | No
| 148387 | 2024-11-08 | 9:11 | 2024-11-08 | 13:00 | WD36 | WEST DONCASTER | Urban | Planned |  | 67 | 15343 | 229 | 1 | No
| 148391 | 30/07/2024 | 8:00 | 30/07/2024 | 12:00 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 1 | 240 | 240 | 1 | No
| 148391 | 30/07/2024 | 9:06 | 30/07/2024 | 10:40 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 41 | 3854 | 94 | 1 | No
| 148392 | 24/07/2024 | 8:39 | 24/07/2024 | 11:47 | MGE34 | MULGRAVE | Urban | Planned |  | 25 | 4700 | 188 | 1 | No
| 148393 | 30/07/2024 | 11:14 | 30/07/2024 | 11:58 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 23 | 1012 | 44 | 1 | No
| 148395 | 23/07/2024 | 9:30 | 23/07/2024 | 14:41 | EW2 | ELWOOD | Urban | Planned |  | 126 | 39186 | 311 | 1 | No
| 148396 | 2024-01-08 | 13:28 | 2024-01-08 | 14:09 | OE9 | OAKLEIGH EAST | Urban | Planned |  | 3 | 123 | 41 | 1 | No
| 148397 | 2024-02-08 | 8:00 | 2024-02-08 | 11:46 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 93 | 21018 | 226 | 1 | No
| 148400 | 2024-04-08 | 9:00 | 2024-04-08 | 12:22 | K24 | GARDINER | Urban | Planned |  | 14 | 2828 | 202 | 1 | No
| 148401 | 2024-08-08 | 8:21 | 2024-08-08 | 9:01 | EW8 | ELWOOD | Urban | Planned |  | 82 | 3280 | 40 | 1 | No
| 148402 | 30/07/2024 | 8:33 | 30/07/2024 | 11:25 | DC10 | DONCASTER | Urban | Planned |  | 47 | 8084 | 172 | 1 | No
| 148403 | 30/07/2024 | 8:05 | 30/07/2024 | 12:50 | NW33 | NUNAWADING | Urban | Planned |  | 76 | 21660 | 285 | 1 | No
| 148403 | 30/07/2024 | 8:05 | 30/07/2024 | 12:50 | RWT34 | RINGWOOD | Urban | Planned |  | 65 | 18525 | 285 | 1 | No
| 148404 | 30/07/2024 | 8:20 | 30/07/2024 | 9:57 | RWT24 | RINGWOOD | Urban | Planned |  | 11 | 1067 | 97 | 1 | No
| 148405 | 30/07/2024 | 11:38 | 30/07/2024 | 13:36 | RWT24 | RINGWOOD | Urban | Planned |  | 11 | 1298 | 118 | 1 | No
| 148406 | 2024-02-08 | 9:05 | 2024-02-08 | 10:12 | LWN34 | LANGWARRIN | Urban | Planned |  | 26 | 1742 | 67 | 1 | No
| 148408 | 26/09/2024 | 9:57 | 26/09/2024 | 12:35 | EB11 | EAST BURWOOD | Urban | Planned |  | 47 | 7426 | 158 | 1 | No
| 148411 | 2024-06-08 | 9:07 | 2024-06-08 | 13:28 | RWT24 | RINGWOOD | Urban | Planned |  | 68 | 17748 | 261 | 1 | No
| 148411 | 2024-06-08 | 9:07 | 2024-06-08 | 13:28 | RWT34 | RINGWOOD | Urban | Planned |  | 65 | 16965 | 261 | 1 | No
| 148412 | 2024-07-08 | 9:13 | 2024-07-08 | 12:51 | LWN23 | LANGWARRIN | Urban | Planned |  | 29 | 6322 | 218 | 1 | No
| 148413 | 24/07/2024 | 8:54 | 24/07/2024 | 12:49 | DC12 | DONCASTER | Urban | Planned |  | 6 | 1410 | 235 | 1 | No
| 148414 | 21/07/2024 | 9:01 | 21/07/2024 | 15:07 | FTN23 | FRANKSTON | Urban | Planned |  | 153 | 55998 | 366 | 1 | No
| 148415 | 24/07/2024 | 9:05 | 24/07/2024 | 11:15 | NW14 | NUNAWADING | Urban | Planned |  | 31 | 4030 | 130 | 1 | No
| 148415 | 24/07/2024 | 9:05 | 24/07/2024 | 11:15 | NW21 | NUNAWADING | Urban | Planned |  | 17 | 2210 | 130 | 1 | No
| 148419 | 24/07/2024 | 11:33 | 24/07/2024 | 14:39 | NW33 | NUNAWADING | Urban | Planned |  | 146 | 27156 | 186 | 1 | No
| 148420 | 18/07/2024 | 9:05 | 18/07/2024 | 12:08 | GW7 | GLEN WAVERLEY | Urban | Planned |  | 38 | 6954 | 183 | 1 | No
| 148421 | 26/07/2024 | 6:00 | 26/07/2024 | 14:33 | DC6 | DONCASTER | Urban | Planned |  | 40 | 20520 | 513 | 1 | No
| 148421 | 26/07/2024 | 6:00 | 26/07/2024 | 14:33 | DC7 | DONCASTER | Urban | Planned |  | 192 | 98496 | 513 | 1 | No
| 148422 | 26/07/2024 | 8:30 | 26/07/2024 | 16:00 | DC8 | DONCASTER | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 148422 | 26/07/2024 | 9:52 | 26/07/2024 | 14:45 | DC7 | DONCASTER | Urban | Planned |  | 66 | 19338 | 293 | 1 | No
| 148422 | 26/07/2024 | 9:52 | 26/07/2024 | 14:45 | DC8 | DONCASTER | Urban | Planned |  | 26 | 7618 | 293 | 1 | No
| 148423 | 19/07/2024 | 8:00 | 19/07/2024 | 16:00 | DC1 | DONCASTER | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 148423 | 19/07/2024 | 9:38 | 19/07/2024 | 13:45 | DC1 | DONCASTER | Urban | Planned |  | 50 | 12350 | 247 | 1 | No
| 148427 | 21/07/2024 | 7:00 | 21/07/2024 | 18:20 | M21 | MENTONE | Urban | Planned |  | 3 | 2040 | 680 | 1 | No
| 148434 | 31/07/2024 | 9:32 | 31/07/2024 | 11:04 | WD34 | WEST DONCASTER | Urban | Planned |  | 51 | 4692 | 92 | 1 | No
| 148441 | 2024-04-08 | 10:57 | 2024-04-08 | 13:26 | CFD13 | CAULFIELD | Urban | Planned |  | 36 | 5364 | 149 | 1 | No
| 148441 | 2024-04-08 | 10:57 | 2024-04-08 | 13:26 | EL35 | ELSTERNWICK | Urban | Planned |  | 41 | 6109 | 149 | 1 | No
| 148443 | 22/07/2024 | 9:47 | 22/07/2024 | 13:19 | CDA23 | CLARINDA | Urban | Planned |  | 55 | 11660 | 212 | 1 | No
| 148444 | 26/07/2024 | 15:35 | 26/07/2024 | 17:56 | DVY23 | DANDENONG VALLEY | Urban | Planned |  | 2 | 282 | 141 | 1 | No
| 148446 | 24/07/2024 | 7:31 | 25/07/2024 | 15:15 | MR33 | MOORABBIN | Urban | Planned |  | 5 | 9520 | 1904 | 1 | No
| 148449 | 2024-04-08 | 5:30 | 2024-04-08 | 5:31 | HGS32 | HASTINGS | Urban | Planned |  | 23 | 23 | 1 | 1 | No
| 148451 | 26/07/2024 | 7:44 | 26/07/2024 | 10:30 | NP12 | NOBLE PARK | Urban | Planned |  | 1 | 166 | 166 | 1 | No
| 148455 | 14/08/2024 | 8:31 | 14/08/2024 | 18:26 | MC34 | MORDIALLOC | Urban | Planned |  | 74 | 44030 | 595 | 1 | No
| 148456 | 2024-02-10 | 8:36 | 2024-02-10 | 13:17 | MC15 | MORDIALLOC | Urban | Planned |  | 45 | 12645 | 281 | 1 | No
| 148459 | 24/07/2024 | 8:20 | 24/07/2024 | 13:58 | MTN32 | MORNINGTON | Rural Short | Planned |  | 1 | 338 | 338 | 1 | No
| 148462 | 23/07/2024 | 8:10 | 23/07/2024 | 13:15 | CRM14 | CARRUM | Rural Short | Planned |  | 16 | 4880 | 305 | 1 | No
| 148475 | 2024-01-08 | 8:38 | 2024-01-08 | 17:40 | DN22 | DANDENONG | Urban | Planned |  | 92 | 49864 | 542 | 1 | No
| 148481 | 2024-06-08 | 9:16 | 2024-06-08 | 11:39 | STO21 | SORRENTO | Rural Short | Planned |  | 166 | 23738 | 143 | 1 | No
| 148483 | 2024-01-08 | 8:30 | 2024-01-08 | 11:55 | LWN33 | LANGWARRIN | Urban | Planned |  | 119 | 24395 | 205 | 1 | No
| 148485 | 22/07/2024 | 8:45 | 22/07/2024 | 14:09 | BW21 | BURWOOD | Urban | Planned |  | 24 | 7776 | 324 | 1 | No
| 148489 | 2024-06-08 | 13:02 | 2024-06-08 | 14:36 | MTN32 | MORNINGTON | Rural Short | Planned |  | 2 | 188 | 94 | 1 | No
| 148493 | 25/07/2024 | 8:00 | 25/07/2024 | 14:14 | MR22 | MOORABBIN | Urban | Planned |  | 84 | 31416 | 374 | 1 | No
| 148493 | 25/07/2024 | 8:00 | 25/07/2024 | 14:14 | MR24 | MOORABBIN | Urban | Planned |  | 113 | 42262 | 374 | 2 | No
| 148493 | 25/07/2024 | 8:00 | 25/07/2024 | 15:30 | MR24 | MOORABBIN | Urban | Planned |  | 3 | 1350 | 450 | 1 | No
| 148494 | 30/07/2024 | 8:12 | 30/07/2024 | 13:07 | NW23 | NUNAWADING | Urban | Planned |  | 182 | 53690 | 295 | 1 | No
| 148498 | 22/10/2024 | 20:40 | 23/10/2024 | 4:04 | CDA22 | CLARINDA | Urban | Planned |  | 27 | 11988 | 444 | 1 | No
| 148505 | 24/07/2024 | 10:21 | 24/07/2024 | 12:38 | NW21 | NUNAWADING | Urban | Planned |  | 4 | 548 | 137 | 1 | No
| 148508 | 2024-01-08 | 10:06 | 2024-01-08 | 11:32 | DC4 | DONCASTER | Urban | Planned |  | 15 | 1290 | 86 | 1 | No
| 148510 | 2024-08-08 | 9:08 | 2024-08-08 | 16:48 | HGS22 | HASTINGS | Rural Short | Planned |  | 133 | 61180 | 460 | 1 | No
| 148513 | 23/07/2024 | 8:30 | 23/07/2024 | 12:30 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 1 | 240 | 240 | 1 | No
| 148513 | 23/07/2024 | 8:50 | 23/07/2024 | 10:50 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 59 | 7080 | 120 | 1 | No
| 148515 | 23/07/2024 | 11:56 | 23/07/2024 | 14:05 | GW8 | GLEN WAVERLEY | Urban | Planned |  | 103 | 13287 | 129 | 1 | No
| 148517 | 30/07/2024 | 9:10 | 30/07/2024 | 12:18 | DN21 | DANDENONG | Urban | Planned |  | 26 | 4888 | 188 | 1 | No
| 148519 | 24/07/2024 | 8:07 | 24/07/2024 | 11:13 | EM11 | EAST MALVERN | Urban | Planned |  | 75 | 13950 | 186 | 1 | No
| 148519 | 24/07/2024 | 8:07 | 24/07/2024 | 11:13 | OAK23 | OAKLEIGH | Urban | Planned |  | 50 | 9300 | 186 | 1 | No
| 148522 | 23/07/2024 | 8:40 | 23/07/2024 | 8:50 | GW12 | GLEN WAVERLEY | Urban | Planned |  | 2 | 20 | 10 | 1 | No
| 148523 | 22/07/2024 | 8:41 | 22/07/2024 | 10:35 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 45 | 5130 | 114 | 1 | No
| 148524 | 22/07/2024 | 10:55 | 22/07/2024 | 12:35 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 36 | 3600 | 100 | 1 | No
| 148529 | 27/07/2024 | 7:37 | 27/07/2024 | 12:06 | GW12 | GLEN WAVERLEY | Urban | Planned |  | 36 | 9684 | 269 | 1 | No
| 148530 | 2024-06-08 | 9:05 | 2024-06-08 | 16:41 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 151 | 68856 | 456 | 1 | No
| 148536 | 26/07/2024 | 8:05 | 26/07/2024 | 12:08 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 68 | 16524 | 243 | 1 | No
| 148538 | 2024-09-08 | 9:17 | 2024-09-08 | 13:03 | FTN25 | FRANKSTON | Urban | Planned |  | 133 | 30058 | 226 | 1 | No
| 148543 | 28/07/2024 | 11:37 | 28/07/2024 | 14:05 | HGS21 | HASTINGS | Rural Short | Planned |  | 1 | 148 | 148 | 1 | No
| 148544 | 26/07/2024 | 10:21 | 26/07/2024 | 16:52 | HGS21 | HASTINGS | Rural Short | Planned |  | 135 | 52785 | 391 | 1 | No
| 148544 | 26/07/2024 | 10:21 | 26/07/2024 | 16:52 | HGS31 | HASTINGS | Rural Short | Planned |  | 9 | 3519 | 391 | 1 | No
| 148546 | 2024-01-08 | 5:49 | 2024-01-08 | 13:30 | NO7 | NOTTING HILL | Urban | Planned |  | 32 | 14752 | 461 | 1 | No
| 148547 | 2024-01-08 | 11:03 | 2024-01-08 | 16:07 | NW13 | NUNAWADING | Urban | Planned |  | 18 | 5472 | 304 | 1 | No
| 148561 | 2024-05-08 | 9:04 | 2024-05-08 | 14:37 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 121 | 40293 | 333 | 1 | No
| 148563 | 2024-05-08 | 13:30 | 2024-05-08 | 17:33 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 22 | 5346 | 243 | 1 | No
| 148567 | 15/08/2024 | 9:25 | 15/08/2024 | 15:49 | NW13 | NUNAWADING | Urban | Planned |  | 151 | 57984 | 384 | 1 | No
| 148570 | 2024-04-08 | 8:03 | 2024-04-08 | 9:44 | FTN12 | FRANKSTON | Urban | Planned |  | 2 | 202 | 101 | 1 | No
| 148578 | 28/07/2024 | 8:33 | 28/07/2024 | 11:52 | RD2 | RIVERSDALE | Urban | Planned |  | 11 | 2189 | 199 | 1 | No
| 148581 | 30/07/2024 | 11:02 | 30/07/2024 | 13:40 | CFD13 | CAULFIELD | Urban | Planned |  | 76 | 12008 | 158 | 1 | No
| 148595 | 2024-07-08 | 8:00 | 2024-07-08 | 9:00 | RBD23 | ROSEBUD | Urban | Planned |  | 1 | 60 | 60 | 1 | No
| 148595 | 2024-07-08 | 9:16 | 2024-07-08 | 9:27 | RBD23 | ROSEBUD | Urban | Planned |  | 951 | 10461 | 11 | 1 | No
| 148596 | 2024-02-08 | 9:48 | 2024-02-08 | 13:43 | MGE23 | MULGRAVE | Urban | Planned |  | 42 | 9870 | 235 | 1 | No
| 148598 | 2024-01-08 | 9:07 | 2024-01-08 | 13:11 | DN11 | DANDENONG | Urban | Planned |  | 1 | 244 | 244 | 1 | No
| 148599 | 2024-01-08 | 8:00 | 2024-01-08 | 15:30 | RBD13 | ROSEBUD | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 148599 | 2024-01-08 | 9:33 | 2024-01-08 | 12:40 | RBD13 | ROSEBUD | Urban | Planned |  | 40 | 7480 | 187 | 1 | No
| 148600 | 31/07/2024 | 9:06 | 31/07/2024 | 11:25 | FSH34 | FRANKSTON SOUTH | Urban | Planned |  | 24 | 3336 | 139 | 1 | No
| 148601 | 2024-03-08 | 5:30 | 2024-03-08 | 13:27 | DN25 | DANDENONG | Urban | Planned |  | 8 | 3816 | 477 | 1 | No
| 148603 | 2024-04-08 | 4:00 | 2024-04-08 | 14:22 | GW1 | GLEN WAVERLEY | Urban | Planned |  | 2 | 1244 | 622 | 1 | No
| 148610 | 2024-06-08 | 7:50 | 2024-06-08 | 8:25 | CRM24 | CARRUM | Urban | Planned |  | 3 | 105 | 35 | 1 | No
| 148620 | 2024-07-08 | 9:02 | 2024-07-08 | 13:08 | OAK26 | OAKLEIGH | Urban | Planned |  | 39 | 9594 | 246 | 1 | No
| 148621 | 27/07/2024 | 8:55 | 27/07/2024 | 12:10 | LD7 | LYNDALE | Urban | Planned |  | 3 | 585 | 195 | 1 | No
| 148629 | 2024-11-09 | 8:05 | 2024-11-09 | 14:38 | CRM15 | CARRUM | Urban | Planned |  | 1 | 393 | 393 | 1 | No
| 148634 | 30/07/2024 | 10:42 | 30/07/2024 | 14:22 | EM2 | EAST MALVERN | Urban | Planned |  | 35 | 7700 | 220 | 1 | No
| 148635 | 31/07/2024 | 8:51 | 31/07/2024 | 13:25 | EM5 | EAST MALVERN | Urban | Planned |  | 43 | 11782 | 274 | 1 | No
| 148636 | 31/07/2024 | 8:54 | 31/07/2024 | 13:54 | MGE23 | MULGRAVE | Urban | Planned |  | 22 | 6600 | 300 | 1 | No
| 148637 | 31/07/2024 | 8:35 | 31/07/2024 | 13:15 | GW7 | GLEN WAVERLEY | Urban | Planned |  | 124 | 34720 | 280 | 1 | No
| 148644 | 27/07/2024 | 6:34 | 27/07/2024 | 7:31 | MGE12 | MULGRAVE | Urban | Planned |  | 33 | 1881 | 57 | 1 | No
| 148647 | 16/08/2024 | 8:04 | 16/08/2024 | 12:33 | MTN32 | MORNINGTON | Rural Short | Planned |  | 13 | 3497 | 269 | 1 | No
| 148649 | 2024-01-08 | 9:28 | 2024-01-08 | 12:37 | EB32 | EAST BURWOOD | Urban | Planned |  | 24 | 4536 | 189 | 1 | No
| 148651 | 2024-01-08 | 12:15 | 2024-01-08 | 14:54 | EB32 | EAST BURWOOD | Urban | Planned |  | 28 | 4452 | 159 | 1 | No
| 148658 | 2024-12-08 | 9:14 | 2024-12-08 | 11:35 | RWT35 | RINGWOOD | Urban | Planned |  | 39 | 5499 | 141 | 1 | No
| 148661 | 2024-01-08 | 10:32 | 2024-01-08 | 14:16 | SR22 | SANDRINGHAM | Urban | Planned |  | 19 | 4256 | 224 | 1 | No
| 148670 | 2024-02-08 | 9:40 | 2024-02-08 | 12:09 | DMA21 | DROMANA | Urban | Planned |  | 124 | 18476 | 149 | 1 | No
| 148674 | 28/07/2024 | 7:30 | 28/07/2024 | 15:35 | MC14 | MORDIALLOC | Urban | Planned |  | 7 | 3395 | 485 | 1 | No
| 148676 | 28/07/2024 | 8:00 | 28/07/2024 | 11:18 | MC32 | MORDIALLOC | Urban | Planned |  | 17 | 3366 | 198 | 1 | No
| 148677 | 28/07/2024 | 13:50 | 28/07/2024 | 17:02 | MC34 | MORDIALLOC | Urban | Planned |  | 42 | 8064 | 192 | 1 | No
| 148678 | 2024-09-08 | 9:03 | 2024-09-08 | 15:45 | MTN32 | MORNINGTON | Rural Short | Planned |  | 16 | 6432 | 402 | 1 | No
| 148683 | 2024-04-08 | 7:58 | 2024-04-08 | 12:40 | FTN25 | FRANKSTON | Urban | Planned |  | 1 | 282 | 282 | 1 | No
| 148685 | 2024-01-08 | 9:34 | 2024-01-08 | 13:07 | BT22 | BENTLEIGH | Urban | Planned |  | 20 | 4260 | 213 | 1 | No
| 148687 | 29/07/2024 | 21:01 | 30/07/2024 | 4:18 | M23 | MENTONE | Urban | Planned |  | 15 | 6555 | 437 | 1 | No
| 148688 | 27/07/2024 | 8:08 | 27/07/2024 | 14:08 | HT1 | HEATHERTON | Urban | Planned |  | 273 | 98280 | 360 | 1 | No
| 148688 | 27/07/2024 | 8:08 | 27/07/2024 | 14:08 | M21 | MENTONE | Urban | Planned |  | 5 | 1800 | 360 | 1 | No
| 148694 | 2024-03-08 | 7:31 | 2024-03-08 | 14:33 | WD36 | WEST DONCASTER | Urban | Planned |  | 26 | 10980.2342 | 422.3167 | 1 | No
| 148695 | 30/07/2024 | 8:34 | 30/07/2024 | 12:47 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 82 | 20746 | 253 | 1 | No
| 148702 | 30/07/2024 | 11:00 | 30/07/2024 | 15:30 | HGS21 | HASTINGS | Rural Short | Planned |  | 1 | 270 | 270 | 1 | No
| 148702 | 30/07/2024 | 11:57 | 30/07/2024 | 14:32 | HGS21 | HASTINGS | Rural Short | Planned |  | 56 | 8680 | 155 | 1 | No
| 148704 | 2024-06-08 | 9:27 | 2024-06-08 | 14:59 | MGE32 | MULGRAVE | Urban | Planned |  | 36 | 11952 | 332 | 1 | No
| 148708 | 29/07/2024 | 8:19 | 29/07/2024 | 10:45 | NP36 | NOBLE PARK | Urban | Planned |  | 8 | 1168 | 146 | 1 | No
| 148710 | 2024-09-08 | 9:04 | 2024-09-08 | 11:16 | DC5 | DONCASTER | Urban | Planned |  | 36 | 4752 | 132 | 1 | No
| 148714 | 26/07/2024 | 12:25 | 26/07/2024 | 14:55 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 76 | 11400 | 150 | 1 | No
| 148715 | 2024-09-08 | 12:30 | 2024-09-08 | 13:27 | NW33 | NUNAWADING | Urban | Planned |  | 36 | 2052 | 57 | 1 | No
| 148722 | 2024-01-08 | 9:34 | 2024-01-08 | 12:29 | M12 | MENTONE | Urban | Planned |  | 29 | 5075 | 175 | 1 | No
| 148722 | 2024-01-08 | 9:34 | 2024-01-08 | 12:29 | M32 | MENTONE | Urban | Planned |  | 35 | 6125 | 175 | 1 | No
| 148729 | 2024-11-08 | 9:29 | 2024-11-08 | 16:30 | BT13 | BENTLEIGH | Urban | Planned |  | 75 | 31575 | 421 | 1 | No
| 148745 | 30/07/2024 | 9:29 | 30/07/2024 | 9:40 | LD6 | LYNDALE | Urban | Planned |  | 11 | 121 | 11 | 1 | No
| 148752 | 31/07/2024 | 10:48 | 31/07/2024 | 12:00 | HGS33 | HASTINGS | Rural Short | Planned |  | 4 | 288 | 72 | 1 | No
| 148753 | 31/07/2024 | 13:00 | 31/07/2024 | 14:08 | HGS33 | HASTINGS | Rural Short | Planned |  | 2 | 136 | 68 | 1 | No
| 148763 | 2024-05-08 | 10:18 | 2024-05-08 | 13:54 | EW8 | ELWOOD | Urban | Planned |  | 55 | 11880 | 216 | 1 | No
| 148773 | 2024-07-08 | 9:02 | 2024-07-08 | 14:31 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 45 | 14805 | 329 | 1 | No
| 148775 | 2024-06-08 | 9:27 | 2024-06-08 | 11:21 | MGE23 | MULGRAVE | Urban | Planned |  | 36 | 4104 | 114 | 1 | No
| 148776 | 2024-07-08 | 11:03 | 2024-07-08 | 16:46 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 25 | 8575 | 343 | 1 | No
| 148785 | 2024-11-09 | 8:30 | 2024-11-09 | 18:30 | DN22 | DANDENONG | Urban | Planned |  | 94 | 56400 | 600 | 1 | No
| 148793 | 2024-04-08 | 7:30 | 2024-04-08 | 17:30 | WD36 | WEST DONCASTER | Urban | Planned |  | 22 | 13194.8674 | 599.7667 | 1 | No
| 148798 | 2024-09-08 | 9:03 | 2024-09-08 | 15:49 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 74 | 30044 | 406 | 1 | No
| 148800 | 2024-02-08 | 8:30 | 2024-02-08 | 13:34 | DN11 | DANDENONG | Urban | Planned |  | 3 | 912 | 304 | 1 | No
| 148800 | 2024-02-08 | 8:30 | 2024-02-08 | 13:34 | DN13 | DANDENONG | Urban | Planned |  | 4 | 1216 | 304 | 1 | No
| 148801 | 2024-05-08 | 8:30 | 2024-05-08 | 15:31 | NW22 | NUNAWADING | Urban | Planned |  | 1 | 420.9833 | 420.9833 | 1 | No
| 148801 | 2024-05-08 | 10:12 | 2024-05-08 | 15:49 | NW22 | NUNAWADING | Urban | Planned |  | 148 | 49876 | 337 | 1 | No
| 148802 | 13/08/2024 | 23:25 | 14/08/2024 | 1:02 | BH12 | BOX HILL | Urban | Planned |  | 12 | 1164 | 97 | 1 | No
| 148803 | 13/08/2024 | 9:02 | 13/08/2024 | 13:13 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 115 | 28865 | 251 | 1 | No
| 148804 | 15/07/2024 | 8:11 | 15/07/2024 | 8:12 | RBD21 | ROSEBUD | Rural Short | Planned |  | 3 | 3 | 1 | 1 | No
| 148808 | 29/08/2024 | 8:20 | 29/08/2024 | 14:27 | STO21 | SORRENTO | Rural Short | Planned |  | 78 | 28626 | 367 | 1 | No
| 148809 | 20/08/2024 | 10:18 | 20/08/2024 | 14:41 | STO14 | SORRENTO | Rural Short | Planned |  | 93 | 24459 | 263 | 1 | No
| 148818 | 16/08/2024 | 6:02 | 16/08/2024 | 6:24 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 6 | 132 | 22 | 1 | No
| 148821 | 2024-02-08 | 9:21 | 2024-02-08 | 12:20 | STO14 | SORRENTO | Rural Short | Planned |  | 99 | 17721 | 179 | 1 | No
| 148828 | 20/08/2024 | 8:20 | 20/08/2024 | 11:27 | RBD14 | ROSEBUD | Urban | Planned |  | 41 | 7667 | 187 | 1 | No
| 148829 | 2024-10-08 | 9:07 | 2024-10-08 | 13:52 | CFD11 | CAULFIELD | Urban | Planned |  | 71 | 20235 | 285 | 1 | No
| 148830 | 16/08/2024 | 8:00 | 16/08/2024 | 16:30 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 148830 | 16/08/2024 | 8:05 | 16/08/2024 | 15:34 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 304 | 136496 | 449 | 1 | No
| 148831 | 22/08/2024 | 7:30 | 23/08/2024 | 17:30 | NP12 | NOBLE PARK | Urban | Planned |  | 1 | 2039.7167 | 2039.7167 | 1 | No
| 148839 | 2024-02-08 | 9:01 | 2024-02-08 | 14:49 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 30 | 10440 | 348 | 1 | No
| 148840 | 2024-10-09 | 8:00 | 2024-10-09 | 10:00 | MC12 | MORDIALLOC | Urban | Planned |  | 12 | 1440 | 120 | 1 | No
| 148854 | 2024-04-08 | 7:30 | 2024-04-08 | 15:30 | DVY33 | DANDENONG VALLEY | Urban | Planned |  | 11 | 5280 | 480 | 1 | No
| 148858 | 2024-04-08 | 10:48 | 2024-04-08 | 11:18 | SVW45 | SPRINGVALE WEST | Urban | Planned |  | 4 | 120 | 30 | 1 | No
| 148860 | 31/07/2024 | 8:00 | 31/07/2024 | 14:00 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 1 | 360 | 360 | 1 | No
| 148860 | 31/07/2024 | 8:01 | 31/07/2024 | 9:13 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 47 | 3384 | 72 | 1 | No
| 148863 | 2024-08-08 | 9:02 | 2024-08-08 | 16:17 | NO6 | NOTTING HILL | Urban | Planned |  | 68 | 29580 | 435 | 1 | No
| 148866 | 2024-07-08 | 10:06 | 2024-07-08 | 13:38 | BU22 | BULLEEN | Urban | Planned |  | 1 | 212 | 212 | 1 | No
| 148873 | 2024-07-08 | 8:00 | 2024-07-08 | 16:00 | SR21 | SANDRINGHAM | Urban | Planned |  | 9 | 4320 | 480 | 1 | No
| 148873 | 2024-07-08 | 9:00 | 2024-07-08 | 14:41 | SR21 | SANDRINGHAM | Urban | Planned |  | 157 | 53537 | 341 | 1 | No
| 148875 | 21/08/2024 | 9:50 | 21/08/2024 | 14:10 | STO14 | SORRENTO | Rural Short | Planned |  | 61 | 15860 | 260 | 1 | No
| 148886 | 23/08/2024 | 11:00 | 23/08/2024 | 15:44 | RBD14 | ROSEBUD | Urban | Planned |  | 56 | 15904 | 284 | 1 | No
| 148891 | 2024-06-08 | 12:02 | 2024-06-08 | 15:24 | FSH11 | FRANKSTON SOUTH | Urban | Planned |  | 60 | 12120 | 202 | 1 | No
| 148894 | 15/08/2024 | 9:19 | 15/08/2024 | 14:32 | STO13 | SORRENTO | Urban | Planned |  | 195 | 61035 | 313 | 1 | No
| 148900 | 13/08/2024 | 8:00 | 13/08/2024 | 20:30 | EW1 | ELWOOD | Urban | Planned |  | 706 | 529500 | 750 | 1 | No
| 148901 | 2024-07-08 | 6:50 | 2024-07-08 | 17:15 | EB23 | EAST BURWOOD | Urban | Planned |  | 2 | 1250 | 625 | 1 | No
| 148905 | 16/08/2024 | 8:25 | 16/08/2024 | 15:25 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 1 | 420 | 420 | 1 | No
| 148914 | 2024-07-08 | 9:03 | 2024-07-08 | 13:47 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 68 | 19312 | 284 | 1 | No
| 148915 | 2024-11-08 | 9:13 | 2024-11-08 | 11:39 | NW11 | NUNAWADING | Urban | Planned |  | 14 | 2044 | 146 | 1 | No
| 148915 | 2024-11-08 | 9:13 | 2024-11-08 | 11:39 | NW21 | NUNAWADING | Urban | Planned |  | 28 | 4088 | 146 | 1 | No
| 148921 | 23/08/2024 | 8:00 | 23/08/2024 | 13:30 | RBD14 | ROSEBUD | Urban | Planned |  | 9 | 2970 | 330 | 1 | No
| 148921 | 23/08/2024 | 8:10 | 23/08/2024 | 11:10 | RBD14 | ROSEBUD | Urban | Planned |  | 1 | 180 | 180 | 1 | No
| 148924 | 24/08/2024 | 7:32 | 24/08/2024 | 13:03 | BH21 | BOX HILL | Urban | Planned |  | 337 | 111547 | 331 | 1 | No
| 148927 | 2024-10-08 | 8:28 | 2024-10-08 | 15:14 | HGS31 | HASTINGS | Rural Short | Planned |  | 8 | 3248 | 406 | 1 | No
| 148934 | 2024-10-08 | 9:37 | 2024-10-08 | 13:45 | MGE31 | MULGRAVE | Urban | Planned |  | 12 | 2976 | 248 | 1 | No
| 148941 | 18/08/2024 | 6:55 | 18/08/2024 | 15:12 | NW22 | NUNAWADING | Urban | Planned |  | 10 | 4970 | 497 | 1 | No
| 148941 | 18/08/2024 | 6:55 | 18/08/2024 | 15:12 | RWT12 | RINGWOOD | Urban | Planned |  | 142 | 70574 | 497 | 1 | No
| 148945 | 13/08/2024 | 10:20 | 13/08/2024 | 14:14 | BH22 | BOX HILL | Urban | Planned |  | 11 | 2574 | 234 | 1 | No
| 148947 | 2024-06-09 | 11:40 | 2024-06-09 | 13:00 | RWT34 | RINGWOOD | Urban | Planned |  | 32 | 2560 | 80 | 1 | No
| 148949 | 18/08/2024 | 4:39 | 18/08/2024 | 5:18 | SVW55 | SPRINGVALE WEST | Urban | Planned |  | 2 | 78 | 39 | 1 | No
| 148952 | 2024-09-08 | 5:30 | 2024-09-08 | 5:31 | EW1 | ELWOOD | Urban | Planned |  | 97 | 97 | 1 | 1 | No
| 148952 | 2024-09-08 | 8:00 | 2024-09-08 | 15:30 | EW1 | ELWOOD | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 148954 | 18/08/2024 | 7:30 | 18/08/2024 | 8:17 | GW4 | GLEN WAVERLEY | Urban | Planned |  | 28 | 1316 | 47 | 1 | No
| 148960 | 18/08/2024 | 12:00 | 18/08/2024 | 12:20 | DVY14 | DANDENONG VALLEY | Urban | Planned |  | 1 | 20 | 20 | 1 | No
| 148962 | 2024-09-08 | 9:10 | 2024-09-08 | 16:48 | DMA23 | DROMANA | Rural Short | Planned |  | 40 | 18320 | 458 | 1 | No
| 148983 | 22/08/2024 | 9:18 | 22/08/2024 | 9:38 | RWT23 | RINGWOOD | Urban | Planned |  | 58 | 1160 | 20 | 1 | No
| 148984 | 25/08/2024 | 7:42 | 25/08/2024 | 8:26 | M21 | MENTONE | Urban | Planned |  | 4 | 176 | 44 | 1 | No
| 148985 | 25/08/2024 | 10:10 | 25/08/2024 | 10:43 | M34 | MENTONE | Urban | Planned |  | 11 | 363 | 33 | 1 | No
| 148988 | 30/08/2024 | 8:10 | 30/08/2024 | 12:31 | CRM35 | CARRUM | Urban | Planned |  | 112 | 29232 | 261 | 1 | No
| 148989 | 2024-08-08 | 9:01 | 2024-08-08 | 14:15 | RBD11 | ROSEBUD | Urban | Planned |  | 101 | 31714 | 314 | 1 | No
| 148994 | 2024-09-08 | 10:50 | 2024-09-08 | 11:51 | K21 | GARDINER | Urban | Planned |  | 57 | 3477 | 61 | 1 | No
| 148997 | 2024-09-08 | 13:27 | 2024-09-08 | 14:11 | K24 | GARDINER | Urban | Planned |  | 9 | 396 | 44 | 1 | No
| 149001 | 2024-09-08 | 9:35 | 2024-09-08 | 14:08 | BW35 | BURWOOD | Urban | Planned |  | 37 | 10101 | 273 | 1 | No
| 149004 | 2024-11-08 | 9:03 | 2024-11-08 | 13:52 | OAK34 | OAKLEIGH | Urban | Planned |  | 3 | 867 | 289 | 1 | No
| 149005 | 2024-09-08 | 9:05 | 2024-09-08 | 12:45 | NW31 | NUNAWADING | Urban | Planned |  | 2 | 440 | 220 | 1 | No
| 149019 | 2024-11-08 | 8:05 | 2024-11-08 | 13:35 | MGE22 | MULGRAVE | Urban | Planned |  | 45 | 14850 | 330 | 1 | No
| 149025 | 2024-12-08 | 11:54 | 2024-12-08 | 13:00 | STO21 | SORRENTO | Rural Short | Planned |  | 60 | 3960 | 66 | 1 | No
| 149028 | 2024-12-08 | 9:04 | 2024-12-08 | 15:12 | OAK23 | OAKLEIGH | Urban | Planned |  | 47 | 17296 | 368 | 1 | No
| 149028 | 2024-12-08 | 9:04 | 2024-12-08 | 15:12 | OAK24 | OAKLEIGH | Urban | Planned |  | 19 | 6992 | 368 | 1 | No
| 149029 | 13/08/2024 | 9:07 | 13/08/2024 | 13:58 | CDA23 | CLARINDA | Urban | Planned |  | 302 | 87882 | 291 | 1 | No
| 149034 | 14/08/2024 | 8:20 | 14/08/2024 | 11:05 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 9 | 1485 | 165 | 1 | No
| 149037 | 13/08/2024 | 9:05 | 13/08/2024 | 15:37 | GW7 | GLEN WAVERLEY | Urban | Planned |  | 39 | 15288 | 392 | 1 | No
| 149043 | 2024-11-08 | 9:45 | 2024-11-08 | 13:35 | HT11 | HEATHERTON | Urban | Planned |  | 78 | 17940 | 230 | 1 | No
| 149045 | 14/08/2024 | 9:00 | 14/08/2024 | 12:37 | K34 | GARDINER | Urban | Planned |  | 31 | 6727 | 217 | 1 | No
| 149050 | 13/08/2024 | 9:33 | 13/08/2024 | 16:49 | EM10 | EAST MALVERN | Urban | Planned |  | 99 | 43164 | 436 | 1 | No
| 149051 | 2024-08-09 | 8:30 | 2024-08-09 | 13:45 | K27 | GARDINER | Urban | Planned |  | 13 | 4095 | 315 | 1 | No
| 149063 | 26/08/2024 | 8:27 | 26/08/2024 | 13:12 | LWN32 | LANGWARRIN | Rural Short | Planned |  | 52 | 14820 | 285 | 1 | No
| 149064 | 21/08/2024 | 8:00 | 21/08/2024 | 11:50 | LWN32 | LANGWARRIN | Rural Short | Planned |  | 48 | 11040 | 230 | 1 | No
| 149069 | 15/08/2024 | 9:35 | 15/08/2024 | 12:40 | DC12 | DONCASTER | Urban | Planned |  | 28 | 5180 | 185 | 1 | No
| 149074 | 22/08/2024 | 8:00 | 22/08/2024 | 13:36 | DMA13 | DROMANA | Rural Short | Planned |  | 69 | 23184 | 336 | 1 | No
| 149075 | 16/08/2024 | 8:40 | 16/08/2024 | 10:06 | HGS33 | HASTINGS | Rural Short | Planned |  | 2 | 172 | 86 | 1 | No
| 149076 | 18/08/2024 | 8:13 | 18/08/2024 | 13:57 | EB31 | EAST BURWOOD | Urban | Planned |  | 27 | 9288 | 344 | 1 | No
| 149078 | 16/08/2024 | 8:07 | 16/08/2024 | 14:10 | RWT12 | RINGWOOD | Urban | Planned |  | 77 | 27951 | 363 | 1 | No
| 149078 | 16/08/2024 | 8:07 | 16/08/2024 | 14:10 | RWT24 | RINGWOOD | Urban | Planned |  | 132 | 47916 | 363 | 1 | No
| 149083 | 14/08/2024 | 8:00 | 14/08/2024 | 15:30 | EM5 | EAST MALVERN | Urban | Planned |  | 3 | 1350 | 450 | 1 | No
| 149083 | 14/08/2024 | 8:20 | 14/08/2024 | 15:00 | EM5 | EAST MALVERN | Urban | Planned |  | 203 | 81200 | 400 | 1 | No
| 149086 | 14/08/2024 | 9:00 | 14/08/2024 | 11:53 | KBH34 | KEYSBOROUGH | Urban | Planned |  | 61 | 10553 | 173 | 1 | No
| 149086 | 14/08/2024 | 9:00 | 14/08/2024 | 11:53 | KBH35 | KEYSBOROUGH | Urban | Planned |  | 51 | 8823 | 173 | 1 | No
| 149089 | 23/08/2024 | 8:16 | 23/08/2024 | 10:34 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 22 | 3036 | 138 | 1 | No
| 149091 | 24/08/2024 | 10:32 | 24/08/2024 | 12:39 | DSH31 | DANDENONG SOUTH | Urban | Planned |  | 29 | 3683 | 127 | 1 | No
| 149092 | 29/08/2024 | 8:01 | 29/08/2024 | 10:08 | BU14 | BULLEEN | Urban | Planned |  | 46 | 5847.3682 | 127.1167 | 1 | No
| 149098 | 13/08/2024 | 7:11 | 13/08/2024 | 7:34 | MC14 | MORDIALLOC | Urban | Planned |  | 4 | 92 | 23 | 1 | No
| 149106 | 21/08/2024 | 8:00 | 21/08/2024 | 12:05 | MTN35 | MORNINGTON | Rural Short | Planned |  | 2 | 490 | 245 | 1 | No
| 149107 | 15/08/2024 | 9:48 | 15/08/2024 | 14:14 | STO14 | SORRENTO | Rural Short | Planned |  | 57 | 15162 | 266 | 1 | No
| 149108 | 17/08/2024 | 8:30 | 17/08/2024 | 12:00 | BH11 | BOX HILL | Urban | Planned |  | 1 | 210 | 210 | 1 | No
| 149108 | 17/08/2024 | 8:45 | 17/08/2024 | 10:03 | BH11 | BOX HILL | Urban | Planned |  | 94 | 7332 | 78 | 1 | No
| 149111 | 16/08/2024 | 8:00 | 16/08/2024 | 10:55 | HT11 | HEATHERTON | Urban | Planned |  | 71 | 12425 | 175 | 1 | No
| 149116 | 17/08/2024 | 13:33 | 17/08/2024 | 15:10 | BH11 | BOX HILL | Urban | Planned |  | 19 | 1843 | 97 | 1 | No
| 149119 | 14/08/2024 | 9:38 | 14/08/2024 | 11:19 | GW1 | GLEN WAVERLEY | Urban | Planned |  | 5 | 505 | 101 | 1 | No
| 149127 | 20/08/2024 | 10:19 | 20/08/2024 | 15:00 | EL32 | ELSTERNWICK | Urban | Planned |  | 80 | 22480 | 281 | 1 | No
| 149133 | 16/08/2024 | 8:30 | 16/08/2024 | 13:30 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 2 | 600 | 300 | 1 | No
| 149133 | 16/08/2024 | 8:49 | 16/08/2024 | 11:05 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 60 | 8160 | 136 | 1 | No
| 149133 | 16/08/2024 | 8:49 | 16/08/2024 | 11:05 | NB35 | NORTH BRIGHTON | Urban | Planned |  | 74 | 10064 | 136 | 1 | No
| 149134 | 16/08/2024 | 8:20 | 16/08/2024 | 14:20 | EB32 | EAST BURWOOD | Urban | Planned |  | 119 | 42840 | 360 | 1 | No
| 149135 | 26/08/2024 | 8:20 | 26/08/2024 | 10:45 | DMA13 | DROMANA | Rural Short | Planned |  | 8 | 1160 | 145 | 1 | No
| 149137 | 20/08/2024 | 8:00 | 20/08/2024 | 16:00 | EM3 | EAST MALVERN | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 149137 | 20/08/2024 | 8:22 | 20/08/2024 | 13:22 | EM10 | EAST MALVERN | Urban | Planned |  | 55 | 16500 | 300 | 1 | No
| 149137 | 20/08/2024 | 8:22 | 20/08/2024 | 13:22 | EM3 | EAST MALVERN | Urban | Planned |  | 64 | 19200 | 300 | 1 | No
| 149138 | 15/08/2024 | 10:22 | 15/08/2024 | 13:55 | BH11 | BOX HILL | Urban | Planned |  | 3 | 639 | 213 | 1 | No
| 149139 | 16/08/2024 | 8:33 | 16/08/2024 | 11:15 | SR35 | SANDRINGHAM | Urban | Planned |  | 77 | 12474 | 162 | 1 | No
| 149140 | 13/08/2024 | 9:45 | 13/08/2024 | 10:01 | CRM24 | CARRUM | Urban | Planned |  | 2 | 32 | 16 | 1 | No
| 149141 | 16/08/2024 | 9:23 | 16/08/2024 | 12:21 | EB32 | EAST BURWOOD | Urban | Planned |  | 41 | 7298 | 178 | 1 | No
| 149157 | 13/08/2024 | 9:05 | 13/08/2024 | 10:45 | HGS31 | HASTINGS | Rural Short | Planned |  | 14 | 1400 | 100 | 1 | No
| 149158 | 13/08/2024 | 8:08 | 13/08/2024 | 10:17 | FSH11 | FRANKSTON SOUTH | Urban | Planned |  | 51 | 6579 | 129 | 1 | No
| 149158 | 13/08/2024 | 8:08 | 13/08/2024 | 10:17 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 10 | 1290 | 129 | 1 | No
| 149159 | 19/08/2024 | 8:30 | 19/08/2024 | 16:15 | FTN25 | FRANKSTON | Urban | Planned |  | 101 | 46965 | 465 | 1 | No
| 149160 | 19/08/2024 | 8:20 | 19/08/2024 | 11:05 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 25 | 4125 | 165 | 1 | No
| 149161 | 20/08/2024 | 8:13 | 20/08/2024 | 13:41 | FTN25 | FRANKSTON | Urban | Planned |  | 99 | 32472 | 328 | 1 | No
| 149162 | 20/08/2024 | 8:35 | 20/08/2024 | 10:35 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 9 | 1080 | 120 | 1 | No
| 149172 | 13/09/2024 | 8:00 | 13/09/2024 | 11:40 | OR34 | ORMOND | Urban | Planned |  | 67 | 14740 | 220 | 1 | No
| 149173 | 21/08/2024 | 8:00 | 21/08/2024 | 12:17 | FTN25 | FRANKSTON | Urban | Planned |  | 89 | 22873 | 257 | 1 | No
| 149174 | 2024-01-10 | 8:05 | 2024-01-10 | 11:57 | CRM35 | CARRUM | Urban | Planned |  | 32 | 7424 | 232 | 1 | No
| 149176 | 18/08/2024 | 8:04 | 18/08/2024 | 12:00 | DSH14 | DANDENONG SOUTH | Urban | Planned |  | 5 | 1180 | 236 | 1 | No
| 149177 | 2024-06-10 | 8:10 | 2024-06-10 | 11:31 | OR33 | ORMOND | Urban | Planned |  | 103 | 20703 | 201 | 1 | No
| 149181 | 15/10/2024 | 8:00 | 15/10/2024 | 15:00 | OR24 | ORMOND | Urban | Planned |  | 75 | 31500 | 420 | 1 | No
| 149187 | 13/09/2024 | 8:55 | 13/09/2024 | 10:20 | MTN23 | MORNINGTON | Urban | Planned |  | 194 | 16490 | 85 | 1 | No
| 149188 | 21/08/2024 | 1:00 | 21/08/2024 | 1:43 | EB31 | EAST BURWOOD | Urban | Planned |  | 17 | 731 | 43 | 1 | No
| 149189 | 21/08/2024 | 3:30 | 21/08/2024 | 3:54 | RWT35 | RINGWOOD | Urban | Planned |  | 1 | 24 | 24 | 1 | No
| 149190 | 15/08/2024 | 9:20 | 15/08/2024 | 11:46 | MTN32 | MORNINGTON | Rural Short | Planned |  | 10 | 1460 | 146 | 1 | No
| 149191 | 15/08/2024 | 14:00 | 15/08/2024 | 14:28 | MTN24 | MORNINGTON | Rural Short | Planned |  | 1 | 28 | 28 | 1 | No
| 149201 | 19/08/2024 | 8:42 | 19/08/2024 | 14:38 | BC23 | BALACLAVA | Urban | Planned |  | 151 | 53756 | 356 | 1 | No
| 149208 | 22/08/2024 | 9:28 | 22/08/2024 | 14:08 | MTN22 | MORNINGTON | Rural Short | Planned |  | 29 | 8120 | 280 | 1 | No
| 149210 | 25/08/2024 | 7:04 | 25/08/2024 | 9:07 | GW7 | GLEN WAVERLEY | Urban | Planned |  | 47 | 5781 | 123 | 1 | No
| 149211 | 22/08/2024 | 8:30 | 22/08/2024 | 12:31 | SV34 | SPRINGVALE | Urban | Planned |  | 15 | 3615 | 241 | 1 | No
| 149214 | 23/08/2024 | 4:17 | 23/08/2024 | 4:49 | NO3 | NOTTING HILL | Urban | Planned |  | 4 | 128 | 32 | 1 | No
| 149215 | 31/08/2024 | 8:14 | 31/08/2024 | 16:18 | NW21 | NUNAWADING | Urban | Planned |  | 204 | 98736 | 484 | 1 | No
| 149219 | 25/08/2024 | 9:29 | 26/08/2024 | 17:46 | NP34 | NOBLE PARK | Urban | Planned |  | 32 | 61984 | 1937 | 1 | No
| 149221 | 21/08/2024 | 8:00 | 21/08/2024 | 17:00 | EB32 | EAST BURWOOD | Urban | Planned |  | 132 | 71280 | 540 | 1 | No
| 149227 | 25/08/2024 | 8:00 | 25/08/2024 | 11:14 | MR15 | MOORABBIN | Urban | Planned |  | 17 | 3298 | 194 | 1 | No
| 149227 | 25/08/2024 | 8:00 | 25/08/2024 | 11:14 | MR23 | MOORABBIN | Urban | Planned |  | 22 | 4268 | 194 | 1 | No
| 149237 | 21/08/2024 | 8:56 | 21/08/2024 | 12:57 | EW2 | ELWOOD | Urban | Planned |  | 72 | 17352 | 241 | 1 | No
| 149239 | 25/08/2024 | 8:08 | 25/08/2024 | 9:58 | CDA24 | CLARINDA | Urban | Planned |  | 3 | 330 | 110 | 1 | No
| 149240 | 24/08/2024 | 7:01 | 24/08/2024 | 17:30 | HT7 | HEATHERTON | Urban | Planned |  | 1 | 629.3167 | 629.3167 | 1 | No
| 149240 | 24/08/2024 | 7:09 | 24/08/2024 | 7:19 | HT7 | HEATHERTON | Urban | Planned |  | 60 | 600 | 10 | 1 | No
| 149242 | 23/08/2024 | 8:24 | 23/08/2024 | 10:19 | M11 | MENTONE | Urban | Planned |  | 29 | 3335 | 115 | 1 | No
| 149246 | 2024-01-11 | 8:02 | 2024-01-11 | 12:22 | CRM11 | CARRUM | Urban | Planned |  | 6 | 1560 | 260 | 1 | No
| 149250 | 23/08/2024 | 8:01 | 23/08/2024 | 16:52 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 178 | 94518 | 531 | 1 | No
| 149266 | 29/08/2024 | 9:28 | 29/08/2024 | 12:08 | RBD21 | ROSEBUD | Rural Short | Planned |  | 31 | 4960 | 160 | 1 | No
| 149267 | 21/08/2024 | 8:15 | 21/08/2024 | 10:35 | EM8 | EAST MALVERN | Urban | Planned |  | 71 | 9940 | 140 | 1 | No
| 149271 | 19/08/2024 | 7:50 | 19/08/2024 | 12:55 | CRM14 | CARRUM | Rural Short | Planned |  | 13 | 3965 | 305 | 1 | No
| 149285 | 29/08/2024 | 20:31 | 30/08/2024 | 1:49 | SV34 | SPRINGVALE | Urban | Planned |  | 82 | 26076 | 318 | 1 | No
| 149287 | 2024-01-10 | 8:50 | 2024-01-10 | 12:00 | DMA23 | DROMANA | Rural Short | Planned |  | 6 | 1140 | 190 | 1 | No
| 149296 | 2024-05-09 | 8:18 | 2024-05-09 | 13:18 | GW6 | GLEN WAVERLEY | Urban | Planned |  | 20 | 6000 | 300 | 1 | No
| 149297 | 2024-08-09 | 8:00 | 2024-08-09 | 11:15 | DVY14 | DANDENONG VALLEY | Urban | Planned |  | 43 | 8385 | 195 | 1 | No
| 149299 | 17/09/2024 | 8:05 | 17/09/2024 | 10:20 | MTN32 | MORNINGTON | Rural Short | Planned |  | 56 | 7560 | 135 | 1 | No
| 149303 | 30/08/2024 | 8:00 | 30/08/2024 | 12:10 | DN10 | DANDENONG | Urban | Planned |  | 296 | 74000 | 250 | 1 | No
| 149304 | 25/08/2024 | 8:00 | 25/08/2024 | 16:30 | DC10 | DONCASTER | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 149304 | 25/08/2024 | 8:09 | 25/08/2024 | 14:47 | DC10 | DONCASTER | Urban | Planned |  | 293 | 116614 | 398 | 1 | No
| 149306 | 29/08/2024 | 8:29 | 29/08/2024 | 11:41 | M22 | MENTONE | Urban | Planned |  | 55 | 10560 | 192 | 1 | No
| 149306 | 29/08/2024 | 8:29 | 29/08/2024 | 11:41 | M35 | MENTONE | Urban | Planned |  | 15 | 2880 | 192 | 1 | No
| 149311 | 29/08/2024 | 8:03 | 29/08/2024 | 11:03 | M25 | MENTONE | Urban | Planned |  | 46 | 8280 | 180 | 1 | No
| 149314 | 18/08/2024 | 9:04 | 18/08/2024 | 12:56 | FTN23 | FRANKSTON | Urban | Planned |  | 132 | 30624 | 232 | 1 | No
| 149314 | 18/08/2024 | 9:04 | 18/08/2024 | 12:56 | FTN24 | FRANKSTON | Urban | Planned |  | 229 | 53128 | 232 | 1 | No
| 149318 | 2024-09-09 | 8:35 | 2024-09-09 | 12:12 | STO14 | SORRENTO | Rural Short | Planned |  | 19 | 4123 | 217 | 1 | No
| 149324 | 2024-06-09 | 8:33 | 2024-06-09 | 10:58 | RBD12 | ROSEBUD | Rural Short | Planned |  | 23 | 3335 | 145 | 1 | No
| 149335 | 24/08/2024 | 12:53 | 24/08/2024 | 14:01 | OE5 | OAKLEIGH EAST | Urban | Planned |  | 2 | 136 | 68 | 1 | No
| 149345 | 18/08/2024 | 8:00 | 18/08/2024 | 13:25 | SS13 | SPRINGVALE SOUTH | Urban | Planned |  | 64 | 20800 | 325 | 1 | No
| 149347 | 2024-02-10 | 8:51 | 2024-02-10 | 11:44 | DMA23 | DROMANA | Rural Short | Planned |  | 24 | 4152 | 173 | 1 | No
| 149349 | 20/09/2024 | 8:00 | 20/09/2024 | 10:30 | MTN21 | MORNINGTON | Urban | Planned |  | 117 | 17550 | 150 | 1 | No
| 149350 | 29/08/2024 | 8:30 | 29/08/2024 | 15:00 | HT11 | HEATHERTON | Urban | Planned |  | 1 | 390 | 390 | 1 | No
| 149350 | 29/08/2024 | 8:36 | 29/08/2024 | 12:57 | HT11 | HEATHERTON | Urban | Planned |  | 162 | 42282 | 261 | 1 | No
| 149360 | 18/09/2024 | 8:00 | 18/09/2024 | 15:00 | DMA13 | DROMANA | Rural Short | Planned |  | 41 | 17220 | 420 | 1 | No
| 149367 | 28/08/2024 | 8:49 | 28/08/2024 | 13:08 | FTN13 | FRANKSTON | Urban | Planned |  | 18 | 4662 | 259 | 1 | Yes
| 149369 | 2024-04-09 | 8:19 | 2024-04-09 | 15:00 | RWT34 | RINGWOOD | Urban | Planned |  | 45 | 18045 | 401 | 1 | No
| 149370 | 2024-05-09 | 8:00 | 2024-05-09 | 12:25 | CRM35 | CARRUM | Urban | Planned |  | 73 | 19345 | 265 | 2 | No
| 149370 | 2024-05-09 | 8:00 | 2024-05-09 | 16:00 | CRM35 | CARRUM | Urban | Planned |  | 5 | 2400 | 480 | 1 | No
| 149377 | 29/08/2024 | 7:45 | 29/08/2024 | 16:40 | DVY34 | DANDENONG VALLEY | Urban | Planned |  | 4 | 2140 | 535 | 1 | No
| 149381 | 2024-12-08 | 7:30 | 2024-12-08 | 10:30 | SVW44 | SPRINGVALE WEST | Urban | Planned |  | 1 | 180 | 180 | 1 | No
| 149382 | 29/08/2024 | 8:19 | 29/08/2024 | 16:14 | DMA15 | DROMANA | Rural Short | Planned |  | 25 | 11875 | 475 | 1 | No
| 149385 | 21/08/2024 | 8:26 | 21/08/2024 | 11:14 | HGS31 | HASTINGS | Rural Short | Planned |  | 13 | 2184 | 168 | 1 | No
| 149386 | 21/08/2024 | 8:00 | 21/08/2024 | 8:58 | HGS33 | HASTINGS | Rural Short | Planned |  | 154 | 8932 | 58 | 1 | No
| 149387 | 21/08/2024 | 10:10 | 21/08/2024 | 10:56 | HGS22 | HASTINGS | Rural Short | Planned |  | 4 | 184 | 46 | 1 | No
| 149389 | 23/08/2024 | 9:05 | 23/08/2024 | 11:25 | FTN25 | FRANKSTON | Urban | Planned |  | 39 | 5460 | 140 | 1 | No
| 149390 | 23/08/2024 | 8:02 | 23/08/2024 | 12:24 | DC10 | DONCASTER | Urban | Planned |  | 221 | 57902 | 262 | 1 | No
| 149391 | 2024-12-08 | 10:00 | 2024-12-08 | 13:00 | SVW44 | SPRINGVALE WEST | Urban | Planned |  | 1 | 180 | 180 | 1 | No
| 149398 | 21/08/2024 | 11:14 | 21/08/2024 | 12:42 | EB32 | EAST BURWOOD | Urban | Planned |  | 13 | 1144 | 88 | 1 | No
| 149418 | 30/08/2024 | 8:30 | 30/08/2024 | 12:10 | DN11 | DANDENONG | Urban | Planned |  | 101 | 22220 | 220 | 1 | No
| 149423 | 13/09/2024 | 8:10 | 13/09/2024 | 12:18 | RBD11 | ROSEBUD | Urban | Planned |  | 38 | 9424 | 248 | 1 | No
| 149431 | 23/08/2024 | 8:30 | 23/08/2024 | 15:30 | GW6 | GLEN WAVERLEY | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 149431 | 23/08/2024 | 8:33 | 23/08/2024 | 12:30 | GW6 | GLEN WAVERLEY | Urban | Planned |  | 27 | 6399 | 237 | 1 | No
| 149432 | 2024-05-09 | 9:15 | 2024-05-09 | 14:47 | STO21 | SORRENTO | Rural Short | Planned |  | 23 | 7636 | 332 | 1 | No
| 149436 | 28/08/2024 | 8:00 | 28/08/2024 | 12:29 | MTN24 | MORNINGTON | Rural Short | Planned |  | 20 | 5380 | 269 | 1 | Yes
| 149437 | 28/08/2024 | 8:00 | 28/08/2024 | 8:58 | GW12 | GLEN WAVERLEY | Urban | Planned |  | 28 | 1624 | 58 | 1 | Yes
| 149440 | 28/08/2024 | 9:25 | 28/08/2024 | 12:17 | GW12 | GLEN WAVERLEY | Urban | Planned |  | 54 | 9288 | 172 | 1 | Yes
| 149451 | 22/08/2024 | 8:30 | 22/08/2024 | 16:00 | SVW56 | SPRINGVALE WEST | Urban | Planned |  | 59 | 26550 | 450 | 1 | No
| 149454 | 25/08/2024 | 11:55 | 25/08/2024 | 14:23 | DC1 | DONCASTER | Urban | Planned |  | 179 | 26492 | 148 | 1 | No
| 149464 | 23/08/2024 | 6:35 | 23/08/2024 | 6:59 | SVW54 | SPRINGVALE WEST | Urban | Planned |  | 2 | 48 | 24 | 1 | No
| 149466 | 27/08/2024 | 8:04 | 27/08/2024 | 13:51 | GW12 | GLEN WAVERLEY | Urban | Planned |  | 79 | 27413 | 347 | 1 | No
| 149468 | 31/08/2024 | 8:05 | 31/08/2024 | 13:08 | M22 | MENTONE | Urban | Planned |  | 41 | 12423 | 303 | 1 | No
| 149472 | 2024-06-09 | 8:21 | 2024-06-09 | 13:17 | OR24 | ORMOND | Urban | Planned |  | 117 | 34632 | 296 | 1 | No
| 149481 | 14/09/2024 | 8:44 | 14/09/2024 | 13:19 | NO2 | NOTTING HILL | Urban | Planned |  | 221 | 60775 | 275 | 1 | No
| 149481 | 14/09/2024 | 8:44 | 14/09/2024 | 13:19 | NO5 | NOTTING HILL | Urban | Planned |  | 14 | 3850 | 275 | 1 | No
| 149489 | 24/08/2024 | 8:01 | 24/08/2024 | 14:20 | OAK32 | OAKLEIGH | Urban | Planned |  | 87 | 32983.1529 | 379.1167 | 1 | No
| 149489 | 24/08/2024 | 8:01 | 24/08/2024 | 14:20 | OE14 | OAKLEIGH EAST | Urban | Planned |  | 18 | 6824.1006 | 379.1167 | 1 | No
| 149493 | 15/09/2024 | 9:00 | 15/09/2024 | 14:30 | DN13 | DANDENONG | Urban | Planned |  | 62 | 20460 | 330 | 1 | No
| 149497 | 15/09/2024 | 11:00 | 15/09/2024 | 12:42 | OE5 | OAKLEIGH EAST | Urban | Planned |  | 11 | 1122 | 102 | 1 | No
| 149501 | 25/08/2024 | 8:09 | 25/08/2024 | 10:44 | DC1 | DONCASTER | Urban | Planned |  | 30 | 4650 | 155 | 1 | No
| 149502 | 26/08/2024 | 8:07 | 26/08/2024 | 9:20 | DC10 | DONCASTER | Urban | Planned |  | 57 | 4161 | 73 | 1 | No
| 149516 | 30/08/2024 | 8:35 | 30/08/2024 | 10:20 | KBH32 | KEYSBOROUGH | Urban | Planned |  | 201 | 21105 | 105 | 1 | No
| 149519 | 29/08/2024 | 8:45 | 29/08/2024 | 12:35 | EB31 | EAST BURWOOD | Urban | Planned |  | 34 | 7820 | 230 | 1 | No
| 149520 | 29/08/2024 | 13:11 | 29/08/2024 | 15:44 | EB31 | EAST BURWOOD | Urban | Planned |  | 16 | 2448 | 153 | 1 | No
| 149525 | 27/08/2024 | 8:10 | 27/08/2024 | 11:30 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 22 | 4400 | 200 | 1 | No
| 149531 | 2024-04-09 | 8:04 | 2024-04-09 | 13:22 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 30 | 9540 | 318 | 1 | No
| 149536 | 23/08/2024 | 8:06 | 23/08/2024 | 11:36 | LWN33 | LANGWARRIN | Urban | Planned |  | 131 | 27510 | 210 | 1 | No
| 149539 | 29/08/2024 | 8:24 | 29/08/2024 | 10:56 | CDA23 | CLARINDA | Urban | Planned |  | 24 | 3648 | 152 | 1 | No
| 149544 | 2024-12-09 | 8:40 | 2024-12-09 | 15:30 | LWN23 | LANGWARRIN | Urban | Planned |  | 52 | 21320 | 410 | 1 | No
| 149544 | 2024-12-09 | 8:40 | 2024-12-09 | 15:30 | LWN32 | LANGWARRIN | Rural Short | Planned |  | 26 | 10660 | 410 | 1 | No
| 149546 | 22/09/2024 | 8:00 | 22/09/2024 | 14:00 | MC23 | MORDIALLOC | Urban | Planned |  | 274 | 98608.0242 | 359.8833 | 1 | No
| 149546 | 22/09/2024 | 8:00 | 22/09/2024 | 14:00 | MC34 | MORDIALLOC | Urban | Planned |  | 7 | 2519.1831 | 359.8833 | 1 | No
| 149550 | 26/08/2024 | 8:04 | 26/08/2024 | 16:17 | EB31 | EAST BURWOOD | Urban | Planned |  | 136 | 67048 | 493 | 1 | No
| 149551 | 18/09/2024 | 9:25 | 18/09/2024 | 9:30 | FTN13 | FRANKSTON | Urban | Planned |  | 93 | 465 | 5 | 1 | No
| 149557 | 27/08/2024 | 21:30 | 27/08/2024 | 21:45 | GW11 | GLEN WAVERLEY | Urban | Planned |  | 1 | 15 | 15 | 1 | No
| 149558 | 27/08/2024 | 8:47 | 27/08/2024 | 13:06 | HGS31 | HASTINGS | Rural Short | Planned |  | 27 | 6993 | 259 | 1 | No
| 149559 | 26/08/2024 | 10:04 | 26/08/2024 | 10:42 | LD6 | LYNDALE | Urban | Planned |  | 11 | 418 | 38 | 1 | No
| 149562 | 27/08/2024 | 9:30 | 27/08/2024 | 12:30 | LD33 | LYNDALE | Urban | Planned |  | 1 | 180 | 180 | 1 | No
| 149562 | 27/08/2024 | 9:37 | 27/08/2024 | 11:26 | LD33 | LYNDALE | Urban | Planned |  | 110 | 11990 | 109 | 1 | No
| 149565 | 28/08/2024 | 9:20 | 28/08/2024 | 15:58 | WD34 | WEST DONCASTER | Urban | Planned |  | 46 | 18308 | 398 | 1 | Yes
| 149568 | 2024-04-09 | 8:30 | 2024-04-09 | 15:30 | EB32 | EAST BURWOOD | Urban | Planned |  | 74 | 31080 | 420 | 1 | No
| 149570 | 2024-05-09 | 8:36 | 2024-05-09 | 13:27 | HT4 | HEATHERTON | Urban | Planned |  | 1 | 291 | 291 | 1 | No
| 149570 | 2024-05-09 | 8:36 | 2024-05-09 | 13:27 | HT8 | HEATHERTON | Urban | Planned |  | 30 | 8730 | 291 | 1 | No
| 149571 | 2024-09-10 | 8:10 | 2024-09-10 | 10:20 | RBD23 | ROSEBUD | Urban | Planned |  | 6 | 780 | 130 | 1 | No
| 149575 | 27/08/2024 | 8:05 | 27/08/2024 | 8:12 | LD6 | LYNDALE | Urban | Planned |  | 4 | 28 | 7 | 1 | No
| 149579 | 27/08/2024 | 8:42 | 27/08/2024 | 14:05 | HGS22 | HASTINGS | Rural Short | Planned |  | 5 | 1615 | 323 | 1 | No
| 149581 | 2024-10-09 | 8:15 | 2024-10-09 | 10:40 | RWT24 | RINGWOOD | Urban | Planned |  | 35 | 5075 | 145 | 1 | No
| 149582 | 2024-12-09 | 8:00 | 2024-12-09 | 10:15 | M13 | MENTONE | Urban | Planned |  | 83 | 11205 | 135 | 1 | No
| 149583 | 2024-12-09 | 8:40 | 2024-12-09 | 15:00 | RWT24 | RINGWOOD | Urban | Planned |  | 32 | 12160 | 380 | 1 | No
| 149584 | 17/09/2024 | 8:40 | 17/09/2024 | 14:10 | RWT24 | RINGWOOD | Urban | Planned |  | 66 | 21780 | 330 | 1 | No
| 149586 | 22/09/2024 | 10:56 | 22/09/2024 | 12:35 | RWT34 | RINGWOOD | Urban | Planned |  | 7 | 693 | 99 | 1 | No
| 149587 | 27/08/2024 | 10:00 | 27/08/2024 | 10:01 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 2 | 2 | 1 | 1 | No
| 149592 | 21/08/2024 | 8:00 | 21/08/2024 | 8:15 | MTN35 | MORNINGTON | Rural Short | Planned |  | 52 | 780 | 15 | 2 | No
| 149592 | 21/08/2024 | 8:00 | 21/08/2024 | 8:30 | MTN35 | MORNINGTON | Rural Short | Planned |  | 1 | 30 | 30 | 1 | No
| 149593 | 27/08/2024 | 8:15 | 27/08/2024 | 8:55 | DN6 | DANDENONG | Urban | Planned |  | 100 | 4000 | 40 | 1 | No
| 149596 | 19/09/2024 | 8:10 | 19/09/2024 | 12:55 | STO21 | SORRENTO | Rural Short | Planned |  | 217 | 61845 | 285 | 1 | No
| 149598 | 17/09/2024 | 8:59 | 17/09/2024 | 12:33 | FTN13 | FRANKSTON | Urban | Planned |  | 62 | 13268 | 214 | 1 | No
| 149607 | 2024-03-09 | 9:30 | 2024-03-09 | 14:30 | BC6 | BALACLAVA | Urban | Planned |  | 50 | 15000 | 300 | 1 | No
| 149608 | 25/08/2024 | 8:00 | 25/08/2024 | 13:33 | SR26 | SANDRINGHAM | Urban | Planned |  | 4 | 1331.7332 | 332.9333 | 1 | No
| 149615 | 2024-05-09 | 8:35 | 2024-05-09 | 11:50 | EB32 | EAST BURWOOD | Urban | Planned |  | 14 | 2730 | 195 | 1 | No
| 149616 | 2024-05-09 | 12:28 | 2024-05-09 | 14:45 | EB32 | EAST BURWOOD | Urban | Planned |  | 13 | 1781 | 137 | 1 | No
| 149616 | 2024-05-09 | 12:28 | 2024-05-09 | 14:45 | RWT35 | RINGWOOD | Urban | Planned |  | 64 | 8768 | 137 | 1 | No
| 149617 | 28/08/2024 | 8:09 | 28/08/2024 | 9:50 | RWT12 | RINGWOOD | Urban | Planned |  | 3 | 303 | 101 | 1 | Yes
| 149620 | 27/08/2024 | 13:00 | 27/08/2024 | 15:30 | DMA23 | DROMANA | Rural Short | Planned |  | 1 | 150 | 150 | 1 | No
| 149620 | 27/08/2024 | 13:49 | 27/08/2024 | 13:59 | DMA23 | DROMANA | Rural Short | Planned |  | 40 | 400 | 10 | 1 | No
| 149621 | 2024-04-09 | 8:14 | 2024-04-09 | 16:40 | NW23 | NUNAWADING | Urban | Planned |  | 54 | 27324 | 506 | 1 | No
| 149624 | 28/08/2024 | 10:30 | 28/08/2024 | 11:30 | NW14 | NUNAWADING | Urban | Planned |  | 24 | 1440 | 60 | 1 | Yes
| 149625 | 2024-04-09 | 5:00 | 2024-04-09 | 7:10 | SVW53 | SPRINGVALE WEST | Urban | Planned |  | 34 | 4420 | 130 | 1 | No
| 149627 | 2024-04-09 | 8:45 | 2024-04-09 | 14:37 | RBD23 | ROSEBUD | Urban | Planned |  | 403 | 141856 | 352 | 1 | No
| 149630 | 15/09/2024 | 12:01 | 15/09/2024 | 14:35 | EB32 | EAST BURWOOD | Urban | Planned |  | 51 | 7854 | 154 | 1 | No
| 149631 | 2024-05-09 | 8:32 | 2024-05-09 | 12:35 | SR24 | SANDRINGHAM | Urban | Planned |  | 3 | 729 | 243 | 1 | No
| 149632 | 15/09/2024 | 8:00 | 15/09/2024 | 14:00 | GW12 | GLEN WAVERLEY | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 149633 | 2024-10-09 | 8:00 | 2024-10-09 | 15:20 | LD4 | LYNDALE | Urban | Planned |  | 149 | 65560 | 440 | 1 | No
| 149639 | 29/08/2024 | 9:28 | 29/08/2024 | 12:20 | MGE12 | MULGRAVE | Urban | Planned |  | 29 | 4988 | 172 | 1 | No
| 149643 | 2024-05-09 | 8:50 | 2024-05-09 | 12:40 | MGE13 | MULGRAVE | Urban | Planned |  | 14 | 3220 | 230 | 1 | No
| 149656 | 29/08/2024 | 8:29 | 29/08/2024 | 11:54 | DC5 | DONCASTER | Urban | Planned |  | 74 | 15170 | 205 | 1 | No
| 149662 | 24/09/2024 | 8:01 | 24/09/2024 | 17:13 | MGE12 | MULGRAVE | Urban | Planned |  | 1 | 552 | 552 | 1 | No
| 149670 | 2024-08-09 | 8:42 | 2024-08-09 | 15:39 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 154 | 64218 | 417 | 1 | No
| 149671 | 22/09/2024 | 8:00 | 22/09/2024 | 10:45 | K34 | GARDINER | Urban | Planned |  | 47 | 7755 | 165 | 1 | No
| 149672 | 22/09/2024 | 13:05 | 22/09/2024 | 15:00 | EM6 | EAST MALVERN | Urban | Planned |  | 1 | 115 | 115 | 1 | No
| 149677 | 20/09/2024 | 12:00 | 20/09/2024 | 14:30 | RBD23 | ROSEBUD | Urban | Planned |  | 1 | 150 | 150 | 1 | No
| 149680 | 2024-04-10 | 11:55 | 2024-04-10 | 14:20 | RWT24 | RINGWOOD | Urban | Planned |  | 48 | 6960 | 145 | 1 | No
| 149682 | 30/08/2024 | 9:00 | 30/08/2024 | 12:00 | RBD23 | ROSEBUD | Urban | Planned |  | 12 | 2160 | 180 | 1 | No
| 149683 | 2024-05-09 | 8:30 | 2024-05-09 | 16:10 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 29 | 13340 | 460 | 1 | No
| 149688 | 30/08/2024 | 8:05 | 30/08/2024 | 15:00 | STO14 | SORRENTO | Rural Short | Planned |  | 36 | 14940 | 415 | 1 | No
| 149696 | 2024-05-09 | 6:46 | 2024-05-09 | 8:25 | MR12 | MOORABBIN | Urban | Planned |  | 94 | 9306 | 99 | 1 | No
| 149698 | 2024-06-09 | 9:55 | 2024-06-09 | 11:40 | STO13 | SORRENTO | Urban | Planned |  | 32 | 3360 | 105 | 1 | No
| 149700 | 30/08/2024 | 5:30 | 30/08/2024 | 5:31 | RBD13 | ROSEBUD | Urban | Planned |  | 275 | 275 | 1 | 1 | No
| 149701 | 2024-10-09 | 8:15 | 2024-10-09 | 14:32 | BU11 | BULLEEN | Urban | Planned |  | 72 | 27144 | 377 | 1 | No
| 149704 | 29/08/2024 | 8:15 | 29/08/2024 | 14:50 | MTN31 | MORNINGTON | Urban | Planned |  | 28 | 11060 | 395 | 1 | No
| 149710 | 28/08/2024 | 8:36 | 28/08/2024 | 13:23 | MGE31 | MULGRAVE | Urban | Planned |  | 155 | 44485 | 287 | 1 | Yes
| 149711 | 16/09/2024 | 22:15 | 17/09/2024 | 5:00 | CRM23 | CARRUM | Urban | Planned |  | 27 | 10935 | 405 | 1 | No
| 149714 | 25/08/2024 | 9:00 | 25/08/2024 | 12:00 | MC22 | MORDIALLOC | Urban | Planned |  | 1 | 180 | 180 | 1 | No
| 149721 | 2024-08-09 | 7:01 | 2024-08-09 | 15:33 | BH33 | BOX HILL | Urban | Planned |  | 12 | 6144 | 512 | 1 | No
| 149728 | 2024-04-09 | 8:20 | 2024-04-09 | 13:45 | OR25 | ORMOND | Urban | Planned |  | 80 | 26000 | 325 | 1 | No
| 149729 | 2024-09-12 | 21:50 | 2024-10-12 | 4:30 | SR24 | SANDRINGHAM | Urban | Planned |  | 70 | 28000 | 400 | 1 | No
| 149732 | 31/08/2024 | 8:45 | 31/08/2024 | 12:45 | SR31 | SANDRINGHAM | Urban | Planned |  | 17 | 4080 | 240 | 1 | No
| 149733 | 14/09/2024 | 8:50 | 14/09/2024 | 10:43 | M21 | MENTONE | Urban | Planned |  | 28 | 3164 | 113 | 1 | No
| 149736 | 2024-05-09 | 12:12 | 2024-05-09 | 14:25 | NB34 | NORTH BRIGHTON | Urban | Planned |  | 5 | 665 | 133 | 1 | No
| 149738 | 30/08/2024 | 8:18 | 30/08/2024 | 10:33 | CDA22 | CLARINDA | Urban | Planned |  | 41 | 5535 | 135 | 1 | No
| 149742 | 31/08/2024 | 13:45 | 31/08/2024 | 15:15 | EW9 | ELWOOD | Urban | Planned |  | 1 | 90 | 90 | 1 | No
| 149752 | 2024-06-09 | 9:45 | 2024-06-09 | 12:20 | K25 | GARDINER | Urban | Planned |  | 7 | 1085 | 155 | 1 | No
| 149757 | 2024-11-09 | 8:00 | 2024-11-09 | 11:50 | RBD21 | ROSEBUD | Rural Short | Planned |  | 19 | 4370 | 230 | 1 | No
| 149760 | 2024-10-09 | 8:30 | 2024-10-09 | 11:30 | KBH32 | KEYSBOROUGH | Urban | Planned |  | 33 | 5940 | 180 | 1 | No
| 149760 | 2024-10-09 | 8:30 | 2024-10-09 | 11:30 | NP36 | NOBLE PARK | Urban | Planned |  | 22 | 3960 | 180 | 1 | No
| 149764 | 2024-03-10 | 8:00 | 2024-03-10 | 16:00 | CRM14 | CARRUM | Rural Short | Planned |  | 1 | 480 | 480 | 1 | No
| 149764 | 2024-03-10 | 8:09 | 2024-03-10 | 13:36 | CRM14 | CARRUM | Rural Short | Planned |  | 443 | 144861 | 327 | 1 | No
| 149765 | 2024-03-09 | 8:43 | 2024-03-09 | 15:42 | MTN34 | MORNINGTON | Urban | Planned |  | 15 | 6285 | 419 | 1 | No
| 149767 | 14/09/2024 | 16:30 | 15/09/2024 | 2:00 | MGE24 | MULGRAVE | Urban | Planned |  | 1 | 570 | 570 | 1 | No
| 149772 | 2024-07-09 | 8:00 | 2024-07-09 | 10:05 | HT7 | HEATHERTON | Urban | Planned |  | 2 | 250 | 125 | 1 | No
| 149773 | 2024-08-09 | 8:30 | 2024-08-09 | 11:18 | CDA22 | CLARINDA | Urban | Planned |  | 86 | 14448 | 168 | 1 | No
| 149775 | 2024-06-09 | 8:00 | 2024-06-09 | 16:00 | HGS21 | HASTINGS | Rural Short | Planned |  | 1 | 480 | 480 | 1 | No
| 149783 | 2024-05-09 | 9:45 | 2024-05-09 | 15:30 | EL35 | ELSTERNWICK | Urban | Planned |  | 15 | 5175 | 345 | 1 | No
| 149787 | 2024-07-09 | 11:29 | 2024-07-09 | 12:25 | CDA24 | CLARINDA | Urban | Planned |  | 13 | 728 | 56 | 1 | No
| 149793 | 2024-01-09 | 8:10 | 2024-01-09 | 11:17 | HT1 | HEATHERTON | Urban | Planned |  | 57 | 10659 | 187 | 1 | No
| 149795 | 2024-12-09 | 8:48 | 2024-12-09 | 17:01 | MTN31 | MORNINGTON | Urban | Planned |  | 30 | 14786.499 | 492.8833 | 1 | No
| 149799 | 24/10/2024 | 8:00 | 24/10/2024 | 14:15 | STO21 | SORRENTO | Rural Short | Planned |  | 264 | 99000 | 375 | 1 | No
| 149804 | 2024-06-09 | 8:00 | 2024-06-09 | 11:55 | OR25 | ORMOND | Urban | Planned |  | 127 | 29845 | 235 | 1 | No
| 149806 | 2024-10-09 | 22:01 | 2024-11-09 | 5:57 | CDA22 | CLARINDA | Urban | Planned |  | 2 | 952 | 476 | 1 | No
| 149808 | 2024-11-09 | 8:15 | 2024-11-09 | 15:30 | EM5 | EAST MALVERN | Urban | Planned |  | 115 | 50025 | 435 | 1 | No
| 149811 | 2024-11-09 | 8:30 | 2024-11-09 | 14:55 | BU22 | BULLEEN | Urban | Planned |  | 1 | 385 | 385 | 1 | No
| 149812 | 2024-04-09 | 8:00 | 2024-04-09 | 10:31 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 78 | 11778 | 151 | 1 | No
| 149813 | 2024-04-10 | 8:02 | 2024-04-10 | 12:12 | SR21 | SANDRINGHAM | Urban | Planned |  | 235 | 58750 | 250 | 1 | No
| 149813 | 2024-04-10 | 8:02 | 2024-04-10 | 12:12 | SR36 | SANDRINGHAM | Urban | Planned |  | 33 | 8250 | 250 | 1 | No
| 149817 | 13/09/2024 | 4:00 | 13/09/2024 | 4:10 | DMA15 | DROMANA | Rural Short | Planned |  | 5 | 48.5 | 9.7 | 1 | No
| 149818 | 2024-10-09 | 23:17 | 2024-11-09 | 1:35 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 12 | 1656 | 138 | 1 | No
| 149820 | 13/09/2024 | 1:41 | 13/09/2024 | 1:53 | DMA21 | DROMANA | Urban | Planned |  | 15 | 180 | 12 | 1 | No
| 149833 | 2024-05-09 | 8:35 | 2024-05-09 | 11:50 | NB22 | NORTH BRIGHTON | Urban | Planned |  | 62 | 12090 | 195 | 1 | No
| 149835 | 2024-09-09 | 8:04 | 2024-09-09 | 10:45 | M21 | MENTONE | Urban | Planned |  | 44 | 7084 | 161 | 1 | No
| 149844 | 2024-11-09 | 8:00 | 2024-11-09 | 16:00 | MTN24 | MORNINGTON | Rural Short | Planned |  | 2 | 960 | 480 | 1 | No
| 149845 | 2024-04-09 | 8:08 | 2024-04-09 | 15:36 | MTN22 | MORNINGTON | Rural Short | Planned |  | 155 | 69440 | 448 | 1 | No
| 149846 | 20/09/2024 | 8:30 | 20/09/2024 | 12:20 | EW8 | ELWOOD | Urban | Planned |  | 126 | 28980 | 230 | 1 | No
| 149847 | 2024-07-09 | 7:30 | 2024-07-09 | 16:21 | BW32 | BURWOOD | Urban | Planned |  | 27 | 14337 | 531 | 1 | No
| 149858 | 13/09/2024 | 8:13 | 13/09/2024 | 10:23 | EM8 | EAST MALVERN | Urban | Planned |  | 69 | 8970 | 130 | 1 | No
| 149860 | 25/09/2024 | 8:57 | 25/09/2024 | 11:59 | DMA23 | DROMANA | Rural Short | Planned |  | 135 | 24570 | 182 | 1 | No
| 149863 | 2024-07-09 | 8:00 | 2024-07-09 | 11:56 | MC32 | MORDIALLOC | Urban | Planned |  | 16 | 3774.1328 | 235.8833 | 1 | No
| 149864 | 2024-07-09 | 13:09 | 2024-07-09 | 16:14 | MC34 | MORDIALLOC | Urban | Planned |  | 42 | 7770 | 185 | 1 | No
| 149873 | 24/09/2024 | 8:40 | 24/09/2024 | 14:58 | EB13 | EAST BURWOOD | Urban | Planned |  | 142 | 53676 | 378 | 1 | No
| 149873 | 24/09/2024 | 8:40 | 24/09/2024 | 14:58 | EB32 | EAST BURWOOD | Urban | Planned |  | 13 | 4914 | 378 | 1 | No
| 149882 | 25/09/2024 | 8:18 | 25/09/2024 | 12:15 | EB32 | EAST BURWOOD | Urban | Planned |  | 21 | 4977 | 237 | 1 | No
| 149888 | 26/09/2024 | 8:35 | 26/09/2024 | 12:06 | DC10 | DONCASTER | Urban | Planned |  | 26 | 5486 | 211 | 1 | No
| 149893 | 17/09/2024 | 8:48 | 17/09/2024 | 14:18 | EW1 | ELWOOD | Urban | Planned |  | 97 | 32010 | 330 | 1 | No
| 149896 | 2024-06-09 | 9:00 | 2024-06-09 | 10:52 | STO23 | SORRENTO | Urban | Planned |  | 23 | 2576 | 112 | 1 | No
| 149898 | 2024-08-09 | 8:44 | 2024-08-09 | 13:00 | HT11 | HEATHERTON | Urban | Planned |  | 103 | 26368 | 256 | 1 | No
| 149899 | 2024-12-09 | 8:03 | 2024-12-09 | 12:30 | DC1 | DONCASTER | Urban | Planned |  | 17 | 4539 | 267 | 1 | No
| 149904 | 13/09/2024 | 8:30 | 13/09/2024 | 15:30 | EB31 | EAST BURWOOD | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 149904 | 13/09/2024 | 8:31 | 13/09/2024 | 14:10 | EB23 | EAST BURWOOD | Urban | Planned |  | 28 | 9492 | 339 | 1 | No
| 149904 | 13/09/2024 | 8:31 | 13/09/2024 | 14:10 | EB31 | EAST BURWOOD | Urban | Planned |  | 79 | 26781 | 339 | 1 | No
| 149922 | 2024-10-09 | 8:45 | 2024-10-09 | 12:23 | STO13 | SORRENTO | Urban | Planned |  | 41 | 8938 | 218 | 1 | No
| 149936 | 19/09/2024 | 8:06 | 19/09/2024 | 12:47 | RBD23 | ROSEBUD | Urban | Planned |  | 296 | 83176 | 281 | 1 | No
| 149940 | 2024-01-10 | 8:35 | 2024-01-10 | 13:40 | FTN14 | FRANKSTON | Urban | Planned |  | 53 | 16165 | 305 | 1 | No
| 149941 | 2024-06-09 | 8:00 | 2024-06-09 | 16:30 | NO31 | NOTTING HILL | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 149941 | 2024-06-09 | 8:00 | 2024-06-09 | 16:30 | NO6 | NOTTING HILL | Urban | Planned |  | 7 | 3570 | 510 | 1 | No
| 149941 | 2024-06-09 | 8:26 | 2024-06-09 | 16:10 | NO31 | NOTTING HILL | Urban | Planned |  | 58 | 26912 | 464 | 1 | No
| 149941 | 2024-06-09 | 8:26 | 2024-06-09 | 16:10 | NO6 | NOTTING HILL | Urban | Planned |  | 308 | 142912 | 464 | 1 | No
| 149942 | 2024-11-09 | 11:30 | 2024-11-09 | 12:10 | HGS31 | HASTINGS | Rural Short | Planned |  | 8 | 320 | 40 | 1 | No
| 149944 | 24/08/2024 | 14:52 | 24/08/2024 | 17:35 | OE5 | OAKLEIGH EAST | Urban | Planned |  | 10 | 1630 | 163 | 1 | No
| 149946 | 2024-11-09 | 8:00 | 2024-11-09 | 13:30 | M35 | MENTONE | Urban | Planned |  | 101 | 33330 | 330 | 1 | No
| 149950 | 2024-09-09 | 15:45 | 2024-09-09 | 16:11 | DMA23 | DROMANA | Rural Short | Planned |  | 27 | 702 | 26 | 1 | No
| 149955 | 2024-07-09 | 7:30 | 2024-07-09 | 15:49 | NP12 | NOBLE PARK | Urban | Planned |  | 8 | 3988.2664 | 498.5333 | 1 | No
| 149957 | 2024-10-09 | 8:00 | 2024-10-09 | 12:00 | EB11 | EAST BURWOOD | Urban | Planned |  | 110 | 26400 | 240 | 1 | No
| 149963 | 14/09/2024 | 8:30 | 15/09/2024 | 15:30 | SV20 | SPRINGVALE | Urban | Planned |  | 1 | 1860 | 1860 | 1 | No
| 149966 | 2024-10-09 | 9:00 | 2024-10-09 | 13:15 | NW11 | NUNAWADING | Urban | Planned |  | 37 | 9435 | 255 | 1 | No
| 149966 | 2024-10-09 | 9:00 | 2024-10-09 | 13:15 | NW13 | NUNAWADING | Urban | Planned |  | 39 | 9945 | 255 | 1 | No
| 149970 | 2024-10-09 | 8:40 | 2024-10-09 | 12:25 | MR12 | MOORABBIN | Urban | Planned |  | 84 | 18900 | 225 | 1 | No
| 149973 | 2024-10-09 | 13:45 | 2024-10-09 | 16:05 | M11 | MENTONE | Urban | Planned |  | 23 | 3220 | 140 | 1 | No
| 149973 | 2024-10-09 | 13:45 | 2024-10-09 | 16:05 | M31 | MENTONE | Urban | Planned |  | 43 | 6020 | 140 | 1 | No
| 149982 | 2024-02-10 | 8:16 | 2024-02-10 | 14:39 | RBD23 | ROSEBUD | Urban | Planned |  | 248 | 94984 | 383 | 1 | No
| 149997 | 20/09/2024 | 8:05 | 20/09/2024 | 11:54 | MTN24 | MORNINGTON | Rural Short | Planned |  | 7 | 1603 | 229 | 1 | No
| 150007 | 2024-12-09 | 8:38 | 2024-12-09 | 14:00 | RBD11 | ROSEBUD | Urban | Planned |  | 1 | 322 | 322 | 1 | No
| 150011 | 2024-10-09 | 9:34 | 2024-10-09 | 13:57 | RBD11 | ROSEBUD | Urban | Planned |  | 1 | 263 | 263 | 1 | No
| 150012 | 13/09/2024 | 8:28 | 13/09/2024 | 11:59 | RBD23 | ROSEBUD | Urban | Planned |  | 137 | 28907 | 211 | 1 | No
| 150014 | 2024-11-09 | 8:00 | 2024-11-09 | 14:00 | LWN24 | LANGWARRIN | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 150014 | 2024-11-09 | 8:00 | 2024-11-09 | 14:00 | LWN35 | LANGWARRIN | Urban | Planned |  | 50 | 18000 | 360 | 1 | No
| 150017 | 2024-10-09 | 8:00 | 2024-10-09 | 13:00 | WD36 | WEST DONCASTER | Urban | Planned |  | 109 | 32700 | 300 | 1 | No
| 150028 | 2024-11-09 | 10:30 | 2024-11-09 | 16:00 | LWN35 | LANGWARRIN | Urban | Planned |  | 7 | 2310 | 330 | 1 | No
| 150029 | 2024-06-10 | 6:40 | 2024-06-10 | 16:00 | EB12 | EAST BURWOOD | Urban | Planned |  | 95 | 53200 | 560 | 1 | No
| 150029 | 2024-06-10 | 6:40 | 2024-06-10 | 16:00 | GW8 | GLEN WAVERLEY | Urban | Planned |  | 25 | 14000 | 560 | 1 | No
| 150032 | 15/09/2024 | 7:30 | 15/09/2024 | 16:30 | MR31 | MOORABBIN | Urban | Planned |  | 1 | 540 | 540 | 1 | No
| 150032 | 15/09/2024 | 8:05 | 15/09/2024 | 16:40 | MR31 | MOORABBIN | Urban | Planned |  | 11 | 5665 | 515 | 1 | No
| 150048 | 2024-09-10 | 8:03 | 2024-09-10 | 12:44 | RBD14 | ROSEBUD | Urban | Planned |  | 10 | 2810 | 281 | 1 | No
| 150048 | 2024-09-10 | 8:03 | 2024-09-10 | 12:44 | RBD23 | ROSEBUD | Urban | Planned |  | 51 | 14331 | 281 | 1 | No
| 150051 | 13/09/2024 | 8:09 | 13/09/2024 | 10:51 | HT2 | HEATHERTON | Urban | Planned |  | 4 | 648 | 162 | 1 | No
| 150051 | 13/09/2024 | 8:09 | 13/09/2024 | 10:51 | MR33 | MOORABBIN | Urban | Planned |  | 25 | 4050 | 162 | 1 | No
| 150052 | 17/09/2024 | 8:00 | 17/09/2024 | 16:00 | EB32 | EAST BURWOOD | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 150052 | 17/09/2024 | 8:35 | 17/09/2024 | 14:20 | EB32 | EAST BURWOOD | Urban | Planned |  | 50 | 17250 | 345 | 1 | No
| 150053 | 13/09/2024 | 8:38 | 13/09/2024 | 11:50 | MR33 | MOORABBIN | Urban | Planned |  | 6 | 1152 | 192 | 1 | No
| 150054 | 18/09/2024 | 8:48 | 18/09/2024 | 13:45 | OE9 | OAKLEIGH EAST | Urban | Planned |  | 46 | 13662 | 297 | 1 | No
| 150055 | 2024-11-09 | 9:00 | 2024-11-09 | 10:10 | HGS22 | HASTINGS | Rural Short | Planned |  | 5 | 350 | 70 | 1 | No
| 150056 | 17/09/2024 | 8:37 | 17/09/2024 | 12:04 | RBD21 | ROSEBUD | Rural Short | Planned |  | 4 | 828 | 207 | 1 | No
| 150057 | 2024-11-09 | 11:00 | 2024-11-09 | 16:00 | HGS22 | HASTINGS | Rural Short | Planned |  | 1 | 300 | 300 | 1 | No
| 150058 | 18/09/2024 | 8:11 | 18/09/2024 | 14:55 | MTN23 | MORNINGTON | Urban | Planned |  | 119 | 48076 | 404 | 1 | No
| 150061 | 19/09/2024 | 9:15 | 19/09/2024 | 10:45 | WD16 | WEST DONCASTER | Urban | Planned |  | 34 | 3060 | 90 | 1 | No
| 150063 | 2024-12-09 | 9:30 | 2024-12-09 | 18:28 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 82 | 44116 | 538 | 1 | No
| 150067 | 2024-12-09 | 8:00 | 2024-12-09 | 13:30 | RWT12 | RINGWOOD | Urban | Planned |  | 64 | 21120 | 330 | 1 | No
| 150070 | 2024-11-09 | 8:05 | 2024-11-09 | 9:10 | HGS22 | HASTINGS | Rural Short | Planned |  | 3 | 195 | 65 | 1 | No
| 150071 | 2024-11-09 | 8:00 | 2024-11-09 | 13:00 | DC7 | DONCASTER | Urban | Planned |  | 17 | 5100 | 300 | 1 | No
| 150078 | 15/09/2024 | 8:00 | 15/09/2024 | 12:10 | HT2 | HEATHERTON | Urban | Planned |  | 28 | 7000 | 250 | 1 | No
| 150082 | 2024-11-09 | 8:15 | 2024-11-09 | 18:00 | NB35 | NORTH BRIGHTON | Urban | Planned |  | 46 | 26910 | 585 | 1 | No
| 150094 | 13/10/2024 | 7:29 | 13/10/2024 | 19:24 | MR31 | MOORABBIN | Urban | Planned |  | 11 | 7865 | 715 | 1 | No
| 150097 | 13/09/2024 | 8:25 | 13/09/2024 | 13:33 | NW31 | NUNAWADING | Urban | Planned |  | 258 | 79464 | 308 | 1 | No
| 150099 | 16/09/2024 | 9:05 | 16/09/2024 | 12:30 | RBD21 | ROSEBUD | Rural Short | Planned |  | 116 | 23780 | 205 | 1 | No
| 150100 | 20/09/2024 | 12:00 | 20/09/2024 | 16:00 | DMA21 | DROMANA | Urban | Planned |  | 2 | 480 | 240 | 1 | No
| 150107 | 21/09/2024 | 8:00 | 21/09/2024 | 16:00 | EL26 | ELSTERNWICK | Urban | Planned |  | 68 | 32640 | 480 | 1 | No
| 150111 | 13/09/2024 | 10:20 | 13/09/2024 | 12:51 | FTN21 | FRANKSTON | Urban | Planned |  | 201 | 30351 | 151 | 1 | No
| 150114 | 20/09/2024 | 8:00 | 20/09/2024 | 13:30 | NW11 | NUNAWADING | Urban | Planned |  | 74 | 24420 | 330 | 1 | No
| 150116 | 20/09/2024 | 12:00 | 20/09/2024 | 15:30 | NW11 | NUNAWADING | Urban | Planned |  | 54 | 11340 | 210 | 1 | No
| 150117 | 2024-08-10 | 8:32 | 2024-08-10 | 13:50 | RBD21 | ROSEBUD | Rural Short | Planned |  | 133 | 42294 | 318 | 1 | No
| 150139 | 20/09/2024 | 8:00 | 20/09/2024 | 12:12 | M11 | MENTONE | Urban | Planned |  | 115 | 28980 | 252 | 1 | No
| 150140 | 13/09/2024 | 8:38 | 13/09/2024 | 12:03 | BU11 | BULLEEN | Urban | Planned |  | 28 | 5740 | 205 | 1 | No
| 150141 | 20/09/2024 | 10:00 | 20/09/2024 | 16:00 | EL33 | ELSTERNWICK | Urban | Planned |  | 15 | 5400 | 360 | 1 | No
| 150142 | 16/09/2024 | 8:30 | 16/09/2024 | 11:46 | DMA13 | DROMANA | Rural Short | Planned |  | 117 | 22932 | 196 | 1 | No
| 150145 | 2024-06-10 | 9:45 | 2024-06-10 | 14:35 | M21 | MENTONE | Urban | Planned |  | 15 | 4350 | 290 | 1 | No
| 150150 | 24/09/2024 | 8:13 | 24/09/2024 | 15:01 | EB24 | EAST BURWOOD | Urban | Planned |  | 44 | 17952 | 408 | 1 | No
| 150153 | 13/09/2024 | 8:00 | 13/09/2024 | 10:50 | MC34 | MORDIALLOC | Urban | Planned |  | 45 | 7650 | 170 | 1 | No
| 150155 | 16/09/2024 | 12:40 | 16/09/2024 | 14:12 | DMA13 | DROMANA | Rural Short | Planned |  | 185 | 17020 | 92 | 1 | No
| 150156 | 13/09/2024 | 11:12 | 13/09/2024 | 13:26 | MC12 | MORDIALLOC | Urban | Planned |  | 59 | 7906 | 134 | 1 | No
| 150160 | 23/09/2024 | 8:50 | 23/09/2024 | 14:30 | NW23 | NUNAWADING | Urban | Planned |  | 29 | 9860 | 340 | 1 | No
| 150162 | 17/09/2024 | 8:55 | 17/09/2024 | 12:35 | MTN32 | MORNINGTON | Rural Short | Planned |  | 40 | 8800 | 220 | 1 | No
| 150168 | 2024-03-10 | 8:32 | 2024-03-10 | 10:17 | HGS33 | HASTINGS | Rural Short | Planned |  | 6 | 630 | 105 | 1 | No
| 150171 | 2024-10-10 | 8:40 | 2024-10-10 | 11:48 | RBD14 | ROSEBUD | Urban | Planned |  | 59 | 11092 | 188 | 1 | No
| 150173 | 20/09/2024 | 8:03 | 20/09/2024 | 14:00 | MTN32 | MORNINGTON | Rural Short | Planned |  | 47 | 16779 | 357 | 1 | No
| 150180 | 16/09/2024 | 9:35 | 16/09/2024 | 10:45 | RBD12 | ROSEBUD | Rural Short | Planned |  | 128 | 8960 | 70 | 1 | No
| 150181 | 20/09/2024 | 8:36 | 20/09/2024 | 10:30 | M11 | MENTONE | Urban | Planned |  | 9 | 1026 | 114 | 1 | No
| 150188 | 15/09/2024 | 7:04 | 15/09/2024 | 11:32 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 1 | 268 | 268 | 1 | No
| 150192 | 16/09/2024 | 8:03 | 16/09/2024 | 10:00 | DN13 | DANDENONG | Urban | Planned |  | 30 | 3510 | 117 | 1 | No
| 150200 | 18/09/2024 | 8:13 | 18/09/2024 | 12:17 | RBD13 | ROSEBUD | Urban | Planned |  | 155 | 37820 | 244 | 1 | No
| 150205 | 15/09/2024 | 10:41 | 15/09/2024 | 11:40 | HT3 | HEATHERTON | Urban | Planned |  | 43 | 2537 | 59 | 1 | No
| 150206 | 18/09/2024 | 8:37 | 18/09/2024 | 11:15 | CRM23 | CARRUM | Urban | Planned |  | 71 | 11218 | 158 | 1 | No
| 150208 | 15/09/2024 | 8:15 | 15/09/2024 | 9:35 | HGS21 | HASTINGS | Rural Short | Planned |  | 24 | 1920 | 80 | 1 | No
| 150209 | 19/09/2024 | 20:30 | 20/09/2024 | 5:30 | K34 | GARDINER | Urban | Planned |  | 72 | 38880 | 540 | 1 | No
| 150210 | 2024-10-10 | 10:20 | 2024-10-10 | 13:36 | RBD21 | ROSEBUD | Rural Short | Planned |  | 8 | 1568 | 196 | 1 | No
| 150210 | 2024-10-10 | 10:20 | 2024-10-10 | 13:36 | STO21 | SORRENTO | Rural Short | Planned |  | 2 | 392 | 196 | 1 | No
| 150212 | 15/09/2024 | 8:07 | 15/09/2024 | 9:58 | NO7 | NOTTING HILL | Urban | Planned |  | 32 | 3552 | 111 | 1 | No
| 150213 | 15/09/2024 | 10:25 | 15/09/2024 | 13:35 | SR24 | SANDRINGHAM | Urban | Planned |  | 60 | 11400 | 190 | 1 | No
| 150214 | 15/09/2024 | 10:55 | 15/09/2024 | 13:06 | DN6 | DANDENONG | Urban | Planned |  | 14 | 1834 | 131 | 1 | No
| 150216 | 16/09/2024 | 9:00 | 16/09/2024 | 11:00 | NW31 | NUNAWADING | Urban | Planned |  | 16 | 1920 | 120 | 1 | No
| 150217 | 15/09/2024 | 7:32 | 15/09/2024 | 12:25 | EM3 | EAST MALVERN | Urban | Planned |  | 20 | 5860 | 293 | 1 | No
| 150217 | 15/09/2024 | 7:32 | 15/09/2024 | 12:25 | OR35 | ORMOND | Urban | Planned |  | 132 | 38676 | 293 | 1 | No
| 150218 | 16/10/2024 | 9:07 | 16/10/2024 | 16:09 | DMA14 | DROMANA | Urban | Planned |  | 163 | 68786 | 422 | 1 | No
| 150221 | 15/10/2024 | 8:25 | 15/10/2024 | 12:31 | RBD14 | ROSEBUD | Urban | Planned |  | 84 | 20664 | 246 | 1 | No
| 150231 | 21/09/2024 | 7:31 | 21/09/2024 | 16:01 | GW12 | GLEN WAVERLEY | Urban | Planned |  | 30 | 15300 | 510 | 1 | No
| 150231 | 21/09/2024 | 7:31 | 21/09/2024 | 16:01 | MGE34 | MULGRAVE | Urban | Planned |  | 31 | 15810 | 510 | 1 | No
| 150235 | 25/09/2024 | 8:00 | 25/09/2024 | 11:38 | BU21 | BULLEEN | Urban | Planned |  | 37 | 8066 | 218 | 1 | No
| 150237 | 27/08/2024 | 7:00 | 27/08/2024 | 14:35 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 2 | 910 | 455 | 1 | No
| 150238 | 18/09/2024 | 8:15 | 18/09/2024 | 16:10 | NB34 | NORTH BRIGHTON | Urban | Planned |  | 42 | 19950 | 475 | 1 | No
| 150239 | 23/09/2024 | 8:39 | 23/09/2024 | 11:58 | SV16 | SPRINGVALE | Urban | Planned |  | 60 | 11940 | 199 | 1 | No
| 150253 | 30/10/2024 | 9:12 | 30/10/2024 | 17:18 | DC1 | DONCASTER | Urban | Planned |  | 90 | 43740 | 486 | 1 | No
| 150254 | 29/09/2024 | 7:37 | 29/09/2024 | 15:55 | FTN12 | FRANKSTON | Urban | Planned |  | 2 | 996 | 498 | 1 | No
| 150258 | 17/09/2024 | 8:03 | 17/09/2024 | 12:28 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 95 | 25175 | 265 | 1 | No
| 150259 | 16/10/2024 | 8:00 | 16/10/2024 | 14:27 | RBD14 | ROSEBUD | Urban | Planned |  | 61 | 23607 | 387 | 1 | No
| 150260 | 17/09/2024 | 12:55 | 17/09/2024 | 15:55 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 89 | 16020 | 180 | 1 | No
| 150261 | 18/09/2024 | 9:17 | 18/09/2024 | 14:27 | M12 | MENTONE | Urban | Planned |  | 32 | 9920 | 310 | 1 | No
| 150265 | 2024-06-09 | 8:00 | 2024-06-09 | 8:30 | LYD14 | LYSTERFIELD | Rural Short | Planned |  | 1 | 30 | 30 | 1 | No
| 150270 | 17/09/2024 | 8:00 | 17/09/2024 | 15:30 | NW11 | NUNAWADING | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 150270 | 17/09/2024 | 8:05 | 17/09/2024 | 14:35 | NW11 | NUNAWADING | Urban | Planned |  | 50 | 19500 | 390 | 1 | No
| 150271 | 20/10/2024 | 7:30 | 20/10/2024 | 15:00 | M22 | MENTONE | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 150271 | 20/10/2024 | 7:37 | 20/10/2024 | 13:40 | M22 | MENTONE | Urban | Planned |  | 97 | 35211 | 363 | 1 | No
| 150272 | 16/09/2024 | 10:00 | 16/09/2024 | 15:25 | BU11 | BULLEEN | Urban | Planned |  | 83 | 26975 | 325 | 1 | No
| 150272 | 16/09/2024 | 10:00 | 16/09/2024 | 15:25 | BU21 | BULLEEN | Urban | Planned |  | 70 | 22750 | 325 | 1 | No
| 150276 | 20/09/2024 | 8:11 | 20/09/2024 | 11:23 | M11 | MENTONE | Urban | Planned |  | 8 | 1536 | 192 | 1 | No
| 150278 | 2024-03-10 | 8:30 | 2024-03-10 | 15:30 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 1 | 420 | 420 | 1 | No
| 150278 | 2024-03-10 | 8:38 | 2024-03-10 | 12:28 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 45 | 10350 | 230 | 1 | No
| 150279 | 19/09/2024 | 8:00 | 19/09/2024 | 11:10 | MC34 | MORDIALLOC | Urban | Planned |  | 174 | 33060 | 190 | 1 | No
| 150280 | 18/09/2024 | 8:15 | 18/09/2024 | 14:10 | NW11 | NUNAWADING | Urban | Planned |  | 54 | 19170 | 355 | 1 | No
| 150284 | 19/09/2024 | 8:55 | 19/09/2024 | 12:32 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 67 | 14539 | 217 | 1 | No
| 150285 | 18/09/2024 | 8:00 | 18/09/2024 | 10:12 | NW21 | NUNAWADING | Urban | Planned |  | 41 | 5412 | 132 | 1 | No
| 150287 | 18/09/2024 | 11:15 | 18/09/2024 | 12:40 | NW21 | NUNAWADING | Urban | Planned |  | 103 | 8755 | 85 | 1 | No
| 150298 | 2024-02-10 | 8:06 | 2024-02-10 | 16:15 | FTN25 | FRANKSTON | Urban | Planned |  | 158 | 77262 | 489 | 1 | No
| 150304 | 19/09/2024 | 8:05 | 19/09/2024 | 11:26 | HGS31 | HASTINGS | Rural Short | Planned |  | 217 | 43617 | 201 | 1 | No
| 150306 | 20/09/2024 | 8:03 | 20/09/2024 | 13:53 | WD36 | WEST DONCASTER | Urban | Planned |  | 132 | 46200 | 350 | 1 | No
| 150307 | 20/09/2024 | 10:00 | 20/09/2024 | 16:00 | WD36 | WEST DONCASTER | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 150307 | 20/09/2024 | 10:37 | 20/09/2024 | 14:35 | WD36 | WEST DONCASTER | Urban | Planned |  | 21 | 4998 | 238 | 1 | No
| 150323 | 2024-10-09 | 8:40 | 2024-10-09 | 10:55 | BRA21 | BORONIA | Urban | Planned |  | 14 | 1890 | 135 | 1 | No
| 150329 | 18/10/2024 | 9:35 | 18/10/2024 | 12:23 | DMA23 | DROMANA | Rural Short | Planned |  | 4 | 672 | 168 | 1 | No
| 150330 | 19/10/2024 | 8:30 | 19/10/2024 | 14:01 | SR26 | SANDRINGHAM | Urban | Planned |  | 58 | 19198 | 331 | 1 | No
| 150337 | 24/09/2024 | 8:02 | 24/09/2024 | 12:49 | FTN14 | FRANKSTON | Urban | Planned |  | 35 | 10045 | 287 | 1 | No
| 150339 | 2024-06-10 | 8:00 | 2024-06-10 | 12:27 | M13 | MENTONE | Urban | Planned |  | 177 | 47259 | 267 | 2 | No
| 150339 | 2024-06-10 | 8:00 | 2024-06-10 | 15:30 | M13 | MENTONE | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 150339 | 2024-06-10 | 8:00 | 2024-06-10 | 12:27 | MC23 | MORDIALLOC | Urban | Planned |  | 32 | 8544 | 267 | 1 | No
| 150348 | 2024-10-10 | 8:01 | 2024-10-10 | 8:01 | LD7 | LYNDALE | Urban | Planned |  | 4 | 1.8668 | 0.46667 | 1 | No
| 150352 | 2024-01-10 | 8:14 | 2024-01-10 | 14:08 | EW3 | ELWOOD | Urban | Planned |  | 132 | 46728 | 354 | 1 | No
| 150355 | 2024-04-10 | 9:07 | 2024-04-10 | 12:09 | RBD24 | ROSEBUD | Urban | Planned |  | 67 | 12194 | 182 | 1 | No
| 150356 | 24/09/2024 | 8:25 | 24/09/2024 | 11:05 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 5 | 800 | 160 | 1 | No
| 150362 | 26/09/2024 | 8:30 | 26/09/2024 | 17:55 | STO21 | SORRENTO | Rural Short | Planned |  | 54 | 30510 | 565 | 1 | No
| 150369 | 2024-06-10 | 6:30 | 2024-06-10 | 16:00 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 21 | 11970 | 570 | 1 | No
| 150374 | 25/09/2024 | 8:05 | 25/09/2024 | 11:55 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 24 | 5520 | 230 | 1 | No
| 150386 | 24/09/2024 | 8:12 | 24/09/2024 | 11:03 | DMA21 | DROMANA | Urban | Planned |  | 54 | 9234 | 171 | 1 | No
| 150387 | 26/09/2024 | 8:20 | 26/09/2024 | 15:00 | DMA21 | DROMANA | Urban | Planned |  | 113 | 45200 | 400 | 1 | No
| 150392 | 18/09/2024 | 5:10 | 18/09/2024 | 6:30 | MC34 | MORDIALLOC | Urban | Planned |  | 1 | 80 | 80 | 1 | No
| 150396 | 25/09/2024 | 8:02 | 25/09/2024 | 10:43 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 81 | 13041 | 161 | 1 | No
| 150399 | 2024-03-10 | 9:21 | 2024-03-10 | 13:46 | STO23 | SORRENTO | Urban | Planned |  | 26 | 6890 | 265 | 1 | No
| 150400 | 2024-03-10 | 8:14 | 2024-03-10 | 14:31 | FTN21 | FRANKSTON | Urban | Planned |  | 386 | 145522 | 377 | 1 | No
| 150402 | 20/10/2024 | 8:02 | 20/10/2024 | 14:33 | NP11 | NOBLE PARK | Urban | Planned |  | 29 | 11339 | 391 | 1 | No
| 150403 | 21/10/2024 | 8:15 | 21/10/2024 | 11:05 | RBD13 | ROSEBUD | Urban | Planned |  | 8 | 1360 | 170 | 1 | No
| 150406 | 2024-08-10 | 8:15 | 2024-08-10 | 10:40 | OR34 | ORMOND | Urban | Planned |  | 68 | 9860 | 145 | 1 | No
| 150407 | 29/09/2024 | 8:00 | 29/09/2024 | 16:30 | BU24 | BULLEEN | Urban | Planned |  | 36 | 18360 | 510 | 1 | No
| 150409 | 25/09/2024 | 8:00 | 25/09/2024 | 16:00 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 150409 | 25/09/2024 | 8:17 | 25/09/2024 | 10:00 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 79 | 8137 | 103 | 1 | No
| 150411 | 17/11/2024 | 8:05 | 17/11/2024 | 13:08 | CDA24 | CLARINDA | Urban | Planned |  | 5 | 1515 | 303 | 1 | No
| 150415 | 24/09/2024 | 8:35 | 24/09/2024 | 9:30 | HGS22 | HASTINGS | Rural Short | Planned |  | 2 | 110 | 55 | 1 | No
| 150425 | 24/09/2024 | 12:00 | 24/09/2024 | 12:50 | HGS33 | HASTINGS | Rural Short | Planned |  | 2 | 100 | 50 | 1 | No
| 150426 | 26/09/2024 | 8:18 | 26/09/2024 | 14:15 | OR33 | ORMOND | Urban | Planned |  | 509 | 181713 | 357 | 1 | No
| 150430 | 25/09/2024 | 10:14 | 25/09/2024 | 13:27 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 273 | 52689 | 193 | 1 | No
| 150441 | 18/10/2024 | 8:35 | 18/10/2024 | 12:06 | OR24 | ORMOND | Urban | Planned |  | 22 | 4642 | 211 | 1 | No
| 150443 | 22/10/2024 | 9:28 | 22/10/2024 | 15:11 | RBD14 | ROSEBUD | Urban | Planned |  | 17 | 5831 | 343 | 1 | No
| 150444 | 21/10/2024 | 8:53 | 21/10/2024 | 13:11 | RBD24 | ROSEBUD | Urban | Planned |  | 17 | 4386 | 258 | 1 | No
| 150452 | 30/10/2024 | 11:19 | 30/10/2024 | 13:12 | DMA24 | DROMANA | Rural Short | Planned |  | 7 | 791 | 113 | 1 | No
| 150455 | 30/10/2024 | 8:12 | 30/10/2024 | 10:00 | RBD21 | ROSEBUD | Rural Short | Planned |  | 45 | 4860 | 108 | 1 | No
| 150466 | 13/10/2024 | 9:27 | 13/10/2024 | 12:42 | NO2 | NOTTING HILL | Urban | Planned |  | 1 | 195 | 195 | 1 | No
| 150477 | 26/09/2024 | 8:07 | 26/09/2024 | 10:31 | OR25 | ORMOND | Urban | Planned |  | 49 | 7056 | 144 | 1 | No
| 150477 | 26/09/2024 | 8:07 | 26/09/2024 | 10:31 | OR34 | ORMOND | Urban | Planned |  | 70 | 10080 | 144 | 1 | No
| 150483 | 2024-04-10 | 8:09 | 2024-04-10 | 15:30 | MGE32 | MULGRAVE | Urban | Planned |  | 8 | 3528 | 441 | 1 | No
| 150495 | 22/09/2024 | 7:11 | 22/09/2024 | 15:25 | DSH14 | DANDENONG SOUTH | Urban | Planned |  | 15 | 7410 | 494 | 1 | No
| 150497 | 2024-10-10 | 8:00 | 2024-10-10 | 16:10 | WD14 | WEST DONCASTER | Urban | Planned |  | 85 | 41650 | 490 | 1 | No
| 150503 | 25/09/2024 | 0:30 | 25/09/2024 | 5:30 | DC6 | DONCASTER | Urban | Planned |  | 18 | 5400 | 300 | 1 | No
| 150511 | 24/10/2024 | 8:00 | 24/10/2024 | 15:30 | OR24 | ORMOND | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 150511 | 24/10/2024 | 8:35 | 24/10/2024 | 13:57 | OR24 | ORMOND | Urban | Planned |  | 229 | 73738 | 322 | 1 | No
| 150511 | 24/10/2024 | 8:35 | 24/10/2024 | 13:57 | OR33 | ORMOND | Urban | Planned |  | 77 | 24794 | 322 | 1 | No
| 150512 | 25/10/2024 | 8:25 | 25/10/2024 | 12:55 | RBD23 | ROSEBUD | Urban | Planned |  | 12 | 3240 | 270 | 1 | No
| 150513 | 23/10/2024 | 8:33 | 23/10/2024 | 15:17 | OR24 | ORMOND | Urban | Planned |  | 23 | 9292 | 404 | 1 | No
| 150513 | 23/10/2024 | 8:33 | 23/10/2024 | 15:17 | OR34 | ORMOND | Urban | Planned |  | 121 | 48884 | 404 | 1 | No
| 150514 | 30/09/2024 | 8:35 | 30/09/2024 | 14:31 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 111 | 39516 | 356 | 1 | No
| 150517 | 30/09/2024 | 10:10 | 30/09/2024 | 15:21 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 55 | 17105 | 311 | 1 | No
| 150519 | 22/09/2024 | 7:31 | 22/09/2024 | 14:22 | DVY23 | DANDENONG VALLEY | Urban | Planned |  | 18 | 7398 | 411 | 1 | No
| 150520 | 25/09/2024 | 8:34 | 25/09/2024 | 11:01 | LWN33 | LANGWARRIN | Urban | Planned |  | 21 | 3087 | 147 | 1 | No
| 150521 | 30/09/2024 | 8:43 | 30/09/2024 | 14:02 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 94 | 29986 | 319 | 1 | No
| 150528 | 2024-03-10 | 8:01 | 2024-03-10 | 16:50 | DMA15 | DROMANA | Rural Short | Planned |  | 25 | 13232.9175 | 529.3167 | 1 | No
| 150529 | 21/09/2024 | 6:30 | 21/09/2024 | 13:00 | MC34 | MORDIALLOC | Urban | Planned |  | 4 | 1560 | 390 | 1 | No
| 150530 | 16/10/2024 | 8:30 | 16/10/2024 | 8:31 | BU15 | BULLEEN | Urban | Planned |  | 11 | 11 | 1 | 1 | No
| 150531 | 24/09/2024 | 8:45 | 24/09/2024 | 12:40 | OR35 | ORMOND | Urban | Planned |  | 45 | 10575 | 235 | 1 | No
| 150532 | 29/09/2024 | 8:00 | 29/09/2024 | 12:55 | EM6 | EAST MALVERN | Urban | Planned |  | 43 | 12685 | 295 | 2 | No
| 150532 | 29/09/2024 | 8:00 | 29/09/2024 | 16:00 | EM6 | EAST MALVERN | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 150533 | 2024-07-10 | 8:27 | 2024-07-10 | 10:54 | STO13 | SORRENTO | Urban | Planned |  | 37 | 5439 | 147 | 1 | No
| 150541 | 24/09/2024 | 7:32 | 28/09/2024 | 11:26 | NB31 | NORTH BRIGHTON | Urban | Planned |  | 2 | 11988 | 5994 | 1 | No
| 150542 | 18/09/2024 | 8:16 | 18/09/2024 | 12:35 | NP36 | NOBLE PARK | Urban | Planned |  | 77 | 19943 | 259 | 1 | No
| 150545 | 24/09/2024 | 8:40 | 24/09/2024 | 10:34 | KBH34 | KEYSBOROUGH | Urban | Planned |  | 1 | 114 | 114 | 1 | No
| 150549 | 14/10/2024 | 8:04 | 14/10/2024 | 14:24 | WD34 | WEST DONCASTER | Urban | Planned |  | 10 | 3800 | 380 | 1 | No
| 150552 | 25/09/2024 | 7:47 | 25/09/2024 | 15:30 | DC2 | DONCASTER | Urban | Planned |  | 1 | 463 | 463 | 1 | No
| 150556 | 20/09/2024 | 8:00 | 20/09/2024 | 9:00 | MTN21 | MORNINGTON | Urban | Planned |  | 320 | 19200 | 60 | 1 | No
| 150566 | 2024-01-10 | 8:36 | 2024-01-10 | 12:16 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 1 | 220 | 220 | 1 | No
| 150593 | 2024-05-10 | 7:30 | 2024-05-10 | 12:39 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 1 | 309 | 309 | 1 | No
| 150600 | 2024-08-10 | 8:00 | 2024-08-10 | 16:30 | HGS21 | HASTINGS | Rural Short | Planned |  | 2 | 1020 | 510 | 1 | No
| 150600 | 2024-08-10 | 8:30 | 2024-08-10 | 15:30 | HGS21 | HASTINGS | Rural Short | Planned |  | 81 | 34020 | 420 | 1 | No
| 150600 | 2024-08-10 | 8:30 | 2024-08-10 | 15:30 | HGS23 | HASTINGS | Rural Short | Planned |  | 69 | 28980 | 420 | 1 | No
| 150601 | 26/09/2024 | 8:38 | 26/09/2024 | 12:00 | NW31 | NUNAWADING | Urban | Planned |  | 13 | 2626 | 202 | 1 | No
| 150604 | 17/10/2024 | 8:00 | 17/10/2024 | 15:30 | OR23 | ORMOND | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 150604 | 17/10/2024 | 8:07 | 17/10/2024 | 13:47 | OR23 | ORMOND | Urban | Planned |  | 80 | 27200 | 340 | 1 | No
| 150605 | 26/09/2024 | 8:27 | 26/09/2024 | 12:05 | RWT12 | RINGWOOD | Urban | Planned |  | 26 | 5668 | 218 | 1 | No
| 150605 | 26/09/2024 | 8:27 | 26/09/2024 | 12:05 | RWT24 | RINGWOOD | Urban | Planned |  | 30 | 6540 | 218 | 1 | No
| 150617 | 2024-02-10 | 7:31 | 2024-02-10 | 18:38 | FTN11 | FRANKSTON | Urban | Planned |  | 1 | 667 | 667 | 1 | No
| 150620 | 15/10/2024 | 9:14 | 15/10/2024 | 15:13 | EW14 | ELWOOD | Urban | Planned |  | 85 | 30515 | 359 | 1 | No
| 150624 | 2024-01-10 | 8:10 | 2024-01-10 | 15:05 | OR33 | ORMOND | Urban | Planned |  | 295 | 122425 | 415 | 1 | No
| 150625 | 2024-01-10 | 8:02 | 2024-01-10 | 15:14 | WD14 | WEST DONCASTER | Urban | Planned |  | 19 | 8208 | 432 | 1 | No
| 150632 | 2024-03-10 | 5:27 | 2024-03-10 | 6:20 | NO2 | NOTTING HILL | Urban | Planned |  | 1 | 53 | 53 | 1 | No
| 150633 | 2024-06-10 | 8:00 | 2024-06-10 | 11:40 | HGS32 | HASTINGS | Urban | Planned |  | 23 | 5059.2341 | 219.9667 | 1 | No
| 150634 | 2024-09-10 | 22:01 | 2024-10-10 | 3:42 | FTN11 | FRANKSTON | Urban | Planned |  | 46 | 15686 | 341 | 1 | No
| 150635 | 2024-09-10 | 8:10 | 2024-09-10 | 10:57 | DN11 | DANDENONG | Urban | Planned |  | 40 | 6680 | 167 | 1 | No
| 150643 | 2024-02-10 | 8:00 | 2024-02-10 | 16:00 | NW23 | NUNAWADING | Urban | Planned |  | 3 | 1440 | 480 | 1 | No
| 150643 | 2024-02-10 | 8:14 | 2024-02-10 | 14:19 | NW23 | NUNAWADING | Urban | Planned |  | 498 | 181770 | 365 | 1 | No
| 150645 | 2024-02-10 | 8:25 | 2024-02-10 | 17:36 | EW9 | ELWOOD | Urban | Planned |  | 30 | 16530 | 551 | 1 | No
| 150646 | 2024-04-10 | 8:20 | 2024-04-10 | 12:07 | FTN24 | FRANKSTON | Urban | Planned |  | 105 | 23835 | 227 | 1 | No
| 150649 | 30/10/2024 | 8:00 | 30/10/2024 | 12:00 | MTN34 | MORNINGTON | Urban | Planned |  | 216 | 51840 | 240 | 1 | No
| 150652 | 2024-02-10 | 10:00 | 2024-02-10 | 14:15 | RWT35 | RINGWOOD | Urban | Planned |  | 4 | 1020 | 255 | 1 | No
| 150654 | 2024-04-10 | 8:29 | 2024-04-10 | 12:23 | NB26 | NORTH BRIGHTON | Urban | Planned |  | 95 | 22230 | 234 | 1 | No
| 150655 | 2024-04-10 | 9:42 | 2024-04-10 | 13:08 | BU15 | BULLEEN | Urban | Planned |  | 103 | 21218 | 206 | 1 | No
| 150658 | 2024-04-10 | 8:58 | 2024-04-10 | 10:54 | NW22 | NUNAWADING | Urban | Planned |  | 44 | 5104 | 116 | 1 | No
| 150673 | 30/09/2024 | 19:46 | 2024-01-10 | 5:31 | DN7 | DANDENONG | Urban | Planned |  | 3 | 1755 | 585 | 1 | No
| 150680 | 2024-03-10 | 8:30 | 2024-03-10 | 10:10 | BU25 | BULLEEN | Urban | Planned |  | 40 | 4000 | 100 | 1 | No
| 150683 | 2024-07-10 | 9:29 | 2024-07-10 | 12:50 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 1 | 201 | 201 | 1 | No
| 150684 | 2024-03-10 | 11:18 | 2024-03-10 | 14:38 | RWT24 | RINGWOOD | Urban | Planned |  | 112 | 22400 | 200 | 1 | No
| 150685 | 2024-02-10 | 9:31 | 2024-02-10 | 14:31 | MR33 | MOORABBIN | Urban | Planned |  | 1 | 300 | 300 | 1 | No
| 150685 | 2024-02-10 | 10:04 | 2024-02-10 | 12:54 | MR33 | MOORABBIN | Urban | Planned |  | 25 | 4250 | 170 | 1 | No
| 150686 | 2024-08-10 | 11:00 | 2024-08-10 | 13:01 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 51 | 6145.5 | 120.5 | 1 | No
| 150691 | 19/11/2024 | 8:00 | 19/11/2024 | 16:00 | RBD13 | ROSEBUD | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 150691 | 19/11/2024 | 8:10 | 19/11/2024 | 14:07 | RBD13 | ROSEBUD | Urban | Planned |  | 274 | 97818 | 357 | 1 | No
| 150692 | 2024-06-10 | 8:06 | 2024-06-10 | 14:30 | MC31 | MORDIALLOC | Urban | Planned |  | 14 | 5376 | 384 | 1 | No
| 150694 | 14/10/2024 | 8:07 | 14/10/2024 | 14:51 | MTN23 | MORNINGTON | Urban | Planned |  | 5 | 2020 | 404 | 1 | No
| 150695 | 2024-08-10 | 9:05 | 2024-08-10 | 14:48 | OR25 | ORMOND | Urban | Planned |  | 82 | 28126 | 343 | 1 | No
| 150696 | 2024-08-11 | 8:35 | 2024-08-11 | 11:35 | DMA23 | DROMANA | Rural Short | Planned |  | 148 | 26640 | 180 | 1 | No
| 150702 | 22/10/2024 | 9:32 | 22/10/2024 | 13:26 | HT2 | HEATHERTON | Urban | Planned |  | 58 | 13572 | 234 | 1 | No
| 150709 | 2024-01-10 | 8:01 | 2024-01-10 | 13:19 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 53 | 16854 | 318 | 1 | No
| 150710 | 2024-11-10 | 11:30 | 2024-11-10 | 16:00 | NW22 | NUNAWADING | Urban | Planned |  | 115 | 31050 | 270 | 1 | No
| 150711 | 2024-11-10 | 8:00 | 2024-11-10 | 14:00 | NW22 | NUNAWADING | Urban | Planned |  | 187 | 67320 | 360 | 1 | No
| 150717 | 2024-08-10 | 8:02 | 2024-08-10 | 11:45 | HT10 | HEATHERTON | Urban | Planned |  | 23 | 5129 | 223 | 1 | No
| 150719 | 2024-08-10 | 8:40 | 2024-08-10 | 10:15 | NW22 | NUNAWADING | Urban | Planned |  | 25 | 2375 | 95 | 1 | No
| 150721 | 2024-08-10 | 10:39 | 2024-08-10 | 11:55 | NW22 | NUNAWADING | Urban | Planned |  | 18 | 1368 | 76 | 1 | No
| 150728 | 13/10/2024 | 7:20 | 13/10/2024 | 13:49 | DSH33 | DANDENONG SOUTH | Urban | Planned |  | 1 | 389 | 389 | 1 | No
| 150729 | 2024-08-10 | 8:42 | 2024-08-10 | 15:09 | SR22 | SANDRINGHAM | Urban | Planned |  | 6 | 2322 | 387 | 1 | No
| 150730 | 2024-02-10 | 8:11 | 2024-02-10 | 9:41 | MTN22 | MORNINGTON | Rural Short | Planned |  | 1 | 90 | 90 | 1 | No
| 150731 | 23/09/2024 | 23:15 | 24/09/2024 | 3:05 | AR2 | ARMADALE | Urban | Planned |  | 26 | 5980 | 230 | 1 | No
| 150732 | 16/10/2024 | 9:15 | 16/10/2024 | 10:15 | DC5 | DONCASTER | Urban | Planned |  | 36 | 2160 | 60 | 1 | No
| 150733 | 16/10/2024 | 10:30 | 16/10/2024 | 13:25 | BH33 | BOX HILL | Urban | Planned |  | 12 | 2100 | 175 | 1 | No
| 150735 | 2024-01-10 | 8:38 | 2024-01-10 | 13:57 | DMA23 | DROMANA | Rural Short | Planned |  | 92 | 29348 | 319 | 1 | No
| 150751 | 2024-03-10 | 8:01 | 2024-03-10 | 17:30 | MGE21 | MULGRAVE | Urban | Planned |  | 2 | 1138.0666 | 569.0333 | 1 | No
| 150761 | 2024-11-10 | 8:15 | 2024-11-10 | 11:46 | HGS33 | HASTINGS | Rural Short | Planned |  | 22 | 4642 | 211 | 1 | No
| 150776 | 31/10/2024 | 22:00 | 2024-01-11 | 5:00 | DN22 | DANDENONG | Urban | Planned |  | 75 | 31500 | 420 | 1 | No
| 150798 | 2024-11-10 | 8:20 | 2024-11-10 | 9:57 | DMA23 | DROMANA | Rural Short | Planned |  | 2 | 194 | 97 | 1 | No
| 150799 | 20/10/2024 | 7:45 | 20/10/2024 | 16:25 | RWT24 | RINGWOOD | Urban | Planned |  | 35 | 18200 | 520 | 1 | No
| 150800 | 2024-08-10 | 10:06 | 2024-08-10 | 14:36 | DC3 | DONCASTER | Urban | Planned |  | 36 | 9720 | 270 | 1 | No
| 150801 | 2024-09-10 | 9:45 | 2024-09-10 | 11:35 | CRM35 | CARRUM | Urban | Planned |  | 12 | 1320 | 110 | 1 | No
| 150802 | 2024-10-10 | 8:40 | 2024-10-10 | 11:50 | RWT34 | RINGWOOD | Urban | Planned |  | 8 | 1520 | 190 | 1 | No
| 150803 | 2024-11-10 | 8:30 | 2024-11-10 | 12:25 | EB32 | EAST BURWOOD | Urban | Planned |  | 9 | 2115 | 235 | 1 | No
| 150819 | 2024-09-10 | 8:58 | 2024-09-10 | 12:07 | SH22 | SURREY HILLS | Urban | Planned |  | 32 | 6048 | 189 | 1 | No
| 150837 | 2024-10-10 | 8:00 | 2024-10-10 | 12:38 | MTN32 | MORNINGTON | Rural Short | Planned |  | 47 | 13066 | 278 | 1 | No
| 150841 | 2024-07-10 | 9:05 | 2024-07-10 | 12:53 | M22 | MENTONE | Urban | Planned |  | 39 | 8892 | 228 | 1 | No
| 150843 | 15/10/2024 | 8:42 | 15/10/2024 | 15:20 | GW12 | GLEN WAVERLEY | Urban | Planned |  | 18 | 7164 | 398 | 1 | No
| 150848 | 2024-05-10 | 8:00 | 2024-05-10 | 10:00 | HT7 | HEATHERTON | Urban | Planned |  | 28 | 3360 | 120 | 1 | No
| 150852 | 2024-11-10 | 9:42 | 2024-11-10 | 14:54 | MTN32 | MORNINGTON | Rural Short | Planned |  | 17 | 5304 | 312 | 1 | No
| 150854 | 2024-01-11 | 8:05 | 2024-01-11 | 11:55 | HGS33 | HASTINGS | Rural Short | Planned |  | 63 | 14490 | 230 | 1 | No
| 150856 | 2024-04-10 | 9:23 | 2024-04-10 | 13:13 | BU22 | BULLEEN | Urban | Planned |  | 31 | 7130 | 230 | 1 | No
| 150856 | 2024-04-10 | 9:23 | 2024-04-10 | 13:13 | WD34 | WEST DONCASTER | Urban | Planned |  | 5 | 1150 | 230 | 1 | No
| 150860 | 15/10/2024 | 10:00 | 15/10/2024 | 14:25 | DC6 | DONCASTER | Urban | Planned |  | 43 | 11395 | 265 | 1 | No
| 150861 | 24/11/2024 | 8:00 | 24/11/2024 | 12:00 | MC34 | MORDIALLOC | Urban | Planned |  | 43 | 10312.8319 | 239.8333 | 1 | No
| 150862 | 13/10/2024 | 8:14 | 13/10/2024 | 12:22 | DC4 | DONCASTER | Urban | Planned |  | 5 | 1240 | 248 | 1 | No
| 150866 | 2024-08-10 | 8:15 | 2024-08-10 | 11:05 | MR33 | MOORABBIN | Urban | Planned |  | 44 | 7480 | 170 | 1 | No
| 150868 | 2024-07-10 | 8:55 | 2024-07-10 | 12:40 | NW33 | NUNAWADING | Urban | Planned |  | 167 | 37575 | 225 | 1 | No
| 150869 | 15/10/2024 | 8:01 | 15/10/2024 | 15:01 | RBD21 | ROSEBUD | Rural Short | Planned |  | 1 | 420 | 420 | 1 | No
| 150869 | 15/10/2024 | 8:15 | 15/10/2024 | 14:41 | RBD21 | ROSEBUD | Rural Short | Planned |  | 22 | 8492 | 386 | 1 | No
| 150871 | 2024-06-10 | 8:55 | 2024-06-10 | 16:07 | CFD13 | CAULFIELD | Urban | Planned |  | 193 | 83376 | 432 | 1 | No
| 150875 | 2024-04-10 | 13:30 | 2024-06-10 | 16:00 | SV32 | SPRINGVALE | Urban | Planned |  | 1 | 3030 | 3030 | 1 | No
| 150876 | 21/10/2024 | 8:17 | 21/10/2024 | 9:45 | RBD12 | ROSEBUD | Rural Short | Planned |  | 31 | 2728 | 88 | 1 | No
| 150879 | 13/11/2024 | 8:05 | 13/11/2024 | 11:54 | RBD12 | ROSEBUD | Rural Short | Planned |  | 18 | 4122 | 229 | 1 | No
| 150880 | 2024-10-10 | 20:00 | 2024-11-10 | 1:30 | MR23 | MOORABBIN | Urban | Planned |  | 21 | 6930 | 330 | 1 | No
| 150885 | 2024-10-10 | 8:07 | 2024-10-10 | 14:41 | EB11 | EAST BURWOOD | Urban | Planned |  | 23 | 9062 | 394 | 1 | No
| 150885 | 2024-10-10 | 8:07 | 2024-10-10 | 14:41 | EB21 | EAST BURWOOD | Urban | Planned |  | 15 | 5910 | 394 | 1 | No
| 150888 | 22/10/2024 | 8:00 | 22/10/2024 | 16:30 | CFD14 | CAULFIELD | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 150888 | 22/10/2024 | 9:06 | 22/10/2024 | 13:06 | CFD14 | CAULFIELD | Urban | Planned |  | 334 | 80160 | 240 | 1 | No
| 150889 | 22/10/2024 | 9:30 | 22/10/2024 | 12:19 | BU11 | BULLEEN | Urban | Planned |  | 34 | 5746 | 169 | 1 | No
| 150891 | 2024-06-10 | 8:00 | 2024-06-10 | 17:00 | SV33 | SPRINGVALE | Urban | Planned |  | 1 | 540 | 540 | 1 | No
| 150891 | 2024-06-10 | 8:06 | 2024-06-10 | 13:02 | NP33 | NOBLE PARK | Urban | Planned |  | 106 | 31376 | 296 | 1 | No
| 150891 | 2024-06-10 | 8:06 | 2024-06-10 | 13:02 | SV33 | SPRINGVALE | Urban | Planned |  | 580 | 171680 | 296 | 1 | No
| 150899 | 2024-11-10 | 8:26 | 2024-11-10 | 11:55 | RBD12 | ROSEBUD | Rural Short | Planned |  | 41 | 8569 | 209 | 1 | No
| 150900 | 2024-06-10 | 8:04 | 2024-06-10 | 13:54 | NO32 | NOTTING HILL | Urban | Planned |  | 9 | 3150 | 350 | 1 | No
| 150900 | 2024-06-10 | 8:04 | 2024-06-10 | 13:54 | NO4 | NOTTING HILL | Urban | Planned |  | 36 | 12600 | 350 | 1 | No
| 150900 | 2024-06-10 | 8:04 | 2024-06-10 | 13:54 | NO5 | NOTTING HILL | Urban | Planned |  | 5 | 1750 | 350 | 1 | No
| 150902 | 17/09/2024 | 14:04 | 17/09/2024 | 14:30 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 52 | 26 | 1 | No
| 150903 | 2024-08-10 | 9:13 | 2024-08-10 | 13:15 | GW11 | GLEN WAVERLEY | Urban | Planned |  | 15 | 3630 | 242 | 1 | No
| 150908 | 18/10/2024 | 8:53 | 18/10/2024 | 11:45 | HGS22 | HASTINGS | Rural Short | Planned |  | 1 | 172 | 172 | 1 | No
| 150913 | 2024-06-10 | 7:50 | 2024-06-10 | 21:25 | HT3 | HEATHERTON | Urban | Planned |  | 34 | 27710 | 815 | 1 | No
| 150916 | 2024-07-10 | 10:10 | 2024-07-10 | 13:13 | BC6 | BALACLAVA | Urban | Planned |  | 48 | 8784 | 183 | 1 | No
| 150921 | 23/10/2024 | 7:31 | 23/10/2024 | 17:30 | DSH24 | DANDENONG SOUTH | Urban | Planned |  | 1 | 599.3 | 599.3 | 1 | No
| 150922 | 20/10/2024 | 7:37 | 20/10/2024 | 13:51 | CRM35 | CARRUM | Urban | Planned |  | 155 | 57970 | 374 | 1 | No
| 150923 | 2024-09-10 | 1:30 | 2024-09-10 | 3:30 | BH33 | BOX HILL | Urban | Planned |  | 3 | 360 | 120 | 1 | No
| 150927 | 13/10/2024 | 7:30 | 13/10/2024 | 15:30 | MR23 | MOORABBIN | Urban | Planned |  | 1 | 480 | 480 | 2 | No
| 150927 | 13/10/2024 | 7:30 | 13/10/2024 | 16:20 | MR23 | MOORABBIN | Urban | Planned |  | 9 | 4770 | 530 | 1 | No
| 150929 | 2024-06-10 | 7:20 | 2024-06-10 | 16:19 | EB21 | EAST BURWOOD | Urban | Planned |  | 13 | 7007 | 539 | 1 | No
| 150937 | 21/10/2024 | 9:59 | 21/10/2024 | 13:56 | MTN32 | MORNINGTON | Rural Short | Planned |  | 2 | 474 | 237 | 1 | No
| 150939 | 15/10/2024 | 9:15 | 15/10/2024 | 10:29 | BT23 | BENTLEIGH | Urban | Planned |  | 2 | 148 | 74 | 1 | No
| 150940 | 23/10/2024 | 8:32 | 23/10/2024 | 15:35 | MGE13 | MULGRAVE | Urban | Planned |  | 63 | 26649 | 423 | 1 | No
| 150941 | 2025-06-01 | 21:01 | 2025-07-01 | 3:31 | FTN11 | FRANKSTON | Urban | Planned |  | 1 | 390 | 390 | 1 | No
| 150943 | 22/10/2024 | 8:32 | 22/10/2024 | 13:41 | HGS33 | HASTINGS | Rural Short | Planned |  | 1 | 309 | 309 | 1 | No
| 150945 | 2024-10-10 | 8:10 | 2024-10-10 | 11:25 | SR24 | SANDRINGHAM | Urban | Planned |  | 54 | 10530 | 195 | 1 | No
| 150953 | 2024-11-10 | 8:40 | 2024-11-10 | 11:10 | OR33 | ORMOND | Urban | Planned |  | 102 | 15300 | 150 | 1 | No
| 150954 | 2024-09-10 | 8:43 | 2024-09-10 | 16:45 | RBD21 | ROSEBUD | Rural Short | Planned |  | 5 | 2410 | 482 | 1 | No
| 150956 | 20/09/2024 | 13:17 | 20/09/2024 | 13:41 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 48 | 24 | 1 | No
| 150957 | 30/09/2024 | 10:00 | 30/09/2024 | 16:00 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 720 | 360 | 1 | No
| 150958 | 2024-01-10 | 10:01 | 2024-01-10 | 10:01 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 0.7334 | 0.36667 | 1 | No
| 150959 | 2024-02-10 | 12:31 | 2024-02-10 | 13:51 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 160 | 80 | 1 | No
| 150960 | 2024-07-10 | 11:49 | 2024-07-10 | 12:49 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 120 | 60 | 1 | No
| 150966 | 2024-07-10 | 9:43 | 2024-07-10 | 11:45 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 5 | 610 | 122 | 1 | No
| 150970 | 27/10/2024 | 8:37 | 27/10/2024 | 18:11 | RWT12 | RINGWOOD | Urban | Planned |  | 56 | 32144 | 574 | 1 | No
| 150970 | 27/10/2024 | 8:37 | 27/10/2024 | 18:11 | RWT23 | RINGWOOD | Urban | Planned |  | 42 | 24108 | 574 | 1 | No
| 150972 | 14/10/2024 | 12:14 | 14/10/2024 | 13:15 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 122 | 61 | 1 | No
| 150973 | 18/10/2024 | 10:32 | 18/10/2024 | 10:45 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 26 | 13 | 1 | No
| 150975 | 21/11/2024 | 11:36 | 21/11/2024 | 11:58 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 44 | 22 | 1 | No
| 150976 | 2024-11-12 | 8:00 | 2024-11-12 | 12:37 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 2 | 554 | 277 | 1 | No
| 150977 | 2024-08-10 | 8:01 | 2024-08-10 | 10:07 | NP33 | NOBLE PARK | Urban | Planned |  | 2 | 252 | 126 | 1 | No
| 150978 | 24/10/2024 | 8:15 | 24/10/2024 | 9:54 | MGE31 | MULGRAVE | Urban | Planned |  | 29 | 2871 | 99 | 1 | No
| 150979 | 2024-11-10 | 9:48 | 2024-11-10 | 13:54 | M11 | MENTONE | Urban | Planned |  | 36 | 8856 | 246 | 1 | No
| 150979 | 2024-11-10 | 9:48 | 2024-11-10 | 13:54 | M31 | MENTONE | Urban | Planned |  | 30 | 7380 | 246 | 1 | No
| 150980 | 24/10/2024 | 10:25 | 24/10/2024 | 11:12 | MGE31 | MULGRAVE | Urban | Planned |  | 21 | 987 | 47 | 1 | No
| 150983 | 2024-11-10 | 9:19 | 2024-11-10 | 13:55 | BW21 | BURWOOD | Urban | Planned |  | 3 | 828 | 276 | 1 | No
| 150983 | 2024-11-10 | 9:19 | 2024-11-10 | 13:55 | RD10 | RIVERSDALE | Urban | Planned |  | 69 | 19044 | 276 | 1 | No
| 150985 | 13/10/2024 | 8:00 | 13/10/2024 | 12:12 | EL35 | ELSTERNWICK | Urban | Planned |  | 61 | 15372 | 252 | 1 | No
| 150986 | 13/10/2024 | 9:27 | 13/10/2024 | 9:28 | NO2 | NOTTING HILL | Urban | Planned |  | 35 | 35 | 1 | 1 | No
| 150987 | 13/10/2024 | 13:50 | 13/10/2024 | 15:21 | NO4 | NOTTING HILL | Urban | Planned |  | 52 | 4732 | 91 | 1 | No
| 150987 | 13/10/2024 | 13:50 | 13/10/2024 | 15:21 | NO7 | NOTTING HILL | Urban | Planned |  | 7 | 637 | 91 | 1 | No
| 150988 | 2024-12-11 | 8:20 | 2024-12-11 | 17:57 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 95 | 54815 | 577 | 1 | No
| 150990 | 17/10/2024 | 8:35 | 17/10/2024 | 12:30 | MTN32 | MORNINGTON | Rural Short | Planned |  | 2 | 470 | 235 | 1 | No
| 150991 | 20/11/2024 | 7:37 | 20/11/2024 | 15:50 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 22 | 10846 | 493 | 1 | No
| 150992 | 2024-10-10 | 9:40 | 2024-10-10 | 10:40 | HT8 | HEATHERTON | Urban | Planned |  | 32 | 1920 | 60 | 1 | No
| 150993 | 2024-10-10 | 11:05 | 2024-10-10 | 12:50 | HT4 | HEATHERTON | Urban | Planned |  | 6 | 630 | 105 | 1 | No
| 150996 | 14/10/2024 | 9:40 | 14/10/2024 | 11:21 | STO21 | SORRENTO | Rural Short | Planned |  | 1 | 101 | 101 | 1 | No
| 150998 | 29/10/2024 | 8:42 | 29/10/2024 | 11:01 | HGS23 | HASTINGS | Rural Short | Planned |  | 31 | 4309 | 139 | 1 | No
| 151000 | 2024-10-10 | 8:30 | 2024-10-10 | 11:40 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 4 | 760 | 190 | 1 | No
| 151036 | 16/10/2024 | 8:50 | 16/10/2024 | 14:50 | MGE31 | MULGRAVE | Urban | Planned |  | 26 | 9360 | 360 | 1 | No
| 151045 | 2024-01-11 | 8:01 | 2024-01-11 | 9:16 | LD3 | LYNDALE | Urban | Planned |  | 53 | 3975 | 75 | 1 | No
| 151049 | 31/10/2024 | 8:00 | 31/10/2024 | 11:00 | LWN34 | LANGWARRIN | Urban | Planned |  | 49 | 8820 | 180 | 1 | No
| 151050 | 19/10/2024 | 8:46 | 19/10/2024 | 11:19 | M21 | MENTONE | Urban | Planned |  | 24 | 3672 | 153 | 1 | No
| 151052 | 13/10/2024 | 7:33 | 13/10/2024 | 13:18 | DSH33 | DANDENONG SOUTH | Urban | Planned |  | 7 | 2415 | 345 | 1 | No
| 151062 | 13/10/2024 | 9:40 | 13/10/2024 | 11:37 | SV32 | SPRINGVALE | Urban | Planned |  | 61 | 7137 | 117 | 1 | No
| 151063 | 2024-11-10 | 11:01 | 13/10/2024 | 14:25 | SS14 | SPRINGVALE SOUTH | Urban | Planned |  | 1 | 3084 | 3084 | 1 | No
| 151067 | 2024-11-11 | 8:43 | 2024-11-11 | 10:37 | STO22 | SORRENTO | Urban | Planned |  | 16 | 1824 | 114 | 1 | No
| 151073 | 13/10/2024 | 8:03 | 13/10/2024 | 8:55 | NP33 | NOBLE PARK | Urban | Planned |  | 117 | 6084 | 52 | 1 | No
| 151094 | 2024-10-10 | 12:13 | 2024-10-10 | 12:18 | MTN32 | MORNINGTON | Rural Short | Planned |  | 3 | 15 | 5 | 1 | No
| 151095 | 13/10/2024 | 12:33 | 13/10/2024 | 14:24 | MC31 | MORDIALLOC | Urban | Planned |  | 25 | 2775 | 111 | 1 | No
| 151098 | 2024-12-11 | 8:22 | 2024-12-11 | 12:37 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 149 | 37995 | 255 | 1 | No
| 151104 | 2024-10-11 | 7:30 | 2024-10-11 | 13:31 | HT11 | HEATHERTON | Urban | Planned |  | 16 | 5776 | 361 | 1 | No
| 151107 | 16/10/2024 | 8:30 | 16/10/2024 | 15:30 | NB36 | NORTH BRIGHTON | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 151107 | 16/10/2024 | 8:50 | 16/10/2024 | 13:41 | NB36 | NORTH BRIGHTON | Urban | Planned |  | 87 | 25317 | 291 | 1 | No
| 151110 | 2024-12-10 | 8:00 | 2024-12-10 | 12:50 | MGE22 | MULGRAVE | Urban | Planned |  | 1 | 290 | 290 | 1 | No
| 151117 | 16/10/2024 | 12:51 | 16/10/2024 | 15:25 | DN11 | DANDENONG | Urban | Planned |  | 88 | 13552 | 154 | 1 | No
| 151123 | 14/10/2024 | 12:01 | 14/10/2024 | 12:49 | HGS33 | HASTINGS | Rural Short | Planned |  | 108 | 5184 | 48 | 1 | No
| 151126 | 13/10/2024 | 8:12 | 13/10/2024 | 12:27 | SV23 | SPRINGVALE | Urban | Planned |  | 109 | 27795 | 255 | 1 | No
| 151127 | 2024-12-10 | 9:35 | 2024-12-10 | 14:39 | NW21 | NUNAWADING | Urban | Planned |  | 28 | 8512 | 304 | 1 | No
| 151130 | 13/10/2024 | 8:01 | 13/10/2024 | 14:41 | MC31 | MORDIALLOC | Urban | Planned |  | 18 | 7200 | 400 | 1 | No
| 151130 | 13/10/2024 | 8:01 | 13/10/2024 | 14:41 | MC34 | MORDIALLOC | Urban | Planned |  | 104 | 41600 | 400 | 1 | No
| 151133 | 16/10/2024 | 8:01 | 16/10/2024 | 11:13 | NP14 | NOBLE PARK | Urban | Planned |  | 85 | 16320 | 192 | 1 | No
| 151136 | 20/10/2024 | 8:11 | 20/10/2024 | 16:26 | BU22 | BULLEEN | Urban | Planned |  | 30 | 14850 | 495 | 1 | No
| 151136 | 20/10/2024 | 8:11 | 20/10/2024 | 16:26 | WD16 | WEST DONCASTER | Urban | Planned |  | 268 | 132660 | 495 | 1 | No
| 151137 | 2024-07-11 | 8:00 | 2024-07-11 | 13:00 | DMA13 | DROMANA | Rural Short | Planned |  | 1 | 300 | 300 | 1 | No
| 151137 | 2024-07-11 | 8:31 | 2024-07-11 | 12:00 | DMA13 | DROMANA | Rural Short | Planned |  | 700 | 146300 | 209 | 1 | No
| 151139 | 2024-07-11 | 14:54 | 2024-07-11 | 16:42 | RBD24 | ROSEBUD | Urban | Planned |  | 424 | 45792 | 108 | 1 | No
| 151143 | 17/10/2024 | 9:08 | 17/10/2024 | 12:05 | EM11 | EAST MALVERN | Urban | Planned |  | 13 | 2301 | 177 | 1 | No
| 151145 | 18/10/2024 | 8:30 | 18/10/2024 | 12:40 | M11 | MENTONE | Urban | Planned |  | 277 | 69250 | 250 | 2 | No
| 151145 | 18/10/2024 | 8:30 | 18/10/2024 | 15:00 | M11 | MENTONE | Urban | Planned |  | 2 | 780 | 390 | 1 | No
| 151147 | 17/10/2024 | 11:40 | 17/10/2024 | 13:20 | CRM23 | CARRUM | Urban | Planned |  | 12 | 1200 | 100 | 1 | No
| 151148 | 15/10/2024 | 8:21 | 15/10/2024 | 12:04 | FSH21 | FRANKSTON SOUTH | Rural Short | Planned |  | 26 | 5798 | 223 | 1 | No
| 151150 | 22/11/2024 | 12:01 | 22/11/2024 | 17:01 | MTN32 | MORNINGTON | Rural Short | Planned |  | 2 | 600 | 300 | 1 | No
| 151150 | 22/11/2024 | 13:50 | 22/11/2024 | 16:30 | MTN32 | MORNINGTON | Rural Short | Planned |  | 42 | 6720 | 160 | 1 | No
| 151153 | 15/10/2024 | 10:55 | 15/10/2024 | 13:27 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 31 | 4712 | 152 | 1 | No
| 151158 | 15/10/2024 | 13:44 | 15/10/2024 | 13:52 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 4 | 32 | 8 | 1 | No
| 151168 | 23/10/2024 | 8:30 | 23/10/2024 | 10:16 | EM6 | EAST MALVERN | Urban | Planned |  | 3 | 318 | 106 | 1 | No
| 151174 | 28/10/2024 | 7:45 | 28/10/2024 | 13:35 | OE14 | OAKLEIGH EAST | Urban | Planned |  | 34 | 11900 | 350 | 1 | No
| 151178 | 14/10/2024 | 12:05 | 14/10/2024 | 13:00 | STO21 | SORRENTO | Rural Short | Planned |  | 1 | 55 | 55 | 1 | No
| 151179 | 22/10/2024 | 9:34 | 22/10/2024 | 13:21 | HT4 | HEATHERTON | Urban | Planned |  | 61 | 13847 | 227 | 1 | No
| 151184 | 16/10/2024 | 10:50 | 16/10/2024 | 13:05 | MTN32 | MORNINGTON | Rural Short | Planned |  | 3 | 405 | 135 | 1 | No
| 151190 | 2024-11-10 | 8:02 | 2024-11-10 | 12:43 | FTN13 | FRANKSTON | Urban | Planned |  | 93 | 26133 | 281 | 1 | No
| 151194 | 2024-09-10 | 8:25 | 2024-09-10 | 13:40 | RBD13 | ROSEBUD | Urban | Planned |  | 29 | 9135 | 315 | 1 | No
| 151195 | 2024-08-11 | 8:00 | 2024-08-11 | 11:30 | DMA24 | DROMANA | Rural Short | Planned |  | 65 | 13650 | 210 | 1 | No
| 151203 | 16/10/2024 | 4:30 | 16/10/2024 | 4:45 | DVY31 | DANDENONG VALLEY | Urban | Planned |  | 2 | 30 | 15 | 1 | No
| 151205 | 16/10/2024 | 2:30 | 16/10/2024 | 3:03 | DSH32 | DANDENONG SOUTH | Urban | Planned |  | 15 | 495 | 33 | 1 | No
| 151208 | 18/10/2024 | 9:00 | 18/10/2024 | 12:00 | BT21 | BENTLEIGH | Urban | Planned |  | 14 | 2520 | 180 | 1 | No
| 151214 | 20/10/2024 | 8:03 | 20/10/2024 | 8:30 | KBH33 | KEYSBOROUGH | Urban | Planned |  | 8 | 216 | 27 | 1 | No
| 151220 | 20/10/2024 | 12:30 | 20/10/2024 | 14:30 | KBH35 | KEYSBOROUGH | Urban | Planned |  | 1 | 120 | 120 | 1 | No
| 151220 | 20/10/2024 | 12:35 | 20/10/2024 | 13:50 | KBH35 | KEYSBOROUGH | Urban | Planned |  | 28 | 2100 | 75 | 1 | No
| 151221 | 13/10/2024 | 7:30 | 13/10/2024 | 14:30 | HGS31 | HASTINGS | Rural Short | Planned |  | 1 | 420 | 420 | 1 | No
| 151221 | 13/10/2024 | 8:15 | 13/10/2024 | 10:35 | HGS31 | HASTINGS | Rural Short | Planned |  | 264 | 36960 | 140 | 1 | No
| 151222 | 20/11/2024 | 8:06 | 20/11/2024 | 15:30 | STO13 | SORRENTO | Urban | Planned |  | 124 | 55056 | 444 | 1 | No
| 151224 | 30/10/2024 | 9:06 | 30/10/2024 | 14:24 | BH21 | BOX HILL | Urban | Planned |  | 78 | 24804 | 318 | 1 | No
| 151224 | 30/10/2024 | 9:06 | 30/10/2024 | 14:24 | BH31 | BOX HILL | Urban | Planned |  | 46 | 14628 | 318 | 1 | No
| 151228 | 22/10/2024 | 9:02 | 22/10/2024 | 15:07 | RBD21 | ROSEBUD | Rural Short | Planned |  | 12 | 4380 | 365 | 1 | No
| 151233 | 20/10/2024 | 7:30 | 20/10/2024 | 16:30 | HT11 | HEATHERTON | Urban | Planned |  | 7 | 3780 | 540 | 1 | No
| 151234 | 17/10/2024 | 8:05 | 17/10/2024 | 11:46 | NP33 | NOBLE PARK | Urban | Planned |  | 386 | 85306 | 221 | 1 | No
| 151235 | 17/10/2024 | 11:25 | 17/10/2024 | 13:55 | SS13 | SPRINGVALE SOUTH | Urban | Planned |  | 13 | 1950 | 150 | 1 | No
| 151242 | 27/10/2024 | 7:52 | 27/10/2024 | 15:35 | WD23 | WEST DONCASTER | Urban | Planned |  | 13 | 6019 | 463 | 1 | No
| 151243 | 29/10/2024 | 8:00 | 29/10/2024 | 17:00 | WD14 | WEST DONCASTER | Urban | Planned |  | 1 | 540 | 540 | 1 | No
| 151243 | 29/10/2024 | 8:05 | 29/10/2024 | 17:56 | WD14 | WEST DONCASTER | Urban | Planned |  | 84 | 49644 | 591 | 1 | No
| 151244 | 23/10/2024 | 8:03 | 23/10/2024 | 14:51 | FTN13 | FRANKSTON | Urban | Planned |  | 110 | 44880 | 408 | 1 | No
| 151245 | 17/10/2024 | 22:17 | 18/10/2024 | 3:46 | RWT34 | RINGWOOD | Urban | Planned |  | 60 | 19740 | 329 | 1 | No
| 151254 | 16/10/2024 | 8:04 | 16/10/2024 | 15:21 | OE4 | OAKLEIGH EAST | Urban | Planned |  | 54 | 23598 | 437 | 1 | No
| 151272 | 18/10/2024 | 12:00 | 18/10/2024 | 12:01 | M21 | MENTONE | Urban | Planned |  | 45 | 45 | 1 | 1 | No
| 151275 | 24/10/2024 | 9:19 | 24/10/2024 | 14:21 | DC10 | DONCASTER | Urban | Planned |  | 17 | 5134 | 302 | 1 | No
| 151281 | 26/10/2024 | 19:30 | 27/10/2024 | 2:17 | SR22 | SANDRINGHAM | Urban | Planned |  | 29 | 11803 | 407 | 1 | No
| 151288 | 25/10/2024 | 8:20 | 25/10/2024 | 11:05 | M25 | MENTONE | Urban | Planned |  | 52 | 8580 | 165 | 1 | No
| 151289 | 18/10/2024 | 8:00 | 18/10/2024 | 11:21 | BT21 | BENTLEIGH | Urban | Planned |  | 13 | 2613 | 201 | 1 | No
| 151289 | 18/10/2024 | 8:00 | 18/10/2024 | 11:21 | BT22 | BENTLEIGH | Urban | Planned |  | 325 | 65325 | 201 | 1 | No
| 151295 | 28/11/2024 | 8:08 | 28/11/2024 | 14:05 | STO23 | SORRENTO | Urban | Planned |  | 146 | 52122 | 357 | 1 | No
| 151296 | 2024-03-12 | 8:30 | 2024-03-12 | 14:00 | HGS32 | HASTINGS | Urban | Planned |  | 6 | 1980 | 330 | 1 | No
| 151298 | 23/10/2024 | 1:00 | 23/10/2024 | 3:40 | SVW53 | SPRINGVALE WEST | Urban | Planned |  | 34 | 5440 | 160 | 1 | No
| 151306 | 31/10/2024 | 9:11 | 31/10/2024 | 13:14 | MTN24 | MORNINGTON | Rural Short | Planned |  | 105 | 25515 | 243 | 1 | No
| 151308 | 24/10/2024 | 8:01 | 24/10/2024 | 10:35 | NP23 | NOBLE PARK | Urban | Planned |  | 41 | 6314 | 154 | 1 | No
| 151315 | 24/10/2024 | 8:10 | 24/10/2024 | 10:15 | OR32 | ORMOND | Urban | Planned |  | 37 | 4625 | 125 | 1 | No
| 151316 | 25/10/2024 | 0:30 | 25/10/2024 | 0:52 | STO13 | SORRENTO | Urban | Planned |  | 161 | 3542 | 22 | 1 | No
| 151317 | 24/10/2024 | 9:30 | 24/10/2024 | 15:30 | OR32 | ORMOND | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 151317 | 24/10/2024 | 10:43 | 24/10/2024 | 12:32 | OR32 | ORMOND | Urban | Planned |  | 62 | 6758 | 109 | 1 | No
| 151323 | 25/10/2024 | 3:06 | 25/10/2024 | 3:45 | STO21 | SORRENTO | Rural Short | Planned |  | 69 | 2691 | 39 | 1 | No
| 151331 | 14/11/2024 | 8:01 | 14/11/2024 | 9:25 | DMA15 | DROMANA | Rural Short | Planned |  | 8 | 672 | 84 | 1 | No
| 151335 | 29/10/2024 | 8:25 | 29/10/2024 | 11:45 | K35 | GARDINER | Urban | Planned |  | 25 | 5000 | 200 | 1 | No
| 151336 | 25/10/2024 | 8:21 | 25/10/2024 | 11:21 | HT11 | HEATHERTON | Urban | Planned |  | 60 | 10800 | 180 | 1 | No
| 151336 | 25/10/2024 | 8:21 | 25/10/2024 | 11:21 | M23 | MENTONE | Urban | Planned |  | 25 | 4500 | 180 | 1 | No
| 151337 | 25/10/2024 | 8:44 | 25/10/2024 | 13:52 | HT2 | HEATHERTON | Urban | Planned |  | 11 | 3388 | 308 | 1 | No
| 151338 | 30/10/2024 | 8:19 | 30/10/2024 | 12:11 | CFD22 | CAULFIELD | Urban | Planned |  | 10 | 2320 | 232 | 1 | No
| 151339 | 14/11/2024 | 11:35 | 14/11/2024 | 12:36 | DMA23 | DROMANA | Rural Short | Planned |  | 4 | 244 | 61 | 1 | No
| 151350 | 2024-03-11 | 8:05 | 2024-03-11 | 14:20 | HT11 | HEATHERTON | Urban | Planned |  | 56 | 21000 | 375 | 1 | No
| 151350 | 2024-03-11 | 8:05 | 2024-03-11 | 14:20 | HT2 | HEATHERTON | Urban | Planned |  | 1 | 375 | 375 | 1 | No
| 151356 | 24/10/2024 | 8:34 | 24/10/2024 | 12:14 | BU22 | BULLEEN | Urban | Planned |  | 2 | 440 | 220 | 1 | No
| 151357 | 26/10/2024 | 8:14 | 26/10/2024 | 13:58 | NW21 | NUNAWADING | Urban | Planned |  | 1 | 344 | 344 | 1 | No
| 151358 | 26/10/2024 | 8:19 | 26/10/2024 | 13:01 | HT13 | HEATHERTON | Urban | Planned |  | 38 | 10716 | 282 | 1 | No
| 151358 | 26/10/2024 | 8:19 | 26/10/2024 | 13:01 | HT7 | HEATHERTON | Urban | Planned |  | 3 | 846 | 282 | 1 | No
| 151361 | 21/10/2024 | 8:05 | 21/10/2024 | 12:50 | M25 | MENTONE | Urban | Planned |  | 105 | 29925 | 285 | 1 | No
| 151362 | 27/10/2024 | 8:11 | 27/10/2024 | 15:21 | MTN32 | MORNINGTON | Rural Short | Planned |  | 69 | 29670 | 430 | 1 | No
| 151364 | 24/10/2024 | 8:01 | 24/10/2024 | 10:06 | MC34 | MORDIALLOC | Urban | Planned |  | 15 | 1875 | 125 | 1 | No
| 151365 | 31/10/2024 | 8:42 | 31/10/2024 | 11:56 | RWT35 | RINGWOOD | Urban | Planned |  | 39 | 7566 | 194 | 1 | No
| 151374 | 2024-01-11 | 9:35 | 2024-01-11 | 10:22 | WD34 | WEST DONCASTER | Urban | Planned |  | 86 | 4042 | 47 | 1 | No
| 151377 | 13/11/2024 | 8:00 | 13/11/2024 | 14:00 | RBD21 | ROSEBUD | Rural Short | Planned |  | 2 | 720 | 360 | 1 | No
| 151380 | 30/10/2024 | 8:30 | 30/10/2024 | 16:06 | EM3 | EAST MALVERN | Urban | Planned |  | 55 | 25080 | 456 | 1 | No
| 151382 | 30/11/2024 | 8:10 | 30/11/2024 | 13:15 | KBH31 | KEYSBOROUGH | Urban | Planned |  | 317 | 96685 | 305 | 1 | No
| 151383 | 2024-06-11 | 8:00 | 2024-06-11 | 12:45 | SVW41 | SPRINGVALE WEST | Urban | Planned |  | 15 | 4275 | 285 | 1 | No
| 151384 | 23/10/2024 | 8:45 | 23/10/2024 | 11:27 | RWT35 | RINGWOOD | Urban | Planned |  | 64 | 10368 | 162 | 1 | No
| 151385 | 13/11/2024 | 9:30 | 13/11/2024 | 12:25 | RBD21 | ROSEBUD | Rural Short | Planned |  | 3 | 525 | 175 | 1 | No
| 151386 | 13/11/2024 | 8:10 | 13/11/2024 | 15:45 | CDA24 | CLARINDA | Urban | Planned |  | 38 | 17290 | 455 | 1 | No
| 151387 | 23/10/2024 | 12:00 | 23/10/2024 | 13:15 | EB32 | EAST BURWOOD | Urban | Planned |  | 30 | 2250 | 75 | 1 | No
| 151397 | 20/11/2024 | 8:00 | 20/11/2024 | 11:05 | NP36 | NOBLE PARK | Urban | Planned |  | 4 | 740 | 185 | 1 | No
| 151398 | 25/11/2024 | 8:55 | 25/11/2024 | 13:38 | RBD13 | ROSEBUD | Urban | Planned |  | 39 | 11037 | 283 | 1 | No
| 151399 | 2024-09-12 | 9:00 | 2024-09-12 | 13:05 | STO21 | SORRENTO | Rural Short | Planned |  | 52 | 12740 | 245 | 1 | No
| 151415 | 22/10/2024 | 10:38 | 22/10/2024 | 12:31 | HGS33 | HASTINGS | Rural Short | Planned |  | 4 | 452 | 113 | 1 | No
| 151452 | 24/10/2024 | 11:30 | 24/10/2024 | 13:30 | HGS22 | HASTINGS | Rural Short | Planned |  | 40 | 4800 | 120 | 1 | No
| 151456 | 24/10/2024 | 8:10 | 24/10/2024 | 12:15 | HGS22 | HASTINGS | Rural Short | Planned |  | 53 | 12985 | 245 | 1 | No
| 151461 | 25/10/2024 | 8:55 | 25/10/2024 | 11:21 | HGS33 | HASTINGS | Rural Short | Planned |  | 28 | 4088 | 146 | 1 | No
| 151462 | 25/10/2024 | 11:18 | 25/10/2024 | 14:27 | RWT23 | RINGWOOD | Urban | Planned |  | 121 | 22869 | 189 | 1 | No
| 151463 | 25/10/2024 | 11:51 | 25/10/2024 | 14:45 | HGS32 | HASTINGS | Urban | Planned |  | 49 | 8526 | 174 | 1 | No
| 151468 | 29/10/2024 | 8:32 | 29/10/2024 | 11:38 | MR14 | MOORABBIN | Urban | Planned |  | 22 | 4092 | 186 | 1 | No
| 151472 | 25/10/2024 | 9:30 | 25/10/2024 | 11:50 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 31 | 4340 | 140 | 1 | No
| 151473 | 29/10/2024 | 8:34 | 29/10/2024 | 15:37 | NW23 | NUNAWADING | Urban | Planned |  | 53 | 22419 | 423 | 1 | No
| 151477 | 19/11/2024 | 8:00 | 19/11/2024 | 13:05 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 79 | 24095 | 305 | 1 | No
| 151482 | 31/10/2024 | 8:43 | 31/10/2024 | 12:04 | OR34 | ORMOND | Urban | Planned |  | 57 | 11457 | 201 | 1 | No
| 151483 | 2024-01-11 | 8:55 | 2024-01-11 | 11:30 | RBD23 | ROSEBUD | Urban | Planned |  | 37 | 5735 | 155 | 1 | No
| 151484 | 2024-01-11 | 12:02 | 2024-01-11 | 13:43 | RBD23 | ROSEBUD | Urban | Planned |  | 83 | 8383 | 101 | 1 | No
| 151486 | 20/11/2024 | 10:03 | 20/11/2024 | 12:56 | RBD24 | ROSEBUD | Urban | Planned |  | 227 | 39271 | 173 | 1 | No
| 151487 | 2024-06-11 | 9:40 | 2024-06-11 | 13:40 | RBD23 | ROSEBUD | Urban | Planned |  | 58 | 13920 | 240 | 1 | No
| 151488 | 2024-07-11 | 9:15 | 2024-07-11 | 12:35 | RWT34 | RINGWOOD | Urban | Planned |  | 48 | 9600 | 200 | 1 | No
| 151494 | 29/10/2024 | 8:04 | 29/10/2024 | 10:52 | SV16 | SPRINGVALE | Urban | Planned |  | 1 | 168 | 168 | 1 | No
| 151499 | 25/10/2024 | 8:08 | 25/10/2024 | 13:49 | BU11 | BULLEEN | Urban | Planned |  | 45 | 15345 | 341 | 1 | No
| 151500 | 29/10/2024 | 8:55 | 29/10/2024 | 15:07 | EB32 | EAST BURWOOD | Urban | Planned |  | 38 | 14136 | 372 | 1 | No
| 151501 | 13/11/2024 | 9:55 | 13/11/2024 | 14:20 | CRM35 | CARRUM | Urban | Planned |  | 2 | 530 | 265 | 1 | No
| 151502 | 2024-04-12 | 11:15 | 2024-04-12 | 12:54 | RBD21 | ROSEBUD | Rural Short | Planned |  | 8 | 792 | 99 | 1 | No
| 151507 | 29/10/2024 | 8:52 | 29/10/2024 | 14:14 | BT23 | BENTLEIGH | Urban | Planned |  | 64 | 20608 | 322 | 1 | No
| 151512 | 29/10/2024 | 10:32 | 29/10/2024 | 13:15 | BT12 | BENTLEIGH | Urban | Planned |  | 73 | 11899 | 163 | 1 | No
| 151513 | 29/10/2024 | 8:08 | 29/10/2024 | 9:36 | BT23 | BENTLEIGH | Urban | Planned |  | 47 | 4136 | 88 | 1 | No
| 151514 | 26/11/2024 | 8:00 | 26/11/2024 | 15:30 | OR23 | ORMOND | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 151514 | 26/11/2024 | 8:05 | 26/11/2024 | 13:38 | OR23 | ORMOND | Urban | Planned |  | 80 | 26640 | 333 | 1 | No
| 151515 | 24/10/2024 | 8:00 | 24/10/2024 | 15:30 | CRM23 | CARRUM | Urban | Planned |  | 13 | 5850 | 450 | 1 | No
| 151516 | 30/10/2024 | 8:00 | 30/10/2024 | 13:47 | BT16 | BENTLEIGH | Urban | Planned |  | 161 | 55867 | 347 | 1 | No
| 151517 | 30/10/2024 | 9:05 | 30/10/2024 | 13:26 | BT16 | BENTLEIGH | Urban | Planned |  | 32 | 8352 | 261 | 1 | No
| 151525 | 29/10/2024 | 12:17 | 29/10/2024 | 14:00 | BT12 | BENTLEIGH | Urban | Planned |  | 70 | 7210 | 103 | 1 | No
| 151526 | 22/11/2024 | 8:12 | 22/11/2024 | 13:30 | MTN32 | MORNINGTON | Rural Short | Planned |  | 4 | 1272 | 318 | 1 | No
| 151527 | 28/10/2024 | 8:44 | 28/10/2024 | 12:45 | CDA23 | CLARINDA | Urban | Planned |  | 26 | 6266 | 241 | 1 | No
| 151534 | 2024-04-12 | 8:40 | 2024-04-12 | 10:33 | RBD21 | ROSEBUD | Rural Short | Planned |  | 5 | 565 | 113 | 1 | No
| 151535 | 2024-05-12 | 8:49 | 2024-05-12 | 13:14 | STO21 | SORRENTO | Rural Short | Planned |  | 26 | 6890 | 265 | 1 | No
| 151536 | 31/10/2024 | 8:00 | 31/10/2024 | 14:52 | LD33 | LYNDALE | Urban | Planned |  | 63 | 25956 | 412 | 1 | No
| 151537 | 27/10/2024 | 8:10 | 27/10/2024 | 18:39 | SR21 | SANDRINGHAM | Urban | Planned |  | 85 | 53465 | 629 | 1 | No
| 151537 | 27/10/2024 | 8:10 | 27/10/2024 | 18:39 | SR22 | SANDRINGHAM | Urban | Planned |  | 99 | 62271 | 629 | 1 | No
| 151539 | 28/11/2024 | 11:35 | 28/11/2024 | 13:35 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 9 | 1080 | 120 | 1 | No
| 151545 | 27/10/2024 | 10:08 | 27/10/2024 | 11:28 | SS24 | SPRINGVALE SOUTH | Urban | Planned |  | 7 | 560 | 80 | 1 | No
| 151548 | 20/11/2024 | 22:50 | 21/11/2024 | 4:55 | DC6 | DONCASTER | Urban | Planned |  | 18 | 6570 | 365 | 1 | No
| 151550 | 2024-06-11 | 7:30 | 2024-06-11 | 17:30 | NP12 | NOBLE PARK | Urban | Planned |  | 6 | 3600 | 600 | 1 | No
| 151560 | 31/10/2024 | 12:26 | 31/10/2024 | 15:47 | BT22 | BENTLEIGH | Urban | Planned |  | 44 | 8844 | 201 | 1 | No
| 151561 | 31/10/2024 | 8:37 | 31/10/2024 | 12:09 | BT22 | BENTLEIGH | Urban | Planned |  | 53 | 11236 | 212 | 1 | No
| 151565 | 24/10/2024 | 8:28 | 24/10/2024 | 16:20 | RWT35 | RINGWOOD | Urban | Planned |  | 1 | 472 | 472 | 1 | No
| 151570 | 2024-12-12 | 8:00 | 2024-12-12 | 16:05 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 11 | 5335 | 485 | 1 | No
| 151570 | 2024-12-12 | 8:00 | 2024-12-12 | 16:05 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 90 | 43650 | 485 | 1 | No
| 151571 | 29/10/2024 | 13:50 | 29/10/2024 | 14:50 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 14 | 840 | 60 | 1 | No
| 151572 | 29/10/2024 | 8:50 | 29/10/2024 | 14:30 | EL23 | ELSTERNWICK | Urban | Planned |  | 32 | 10880 | 340 | 1 | No
| 151581 | 29/10/2024 | 8:45 | 29/10/2024 | 14:03 | EL34 | ELSTERNWICK | Urban | Planned |  | 37 | 11766 | 318 | 1 | No
| 151588 | 30/10/2024 | 12:17 | 30/10/2024 | 15:03 | NW21 | NUNAWADING | Urban | Planned |  | 70 | 11620 | 166 | 1 | No
| 151590 | 27/10/2024 | 7:30 | 27/10/2024 | 9:03 | SS14 | SPRINGVALE SOUTH | Urban | Planned |  | 9 | 834.1497 | 92.6833 | 1 | No
| 151591 | 28/10/2024 | 22:45 | 29/10/2024 | 5:30 | BR1 | BEAUMARIS | Urban | Planned |  | 2 | 810 | 405 | 1 | No
| 151593 | 30/10/2024 | 8:35 | 30/10/2024 | 14:02 | STO13 | SORRENTO | Urban | Planned |  | 1 | 327 | 327 | 1 | No
| 151598 | 2024-06-11 | 8:00 | 2024-06-11 | 9:20 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 21 | 1680 | 80 | 1 | No
| 151600 | 2024-01-11 | 10:25 | 2024-01-11 | 12:52 | SV32 | SPRINGVALE | Urban | Planned |  | 65 | 9555 | 147 | 1 | No
| 151603 | 27/11/2024 | 8:00 | 27/11/2024 | 14:20 | DMA15 | DROMANA | Rural Short | Planned |  | 47 | 17848.25 | 379.75 | 1 | No
| 151604 | 2024-11-12 | 8:16 | 2024-11-12 | 9:49 | NB33 | NORTH BRIGHTON | Urban | Planned |  | 20 | 1860 | 93 | 1 | No
| 151605 | 31/10/2024 | 8:30 | 31/10/2024 | 8:31 | BT16 | BENTLEIGH | Urban | Planned |  | 113 | 113 | 1 | 1 | No
| 151607 | 2024-03-11 | 8:00 | 2024-03-11 | 10:57 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 48 | 8496 | 177 | 1 | No
| 151608 | 29/10/2024 | 8:03 | 29/10/2024 | 10:25 | BT13 | BENTLEIGH | Urban | Planned |  | 19 | 2698 | 142 | 1 | No
| 151608 | 29/10/2024 | 8:03 | 29/10/2024 | 10:25 | BT21 | BENTLEIGH | Urban | Planned |  | 57 | 8094 | 142 | 1 | No
| 151609 | 2024-07-11 | 8:55 | 2024-07-11 | 12:30 | RBD23 | ROSEBUD | Urban | Planned |  | 66 | 14190 | 215 | 1 | No
| 151610 | 30/10/2024 | 9:30 | 30/10/2024 | 14:05 | CFD13 | CAULFIELD | Urban | Planned |  | 57 | 15675 | 275 | 1 | No
| 151611 | 2024-01-11 | 8:34 | 2024-01-11 | 12:13 | DC5 | DONCASTER | Urban | Planned |  | 30 | 6570 | 219 | 1 | No
| 151613 | 2024-06-11 | 12:30 | 2024-06-11 | 16:00 | DMA21 | DROMANA | Urban | Planned |  | 2 | 420 | 210 | 1 | No
| 151613 | 2024-06-11 | 13:05 | 2024-06-11 | 14:52 | DMA21 | DROMANA | Urban | Planned |  | 73 | 7811 | 107 | 1 | No
| 151615 | 2024-01-11 | 8:00 | 2024-01-11 | 12:00 | DC5 | DONCASTER | Urban | Planned |  | 43 | 10320 | 240 | 1 | No
| 151618 | 28/11/2024 | 8:01 | 28/11/2024 | 16:38 | WD14 | WEST DONCASTER | Urban | Planned |  | 84 | 43428 | 517 | 1 | No
| 151620 | 2024-01-11 | 9:30 | 2024-01-11 | 15:00 | DC5 | DONCASTER | Urban | Planned |  | 31 | 10230 | 330 | 1 | No
| 151621 | 2024-01-11 | 10:20 | 2024-01-11 | 13:40 | BT22 | BENTLEIGH | Urban | Planned |  | 115 | 23000 | 200 | 1 | No
| 151623 | 2024-04-11 | 6:31 | 2024-04-11 | 16:01 | DN23 | DANDENONG | Urban | Planned |  | 1 | 570 | 570 | 1 | No
| 151625 | 2024-02-12 | 12:15 | 2024-02-12 | 14:25 | DC5 | DONCASTER | Urban | Planned |  | 43 | 5590 | 130 | 1 | No
| 151626 | 31/10/2024 | 8:06 | 31/10/2024 | 11:49 | GW6 | GLEN WAVERLEY | Urban | Planned |  | 1 | 223 | 223 | 1 | No
| 151633 | 2024-10-11 | 8:00 | 2024-10-11 | 15:26 | HGS32 | HASTINGS | Urban | Planned |  | 2 | 892 | 446 | 1 | No
| 151639 | 2024-08-11 | 8:00 | 2024-08-11 | 14:35 | DMA15 | DROMANA | Rural Short | Planned |  | 5 | 1975 | 395 | 1 | No
| 151641 | 2024-01-11 | 8:30 | 2024-01-11 | 15:45 | M12 | MENTONE | Urban | Planned |  | 29 | 12615 | 435 | 1 | No
| 151646 | 2024-07-11 | 9:01 | 2024-07-11 | 15:31 | NW14 | NUNAWADING | Urban | Planned |  | 7 | 2730 | 390 | 1 | No
| 151648 | 2024-02-11 | 8:43 | 2024-02-11 | 11:40 | NW32 | NUNAWADING | Urban | Planned |  | 1 | 177 | 177 | 1 | No
| 151661 | 31/10/2024 | 8:40 | 31/10/2024 | 13:05 | WD34 | WEST DONCASTER | Urban | Planned |  | 27 | 7155 | 265 | 1 | No
| 151664 | 2024-07-11 | 9:12 | 2024-07-11 | 12:05 | NB31 | NORTH BRIGHTON | Urban | Planned |  | 16 | 2768 | 173 | 1 | No
| 151668 | 31/10/2024 | 12:05 | 31/10/2024 | 13:23 | DC8 | DONCASTER | Urban | Planned |  | 22 | 1716 | 78 | 1 | No
| 151670 | 2024-07-11 | 9:54 | 2024-07-11 | 15:50 | RWT23 | RINGWOOD | Urban | Planned |  | 9 | 3204 | 356 | 1 | No
| 151672 | 30/10/2024 | 4:43 | 30/10/2024 | 6:45 | LD5 | LYNDALE | Urban | Planned |  | 4 | 488 | 122 | 1 | No
| 151674 | 2024-06-11 | 9:32 | 2024-06-11 | 11:56 | BU21 | BULLEEN | Urban | Planned |  | 37 | 5328 | 144 | 1 | No
| 151679 | 2024-12-11 | 8:57 | 2024-12-11 | 14:56 | EW2 | ELWOOD | Urban | Planned |  | 137 | 49183 | 359 | 1 | No
| 151681 | 2024-07-11 | 10:00 | 2024-07-11 | 14:00 | K21 | GARDINER | Urban | Planned |  | 8 | 1920 | 240 | 1 | No
| 151685 | 2024-08-11 | 9:10 | 2024-08-11 | 12:20 | BR6 | BEAUMARIS | Urban | Planned |  | 15 | 2850 | 190 | 1 | No
| 151688 | 2024-07-11 | 8:30 | 2024-07-11 | 17:40 | MGE23 | MULGRAVE | Urban | Planned |  | 38 | 20894.3 | 549.85 | 1 | No
| 151700 | 2024-07-11 | 10:12 | 2024-07-11 | 12:20 | NB36 | NORTH BRIGHTON | Urban | Planned |  | 44 | 5632 | 128 | 1 | No
| 151703 | 2024-06-11 | 9:32 | 2024-06-11 | 13:53 | K35 | GARDINER | Urban | Planned |  | 61 | 15921 | 261 | 1 | No
| 151706 | 2024-06-11 | 14:30 | 2024-06-11 | 16:43 | DN10 | DANDENONG | Urban | Planned |  | 6 | 798 | 133 | 1 | No
| 151707 | 2024-07-11 | 8:00 | 2024-07-11 | 8:20 | RBD21 | ROSEBUD | Rural Short | Planned |  | 2 | 40 | 20 | 1 | No
| 151710 | 2024-02-11 | 8:34 | 2024-02-11 | 12:54 | EM7 | EAST MALVERN | Urban | Planned |  | 2 | 520 | 260 | 1 | No
| 151717 | 2024-07-11 | 9:15 | 2024-07-11 | 13:50 | MR13 | MOORABBIN | Urban | Planned |  | 100 | 27500 | 275 | 1 | No
| 151718 | 2024-07-11 | 12:30 | 2024-07-11 | 14:33 | MTN34 | MORNINGTON | Urban | Planned |  | 76 | 9348 | 123 | 1 | No
| 151728 | 16/11/2024 | 8:12 | 16/11/2024 | 13:34 | DVY23 | DANDENONG VALLEY | Urban | Planned |  | 25 | 8050 | 322 | 1 | No
| 151730 | 2024-06-11 | 11:00 | 2024-06-11 | 13:45 | MTN23 | MORNINGTON | Urban | Planned |  | 123 | 20295 | 165 | 1 | No
| 151731 | 16/11/2024 | 14:20 | 16/11/2024 | 15:30 | DVY34 | DANDENONG VALLEY | Urban | Planned |  | 1 | 70 | 70 | 1 | No
| 151734 | 15/11/2024 | 0:31 | 15/11/2024 | 0:41 | BR9 | BEAUMARIS | Urban | Planned |  | 60 | 600 | 10 | 1 | No
| 151741 | 2024-11-11 | 8:40 | 2024-11-11 | 9:40 | RWT12 | RINGWOOD | Urban | Planned |  | 27 | 1620 | 60 | 1 | No
| 151743 | 13/11/2024 | 22:10 | 14/11/2024 | 4:15 | MR12 | MOORABBIN | Urban | Planned |  | 45 | 16425 | 365 | 1 | No
| 151744 | 14/11/2024 | 8:36 | 14/11/2024 | 12:25 | M22 | MENTONE | Urban | Planned |  | 9 | 2061 | 229 | 1 | No
| 151748 | 2024-11-11 | 10:25 | 2024-11-11 | 12:25 | NW23 | NUNAWADING | Urban | Planned |  | 58 | 6960 | 120 | 1 | No
| 151749 | 2024-10-12 | 8:00 | 2024-10-12 | 16:00 | MTN24 | MORNINGTON | Rural Short | Planned |  | 1 | 480 | 480 | 1 | No
| 151749 | 2024-10-12 | 8:45 | 2024-10-12 | 11:39 | MTN24 | MORNINGTON | Rural Short | Planned |  | 51 | 8874 | 174 | 1 | No
| 151750 | 2024-11-11 | 12:55 | 2024-11-11 | 14:00 | NW31 | NUNAWADING | Urban | Planned |  | 34 | 2210 | 65 | 1 | No
| 151751 | 2024-09-11 | 7:25 | 2024-09-11 | 8:29 | DN2 | DANDENONG | Urban | Planned |  | 25 | 1600 | 64 | 1 | No
| 151752 | 14/11/2024 | 10:00 | 14/11/2024 | 13:08 | SS21 | SPRINGVALE SOUTH | Urban | Planned |  | 7 | 1316 | 188 | 1 | No
| 151756 | 2024-09-11 | 7:31 | 2024-09-11 | 17:01 | EB24 | EAST BURWOOD | Urban | Planned |  | 1 | 570 | 570 | 1 | No
| 151756 | 2024-09-11 | 8:00 | 2024-09-11 | 17:20 | EB24 | EAST BURWOOD | Urban | Planned |  | 148 | 82880 | 560 | 1 | No
| 151762 | 2024-12-11 | 8:04 | 2024-12-11 | 15:37 | DC10 | DONCASTER | Urban | Planned |  | 48 | 21744 | 453 | 1 | No
| 151766 | 24/11/2024 | 7:21 | 24/11/2024 | 16:26 | CFD26 | CAULFIELD | Urban | Planned |  | 126 | 68670 | 545 | 1 | No
| 151769 | 17/11/2024 | 8:00 | 17/11/2024 | 16:00 | FTN21 | FRANKSTON | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 151769 | 17/11/2024 | 8:03 | 17/11/2024 | 13:15 | FTN21 | FRANKSTON | Urban | Planned |  | 75 | 23400 | 312 | 1 | No
| 151773 | 2024-07-11 | 8:00 | 2024-07-11 | 16:50 | DN10 | DANDENONG | Urban | Planned |  | 113 | 59890 | 530 | 1 | No
| 151775 | 2024-12-11 | 8:02 | 2024-12-11 | 9:03 | HGS21 | HASTINGS | Rural Short | Planned |  | 2 | 122 | 61 | 1 | No
| 151776 | 2024-09-11 | 8:10 | 2024-09-11 | 10:35 | HT8 | HEATHERTON | Urban | Planned |  | 31 | 4495 | 145 | 1 | No
| 151780 | 13/11/2024 | 11:35 | 13/11/2024 | 12:50 | NW31 | NUNAWADING | Urban | Planned |  | 16 | 1200 | 75 | 1 | No
| 151781 | 2024-09-11 | 11:20 | 2024-09-11 | 12:26 | HT3 | HEATHERTON | Urban | Planned |  | 26 | 1716 | 66 | 1 | No
| 151784 | 2024-06-11 | 8:45 | 2024-06-11 | 11:30 | DC7 | DONCASTER | Urban | Planned |  | 51 | 8415 | 165 | 1 | No
| 151788 | 15/11/2024 | 9:05 | 15/11/2024 | 12:06 | LWN23 | LANGWARRIN | Urban | Planned |  | 50 | 9050 | 181 | 1 | No
| 151795 | 19/11/2024 | 8:20 | 19/11/2024 | 17:05 | NW21 | NUNAWADING | Urban | Planned |  | 38 | 19950 | 525 | 1 | No
| 151796 | 2024-10-11 | 7:36 | 2024-10-11 | 7:54 | MC22 | MORDIALLOC | Urban | Planned |  | 36 | 648 | 18 | 1 | No
| 151796 | 2024-10-11 | 8:00 | 2024-10-11 | 9:00 | MC22 | MORDIALLOC | Urban | Planned |  | 1 | 60 | 60 | 1 | No
| 151798 | 2024-08-11 | 8:50 | 2024-08-11 | 11:12 | MGE13 | MULGRAVE | Urban | Planned |  | 26 | 3692 | 142 | 1 | No
| 151798 | 2024-08-11 | 8:50 | 2024-08-11 | 11:12 | MGE21 | MULGRAVE | Urban | Planned |  | 14 | 1988 | 142 | 1 | No
| 151801 | 2024-10-11 | 10:30 | 2024-10-11 | 12:30 | MC14 | MORDIALLOC | Urban | Planned |  | 6 | 720 | 120 | 1 | No
| 151805 | 18/10/2024 | 8:01 | 18/10/2024 | 12:55 | M33 | MENTONE | Urban | Planned |  | 23 | 6762.7659 | 294.0333 | 1 | No
| 151812 | 2024-06-11 | 8:20 | 2024-06-11 | 13:35 | GW11 | GLEN WAVERLEY | Urban | Planned |  | 32 | 10080 | 315 | 1 | No
| 151814 | 2024-08-11 | 9:50 | 2024-08-11 | 11:20 | CM25 | CHELTENHAM | Urban | Planned |  | 43 | 3870 | 90 | 1 | No
| 151815 | 2024-04-12 | 8:32 | 2024-04-12 | 12:42 | MTN22 | MORNINGTON | Rural Short | Planned |  | 69 | 17250 | 250 | 1 | No
| 151818 | 17/11/2024 | 8:00 | 17/11/2024 | 13:38 | MC14 | MORDIALLOC | Urban | Planned |  | 70 | 23660 | 338 | 1 | No
| 151819 | 15/11/2024 | 8:10 | 15/11/2024 | 11:20 | RBD13 | ROSEBUD | Urban | Planned |  | 22 | 4180 | 190 | 1 | No
| 151830 | 19/11/2024 | 10:00 | 19/11/2024 | 15:05 | WD14 | WEST DONCASTER | Urban | Planned |  | 21 | 6405 | 305 | 1 | No
| 151839 | 19/11/2024 | 8:07 | 19/11/2024 | 15:05 | CRM13 | CARRUM | Urban | Planned |  | 175 | 73150 | 418 | 1 | No
| 151841 | 22/11/2024 | 8:00 | 22/11/2024 | 14:45 | HGS23 | HASTINGS | Rural Short | Planned |  | 74 | 29970 | 405 | 1 | No
| 151842 | 22/11/2024 | 8:20 | 22/11/2024 | 13:15 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 32 | 9440 | 295 | 1 | No
| 151844 | 26/11/2024 | 9:33 | 26/11/2024 | 12:59 | RWT35 | RINGWOOD | Urban | Planned |  | 48 | 9888 | 206 | 1 | No
| 151845 | 26/11/2024 | 8:04 | 26/11/2024 | 9:47 | RWT35 | RINGWOOD | Urban | Planned |  | 44 | 4532 | 103 | 1 | No
| 151847 | 2024-03-12 | 13:15 | 2024-03-12 | 15:40 | RBD23 | ROSEBUD | Urban | Planned |  | 75 | 10875 | 145 | 1 | No
| 151848 | 2024-08-11 | 8:00 | 2024-08-11 | 13:45 | RBD13 | ROSEBUD | Urban | Planned |  | 36 | 12411 | 344.75 | 1 | No
| 151848 | 2024-08-11 | 8:00 | 2024-08-11 | 13:45 | RBD22 | ROSEBUD | Urban | Planned |  | 101 | 34819.75 | 344.75 | 1 | No
| 151850 | 25/11/2024 | 8:48 | 25/11/2024 | 18:38 | DMA15 | DROMANA | Rural Short | Planned |  | 70 | 41300 | 590 | 1 | No
| 151852 | 18/11/2024 | 8:00 | 18/11/2024 | 16:20 | DC4 | DONCASTER | Urban | Planned |  | 44 | 22000 | 500 | 1 | No
| 151853 | 29/11/2024 | 8:08 | 29/11/2024 | 13:42 | RWT35 | RINGWOOD | Urban | Planned |  | 127 | 42418 | 334 | 1 | No
| 151854 | 29/11/2024 | 12:18 | 29/11/2024 | 14:02 | RWT23 | RINGWOOD | Urban | Planned |  | 23 | 2392 | 104 | 1 | No
| 151855 | 28/11/2024 | 8:00 | 28/11/2024 | 11:18 | RWT34 | RINGWOOD | Urban | Planned |  | 64 | 12672 | 198 | 1 | No
| 151857 | 29/11/2024 | 8:30 | 29/11/2024 | 12:13 | RBD11 | ROSEBUD | Urban | Planned |  | 36 | 8028 | 223 | 1 | No
| 151868 | 2024-12-11 | 10:13 | 2024-12-11 | 11:50 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 1 | 97 | 97 | 1 | No
| 151873 | 2024-07-11 | 11:51 | 2024-07-11 | 13:32 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 13 | 1313 | 101 | 1 | No
| 151874 | 2024-08-11 | 9:18 | 2024-08-11 | 11:48 | MGE33 | MULGRAVE | Urban | Planned |  | 49 | 7350 | 150 | 1 | No
| 151875 | 2024-07-11 | 8:31 | 2024-07-11 | 10:19 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 54 | 5832 | 108 | 1 | No
| 151876 | 2024-07-11 | 9:54 | 2024-07-11 | 15:00 | EB21 | EAST BURWOOD | Urban | Planned |  | 72 | 22032 | 306 | 1 | No
| 151891 | 2024-08-11 | 8:44 | 2024-08-11 | 10:32 | EB14 | EAST BURWOOD | Urban | Planned |  | 74 | 7992 | 108 | 1 | No
| 151897 | 2024-08-11 | 8:00 | 2024-08-11 | 11:40 | WD36 | WEST DONCASTER | Urban | Planned |  | 11 | 2420 | 220 | 1 | No
| 151899 | 13/11/2024 | 8:28 | 13/11/2024 | 13:28 | EW9 | ELWOOD | Urban | Planned |  | 4 | 1200 | 300 | 1 | No
| 151910 | 2024-07-11 | 8:40 | 2024-07-11 | 11:20 | WD14 | WEST DONCASTER | Urban | Planned |  | 2 | 320 | 160 | 1 | No
| 151911 | 13/11/2024 | 8:15 | 13/11/2024 | 10:17 | MR22 | MOORABBIN | Urban | Planned |  | 28 | 3416 | 122 | 1 | No
| 151911 | 13/11/2024 | 8:15 | 13/11/2024 | 10:17 | MR23 | MOORABBIN | Urban | Planned |  | 42 | 5124 | 122 | 1 | No
| 151913 | 27/11/2024 | 11:10 | 27/11/2024 | 13:00 | NP36 | NOBLE PARK | Urban | Planned |  | 4 | 440 | 110 | 1 | No
| 151915 | 13/11/2024 | 8:00 | 13/11/2024 | 11:01 | NP23 | NOBLE PARK | Urban | Planned |  | 38 | 6878 | 181 | 1 | No
| 151917 | 13/11/2024 | 11:00 | 13/11/2024 | 15:30 | NP36 | NOBLE PARK | Urban | Planned |  | 9 | 2430 | 270 | 1 | No
| 151920 | 2024-10-11 | 8:05 | 2024-10-11 | 13:33 | BT16 | BENTLEIGH | Urban | Planned |  | 237 | 77736 | 328 | 1 | No
| 151926 | 16/11/2024 | 8:00 | 16/11/2024 | 12:33 | EM6 | EAST MALVERN | Urban | Planned |  | 43 | 11739 | 273 | 1 | No
| 151927 | 13/11/2024 | 9:30 | 13/11/2024 | 12:30 | DC5 | DONCASTER | Urban | Planned |  | 70 | 12600 | 180 | 1 | No
| 151928 | 15/11/2024 | 8:31 | 15/11/2024 | 14:40 | NW22 | NUNAWADING | Urban | Planned |  | 187 | 69031.05 | 369.15 | 2 | No
| 151928 | 15/11/2024 | 8:31 | 15/11/2024 | 15:01 | NW22 | NUNAWADING | Urban | Planned |  | 1 | 390 | 390 | 1 | No
| 151939 | 2024-12-11 | 8:35 | 2024-12-11 | 11:15 | SS11 | SPRINGVALE SOUTH | Urban | Planned |  | 165 | 26400 | 160 | 1 | No
| 151940 | 2024-10-12 | 10:15 | 2024-10-12 | 10:45 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 60 | 30 | 1 | No
| 151941 | 2024-06-12 | 12:15 | 2024-06-12 | 13:45 | NP36 | NOBLE PARK | Urban | Planned |  | 4 | 360 | 90 | 1 | No
| 151944 | 17/12/2024 | 8:07 | 17/12/2024 | 13:04 | RBD23 | ROSEBUD | Urban | Planned |  | 166 | 49302 | 297 | 1 | No
| 151950 | 16/11/2024 | 6:00 | 16/11/2024 | 15:30 | DN11 | DANDENONG | Urban | Planned |  | 1 | 570 | 570 | 1 | No
| 151951 | 2024-05-12 | 8:04 | 2024-05-12 | 14:06 | LWN33 | LANGWARRIN | Urban | Planned |  | 182 | 65884 | 362 | 1 | No
| 151956 | 2024-12-11 | 9:15 | 2024-12-11 | 13:33 | RWT35 | RINGWOOD | Urban | Planned |  | 95 | 24510 | 258 | 1 | No
| 151957 | 21/11/2024 | 8:00 | 21/11/2024 | 18:00 | MTN32 | MORNINGTON | Rural Short | Planned |  | 104 | 62400 | 600 | 1 | No
| 151975 | 21/11/2024 | 8:42 | 21/11/2024 | 16:32 | DN10 | DANDENONG | Urban | Planned |  | 52 | 24440 | 470 | 1 | No
| 151979 | 17/11/2024 | 8:00 | 17/11/2024 | 13:00 | CDA22 | CLARINDA | Urban | Planned |  | 43 | 12900 | 300 | 1 | No
| 151984 | 21/11/2024 | 8:55 | 21/11/2024 | 10:55 | RWT35 | RINGWOOD | Urban | Planned |  | 34 | 4080 | 120 | 1 | No
| 151987 | 2024-12-11 | 8:50 | 2024-12-11 | 12:45 | DN21 | DANDENONG | Urban | Planned |  | 56 | 13160 | 235 | 1 | No
| 151990 | 15/11/2024 | 8:30 | 15/11/2024 | 11:35 | CRM35 | CARRUM | Urban | Planned |  | 186 | 34410 | 185 | 1 | No
| 151993 | 15/11/2024 | 8:31 | 15/11/2024 | 11:18 | KBH32 | KEYSBOROUGH | Urban | Planned |  | 77 | 12859 | 167 | 1 | No
| 151994 | 2024-12-11 | 9:35 | 2024-12-11 | 15:15 | DMA14 | DROMANA | Urban | Planned |  | 33 | 11220 | 340 | 1 | No
| 151996 | 15/11/2024 | 8:57 | 15/11/2024 | 10:54 | SH22 | SURREY HILLS | Urban | Planned |  | 60 | 7020 | 117 | 1 | No
| 151999 | 19/11/2024 | 8:00 | 19/11/2024 | 15:00 | NW21 | NUNAWADING | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 151999 | 19/11/2024 | 8:40 | 19/11/2024 | 14:55 | NW21 | NUNAWADING | Urban | Planned |  | 42 | 15750 | 375 | 1 | No
| 152001 | 15/11/2024 | 8:50 | 15/11/2024 | 11:50 | DC1 | DONCASTER | Urban | Planned |  | 23 | 4140 | 180 | 1 | No
| 152008 | 14/11/2024 | 8:50 | 14/11/2024 | 12:00 | STO22 | SORRENTO | Urban | Planned |  | 44 | 8360 | 190 | 1 | No
| 152013 | 21/11/2024 | 9:10 | 21/11/2024 | 14:09 | CRM13 | CARRUM | Urban | Planned |  | 93 | 27807 | 299 | 1 | No
| 152015 | 14/11/2024 | 8:05 | 14/11/2024 | 16:15 | EW3 | ELWOOD | Urban | Planned |  | 98 | 48020 | 490 | 1 | No
| 152016 | 2024-05-12 | 8:26 | 2024-05-12 | 12:05 | CRM35 | CARRUM | Urban | Planned |  | 38 | 8322 | 219 | 1 | No
| 152017 | 22/11/2024 | 8:36 | 22/11/2024 | 17:30 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 10 | 5340 | 534 | 1 | No
| 152018 | 2024-03-12 | 8:00 | 2024-03-12 | 12:57 | RBD23 | ROSEBUD | Urban | Planned |  | 50 | 14850 | 297 | 1 | No
| 152021 | 2024-10-12 | 11:25 | 2024-10-12 | 14:32 | RWT12 | RINGWOOD | Urban | Planned |  | 64 | 11968 | 187 | 1 | No
| 152024 | 23/01/2025 | 8:00 | 23/01/2025 | 17:00 | SVW55 | SPRINGVALE WEST | Urban | Planned |  | 111 | 59940 | 540 | 1 | No
| 152030 | 24/11/2024 | 6:30 | 24/11/2024 | 17:31 | CFD26 | CAULFIELD | Urban | Planned |  | 1 | 660.85 | 660.85 | 1 | No
| 152034 | 13/11/2024 | 9:55 | 13/11/2024 | 14:00 | GW2 | GLEN WAVERLEY | Urban | Planned |  | 60 | 14700 | 245 | 1 | No
| 152035 | 16/01/2025 | 9:43 | 16/01/2025 | 14:42 | EM8 | EAST MALVERN | Urban | Planned |  | 8 | 2392 | 299 | 1 | No
| 152038 | 13/11/2024 | 8:50 | 13/11/2024 | 11:55 | NO7 | NOTTING HILL | Urban | Planned |  | 15 | 2775 | 185 | 1 | No
| 152042 | 21/11/2024 | 8:50 | 21/11/2024 | 15:00 | GW11 | GLEN WAVERLEY | Urban | Planned |  | 11 | 4070 | 370 | 1 | No
| 152043 | 20/11/2024 | 8:00 | 20/11/2024 | 16:00 | GW12 | GLEN WAVERLEY | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 152043 | 20/11/2024 | 8:09 | 20/11/2024 | 13:58 | GW4 | GLEN WAVERLEY | Urban | Planned |  | 40 | 13960 | 349 | 1 | No
| 152045 | 14/11/2024 | 8:00 | 14/11/2024 | 13:09 | DN10 | DANDENONG | Urban | Planned |  | 235 | 72615 | 309 | 1 | No
| 152051 | 19/11/2024 | 9:00 | 19/11/2024 | 12:00 | STO21 | SORRENTO | Rural Short | Planned |  | 11 | 1980 | 180 | 1 | No
| 152053 | 2024-01-12 | 8:18 | 2024-01-12 | 13:28 | BT12 | BENTLEIGH | Urban | Planned |  | 124 | 38440 | 310 | 1 | No
| 152054 | 19/11/2024 | 11:35 | 19/11/2024 | 12:30 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 28 | 1540 | 55 | 1 | No
| 152059 | 29/11/2024 | 8:50 | 29/11/2024 | 13:20 | RBD21 | ROSEBUD | Rural Short | Planned |  | 35 | 9450 | 270 | 1 | No
| 152074 | 21/11/2024 | 5:08 | 21/11/2024 | 5:20 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 12 | 144 | 12 | 1 | No
| 152077 | 2024-04-12 | 8:02 | 2024-04-12 | 9:35 | EW9 | ELWOOD | Urban | Planned |  | 4 | 372 | 93 | 1 | No
| 152078 | 26/11/2024 | 8:35 | 26/11/2024 | 9:13 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 67 | 2546 | 38 | 1 | No
| 152080 | 14/11/2024 | 3:42 | 14/11/2024 | 6:40 | DVY34 | DANDENONG VALLEY | Urban | Planned |  | 2 | 356 | 178 | 1 | No
| 152081 | 20/11/2024 | 8:50 | 20/11/2024 | 14:35 | RWT23 | RINGWOOD | Urban | Planned |  | 64 | 22080 | 345 | 1 | No
| 152083 | 25/11/2024 | 8:20 | 25/11/2024 | 10:50 | DC8 | DONCASTER | Urban | Planned |  | 2 | 300 | 150 | 1 | No
| 152087 | 20/11/2024 | 8:20 | 20/11/2024 | 15:56 | LD6 | LYNDALE | Urban | Planned |  | 14 | 6384 | 456 | 1 | No
| 152098 | 15/11/2024 | 8:00 | 15/11/2024 | 14:08 | CRM23 | CARRUM | Urban | Planned |  | 156 | 57408 | 368 | 1 | No
| 152098 | 15/11/2024 | 8:00 | 15/11/2024 | 14:08 | CRM35 | CARRUM | Urban | Planned |  | 145 | 53360 | 368 | 1 | No
| 152099 | 2025-07-01 | 8:36 | 2025-07-01 | 13:10 | RBD14 | ROSEBUD | Urban | Planned |  | 100 | 27400 | 274 | 1 | No
| 152102 | 20/11/2024 | 8:10 | 20/11/2024 | 12:10 | MTN31 | MORNINGTON | Urban | Planned |  | 16 | 3840 | 240 | 1 | No
| 152104 | 23/11/2024 | 7:23 | 23/11/2024 | 9:00 | BU15 | BULLEEN | Urban | Planned |  | 1 | 97 | 97 | 1 | No
| 152106 | 25/11/2024 | 12:00 | 25/11/2024 | 13:30 | BH31 | BOX HILL | Urban | Planned |  | 10 | 900 | 90 | 1 | No
| 152107 | 2025-07-01 | 13:10 | 2025-07-01 | 15:55 | RBD24 | ROSEBUD | Urban | Planned |  | 29 | 4785 | 165 | 1 | No
| 152111 | 2024-08-12 | 7:20 | 2024-08-12 | 16:08 | MR33 | MOORABBIN | Urban | Planned |  | 74 | 39072 | 528 | 1 | No
| 152113 | 15/01/2025 | 8:53 | 15/01/2025 | 11:20 | MC21 | MORDIALLOC | Urban | Planned |  | 7 | 1029 | 147 | 1 | No
| 152114 | 23/11/2024 | 8:00 | 23/11/2024 | 11:15 | HT13 | HEATHERTON | Urban | Planned |  | 14 | 2730 | 195 | 1 | No
| 152114 | 23/11/2024 | 8:00 | 23/11/2024 | 11:15 | HT3 | HEATHERTON | Urban | Planned |  | 62 | 12090 | 195 | 1 | No
| 152118 | 29/01/2025 | 9:32 | 29/01/2025 | 15:00 | SV34 | SPRINGVALE | Urban | Planned |  | 26 | 8528 | 328 | 1 | No
| 152120 | 17/11/2024 | 7:01 | 17/11/2024 | 13:25 | OE2 | OAKLEIGH EAST | Urban | Planned |  | 17 | 6530.55 | 384.15 | 1 | No
| 152126 | 30/01/2025 | 8:10 | 30/01/2025 | 15:20 | DN25 | DANDENONG | Urban | Planned |  | 55 | 23650 | 430 | 1 | No
| 152137 | 21/11/2024 | 8:25 | 21/11/2024 | 11:32 | BU21 | BULLEEN | Urban | Planned |  | 14 | 2618 | 187 | 1 | No
| 152146 | 19/11/2024 | 8:33 | 19/11/2024 | 13:09 | CDA22 | CLARINDA | Urban | Planned |  | 70 | 19320 | 276 | 1 | No
| 152150 | 25/11/2024 | 8:42 | 25/11/2024 | 12:00 | DC1 | DONCASTER | Urban | Planned |  | 16 | 3168 | 198 | 1 | No
| 152157 | 20/11/2024 | 8:00 | 20/11/2024 | 11:42 | NW31 | NUNAWADING | Urban | Planned |  | 68 | 15096 | 222 | 1 | No
| 152160 | 20/11/2024 | 8:00 | 20/11/2024 | 14:05 | CDA22 | CLARINDA | Urban | Planned |  | 191 | 69715 | 365 | 1 | No
| 152171 | 22/11/2024 | 8:00 | 22/11/2024 | 12:33 | BR15 | BEAUMARIS | Urban | Planned |  | 34 | 9282 | 273 | 2 | No
| 152171 | 22/11/2024 | 8:00 | 22/11/2024 | 16:30 | BR15 | BEAUMARIS | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 152173 | 19/12/2024 | 8:00 | 19/12/2024 | 11:05 | STO23 | SORRENTO | Urban | Planned |  | 157 | 29024.0719 | 184.8667 | 1 | No
| 152180 | 28/11/2024 | 8:01 | 28/11/2024 | 15:10 | BR1 | BEAUMARIS | Urban | Planned |  | 65 | 27885 | 429 | 1 | No
| 152186 | 22/11/2024 | 9:00 | 22/11/2024 | 16:00 | NW33 | NUNAWADING | Urban | Planned |  | 41 | 17220 | 420 | 1 | No
| 152195 | 23/11/2024 | 7:04 | 23/11/2024 | 7:22 | DVY22 | DANDENONG VALLEY | Urban | Planned |  | 1 | 18 | 18 | 1 | No
| 152197 | 23/11/2024 | 10:01 | 23/11/2024 | 12:01 | DSH32 | DANDENONG SOUTH | Urban | Planned |  | 2 | 240 | 120 | 1 | No
| 152205 | 20/11/2024 | 8:00 | 20/11/2024 | 15:30 | SH32 | SURREY HILLS | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 152205 | 20/11/2024 | 9:49 | 20/11/2024 | 14:52 | SH32 | SURREY HILLS | Urban | Planned |  | 62 | 18786 | 303 | 1 | No
| 152215 | 2024-03-12 | 8:00 | 2024-03-12 | 14:44 | DMA24 | DROMANA | Rural Short | Planned |  | 41 | 16564 | 404 | 1 | No
| 152218 | 2024-02-12 | 8:23 | 2024-02-12 | 11:30 | OR25 | ORMOND | Urban | Planned |  | 1 | 187 | 187 | 1 | No
| 152223 | 2024-08-12 | 8:23 | 2024-08-12 | 10:40 | DC12 | DONCASTER | Urban | Planned |  | 41 | 5617 | 137 | 1 | No
| 152224 | 2024-08-12 | 12:00 | 2024-08-12 | 13:16 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 12 | 912 | 76 | 1 | No
| 152225 | 13/12/2024 | 8:20 | 13/12/2024 | 14:10 | DMA14 | DROMANA | Urban | Planned |  | 15 | 5250 | 350 | 1 | No
| 152226 | 14/11/2024 | 8:00 | 14/11/2024 | 17:00 | RBD12 | ROSEBUD | Rural Short | Planned |  | 1 | 540 | 540 | 1 | No
| 152226 | 14/11/2024 | 8:10 | 14/11/2024 | 23:35 | RBD12 | ROSEBUD | Rural Short | Planned |  | 88 | 81400 | 925 | 1 | No
| 152228 | 22/11/2024 | 8:36 | 22/11/2024 | 11:47 | DMA23 | DROMANA | Rural Short | Planned |  | 47 | 8977 | 191 | 1 | No
| 152231 | 13/12/2024 | 11:05 | 13/12/2024 | 12:30 | DMA14 | DROMANA | Urban | Planned |  | 24 | 2040 | 85 | 1 | No
| 152234 | 29/11/2024 | 8:40 | 29/11/2024 | 12:41 | NW22 | NUNAWADING | Urban | Planned |  | 50 | 12050 | 241 | 1 | No
| 152234 | 29/11/2024 | 8:40 | 29/11/2024 | 12:41 | RWT23 | RINGWOOD | Urban | Planned |  | 45 | 10845 | 241 | 1 | No
| 152240 | 25/11/2024 | 10:33 | 25/11/2024 | 16:48 | HGS33 | HASTINGS | Rural Short | Planned |  | 63 | 23625 | 375 | 1 | No
| 152248 | 2024-06-12 | 8:38 | 2024-06-12 | 12:08 | NW11 | NUNAWADING | Urban | Planned |  | 71 | 14910 | 210 | 1 | No
| 152249 | 2024-06-12 | 12:45 | 2024-06-12 | 13:55 | NW11 | NUNAWADING | Urban | Planned |  | 54 | 3780 | 70 | 1 | No
| 152250 | 2024-03-12 | 8:00 | 2024-03-12 | 18:09 | BR1 | BEAUMARIS | Urban | Planned |  | 34 | 20706 | 609 | 1 | No
| 152258 | 28/11/2024 | 12:05 | 28/11/2024 | 14:14 | NW21 | NUNAWADING | Urban | Planned |  | 33 | 4257 | 129 | 1 | No
| 152262 | 28/11/2024 | 8:30 | 28/11/2024 | 11:35 | GW10 | GLEN WAVERLEY | Urban | Planned |  | 57 | 10545 | 185 | 1 | No
| 152272 | 24/11/2024 | 8:00 | 24/11/2024 | 17:00 | NP33 | NOBLE PARK | Urban | Planned |  | 1 | 540 | 540 | 1 | No
| 152272 | 24/11/2024 | 8:13 | 24/11/2024 | 17:10 | NP33 | NOBLE PARK | Urban | Planned |  | 104 | 55848 | 537 | 1 | No
| 152272 | 24/11/2024 | 8:13 | 24/11/2024 | 17:10 | SV33 | SPRINGVALE | Urban | Planned |  | 111 | 59607 | 537 | 1 | No
| 152287 | 21/11/2024 | 8:00 | 21/11/2024 | 16:00 | M35 | MENTONE | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 152287 | 21/11/2024 | 8:05 | 21/11/2024 | 15:08 | M35 | MENTONE | Urban | Planned |  | 162 | 68526 | 423 | 1 | No
| 152291 | 27/11/2024 | 8:42 | 27/11/2024 | 11:01 | M21 | MENTONE | Urban | Planned |  | 46 | 6394 | 139 | 1 | No
| 152302 | 2024-03-12 | 8:00 | 2024-03-12 | 16:00 | NW23 | NUNAWADING | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 152302 | 2024-03-12 | 8:45 | 2024-03-12 | 14:00 | NW23 | NUNAWADING | Urban | Planned |  | 164 | 51660 | 315 | 1 | No
| 152311 | 29/11/2024 | 8:00 | 29/11/2024 | 16:00 | MR33 | MOORABBIN | Urban | Planned |  | 14 | 6720 | 480 | 1 | No
| 152319 | 23/11/2024 | 19:30 | 24/11/2024 | 4:25 | SR22 | SANDRINGHAM | Urban | Planned |  | 29 | 15503.8843 | 534.6167 | 1 | No
| 152322 | 2025-08-01 | 8:20 | 2025-08-01 | 11:30 | NW14 | NUNAWADING | Urban | Planned |  | 1 | 190 | 190 | 1 | No
| 152323 | 2024-09-12 | 8:00 | 2024-09-12 | 16:00 | STO13 | SORRENTO | Urban | Planned |  | 10 | 4800 | 480 | 1 | No
| 152324 | 22/11/2024 | 5:13 | 22/11/2024 | 8:00 | HT2 | HEATHERTON | Urban | Planned |  | 6 | 1002 | 167 | 1 | No
| 152327 | 23/11/2024 | 8:00 | 23/11/2024 | 18:00 | EB33 | EAST BURWOOD | Urban | Planned |  | 18 | 10800 | 600 | 1 | No
| 152330 | 29/11/2024 | 8:30 | 29/11/2024 | 15:30 | BW33 | BURWOOD | Urban | Planned |  | 2 | 840 | 420 | 1 | No
| 152330 | 29/11/2024 | 8:32 | 29/11/2024 | 13:07 | BW33 | BURWOOD | Urban | Planned |  | 47 | 12925 | 275 | 1 | No
| 152332 | 2024-02-12 | 22:00 | 2024-03-12 | 5:33 | SS13 | SPRINGVALE SOUTH | Urban | Planned |  | 2 | 906 | 453 | 1 | No
| 152335 | 26/11/2024 | 8:09 | 26/11/2024 | 13:45 | NW23 | NUNAWADING | Urban | Planned |  | 1 | 336 | 336 | 1 | No
| 152337 | 2024-01-12 | 8:00 | 2024-01-12 | 11:30 | M34 | MENTONE | Urban | Planned |  | 101 | 21210 | 210 | 1 | No
| 152341 | 24/11/2024 | 8:07 | 24/11/2024 | 11:34 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 48 | 9936 | 207 | 1 | No
| 152342 | 29/11/2024 | 8:45 | 29/11/2024 | 15:00 | DN9 | DANDENONG | Urban | Planned |  | 1 | 375 | 375 | 1 | No
| 152346 | 13/12/2024 | 11:16 | 13/12/2024 | 11:52 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 72 | 36 | 1 | No
| 152354 | 2024-04-12 | 8:00 | 2024-04-12 | 13:05 | BR1 | BEAUMARIS | Urban | Planned |  | 12 | 3658.2 | 304.85 | 1 | No
| 152358 | 27/11/2024 | 10:57 | 27/11/2024 | 13:19 | OR34 | ORMOND | Urban | Planned |  | 52 | 7384 | 142 | 1 | No
| 152365 | 2024-01-12 | 10:00 | 2024-01-12 | 16:00 | MC32 | MORDIALLOC | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 152365 | 2024-01-12 | 12:30 | 2024-01-12 | 14:06 | MC32 | MORDIALLOC | Urban | Planned |  | 90 | 8640 | 96 | 1 | No
| 152369 | 2024-11-12 | 8:55 | 2024-11-12 | 15:50 | EM5 | EAST MALVERN | Urban | Planned |  | 39 | 16185 | 415 | 1 | No
| 152371 | 30/11/2024 | 8:01 | 30/11/2024 | 12:20 | NO5 | NOTTING HILL | Urban | Planned |  | 12 | 3108 | 259 | 1 | No
| 152372 | 27/11/2024 | 8:00 | 27/11/2024 | 16:00 | SR26 | SANDRINGHAM | Urban | Planned |  | 2 | 960 | 480 | 1 | No
| 152372 | 27/11/2024 | 8:06 | 27/11/2024 | 14:15 | SR26 | SANDRINGHAM | Urban | Planned |  | 143 | 52767 | 369 | 1 | No
| 152373 | 28/11/2024 | 8:50 | 28/11/2024 | 12:36 | MGE34 | MULGRAVE | Urban | Planned |  | 56 | 12656 | 226 | 1 | No
| 152374 | 13/12/2024 | 8:00 | 13/12/2024 | 17:00 | CFD14 | CAULFIELD | Urban | Planned |  | 4 | 2160 | 540 | 1 | No
| 152374 | 13/12/2024 | 8:01 | 13/12/2024 | 14:55 | CFD14 | CAULFIELD | Urban | Planned |  | 291 | 120474 | 414 | 1 | No
| 152378 | 2024-01-12 | 8:34 | 2024-01-12 | 15:26 | NW23 | NUNAWADING | Urban | Planned |  | 15 | 6180 | 412 | 1 | No
| 152381 | 28/11/2024 | 8:00 | 28/11/2024 | 15:30 | CRM13 | CARRUM | Urban | Planned |  | 5 | 2250 | 450 | 1 | No
| 152381 | 28/11/2024 | 8:07 | 28/11/2024 | 15:40 | CRM13 | CARRUM | Urban | Planned |  | 197 | 89241 | 453 | 1 | No
| 152386 | 2024-10-12 | 8:47 | 2024-10-12 | 15:06 | GW4 | GLEN WAVERLEY | Urban | Planned |  | 1 | 379 | 379 | 1 | No
| 152392 | 2024-08-12 | 7:30 | 2024-08-12 | 14:45 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 17 | 7395 | 435 | 1 | No
| 152404 | 2024-03-12 | 9:15 | 2024-03-12 | 13:25 | BT12 | BENTLEIGH | Urban | Planned |  | 58 | 14500 | 250 | 1 | No
| 152408 | 30/11/2024 | 8:34 | 30/11/2024 | 10:06 | HGS22 | HASTINGS | Rural Short | Planned |  | 1 | 92 | 92 | 1 | No
| 152422 | 30/11/2024 | 12:30 | 30/11/2024 | 13:55 | HGS22 | HASTINGS | Rural Short | Planned |  | 1 | 85 | 85 | 1 | No
| 152423 | 28/11/2024 | 8:04 | 28/11/2024 | 15:34 | MTN35 | MORNINGTON | Rural Short | Planned |  | 142 | 63900 | 450 | 1 | No
| 152432 | 27/11/2024 | 9:20 | 27/11/2024 | 13:00 | EB11 | EAST BURWOOD | Urban | Planned |  | 23 | 5060 | 220 | 1 | No
| 152432 | 27/11/2024 | 9:20 | 27/11/2024 | 13:00 | EB21 | EAST BURWOOD | Urban | Planned |  | 15 | 3300 | 220 | 1 | No
| 152436 | 30/11/2024 | 14:16 | 30/11/2024 | 15:50 | HGS21 | HASTINGS | Rural Short | Planned |  | 7 | 658 | 94 | 1 | No
| 152437 | 15/12/2024 | 8:10 | 15/12/2024 | 11:55 | GW5 | GLEN WAVERLEY | Urban | Planned |  | 2 | 450 | 225 | 1 | No
| 152440 | 2024-01-12 | 6:31 | 2024-01-12 | 16:19 | HT6 | HEATHERTON | Urban | Planned |  | 1 | 588 | 588 | 1 | No
| 152443 | 24/11/2024 | 8:00 | 24/11/2024 | 9:30 | BW33 | BURWOOD | Urban | Planned |  | 187 | 16811.3 | 89.9 | 2 | No
| 152443 | 24/11/2024 | 8:00 | 24/11/2024 | 17:30 | BW33 | BURWOOD | Urban | Planned |  | 1 | 570 | 570 | 1 | No
| 152447 | 29/11/2024 | 8:05 | 29/11/2024 | 11:35 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 21 | 4410 | 210 | 1 | No
| 152463 | 24/11/2024 | 7:30 | 24/11/2024 | 8:50 | K21 | GARDINER | Urban | Planned |  | 60 | 4800 | 80 | 1 | No
| 152475 | 2024-07-12 | 8:01 | 2024-07-12 | 18:15 | BW21 | BURWOOD | Urban | Planned |  | 62 | 38088.6646 | 614.3333 | 1 | No
| 152487 | 30/11/2024 | 9:00 | 30/11/2024 | 11:20 | SR31 | SANDRINGHAM | Urban | Planned |  | 79 | 11060 | 140 | 1 | No
| 152492 | 19/12/2024 | 11:45 | 19/12/2024 | 13:34 | HGS22 | HASTINGS | Rural Short | Planned |  | 24 | 2616 | 109 | 1 | No
| 152495 | 2024-04-12 | 8:50 | 2024-04-12 | 11:30 | NW21 | NUNAWADING | Urban | Planned |  | 38 | 6080 | 160 | 1 | No
| 152503 | 2024-10-12 | 9:15 | 2024-10-12 | 15:15 | HT4 | HEATHERTON | Urban | Planned |  | 147 | 52920 | 360 | 1 | No
| 152510 | 15/12/2024 | 7:06 | 15/12/2024 | 13:25 | NW23 | NUNAWADING | Urban | Planned |  | 91 | 34489 | 379 | 1 | No
| 152516 | 30/11/2024 | 6:31 | 30/11/2024 | 16:01 | DVY33 | DANDENONG VALLEY | Urban | Planned |  | 1 | 570 | 570 | 1 | No
| 152522 | 19/12/2024 | 8:12 | 19/12/2024 | 12:15 | FSH21 | FRANKSTON SOUTH | Rural Short | Planned |  | 70 | 17010 | 243 | 1 | No
| 152526 | 2024-03-12 | 8:23 | 2024-03-12 | 10:47 | NB36 | NORTH BRIGHTON | Urban | Planned |  | 49 | 7056 | 144 | 1 | No
| 152529 | 2024-05-12 | 9:55 | 2024-05-12 | 13:25 | BR4 | BEAUMARIS | Urban | Planned |  | 40 | 8400 | 210 | 1 | No
| 152530 | 2024-09-12 | 8:20 | 2024-09-12 | 13:12 | HT1 | HEATHERTON | Urban | Planned |  | 171 | 49932 | 292 | 1 | No
| 152531 | 2024-03-12 | 8:45 | 2024-03-12 | 11:08 | DMA21 | DROMANA | Urban | Planned |  | 42 | 6006 | 143 | 1 | No
| 152533 | 2024-08-12 | 6:31 | 2024-08-12 | 16:01 | DVY23 | DANDENONG VALLEY | Urban | Planned |  | 1 | 570 | 570 | 1 | No
| 152534 | 2024-01-12 | 8:07 | 2024-01-12 | 16:01 | STO13 | SORRENTO | Urban | Planned |  | 225 | 106646.2425 | 473.9833 | 1 | No
| 152537 | 2024-06-12 | 8:00 | 2024-06-12 | 16:00 | DC1 | DONCASTER | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 152537 | 2024-06-12 | 10:30 | 2024-06-12 | 15:45 | DC1 | DONCASTER | Urban | Planned |  | 31 | 9765 | 315 | 1 | No
| 152538 | 2024-06-12 | 8:05 | 2024-06-12 | 14:35 | EM7 | EAST MALVERN | Urban | Planned |  | 2 | 780 | 390 | 1 | No
| 152548 | 2024-03-12 | 8:03 | 2024-03-12 | 11:48 | EB24 | EAST BURWOOD | Urban | Planned |  | 42 | 9450 | 225 | 1 | No
| 152552 | 2024-05-12 | 8:01 | 2024-05-12 | 12:15 | NP33 | NOBLE PARK | Urban | Planned |  | 52 | 13208 | 254 | 1 | No
| 152552 | 2024-05-12 | 8:01 | 2024-05-12 | 12:15 | SV32 | SPRINGVALE | Urban | Planned |  | 2 | 508 | 254 | 1 | No
| 152553 | 18/12/2024 | 9:00 | 18/12/2024 | 15:30 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 174 | 67860 | 390 | 1 | No
| 152555 | 28/11/2024 | 8:00 | 28/11/2024 | 16:30 | SR22 | SANDRINGHAM | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 152555 | 28/11/2024 | 8:42 | 28/11/2024 | 16:32 | SR34 | SANDRINGHAM | Urban | Planned |  | 121 | 56870 | 470 | 1 | No
| 152558 | 18/12/2024 | 8:25 | 18/12/2024 | 11:00 | MTN22 | MORNINGTON | Rural Short | Planned |  | 52 | 8060 | 155 | 1 | No
| 152563 | 2025-12-01 | 7:31 | 2025-12-01 | 9:27 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 192 | 22348.8 | 116.4 | 2 | No
| 152563 | 2025-12-01 | 7:31 | 2025-12-01 | 13:01 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 2 | 660 | 330 | 1 | No
| 152563 | 2025-12-01 | 7:31 | 2025-12-01 | 9:27 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 29 | 3375.6 | 116.4 | 1 | No
| 152566 | 2024-07-12 | 8:08 | 2024-07-12 | 12:15 | HT11 | HEATHERTON | Urban | Planned |  | 65 | 16055 | 247 | 1 | No
| 152567 | 2024-03-12 | 8:19 | 2024-03-12 | 19:30 | DMA14 | DROMANA | Urban | Planned |  | 115 | 77165 | 671 | 1 | No
| 152570 | 20/01/2025 | 9:16 | 20/01/2025 | 15:29 | MTN32 | MORNINGTON | Rural Short | Planned |  | 133 | 49609 | 373 | 1 | No
| 152571 | 2024-06-12 | 8:30 | 2024-06-12 | 11:15 | M34 | MENTONE | Urban | Planned |  | 47 | 7755 | 165 | 1 | No
| 152572 | 2025-08-01 | 8:00 | 2025-08-01 | 9:51 | DVY12 | DANDENONG VALLEY | Urban | Planned |  | 1 | 111 | 111 | 1 | No
| 152575 | 2025-08-01 | 10:32 | 2025-08-01 | 11:55 | DVY12 | DANDENONG VALLEY | Urban | Planned |  | 1 | 83 | 83 | 1 | No
| 152577 | 2024-03-12 | 6:24 | 2024-03-12 | 6:45 | DMA23 | DROMANA | Rural Short | Planned |  | 5 | 105 | 21 | 1 | No
| 152580 | 2024-10-12 | 8:17 | 2024-10-12 | 10:31 | BT25 | BENTLEIGH | Urban | Planned |  | 49 | 6566 | 134 | 1 | No
| 152583 | 2024-04-12 | 8:45 | 2024-04-12 | 13:40 | EW14 | ELWOOD | Urban | Planned |  | 56 | 16520 | 295 | 1 | No
| 152583 | 2024-04-12 | 8:45 | 2024-04-12 | 13:40 | EW2 | ELWOOD | Urban | Planned |  | 72 | 21240 | 295 | 1 | No
| 152584 | 2024-05-12 | 8:00 | 2024-05-12 | 12:12 | MR24 | MOORABBIN | Urban | Planned |  | 56 | 14112 | 252 | 1 | No
| 152585 | 2025-08-01 | 8:05 | 2025-08-01 | 11:30 | KBH34 | KEYSBOROUGH | Urban | Planned |  | 2 | 410 | 205 | 1 | No
| 152591 | 2025-08-01 | 12:30 | 2025-08-01 | 13:35 | KBH34 | KEYSBOROUGH | Urban | Planned |  | 3 | 195 | 65 | 1 | No
| 152594 | 2024-02-12 | 3:55 | 2024-02-12 | 6:50 | DC1 | DONCASTER | Urban | Planned |  | 1 | 175 | 175 | 1 | No
| 152597 | 2024-03-12 | 22:09 | 2024-04-12 | 0:10 | CRM13 | CARRUM | Urban | Planned |  | 254 | 30734 | 121 | 1 | No
| 152598 | 2024-12-12 | 8:00 | 2024-12-12 | 10:26 | HT1 | HEATHERTON | Urban | Planned |  | 43 | 6278 | 146 | 1 | No
| 152599 | 2024-12-12 | 12:25 | 2024-12-12 | 13:55 | HT1 | HEATHERTON | Urban | Planned |  | 14 | 1260 | 90 | 1 | No
| 152600 | 2024-06-12 | 9:02 | 2024-06-12 | 11:30 | DC1 | DONCASTER | Urban | Planned |  | 76 | 11248 | 148 | 1 | No
| 152601 | 2024-12-12 | 8:00 | 2024-12-12 | 10:50 | HT10 | HEATHERTON | Urban | Planned |  | 34 | 5780 | 170 | 1 | No
| 152612 | 2024-03-12 | 10:30 | 2024-03-12 | 13:25 | BT12 | BENTLEIGH | Urban | Planned |  | 121 | 21175 | 175 | 1 | No
| 152613 | 2024-12-12 | 4:30 | 2024-12-12 | 6:30 | HT7 | HEATHERTON | Urban | Planned |  | 11 | 1320 | 120 | 1 | No
| 152614 | 2024-08-12 | 8:00 | 2024-08-12 | 15:13 | HT6 | HEATHERTON | Urban | Planned |  | 1 | 433 | 433 | 1 | No
| 152614 | 2024-08-12 | 8:00 | 2024-08-12 | 15:13 | HT7 | HEATHERTON | Urban | Planned |  | 92 | 39836 | 433 | 1 | No
| 152617 | 2024-08-12 | 10:50 | 2024-08-12 | 11:32 | BT22 | BENTLEIGH | Urban | Planned |  | 50 | 2100 | 42 | 1 | No
| 152618 | 2024-06-12 | 8:19 | 2024-06-12 | 9:44 | DC8 | DONCASTER | Urban | Planned |  | 65 | 5525 | 85 | 1 | No
| 152620 | 2024-06-12 | 10:20 | 2024-06-12 | 10:55 | EB33 | EAST BURWOOD | Urban | Planned |  | 21 | 735 | 35 | 1 | No
| 152622 | 13/12/2024 | 8:31 | 13/12/2024 | 11:14 | HGS33 | HASTINGS | Rural Short | Planned |  | 35 | 5705 | 163 | 1 | No
| 152623 | 2025-09-01 | 6:50 | 2025-09-01 | 17:30 | GW6 | GLEN WAVERLEY | Urban | Planned |  | 1 | 640 | 640 | 1 | No
| 152625 | 2025-09-01 | 6:50 | 2025-10-01 | 13:15 | GW6 | GLEN WAVERLEY | Urban | Planned |  | 1 | 1825 | 1825 | 1 | No
| 152632 | 19/12/2024 | 8:20 | 19/12/2024 | 10:15 | CRM13 | CARRUM | Urban | Planned |  | 51 | 5865 | 115 | 1 | No
| 152640 | 2024-03-12 | 8:30 | 2024-03-12 | 11:15 | NW22 | NUNAWADING | Urban | Planned |  | 55 | 9075 | 165 | 1 | No
| 152641 | 2024-03-12 | 12:00 | 2024-03-12 | 14:40 | NW22 | NUNAWADING | Urban | Planned |  | 123 | 19680 | 160 | 1 | No
| 152643 | 2024-04-12 | 12:30 | 2024-04-12 | 14:10 | DC4 | DONCASTER | Urban | Planned |  | 2 | 200 | 100 | 1 | No
| 152645 | 2024-10-12 | 8:00 | 2024-10-12 | 13:00 | EB31 | EAST BURWOOD | Urban | Planned |  | 1 | 300 | 300 | 1 | No
| 152646 | 2024-10-12 | 10:30 | 2024-10-12 | 13:15 | DC8 | DONCASTER | Urban | Planned |  | 28 | 4620 | 165 | 1 | No
| 152648 | 17/12/2024 | 22:35 | 18/12/2024 | 2:30 | DC3 | DONCASTER | Urban | Planned |  | 1 | 235 | 235 | 1 | No
| 152651 | 15/12/2024 | 8:10 | 15/12/2024 | 16:47 | FTN21 | FRANKSTON | Urban | Planned |  | 73 | 37741 | 517 | 1 | No
| 152653 | 2024-04-12 | 8:40 | 2024-04-12 | 10:02 | BH21 | BOX HILL | Urban | Planned |  | 21 | 1722 | 82 | 1 | No
| 152654 | 2024-08-12 | 8:00 | 2024-08-12 | 10:07 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 15 | 1905 | 127 | 1 | No
| 152656 | 2024-05-12 | 8:45 | 2024-05-12 | 12:25 | GW11 | GLEN WAVERLEY | Urban | Planned |  | 46 | 10120 | 220 | 1 | No
| 152657 | 2024-10-12 | 8:14 | 2024-10-12 | 11:34 | SR35 | SANDRINGHAM | Urban | Planned |  | 112 | 22400 | 200 | 1 | No
| 152659 | 19/12/2024 | 8:23 | 19/12/2024 | 10:45 | RBD13 | ROSEBUD | Urban | Planned |  | 37 | 5254 | 142 | 1 | No
| 152659 | 19/12/2024 | 8:23 | 19/12/2024 | 10:45 | RBD22 | ROSEBUD | Urban | Planned |  | 52 | 7384 | 142 | 1 | No
| 152660 | 2024-10-12 | 8:00 | 2024-10-12 | 15:30 | EW9 | ELWOOD | Urban | Planned |  | 4 | 1800 | 450 | 1 | No
| 152660 | 2024-10-12 | 10:15 | 2024-10-12 | 13:55 | EW9 | ELWOOD | Urban | Planned |  | 27 | 5940 | 220 | 1 | No
| 152664 | 2024-05-12 | 8:00 | 2024-05-12 | 14:23 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 347 | 132901 | 383 | 1 | No
| 152665 | 2024-12-12 | 8:00 | 2024-12-12 | 12:00 | DC5 | DONCASTER | Urban | Planned |  | 43 | 10320 | 240 | 1 | No
| 152667 | 2024-12-12 | 9:30 | 2024-12-12 | 15:00 | DC5 | DONCASTER | Urban | Planned |  | 31 | 10230 | 330 | 1 | No
| 152668 | 2024-09-12 | 4:00 | 2024-09-12 | 5:11 | EB11 | EAST BURWOOD | Urban | Planned |  | 1 | 71 | 71 | 1 | No
| 152678 | 2024-09-12 | 7:30 | 2024-09-12 | 15:30 | BW35 | BURWOOD | Urban | Planned |  | 3 | 1440 | 480 | 1 | No
| 152685 | 17/01/2025 | 8:20 | 17/01/2025 | 11:15 | MR22 | MOORABBIN | Urban | Planned |  | 179 | 31325 | 175 | 1 | No
| 152686 | 2024-06-12 | 8:02 | 2024-06-12 | 9:56 | EM9 | EAST MALVERN | Urban | Planned |  | 21 | 2394 | 114 | 1 | No
| 152688 | 2024-10-12 | 8:40 | 2024-10-12 | 13:09 | CM22 | CHELTENHAM | Urban | Planned |  | 48 | 12912 | 269 | 1 | No
| 152690 | 2024-10-12 | 9:00 | 2024-10-12 | 12:30 | DC2 | DONCASTER | Urban | Planned |  | 14 | 2940 | 210 | 1 | No
| 152692 | 15/12/2024 | 7:30 | 15/12/2024 | 15:30 | LD5 | LYNDALE | Urban | Planned |  | 2 | 960 | 480 | 1 | No
| 152698 | 2024-04-12 | 8:00 | 2024-04-12 | 11:10 | NP12 | NOBLE PARK | Urban | Planned |  | 93 | 17670 | 190 | 1 | No
| 152699 | 2024-04-12 | 11:28 | 2024-04-12 | 12:17 | NP36 | NOBLE PARK | Urban | Planned |  | 41 | 2009 | 49 | 1 | No
| 152700 | 2024-12-12 | 8:00 | 2024-12-12 | 10:08 | DMA12 | DROMANA | Urban | Planned |  | 83 | 10624 | 128 | 1 | No
| 152702 | 2024-12-12 | 11:00 | 2024-12-12 | 16:00 | DMA12 | DROMANA | Urban | Planned |  | 1 | 300 | 300 | 1 | No
| 152702 | 2024-12-12 | 11:33 | 2024-12-12 | 13:41 | DMA12 | DROMANA | Urban | Planned |  | 162 | 20736 | 128 | 1 | No
| 152704 | 2024-12-12 | 8:57 | 2024-12-12 | 12:07 | MTN35 | MORNINGTON | Rural Short | Planned |  | 36 | 6840 | 190 | 1 | No
| 152706 | 2024-10-12 | 8:20 | 2024-10-12 | 9:45 | DC5 | DONCASTER | Urban | Planned |  | 53 | 4505 | 85 | 1 | No
| 152707 | 2024-10-12 | 10:00 | 2024-10-12 | 11:08 | DC5 | DONCASTER | Urban | Planned |  | 46 | 3128 | 68 | 1 | No
| 152708 | 18/12/2024 | 8:00 | 18/12/2024 | 17:00 | OAK23 | OAKLEIGH | Urban | Planned |  | 47 | 25380 | 540 | 1 | No
| 152709 | 2024-06-12 | 8:00 | 2024-06-12 | 12:00 | HT10 | HEATHERTON | Urban | Planned |  | 128 | 30720 | 240 | 1 | No
| 152710 | 2025-08-01 | 9:15 | 2025-08-01 | 11:53 | HGS22 | HASTINGS | Rural Short | Planned |  | 42 | 6636 | 158 | 1 | No
| 152721 | 2024-10-12 | 8:20 | 2024-10-12 | 15:30 | DN10 | DANDENONG | Urban | Planned |  | 68 | 29240 | 430 | 1 | No
| 152728 | 30/11/2024 | 8:06 | 30/11/2024 | 12:50 | SVW56 | SPRINGVALE WEST | Urban | Planned |  | 59 | 16756 | 284 | 1 | No
| 152730 | 2024-08-12 | 7:30 | 2024-08-12 | 13:01 | OR33 | ORMOND | Urban | Planned |  | 2 | 662 | 331 | 1 | No
| 152732 | 13/12/2024 | 8:05 | 13/12/2024 | 13:30 | DMA12 | DROMANA | Urban | Planned |  | 85 | 27625 | 325 | 1 | No
| 152744 | 2024-12-12 | 8:00 | 2024-12-12 | 13:07 | NO6 | NOTTING HILL | Urban | Planned |  | 51 | 15657 | 307 | 1 | No
| 152747 | 17/12/2024 | 9:00 | 17/12/2024 | 15:40 | EM9 | EAST MALVERN | Urban | Planned |  | 221 | 88400 | 400 | 1 | No
| 152756 | 2024-07-12 | 8:00 | 2024-07-12 | 17:55 | WD26 | WEST DONCASTER | Urban | Planned |  | 25 | 14867.5 | 594.7 | 1 | No
| 152763 | 13/12/2024 | 8:30 | 13/12/2024 | 11:20 | EM3 | EAST MALVERN | Urban | Planned |  | 8 | 1360 | 170 | 1 | No
| 152765 | 18/12/2024 | 8:00 | 18/12/2024 | 16:30 | CRM35 | CARRUM | Urban | Planned |  | 2 | 1020 | 510 | 1 | No
| 152769 | 2024-11-12 | 8:35 | 2024-11-12 | 14:15 | NW13 | NUNAWADING | Urban | Planned |  | 20 | 6800 | 340 | 1 | No
| 152772 | 2024-10-12 | 13:00 | 2024-10-12 | 14:45 | MTN22 | MORNINGTON | Rural Short | Planned |  | 6 | 630 | 105 | 1 | No
| 152784 | 2025-02-02 | 8:00 | 2025-02-02 | 10:10 | CRM14 | CARRUM | Rural Short | Planned |  | 580 | 75400 | 130 | 1 | No
| 152785 | 2024-11-12 | 8:00 | 2024-11-12 | 10:40 | MR11 | MOORABBIN | Urban | Planned |  | 14 | 2240 | 160 | 1 | No
| 152788 | 2024-03-12 | 8:00 | 2024-03-12 | 9:50 | MR13 | MOORABBIN | Urban | Planned |  | 15 | 1650 | 110 | 1 | No
| 152792 | 20/01/2025 | 21:00 | 21/01/2025 | 3:30 | SR32 | SANDRINGHAM | Urban | Planned |  | 1 | 390 | 390 | 1 | No
| 152796 | 2024-11-12 | 9:00 | 2024-11-12 | 11:20 | CFD13 | CAULFIELD | Urban | Planned |  | 76 | 10640 | 140 | 1 | No
| 152799 | 2024-11-12 | 8:10 | 2024-11-12 | 14:45 | RWT24 | RINGWOOD | Urban | Planned |  | 191 | 75445 | 395 | 1 | No
| 152800 | 18/11/2024 | 9:30 | 18/11/2024 | 13:45 | MTN32 | MORNINGTON | Rural Short | Planned |  | 2 | 510 | 255 | 1 | No
| 152802 | 2024-11-12 | 9:23 | 2024-11-12 | 13:15 | STO13 | SORRENTO | Urban | Planned |  | 30 | 6960 | 232 | 1 | No
| 152805 | 14/01/2025 | 8:01 | 14/01/2025 | 14:45 | WD36 | WEST DONCASTER | Urban | Planned |  | 11 | 4447.3 | 404.3 | 1 | No
| 152806 | 17/12/2024 | 8:35 | 17/12/2024 | 11:24 | MR13 | MOORABBIN | Urban | Planned |  | 19 | 3211 | 169 | 1 | No
| 152806 | 17/12/2024 | 8:35 | 17/12/2024 | 11:24 | MR21 | MOORABBIN | Urban | Planned |  | 16 | 2704 | 169 | 1 | No
| 152807 | 18/12/2024 | 8:30 | 18/12/2024 | 15:30 | MR11 | MOORABBIN | Urban | Planned |  | 88 | 36960 | 420 | 1 | No
| 152811 | 14/12/2024 | 23:49 | 15/12/2024 | 2:10 | STO23 | SORRENTO | Urban | Planned |  | 14 | 1974 | 141 | 1 | No
| 152814 | 2024-11-12 | 8:04 | 2024-11-12 | 9:55 | SVW45 | SPRINGVALE WEST | Urban | Planned |  | 45 | 4995 | 111 | 1 | No
| 152815 | 17/12/2024 | 8:20 | 17/12/2024 | 13:40 | M31 | MENTONE | Urban | Planned |  | 9 | 2880 | 320 | 1 | No
| 152816 | 19/12/2024 | 8:00 | 19/12/2024 | 16:00 | RBD23 | ROSEBUD | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 152816 | 19/12/2024 | 8:27 | 19/12/2024 | 14:35 | RBD23 | ROSEBUD | Urban | Planned |  | 194 | 71392 | 368 | 1 | No
| 152828 | 2024-12-12 | 7:30 | 2024-12-12 | 10:30 | STO21 | SORRENTO | Rural Short | Planned |  | 1 | 180 | 180 | 1 | No
| 152828 | 2024-12-12 | 7:49 | 2024-12-12 | 8:00 | STO21 | SORRENTO | Rural Short | Planned |  | 8 | 88 | 11 | 1 | No
| 152829 | 18/12/2024 | 10:20 | 18/12/2024 | 10:40 | DSH32 | DANDENONG SOUTH | Urban | Planned |  | 2 | 40 | 20 | 1 | No
| 152836 | 20/12/2024 | 8:00 | 20/12/2024 | 11:43 | DN11 | DANDENONG | Urban | Planned |  | 151 | 33673 | 223 | 2 | No
| 152836 | 20/12/2024 | 8:00 | 20/12/2024 | 16:00 | DN11 | DANDENONG | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 152842 | 2024-12-12 | 23:09 | 13/12/2024 | 2:47 | RBD13 | ROSEBUD | Urban | Planned |  | 5 | 1090 | 218 | 1 | No
| 152843 | 29/01/2025 | 8:15 | 29/01/2025 | 14:20 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 15 | 5475 | 365 | 1 | No
| 152852 | 2024-12-12 | 10:19 | 2024-12-12 | 11:26 | DMA12 | DROMANA | Urban | Planned |  | 54 | 3618 | 67 | 1 | No
| 152854 | 19/12/2024 | 8:03 | 19/12/2024 | 13:44 | HGS31 | HASTINGS | Rural Short | Planned |  | 81 | 27621 | 341 | 1 | No
| 152857 | 18/12/2024 | 8:32 | 18/12/2024 | 16:30 | EB13 | EAST BURWOOD | Urban | Planned |  | 33 | 15774.5511 | 478.0167 | 1 | No
| 152858 | 13/12/2024 | 8:00 | 13/12/2024 | 16:30 | OAK35 | OAKLEIGH | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 152858 | 13/12/2024 | 8:50 | 13/12/2024 | 12:25 | OAK35 | OAKLEIGH | Urban | Planned |  | 33 | 7095 | 215 | 1 | No
| 152868 | 19/02/2025 | 8:00 | 19/02/2025 | 12:40 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 15 | 4200 | 280 | 1 | No
| 152870 | 15/01/2025 | 8:01 | 15/01/2025 | 16:01 | OR34 | ORMOND | Urban | Planned |  | 2 | 960 | 480 | 1 | No
| 152870 | 15/01/2025 | 8:03 | 15/01/2025 | 13:10 | OR34 | ORMOND | Urban | Planned |  | 89 | 27323 | 307 | 1 | No
| 152874 | 19/12/2024 | 8:30 | 19/12/2024 | 12:25 | MR14 | MOORABBIN | Urban | Planned |  | 59 | 13865 | 235 | 1 | No
| 152874 | 19/12/2024 | 8:30 | 19/12/2024 | 12:25 | MR22 | MOORABBIN | Urban | Planned |  | 24 | 5640 | 235 | 1 | No
| 152875 | 15/12/2024 | 8:00 | 15/12/2024 | 14:50 | CRM24 | CARRUM | Urban | Planned |  | 16 | 6560 | 410 | 1 | No
| 152878 | 16/01/2025 | 8:00 | 16/01/2025 | 13:00 | HGS31 | HASTINGS | Rural Short | Planned |  | 143 | 42900 | 300 | 1 | No
| 152879 | 19/12/2024 | 8:35 | 19/12/2024 | 12:25 | DC2 | DONCASTER | Urban | Planned |  | 60 | 13800 | 230 | 1 | No
| 152886 | 19/12/2024 | 8:30 | 19/12/2024 | 12:25 | MR11 | MOORABBIN | Urban | Planned |  | 60 | 14100 | 235 | 1 | No
| 152886 | 19/12/2024 | 8:30 | 19/12/2024 | 12:25 | MR24 | MOORABBIN | Urban | Planned |  | 37 | 8695 | 235 | 1 | No
| 152890 | 18/12/2024 | 8:15 | 18/12/2024 | 16:30 | BW35 | BURWOOD | Urban | Planned |  | 66 | 32691.9978 | 495.3333 | 1 | No
| 152891 | 15/01/2025 | 8:00 | 15/01/2025 | 12:15 | HGS22 | HASTINGS | Rural Short | Planned |  | 20 | 5100 | 255 | 1 | No
| 152894 | 30/12/2024 | 7:05 | 30/12/2024 | 16:01 | DVY13 | DANDENONG VALLEY | Urban | Planned |  | 1 | 535.6667 | 535.6667 | 1 | No
| 152895 | 17/12/2024 | 8:00 | 17/12/2024 | 16:00 | OAK23 | OAKLEIGH | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 152896 | 2025-02-01 | 7:01 | 2025-02-01 | 16:01 | DSH21 | DANDENONG SOUTH | Urban | Planned |  | 2 | 1080 | 540 | 1 | No
| 152900 | 2025-08-01 | 8:25 | 2025-08-01 | 11:38 | BT13 | BENTLEIGH | Urban | Planned |  | 129 | 24897 | 193 | 1 | No
| 152901 | 18/12/2024 | 8:20 | 18/12/2024 | 10:20 | RBD21 | ROSEBUD | Rural Short | Planned |  | 2 | 240 | 120 | 1 | No
| 152908 | 18/12/2024 | 8:00 | 18/12/2024 | 16:30 | MTN32 | MORNINGTON | Rural Short | Planned |  | 10 | 5100 | 510 | 1 | No
| 152910 | 17/12/2024 | 8:27 | 17/12/2024 | 13:38 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 205 | 63755 | 311 | 1 | No
| 152911 | 19/12/2024 | 11:10 | 19/12/2024 | 12:55 | BU12 | BULLEEN | Urban | Planned |  | 26 | 2730 | 105 | 1 | No
| 152913 | 27/02/2025 | 8:00 | 27/02/2025 | 14:08 | BT21 | BENTLEIGH | Urban | Planned |  | 5 | 1840 | 368 | 1 | No
| 152913 | 27/02/2025 | 8:00 | 27/02/2025 | 14:08 | MR31 | MOORABBIN | Urban | Planned |  | 84 | 30912 | 368 | 1 | No
| 152919 | 17/12/2024 | 8:10 | 17/12/2024 | 14:35 | SVW55 | SPRINGVALE WEST | Urban | Planned |  | 18 | 6930 | 385 | 1 | No
| 152921 | 18/12/2024 | 11:00 | 18/12/2024 | 16:00 | MTN23 | MORNINGTON | Urban | Planned |  | 27 | 8100 | 300 | 1 | No
| 152927 | 17/12/2024 | 8:00 | 17/12/2024 | 15:30 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 3 | 1350 | 450 | 1 | No
| 152928 | 19/12/2024 | 8:00 | 19/12/2024 | 15:00 | SV34 | SPRINGVALE | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 152928 | 19/12/2024 | 8:18 | 19/12/2024 | 13:00 | SV34 | SPRINGVALE | Urban | Planned |  | 97 | 27354 | 282 | 1 | No
| 152928 | 19/12/2024 | 8:18 | 19/12/2024 | 13:00 | SVW54 | SPRINGVALE WEST | Urban | Planned |  | 42 | 11844 | 282 | 1 | No
| 152943 | 18/12/2024 | 8:00 | 18/12/2024 | 16:00 | K32 | GARDINER | Urban | Planned |  | 68 | 32640 | 480 | 1 | No
| 152953 | 21/01/2025 | 8:14 | 21/01/2025 | 13:35 | HGS22 | HASTINGS | Rural Short | Planned |  | 256 | 82176 | 321 | 1 | No
| 152954 | 16/12/2024 | 4:30 | 16/12/2024 | 6:00 | DN8 | DANDENONG | Urban | Planned |  | 14 | 1260 | 90 | 1 | No
| 152955 | 18/12/2024 | 9:00 | 18/12/2024 | 14:00 | DC5 | DONCASTER | Urban | Planned |  | 60 | 18000 | 300 | 1 | No
| 152956 | 2024-11-12 | 8:30 | 2024-11-12 | 13:47 | GW5 | GLEN WAVERLEY | Urban | Planned |  | 171 | 54207 | 317 | 1 | No
| 152957 | 18/12/2024 | 8:00 | 18/12/2024 | 16:00 | BT12 | BENTLEIGH | Urban | Planned |  | 141 | 67680 | 480 | 1 | No
| 152960 | 2025-07-01 | 8:30 | 2025-07-01 | 12:45 | DMA13 | DROMANA | Rural Short | Planned |  | 76 | 19380 | 255 | 1 | No
| 152961 | 22/12/2024 | 7:10 | 22/12/2024 | 14:18 | GW6 | GLEN WAVERLEY | Urban | Planned |  | 2 | 856 | 428 | 1 | No
| 152962 | 2024-12-12 | 8:05 | 2024-12-12 | 14:40 | EM3 | EAST MALVERN | Urban | Planned |  | 61 | 24095 | 395 | 1 | No
| 152964 | 17/12/2024 | 8:00 | 17/12/2024 | 16:30 | EM7 | EAST MALVERN | Urban | Planned |  | 90 | 45900 | 510 | 1 | No
| 152968 | 19/12/2024 | 8:32 | 19/12/2024 | 10:43 | DC1 | DONCASTER | Urban | Planned |  | 18 | 2358 | 131 | 1 | No
| 152973 | 2025-07-01 | 8:00 | 2025-07-01 | 12:12 | STO22 | SORRENTO | Urban | Planned |  | 52 | 13104 | 252 | 1 | No
| 152974 | 2025-08-01 | 8:17 | 2025-08-01 | 11:35 | OE9 | OAKLEIGH EAST | Urban | Planned |  | 25 | 4950 | 198 | 1 | No
| 152975 | 2025-08-01 | 12:34 | 2025-08-01 | 14:56 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 76 | 10792 | 142 | 1 | No
| 152977 | 2025-09-01 | 8:10 | 2025-09-01 | 12:51 | STO23 | SORRENTO | Urban | Planned |  | 143 | 40183 | 281 | 1 | No
| 152978 | 2025-10-01 | 8:00 | 2025-10-01 | 11:00 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 45 | 8100 | 180 | 1 | No
| 152983 | 30/01/2025 | 9:10 | 30/01/2025 | 12:45 | EB23 | EAST BURWOOD | Urban | Planned |  | 20 | 4300 | 215 | 1 | No
| 152986 | 17/12/2024 | 8:15 | 17/12/2024 | 12:50 | RBD21 | ROSEBUD | Rural Short | Planned |  | 2 | 550 | 275 | 1 | No
| 152987 | 17/12/2024 | 8:00 | 17/12/2024 | 16:00 | CRM14 | CARRUM | Rural Short | Planned |  | 10 | 4800 | 480 | 1 | No
| 152992 | 13/01/2025 | 8:20 | 13/01/2025 | 14:04 | BU21 | BULLEEN | Urban | Planned |  | 59 | 20296 | 344 | 1 | No
| 152993 | 14/01/2025 | 8:00 | 14/01/2025 | 10:07 | DC8 | DONCASTER | Urban | Planned |  | 150 | 19050 | 127 | 1 | No
| 152994 | 14/01/2025 | 10:33 | 14/01/2025 | 11:52 | DC6 | DONCASTER | Urban | Planned |  | 8 | 632 | 79 | 1 | No
| 152995 | 21/01/2025 | 8:00 | 21/01/2025 | 9:58 | DC12 | DONCASTER | Urban | Planned |  | 44 | 5192 | 118 | 1 | No
| 152996 | 21/01/2025 | 9:40 | 21/01/2025 | 11:50 | RBD24 | ROSEBUD | Urban | Planned |  | 89 | 11570 | 130 | 1 | No
| 152997 | 19/12/2024 | 7:30 | 19/12/2024 | 16:30 | NO31 | NOTTING HILL | Urban | Planned |  | 3 | 1620 | 540 | 1 | No
| 152998 | 22/01/2025 | 10:19 | 22/01/2025 | 11:32 | DC8 | DONCASTER | Urban | Planned |  | 66 | 4818 | 73 | 1 | No
| 152999 | 31/01/2025 | 8:05 | 31/01/2025 | 10:33 | STO23 | SORRENTO | Urban | Planned |  | 51 | 7548 | 148 | 1 | No
| 153000 | 31/01/2025 | 11:10 | 31/01/2025 | 12:40 | STO21 | SORRENTO | Rural Short | Planned |  | 27 | 2430 | 90 | 1 | No
| 153003 | 2024-12-12 | 8:00 | 2024-12-12 | 12:02 | OR32 | ORMOND | Urban | Planned |  | 59 | 14278 | 242 | 1 | No
| 153006 | 19/01/2025 | 6:56 | 19/01/2025 | 15:22 | RD2 | RIVERSDALE | Urban | Planned |  | 11 | 5566 | 506 | 1 | No
| 153007 | 22/01/2025 | 8:01 | 22/01/2025 | 16:08 | SR26 | SANDRINGHAM | Urban | Planned |  | 105 | 51168.2535 | 487.3167 | 1 | No
| 153008 | 16/01/2025 | 8:00 | 16/01/2025 | 9:32 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 25 | 2300 | 92 | 1 | No
| 153009 | 22/01/2025 | 8:31 | 22/01/2025 | 11:17 | DC5 | DONCASTER | Urban | Planned |  | 35 | 5810 | 166 | 1 | No
| 153011 | 24/01/2025 | 8:30 | 24/01/2025 | 10:20 | STO23 | SORRENTO | Urban | Planned |  | 19 | 2090 | 110 | 1 | No
| 153012 | 24/01/2025 | 8:14 | 24/01/2025 | 11:15 | DMA14 | DROMANA | Urban | Planned |  | 33 | 5973 | 181 | 1 | No
| 153013 | 24/01/2025 | 11:00 | 24/01/2025 | 11:55 | STO23 | SORRENTO | Urban | Planned |  | 5 | 275 | 55 | 1 | No
| 153014 | 2025-09-01 | 8:16 | 2025-09-01 | 11:56 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 30 | 6600 | 220 | 1 | No
| 153022 | 19/12/2024 | 4:01 | 19/12/2024 | 5:31 | KBH35 | KEYSBOROUGH | Urban | Planned |  | 8 | 720 | 90 | 1 | No
| 153024 | 19/01/2025 | 8:46 | 19/01/2025 | 14:21 | DC8 | DONCASTER | Urban | Planned |  | 1 | 335 | 335 | 1 | No
| 153029 | 15/01/2025 | 9:27 | 15/01/2025 | 10:20 | MR12 | MOORABBIN | Urban | Planned |  | 2 | 106 | 53 | 1 | No
| 153032 | 15/01/2025 | 12:30 | 15/01/2025 | 13:57 | MR12 | MOORABBIN | Urban | Planned |  | 22 | 1914 | 87 | 1 | No
| 153034 | 15/01/2025 | 9:40 | 15/01/2025 | 11:52 | MR12 | MOORABBIN | Urban | Planned |  | 79 | 10428 | 132 | 1 | No
| 153038 | 15/01/2025 | 8:00 | 15/01/2025 | 16:20 | EM7 | EAST MALVERN | Urban | Planned |  | 134 | 67000 | 500 | 1 | No
| 153042 | 14/01/2025 | 9:53 | 14/01/2025 | 11:37 | LD2 | LYNDALE | Urban | Planned |  | 30 | 3120 | 104 | 1 | No
| 153052 | 2025-12-01 | 6:55 | 2025-12-01 | 12:50 | SVW53 | SPRINGVALE WEST | Urban | Planned |  | 17 | 6035 | 355 | 1 | No
| 153055 | 20/12/2024 | 5:30 | 20/12/2024 | 6:00 | OR24 | ORMOND | Urban | Planned |  | 1 | 29.85 | 29.85 | 1 | No
| 153056 | 19/12/2024 | 8:00 | 19/12/2024 | 11:47 | MTN32 | MORNINGTON | Rural Short | Planned |  | 38 | 8626 | 227 | 2 | No
| 153056 | 19/12/2024 | 8:00 | 19/12/2024 | 15:00 | MTN32 | MORNINGTON | Rural Short | Planned |  | 1 | 420 | 420 | 1 | No
| 153059 | 15/01/2025 | 11:55 | 15/01/2025 | 13:05 | MTN32 | MORNINGTON | Rural Short | Planned |  | 13 | 910 | 70 | 1 | No
| 153063 | 18/12/2024 | 8:00 | 18/12/2024 | 16:00 | DC4 | DONCASTER | Urban | Planned |  | 38 | 18240 | 480 | 1 | No
| 153065 | 14/01/2025 | 8:30 | 14/01/2025 | 15:30 | BH12 | BOX HILL | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 153065 | 14/01/2025 | 8:54 | 14/01/2025 | 14:14 | BH12 | BOX HILL | Urban | Planned |  | 36 | 11520 | 320 | 1 | No
| 153071 | 22/01/2025 | 8:00 | 22/01/2025 | 16:00 | CM22 | CHELTENHAM | Urban | Planned |  | 2 | 960 | 480 | 1 | No
| 153071 | 22/01/2025 | 8:10 | 22/01/2025 | 14:45 | CM22 | CHELTENHAM | Urban | Planned |  | 182 | 71890 | 395 | 1 | No
| 153081 | 2025-03-01 | 9:00 | 2025-03-01 | 10:40 | BU15 | BULLEEN | Urban | Planned |  | 26 | 2600 | 100 | 1 | No
| 153084 | 2025-09-02 | 7:45 | 2025-09-02 | 13:30 | OR25 | ORMOND | Urban | Planned |  | 43 | 14835 | 345 | 1 | No
| 153094 | 2025-12-01 | 8:08 | 2025-12-01 | 16:15 | EM3 | EAST MALVERN | Urban | Planned |  | 32 | 15584 | 487 | 1 | No
| 153095 | 2025-07-01 | 9:15 | 2025-07-01 | 11:20 | OAK35 | OAKLEIGH | Urban | Planned |  | 34 | 4250 | 125 | 1 | No
| 153096 | 14/01/2025 | 10:05 | 14/01/2025 | 12:05 | EM11 | EAST MALVERN | Urban | Planned |  | 5 | 600 | 120 | 1 | No
| 153102 | 17/01/2025 | 8:51 | 17/01/2025 | 12:40 | HGS33 | HASTINGS | Rural Short | Planned |  | 41 | 9389 | 229 | 1 | No
| 153110 | 2025-09-01 | 8:00 | 2025-09-01 | 16:00 | BU11 | BULLEEN | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 153110 | 2025-09-01 | 8:43 | 2025-09-01 | 12:55 | BU11 | BULLEEN | Urban | Planned |  | 28 | 7056 | 252 | 1 | No
| 153115 | 27/02/2025 | 8:01 | 27/02/2025 | 11:30 | FTN13 | FRANKSTON | Urban | Planned |  | 40 | 8374 | 209.35 | 1 | No
| 153117 | 2025-08-01 | 8:01 | 2025-08-01 | 11:38 | RBD23 | ROSEBUD | Urban | Planned |  | 4 | 869.9332 | 217.4833 | 1 | No
| 153118 | 26/02/2025 | 8:00 | 26/02/2025 | 15:30 | SV34 | SPRINGVALE | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 153118 | 26/02/2025 | 8:12 | 26/02/2025 | 12:32 | SV34 | SPRINGVALE | Urban | Planned |  | 26 | 6760 | 260 | 1 | No
| 153120 | 2025-07-01 | 8:30 | 2025-07-01 | 14:10 | MR21 | MOORABBIN | Urban | Planned |  | 93 | 31620 | 340 | 1 | No
| 153121 | 16/01/2025 | 10:25 | 16/01/2025 | 11:00 | DN25 | DANDENONG | Urban | Planned |  | 3 | 105 | 35 | 1 | No
| 153125 | 20/01/2025 | 8:39 | 20/01/2025 | 13:36 | GW7 | GLEN WAVERLEY | Urban | Planned |  | 6 | 1782 | 297 | 1 | No
| 153126 | 21/01/2025 | 8:38 | 21/01/2025 | 13:34 | DN10 | DANDENONG | Urban | Planned |  | 22 | 6512 | 296 | 1 | No
| 153128 | 22/01/2025 | 8:35 | 22/01/2025 | 11:50 | NP14 | NOBLE PARK | Urban | Planned |  | 27 | 5265 | 195 | 1 | No
| 153136 | 30/01/2025 | 8:35 | 30/01/2025 | 11:10 | HGS33 | HASTINGS | Rural Short | Planned |  | 11 | 1705 | 155 | 1 | No
| 153146 | 24/01/2025 | 8:15 | 24/01/2025 | 15:05 | NW13 | NUNAWADING | Urban | Planned |  | 72 | 29520 | 410 | 1 | No
| 153147 | 19/01/2025 | 7:20 | 19/01/2025 | 18:10 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 11 | 7150 | 650 | 1 | No
| 153148 | 14/02/2025 | 8:15 | 14/02/2025 | 13:45 | SR21 | SANDRINGHAM | Urban | Planned |  | 71 | 23430 | 330 | 1 | No
| 153151 | 2025-09-01 | 8:29 | 2025-09-01 | 10:40 | DMA14 | DROMANA | Urban | Planned |  | 36 | 4716 | 131 | 1 | No
| 153152 | 2025-09-01 | 12:15 | 2025-09-01 | 14:01 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 55 | 5830 | 106 | 1 | No
| 153161 | 17/01/2025 | 8:01 | 17/01/2025 | 10:21 | GW10 | GLEN WAVERLEY | Urban | Planned |  | 68 | 9550.6 | 140.45 | 1 | No
| 153165 | 2025-06-01 | 8:00 | 2025-06-01 | 13:00 | HT4 | HEATHERTON | Urban | Planned |  | 1 | 300 | 300 | 1 | No
| 153165 | 2025-06-01 | 8:30 | 2025-06-01 | 10:35 | HT4 | HEATHERTON | Urban | Planned |  | 65 | 8125 | 125 | 1 | No
| 153166 | 2025-09-01 | 9:16 | 2025-09-01 | 12:25 | CDA21 | CLARINDA | Urban | Planned |  | 18 | 3402 | 189 | 1 | No
| 153166 | 2025-09-01 | 9:16 | 2025-09-01 | 12:25 | HT4 | HEATHERTON | Urban | Planned |  | 61 | 11529 | 189 | 1 | No
| 153173 | 22/01/2025 | 8:50 | 22/01/2025 | 12:50 | DN22 | DANDENONG | Urban | Planned |  | 43 | 10320 | 240 | 1 | No
| 153174 | 19/01/2025 | 9:30 | 19/01/2025 | 12:30 | CRM15 | CARRUM | Urban | Planned |  | 1 | 180 | 180 | 1 | No
| 153184 | 30/01/2025 | 12:00 | 30/01/2025 | 14:05 | DMA13 | DROMANA | Rural Short | Planned |  | 46 | 5750 | 125 | 1 | No
| 153188 | 22/01/2025 | 8:01 | 22/01/2025 | 13:52 | BR1 | BEAUMARIS | Urban | Planned |  | 34 | 11934 | 351 | 1 | No
| 153190 | 28/01/2025 | 8:15 | 28/01/2025 | 13:00 | SR34 | SANDRINGHAM | Urban | Planned |  | 6 | 1710 | 285 | 1 | No
| 153199 | 17/01/2025 | 8:24 | 17/01/2025 | 13:42 | K31 | GARDINER | Urban | Planned |  | 38 | 12084 | 318 | 1 | No
| 153201 | 17/01/2025 | 10:00 | 17/01/2025 | 10:52 | BH33 | BOX HILL | Urban | Planned |  | 13 | 676 | 52 | 1 | No
| 153202 | 17/01/2025 | 12:20 | 17/01/2025 | 13:40 | NW21 | NUNAWADING | Urban | Planned |  | 16 | 1280 | 80 | 1 | No
| 153205 | 14/01/2025 | 9:00 | 14/01/2025 | 17:00 | BU14 | BULLEEN | Urban | Planned |  | 7 | 3360 | 480 | 1 | No
| 153214 | 2025-08-01 | 12:35 | 2025-08-01 | 13:23 | MTN22 | MORNINGTON | Rural Short | Planned |  | 1 | 48 | 48 | 1 | No
| 153215 | 30/01/2025 | 8:08 | 30/01/2025 | 14:50 | MR13 | MOORABBIN | Urban | Planned |  | 6 | 2412 | 402 | 1 | No
| 153219 | 23/01/2025 | 8:15 | 23/01/2025 | 12:20 | RBD13 | ROSEBUD | Urban | Planned |  | 121 | 29645 | 245 | 1 | No
| 153222 | 2025-12-01 | 7:45 | 2025-12-01 | 18:15 | HT2 | HEATHERTON | Urban | Planned |  | 12 | 7560 | 630 | 1 | No
| 153224 | 2025-07-01 | 8:30 | 2025-07-01 | 11:34 | K35 | GARDINER | Urban | Planned |  | 64 | 11776 | 184 | 1 | No
| 153227 | 2025-07-01 | 8:04 | 2025-07-01 | 16:05 | HGS31 | HASTINGS | Rural Short | Planned |  | 1 | 481 | 481 | 1 | No
| 153228 | 2025-09-02 | 8:05 | 2025-09-02 | 13:50 | HT6 | HEATHERTON | Urban | Planned |  | 1 | 345 | 345 | 1 | No
| 153228 | 2025-09-02 | 8:05 | 2025-09-02 | 13:50 | HT7 | HEATHERTON | Urban | Planned |  | 80 | 27600 | 345 | 1 | No
| 153229 | 2025-12-01 | 8:28 | 2025-12-01 | 15:52 | MR31 | MOORABBIN | Urban | Planned |  | 90 | 39960 | 444 | 1 | No
| 153235 | 2025-08-01 | 9:00 | 2025-08-01 | 11:07 | MTN32 | MORNINGTON | Rural Short | Planned |  | 4 | 508 | 127 | 1 | No
| 153243 | 2025-07-02 | 8:00 | 2025-07-02 | 16:34 | HGS31 | HASTINGS | Rural Short | Planned |  | 83 | 42662 | 514 | 1 | No
| 153244 | 2025-08-01 | 12:33 | 2025-08-01 | 13:26 | DMA23 | DROMANA | Rural Short | Planned |  | 30 | 1590 | 53 | 1 | No
| 153246 | 2025-10-01 | 9:10 | 2025-10-01 | 10:20 | DMA13 | DROMANA | Rural Short | Planned |  | 1 | 70 | 70 | 1 | No
| 153262 | 2024-12-12 | 8:48 | 2024-12-12 | 11:45 | DN22 | DANDENONG | Urban | Planned |  | 19 | 3363 | 177 | 1 | No
| 153267 | 16/01/2025 | 8:08 | 16/01/2025 | 16:33 | DMA15 | DROMANA | Rural Short | Planned |  | 263 | 132815 | 505 | 1 | No
| 153272 | 14/01/2025 | 8:00 | 14/01/2025 | 11:45 | MGE21 | MULGRAVE | Urban | Planned |  | 15 | 3375 | 225 | 1 | No
| 153273 | 14/01/2025 | 12:45 | 14/01/2025 | 14:15 | MGE21 | MULGRAVE | Urban | Planned |  | 90 | 8100 | 90 | 1 | No
| 153275 | 2025-07-01 | 6:02 | 2025-07-01 | 6:12 | KBH35 | KEYSBOROUGH | Urban | Planned |  | 3 | 30 | 10 | 1 | No
| 153276 | 23/01/2025 | 8:40 | 23/01/2025 | 9:23 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 23 | 989 | 43 | 1 | No
| 153277 | 2025-07-02 | 8:15 | 2025-07-02 | 12:11 | DN10 | DANDENONG | Urban | Planned |  | 55 | 12980 | 236 | 1 | No
| 153280 | 23/01/2025 | 8:11 | 23/01/2025 | 14:30 | NB33 | NORTH BRIGHTON | Urban | Planned |  | 2 | 758 | 379 | 1 | No
| 153282 | 17/01/2025 | 8:00 | 17/01/2025 | 11:48 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 62 | 14136 | 228 | 1 | No
| 153286 | 14/01/2025 | 8:00 | 14/01/2025 | 15:00 | SR34 | SANDRINGHAM | Urban | Planned |  | 2 | 840 | 420 | 1 | No
| 153286 | 14/01/2025 | 8:46 | 14/01/2025 | 14:17 | SR34 | SANDRINGHAM | Urban | Planned |  | 113 | 37403 | 331 | 1 | No
| 153287 | 18/02/2025 | 8:00 | 18/02/2025 | 14:00 | DMA15 | DROMANA | Rural Short | Planned |  | 114 | 41003.8962 | 359.6833 | 1 | No
| 153288 | 28/01/2025 | 8:50 | 28/01/2025 | 15:24 | CDA24 | CLARINDA | Urban | Planned |  | 36 | 14184 | 394 | 1 | No
| 153295 | 15/01/2025 | 8:30 | 15/01/2025 | 10:48 | HGS23 | HASTINGS | Rural Short | Planned |  | 9 | 1242 | 138 | 1 | No
| 153298 | 2025-08-01 | 10:50 | 2025-08-01 | 11:45 | MTN32 | MORNINGTON | Rural Short | Planned |  | 3 | 165 | 55 | 1 | No
| 153303 | 21/01/2025 | 8:08 | 21/01/2025 | 12:25 | HGS23 | HASTINGS | Rural Short | Planned |  | 414 | 106398 | 257 | 1 | No
| 153304 | 30/01/2025 | 9:20 | 30/01/2025 | 11:45 | BC23 | BALACLAVA | Urban | Planned |  | 16 | 2320 | 145 | 1 | No
| 153306 | 2025-09-02 | 6:40 | 2025-09-02 | 11:10 | OE15 | OAKLEIGH EAST | Urban | Planned |  | 10 | 2700 | 270 | 1 | No
| 153307 | 19/01/2025 | 7:44 | 19/01/2025 | 12:32 | HT3 | HEATHERTON | Urban | Planned |  | 48 | 13824 | 288 | 1 | No
| 153310 | 2025-12-02 | 8:16 | 2025-12-02 | 14:55 | KBH31 | KEYSBOROUGH | Urban | Planned |  | 2 | 798 | 399 | 1 | No
| 153313 | 24/01/2025 | 8:03 | 24/01/2025 | 12:45 | LWN33 | LANGWARRIN | Urban | Planned |  | 104 | 29328 | 282 | 1 | No
| 153318 | 20/01/2025 | 8:03 | 20/01/2025 | 13:03 | HGS22 | HASTINGS | Rural Short | Planned |  | 558 | 167400 | 300 | 1 | No
| 153321 | 2025-12-01 | 7:35 | 2025-12-01 | 13:28 | MC14 | MORDIALLOC | Urban | Planned |  | 1 | 353 | 353 | 1 | No
| 153328 | 30/01/2025 | 8:00 | 30/01/2025 | 12:30 | NW13 | NUNAWADING | Urban | Planned |  | 1 | 270 | 270 | 1 | No
| 153328 | 30/01/2025 | 8:45 | 30/01/2025 | 11:00 | NW13 | NUNAWADING | Urban | Planned |  | 46 | 6210 | 135 | 1 | No
| 153330 | 19/01/2025 | 6:30 | 19/01/2025 | 10:30 | NW11 | NUNAWADING | Urban | Planned |  | 73 | 17520 | 240 | 1 | No
| 153330 | 19/01/2025 | 6:30 | 19/01/2025 | 10:30 | NW31 | NUNAWADING | Urban | Planned |  | 19 | 4560 | 240 | 1 | No
| 153333 | 19/01/2025 | 12:00 | 19/01/2025 | 13:30 | DC2 | DONCASTER | Urban | Planned |  | 6 | 540 | 90 | 1 | No
| 153334 | 13/01/2025 | 21:00 | 14/01/2025 | 1:48 | SR23 | SANDRINGHAM | Urban | Planned |  | 42 | 12096 | 288 | 1 | No
| 153335 | 19/01/2025 | 6:45 | 19/01/2025 | 8:56 | NO32 | NOTTING HILL | Urban | Planned |  | 2 | 262 | 131 | 1 | No
| 153336 | 22/01/2025 | 8:00 | 22/01/2025 | 12:20 | RBD23 | ROSEBUD | Urban | Planned |  | 116 | 30160 | 260 | 1 | No
| 153337 | 19/01/2025 | 10:37 | 19/01/2025 | 12:41 | HGS31 | HASTINGS | Rural Short | Planned |  | 36 | 4464 | 124 | 1 | No
| 153339 | 2025-08-01 | 8:00 | 2025-08-01 | 16:00 | RWT34 | RINGWOOD | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 153339 | 2025-08-01 | 8:07 | 2025-08-01 | 13:00 | RWT34 | RINGWOOD | Urban | Planned |  | 73 | 21389 | 293 | 1 | No
| 153352 | 14/01/2025 | 8:00 | 14/01/2025 | 12:15 | NW31 | NUNAWADING | Urban | Planned |  | 108 | 27540 | 255 | 2 | No
| 153352 | 14/01/2025 | 8:00 | 14/01/2025 | 13:00 | NW31 | NUNAWADING | Urban | Planned |  | 1 | 300 | 300 | 1 | No
| 153353 | 14/01/2025 | 11:01 | 14/01/2025 | 16:01 | NW31 | NUNAWADING | Urban | Planned |  | 1 | 300 | 300 | 1 | No
| 153353 | 14/01/2025 | 12:30 | 14/01/2025 | 14:40 | NW31 | NUNAWADING | Urban | Planned |  | 64 | 8320 | 130 | 1 | No
| 153358 | 18/01/2025 | 8:01 | 19/01/2025 | 2:07 | EB33 | EAST BURWOOD | Urban | Planned |  | 18 | 19548 | 1086 | 1 | No
| 153360 | 16/01/2025 | 8:00 | 16/01/2025 | 9:02 | HGS22 | HASTINGS | Rural Short | Planned |  | 3 | 186 | 62 | 1 | No
| 153361 | 16/01/2025 | 8:30 | 16/01/2025 | 10:40 | NW22 | NUNAWADING | Urban | Planned |  | 48 | 6240 | 130 | 1 | No
| 153362 | 16/01/2025 | 8:33 | 16/01/2025 | 9:23 | HGS22 | HASTINGS | Rural Short | Planned |  | 20 | 1000 | 50 | 1 | No
| 153363 | 16/01/2025 | 10:54 | 16/01/2025 | 11:29 | HGS33 | HASTINGS | Rural Short | Planned |  | 3 | 105 | 35 | 1 | No
| 153364 | 15/01/2025 | 8:50 | 15/01/2025 | 12:30 | MR15 | MOORABBIN | Urban | Planned |  | 112 | 24640 | 220 | 1 | No
| 153368 | 16/01/2025 | 11:30 | 16/01/2025 | 12:45 | NO7 | NOTTING HILL | Urban | Planned |  | 40 | 3000 | 75 | 1 | No
| 153369 | 16/01/2025 | 10:30 | 16/01/2025 | 12:17 | HGS33 | HASTINGS | Rural Short | Planned |  | 40 | 4280 | 107 | 1 | No
| 153370 | 14/01/2025 | 8:01 | 14/01/2025 | 15:39 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 35 | 16041.6655 | 458.3333 | 1 | No
| 153371 | 16/01/2025 | 12:42 | 16/01/2025 | 13:56 | HGS22 | HASTINGS | Rural Short | Planned |  | 6 | 444 | 74 | 1 | No
| 153374 | 2025-03-01 | 3:32 | 2025-03-01 | 4:40 | CFD23 | CAULFIELD | Urban | Planned |  | 60 | 4080 | 68 | 1 | No
| 153375 | 23/01/2025 | 8:14 | 23/01/2025 | 11:03 | NW31 | NUNAWADING | Urban | Planned |  | 66 | 11154 | 169 | 1 | No
| 153378 | 2025-09-01 | 8:05 | 2025-09-01 | 10:46 | OR24 | ORMOND | Urban | Planned |  | 28 | 4508 | 161 | 1 | No
| 153380 | 24/01/2025 | 10:30 | 24/01/2025 | 12:30 | MTN35 | MORNINGTON | Rural Short | Planned |  | 78 | 9360 | 120 | 1 | No
| 153381 | 31/01/2025 | 8:00 | 31/01/2025 | 13:20 | MR33 | MOORABBIN | Urban | Planned |  | 64 | 20480 | 320 | 1 | No
| 153384 | 2025-05-02 | 8:00 | 2025-05-02 | 16:00 | BU24 | BULLEEN | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 153385 | 2025-08-01 | 8:39 | 2025-08-01 | 13:35 | MR32 | MOORABBIN | Urban | Planned |  | 64 | 18944 | 296 | 1 | No
| 153390 | 2025-04-02 | 9:15 | 2025-04-02 | 13:15 | BU11 | BULLEEN | Urban | Planned |  | 75 | 18000 | 240 | 1 | No
| 153393 | 2025-05-03 | 8:00 | 2025-05-03 | 14:25 | MR33 | MOORABBIN | Urban | Planned |  | 64 | 24613.3312 | 384.5833 | 1 | No
| 153394 | 15/01/2025 | 8:00 | 15/01/2025 | 15:30 | EM3 | EAST MALVERN | Urban | Planned |  | 55 | 24750 | 450 | 1 | No
| 153395 | 13/12/2024 | 8:30 | 13/12/2024 | 14:30 | RBD21 | ROSEBUD | Rural Short | Planned |  | 1 | 360 | 360 | 1 | No
| 153397 | 15/01/2025 | 7:30 | 15/01/2025 | 16:30 | SVW43 | SPRINGVALE WEST | Urban | Planned |  | 1 | 540 | 540 | 1 | No
| 153399 | 17/01/2025 | 8:27 | 17/01/2025 | 14:20 | HGS22 | HASTINGS | Rural Short | Planned |  | 5 | 1765 | 353 | 1 | No
| 153404 | 15/01/2025 | 8:07 | 15/01/2025 | 10:31 | NP36 | NOBLE PARK | Urban | Planned |  | 18 | 2592 | 144 | 1 | No
| 153405 | 15/01/2025 | 11:15 | 15/01/2025 | 13:13 | NP36 | NOBLE PARK | Urban | Planned |  | 11 | 1298 | 118 | 1 | No
| 153409 | 2025-05-02 | 8:00 | 2025-05-02 | 11:00 | RBD23 | ROSEBUD | Urban | Planned |  | 2 | 360 | 180 | 1 | No
| 153410 | 2025-07-02 | 8:10 | 2025-07-02 | 12:00 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 66 | 15180 | 230 | 1 | No
| 153411 | 2025-07-02 | 8:00 | 2025-07-02 | 12:41 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 96 | 26976 | 281 | 1 | No
| 153412 | 24/01/2025 | 8:00 | 24/01/2025 | 10:18 | LWN33 | LANGWARRIN | Urban | Planned |  | 4 | 552 | 138 | 1 | No
| 153414 | 24/01/2025 | 8:00 | 24/01/2025 | 10:35 | LWN33 | LANGWARRIN | Urban | Planned |  | 16 | 2480 | 155 | 1 | No
| 153415 | 13/02/2025 | 9:11 | 13/02/2025 | 11:05 | OR34 | ORMOND | Urban | Planned |  | 54 | 6156 | 114 | 1 | No
| 153416 | 23/01/2025 | 10:00 | 23/01/2025 | 14:30 | MR31 | MOORABBIN | Urban | Planned |  | 1 | 270 | 270 | 1 | No
| 153416 | 23/01/2025 | 10:24 | 23/01/2025 | 12:08 | MR31 | MOORABBIN | Urban | Planned |  | 76 | 7904 | 104 | 1 | No
| 153417 | 2025-11-02 | 8:00 | 2025-11-02 | 18:30 | K31 | GARDINER | Urban | Planned |  | 197 | 124110 | 630 | 1 | No
| 153418 | 2025-12-02 | 8:12 | 2025-12-02 | 13:17 | BU21 | BULLEEN | Urban | Planned |  | 112 | 34160 | 305 | 1 | No
| 153419 | 2025-12-02 | 8:00 | 2025-12-02 | 15:30 | MC21 | MORDIALLOC | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 153419 | 2025-12-02 | 8:07 | 2025-12-02 | 14:16 | MC12 | MORDIALLOC | Urban | Planned |  | 12 | 4428 | 369 | 1 | No
| 153419 | 2025-12-02 | 8:07 | 2025-12-02 | 14:16 | MC21 | MORDIALLOC | Urban | Planned |  | 20 | 7380 | 369 | 1 | No
| 153420 | 17/03/2025 | 8:00 | 17/03/2025 | 17:00 | DMA15 | DROMANA | Rural Short | Planned |  | 1 | 540 | 540 | 1 | No
| 153420 | 17/03/2025 | 8:20 | 17/03/2025 | 15:57 | DMA15 | DROMANA | Rural Short | Planned |  | 262 | 119734 | 457 | 1 | No
| 153423 | 20/01/2025 | 8:55 | 20/01/2025 | 10:55 | EL32 | ELSTERNWICK | Urban | Planned |  | 1 | 120 | 120 | 1 | No
| 153428 | 16/01/2025 | 8:35 | 16/01/2025 | 12:15 | NB35 | NORTH BRIGHTON | Urban | Planned |  | 79 | 17380 | 220 | 1 | No
| 153429 | 19/01/2025 | 6:42 | 19/01/2025 | 11:17 | NO3 | NOTTING HILL | Urban | Planned |  | 21 | 5775 | 275 | 1 | No
| 153431 | 23/01/2025 | 8:05 | 23/01/2025 | 9:35 | RBD23 | ROSEBUD | Urban | Planned |  | 94 | 8460 | 90 | 1 | No
| 153437 | 27/02/2025 | 8:00 | 27/02/2025 | 18:38 | K31 | GARDINER | Urban | Planned |  | 100 | 63800 | 638 | 1 | No
| 153443 | 19/01/2025 | 7:40 | 19/01/2025 | 14:18 | NO3 | NOTTING HILL | Urban | Planned |  | 12 | 4776 | 398 | 1 | No
| 153445 | 19/01/2025 | 11:35 | 19/01/2025 | 12:47 | NO31 | NOTTING HILL | Urban | Planned |  | 1 | 72 | 72 | 1 | No
| 153446 | 30/01/2025 | 9:00 | 30/01/2025 | 10:52 | STO23 | SORRENTO | Urban | Planned |  | 33 | 3696 | 112 | 1 | No
| 153447 | 2025-10-02 | 8:29 | 2025-10-02 | 11:27 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 31 | 5518 | 178 | 1 | No
| 153448 | 29/01/2025 | 14:54 | 29/01/2025 | 15:15 | LD32 | LYNDALE | Urban | Planned |  | 30 | 630 | 21 | 1 | No
| 153455 | 14/02/2025 | 8:00 | 14/02/2025 | 11:53 | DC12 | DONCASTER | Urban | Planned |  | 14 | 3262 | 233 | 1 | No
| 153456 | 23/01/2025 | 8:00 | 23/01/2025 | 13:00 | SV32 | SPRINGVALE | Urban | Planned |  | 1 | 300 | 300 | 1 | No
| 153456 | 23/01/2025 | 8:17 | 23/01/2025 | 9:56 | SV32 | SPRINGVALE | Urban | Planned |  | 102 | 10098 | 99 | 1 | No
| 153465 | 2025-07-02 | 8:30 | 2025-07-02 | 14:30 | BU11 | BULLEEN | Urban | Planned |  | 71 | 25560 | 360 | 1 | No
| 153473 | 16/01/2025 | 8:14 | 16/01/2025 | 13:21 | LD6 | LYNDALE | Urban | Planned |  | 15 | 4605 | 307 | 1 | No
| 153474 | 23/01/2025 | 9:00 | 23/01/2025 | 14:32 | LD3 | LYNDALE | Urban | Planned |  | 12 | 3984 | 332 | 1 | No
| 153475 | 2025-06-02 | 8:15 | 2025-06-02 | 9:57 | STO23 | SORRENTO | Urban | Planned |  | 42 | 4284 | 102 | 1 | No
| 153481 | 2025-01-02 | 8:40 | 2025-01-02 | 15:00 | BU14 | BULLEEN | Urban | Planned |  | 101 | 38380 | 380 | 1 | No
| 153485 | 19/01/2025 | 7:35 | 19/01/2025 | 17:20 | DVY23 | DANDENONG VALLEY | Urban | Planned |  | 38 | 22230 | 585 | 1 | No
| 153486 | 19/01/2025 | 7:35 | 19/01/2025 | 12:24 | DVY23 | DANDENONG VALLEY | Urban | Planned |  | 17 | 4913 | 289 | 1 | No
| 153487 | 2025-04-02 | 8:50 | 2025-04-02 | 10:15 | LWN33 | LANGWARRIN | Urban | Planned |  | 83 | 7055 | 85 | 1 | No
| 153492 | 23/01/2025 | 8:15 | 23/01/2025 | 11:15 | BR13 | BEAUMARIS | Urban | Planned |  | 30 | 5400 | 180 | 1 | No
| 153493 | 24/01/2025 | 8:35 | 24/01/2025 | 16:00 | MGE13 | MULGRAVE | Urban | Planned |  | 106 | 47170 | 445 | 1 | No
| 153495 | 21/02/2025 | 8:15 | 21/02/2025 | 12:15 | DMA14 | DROMANA | Urban | Planned |  | 22 | 5280 | 240 | 1 | No
| 153496 | 2025-10-01 | 9:00 | 2025-10-01 | 12:15 | BU25 | BULLEEN | Urban | Planned |  | 31 | 6045 | 195 | 1 | No
| 153497 | 21/01/2025 | 8:05 | 21/01/2025 | 10:05 | HT11 | HEATHERTON | Urban | Planned |  | 58 | 6960 | 120 | 1 | No
| 153500 | 2025-04-02 | 8:00 | 2025-04-02 | 15:30 | K35 | GARDINER | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 153500 | 2025-04-02 | 8:01 | 2025-04-02 | 15:38 | K35 | GARDINER | Urban | Planned |  | 4 | 1828 | 457 | 1 | No
| 153501 | 24/01/2025 | 5:00 | 24/01/2025 | 10:00 | DC2 | DONCASTER | Urban | Planned |  | 2 | 600.9334 | 300.4667 | 1 | No
| 153502 | 24/01/2025 | 5:26 | 24/01/2025 | 8:10 | DC2 | DONCASTER | Urban | Planned |  | 48 | 7872 | 164 | 1 | No
| 153503 | 28/01/2025 | 8:31 | 28/01/2025 | 12:30 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 30 | 7170 | 239 | 1 | No
| 153504 | 30/01/2025 | 10:22 | 30/01/2025 | 13:31 | RBD13 | ROSEBUD | Urban | Planned |  | 65 | 12285 | 189 | 1 | No
| 153508 | 2025-04-02 | 8:55 | 2025-04-02 | 9:08 | BU12 | BULLEEN | Urban | Planned |  | 50 | 650 | 13 | 1 | No
| 153509 | 16/02/2025 | 8:10 | 16/02/2025 | 17:30 | HT8 | HEATHERTON | Urban | Planned |  | 29 | 16240 | 560 | 1 | No
| 153509 | 16/02/2025 | 8:10 | 16/02/2025 | 17:30 | MR33 | MOORABBIN | Urban | Planned |  | 32 | 17920 | 560 | 1 | No
| 153511 | 2025-02-02 | 6:10 | 2025-02-02 | 10:00 | MC34 | MORDIALLOC | Urban | Planned |  | 1 | 230 | 230 | 1 | No
| 153512 | 17/01/2025 | 8:03 | 17/01/2025 | 11:45 | CFD14 | CAULFIELD | Urban | Planned |  | 89 | 19758 | 222 | 1 | No
| 153517 | 23/01/2025 | 8:40 | 23/01/2025 | 14:47 | EM9 | EAST MALVERN | Urban | Planned |  | 90 | 33030 | 367 | 1 | No
| 153518 | 15/01/2025 | 8:00 | 15/01/2025 | 11:40 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 20 | 4392.334 | 219.6167 | 1 | No
| 153519 | 24/01/2025 | 8:46 | 24/01/2025 | 15:10 | BH34 | BOX HILL | Urban | Planned |  | 8 | 3072 | 384 | 1 | No
| 153522 | 22/01/2025 | 8:00 | 22/01/2025 | 16:30 | EM3 | EAST MALVERN | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 153522 | 22/01/2025 | 8:20 | 22/01/2025 | 13:06 | EM3 | EAST MALVERN | Urban | Planned |  | 55 | 15730 | 286 | 1 | No
| 153523 | 29/01/2025 | 10:15 | 29/01/2025 | 12:18 | FTN12 | FRANKSTON | Urban | Planned |  | 59 | 7257 | 123 | 1 | No
| 153525 | 31/01/2025 | 9:50 | 31/01/2025 | 14:10 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 45 | 11700 | 260 | 1 | No
| 153526 | 25/01/2025 | 8:00 | 25/01/2025 | 16:30 | EM6 | EAST MALVERN | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 153526 | 25/01/2025 | 8:22 | 25/01/2025 | 12:45 | EM6 | EAST MALVERN | Urban | Planned |  | 33 | 8679 | 263 | 1 | No
| 153527 | 2025-06-02 | 8:45 | 2025-06-02 | 12:40 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 18 | 4230 | 235 | 1 | No
| 153530 | 28/01/2025 | 8:46 | 28/01/2025 | 12:55 | EL24 | ELSTERNWICK | Urban | Planned |  | 24 | 5976 | 249 | 1 | No
| 153531 | 16/01/2025 | 8:57 | 16/01/2025 | 13:02 | DC3 | DONCASTER | Urban | Planned |  | 77 | 18865 | 245 | 1 | No
| 153537 | 25/01/2025 | 7:50 | 25/01/2025 | 12:35 | MC31 | MORDIALLOC | Urban | Planned |  | 31 | 8835 | 285 | 1 | No
| 153539 | 30/01/2025 | 8:28 | 30/01/2025 | 10:35 | NW21 | NUNAWADING | Urban | Planned |  | 89 | 11303 | 127 | 1 | No
| 153541 | 2025-04-02 | 8:05 | 2025-04-02 | 12:35 | BT14 | BENTLEIGH | Urban | Planned |  | 62 | 16740 | 270 | 1 | No
| 153541 | 2025-04-02 | 8:05 | 2025-04-02 | 12:35 | OR34 | ORMOND | Urban | Planned |  | 36 | 9720 | 270 | 1 | No
| 153544 | 2025-05-02 | 9:10 | 2025-05-02 | 10:50 | DC5 | DONCASTER | Urban | Planned |  | 43 | 4300 | 100 | 1 | No
| 153546 | 2025-05-02 | 11:40 | 2025-05-02 | 13:15 | DC5 | DONCASTER | Urban | Planned |  | 31 | 2945 | 95 | 1 | No
| 153547 | 15/01/2025 | 7:30 | 15/01/2025 | 15:17 | NO7 | NOTTING HILL | Urban | Planned |  | 215 | 100405 | 467 | 1 | No
| 153549 | 2025-03-02 | 7:00 | 2025-03-02 | 16:00 | SVW52 | SPRINGVALE WEST | Urban | Planned |  | 2 | 1080 | 540 | 1 | No
| 153553 | 21/01/2025 | 8:41 | 21/01/2025 | 11:56 | BU14 | BULLEEN | Urban | Planned |  | 37 | 7215 | 195 | 1 | No
| 153560 | 29/01/2025 | 8:05 | 29/01/2025 | 11:36 | BR1 | BEAUMARIS | Urban | Planned |  | 127 | 26797 | 211 | 1 | No
| 153563 | 23/01/2025 | 8:00 | 23/01/2025 | 13:25 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 90 | 29250 | 325 | 1 | No
| 153564 | 13/01/2025 | 21:32 | 14/01/2025 | 4:18 | SV14 | SPRINGVALE | Urban | Planned |  | 10 | 4060 | 406 | 1 | No
| 153564 | 13/01/2025 | 21:32 | 14/01/2025 | 4:18 | SVW41 | SPRINGVALE WEST | Urban | Planned |  | 7 | 2842 | 406 | 1 | No
| 153574 | 30/01/2025 | 8:00 | 30/01/2025 | 12:10 | BT14 | BENTLEIGH | Urban | Planned |  | 52 | 13000 | 250 | 1 | No
| 153575 | 2025-12-02 | 8:00 | 2025-12-02 | 13:55 | M25 | MENTONE | Urban | Planned |  | 105 | 37275 | 355 | 2 | No
| 153575 | 2025-12-02 | 8:00 | 2025-12-02 | 16:00 | M25 | MENTONE | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 153579 | 21/01/2025 | 20:32 | 22/01/2025 | 4:45 | CRM23 | CARRUM | Urban | Planned |  | 213 | 105009 | 493 | 1 | No
| 153584 | 2025-06-02 | 8:25 | 2025-06-02 | 14:00 | STO21 | SORRENTO | Rural Short | Planned |  | 157 | 52595 | 335 | 1 | No
| 153590 | 2025-05-02 | 8:51 | 2025-05-02 | 14:09 | EW1 | ELWOOD | Urban | Planned |  | 1 | 318 | 318 | 1 | No
| 153596 | 23/01/2025 | 8:10 | 23/01/2025 | 9:43 | MTN32 | MORNINGTON | Rural Short | Planned |  | 1 | 93 | 93 | 1 | No
| 153598 | 30/01/2025 | 8:01 | 30/01/2025 | 12:42 | CDA11 | CLARINDA | Urban | Planned |  | 137 | 38497 | 281 | 1 | No
| 153606 | 30/01/2025 | 6:45 | 30/01/2025 | 8:26 | SS21 | SPRINGVALE SOUTH | Urban | Planned |  | 1 | 101 | 101 | 1 | No
| 153609 | 30/01/2025 | 8:00 | 30/01/2025 | 15:38 | MGE23 | MULGRAVE | Urban | Planned |  | 16 | 7328 | 458 | 1 | No
| 153613 | 23/01/2025 | 8:00 | 23/01/2025 | 16:00 | BU22 | BULLEEN | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 153613 | 23/01/2025 | 8:32 | 23/01/2025 | 13:04 | BU22 | BULLEEN | Urban | Planned |  | 38 | 10336 | 272 | 1 | No
| 153617 | 2025-05-02 | 11:05 | 2025-05-02 | 13:30 | MTN22 | MORNINGTON | Rural Short | Planned |  | 1 | 145 | 145 | 1 | No
| 153619 | 31/01/2025 | 8:00 | 31/01/2025 | 10:40 | MR11 | MOORABBIN | Urban | Planned |  | 47 | 7518.4349 | 159.9667 | 2 | No
| 153619 | 31/01/2025 | 8:00 | 31/01/2025 | 15:30 | MR11 | MOORABBIN | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 153620 | 14/01/2025 | 7:00 | 14/01/2025 | 16:00 | EL25 | ELSTERNWICK | Urban | Planned |  | 9 | 4860 | 540 | 1 | No
| 153620 | 14/01/2025 | 7:00 | 14/01/2025 | 16:00 | EL32 | ELSTERNWICK | Urban | Planned |  | 3 | 1620 | 540 | 1 | No
| 153626 | 2025-09-02 | 7:30 | 2025-09-02 | 15:30 | BU25 | BULLEEN | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 153626 | 2025-09-02 | 8:55 | 2025-09-02 | 18:53 | BU25 | BULLEEN | Urban | Planned |  | 170 | 101660 | 598 | 1 | No
| 153628 | 17/02/2025 | 9:45 | 17/02/2025 | 15:28 | NW23 | NUNAWADING | Urban | Planned |  | 45 | 15435 | 343 | 1 | No
| 153632 | 19/02/2025 | 8:40 | 19/02/2025 | 18:15 | FTN25 | FRANKSTON | Urban | Planned |  | 172 | 98900 | 575 | 1 | No
| 153638 | 2025-04-03 | 8:30 | 2025-04-03 | 21:43 | NO7 | NOTTING HILL | Urban | Planned |  | 1 | 793 | 793 | 1 | No
| 153642 | 28/01/2025 | 8:33 | 28/01/2025 | 11:32 | MTN32 | MORNINGTON | Rural Short | Planned |  | 63 | 11277 | 179 | 1 | No
| 153643 | 31/01/2025 | 8:57 | 31/01/2025 | 12:54 | EB21 | EAST BURWOOD | Urban | Planned |  | 48 | 11376 | 237 | 1 | No
| 153645 | 29/01/2025 | 9:02 | 29/01/2025 | 13:15 | NW22 | NUNAWADING | Urban | Planned |  | 24 | 6072 | 253 | 1 | No
| 153646 | 23/01/2025 | 8:08 | 23/01/2025 | 9:47 | HGS23 | HASTINGS | Rural Short | Planned |  | 1 | 99 | 99 | 1 | No
| 153647 | 23/01/2025 | 11:33 | 23/01/2025 | 13:03 | DMA24 | DROMANA | Rural Short | Planned |  | 2 | 180 | 90 | 1 | No
| 153649 | 25/01/2025 | 8:32 | 25/01/2025 | 12:40 | NB36 | NORTH BRIGHTON | Urban | Planned |  | 116 | 28768 | 248 | 1 | No
| 153653 | 20/02/2025 | 8:40 | 20/02/2025 | 14:00 | STO23 | SORRENTO | Urban | Planned |  | 20 | 6400 | 320 | 1 | No
| 153654 | 21/02/2025 | 8:00 | 21/02/2025 | 11:41 | DMA14 | DROMANA | Urban | Planned |  | 54 | 11934 | 221 | 1 | No
| 153655 | 24/02/2025 | 9:33 | 24/02/2025 | 12:35 | STO23 | SORRENTO | Urban | Planned |  | 55 | 10010 | 182 | 1 | No
| 153656 | 26/02/2025 | 8:22 | 26/02/2025 | 12:45 | STO14 | SORRENTO | Rural Short | Planned |  | 45 | 11835 | 263 | 1 | No
| 153661 | 25/02/2025 | 8:40 | 25/02/2025 | 9:45 | NW21 | NUNAWADING | Urban | Planned |  | 5 | 325 | 65 | 1 | No
| 153665 | 23/01/2025 | 8:36 | 23/01/2025 | 13:18 | NW23 | NUNAWADING | Urban | Planned |  | 29 | 8178 | 282 | 1 | No
| 153675 | 20/02/2025 | 8:35 | 20/02/2025 | 10:35 | MR15 | MOORABBIN | Urban | Planned |  | 48 | 5760 | 120 | 1 | No
| 153677 | 23/02/2025 | 8:00 | 23/02/2025 | 10:47 | DVY32 | DANDENONG VALLEY | Urban | Planned |  | 10 | 1670 | 167 | 1 | No
| 153683 | 26/02/2025 | 8:05 | 26/02/2025 | 10:54 | BT14 | BENTLEIGH | Urban | Planned |  | 30 | 5070 | 169 | 1 | No
| 153692 | 2025-04-02 | 8:00 | 2025-04-02 | 10:35 | RBD23 | ROSEBUD | Urban | Planned |  | 63 | 9765 | 155 | 1 | No
| 153693 | 2025-05-02 | 8:20 | 2025-05-02 | 11:40 | OR24 | ORMOND | Urban | Planned |  | 67 | 13400 | 200 | 1 | No
| 153693 | 2025-05-02 | 8:20 | 2025-05-02 | 11:40 | OR33 | ORMOND | Urban | Planned |  | 77 | 15400 | 200 | 1 | No
| 153694 | 2025-05-02 | 11:30 | 2025-05-02 | 14:25 | LWN32 | LANGWARRIN | Rural Short | Planned |  | 29 | 5075 | 175 | 1 | No
| 153696 | 2025-02-03 | 7:34 | 2025-02-03 | 9:30 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 1 | 116 | 116 | 1 | No
| 153697 | 2025-02-03 | 11:45 | 2025-02-03 | 13:22 | MC23 | MORDIALLOC | Urban | Planned |  | 11 | 1067 | 97 | 1 | No
| 153698 | 30/04/2025 | 8:09 | 30/04/2025 | 14:21 | RBD24 | ROSEBUD | Urban | Planned |  | 79 | 29388 | 372 | 1 | No
| 153702 | 2025-08-02 | 8:05 | 2025-08-02 | 15:20 | HGS21 | HASTINGS | Rural Short | Planned |  | 1 | 435 | 435 | 1 | No
| 153712 | 16/02/2025 | 8:00 | 16/02/2025 | 17:00 | BW33 | BURWOOD | Urban | Planned |  | 2 | 1080 | 540 | 1 | No
| 153712 | 16/02/2025 | 8:04 | 16/02/2025 | 16:03 | BW33 | BURWOOD | Urban | Planned |  | 184 | 88136 | 479 | 1 | No
| 153715 | 2025-11-02 | 9:30 | 2025-11-02 | 12:25 | DC4 | DONCASTER | Urban | Planned |  | 35 | 6125 | 175 | 1 | No
| 153717 | 2025-02-03 | 8:15 | 2025-02-03 | 14:50 | BW32 | BURWOOD | Urban | Planned |  | 51 | 20145 | 395 | 1 | No
| 153719 | 2025-06-02 | 8:19 | 2025-06-02 | 11:22 | STO13 | SORRENTO | Urban | Planned |  | 78 | 14274 | 183 | 1 | No
| 153723 | 2025-11-02 | 8:15 | 2025-11-02 | 14:30 | DC4 | DONCASTER | Urban | Planned |  | 49 | 18375 | 375 | 1 | No
| 153748 | 31/01/2025 | 8:46 | 31/01/2025 | 12:40 | MTN32 | MORNINGTON | Rural Short | Planned |  | 24 | 5616 | 234 | 1 | No
| 153749 | 2025-06-02 | 12:19 | 2025-06-02 | 15:22 | DMA13 | DROMANA | Rural Short | Planned |  | 48 | 8784 | 183 | 1 | No
| 153752 | 31/01/2025 | 8:43 | 31/01/2025 | 14:43 | RBD23 | ROSEBUD | Urban | Planned |  | 166 | 59760 | 360 | 1 | No
| 153753 | 30/01/2025 | 9:02 | 30/01/2025 | 11:35 | STO21 | SORRENTO | Rural Short | Planned |  | 61 | 9333 | 153 | 1 | No
| 153754 | 2025-09-02 | 8:30 | 2025-09-02 | 10:10 | SV23 | SPRINGVALE | Urban | Planned |  | 12 | 1200 | 100 | 1 | No
| 153755 | 2025-09-02 | 11:36 | 2025-09-02 | 13:22 | KBH35 | KEYSBOROUGH | Urban | Planned |  | 11 | 1166 | 106 | 1 | No
| 153764 | 2025-07-02 | 8:01 | 2025-07-02 | 11:47 | DN10 | DANDENONG | Urban | Planned |  | 22 | 4972 | 226 | 1 | No
| 153765 | 23/01/2025 | 8:49 | 23/01/2025 | 9:04 | STO14 | SORRENTO | Rural Short | Planned |  | 2 | 30 | 15 | 1 | No
| 153776 | 2025-02-03 | 8:00 | 2025-02-03 | 15:30 | M13 | MENTONE | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 153776 | 2025-02-03 | 8:30 | 2025-02-03 | 14:30 | M13 | MENTONE | Urban | Planned |  | 253 | 91080 | 360 | 1 | No
| 153776 | 2025-02-03 | 8:30 | 2025-02-03 | 14:30 | M22 | MENTONE | Urban | Planned |  | 38 | 13680 | 360 | 1 | No
| 153778 | 2025-08-02 | 7:15 | 2025-08-02 | 17:30 | KBH35 | KEYSBOROUGH | Urban | Planned |  | 10 | 6150 | 615 | 1 | No
| 153781 | 2025-08-02 | 8:10 | 2025-08-02 | 13:00 | DN10 | DANDENONG | Urban | Planned |  | 1 | 290 | 290 | 1 | No
| 153782 | 28/01/2025 | 8:48 | 28/01/2025 | 12:05 | MGE31 | MULGRAVE | Urban | Planned |  | 43 | 8471 | 197 | 1 | No
| 153783 | 29/01/2025 | 8:22 | 29/01/2025 | 15:05 | MGE31 | MULGRAVE | Urban | Planned |  | 96 | 38688 | 403 | 1 | No
| 153784 | 30/01/2025 | 8:10 | 30/01/2025 | 15:15 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 103 | 43775 | 425 | 1 | No
| 153784 | 30/01/2025 | 8:10 | 30/01/2025 | 15:15 | NB36 | NORTH BRIGHTON | Urban | Planned |  | 54 | 22950 | 425 | 1 | No
| 153801 | 30/03/2025 | 8:50 | 30/03/2025 | 13:30 | DN6 | DANDENONG | Urban | Planned |  | 28 | 7840 | 280 | 1 | No
| 153806 | 2025-05-02 | 8:10 | 2025-05-02 | 15:45 | HGS22 | HASTINGS | Rural Short | Planned |  | 108 | 49140 | 455 | 1 | No
| 153820 | 25/02/2025 | 8:55 | 25/02/2025 | 13:45 | DMA13 | DROMANA | Rural Short | Planned |  | 69 | 20010 | 290 | 1 | No
| 153829 | 2025-02-02 | 7:15 | 2025-02-02 | 15:30 | NO2 | NOTTING HILL | Urban | Planned |  | 1 | 495 | 495 | 1 | No
| 153835 | 22/02/2025 | 8:00 | 22/02/2025 | 11:25 | NP23 | NOBLE PARK | Urban | Planned |  | 107 | 21935 | 205 | 1 | No
| 153838 | 31/01/2025 | 8:05 | 31/01/2025 | 13:05 | EB22 | EAST BURWOOD | Urban | Planned |  | 128 | 38400 | 300 | 1 | No
| 153844 | 2025-04-02 | 10:00 | 2025-04-02 | 12:10 | WD14 | WEST DONCASTER | Urban | Planned |  | 30 | 3900 | 130 | 1 | No
| 153846 | 2025-11-02 | 8:00 | 2025-11-02 | 11:30 | M12 | MENTONE | Urban | Planned |  | 96 | 20160 | 210 | 1 | No
| 153847 | 2025-07-02 | 8:32 | 2025-07-02 | 13:59 | NP25 | NOBLE PARK | Urban | Planned |  | 58 | 18966 | 327 | 1 | No
| 153849 | 2025-07-02 | 8:10 | 2025-07-02 | 11:55 | MR21 | MOORABBIN | Urban | Planned |  | 59 | 13275 | 225 | 1 | No
| 153850 | 2025-05-02 | 13:45 | 2025-05-02 | 14:59 | MTN22 | MORNINGTON | Rural Short | Planned |  | 3 | 222 | 74 | 1 | No
| 153855 | 2025-05-02 | 10:48 | 2025-05-02 | 12:37 | MTN22 | MORNINGTON | Rural Short | Planned |  | 5 | 545 | 109 | 1 | No
| 153858 | 2025-03-04 | 8:00 | 2025-03-04 | 15:30 | GW4 | GLEN WAVERLEY | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 153868 | 13/02/2025 | 8:00 | 13/02/2025 | 12:00 | BR15 | BEAUMARIS | Urban | Planned |  | 1 | 240 | 240 | 1 | No
| 153873 | 2025-04-02 | 7:30 | 2025-04-02 | 11:30 | M13 | MENTONE | Urban | Planned |  | 11 | 2640 | 240 | 1 | No
| 153877 | 14/02/2025 | 8:30 | 14/02/2025 | 11:18 | M25 | MENTONE | Urban | Planned |  | 37 | 6216 | 168 | 1 | No
| 153886 | 28/01/2025 | 21:55 | 29/01/2025 | 1:43 | FTN22 | FRANKSTON | Urban | Planned |  | 20 | 4560 | 228 | 1 | No
| 153890 | 2025-04-02 | 8:00 | 2025-04-02 | 11:23 | NP12 | NOBLE PARK | Urban | Planned |  | 1 | 203 | 203 | 1 | No
| 153895 | 20/02/2025 | 8:07 | 20/02/2025 | 15:00 | SR34 | SANDRINGHAM | Urban | Planned |  | 163 | 67319 | 413 | 1 | No
| 153903 | 2025-06-02 | 8:00 | 2025-06-02 | 15:15 | NO6 | NOTTING HILL | Urban | Planned |  | 1 | 435 | 435 | 1 | No
| 153906 | 13/02/2025 | 8:00 | 13/02/2025 | 15:30 | CRM15 | CARRUM | Urban | Planned |  | 89 | 40050 | 450 | 1 | No
| 153910 | 19/02/2025 | 10:00 | 19/02/2025 | 13:33 | M22 | MENTONE | Urban | Planned |  | 46 | 9798 | 213 | 1 | No
| 153915 | 13/02/2025 | 8:15 | 13/02/2025 | 13:50 | EB11 | EAST BURWOOD | Urban | Planned |  | 23 | 7705 | 335 | 1 | No
| 153916 | 18/02/2025 | 9:30 | 18/02/2025 | 14:30 | K33 | GARDINER | Urban | Planned |  | 11 | 3300 | 300 | 1 | No
| 153918 | 2025-07-02 | 8:26 | 2025-07-02 | 11:46 | STO14 | SORRENTO | Rural Short | Planned |  | 42 | 8400 | 200 | 1 | No
| 153929 | 2025-06-02 | 10:30 | 2025-06-02 | 14:30 | BU12 | BULLEEN | Urban | Planned |  | 98 | 23520 | 240 | 1 | No
| 153930 | 2025-06-02 | 8:33 | 2025-06-02 | 12:40 | WD14 | WEST DONCASTER | Urban | Planned |  | 54 | 13338 | 247 | 1 | No
| 153938 | 2025-05-02 | 8:00 | 2025-05-02 | 16:30 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 153938 | 2025-05-02 | 9:45 | 2025-05-02 | 14:17 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 54 | 14688 | 272 | 1 | No
| 153946 | 2025-08-02 | 6:58 | 2025-08-02 | 15:42 | EB13 | EAST BURWOOD | Urban | Planned |  | 1 | 524 | 524 | 1 | No
| 153948 | 2025-08-02 | 7:55 | 2025-08-02 | 9:20 | NW32 | NUNAWADING | Urban | Planned |  | 1 | 85 | 85 | 1 | No
| 153962 | 2025-09-02 | 7:30 | 2025-09-02 | 14:57 | M34 | MENTONE | Urban | Planned |  | 39 | 17433 | 447 | 1 | No
| 153965 | 2025-06-02 | 9:30 | 2025-06-02 | 15:30 | CFD13 | CAULFIELD | Urban | Planned |  | 7 | 2520 | 360 | 1 | No
| 153966 | 2025-09-02 | 8:00 | 2025-09-02 | 16:30 | NW32 | NUNAWADING | Urban | Planned |  | 18 | 9180 | 510 | 1 | No
| 153967 | 21/02/2025 | 8:04 | 21/02/2025 | 10:54 | M23 | MENTONE | Urban | Planned |  | 51 | 8670 | 170 | 1 | No
| 153971 | 2025-09-02 | 7:21 | 2025-09-02 | 14:29 | DC12 | DONCASTER | Urban | Planned |  | 3 | 1284 | 428 | 1 | No
| 153973 | 17/02/2025 | 8:00 | 17/02/2025 | 14:28 | DC2 | DONCASTER | Urban | Planned |  | 5 | 1940 | 388 | 1 | No
| 153974 | 2025-10-02 | 8:20 | 2025-10-02 | 12:34 | NW22 | NUNAWADING | Urban | Planned |  | 44 | 11176 | 254 | 1 | No
| 153978 | 2025-10-02 | 12:10 | 2025-10-02 | 14:45 | DMA15 | DROMANA | Rural Short | Planned |  | 4 | 620 | 155 | 1 | No
| 153987 | 2025-11-02 | 8:30 | 2025-11-02 | 9:40 | DMA15 | DROMANA | Rural Short | Planned |  | 3 | 210 | 70 | 1 | No
| 153988 | 2025-11-02 | 11:23 | 2025-11-02 | 13:19 | DMA15 | DROMANA | Rural Short | Planned |  | 6 | 696 | 116 | 1 | No
| 153989 | 19/02/2025 | 14:25 | 19/02/2025 | 16:46 | RWT35 | RINGWOOD | Urban | Planned |  | 3 | 423 | 141 | 1 | No
| 154000 | 13/02/2025 | 8:40 | 13/02/2025 | 10:23 | DC4 | DONCASTER | Urban | Planned |  | 24 | 2472 | 103 | 1 | No
| 154002 | 2025-07-02 | 8:29 | 2025-07-02 | 14:45 | BU14 | BULLEEN | Urban | Planned |  | 100 | 37600 | 376 | 1 | No
| 154006 | 2025-07-02 | 8:55 | 2025-07-02 | 13:00 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 31 | 7595 | 245 | 1 | No
| 154008 | 2025-11-02 | 8:01 | 2025-11-02 | 13:26 | FTN13 | FRANKSTON | Urban | Planned |  | 11 | 3575 | 325 | 1 | No
| 154016 | 2025-11-02 | 4:00 | 2025-11-02 | 5:00 | DVY22 | DANDENONG VALLEY | Urban | Planned |  | 3 | 180 | 60 | 1 | No
| 154028 | 19/02/2025 | 9:25 | 19/02/2025 | 15:42 | CFD26 | CAULFIELD | Urban | Planned |  | 102 | 38454 | 377 | 1 | No
| 154029 | 25/02/2025 | 8:03 | 25/02/2025 | 12:52 | NP16 | NOBLE PARK | Urban | Planned |  | 188 | 54332 | 289 | 1 | No
| 154037 | 2025-12-02 | 8:45 | 2025-12-02 | 12:45 | FTN11 | FRANKSTON | Urban | Planned |  | 80 | 19200 | 240 | 1 | No
| 154041 | 19/02/2025 | 8:15 | 19/02/2025 | 11:05 | NP23 | NOBLE PARK | Urban | Planned |  | 25 | 4250 | 170 | 1 | No
| 154042 | 15/02/2025 | 8:00 | 15/02/2025 | 10:15 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 62 | 8370 | 135 | 1 | No
| 154043 | 25/02/2025 | 9:45 | 25/02/2025 | 14:36 | MGE34 | MULGRAVE | Urban | Planned |  | 26 | 7566 | 291 | 1 | No
| 154044 | 2025-09-02 | 8:10 | 2025-09-02 | 13:45 | HT6 | HEATHERTON | Urban | Planned |  | 1 | 335 | 335 | 1 | No
| 154046 | 2025-09-02 | 9:20 | 2025-09-02 | 12:13 | CFD16 | CAULFIELD | Urban | Planned |  | 26 | 4498 | 173 | 1 | No
| 154058 | 2025-12-02 | 10:06 | 2025-12-02 | 13:30 | HT2 | HEATHERTON | Urban | Planned |  | 40 | 8160 | 204 | 1 | No
| 154058 | 2025-12-02 | 10:06 | 2025-12-02 | 13:30 | SR31 | SANDRINGHAM | Urban | Planned |  | 19 | 3876 | 204 | 1 | No
| 154060 | 18/02/2025 | 8:00 | 18/02/2025 | 11:25 | NP36 | NOBLE PARK | Urban | Planned |  | 9 | 1843.4997 | 204.8333 | 1 | No
| 154061 | 23/02/2025 | 8:13 | 23/02/2025 | 8:54 | HT13 | HEATHERTON | Urban | Planned |  | 5 | 205 | 41 | 1 | No
| 154061 | 23/02/2025 | 8:13 | 23/02/2025 | 8:54 | HT2 | HEATHERTON | Urban | Planned |  | 25 | 1025 | 41 | 1 | No
| 154062 | 20/02/2025 | 10:00 | 20/02/2025 | 13:00 | MGE21 | MULGRAVE | Urban | Planned |  | 21 | 3780 | 180 | 1 | No
| 154063 | 2025-08-04 | 8:25 | 2025-08-04 | 14:15 | BH34 | BOX HILL | Urban | Planned |  | 116 | 40600 | 350 | 1 | No
| 154064 | 24/02/2025 | 8:15 | 24/02/2025 | 11:57 | OR32 | ORMOND | Urban | Planned |  | 20 | 4440 | 222 | 1 | No
| 154066 | 17/02/2025 | 8:47 | 17/02/2025 | 12:26 | LWN23 | LANGWARRIN | Urban | Planned |  | 52 | 11388 | 219 | 1 | No
| 154066 | 17/02/2025 | 8:47 | 17/02/2025 | 12:26 | LWN32 | LANGWARRIN | Rural Short | Planned |  | 10 | 2190 | 219 | 1 | No
| 154071 | 23/02/2025 | 10:50 | 23/02/2025 | 15:00 | HT3 | HEATHERTON | Urban | Planned |  | 11 | 2750 | 250 | 1 | No
| 154075 | 2025-03-03 | 12:40 | 2025-03-03 | 13:43 | M25 | MENTONE | Urban | Planned |  | 12 | 756 | 63 | 1 | No
| 154076 | 2025-03-03 | 9:51 | 2025-03-03 | 11:24 | MC23 | MORDIALLOC | Urban | Planned |  | 3 | 279 | 93 | 1 | No
| 154077 | 2025-12-02 | 13:33 | 2025-12-02 | 15:20 | HT4 | HEATHERTON | Urban | Planned |  | 2 | 214 | 107 | 1 | No
| 154079 | 2025-12-02 | 9:15 | 2025-12-02 | 12:08 | HT4 | HEATHERTON | Urban | Planned |  | 55 | 9515 | 173 | 1 | No
| 154085 | 2025-08-02 | 12:31 | 2025-08-02 | 17:30 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 71 | 21229 | 299 | 1 | No
| 154086 | 2025-08-02 | 8:28 | 2025-08-02 | 10:48 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 24 | 3360 | 140 | 1 | No
| 154087 | 25/02/2025 | 8:36 | 25/02/2025 | 12:56 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 86 | 22360 | 260 | 1 | No
| 154090 | 2025-11-02 | 9:30 | 2025-11-02 | 11:55 | EL22 | ELSTERNWICK | Urban | Planned |  | 76 | 11020 | 145 | 1 | No
| 154097 | 25/02/2025 | 13:30 | 25/02/2025 | 14:40 | BT14 | BENTLEIGH | Urban | Planned |  | 53 | 3710 | 70 | 1 | No
| 154099 | 19/02/2025 | 8:10 | 19/02/2025 | 13:50 | NB34 | NORTH BRIGHTON | Urban | Planned |  | 158 | 53720 | 340 | 1 | No
| 154114 | 17/02/2025 | 8:37 | 17/02/2025 | 11:01 | CFD14 | CAULFIELD | Urban | Planned |  | 54 | 7776 | 144 | 1 | No
| 154116 | 15/02/2025 | 8:00 | 15/02/2025 | 8:35 | WD26 | WEST DONCASTER | Urban | Planned |  | 25 | 872.0825 | 34.8833 | 1 | No
| 154118 | 19/02/2025 | 8:45 | 19/02/2025 | 10:45 | SVW54 | SPRINGVALE WEST | Urban | Planned |  | 14 | 1680 | 120 | 1 | No
| 154121 | 19/02/2025 | 8:45 | 19/02/2025 | 11:00 | MGE32 | MULGRAVE | Urban | Planned |  | 45 | 6075 | 135 | 1 | No
| 154122 | 19/02/2025 | 12:00 | 19/02/2025 | 14:10 | NW13 | NUNAWADING | Urban | Planned |  | 17 | 2210 | 130 | 1 | No
| 154124 | 28/02/2025 | 8:00 | 28/02/2025 | 12:59 | CRM23 | CARRUM | Urban | Planned |  | 171 | 51129 | 299 | 1 | No
| 154127 | 14/02/2025 | 11:43 | 14/02/2025 | 12:40 | DC5 | DONCASTER | Urban | Planned |  | 23 | 1311 | 57 | 1 | No
| 154128 | 21/02/2025 | 8:01 | 21/02/2025 | 15:15 | NO7 | NOTTING HILL | Urban | Planned |  | 150 | 65100 | 434 | 1 | No
| 154129 | 2025-12-04 | 8:03 | 2025-12-04 | 13:07 | CDA22 | CLARINDA | Urban | Planned |  | 8 | 2432 | 304 | 1 | No
| 154132 | 2025-05-03 | 8:51 | 2025-05-03 | 11:17 | FTN24 | FRANKSTON | Urban | Planned |  | 44 | 6424 | 146 | 1 | No
| 154134 | 2025-07-03 | 8:30 | 2025-07-03 | 12:20 | RBD23 | ROSEBUD | Urban | Planned |  | 40 | 9200 | 230 | 1 | No
| 154136 | 2025-11-03 | 8:02 | 2025-11-03 | 12:28 | STO13 | SORRENTO | Urban | Planned |  | 174 | 46284 | 266 | 1 | No
| 154137 | 2025-12-03 | 8:45 | 2025-12-03 | 13:55 | DMA21 | DROMANA | Urban | Planned |  | 161 | 49910 | 310 | 1 | No
| 154153 | 23/03/2025 | 8:00 | 23/03/2025 | 12:10 | HT7 | HEATHERTON | Urban | Planned |  | 18 | 4500 | 250 | 1 | No
| 154164 | 14/02/2025 | 8:00 | 14/02/2025 | 14:10 | DMA23 | DROMANA | Rural Short | Planned |  | 41 | 15170 | 370 | 1 | No
| 154167 | 26/02/2025 | 8:00 | 26/02/2025 | 16:44 | OR34 | ORMOND | Urban | Planned |  | 7 | 3668 | 524 | 1 | No
| 154169 | 25/02/2025 | 8:10 | 25/02/2025 | 16:15 | NW23 | NUNAWADING | Urban | Planned |  | 54 | 26190 | 485 | 1 | No
| 154170 | 20/02/2025 | 11:30 | 20/02/2025 | 12:13 | BU22 | BULLEEN | Urban | Planned |  | 18 | 774 | 43 | 1 | No
| 154171 | 18/02/2025 | 8:00 | 18/02/2025 | 16:00 | FSH21 | FRANKSTON SOUTH | Rural Short | Planned |  | 41 | 19680 | 480 | 1 | No
| 154172 | 2025-06-03 | 6:30 | 2025-06-03 | 18:00 | NB35 | NORTH BRIGHTON | Urban | Planned |  | 1 | 690 | 690 | 1 | No
| 154172 | 2025-06-03 | 6:47 | 2025-06-03 | 15:45 | NB35 | NORTH BRIGHTON | Urban | Planned |  | 45 | 24210 | 538 | 1 | No
| 154173 | 18/02/2025 | 8:24 | 18/02/2025 | 15:10 | BT12 | BENTLEIGH | Urban | Planned |  | 30 | 12180 | 406 | 1 | No
| 154177 | 21/02/2025 | 8:00 | 21/02/2025 | 14:00 | BT14 | BENTLEIGH | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 154177 | 21/02/2025 | 8:03 | 21/02/2025 | 10:35 | BT14 | BENTLEIGH | Urban | Planned |  | 25 | 3800 | 152 | 1 | No
| 154179 | 21/02/2025 | 11:13 | 21/02/2025 | 12:25 | M31 | MENTONE | Urban | Planned |  | 81 | 5832 | 72 | 1 | No
| 154181 | 18/02/2025 | 8:00 | 18/02/2025 | 14:35 | MTN22 | MORNINGTON | Rural Short | Planned |  | 1 | 395 | 395 | 1 | No
| 154186 | 23/03/2025 | 8:00 | 23/03/2025 | 13:22 | CDA22 | CLARINDA | Urban | Planned |  | 23 | 7406 | 322 | 1 | No
| 154187 | 14/02/2025 | 9:28 | 14/02/2025 | 11:16 | LWN24 | LANGWARRIN | Urban | Planned |  | 2 | 216 | 108 | 1 | No
| 154188 | 14/02/2025 | 9:08 | 14/02/2025 | 12:50 | EM6 | EAST MALVERN | Urban | Planned |  | 19 | 4218 | 222 | 1 | No
| 154189 | 17/02/2025 | 8:30 | 17/02/2025 | 12:28 | DMA14 | DROMANA | Urban | Planned |  | 19 | 4522 | 238 | 1 | No
| 154190 | 23/02/2025 | 8:00 | 23/02/2025 | 10:40 | RWT12 | RINGWOOD | Urban | Planned |  | 1 | 160 | 160 | 1 | No
| 154191 | 14/02/2025 | 12:23 | 14/02/2025 | 13:40 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 3 | 231 | 77 | 1 | No
| 154195 | 20/02/2025 | 8:50 | 20/02/2025 | 12:15 | BU12 | BULLEEN | Urban | Planned |  | 43 | 8815 | 205 | 1 | No
| 154196 | 24/02/2025 | 8:15 | 24/02/2025 | 13:00 | DC1 | DONCASTER | Urban | Planned |  | 114 | 32490 | 285 | 1 | No
| 154197 | 2025-04-03 | 8:15 | 2025-04-03 | 12:17 | M23 | MENTONE | Urban | Planned |  | 204 | 49368 | 242 | 1 | No
| 154201 | 14/03/2025 | 8:00 | 14/03/2025 | 10:49 | SR26 | SANDRINGHAM | Urban | Planned |  | 45 | 7605 | 169 | 1 | No
| 154202 | 18/02/2025 | 8:30 | 18/02/2025 | 13:30 | EB13 | EAST BURWOOD | Urban | Planned |  | 2 | 600 | 300 | 1 | No
| 154208 | 17/02/2025 | 8:00 | 17/02/2025 | 9:49 | HGS21 | HASTINGS | Rural Short | Planned |  | 21 | 2289 | 109 | 1 | No
| 154209 | 17/02/2025 | 10:19 | 17/02/2025 | 13:06 | HGS21 | HASTINGS | Rural Short | Planned |  | 72 | 12024 | 167 | 1 | No
| 154213 | 28/03/2025 | 8:00 | 28/03/2025 | 15:30 | NW21 | NUNAWADING | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 154215 | 21/02/2025 | 8:26 | 21/02/2025 | 11:33 | DMA14 | DROMANA | Urban | Planned |  | 18 | 3366 | 187 | 1 | No
| 154216 | 21/02/2025 | 11:50 | 21/02/2025 | 13:55 | DMA14 | DROMANA | Urban | Planned |  | 57 | 7125 | 125 | 1 | No
| 154218 | 17/02/2025 | 8:14 | 17/02/2025 | 11:45 | NP11 | NOBLE PARK | Urban | Planned |  | 54 | 11394 | 211 | 1 | No
| 154220 | 17/02/2025 | 12:04 | 17/02/2025 | 15:15 | LD32 | LYNDALE | Urban | Planned |  | 28 | 5348 | 191 | 1 | No
| 154222 | 26/02/2025 | 8:30 | 26/02/2025 | 15:30 | BU11 | BULLEEN | Urban | Planned |  | 97 | 40740 | 420 | 1 | No
| 154225 | 17/02/2025 | 10:30 | 17/02/2025 | 14:30 | KBH34 | KEYSBOROUGH | Urban | Planned |  | 2 | 480 | 240 | 1 | No
| 154226 | 18/02/2025 | 8:02 | 18/02/2025 | 14:10 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 151 | 55568 | 368 | 1 | No
| 154227 | 26/02/2025 | 9:00 | 26/02/2025 | 10:30 | M31 | MENTONE | Urban | Planned |  | 38 | 3420 | 90 | 1 | No
| 154230 | 23/02/2025 | 8:15 | 23/02/2025 | 13:20 | HT7 | HEATHERTON | Urban | Planned |  | 98 | 29890 | 305 | 1 | No
| 154232 | 27/02/2025 | 9:11 | 27/02/2025 | 14:43 | HGS31 | HASTINGS | Rural Short | Planned |  | 33 | 10956 | 332 | 1 | No
| 154235 | 2025-05-03 | 9:20 | 2025-05-03 | 11:24 | RBD12 | ROSEBUD | Rural Short | Planned |  | 77 | 9548 | 124 | 1 | No
| 154237 | 18/02/2025 | 8:37 | 18/02/2025 | 11:20 | DN13 | DANDENONG | Urban | Planned |  | 41 | 6683 | 163 | 1 | No
| 154239 | 27/02/2025 | 8:30 | 27/02/2025 | 11:10 | DC2 | DONCASTER | Urban | Planned |  | 97 | 15520 | 160 | 1 | No
| 154241 | 28/02/2025 | 8:19 | 28/02/2025 | 11:17 | MC23 | MORDIALLOC | Urban | Planned |  | 42 | 7476 | 178 | 1 | No
| 154242 | 19/02/2025 | 9:44 | 19/02/2025 | 11:10 | NB34 | NORTH BRIGHTON | Urban | Planned |  | 51 | 4386 | 86 | 1 | No
| 154243 | 2025-05-03 | 8:03 | 2025-05-03 | 14:40 | M35 | MENTONE | Urban | Planned |  | 45 | 17865 | 397 | 1 | No
| 154247 | 19/02/2025 | 12:34 | 19/02/2025 | 14:07 | EL23 | ELSTERNWICK | Urban | Planned |  | 33 | 3069 | 93 | 1 | No
| 154256 | 17/02/2025 | 8:30 | 17/02/2025 | 15:30 | BU25 | BULLEEN | Urban | Planned |  | 156 | 65520 | 420 | 1 | No
| 154260 | 17/02/2025 | 20:00 | 18/02/2025 | 7:00 | WD14 | WEST DONCASTER | Urban | Planned |  | 14 | 9240 | 660 | 1 | No
| 154260 | 17/02/2025 | 20:00 | 18/02/2025 | 7:00 | WD34 | WEST DONCASTER | Urban | Planned |  | 51 | 33660 | 660 | 1 | No
| 154271 | 28/02/2025 | 11:30 | 28/02/2025 | 17:30 | DMA13 | DROMANA | Rural Short | Planned |  | 8 | 2880 | 360 | 1 | No
| 154275 | 28/02/2025 | 8:23 | 28/02/2025 | 9:12 | M25 | MENTONE | Urban | Planned |  | 2 | 98 | 49 | 1 | No
| 154278 | 20/02/2025 | 8:30 | 20/02/2025 | 14:51 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 23 | 8763 | 381 | 1 | No
| 154279 | 23/02/2025 | 8:36 | 23/02/2025 | 13:25 | EB11 | EAST BURWOOD | Urban | Planned |  | 3 | 867 | 289 | 1 | No
| 154280 | 20/02/2025 | 8:00 | 20/02/2025 | 20:02 | OAK35 | OAKLEIGH | Urban | Planned |  | 1 | 722 | 722 | 1 | No
| 154281 | 18/02/2025 | 8:35 | 18/02/2025 | 14:00 | BU11 | BULLEEN | Urban | Planned |  | 29 | 9425 | 325 | 1 | No
| 154282 | 20/02/2025 | 8:05 | 20/02/2025 | 11:59 | HGS22 | HASTINGS | Rural Short | Planned |  | 81 | 18954 | 234 | 1 | No
| 154283 | 2025-04-03 | 8:03 | 2025-04-03 | 10:55 | M25 | MENTONE | Urban | Planned |  | 44 | 7568 | 172 | 1 | No
| 154285 | 2025-02-03 | 7:45 | 2025-02-03 | 13:05 | DN2 | DANDENONG | Urban | Planned |  | 2 | 640 | 320 | 1 | No
| 154286 | 20/02/2025 | 12:24 | 20/02/2025 | 14:27 | FSH23 | FRANKSTON SOUTH | Rural Short | Planned |  | 50 | 6150 | 123 | 1 | No
| 154290 | 26/03/2025 | 8:15 | 26/03/2025 | 15:57 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 23 | 10626 | 462 | 1 | No
| 154296 | 21/02/2025 | 8:00 | 21/02/2025 | 14:10 | BU12 | BULLEEN | Urban | Planned |  | 216 | 79920 | 370 | 1 | No
| 154299 | 20/02/2025 | 8:50 | 20/02/2025 | 16:00 | BU11 | BULLEEN | Urban | Planned |  | 89 | 38270 | 430 | 1 | No
| 154300 | 19/02/2025 | 8:05 | 19/02/2025 | 12:21 | BU14 | BULLEEN | Urban | Planned |  | 73 | 18688 | 256 | 1 | No
| 154302 | 20/02/2025 | 8:00 | 20/02/2025 | 14:25 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 42 | 16170 | 385 | 1 | No
| 154303 | 24/02/2025 | 8:04 | 24/02/2025 | 14:21 | OR23 | ORMOND | Urban | Planned |  | 7 | 2639 | 377 | 1 | No
| 154319 | 28/02/2025 | 10:34 | 28/02/2025 | 11:55 | MC21 | MORDIALLOC | Urban | Planned |  | 63 | 5103 | 81 | 1 | No
| 154330 | 20/02/2025 | 9:02 | 20/02/2025 | 11:00 | NW32 | NUNAWADING | Urban | Planned |  | 129 | 15222 | 118 | 1 | No
| 154332 | 25/02/2025 | 9:01 | 25/02/2025 | 11:07 | NW33 | NUNAWADING | Urban | Planned |  | 3 | 378 | 126 | 1 | No
| 154339 | 21/02/2025 | 8:26 | 21/02/2025 | 13:27 | K34 | GARDINER | Urban | Planned |  | 47 | 14147 | 301 | 1 | No
| 154343 | 21/02/2025 | 13:05 | 21/02/2025 | 17:05 | HT4 | HEATHERTON | Urban | Planned |  | 35 | 8400 | 240 | 1 | No
| 154345 | 21/02/2025 | 8:50 | 21/02/2025 | 11:15 | BH22 | BOX HILL | Urban | Planned |  | 41 | 5945 | 145 | 1 | No
| 154345 | 21/02/2025 | 8:50 | 21/02/2025 | 11:15 | BH34 | BOX HILL | Urban | Planned |  | 7 | 1015 | 145 | 1 | No
| 154351 | 25/02/2025 | 9:30 | 25/02/2025 | 15:00 | BH11 | BOX HILL | Urban | Planned |  | 23 | 7590 | 330 | 1 | No
| 154353 | 25/02/2025 | 11:00 | 25/02/2025 | 13:47 | BU12 | BULLEEN | Urban | Planned |  | 28 | 4676 | 167 | 1 | No
| 154357 | 27/02/2025 | 9:30 | 27/02/2025 | 13:00 | EB32 | EAST BURWOOD | Urban | Planned |  | 32 | 6720 | 210 | 1 | No
| 154358 | 26/02/2025 | 8:00 | 26/02/2025 | 13:50 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 36 | 12600 | 350 | 1 | No
| 154359 | 26/02/2025 | 10:10 | 26/02/2025 | 14:40 | BH11 | BOX HILL | Urban | Planned |  | 29 | 7830 | 270 | 1 | No
| 154362 | 19/03/2025 | 8:00 | 19/03/2025 | 16:30 | DMA14 | DROMANA | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 154362 | 19/03/2025 | 9:10 | 19/03/2025 | 15:30 | DMA14 | DROMANA | Urban | Planned |  | 88 | 33440 | 380 | 1 | No
| 154364 | 2025-05-03 | 8:00 | 2025-05-03 | 14:00 | SVW41 | SPRINGVALE WEST | Urban | Planned |  | 3 | 1080 | 360 | 1 | No
| 154366 | 2025-06-03 | 9:09 | 2025-06-03 | 14:33 | DMA24 | DROMANA | Rural Short | Planned |  | 4 | 1296 | 324 | 1 | No
| 154367 | 2025-07-03 | 8:00 | 2025-07-03 | 12:28 | M11 | MENTONE | Urban | Planned |  | 77 | 20636 | 268 | 1 | No
| 154367 | 2025-07-03 | 8:00 | 2025-07-03 | 12:28 | M23 | MENTONE | Urban | Planned |  | 27 | 7236 | 268 | 1 | No
| 154368 | 2025-05-03 | 8:29 | 2025-05-03 | 13:06 | MTN35 | MORNINGTON | Rural Short | Planned |  | 102 | 28254 | 277 | 1 | No
| 154369 | 27/02/2025 | 8:30 | 27/02/2025 | 13:00 | DMA24 | DROMANA | Rural Short | Planned |  | 149 | 40230 | 270 | 1 | No
| 154373 | 20/02/2025 | 12:45 | 20/02/2025 | 13:15 | HT2 | HEATHERTON | Urban | Planned |  | 65 | 1950 | 30 | 1 | No
| 154376 | 24/02/2025 | 12:34 | 24/02/2025 | 14:25 | SVW54 | SPRINGVALE WEST | Urban | Planned |  | 137 | 15207 | 111 | 1 | No
| 154378 | 14/04/2025 | 8:40 | 14/04/2025 | 14:15 | BH12 | BOX HILL | Urban | Planned |  | 36 | 12060 | 335 | 1 | No
| 154385 | 13/03/2025 | 8:00 | 13/03/2025 | 15:00 | STO13 | SORRENTO | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 154385 | 13/03/2025 | 8:24 | 13/03/2025 | 12:41 | STO13 | SORRENTO | Urban | Planned |  | 37 | 9509 | 257 | 1 | No
| 154386 | 27/02/2025 | 8:06 | 27/02/2025 | 11:34 | LD3 | LYNDALE | Urban | Planned |  | 157 | 32656 | 208 | 1 | No
| 154388 | 2025-11-03 | 8:00 | 2025-11-03 | 14:30 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 1 | 390 | 390 | 1 | No
| 154388 | 2025-11-03 | 8:03 | 2025-11-03 | 12:14 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 114 | 28614 | 251 | 1 | No
| 154389 | 27/03/2025 | 8:10 | 27/03/2025 | 12:30 | EW9 | ELWOOD | Urban | Planned |  | 82 | 21320 | 260 | 1 | No
| 154394 | 2025-04-03 | 8:05 | 2025-04-03 | 15:14 | BU12 | BULLEEN | Urban | Planned |  | 133 | 57057 | 429 | 1 | No
| 154396 | 16/03/2025 | 8:15 | 16/03/2025 | 9:10 | HGS32 | HASTINGS | Urban | Planned |  | 1 | 55 | 55 | 1 | No
| 154397 | 26/03/2025 | 8:06 | 26/03/2025 | 10:50 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 12 | 1968 | 164 | 1 | No
| 154398 | 23/02/2025 | 8:01 | 23/02/2025 | 15:15 | SS14 | SPRINGVALE SOUTH | Urban | Planned |  | 489 | 212226 | 434 | 1 | No
| 154399 | 23/02/2025 | 7:40 | 23/02/2025 | 14:09 | DVY33 | DANDENONG VALLEY | Urban | Planned |  | 15 | 5835 | 389 | 1 | No
| 154403 | 2025-04-03 | 8:00 | 2025-04-03 | 10:38 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 46 | 7268 | 158 | 1 | No
| 154411 | 28/02/2025 | 8:27 | 28/02/2025 | 13:32 | GW6 | GLEN WAVERLEY | Urban | Planned |  | 74 | 22570 | 305 | 1 | No
| 154415 | 2025-03-03 | 9:45 | 2025-03-03 | 13:30 | LD6 | LYNDALE | Urban | Planned |  | 13 | 2925 | 225 | 1 | No
| 154417 | 25/02/2025 | 8:31 | 25/02/2025 | 18:15 | FTN21 | FRANKSTON | Urban | Planned |  | 42 | 24528 | 584 | 1 | No
| 154418 | 26/02/2025 | 8:39 | 26/02/2025 | 12:37 | STO21 | SORRENTO | Rural Short | Planned |  | 69 | 16422 | 238 | 1 | No
| 154420 | 2025-06-03 | 8:05 | 2025-06-03 | 15:53 | FSH21 | FRANKSTON SOUTH | Rural Short | Planned |  | 128 | 59904 | 468 | 1 | No
| 154421 | 2025-05-03 | 8:03 | 2025-05-03 | 15:40 | BU11 | BULLEEN | Urban | Planned |  | 45 | 20565 | 457 | 1 | No
| 154421 | 2025-05-03 | 8:03 | 2025-05-03 | 15:40 | BU12 | BULLEEN | Urban | Planned |  | 42 | 19194 | 457 | 1 | No
| 154422 | 28/02/2025 | 8:00 | 28/02/2025 | 11:50 | MTN22 | MORNINGTON | Rural Short | Planned |  | 89 | 20470 | 230 | 1 | No
| 154426 | 2025-02-02 | 7:41 | 2025-02-02 | 11:45 | NO2 | NOTTING HILL | Urban | Planned |  | 35 | 8540 | 244 | 1 | No
| 154427 | 25/02/2025 | 8:20 | 25/02/2025 | 13:49 | BU11 | BULLEEN | Urban | Planned |  | 52 | 17108 | 329 | 1 | No
| 154428 | 28/02/2025 | 8:35 | 28/02/2025 | 10:57 | LD33 | LYNDALE | Urban | Planned |  | 53 | 7526 | 142 | 1 | No
| 154429 | 27/02/2025 | 8:46 | 27/02/2025 | 11:18 | DMA24 | DROMANA | Rural Short | Planned |  | 33 | 5016 | 152 | 1 | No
| 154432 | 2025-04-03 | 8:48 | 2025-04-03 | 12:20 | BU14 | BULLEEN | Urban | Planned |  | 53 | 11236 | 212 | 1 | No
| 154433 | 2025-05-03 | 8:00 | 2025-05-03 | 16:30 | DN25 | DANDENONG | Urban | Planned |  | 82 | 41820 | 510 | 1 | No
| 154436 | 2025-07-03 | 8:40 | 2025-07-03 | 14:15 | BU15 | BULLEEN | Urban | Planned |  | 46 | 15410 | 335 | 1 | No
| 154447 | 27/02/2025 | 21:40 | 28/02/2025 | 1:56 | SK1 | ST. KILDA | Urban | Planned |  | 19 | 4864 | 256 | 1 | No
| 154465 | 2025-02-03 | 7:00 | 2025-02-03 | 19:43 | SVW45 | SPRINGVALE WEST | Urban | Planned |  | 1 | 763 | 763 | 1 | No
| 154469 | 27/03/2025 | 8:00 | 27/03/2025 | 10:30 | BU21 | BULLEEN | Urban | Planned |  | 20 | 3000 | 150 | 1 | No
| 154471 | 2025-12-03 | 8:12 | 2025-12-03 | 10:25 | RBD24 | ROSEBUD | Urban | Planned |  | 172 | 22876 | 133 | 1 | No
| 154472 | 14/03/2025 | 8:30 | 14/03/2025 | 12:40 | STO13 | SORRENTO | Urban | Planned |  | 24 | 6000 | 250 | 1 | No
| 154477 | 19/03/2025 | 8:53 | 19/03/2025 | 15:15 | RBD23 | ROSEBUD | Urban | Planned |  | 115 | 43930 | 382 | 1 | No
| 154479 | 19/03/2025 | 12:00 | 19/03/2025 | 13:55 | RBD23 | ROSEBUD | Urban | Planned |  | 4 | 460 | 115 | 1 | No
| 154480 | 24/03/2025 | 8:37 | 24/03/2025 | 12:53 | RBD24 | ROSEBUD | Urban | Planned |  | 19 | 4864 | 256 | 1 | No
| 154481 | 25/03/2025 | 8:07 | 25/03/2025 | 10:40 | RBD24 | ROSEBUD | Urban | Planned |  | 41 | 6273 | 153 | 1 | No
| 154483 | 2025-03-04 | 8:21 | 2025-03-04 | 10:50 | DMA21 | DROMANA | Urban | Planned |  | 66 | 9834 | 149 | 1 | No
| 154485 | 2025-04-04 | 8:10 | 2025-04-04 | 11:45 | DMA24 | DROMANA | Rural Short | Planned |  | 7 | 1505 | 215 | 1 | No
| 154486 | 2025-04-03 | 9:40 | 2025-04-03 | 14:50 | LD4 | LYNDALE | Urban | Planned |  | 5 | 1550 | 310 | 1 | No
| 154487 | 2025-09-04 | 8:05 | 2025-09-04 | 9:25 | DMA14 | DROMANA | Urban | Planned |  | 17 | 1360 | 80 | 1 | No
| 154488 | 2025-09-04 | 10:02 | 2025-09-04 | 12:10 | DMA14 | DROMANA | Urban | Planned |  | 38 | 4864 | 128 | 1 | No
| 154490 | 2025-04-03 | 8:00 | 2025-04-03 | 14:40 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 38 | 15200 | 400 | 1 | No
| 154493 | 2025-03-03 | 8:01 | 2025-03-03 | 15:40 | NP36 | NOBLE PARK | Urban | Planned |  | 95 | 43605 | 459 | 1 | No
| 154494 | 2025-09-03 | 7:00 | 2025-09-03 | 16:00 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 1 | 540 | 540 | 1 | No
| 154494 | 2025-09-03 | 7:43 | 2025-09-03 | 15:56 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 23 | 11339 | 493 | 1 | No
| 154495 | 2025-09-03 | 7:00 | 2025-09-03 | 18:00 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 1 | 660.3333 | 660.3333 | 1 | No
| 154497 | 2025-03-04 | 10:40 | 2025-03-04 | 13:00 | STO23 | SORRENTO | Urban | Planned |  | 1 | 140 | 140 | 1 | No
| 154498 | 18/03/2025 | 9:48 | 18/03/2025 | 16:19 | STO13 | SORRENTO | Urban | Planned |  | 108 | 42228 | 391 | 1 | No
| 154499 | 18/03/2025 | 12:55 | 18/03/2025 | 15:00 | STO13 | SORRENTO | Urban | Planned |  | 29 | 3625 | 125 | 1 | No
| 154500 | 18/03/2025 | 8:48 | 18/03/2025 | 11:38 | STO13 | SORRENTO | Urban | Planned |  | 32 | 5440 | 170 | 1 | No
| 154501 | 13/03/2025 | 9:53 | 13/03/2025 | 13:05 | DMA14 | DROMANA | Urban | Planned |  | 13 | 2496 | 192 | 1 | No
| 154502 | 2025-11-04 | 8:11 | 2025-11-04 | 10:25 | RBD24 | ROSEBUD | Urban | Planned |  | 18 | 2412 | 134 | 1 | No
| 154504 | 28/02/2025 | 8:26 | 28/02/2025 | 14:00 | HGS31 | HASTINGS | Rural Short | Planned |  | 181 | 60454 | 334 | 1 | No
| 154509 | 2025-05-03 | 8:00 | 2025-05-03 | 10:53 | M32 | MENTONE | Urban | Planned |  | 33 | 5709 | 173 | 1 | No
| 154512 | 2025-05-03 | 11:03 | 2025-05-03 | 13:28 | M32 | MENTONE | Urban | Planned |  | 36 | 5220 | 145 | 1 | No
| 154517 | 15/03/2025 | 8:10 | 15/03/2025 | 12:22 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 23 | 5796 | 252 | 1 | No
| 154518 | 27/02/2025 | 3:34 | 27/02/2025 | 6:07 | DVY31 | DANDENONG VALLEY | Urban | Planned |  | 2 | 306 | 153 | 1 | No
| 154520 | 28/02/2025 | 7:38 | 28/02/2025 | 11:07 | DC1 | DONCASTER | Urban | Planned |  | 10 | 2090 | 209 | 1 | No
| 154522 | 2025-04-05 | 8:00 | 2025-04-05 | 9:45 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 114 | 11916.7962 | 104.5333 | 1 | No
| 154524 | 27/04/2025 | 9:05 | 27/04/2025 | 14:06 | BT13 | BENTLEIGH | Urban | Planned |  | 115 | 34615 | 301 | 1 | No
| 154530 | 2025-04-03 | 4:32 | 2025-04-03 | 5:12 | SVW55 | SPRINGVALE WEST | Urban | Planned |  | 2 | 80 | 40 | 1 | No
| 154531 | 2025-04-03 | 0:53 | 2025-04-03 | 1:49 | NP12 | NOBLE PARK | Urban | Planned |  | 3 | 168 | 56 | 1 | No
| 154533 | 2025-05-03 | 9:10 | 2025-05-03 | 11:30 | FTN13 | FRANKSTON | Urban | Planned |  | 34 | 4760 | 140 | 1 | No
| 154535 | 2025-05-03 | 15:05 | 2025-05-03 | 16:55 | DMA13 | DROMANA | Rural Short | Planned |  | 2 | 220 | 110 | 1 | No
| 154541 | 2025-02-03 | 7:13 | 2025-02-03 | 11:53 | NO2 | NOTTING HILL | Urban | Planned |  | 23 | 6440 | 280 | 1 | No
| 154544 | 15/04/2025 | 8:04 | 15/04/2025 | 14:05 | GW10 | GLEN WAVERLEY | Urban | Planned |  | 23 | 8303 | 361 | 1 | No
| 154546 | 2025-04-03 | 9:00 | 2025-04-03 | 11:12 | M13 | MENTONE | Urban | Planned |  | 11 | 1452 | 132 | 1 | No
| 154547 | 2025-06-03 | 8:10 | 2025-06-03 | 10:36 | BR9 | BEAUMARIS | Urban | Planned |  | 77 | 11242 | 146 | 1 | No
| 154548 | 2025-01-03 | 9:18 | 2025-01-03 | 10:50 | NO2 | NOTTING HILL | Urban | Planned |  | 3 | 276 | 92 | 1 | No
| 154550 | 2025-02-03 | 8:10 | 2025-02-03 | 11:52 | HT6 | HEATHERTON | Urban | Planned |  | 4 | 888 | 222 | 1 | No
| 154552 | 2025-07-03 | 8:00 | 2025-07-03 | 15:00 | STO13 | SORRENTO | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 154552 | 2025-07-03 | 8:45 | 2025-07-03 | 12:35 | STO13 | SORRENTO | Urban | Planned |  | 16 | 3680 | 230 | 1 | No
| 154556 | 2025-06-03 | 8:01 | 2025-06-03 | 9:27 | CRM23 | CARRUM | Urban | Planned |  | 80 | 6880 | 86 | 1 | No
| 154557 | 2025-06-03 | 10:00 | 2025-06-03 | 11:04 | CRM23 | CARRUM | Urban | Planned |  | 75 | 4800 | 64 | 1 | No
| 154558 | 2025-06-03 | 12:02 | 2025-06-03 | 13:20 | CRM23 | CARRUM | Urban | Planned |  | 146 | 11388 | 78 | 1 | No
| 154559 | 2025-02-03 | 13:10 | 2025-02-03 | 16:00 | HT3 | HEATHERTON | Urban | Planned |  | 4 | 680 | 170 | 1 | No
| 154566 | 20/03/2025 | 8:00 | 20/03/2025 | 12:26 | BT14 | BENTLEIGH | Urban | Planned |  | 63 | 16758 | 266 | 1 | No
| 154566 | 20/03/2025 | 8:00 | 20/03/2025 | 12:26 | OR34 | ORMOND | Urban | Planned |  | 37 | 9842 | 266 | 1 | No
| 154568 | 28/02/2025 | 9:30 | 28/02/2025 | 10:40 | BU12 | BULLEEN | Urban | Planned |  | 3 | 210 | 70 | 1 | No
| 154573 | 2025-05-03 | 8:00 | 2025-05-03 | 10:30 | DC2 | DONCASTER | Urban | Planned |  | 14 | 2100 | 150 | 1 | No
| 154579 | 2025-12-03 | 9:00 | 2025-12-03 | 11:45 | MGE32 | MULGRAVE | Urban | Planned |  | 77 | 12705 | 165 | 1 | No
| 154583 | 21/03/2025 | 8:00 | 21/03/2025 | 11:30 | MTN32 | MORNINGTON | Rural Short | Planned |  | 3 | 630 | 210 | 1 | No
| 154586 | 2025-03-03 | 10:35 | 2025-03-03 | 15:27 | HGS33 | HASTINGS | Rural Short | Planned |  | 1 | 292 | 292 | 1 | No
| 154590 | 18/03/2025 | 11:35 | 18/03/2025 | 13:20 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 67 | 7035 | 105 | 1 | No
| 154593 | 2025-01-03 | 7:31 | 2025-01-03 | 12:25 | NO2 | NOTTING HILL | Urban | Planned |  | 36 | 10596.6 | 294.35 | 1 | No
| 154598 | 2025-05-03 | 22:35 | 2025-06-03 | 5:47 | SV32 | SPRINGVALE | Urban | Planned |  | 18 | 7776 | 432 | 1 | No
| 154602 | 14/03/2025 | 9:15 | 14/03/2025 | 11:51 | EW1 | ELWOOD | Urban | Planned |  | 28 | 4368 | 156 | 1 | No
| 154604 | 2025-12-03 | 9:10 | 2025-12-03 | 14:15 | BW34 | BURWOOD | Urban | Planned |  | 39 | 11895 | 305 | 1 | No
| 154606 | 2025-06-03 | 8:15 | 2025-06-03 | 10:38 | EB31 | EAST BURWOOD | Urban | Planned |  | 1 | 143 | 143 | 1 | No
| 154608 | 15/03/2025 | 6:06 | 15/03/2025 | 8:45 | DN7 | DANDENONG | Urban | Planned |  | 6 | 954 | 159 | 1 | No
| 154610 | 2025-03-03 | 9:46 | 2025-03-03 | 13:43 | NO7 | NOTTING HILL | Urban | Planned |  | 70 | 16590 | 237 | 1 | No
| 154618 | 2025-06-03 | 9:45 | 2025-06-03 | 11:50 | LD4 | LYNDALE | Urban | Planned |  | 40 | 5000 | 125 | 1 | No
| 154622 | 2025-06-03 | 14:35 | 2025-06-03 | 14:55 | LD4 | LYNDALE | Urban | Planned |  | 30 | 600 | 20 | 1 | No
| 154625 | 2025-05-03 | 8:10 | 2025-05-03 | 13:57 | BU14 | BULLEEN | Urban | Planned |  | 102 | 35394 | 347 | 1 | No
| 154628 | 18/03/2025 | 8:00 | 18/03/2025 | 14:10 | MC12 | MORDIALLOC | Urban | Planned |  | 118 | 43660 | 370 | 1 | No
| 154628 | 18/03/2025 | 8:00 | 18/03/2025 | 14:10 | MC21 | MORDIALLOC | Urban | Planned |  | 68 | 25160 | 370 | 1 | No
| 154628 | 18/03/2025 | 8:00 | 18/03/2025 | 14:10 | MC23 | MORDIALLOC | Urban | Planned |  | 12 | 4440 | 370 | 1 | No
| 154632 | 2025-11-03 | 8:05 | 2025-11-03 | 14:10 | BT12 | BENTLEIGH | Urban | Planned |  | 193 | 70445 | 365 | 1 | No
| 154633 | 18/02/2025 | 7:10 | 18/02/2025 | 11:00 | MC31 | MORDIALLOC | Urban | Planned |  | 1 | 230 | 230 | 1 | No
| 154639 | 23/03/2025 | 7:45 | 23/03/2025 | 15:20 | SVW42 | SPRINGVALE WEST | Urban | Planned |  | 19 | 8645 | 455 | 1 | No
| 154640 | 14/03/2025 | 8:00 | 14/03/2025 | 15:30 | RBD21 | ROSEBUD | Rural Short | Planned |  | 1 | 450 | 450 | 1 | No
| 154640 | 14/03/2025 | 8:45 | 14/03/2025 | 12:55 | RBD21 | ROSEBUD | Rural Short | Planned |  | 35 | 8750 | 250 | 1 | No
| 154642 | 13/03/2025 | 8:30 | 13/03/2025 | 17:25 | CRM22 | CARRUM | Urban | Planned |  | 23 | 12305 | 535 | 1 | No
| 154651 | 2025-06-03 | 8:45 | 2025-06-03 | 12:45 | OE9 | OAKLEIGH EAST | Urban | Planned |  | 29 | 6960 | 240 | 1 | No
| 154652 | 2025-06-03 | 11:10 | 2025-06-03 | 14:09 | OE4 | OAKLEIGH EAST | Urban | Planned |  | 21 | 3759 | 179 | 1 | No
| 154674 | 2025-09-03 | 8:19 | 2025-09-03 | 14:30 | HT3 | HEATHERTON | Urban | Planned |  | 23 | 8533 | 371 | 1 | No
| 154674 | 2025-09-03 | 8:19 | 2025-09-03 | 14:30 | HT9 | HEATHERTON | Urban | Planned |  | 20 | 7420 | 371 | 1 | No
| 154680 | 18/03/2025 | 8:10 | 18/03/2025 | 11:40 | BU14 | BULLEEN | Urban | Planned |  | 26 | 5460 | 210 | 1 | No
| 154681 | 16/03/2025 | 8:00 | 16/03/2025 | 13:35 | DVY22 | DANDENONG VALLEY | Urban | Planned |  | 18 | 6030 | 335 | 1 | No
| 154682 | 2025-06-03 | 8:30 | 2025-06-03 | 11:20 | STO21 | SORRENTO | Rural Short | Planned |  | 21 | 3570 | 170 | 1 | No
| 154683 | 2025-11-03 | 8:13 | 2025-11-03 | 12:50 | MR13 | MOORABBIN | Urban | Planned |  | 6 | 1662 | 277 | 1 | No
| 154692 | 2025-06-03 | 11:30 | 2025-06-03 | 16:00 | STO14 | SORRENTO | Rural Short | Planned |  | 1 | 270 | 270 | 1 | No
| 154692 | 2025-06-03 | 12:10 | 2025-06-03 | 14:05 | STO14 | SORRENTO | Rural Short | Planned |  | 86 | 9890 | 115 | 1 | No
| 154694 | 13/03/2025 | 8:46 | 13/03/2025 | 16:00 | BU15 | BULLEEN | Urban | Planned |  | 34 | 14756 | 434 | 1 | No
| 154694 | 13/03/2025 | 8:46 | 13/03/2025 | 16:00 | BU21 | BULLEEN | Urban | Planned |  | 24 | 10416 | 434 | 1 | No
| 154697 | 13/03/2025 | 8:50 | 13/03/2025 | 13:00 | MGE23 | MULGRAVE | Urban | Planned |  | 20 | 5000 | 250 | 1 | No
| 154698 | 2025-01-04 | 9:40 | 2025-01-04 | 14:57 | EB12 | EAST BURWOOD | Urban | Planned |  | 5 | 1585 | 317 | 1 | No
| 154703 | 2025-08-04 | 7:20 | 2025-08-04 | 15:50 | BT25 | BENTLEIGH | Urban | Planned |  | 10 | 5100 | 510 | 1 | No
| 154705 | 30/04/2025 | 8:03 | 30/04/2025 | 13:35 | MTN32 | MORNINGTON | Rural Short | Planned |  | 13 | 4316 | 332 | 1 | No
| 154706 | 2025-11-03 | 8:00 | 2025-11-03 | 10:01 | CRM23 | CARRUM | Urban | Planned |  | 59 | 7130.15 | 120.85 | 1 | No
| 154710 | 2025-01-04 | 8:18 | 2025-01-04 | 14:05 | FTN25 | FRANKSTON | Urban | Planned |  | 23 | 7981 | 347 | 1 | No
| 154712 | 2025-07-03 | 8:37 | 2025-07-03 | 9:49 | EB33 | EAST BURWOOD | Urban | Planned |  | 18 | 1296 | 72 | 1 | No
| 154715 | 26/03/2025 | 8:05 | 26/03/2025 | 15:28 | BU14 | BULLEEN | Urban | Planned |  | 121 | 53603 | 443 | 1 | No
| 154715 | 26/03/2025 | 8:05 | 26/03/2025 | 15:28 | BU15 | BULLEEN | Urban | Planned |  | 40 | 17720 | 443 | 1 | No
| 154726 | 14/03/2025 | 8:00 | 14/03/2025 | 14:00 | BU11 | BULLEEN | Urban | Planned |  | 28 | 10080 | 360 | 1 | No
| 154727 | 2025-12-03 | 8:10 | 2025-12-03 | 13:59 | NB25 | NORTH BRIGHTON | Urban | Planned |  | 191 | 66659 | 349 | 1 | No
| 154735 | 2025-12-03 | 8:03 | 2025-12-03 | 10:53 | MR31 | MOORABBIN | Urban | Planned |  | 33 | 5610 | 170 | 1 | No
| 154736 | 2025-12-03 | 10:15 | 2025-12-03 | 12:15 | MR31 | MOORABBIN | Urban | Planned |  | 29 | 3480 | 120 | 1 | No
| 154748 | 2025-12-03 | 11:44 | 2025-12-03 | 13:15 | MR21 | MOORABBIN | Urban | Planned |  | 35 | 3185 | 91 | 1 | No
| 154750 | 19/03/2025 | 8:00 | 19/03/2025 | 15:30 | HGS31 | HASTINGS | Rural Short | Planned |  | 33 | 14850 | 450 | 1 | No
| 154752 | 19/03/2025 | 20:46 | 20/03/2025 | 1:40 | MC21 | MORDIALLOC | Urban | Planned |  | 54 | 15876 | 294 | 1 | No
| 154754 | 2025-12-03 | 8:01 | 2025-12-03 | 15:31 | STO13 | SORRENTO | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 154754 | 2025-12-03 | 8:32 | 2025-12-03 | 12:41 | STO13 | SORRENTO | Urban | Planned |  | 32 | 7968 | 249 | 1 | No
| 154758 | 2025-12-03 | 8:02 | 2025-12-03 | 14:00 | LD32 | LYNDALE | Urban | Planned |  | 12 | 4296 | 358 | 1 | No
| 154760 | 22/03/2025 | 7:10 | 22/03/2025 | 18:15 | SV23 | SPRINGVALE | Urban | Planned |  | 18 | 11970 | 665 | 1 | No
| 154761 | 2025-12-03 | 8:00 | 2025-12-03 | 9:50 | MR31 | MOORABBIN | Urban | Planned |  | 21 | 2310 | 110 | 1 | No
| 154761 | 2025-12-03 | 8:00 | 2025-12-03 | 9:50 | NB36 | NORTH BRIGHTON | Urban | Planned |  | 3 | 330 | 110 | 1 | No
| 154763 | 2025-12-03 | 8:55 | 2025-12-03 | 13:00 | CFD14 | CAULFIELD | Urban | Planned |  | 48 | 11760 | 245 | 1 | No
| 154766 | 18/03/2025 | 8:40 | 18/03/2025 | 11:20 | BU14 | BULLEEN | Urban | Planned |  | 50 | 8000 | 160 | 1 | No
| 154767 | 23/03/2025 | 8:00 | 23/03/2025 | 15:00 | NW22 | NUNAWADING | Urban | Planned |  | 260 | 109117.658 | 419.6833 | 1 | No
| 154773 | 22/03/2025 | 8:00 | 22/03/2025 | 16:55 | BW34 | BURWOOD | Urban | Planned |  | 1 | 534.8 | 534.8 | 1 | No
| 154775 | 18/03/2025 | 12:30 | 18/03/2025 | 14:25 | BU11 | BULLEEN | Urban | Planned |  | 19 | 2185 | 115 | 1 | No
| 154777 | 14/03/2025 | 8:00 | 14/03/2025 | 16:00 | MGE23 | MULGRAVE | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 154777 | 14/03/2025 | 8:30 | 14/03/2025 | 12:00 | MGE23 | MULGRAVE | Urban | Planned |  | 72 | 15120 | 210 | 1 | No
| 154780 | 16/03/2025 | 8:50 | 16/03/2025 | 9:34 | KBH35 | KEYSBOROUGH | Urban | Planned |  | 18 | 792 | 44 | 1 | No
| 154784 | 13/03/2025 | 8:05 | 13/03/2025 | 11:10 | MR22 | MOORABBIN | Urban | Planned |  | 35 | 6475 | 185 | 1 | No
| 154786 | 2025-12-03 | 8:12 | 2025-12-03 | 16:25 | DVY31 | DANDENONG VALLEY | Urban | Planned |  | 2 | 986 | 493 | 1 | No
| 154789 | 13/03/2025 | 12:10 | 13/03/2025 | 13:55 | SR26 | SANDRINGHAM | Urban | Planned |  | 7 | 735 | 105 | 1 | No
| 154790 | 13/03/2025 | 2:30 | 13/03/2025 | 5:30 | DN24 | DANDENONG | Urban | Planned |  | 1 | 180 | 180 | 1 | No
| 154790 | 13/03/2025 | 2:56 | 13/03/2025 | 4:28 | DN24 | DANDENONG | Urban | Planned |  | 49 | 4508 | 92 | 1 | No
| 154797 | 20/03/2025 | 6:00 | 20/03/2025 | 8:10 | RBD21 | ROSEBUD | Rural Short | Planned |  | 10 | 1300 | 130 | 1 | No
| 154800 | 20/03/2025 | 21:00 | 21/03/2025 | 1:15 | MC12 | MORDIALLOC | Urban | Planned |  | 7 | 1785 | 255 | 1 | No
| 154806 | 26/03/2025 | 8:00 | 26/03/2025 | 16:30 | DMA13 | DROMANA | Rural Short | Planned |  | 1 | 510 | 510 | 1 | No
| 154806 | 26/03/2025 | 8:06 | 26/03/2025 | 14:45 | DMA13 | DROMANA | Rural Short | Planned |  | 259 | 103341 | 399 | 1 | No
| 154809 | 28/03/2025 | 8:35 | 28/03/2025 | 13:10 | BU12 | BULLEEN | Urban | Planned |  | 76 | 20900 | 275 | 1 | No
| 154814 | 2025-01-04 | 8:00 | 2025-01-04 | 16:30 | BU15 | BULLEEN | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 154814 | 2025-01-04 | 8:53 | 2025-01-04 | 14:45 | BU15 | BULLEEN | Urban | Planned |  | 101 | 35552 | 352 | 1 | No
| 154815 | 27/03/2025 | 9:30 | 27/03/2025 | 11:22 | STO21 | SORRENTO | Rural Short | Planned |  | 2 | 224 | 112 | 1 | No
| 154817 | 19/03/2025 | 10:25 | 19/03/2025 | 16:00 | MGE23 | MULGRAVE | Urban | Planned |  | 31 | 10385 | 335 | 1 | No
| 154818 | 2025-04-04 | 8:30 | 2025-04-04 | 12:40 | GW11 | GLEN WAVERLEY | Urban | Planned |  | 42 | 10500 | 250 | 2 | No
| 154818 | 2025-04-04 | 8:30 | 2025-04-04 | 15:30 | GW11 | GLEN WAVERLEY | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 154819 | 27/03/2025 | 11:00 | 27/03/2025 | 15:30 | STO21 | SORRENTO | Rural Short | Planned |  | 1 | 270 | 270 | 1 | No
| 154819 | 27/03/2025 | 11:55 | 27/03/2025 | 13:20 | STO21 | SORRENTO | Rural Short | Planned |  | 24 | 2040 | 85 | 1 | No
| 154821 | 2025-02-04 | 8:45 | 2025-02-04 | 14:45 | BU15 | BULLEEN | Urban | Planned |  | 93 | 33480 | 360 | 1 | No
| 154832 | 13/03/2025 | 8:40 | 13/03/2025 | 15:20 | EB22 | EAST BURWOOD | Urban | Planned |  | 130 | 52000 | 400 | 1 | No
| 154834 | 13/03/2025 | 8:15 | 13/03/2025 | 14:50 | BU14 | BULLEEN | Urban | Planned |  | 6 | 2370 | 395 | 1 | No
| 154836 | 2025-11-03 | 21:31 | 2025-12-03 | 2:30 | LD5 | LYNDALE | Urban | Planned |  | 5 | 1495 | 299 | 1 | No
| 154844 | 21/03/2025 | 8:34 | 21/03/2025 | 14:45 | FTN12 | FRANKSTON | Urban | Planned |  | 106 | 39326 | 371 | 1 | No
| 154855 | 18/03/2025 | 8:05 | 18/03/2025 | 11:50 | MC12 | MORDIALLOC | Urban | Planned |  | 18 | 4050 | 225 | 1 | No
| 154857 | 15/03/2025 | 8:00 | 15/03/2025 | 17:00 | WD26 | WEST DONCASTER | Urban | Planned |  | 25 | 13492.0825 | 539.6833 | 1 | No
| 154859 | 18/03/2025 | 10:50 | 18/03/2025 | 14:38 | MC12 | MORDIALLOC | Urban | Planned |  | 26 | 5928 | 228 | 1 | No
| 154868 | 20/03/2025 | 3:42 | 20/03/2025 | 4:49 | CRM34 | CARRUM | Urban | Planned |  | 21 | 1407 | 67 | 1 | No
| 154872 | 13/03/2025 | 8:45 | 13/03/2025 | 13:10 | HGS22 | HASTINGS | Rural Short | Planned |  | 62 | 16430 | 265 | 1 | No
| 154875 | 2025-06-04 | 6:50 | 2025-06-04 | 13:14 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 18 | 6912 | 384 | 1 | No
| 154876 | 13/03/2025 | 8:13 | 13/03/2025 | 12:45 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 8 | 2176 | 272 | 1 | No
| 154883 | 14/03/2025 | 8:15 | 14/03/2025 | 10:50 | RBD23 | ROSEBUD | Urban | Planned |  | 30 | 4650 | 155 | 1 | No
| 154885 | 14/03/2025 | 11:00 | 14/03/2025 | 13:45 | RBD23 | ROSEBUD | Urban | Planned |  | 10 | 1650 | 165 | 1 | No
| 154886 | 2025-01-04 | 9:50 | 2025-01-04 | 15:30 | EL34 | ELSTERNWICK | Urban | Planned |  | 68 | 23120 | 340 | 1 | No
| 154888 | 30/03/2025 | 8:00 | 30/03/2025 | 15:10 | MC21 | MORDIALLOC | Urban | Planned |  | 11 | 4730 | 430 | 1 | No
| 154890 | 20/03/2025 | 8:13 | 20/03/2025 | 15:25 | DMA23 | DROMANA | Rural Short | Planned |  | 148 | 63936 | 432 | 1 | No
| 154895 | 17/03/2025 | 8:26 | 17/03/2025 | 11:14 | MTN34 | MORNINGTON | Urban | Planned |  | 14 | 2352 | 168 | 1 | No
| 154896 | 15/03/2025 | 9:50 | 15/03/2025 | 11:57 | DN4 | DANDENONG | Urban | Planned |  | 2 | 254 | 127 | 1 | No
| 154900 | 18/03/2025 | 21:38 | 19/03/2025 | 5:45 | NW23 | NUNAWADING | Urban | Planned |  | 17 | 8279 | 487 | 1 | No
| 154903 | 20/03/2025 | 8:00 | 20/03/2025 | 9:30 | MTN22 | MORNINGTON | Rural Short | Planned |  | 1 | 90 | 90 | 1 | No
| 154904 | 14/03/2025 | 8:02 | 14/03/2025 | 13:55 | LD4 | LYNDALE | Urban | Planned |  | 65 | 22945 | 353 | 1 | No
| 154905 | 14/03/2025 | 8:00 | 14/03/2025 | 8:50 | LD3 | LYNDALE | Urban | Planned |  | 39 | 1950 | 50 | 1 | No
| 154910 | 14/03/2025 | 8:05 | 14/03/2025 | 10:30 | BU14 | BULLEEN | Urban | Planned |  | 37 | 5365 | 145 | 1 | No
| 154911 | 14/03/2025 | 11:00 | 14/03/2025 | 13:55 | BU22 | BULLEEN | Urban | Planned |  | 51 | 8925 | 175 | 1 | No
| 154923 | 18/03/2025 | 8:30 | 18/03/2025 | 10:35 | DMA14 | DROMANA | Urban | Planned |  | 54 | 6750 | 125 | 1 | No
| 154924 | 18/03/2025 | 11:10 | 18/03/2025 | 14:15 | RBD13 | ROSEBUD | Urban | Planned |  | 24 | 4440 | 185 | 1 | No
| 154925 | 2025-04-04 | 11:58 | 2025-04-04 | 14:33 | BU22 | BULLEEN | Urban | Planned |  | 53 | 8215 | 155 | 1 | No
| 154926 | 2025-04-04 | 8:59 | 2025-04-04 | 10:58 | WD16 | WEST DONCASTER | Urban | Planned |  | 62 | 7378 | 119 | 1 | No
| 154928 | 25/03/2025 | 8:00 | 25/03/2025 | 16:00 | BU14 | BULLEEN | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 154928 | 25/03/2025 | 8:10 | 25/03/2025 | 14:00 | BU14 | BULLEEN | Urban | Planned |  | 110 | 38500 | 350 | 1 | No
| 154929 | 2025-05-04 | 7:50 | 2025-05-04 | 9:15 | NO5 | NOTTING HILL | Urban | Planned |  | 10 | 850 | 85 | 1 | No
| 154930 | 25/03/2025 | 8:40 | 25/03/2025 | 14:15 | BU14 | BULLEEN | Urban | Planned |  | 43 | 14405 | 335 | 1 | No
| 154930 | 25/03/2025 | 8:40 | 25/03/2025 | 14:15 | BU15 | BULLEEN | Urban | Planned |  | 10 | 3350 | 335 | 1 | No
| 154931 | 2025-05-04 | 11:30 | 2025-05-04 | 12:45 | NO5 | NOTTING HILL | Urban | Planned |  | 1 | 75 | 75 | 1 | No
| 154935 | 20/03/2025 | 0:35 | 20/03/2025 | 4:04 | MC31 | MORDIALLOC | Urban | Planned |  | 30 | 6270 | 209 | 1 | No
| 154936 | 29/03/2025 | 7:02 | 29/03/2025 | 10:27 | CRM34 | CARRUM | Urban | Planned |  | 9 | 1845 | 205 | 1 | No
| 154938 | 19/03/2025 | 8:00 | 19/03/2025 | 9:57 | DSH34 | DANDENONG SOUTH | Urban | Planned |  | 64 | 7488 | 117 | 1 | No
| 154940 | 23/03/2025 | 8:00 | 23/03/2025 | 9:50 | MR23 | MOORABBIN | Urban | Planned |  | 38 | 4180 | 110 | 1 | No
| 154941 | 23/03/2025 | 11:10 | 23/03/2025 | 12:10 | MR22 | MOORABBIN | Urban | Planned |  | 73 | 4380 | 60 | 1 | No
| 154946 | 30/03/2025 | 8:12 | 30/03/2025 | 15:30 | CFD12 | CAULFIELD | Urban | Planned |  | 31 | 13578 | 438 | 1 | No
| 154947 | 16/03/2025 | 8:01 | 16/03/2025 | 15:31 | NW11 | NUNAWADING | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 154947 | 16/03/2025 | 8:47 | 16/03/2025 | 11:38 | NW11 | NUNAWADING | Urban | Planned |  | 130 | 22230 | 171 | 1 | No
| 154948 | 16/03/2025 | 10:30 | 16/03/2025 | 15:05 | NW32 | NUNAWADING | Urban | Planned |  | 13 | 3575 | 275 | 1 | No
| 154951 | 20/03/2025 | 8:00 | 20/03/2025 | 12:40 | DMA14 | DROMANA | Urban | Planned |  | 22 | 6151.2 | 279.6 | 1 | No
| 154957 | 20/03/2025 | 8:00 | 20/03/2025 | 15:30 | MC23 | MORDIALLOC | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 154957 | 20/03/2025 | 8:01 | 20/03/2025 | 11:22 | MC23 | MORDIALLOC | Urban | Planned |  | 87 | 17487 | 201 | 1 | No
| 154958 | 20/03/2025 | 8:15 | 20/03/2025 | 11:20 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 48 | 8880 | 185 | 1 | No
| 154959 | 14/03/2025 | 12:00 | 14/03/2025 | 14:40 | MC12 | MORDIALLOC | Urban | Planned |  | 20 | 3196.334 | 159.8167 | 1 | No
| 154960 | 14/03/2025 | 10:25 | 14/03/2025 | 12:42 | MC12 | MORDIALLOC | Urban | Planned |  | 17 | 2329 | 137 | 1 | No
| 154961 | 14/03/2025 | 8:00 | 14/03/2025 | 9:30 | CRM35 | CARRUM | Urban | Planned |  | 32 | 2880 | 90 | 1 | No
| 154962 | 28/03/2025 | 9:12 | 28/03/2025 | 11:42 | CFD26 | CAULFIELD | Urban | Planned |  | 89 | 13350 | 150 | 1 | No
| 154964 | 16/03/2025 | 8:00 | 16/03/2025 | 16:15 | BC12 | BALACLAVA | Urban | Planned |  | 38 | 18810 | 495 | 1 | No
| 154974 | 22/03/2025 | 8:05 | 22/03/2025 | 13:30 | FSH11 | FRANKSTON SOUTH | Urban | Planned |  | 60 | 19500 | 325 | 1 | No
| 154983 | 17/03/2025 | 10:08 | 17/03/2025 | 15:30 | MGE23 | MULGRAVE | Urban | Planned |  | 19 | 6118 | 322 | 1 | No
| 154986 | 2025-06-05 | 20:10 | 2025-07-05 | 2:45 | CDA23 | CLARINDA | Urban | Planned |  | 3 | 1185 | 395 | 1 | No
| 154989 | 19/03/2025 | 8:48 | 19/03/2025 | 13:00 | SV34 | SPRINGVALE | Urban | Planned |  | 14 | 3528 | 252 | 1 | No
| 154994 | 23/03/2025 | 7:30 | 23/03/2025 | 15:58 | M21 | MENTONE | Urban | Planned |  | 12 | 6096 | 508 | 1 | No
| 154994 | 23/03/2025 | 7:30 | 23/03/2025 | 15:58 | M34 | MENTONE | Urban | Planned |  | 39 | 19812 | 508 | 1 | No
| 154995 | 21/03/2025 | 8:40 | 21/03/2025 | 11:09 | OR25 | ORMOND | Urban | Planned |  | 21 | 3129 | 149 | 1 | No
| 154996 | 15/03/2025 | 8:01 | 15/03/2025 | 10:01 | K35 | GARDINER | Urban | Planned |  | 4 | 480.6668 | 120.1667 | 1 | No
| 154997 | 19/03/2025 | 8:16 | 19/03/2025 | 14:05 | LD2 | LYNDALE | Urban | Planned |  | 22 | 7678 | 349 | 1 | No
| 155003 | 22/03/2025 | 8:04 | 22/03/2025 | 9:40 | MC31 | MORDIALLOC | Urban | Planned |  | 16 | 1536 | 96 | 1 | No
| 155005 | 22/03/2025 | 10:40 | 22/03/2025 | 12:18 | MC34 | MORDIALLOC | Urban | Planned |  | 8 | 784 | 98 | 1 | No
| 155012 | 20/03/2025 | 8:05 | 20/03/2025 | 15:40 | BR13 | BEAUMARIS | Urban | Planned |  | 48 | 21840 | 455 | 1 | No
| 155021 | 22/03/2025 | 10:04 | 22/03/2025 | 12:57 | MC31 | MORDIALLOC | Urban | Planned |  | 8 | 1384 | 173 | 1 | No
| 155021 | 22/03/2025 | 10:04 | 22/03/2025 | 12:57 | MC34 | MORDIALLOC | Urban | Planned |  | 9 | 1557 | 173 | 1 | No
| 155029 | 20/03/2025 | 8:10 | 20/03/2025 | 13:55 | SH22 | SURREY HILLS | Urban | Planned |  | 68 | 23460 | 345 | 1 | No
| 155033 | 2025-10-04 | 8:47 | 2025-10-04 | 12:12 | MC12 | MORDIALLOC | Urban | Planned |  | 113 | 23165 | 205 | 1 | No
| 155035 | 20/03/2025 | 10:20 | 20/03/2025 | 12:00 | RBD21 | ROSEBUD | Rural Short | Planned |  | 33 | 3300 | 100 | 1 | No
| 155040 | 21/03/2025 | 8:20 | 21/03/2025 | 10:10 | NP34 | NOBLE PARK | Urban | Planned |  | 2 | 220 | 110 | 1 | No
| 155041 | 27/03/2025 | 8:10 | 27/03/2025 | 14:15 | NO31 | NOTTING HILL | Urban | Planned |  | 26 | 9490 | 365 | 1 | No
| 155042 | 21/03/2025 | 8:30 | 21/03/2025 | 16:30 | BR10 | BEAUMARIS | Urban | Planned |  | 98 | 47040 | 480 | 1 | No
| 155043 | 21/03/2025 | 9:30 | 21/03/2025 | 13:35 | CFD22 | CAULFIELD | Urban | Planned |  | 94 | 23030 | 245 | 1 | No
| 155047 | 2025-02-04 | 8:00 | 2025-02-04 | 16:00 | BU22 | BULLEEN | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 155047 | 2025-02-04 | 8:38 | 2025-02-04 | 14:36 | BU22 | BULLEEN | Urban | Planned |  | 82 | 29356 | 358 | 1 | No
| 155053 | 21/03/2025 | 8:30 | 21/03/2025 | 16:30 | MR33 | MOORABBIN | Urban | Planned |  | 50 | 24000 | 480 | 1 | No
| 155057 | 25/03/2025 | 10:20 | 25/03/2025 | 13:50 | MTN31 | MORNINGTON | Urban | Planned |  | 4 | 840 | 210 | 1 | No
| 155059 | 27/03/2025 | 8:50 | 27/03/2025 | 14:57 | STO23 | SORRENTO | Urban | Planned |  | 71 | 26057 | 367 | 1 | No
| 155062 | 21/03/2025 | 8:35 | 21/03/2025 | 13:15 | MGE13 | MULGRAVE | Urban | Planned |  | 51 | 14280 | 280 | 1 | No
| 155065 | 27/03/2025 | 9:39 | 27/03/2025 | 11:43 | SR26 | SANDRINGHAM | Urban | Planned |  | 36 | 4464 | 124 | 1 | No
| 155066 | 30/03/2025 | 7:30 | 30/03/2025 | 16:30 | SV32 | SPRINGVALE | Urban | Planned |  | 1 | 540 | 540 | 1 | No
| 155066 | 30/03/2025 | 8:51 | 30/03/2025 | 17:55 | SV32 | SPRINGVALE | Urban | Planned |  | 123 | 66912 | 544 | 1 | No
| 155068 | 28/03/2025 | 5:00 | 28/03/2025 | 6:23 | CDA11 | CLARINDA | Urban | Planned |  | 1 | 83 | 83 | 1 | No
| 155069 | 26/03/2025 | 9:15 | 26/03/2025 | 12:00 | FSH11 | FRANKSTON SOUTH | Urban | Planned |  | 9 | 1485 | 165 | 1 | No
| 155072 | 26/03/2025 | 13:01 | 26/03/2025 | 15:40 | FSH11 | FRANKSTON SOUTH | Urban | Planned |  | 194 | 30846 | 159 | 1 | No
| 155074 | 18/03/2025 | 23:07 | 19/03/2025 | 4:45 | SVW55 | SPRINGVALE WEST | Urban | Planned |  | 2 | 676 | 338 | 1 | No
| 155078 | 26/03/2025 | 8:50 | 26/03/2025 | 12:12 | WD23 | WEST DONCASTER | Urban | Planned |  | 25 | 5050 | 202 | 1 | No
| 155079 | 26/03/2025 | 13:12 | 26/03/2025 | 14:30 | DC10 | DONCASTER | Urban | Planned |  | 2 | 156 | 78 | 1 | No
| 155083 | 29/04/2025 | 8:00 | 29/04/2025 | 11:50 | OE4 | OAKLEIGH EAST | Urban | Planned |  | 39 | 8970 | 230 | 1 | No
| 155086 | 25/03/2025 | 8:01 | 25/03/2025 | 9:43 | M11 | MENTONE | Urban | Planned |  | 58 | 5916 | 102 | 1 | No
| 155090 | 25/03/2025 | 8:55 | 25/03/2025 | 17:55 | WD26 | WEST DONCASTER | Urban | Planned |  | 61 | 32940 | 540 | 1 | No
| 155094 | 2025-02-04 | 8:02 | 2025-02-04 | 14:30 | DMA21 | DROMANA | Urban | Planned |  | 118 | 45784 | 388 | 1 | No
| 155096 | 31/03/2025 | 8:38 | 31/03/2025 | 14:10 | LWN24 | LANGWARRIN | Urban | Planned |  | 52 | 17264 | 332 | 1 | No
| 155099 | 26/03/2025 | 9:05 | 26/03/2025 | 11:20 | WD23 | WEST DONCASTER | Urban | Planned |  | 12 | 1620 | 135 | 1 | No
| 155100 | 26/03/2025 | 12:25 | 26/03/2025 | 15:12 | WD15 | WEST DONCASTER | Urban | Planned |  | 60 | 10020 | 167 | 1 | No
| 155102 | 29/04/2025 | 8:33 | 29/04/2025 | 10:22 | DC8 | DONCASTER | Urban | Planned |  | 47 | 5123 | 109 | 1 | No
| 155106 | 29/04/2025 | 10:37 | 29/04/2025 | 13:52 | DC8 | DONCASTER | Urban | Planned |  | 104 | 20280 | 195 | 1 | No
| 155113 | 2025-08-04 | 8:53 | 2025-08-04 | 14:24 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 71 | 23501 | 331 | 1 | No
| 155116 | 25/03/2025 | 8:00 | 25/03/2025 | 15:30 | MC23 | MORDIALLOC | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 155116 | 25/03/2025 | 8:15 | 25/03/2025 | 13:55 | MC23 | MORDIALLOC | Urban | Planned |  | 81 | 27540 | 340 | 1 | No
| 155121 | 25/03/2025 | 11:30 | 25/03/2025 | 13:05 | M11 | MENTONE | Urban | Planned |  | 9 | 855 | 95 | 1 | No
| 155131 | 15/04/2025 | 8:33 | 15/04/2025 | 12:30 | DMA14 | DROMANA | Urban | Planned |  | 45 | 10665 | 237 | 1 | No
| 155134 | 22/04/2025 | 10:00 | 22/04/2025 | 11:40 | STO14 | SORRENTO | Rural Short | Planned |  | 17 | 1700 | 100 | 1 | No
| 155136 | 29/04/2025 | 8:40 | 29/04/2025 | 10:35 | DMA14 | DROMANA | Urban | Planned |  | 40 | 4600 | 115 | 1 | No
| 155138 | 16/04/2025 | 8:03 | 16/04/2025 | 10:00 | M35 | MENTONE | Urban | Planned |  | 65 | 7605 | 117 | 1 | No
| 155139 | 23/04/2025 | 7:40 | 23/04/2025 | 10:48 | SS13 | SPRINGVALE SOUTH | Urban | Planned |  | 2 | 376 | 188 | 1 | No
| 155142 | 2025-10-04 | 8:30 | 2025-10-04 | 13:30 | GW4 | GLEN WAVERLEY | Urban | Planned |  | 56 | 16800 | 300 | 1 | No
| 155144 | 27/04/2025 | 7:39 | 27/04/2025 | 10:55 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 104 | 20384 | 196 | 1 | No
| 155145 | 28/03/2025 | 12:00 | 28/03/2025 | 13:10 | RBD21 | ROSEBUD | Rural Short | Planned |  | 4 | 280 | 70 | 1 | No
| 155147 | 2025-04-04 | 9:00 | 2025-04-04 | 11:20 | BU22 | BULLEEN | Urban | Planned |  | 46 | 6440 | 140 | 1 | No
| 155150 | 2025-04-05 | 8:05 | 2025-04-05 | 10:58 | RBD21 | ROSEBUD | Rural Short | Planned |  | 19 | 3287 | 173 | 1 | No
| 155157 | 30/03/2025 | 8:00 | 30/03/2025 | 16:30 | MC14 | MORDIALLOC | Urban | Planned |  | 3 | 1530 | 510 | 2 | No
| 155157 | 30/03/2025 | 8:00 | 30/03/2025 | 16:57 | MC14 | MORDIALLOC | Urban | Planned |  | 394 | 211578 | 537 | 1 | No
| 155157 | 30/03/2025 | 8:00 | 30/03/2025 | 16:57 | MC32 | MORDIALLOC | Urban | Planned |  | 36 | 19332 | 537 | 1 | No
| 155158 | 2025-06-05 | 8:28 | 2025-06-05 | 14:28 | MC12 | MORDIALLOC | Urban | Planned |  | 14 | 5040 | 360 | 1 | No
| 155158 | 2025-06-05 | 8:28 | 2025-06-05 | 14:28 | MC21 | MORDIALLOC | Urban | Planned |  | 88 | 31680 | 360 | 1 | No
| 155163 | 2025-02-04 | 10:08 | 2025-02-04 | 14:54 | LD7 | LYNDALE | Urban | Planned |  | 19 | 5434 | 286 | 1 | No
| 155166 | 2025-06-04 | 8:15 | 2025-06-04 | 12:44 | HT13 | HEATHERTON | Urban | Planned |  | 5 | 1345 | 269 | 1 | No
| 155166 | 2025-06-04 | 8:15 | 2025-06-04 | 12:44 | HT2 | HEATHERTON | Urban | Planned |  | 17 | 4573 | 269 | 1 | No
| 155168 | 2025-09-04 | 9:21 | 2025-09-04 | 14:05 | DC10 | DONCASTER | Urban | Planned |  | 54 | 15336 | 284 | 1 | No
| 155176 | 25/03/2025 | 8:05 | 25/03/2025 | 16:27 | MTN32 | MORNINGTON | Rural Short | Planned |  | 17 | 8534 | 502 | 1 | No
| 155183 | 28/03/2025 | 8:21 | 28/03/2025 | 11:51 | MR24 | MOORABBIN | Urban | Planned |  | 54 | 11340 | 210 | 1 | No
| 155188 | 2025-07-05 | 8:05 | 2025-07-05 | 12:27 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 8 | 2096 | 262 | 1 | No
| 155189 | 2025-07-05 | 8:00 | 2025-07-05 | 12:17 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 28 | 7196 | 257 | 1 | No
| 155190 | 2025-09-04 | 8:00 | 2025-09-04 | 16:00 | NW31 | NUNAWADING | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 155190 | 2025-09-04 | 8:14 | 2025-09-04 | 13:47 | NW31 | NUNAWADING | Urban | Planned |  | 170 | 56610 | 333 | 1 | No
| 155195 | 2025-04-06 | 8:02 | 2025-04-06 | 12:37 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 27 | 7425 | 275 | 1 | No
| 155195 | 2025-04-06 | 8:02 | 2025-04-06 | 12:37 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 26 | 7150 | 275 | 1 | No
| 155196 | 26/03/2025 | 9:45 | 26/03/2025 | 14:40 | NO31 | NOTTING HILL | Urban | Planned |  | 48 | 14160 | 295 | 1 | No
| 155202 | 27/03/2025 | 9:15 | 27/03/2025 | 13:45 | MGE23 | MULGRAVE | Urban | Planned |  | 23 | 6210 | 270 | 1 | No
| 155203 | 2025-01-04 | 13:20 | 2025-01-04 | 14:10 | LD3 | LYNDALE | Urban | Planned |  | 5 | 250 | 50 | 1 | No
| 155204 | 29/05/2025 | 8:00 | 29/05/2025 | 15:59 | NW31 | NUNAWADING | Urban | Planned |  | 1 | 479 | 479 | 1 | No
| 155204 | 29/05/2025 | 8:05 | 29/05/2025 | 14:55 | NW31 | NUNAWADING | Urban | Planned |  | 173 | 70930 | 410 | 1 | No
| 155206 | 26/03/2025 | 8:00 | 26/03/2025 | 16:30 | SH22 | SURREY HILLS | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 155207 | 28/03/2025 | 8:45 | 28/03/2025 | 12:00 | MGE23 | MULGRAVE | Urban | Planned |  | 2 | 390 | 195 | 1 | No
| 155212 | 16/03/2025 | 7:00 | 16/03/2025 | 8:00 | MC22 | MORDIALLOC | Urban | Planned |  | 2 | 120 | 60 | 1 | No
| 155215 | 2025-07-04 | 8:01 | 2025-07-04 | 16:01 | CRM23 | CARRUM | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 155215 | 2025-07-04 | 8:05 | 2025-07-04 | 12:50 | CRM23 | CARRUM | Urban | Planned |  | 230 | 65550 | 285 | 1 | No
| 155216 | 25/03/2025 | 12:08 | 25/03/2025 | 14:11 | GW2 | GLEN WAVERLEY | Urban | Planned |  | 50 | 6150 | 123 | 1 | No
| 155221 | 26/03/2025 | 8:00 | 26/03/2025 | 16:00 | BU15 | BULLEEN | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 155221 | 26/03/2025 | 9:00 | 26/03/2025 | 14:27 | BU15 | BULLEEN | Urban | Planned |  | 70 | 22890 | 327 | 1 | No
| 155223 | 26/03/2025 | 8:20 | 26/03/2025 | 15:20 | LWN21 | LANGWARRIN | Rural Short | Planned |  | 32 | 13440 | 420 | 1 | No
| 155226 | 25/03/2025 | 8:20 | 25/03/2025 | 11:00 | NO7 | NOTTING HILL | Urban | Planned |  | 34 | 5440 | 160 | 1 | No
| 155233 | 30/04/2025 | 8:40 | 30/04/2025 | 10:20 | STO14 | SORRENTO | Rural Short | Planned |  | 75 | 7500 | 100 | 1 | No
| 155234 | 27/04/2025 | 11:30 | 27/04/2025 | 15:15 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 12 | 2700 | 225 | 1 | No
| 155235 | 23/04/2025 | 12:55 | 23/04/2025 | 14:03 | SS13 | SPRINGVALE SOUTH | Urban | Planned |  | 3 | 204 | 68 | 1 | No
| 155238 | 29/04/2025 | 9:05 | 29/04/2025 | 12:40 | RBD23 | ROSEBUD | Urban | Planned |  | 17 | 3655 | 215 | 1 | No
| 155239 | 24/04/2025 | 10:24 | 24/04/2025 | 10:29 | DMA21 | DROMANA | Urban | Planned |  | 14 | 70 | 5 | 1 | No
| 155240 | 24/04/2025 | 8:00 | 24/04/2025 | 12:00 | DMA21 | DROMANA | Urban | Planned |  | 1 | 240 | 240 | 1 | No
| 155240 | 24/04/2025 | 8:10 | 24/04/2025 | 9:15 | DMA21 | DROMANA | Urban | Planned |  | 36 | 2340 | 65 | 1 | No
| 155241 | 2025-09-05 | 8:25 | 2025-09-05 | 9:30 | RBD23 | ROSEBUD | Urban | Planned |  | 32 | 2080 | 65 | 1 | No
| 155243 | 27/03/2025 | 9:55 | 27/03/2025 | 12:06 | LD4 | LYNDALE | Urban | Planned |  | 15 | 1965 | 131 | 1 | No
| 155246 | 2025-02-05 | 8:00 | 2025-02-05 | 15:00 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 155246 | 2025-02-05 | 9:35 | 2025-02-05 | 13:25 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 81 | 18630 | 230 | 1 | No
| 155250 | 27/03/2025 | 13:15 | 27/03/2025 | 13:45 | LD7 | LYNDALE | Urban | Planned |  | 1 | 30 | 30 | 1 | No
| 155251 | 2025-01-05 | 10:50 | 2025-01-05 | 12:25 | DC12 | DONCASTER | Urban | Planned |  | 31 | 2945 | 95 | 1 | No
| 155252 | 2025-09-05 | 8:40 | 2025-09-05 | 12:00 | RBD23 | ROSEBUD | Urban | Planned |  | 1 | 200 | 200 | 1 | No
| 155258 | 27/03/2025 | 8:18 | 27/03/2025 | 8:34 | RBD21 | ROSEBUD | Rural Short | Planned |  | 1 | 16 | 16 | 1 | No
| 155262 | 29/03/2025 | 23:25 | 30/03/2025 | 1:30 | STO23 | SORRENTO | Urban | Planned |  | 14 | 1750 | 125 | 1 | No
| 155264 | 2025-06-04 | 7:30 | 2025-06-04 | 12:15 | DVY14 | DANDENONG VALLEY | Urban | Planned |  | 3 | 855 | 285 | 1 | No
| 155270 | 2025-03-04 | 8:10 | 2025-03-04 | 13:15 | MGE34 | MULGRAVE | Urban | Planned |  | 47 | 14335 | 305 | 1 | No
| 155273 | 2025-04-04 | 8:38 | 2025-04-04 | 13:27 | LD6 | LYNDALE | Urban | Planned |  | 38 | 10982 | 289 | 1 | No
| 155281 | 2025-09-04 | 10:55 | 2025-09-04 | 17:00 | CFD14 | CAULFIELD | Urban | Planned |  | 21 | 7665 | 365 | 1 | No
| 155284 | 2025-01-04 | 9:02 | 2025-01-04 | 10:03 | MTN24 | MORNINGTON | Rural Short | Planned |  | 1 | 61 | 61 | 1 | No
| 155285 | 2025-06-04 | 12:35 | 2025-06-04 | 15:02 | DVY14 | DANDENONG VALLEY | Urban | Planned |  | 1 | 147 | 147 | 1 | No
| 155287 | 2025-01-04 | 11:09 | 2025-01-04 | 13:41 | RBD21 | ROSEBUD | Rural Short | Planned |  | 75 | 11400 | 152 | 1 | No
| 155288 | 2025-06-05 | 12:50 | 2025-06-05 | 14:45 | RBD14 | ROSEBUD | Urban | Planned |  | 1 | 115 | 115 | 1 | No
| 155289 | 2025-06-05 | 8:40 | 2025-06-05 | 11:30 | STO21 | SORRENTO | Rural Short | Planned |  | 10 | 1700 | 170 | 1 | No
| 155292 | 31/03/2025 | 13:50 | 31/03/2025 | 14:20 | EB32 | EAST BURWOOD | Urban | Planned |  | 5 | 150 | 30 | 1 | No
| 155292 | 31/03/2025 | 13:50 | 31/03/2025 | 14:20 | GW11 | GLEN WAVERLEY | Urban | Planned |  | 1 | 30 | 30 | 1 | No
| 155295 | 2025-01-04 | 12:00 | 2025-01-04 | 16:33 | WD23 | WEST DONCASTER | Urban | Planned |  | 48 | 13104 | 273 | 1 | No
| 155296 | 16/04/2025 | 8:01 | 16/04/2025 | 12:57 | KBH31 | KEYSBOROUGH | Urban | Planned |  | 2 | 592 | 296 | 1 | No
| 155306 | 28/03/2025 | 8:46 | 28/03/2025 | 14:55 | BU15 | BULLEEN | Urban | Planned |  | 114 | 42066 | 369 | 1 | No
| 155308 | 2025-02-04 | 8:55 | 2025-02-04 | 11:15 | STO23 | SORRENTO | Urban | Planned |  | 62 | 8680 | 140 | 1 | No
| 155310 | 2025-02-04 | 12:35 | 2025-02-04 | 15:15 | RBD21 | ROSEBUD | Rural Short | Planned |  | 15 | 2400 | 160 | 1 | No
| 155311 | 13/04/2025 | 8:00 | 13/04/2025 | 12:42 | MC23 | MORDIALLOC | Urban | Planned |  | 82 | 23124 | 282 | 1 | No
| 155315 | 2025-08-04 | 4:47 | 2025-08-04 | 5:02 | MGE21 | MULGRAVE | Urban | Planned |  | 1 | 15 | 15 | 1 | No
| 155317 | 14/05/2025 | 8:00 | 14/05/2025 | 11:50 | CDA22 | CLARINDA | Urban | Planned |  | 15 | 3450 | 230 | 1 | No
| 155319 | 20/05/2025 | 6:35 | 20/05/2025 | 12:55 | BT25 | BENTLEIGH | Urban | Planned |  | 11 | 4180 | 380 | 1 | No
| 155322 | 2025-02-04 | 8:02 | 2025-02-04 | 16:24 | DC1 | DONCASTER | Urban | Planned |  | 83 | 41666 | 502 | 1 | No
| 155324 | 2025-01-04 | 8:45 | 2025-01-04 | 14:05 | MTN34 | MORNINGTON | Urban | Planned |  | 15 | 4800 | 320 | 1 | No
| 155330 | 2025-10-04 | 8:38 | 2025-10-04 | 16:27 | STO21 | SORRENTO | Rural Short | Planned |  | 11 | 5159 | 469 | 1 | No
| 155332 | 13/03/2025 | 8:30 | 13/03/2025 | 14:00 | MC14 | MORDIALLOC | Urban | Planned |  | 1 | 330 | 330 | 1 | No
| 155333 | 2025-10-04 | 9:30 | 2025-10-04 | 10:50 | MTN24 | MORNINGTON | Rural Short | Planned |  | 3 | 240 | 80 | 1 | No
| 155337 | 2025-02-04 | 8:08 | 2025-02-04 | 11:35 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 101 | 20907 | 207 | 1 | No
| 155338 | 30/03/2025 | 8:02 | 30/03/2025 | 14:00 | DVY22 | DANDENONG VALLEY | Urban | Planned |  | 72 | 25776 | 358 | 1 | No
| 155344 | 23/05/2025 | 8:35 | 23/05/2025 | 11:06 | BU11 | BULLEEN | Urban | Planned |  | 29 | 4379 | 151 | 1 | No
| 155345 | 16/04/2025 | 8:40 | 16/04/2025 | 10:30 | EM5 | EAST MALVERN | Urban | Planned |  | 23 | 2530 | 110 | 1 | No
| 155349 | 2025-03-04 | 8:42 | 2025-03-04 | 9:36 | NB32 | NORTH BRIGHTON | Urban | Planned |  | 22 | 1188 | 54 | 1 | No
| 155351 | 2025-03-04 | 11:00 | 2025-03-04 | 14:03 | FTN23 | FRANKSTON | Urban | Planned |  | 33 | 6039 | 183 | 1 | No
| 155353 | 2025-06-05 | 8:50 | 2025-06-05 | 13:08 | BU11 | BULLEEN | Urban | Planned |  | 88 | 22704 | 258 | 1 | No
| 155357 | 23/05/2025 | 11:55 | 23/05/2025 | 13:45 | BU12 | BULLEEN | Urban | Planned |  | 10 | 1100 | 110 | 1 | No
| 155358 | 2025-03-04 | 8:35 | 2025-03-04 | 10:20 | BH33 | BOX HILL | Urban | Planned |  | 45 | 4725 | 105 | 1 | No
| 155361 | 2025-03-04 | 8:32 | 2025-03-04 | 11:30 | RBD14 | ROSEBUD | Urban | Planned |  | 97 | 17266 | 178 | 1 | No
| 155363 | 2025-05-05 | 11:05 | 2025-05-05 | 12:30 | BU21 | BULLEEN | Urban | Planned |  | 5 | 425 | 85 | 1 | No
| 155364 | 2025-05-05 | 10:00 | 2025-05-05 | 15:00 | STO14 | SORRENTO | Rural Short | Planned |  | 1 | 300 | 300 | 1 | No
| 155364 | 2025-05-05 | 10:35 | 2025-05-05 | 12:10 | STO14 | SORRENTO | Rural Short | Planned |  | 79 | 7505 | 95 | 1 | No
| 155366 | 19/06/2025 | 8:03 | 19/06/2025 | 11:22 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 91 | 18109 | 199 | 1 | No
| 155367 | 24/06/2025 | 11:53 | 24/06/2025 | 13:20 | BU25 | BULLEEN | Urban | Planned |  | 24 | 2088 | 87 | 1 | No
| 155368 | 2025-01-04 | 8:35 | 2025-01-04 | 13:36 | RBD21 | ROSEBUD | Rural Short | Planned |  | 50 | 15050 | 301 | 1 | No
| 155369 | 2025-04-04 | 9:00 | 2025-04-04 | 10:15 | CFD14 | CAULFIELD | Urban | Planned |  | 6 | 450 | 75 | 1 | No
| 155370 | 2025-01-04 | 8:03 | 2025-01-04 | 12:45 | SV16 | SPRINGVALE | Urban | Planned |  | 57 | 16074 | 282 | 1 | No
| 155371 | 31/03/2025 | 8:11 | 31/03/2025 | 14:13 | MR14 | MOORABBIN | Urban | Planned |  | 95 | 34390 | 362 | 1 | No
| 155375 | 2025-03-04 | 8:00 | 2025-03-04 | 13:00 | NW11 | NUNAWADING | Urban | Planned |  | 28 | 8400 | 300 | 1 | No
| 155380 | 14/05/2025 | 8:02 | 14/05/2025 | 11:04 | STO14 | SORRENTO | Rural Short | Planned |  | 12 | 2184 | 182 | 1 | No
| 155381 | 15/05/2025 | 8:10 | 15/05/2025 | 9:31 | DMA24 | DROMANA | Rural Short | Planned |  | 3 | 243 | 81 | 1 | No
| 155384 | 29/04/2025 | 8:00 | 29/04/2025 | 16:00 | EB14 | EAST BURWOOD | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 155384 | 29/04/2025 | 9:30 | 29/04/2025 | 15:26 | EB14 | EAST BURWOOD | Urban | Planned |  | 118 | 42008 | 356 | 1 | No
| 155387 | 20/05/2025 | 8:00 | 20/05/2025 | 8:00 | DC7 | DONCASTER | Urban | Planned |  | 29 | 0 | 0 | 1 | No
| 155387 | 20/05/2025 | 8:00 | 20/05/2025 | 8:00 | DC8 | DONCASTER | Urban | Planned |  | 40 | 0 | 0 | 1 | No
| 155388 | 15/05/2025 | 11:03 | 15/05/2025 | 12:34 | DMA14 | DROMANA | Urban | Planned |  | 78 | 7098 | 91 | 1 | No
| 155391 | 2025-10-04 | 11:32 | 2025-10-04 | 14:20 | MTN31 | MORNINGTON | Urban | Planned |  | 19 | 3192 | 168 | 1 | No
| 155397 | 2025-07-04 | 8:31 | 2025-07-04 | 13:45 | CRM35 | CARRUM | Urban | Planned |  | 106 | 33284 | 314 | 1 | No
| 155397 | 2025-07-04 | 8:31 | 2025-07-04 | 13:45 | MC34 | MORDIALLOC | Urban | Planned |  | 23 | 7222 | 314 | 1 | No
| 155398 | 14/04/2025 | 8:31 | 14/04/2025 | 14:25 | CRM35 | CARRUM | Urban | Planned |  | 106 | 37524 | 354 | 1 | No
| 155398 | 14/04/2025 | 8:31 | 14/04/2025 | 14:25 | MC34 | MORDIALLOC | Urban | Planned |  | 23 | 8142 | 354 | 1 | No
| 155399 | 2025-09-04 | 8:45 | 2025-09-04 | 13:55 | BU14 | BULLEEN | Urban | Planned |  | 8 | 2480 | 310 | 1 | No
| 155402 | 2025-03-04 | 8:00 | 2025-03-04 | 16:00 | BU22 | BULLEEN | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 155402 | 2025-03-04 | 8:10 | 2025-03-04 | 12:55 | BU22 | BULLEEN | Urban | Planned |  | 86 | 24510 | 285 | 1 | No
| 155404 | 2025-03-04 | 8:15 | 2025-03-04 | 15:13 | CFD25 | CAULFIELD | Urban | Planned |  | 28 | 11704 | 418 | 1 | No
| 155407 | 2025-08-06 | 8:00 | 2025-08-06 | 12:30 | KBH32 | KEYSBOROUGH | Urban | Planned |  | 15 | 4050 | 270 | 1 | No
| 155416 | 2025-03-04 | 8:03 | 2025-03-04 | 12:16 | GW5 | GLEN WAVERLEY | Urban | Planned |  | 35 | 8855 | 253 | 1 | No
| 155417 | 2025-01-04 | 8:10 | 2025-01-04 | 14:30 | MTN31 | MORNINGTON | Urban | Planned |  | 186 | 70680 | 380 | 1 | No
| 155422 | 2025-04-04 | 10:00 | 2025-04-04 | 13:15 | LWN33 | LANGWARRIN | Urban | Planned |  | 128 | 24960 | 195 | 1 | No
| 155434 | 2025-03-04 | 8:00 | 2025-03-04 | 15:00 | MTN22 | MORNINGTON | Rural Short | Planned |  | 1 | 420 | 420 | 1 | No
| 155434 | 2025-03-04 | 8:01 | 2025-03-04 | 14:15 | MTN22 | MORNINGTON | Rural Short | Planned |  | 273 | 102102 | 374 | 1 | No
| 155438 | 2025-04-04 | 6:30 | 2025-04-04 | 15:30 | CRM24 | CARRUM | Urban | Planned |  | 1 | 540 | 540 | 1 | No
| 155439 | 2025-12-04 | 7:30 | 2025-12-04 | 9:58 | NP11 | NOBLE PARK | Urban | Planned |  | 4 | 592 | 148 | 1 | No
| 155445 | 2025-04-04 | 8:07 | 2025-04-04 | 10:27 | LWN33 | LANGWARRIN | Urban | Planned |  | 89 | 12460 | 140 | 1 | No
| 155446 | 2025-08-04 | 8:18 | 2025-08-04 | 13:39 | DMA13 | DROMANA | Rural Short | Planned |  | 86 | 27606 | 321 | 1 | No
| 155448 | 2025-08-04 | 8:00 | 2025-08-04 | 16:00 | K21 | GARDINER | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 155448 | 2025-08-04 | 8:08 | 2025-08-04 | 15:07 | K21 | GARDINER | Urban | Planned |  | 77 | 32263 | 419 | 1 | No
| 155451 | 2025-12-04 | 12:39 | 2025-12-04 | 13:50 | DN24 | DANDENONG | Urban | Planned |  | 5 | 355 | 71 | 1 | No
| 155453 | 2025-08-04 | 8:00 | 2025-08-04 | 13:30 | MTN22 | MORNINGTON | Rural Short | Planned |  | 1 | 330 | 330 | 1 | No
| 155453 | 2025-08-04 | 8:02 | 2025-08-04 | 11:06 | MTN22 | MORNINGTON | Rural Short | Planned |  | 42 | 7728 | 184 | 1 | No
| 155456 | 2025-08-04 | 11:33 | 2025-08-04 | 15:38 | MTN22 | MORNINGTON | Rural Short | Planned |  | 59 | 14455 | 245 | 1 | No
| 155462 | 23/04/2025 | 10:05 | 23/04/2025 | 12:44 | OE4 | OAKLEIGH EAST | Urban | Planned |  | 86 | 13674 | 159 | 1 | No
| 155463 | 13/04/2025 | 8:01 | 13/04/2025 | 13:50 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 60 | 20952 | 349.2 | 1 | No
| 155465 | 14/04/2025 | 10:35 | 14/04/2025 | 12:25 | DC1 | DONCASTER | Urban | Planned |  | 7 | 770 | 110 | 1 | No
| 155476 | 2025-07-04 | 8:07 | 2025-07-04 | 9:03 | HGS22 | HASTINGS | Rural Short | Planned |  | 3 | 168 | 56 | 1 | No
| 155478 | 2025-04-04 | 10:17 | 2025-04-04 | 13:18 | CRM23 | CARRUM | Urban | Planned |  | 67 | 12127 | 181 | 1 | No
| 155482 | 16/04/2025 | 9:35 | 16/04/2025 | 10:20 | CRM35 | CARRUM | Urban | Planned |  | 47 | 2115 | 45 | 1 | No
| 155503 | 2025-01-05 | 9:37 | 2025-01-05 | 15:43 | NP23 | NOBLE PARK | Urban | Planned |  | 49 | 17934 | 366 | 1 | No
| 155505 | 2025-07-04 | 8:02 | 2025-07-04 | 13:15 | NP16 | NOBLE PARK | Urban | Planned |  | 106 | 33178 | 313 | 1 | No
| 155508 | 2025-09-04 | 5:17 | 2025-09-04 | 5:33 | K33 | GARDINER | Urban | Planned |  | 2 | 32 | 16 | 1 | No
| 155513 | 2025-04-05 | 8:10 | 2025-04-05 | 13:40 | DN25 | DANDENONG | Urban | Planned |  | 18 | 5940 | 330 | 1 | No
| 155514 | 15/04/2025 | 9:14 | 15/04/2025 | 17:15 | DMA14 | DROMANA | Urban | Planned |  | 109 | 52429 | 481 | 1 | No
| 155515 | 2025-08-04 | 8:00 | 2025-08-04 | 12:30 | WD26 | WEST DONCASTER | Urban | Planned |  | 1 | 270 | 270 | 1 | No
| 155515 | 2025-08-04 | 9:15 | 2025-08-04 | 12:30 | WD26 | WEST DONCASTER | Urban | Planned |  | 31 | 6045 | 195 | 1 | No
| 155516 | 17/04/2025 | 8:58 | 17/04/2025 | 12:27 | RWT12 | RINGWOOD | Urban | Planned |  | 62 | 12958 | 209 | 1 | No
| 155523 | 27/03/2025 | 8:01 | 27/03/2025 | 17:25 | FTN23 | FRANKSTON | Urban | Planned |  | 57 | 32153.7 | 564.1 | 1 | No
| 155528 | 15/04/2025 | 8:54 | 15/04/2025 | 10:38 | MTN24 | MORNINGTON | Rural Short | Planned |  | 4 | 416 | 104 | 1 | No
| 155529 | 15/04/2025 | 12:04 | 15/04/2025 | 13:13 | MTN24 | MORNINGTON | Rural Short | Planned |  | 1 | 69 | 69 | 1 | No
| 155531 | 2025-08-04 | 8:00 | 2025-08-04 | 16:00 | CRM33 | CARRUM | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 155531 | 2025-08-04 | 9:09 | 2025-08-04 | 14:09 | CRM33 | CARRUM | Urban | Planned |  | 32 | 9600 | 300 | 1 | No
| 155532 | 2025-08-04 | 8:22 | 2025-08-04 | 11:52 | M32 | MENTONE | Urban | Planned |  | 168 | 35280 | 210 | 1 | No
| 155537 | 16/04/2025 | 12:30 | 16/04/2025 | 13:28 | LWN23 | LANGWARRIN | Urban | Planned |  | 13 | 754 | 58 | 1 | No
| 155538 | 2025-08-04 | 8:25 | 2025-08-04 | 9:45 | M32 | MENTONE | Urban | Planned |  | 76 | 6080 | 80 | 1 | No
| 155547 | 25/05/2025 | 8:00 | 25/05/2025 | 15:20 | DN25 | DANDENONG | Urban | Planned |  | 44 | 19341.6652 | 439.5833 | 1 | No
| 155548 | 23/04/2025 | 8:08 | 23/04/2025 | 10:24 | SS21 | SPRINGVALE SOUTH | Urban | Planned |  | 23 | 3128 | 136 | 1 | No
| 155551 | 17/04/2025 | 9:25 | 17/04/2025 | 14:25 | EB32 | EAST BURWOOD | Urban | Planned |  | 88 | 26400 | 300 | 1 | No
| 155551 | 17/04/2025 | 9:25 | 17/04/2025 | 14:25 | GW8 | GLEN WAVERLEY | Urban | Planned |  | 38 | 11400 | 300 | 1 | No
| 155557 | 2025-09-04 | 8:09 | 2025-09-04 | 16:50 | HGS32 | HASTINGS | Urban | Planned |  | 326 | 169846 | 521 | 1 | No
| 155565 | 2025-09-04 | 8:00 | 2025-09-04 | 10:20 | MC15 | MORDIALLOC | Urban | Planned |  | 35 | 4900 | 140 | 1 | No
| 155565 | 2025-09-04 | 8:00 | 2025-09-04 | 10:20 | MC21 | MORDIALLOC | Urban | Planned |  | 1 | 140 | 140 | 1 | No
| 155566 | 2025-10-04 | 8:35 | 2025-10-04 | 14:45 | HT4 | HEATHERTON | Urban | Planned |  | 138 | 51060 | 370 | 1 | No
| 155568 | 2025-09-04 | 9:30 | 2025-09-04 | 12:10 | CFD15 | CAULFIELD | Urban | Planned |  | 82 | 13120 | 160 | 1 | No
| 155569 | 2025-09-04 | 8:48 | 2025-09-04 | 12:20 | MC21 | MORDIALLOC | Urban | Planned |  | 50 | 10600 | 212 | 1 | No
| 155570 | 14/04/2025 | 9:15 | 14/04/2025 | 14:27 | LD4 | LYNDALE | Urban | Planned |  | 42 | 13104 | 312 | 1 | No
| 155572 | 2025-06-04 | 10:20 | 2025-06-04 | 13:30 | MGE13 | MULGRAVE | Urban | Planned |  | 1 | 190 | 190 | 1 | No
| 155585 | 13/04/2025 | 8:10 | 13/04/2025 | 17:15 | HT13 | HEATHERTON | Urban | Planned |  | 16 | 8720 | 545 | 1 | No
| 155588 | 2025-10-04 | 8:03 | 2025-10-04 | 11:51 | OR24 | ORMOND | Urban | Planned |  | 42 | 9576 | 228 | 1 | No
| 155590 | 2025-08-04 | 11:00 | 2025-08-04 | 11:20 | KBH34 | KEYSBOROUGH | Urban | Planned |  | 3 | 60 | 20 | 1 | No
| 155591 | 2025-10-04 | 12:30 | 2025-10-04 | 13:35 | SR35 | SANDRINGHAM | Urban | Planned |  | 117 | 7605 | 65 | 1 | No
| 155592 | 2025-09-04 | 9:00 | 2025-09-04 | 16:00 | EW8 | ELWOOD | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 155592 | 2025-09-04 | 9:45 | 2025-09-04 | 14:35 | EL22 | ELSTERNWICK | Urban | Planned |  | 32 | 9280 | 290 | 1 | No
| 155592 | 2025-09-04 | 9:45 | 2025-09-04 | 14:35 | EW8 | ELWOOD | Urban | Planned |  | 80 | 23200 | 290 | 1 | No
| 155593 | 2025-08-04 | 11:54 | 2025-08-04 | 12:20 | KBH34 | KEYSBOROUGH | Urban | Planned |  | 1 | 26 | 26 | 1 | No
| 155594 | 16/04/2025 | 22:18 | 17/04/2025 | 2:08 | DN6 | DANDENONG | Urban | Planned |  | 2 | 460 | 230 | 1 | No
| 155596 | 16/04/2025 | 8:00 | 16/04/2025 | 10:30 | SR24 | SANDRINGHAM | Urban | Planned |  | 26 | 3900 | 150 | 1 | No
| 155601 | 2025-11-04 | 8:00 | 2025-11-04 | 9:48 | NP31 | NOBLE PARK | Urban | Planned |  | 42 | 4536 | 108 | 1 | No
| 155604 | 14/04/2025 | 8:54 | 14/04/2025 | 11:46 | EW1 | ELWOOD | Urban | Planned |  | 97 | 16684 | 172 | 1 | No
| 155606 | 14/04/2025 | 10:30 | 14/04/2025 | 16:30 | AR12 | ARMADALE | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 155606 | 14/04/2025 | 12:42 | 14/04/2025 | 15:22 | AR12 | ARMADALE | Urban | Planned |  | 43 | 6880 | 160 | 1 | No
| 155610 | 16/04/2025 | 8:58 | 16/04/2025 | 15:41 | NW21 | NUNAWADING | Urban | Planned |  | 66 | 26598 | 403 | 1 | No
| 155611 | 2025-03-05 | 7:31 | 2025-03-05 | 16:31 | LD7 | LYNDALE | Urban | Planned |  | 77 | 41612.0859 | 540.4167 | 1 | No
| 155613 | 2025-08-04 | 11:30 | 2025-08-04 | 12:24 | NP24 | NOBLE PARK | Urban | Planned |  | 64 | 3456 | 54 | 1 | No
| 155615 | 2025-11-04 | 8:30 | 2025-11-04 | 13:32 | BU15 | BULLEEN | Urban | Planned |  | 73 | 22046 | 302 | 1 | No
| 155618 | 15/04/2025 | 8:00 | 15/04/2025 | 14:00 | WD23 | WEST DONCASTER | Urban | Planned |  | 5 | 1800 | 360 | 1 | No
| 155619 | 15/04/2025 | 12:30 | 15/04/2025 | 15:45 | WD16 | WEST DONCASTER | Urban | Planned |  | 56 | 10920 | 195 | 1 | No
| 155629 | 2025-09-04 | 13:05 | 2025-09-04 | 15:15 | CFD15 | CAULFIELD | Urban | Planned |  | 64 | 8320 | 130 | 1 | No
| 155638 | 13/04/2025 | 7:30 | 13/04/2025 | 13:30 | HT7 | HEATHERTON | Urban | Planned |  | 2 | 720 | 360 | 2 | No
| 155638 | 13/04/2025 | 7:30 | 13/04/2025 | 13:45 | HT7 | HEATHERTON | Urban | Planned |  | 143 | 53625 | 375 | 1 | No
| 155639 | 14/04/2025 | 8:30 | 14/04/2025 | 11:10 | EB31 | EAST BURWOOD | Urban | Planned |  | 6 | 960 | 160 | 1 | No
| 155642 | 2025-11-04 | 10:34 | 2025-11-04 | 14:00 | STO22 | SORRENTO | Urban | Planned |  | 6 | 1236 | 206 | 1 | No
| 155649 | 2025-04-05 | 7:11 | 2025-04-05 | 9:45 | MGE13 | MULGRAVE | Urban | Planned |  | 1 | 154 | 154 | 1 | No
| 155650 | 24/04/2025 | 8:00 | 24/04/2025 | 13:10 | CFD13 | CAULFIELD | Urban | Planned |  | 58 | 17980 | 310 | 1 | No
| 155650 | 24/04/2025 | 8:00 | 24/04/2025 | 13:10 | CFD14 | CAULFIELD | Urban | Planned |  | 63 | 19530 | 310 | 1 | No
| 155650 | 24/04/2025 | 8:00 | 24/04/2025 | 13:10 | EL35 | ELSTERNWICK | Urban | Planned |  | 415 | 128650 | 310 | 1 | No
| 155651 | 2025-11-05 | 6:35 | 2025-11-05 | 20:28 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 2 | 1666 | 833 | 1 | No
| 155661 | 17/04/2025 | 8:26 | 17/04/2025 | 11:35 | MR14 | MOORABBIN | Urban | Planned |  | 69 | 13041 | 189 | 1 | No
| 155663 | 17/04/2025 | 12:35 | 17/04/2025 | 15:54 | MR22 | MOORABBIN | Urban | Planned |  | 45 | 8955 | 199 | 1 | No
| 155668 | 15/04/2025 | 22:30 | 16/04/2025 | 6:00 | OAK22 | OAKLEIGH | Urban | Planned |  | 31 | 13950 | 450 | 1 | No
| 155672 | 2025-09-04 | 8:05 | 2025-09-04 | 13:18 | RBD21 | ROSEBUD | Rural Short | Planned |  | 116 | 36308 | 313 | 1 | No
| 155673 | 2025-09-04 | 8:30 | 2025-09-04 | 11:45 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 2 | 390 | 195 | 1 | No
| 155675 | 2025-11-04 | 8:50 | 2025-11-04 | 13:30 | STO14 | SORRENTO | Rural Short | Planned |  | 32 | 8960 | 280 | 1 | No
| 155675 | 2025-11-04 | 8:50 | 2025-11-04 | 13:30 | STO21 | SORRENTO | Rural Short | Planned |  | 35 | 9800 | 280 | 1 | No
| 155677 | 2025-10-04 | 8:15 | 2025-10-04 | 14:20 | EB33 | EAST BURWOOD | Urban | Planned |  | 104 | 37960 | 365 | 1 | No
| 155678 | 27/04/2025 | 8:15 | 27/04/2025 | 11:34 | HT3 | HEATHERTON | Urban | Planned |  | 1 | 199 | 199 | 1 | No
| 155679 | 27/04/2025 | 12:05 | 27/04/2025 | 14:10 | HT3 | HEATHERTON | Urban | Planned |  | 2 | 250 | 125 | 1 | No
| 155680 | 27/04/2025 | 14:31 | 27/04/2025 | 16:42 | HT13 | HEATHERTON | Urban | Planned |  | 1 | 131 | 131 | 1 | No
| 155680 | 27/04/2025 | 14:31 | 27/04/2025 | 16:42 | HT2 | HEATHERTON | Urban | Planned |  | 9 | 1179 | 131 | 1 | No
| 155681 | 27/04/2025 | 8:30 | 27/04/2025 | 11:08 | NO4 | NOTTING HILL | Urban | Planned |  | 50 | 7900 | 158 | 1 | No
| 155683 | 2025-10-04 | 11:41 | 2025-10-04 | 12:26 | MTN35 | MORNINGTON | Rural Short | Planned |  | 28 | 1260 | 45 | 1 | No
| 155685 | 17/04/2025 | 9:30 | 17/04/2025 | 13:11 | KBH32 | KEYSBOROUGH | Urban | Planned |  | 12 | 2652 | 221 | 1 | No
| 155687 | 14/04/2025 | 8:59 | 14/04/2025 | 12:14 | RBD12 | ROSEBUD | Rural Short | Planned |  | 23 | 4485 | 195 | 1 | No
| 155702 | 17/05/2025 | 6:56 | 17/05/2025 | 10:50 | MC32 | MORDIALLOC | Urban | Planned |  | 2 | 468 | 234 | 1 | No
| 155704 | 16/04/2025 | 10:15 | 16/04/2025 | 12:40 | MC32 | MORDIALLOC | Urban | Planned |  | 1 | 145 | 145 | 1 | No
| 155709 | 16/04/2025 | 8:00 | 16/04/2025 | 14:30 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 78 | 30420 | 390 | 1 | No
| 155712 | 23/04/2025 | 8:02 | 23/04/2025 | 11:57 | OR32 | ORMOND | Urban | Planned |  | 73 | 17155 | 235 | 1 | No
| 155719 | 23/04/2025 | 8:00 | 23/04/2025 | 12:59 | HGS21 | HASTINGS | Rural Short | Planned |  | 85 | 25415 | 299 | 1 | No
| 155720 | 2025-07-05 | 8:00 | 2025-07-05 | 13:00 | NP16 | NOBLE PARK | Urban | Planned |  | 3 | 900 | 300 | 1 | No
| 155722 | 2025-11-04 | 8:03 | 2025-11-04 | 13:06 | MGE23 | MULGRAVE | Urban | Planned |  | 19 | 5757 | 303 | 1 | No
| 155725 | 15/04/2025 | 8:00 | 15/04/2025 | 13:00 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 1 | 300 | 300 | 1 | No
| 155725 | 15/04/2025 | 8:35 | 15/04/2025 | 11:13 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 80 | 12640 | 158 | 1 | No
| 155726 | 15/04/2025 | 11:58 | 15/04/2025 | 15:14 | MTN35 | MORNINGTON | Rural Short | Planned |  | 55 | 10780 | 196 | 1 | No
| 155729 | 27/05/2025 | 8:01 | 27/05/2025 | 15:00 | DN2 | DANDENONG | Urban | Planned |  | 1 | 419 | 419 | 1 | No
| 155731 | 14/04/2025 | 9:30 | 14/04/2025 | 13:15 | WD26 | WEST DONCASTER | Urban | Planned |  | 35 | 7875 | 225 | 1 | No
| 155733 | 17/04/2025 | 8:01 | 17/04/2025 | 12:18 | NB35 | NORTH BRIGHTON | Urban | Planned |  | 141 | 36237 | 257 | 1 | No
| 155734 | 2025-10-05 | 8:05 | 2025-10-05 | 15:10 | CDA22 | CLARINDA | Urban | Planned |  | 35 | 14875 | 425 | 1 | No
| 155736 | 2025-07-05 | 9:07 | 2025-07-05 | 10:01 | NW23 | NUNAWADING | Urban | Planned |  | 4 | 216 | 54 | 1 | No
| 155738 | 2025-11-04 | 12:03 | 2025-11-04 | 13:24 | HGS32 | HASTINGS | Urban | Planned |  | 29 | 2349 | 81 | 1 | No
| 155745 | 2025-07-05 | 11:04 | 2025-07-05 | 13:10 | NW23 | NUNAWADING | Urban | Planned |  | 7 | 882 | 126 | 1 | No
| 155750 | 2025-07-05 | 11:10 | 2025-07-05 | 11:55 | NP36 | NOBLE PARK | Urban | Planned |  | 2 | 90 | 45 | 1 | No
| 155751 | 17/04/2025 | 8:10 | 17/04/2025 | 13:00 | EM3 | EAST MALVERN | Urban | Planned |  | 2 | 580 | 290 | 1 | No
| 155755 | 2025-07-05 | 13:04 | 2025-07-05 | 13:09 | NP36 | NOBLE PARK | Urban | Planned |  | 3 | 15 | 5 | 1 | No
| 155756 | 2025-12-04 | 7:40 | 2025-12-04 | 14:38 | EM3 | EAST MALVERN | Urban | Planned |  | 170 | 71060 | 418 | 1 | No
| 155761 | 17/04/2025 | 8:07 | 17/04/2025 | 10:45 | MTN31 | MORNINGTON | Urban | Planned |  | 32 | 5056 | 158 | 1 | No
| 155762 | 29/04/2025 | 8:00 | 29/04/2025 | 16:00 | DC8 | DONCASTER | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 155762 | 29/04/2025 | 8:13 | 29/04/2025 | 11:29 | DC8 | DONCASTER | Urban | Planned |  | 107 | 20972 | 196 | 1 | No
| 155768 | 30/04/2025 | 8:20 | 30/04/2025 | 13:48 | DC8 | DONCASTER | Urban | Planned |  | 67 | 21976 | 328 | 1 | No
| 155771 | 30/04/2025 | 12:45 | 30/04/2025 | 14:30 | DMA21 | DROMANA | Urban | Planned |  | 43 | 4515 | 105 | 1 | No
| 155774 | 2025-08-05 | 8:50 | 2025-08-05 | 11:55 | CRM23 | CARRUM | Urban | Planned |  | 52 | 9620 | 185 | 1 | No
| 155787 | 29/04/2025 | 8:45 | 29/04/2025 | 10:07 | SH32 | SURREY HILLS | Urban | Planned |  | 64 | 5248 | 82 | 1 | No
| 155794 | 15/04/2025 | 9:05 | 15/04/2025 | 11:15 | EB32 | EAST BURWOOD | Urban | Planned |  | 2 | 260 | 130 | 1 | No
| 155795 | 2025-07-05 | 8:05 | 2025-07-05 | 9:35 | CRM13 | CARRUM | Urban | Planned |  | 9 | 810 | 90 | 1 | No
| 155799 | 13/04/2025 | 10:11 | 13/04/2025 | 13:25 | BC11 | BALACLAVA | Urban | Planned |  | 23 | 4462 | 194 | 1 | No
| 155807 | 29/04/2025 | 8:02 | 29/04/2025 | 10:34 | HGS32 | HASTINGS | Urban | Planned |  | 13 | 1976 | 152 | 1 | No
| 155819 | 16/04/2025 | 9:10 | 16/04/2025 | 17:10 | MC12 | MORDIALLOC | Urban | Planned |  | 7 | 3360 | 480 | 1 | No
| 155819 | 16/04/2025 | 9:10 | 16/04/2025 | 17:10 | MC21 | MORDIALLOC | Urban | Planned |  | 20 | 9600 | 480 | 1 | No
| 155822 | 16/04/2025 | 9:10 | 16/04/2025 | 12:30 | MGE23 | MULGRAVE | Urban | Planned |  | 1 | 200 | 200 | 1 | No
| 155824 | 30/04/2025 | 8:04 | 30/04/2025 | 14:35 | CRM33 | CARRUM | Urban | Planned |  | 142 | 55522 | 391 | 1 | No
| 155827 | 29/04/2025 | 8:00 | 29/04/2025 | 12:15 | MC23 | MORDIALLOC | Urban | Planned |  | 127 | 32385 | 255 | 2 | No
| 155827 | 29/04/2025 | 8:00 | 29/04/2025 | 15:30 | MC23 | MORDIALLOC | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 155830 | 2025-11-05 | 10:20 | 2025-11-05 | 12:46 | SV16 | SPRINGVALE | Urban | Planned |  | 1 | 146 | 146 | 1 | No
| 155830 | 2025-11-05 | 10:20 | 2025-11-05 | 12:46 | SV20 | SPRINGVALE | Urban | Planned |  | 53 | 7738 | 146 | 1 | No
| 155833 | 17/04/2025 | 8:00 | 17/04/2025 | 16:00 | AR6 | ARMADALE | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 155833 | 17/04/2025 | 9:50 | 17/04/2025 | 11:23 | AR6 | ARMADALE | Urban | Planned |  | 56 | 5208 | 93 | 1 | No
| 155833 | 17/04/2025 | 9:50 | 17/04/2025 | 11:23 | CFD16 | CAULFIELD | Urban | Planned |  | 38 | 3534 | 93 | 1 | No
| 155840 | 2025-01-05 | 8:24 | 2025-01-05 | 20:25 | RBD21 | ROSEBUD | Rural Short | Planned |  | 30 | 21630 | 721 | 1 | No
| 155849 | 18/05/2025 | 7:30 | 18/05/2025 | 15:00 | MGE22 | MULGRAVE | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 155849 | 18/05/2025 | 7:31 | 18/05/2025 | 16:42 | MGE22 | MULGRAVE | Urban | Planned |  | 5 | 2755 | 551 | 1 | No
| 155854 | 2025-04-05 | 11:32 | 2025-04-05 | 16:01 | MTN21 | MORNINGTON | Urban | Planned |  | 170 | 45730 | 269 | 1 | No
| 155863 | 2025-11-05 | 8:50 | 2025-11-05 | 10:31 | SS12 | SPRINGVALE SOUTH | Urban | Planned |  | 4 | 404 | 101 | 1 | No
| 155864 | 16/04/2025 | 12:19 | 16/04/2025 | 14:30 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 78 | 10218 | 131 | 1 | No
| 155865 | 2025-01-05 | 9:56 | 2025-01-05 | 10:56 | KBH34 | KEYSBOROUGH | Urban | Planned |  | 4 | 240 | 60 | 1 | No
| 155868 | 2025-12-05 | 9:48 | 2025-12-05 | 11:55 | STO13 | SORRENTO | Urban | Planned |  | 7 | 889 | 127 | 1 | No
| 155869 | 2025-12-05 | 11:30 | 2025-12-05 | 14:30 | STO13 | SORRENTO | Urban | Planned |  | 3 | 540 | 180 | 1 | No
| 155872 | 22/04/2025 | 4:03 | 22/04/2025 | 4:25 | MGE33 | MULGRAVE | Urban | Planned |  | 2 | 44 | 22 | 1 | No
| 155873 | 26/04/2025 | 8:02 | 26/04/2025 | 12:25 | M11 | MENTONE | Urban | Planned |  | 201 | 52863 | 263 | 1 | No
| 155881 | 13/05/2025 | 8:00 | 13/05/2025 | 18:35 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 24 | 15229.2 | 634.55 | 1 | No
| 155884 | 16/05/2025 | 8:01 | 16/05/2025 | 12:55 | CRM35 | CARRUM | Urban | Planned |  | 12 | 3530.0004 | 294.1667 | 1 | No
| 155888 | 23/04/2025 | 22:00 | 24/04/2025 | 4:16 | FTN21 | FRANKSTON | Urban | Planned |  | 131 | 49256 | 376 | 1 | No
| 155890 | 30/04/2025 | 8:36 | 30/04/2025 | 14:21 | NB36 | NORTH BRIGHTON | Urban | Planned |  | 1 | 345 | 345 | 1 | No
| 155892 | 17/04/2025 | 8:05 | 17/04/2025 | 14:20 | OR23 | ORMOND | Urban | Planned |  | 6 | 2250 | 375 | 1 | No
| 155894 | 2025-06-05 | 10:20 | 2025-06-05 | 14:22 | RBD21 | ROSEBUD | Rural Short | Planned |  | 2 | 484 | 242 | 1 | No
| 155895 | 29/04/2025 | 8:03 | 29/04/2025 | 13:23 | NO7 | NOTTING HILL | Urban | Planned |  | 127 | 40640 | 320 | 1 | No
| 155897 | 2025-02-05 | 8:30 | 2025-02-05 | 10:50 | NP12 | NOBLE PARK | Urban | Planned |  | 29 | 4060 | 140 | 1 | No
| 155898 | 30/04/2025 | 8:46 | 30/04/2025 | 15:23 | CFD14 | CAULFIELD | Urban | Planned |  | 97 | 38509 | 397 | 1 | No
| 155901 | 30/04/2025 | 10:30 | 30/04/2025 | 16:00 | BH11 | BOX HILL | Urban | Planned |  | 106 | 34980 | 330 | 1 | No
| 155905 | 2025-02-05 | 8:30 | 2025-02-05 | 15:30 | CRM13 | CARRUM | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 155905 | 2025-02-05 | 8:43 | 2025-02-05 | 11:54 | CRM13 | CARRUM | Urban | Planned |  | 44 | 8404 | 191 | 1 | No
| 155917 | 29/04/2025 | 10:30 | 29/04/2025 | 13:00 | MC12 | MORDIALLOC | Urban | Planned |  | 6 | 900 | 150 | 1 | No
| 155921 | 30/04/2025 | 10:30 | 30/04/2025 | 12:00 | MC12 | MORDIALLOC | Urban | Planned |  | 4 | 360 | 90 | 1 | No
| 155921 | 30/04/2025 | 10:30 | 30/04/2025 | 12:00 | MC21 | MORDIALLOC | Urban | Planned |  | 8 | 720 | 90 | 1 | No
| 155922 | 21/05/2025 | 8:20 | 21/05/2025 | 11:55 | MGE34 | MULGRAVE | Urban | Planned |  | 40 | 8600 | 215 | 1 | No
| 155923 | 19/06/2025 | 8:00 | 19/06/2025 | 13:25 | DN10 | DANDENONG | Urban | Planned |  | 53 | 17225 | 325 | 1 | No
| 155925 | 21/05/2025 | 12:15 | 21/05/2025 | 13:45 | MGE34 | MULGRAVE | Urban | Planned |  | 64 | 5760 | 90 | 1 | No
| 155928 | 28/04/2025 | 8:57 | 28/04/2025 | 12:32 | CFD24 | CAULFIELD | Urban | Planned |  | 71 | 15265 | 215 | 1 | No
| 155931 | 13/05/2025 | 8:19 | 13/05/2025 | 12:53 | DC3 | DONCASTER | Urban | Planned |  | 74 | 20276 | 274 | 1 | No
| 155933 | 14/05/2025 | 7:29 | 14/05/2025 | 7:30 | NO31 | NOTTING HILL | Urban | Planned |  | 9 | 9 | 1 | 1 | No
| 155935 | 13/05/2025 | 8:00 | 13/05/2025 | 12:43 | CM25 | CHELTENHAM | Urban | Planned |  | 214 | 60526.3262 | 282.8333 | 1 | No
| 155936 | 16/04/2025 | 7:50 | 16/04/2025 | 15:25 | EL33 | ELSTERNWICK | Urban | Planned |  | 5 | 2275 | 455 | 1 | No
| 155937 | 18/05/2025 | 8:00 | 18/05/2025 | 9:22 | CDA21 | CLARINDA | Urban | Planned |  | 8 | 656 | 82 | 1 | No
| 155938 | 2025-01-05 | 9:00 | 2025-01-05 | 14:30 | BU24 | BULLEEN | Urban | Planned |  | 1 | 330 | 330 | 1 | No
| 155939 | 18/05/2025 | 11:32 | 18/05/2025 | 12:55 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 10 | 830 | 83 | 1 | No
| 155941 | 20/05/2025 | 11:00 | 20/05/2025 | 11:42 | CDA21 | CLARINDA | Urban | Planned |  | 49 | 2058 | 42 | 2 | No
| 155941 | 20/05/2025 | 11:00 | 20/05/2025 | 15:30 | CDA21 | CLARINDA | Urban | Planned |  | 1 | 270 | 270 | 1 | No
| 155945 | 2025-12-05 | 9:30 | 2025-12-05 | 12:45 | OR24 | ORMOND | Urban | Planned |  | 5 | 975 | 195 | 1 | No
| 155946 | 28/04/2025 | 9:00 | 28/04/2025 | 14:45 | EB33 | EAST BURWOOD | Urban | Planned |  | 92 | 31740 | 345 | 1 | No
| 155947 | 30/04/2025 | 9:45 | 30/04/2025 | 15:30 | FTN12 | FRANKSTON | Urban | Planned |  | 46 | 15870 | 345 | 1 | No
| 155949 | 2025-01-05 | 10:00 | 2025-01-05 | 13:15 | CFD15 | CAULFIELD | Urban | Planned |  | 170 | 33150 | 195 | 1 | No
| 155950 | 2025-09-05 | 8:38 | 2025-09-05 | 11:33 | HGS32 | HASTINGS | Urban | Planned |  | 4 | 700 | 175 | 1 | No
| 155951 | 2025-01-05 | 8:02 | 2025-01-05 | 14:12 | FTN12 | FRANKSTON | Urban | Planned |  | 25 | 9250 | 370 | 1 | No
| 155958 | 23/05/2025 | 9:25 | 23/05/2025 | 9:40 | OE13 | OAKLEIGH EAST | Urban | Planned |  | 111 | 1665 | 15 | 1 | No
| 155961 | 2025-04-05 | 8:01 | 2025-04-05 | 17:30 | NW31 | NUNAWADING | Urban | Planned |  | 1 | 569.3167 | 569.3167 | 1 | No
| 155961 | 2025-04-05 | 8:48 | 2025-04-05 | 12:36 | NW31 | NUNAWADING | Urban | Planned |  | 37 | 8436 | 228 | 1 | No
| 155964 | 26/04/2025 | 8:04 | 26/04/2025 | 8:50 | MC23 | MORDIALLOC | Urban | Planned |  | 14 | 644 | 46 | 1 | No
| 155964 | 26/04/2025 | 8:04 | 26/04/2025 | 8:50 | MC32 | MORDIALLOC | Urban | Planned |  | 2 | 92 | 46 | 1 | No
| 155970 | 2025-05-05 | 7:50 | 2025-05-05 | 9:39 | SS11 | SPRINGVALE SOUTH | Urban | Planned |  | 1 | 109 | 109 | 1 | No
| 155978 | 22/04/2025 | 6:30 | 22/04/2025 | 15:30 | HT6 | HEATHERTON | Urban | Planned |  | 2 | 1080 | 540 | 1 | No
| 155981 | 30/04/2025 | 8:18 | 30/04/2025 | 9:25 | OR32 | ORMOND | Urban | Planned |  | 45 | 3015 | 67 | 1 | No
| 155987 | 2025-01-05 | 20:21 | 2025-02-05 | 1:08 | MC12 | MORDIALLOC | Urban | Planned |  | 2 | 574 | 287 | 1 | No
| 155987 | 2025-01-05 | 20:21 | 2025-02-05 | 1:08 | MC21 | MORDIALLOC | Urban | Planned |  | 44 | 12628 | 287 | 1 | No
| 155988 | 2025-06-05 | 8:00 | 2025-06-05 | 15:30 | BT14 | BENTLEIGH | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 155988 | 2025-06-05 | 8:03 | 2025-06-05 | 13:34 | BT14 | BENTLEIGH | Urban | Planned |  | 65 | 21515 | 331 | 1 | No
| 155998 | 30/04/2025 | 8:00 | 30/04/2025 | 13:31 | DC2 | DONCASTER | Urban | Planned |  | 45 | 14895 | 331 | 2 | No
| 155998 | 30/04/2025 | 8:00 | 30/04/2025 | 16:00 | DC2 | DONCASTER | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 155998 | 30/04/2025 | 8:00 | 30/04/2025 | 13:31 | DC4 | DONCASTER | Urban | Planned |  | 55 | 18205 | 331 | 1 | No
| 156006 | 29/04/2025 | 21:33 | 30/04/2025 | 2:27 | GW11 | GLEN WAVERLEY | Urban | Planned |  | 9 | 2646 | 294 | 1 | No
| 156011 | 2025-09-05 | 8:10 | 2025-09-05 | 11:25 | MC23 | MORDIALLOC | Urban | Planned |  | 160 | 31200 | 195 | 1 | No
| 156016 | 20/05/2025 | 9:40 | 20/05/2025 | 11:35 | BU14 | BULLEEN | Urban | Planned |  | 36 | 4140 | 115 | 1 | No
| 156017 | 20/05/2025 | 12:00 | 20/05/2025 | 13:55 | BU14 | BULLEEN | Urban | Planned |  | 60 | 6900 | 115 | 1 | No
| 156020 | 29/04/2025 | 1:33 | 29/04/2025 | 3:19 | OAK22 | OAKLEIGH | Urban | Planned |  | 15 | 1590 | 106 | 1 | No
| 156023 | 27/04/2025 | 8:08 | 27/04/2025 | 13:38 | M32 | MENTONE | Urban | Planned |  | 21 | 6930 | 330 | 1 | No
| 156024 | 2025-01-05 | 8:48 | 2025-01-05 | 14:56 | DN10 | DANDENONG | Urban | Planned |  | 23 | 8464 | 368 | 1 | No
| 156027 | 2025-04-05 | 7:05 | 2025-04-05 | 12:55 | DN24 | DANDENONG | Urban | Planned |  | 39 | 13650 | 350 | 1 | No
| 156029 | 2025-09-05 | 8:00 | 2025-09-05 | 9:55 | NB34 | NORTH BRIGHTON | Urban | Planned |  | 51 | 5865 | 115 | 1 | No
| 156031 | 2025-02-05 | 8:00 | 2025-02-05 | 9:57 | MTN24 | MORNINGTON | Rural Short | Planned |  | 20 | 2340 | 117 | 1 | No
| 156032 | 2025-06-05 | 8:01 | 2025-06-05 | 10:20 | EB13 | EAST BURWOOD | Urban | Planned |  | 2 | 278.6666 | 139.3333 | 1 | No
| 156042 | 20/05/2025 | 8:04 | 20/05/2025 | 13:48 | BU21 | BULLEEN | Urban | Planned |  | 17 | 5848 | 344 | 1 | No
| 156043 | 22/05/2025 | 8:20 | 22/05/2025 | 11:10 | STO14 | SORRENTO | Rural Short | Planned |  | 1 | 170 | 170 | 1 | No
| 156044 | 22/05/2025 | 8:13 | 22/05/2025 | 13:05 | STO22 | SORRENTO | Urban | Planned |  | 22 | 6424 | 292 | 1 | No
| 156046 | 23/05/2025 | 8:00 | 23/05/2025 | 11:30 | FTN13 | FRANKSTON | Urban | Planned |  | 47 | 9870 | 210 | 1 | No
| 156047 | 23/05/2025 | 12:20 | 23/05/2025 | 13:57 | CRM14 | CARRUM | Rural Short | Planned |  | 25 | 2425 | 97 | 1 | No
| 156049 | 30/04/2025 | 4:12 | 30/04/2025 | 5:20 | SV20 | SPRINGVALE | Urban | Planned |  | 22 | 1496 | 68 | 1 | No
| 156053 | 21/05/2025 | 8:00 | 21/05/2025 | 11:17 | DMA14 | DROMANA | Urban | Planned |  | 11 | 2167 | 197 | 1 | No
| 156055 | 21/05/2025 | 8:01 | 21/05/2025 | 11:12 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 29 | 5539 | 191 | 1 | No
| 156059 | 2025-04-05 | 9:00 | 2025-04-05 | 14:05 | EM6 | EAST MALVERN | Urban | Planned |  | 141 | 43005 | 305 | 1 | No
| 156062 | 15/04/2025 | 8:08 | 15/04/2025 | 13:15 | OAK35 | OAKLEIGH | Urban | Planned |  | 1 | 307 | 307 | 1 | No
| 156065 | 2025-10-05 | 7:05 | 2025-10-05 | 14:45 | SS14 | SPRINGVALE SOUTH | Urban | Planned |  | 2 | 920 | 460 | 1 | No
| 156070 | 2025-08-05 | 8:03 | 2025-08-05 | 12:00 | BT14 | BENTLEIGH | Urban | Planned |  | 142 | 33654 | 237 | 1 | No
| 156071 | 29/04/2025 | 8:01 | 29/04/2025 | 11:29 | WD23 | WEST DONCASTER | Urban | Planned |  | 11 | 2288 | 208 | 1 | No
| 156079 | 14/05/2025 | 8:20 | 14/05/2025 | 14:10 | RBD21 | ROSEBUD | Rural Short | Planned |  | 35 | 12250 | 350 | 1 | No
| 156080 | 22/05/2025 | 8:02 | 22/05/2025 | 15:15 | HGS22 | HASTINGS | Rural Short | Planned |  | 15 | 6495 | 433 | 1 | No
| 156080 | 22/05/2025 | 8:02 | 22/05/2025 | 15:15 | HGS33 | HASTINGS | Rural Short | Planned |  | 9 | 3897 | 433 | 1 | No
| 156081 | 28/05/2025 | 8:00 | 28/05/2025 | 14:40 | MGE24 | MULGRAVE | Urban | Planned |  | 76 | 30400 | 400 | 1 | No
| 156081 | 28/05/2025 | 8:00 | 28/05/2025 | 14:40 | SVW45 | SPRINGVALE WEST | Urban | Planned |  | 83 | 33200 | 400 | 1 | No
| 156083 | 22/06/2025 | 8:50 | 22/06/2025 | 10:05 | KBH33 | KEYSBOROUGH | Urban | Planned |  | 4 | 300 | 75 | 1 | No
| 156087 | 2025-05-05 | 8:40 | 2025-05-05 | 14:30 | EL22 | ELSTERNWICK | Urban | Planned |  | 113 | 39550 | 350 | 1 | No
| 156090 | 21/05/2025 | 8:30 | 21/05/2025 | 11:20 | SR21 | SANDRINGHAM | Urban | Planned |  | 2 | 340 | 170 | 1 | No
| 156094 | 13/05/2025 | 8:45 | 13/05/2025 | 16:50 | CRM15 | CARRUM | Urban | Planned |  | 346 | 167810 | 485 | 1 | No
| 156100 | 2025-07-05 | 8:05 | 2025-07-05 | 18:50 | LD4 | LYNDALE | Urban | Planned |  | 3 | 1935 | 645 | 1 | No
| 156104 | 31/05/2025 | 6:02 | 31/05/2025 | 13:09 | OR32 | ORMOND | Urban | Planned |  | 6 | 2562 | 427 | 1 | No
| 156105 | 2025-06-05 | 8:01 | 2025-06-05 | 16:31 | DMA15 | DROMANA | Rural Short | Planned |  | 1 | 510 | 510 | 1 | No
| 156105 | 2025-06-05 | 9:35 | 2025-06-05 | 14:35 | DMA15 | DROMANA | Rural Short | Planned |  | 5 | 1500 | 300 | 1 | No
| 156107 | 2025-09-05 | 9:05 | 2025-09-05 | 15:35 | HGS22 | HASTINGS | Rural Short | Planned |  | 42 | 16380 | 390 | 1 | No
| 156108 | 18/05/2025 | 8:00 | 18/05/2025 | 14:25 | HT2 | HEATHERTON | Urban | Planned |  | 147 | 56536.2 | 384.6 | 1 | No
| 156108 | 18/05/2025 | 8:00 | 18/05/2025 | 14:25 | HT7 | HEATHERTON | Urban | Planned |  | 27 | 10384.2 | 384.6 | 1 | No
| 156116 | 25/05/2025 | 8:01 | 25/05/2025 | 15:45 | BU24 | BULLEEN | Urban | Planned |  | 14 | 6498.5662 | 464.1833 | 1 | No
| 156121 | 15/05/2025 | 8:00 | 15/05/2025 | 13:54 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 129 | 45666 | 354 | 1 | No
| 156123 | 2025-08-05 | 8:11 | 2025-08-05 | 12:30 | EB14 | EAST BURWOOD | Urban | Planned |  | 27 | 6993 | 259 | 1 | No
| 156128 | 16/05/2025 | 8:45 | 16/05/2025 | 11:30 | SH22 | SURREY HILLS | Urban | Planned |  | 66 | 10890 | 165 | 1 | No
| 156129 | 19/06/2025 | 9:13 | 19/06/2025 | 11:25 | MGE24 | MULGRAVE | Urban | Planned |  | 32 | 4224 | 132 | 1 | No
| 156130 | 2025-02-05 | 8:00 | 2025-02-05 | 16:30 | DC12 | DONCASTER | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 156130 | 2025-02-05 | 8:04 | 2025-02-05 | 16:55 | DC12 | DONCASTER | Urban | Planned |  | 223 | 118413 | 531 | 1 | No
| 156131 | 25/05/2025 | 8:10 | 25/05/2025 | 17:40 | DVY32 | DANDENONG VALLEY | Urban | Planned |  | 16 | 9120 | 570 | 1 | No
| 156134 | 18/05/2025 | 8:10 | 18/05/2025 | 15:15 | MC12 | MORDIALLOC | Urban | Planned |  | 61 | 25925 | 425 | 1 | No
| 156134 | 18/05/2025 | 8:10 | 18/05/2025 | 15:15 | MC21 | MORDIALLOC | Urban | Planned |  | 13 | 5525 | 425 | 1 | No
| 156140 | 24/04/2025 | 4:00 | 24/04/2025 | 6:00 | NO3 | NOTTING HILL | Urban | Planned |  | 2 | 240 | 120 | 1 | No
| 156140 | 24/04/2025 | 4:12 | 24/04/2025 | 5:30 | NO3 | NOTTING HILL | Urban | Planned |  | 10 | 780 | 78 | 1 | No
| 156141 | 2025-06-05 | 9:25 | 2025-06-05 | 13:15 | CFD26 | CAULFIELD | Urban | Planned |  | 32 | 7360 | 230 | 1 | No
| 156142 | 2025-07-05 | 8:00 | 2025-07-05 | 16:00 | DMA23 | DROMANA | Rural Short | Planned |  | 1 | 480 | 480 | 1 | No
| 156142 | 2025-07-05 | 8:51 | 2025-07-05 | 13:47 | DMA23 | DROMANA | Rural Short | Planned |  | 117 | 34632 | 296 | 1 | No
| 156143 | 15/05/2025 | 8:17 | 15/05/2025 | 13:36 | OR34 | ORMOND | Urban | Planned |  | 7 | 2233 | 319 | 1 | No
| 156144 | 2025-02-05 | 8:22 | 2025-02-05 | 15:24 | FTN12 | FRANKSTON | Urban | Planned |  | 33 | 13926 | 422 | 1 | No
| 156147 | 2025-12-05 | 9:08 | 2025-12-05 | 15:15 | MGE23 | MULGRAVE | Urban | Planned |  | 28 | 10276 | 367 | 1 | No
| 156162 | 2025-03-06 | 9:00 | 2025-03-06 | 12:49 | BH21 | BOX HILL | Urban | Planned |  | 4 | 916 | 229 | 1 | No
| 156164 | 2025-08-05 | 8:47 | 2025-08-05 | 11:11 | M32 | MENTONE | Urban | Planned |  | 2 | 288 | 144 | 1 | No
| 156166 | 22/05/2025 | 9:03 | 22/05/2025 | 11:03 | FSH21 | FRANKSTON SOUTH | Rural Short | Planned |  | 35 | 4200 | 120 | 1 | No
| 156167 | 2025-08-05 | 9:52 | 2025-08-05 | 11:23 | OR35 | ORMOND | Urban | Planned |  | 43 | 3913 | 91 | 1 | No
| 156168 | 2025-08-05 | 8:30 | 2025-08-05 | 11:55 | BW34 | BURWOOD | Urban | Planned |  | 9 | 1845 | 205 | 1 | No
| 156170 | 13/05/2025 | 8:10 | 13/05/2025 | 11:35 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 36 | 7380 | 205 | 1 | No
| 156170 | 13/05/2025 | 8:10 | 13/05/2025 | 11:35 | GW8 | GLEN WAVERLEY | Urban | Planned |  | 52 | 10660 | 205 | 1 | No
| 156173 | 2025-05-05 | 8:55 | 2025-05-05 | 18:30 | MGE12 | MULGRAVE | Urban | Planned |  | 21 | 12075 | 575 | 1 | No
| 156181 | 2025-08-05 | 12:00 | 2025-08-05 | 14:50 | STO21 | SORRENTO | Rural Short | Planned |  | 20 | 3397.334 | 169.8667 | 1 | No
| 156182 | 2025-10-05 | 7:40 | 2025-10-05 | 13:20 | DVY33 | DANDENONG VALLEY | Urban | Planned |  | 15 | 5100 | 340 | 1 | No
| 156184 | 26/05/2025 | 10:25 | 26/05/2025 | 10:35 | CFD16 | CAULFIELD | Urban | Planned |  | 6 | 60 | 10 | 1 | No
| 156192 | 2025-06-05 | 8:14 | 2025-06-05 | 10:49 | HGS22 | HASTINGS | Rural Short | Planned |  | 6 | 930 | 155 | 1 | No
| 156195 | 2025-06-05 | 8:45 | 2025-06-05 | 10:35 | M34 | MENTONE | Urban | Planned |  | 23 | 2530 | 110 | 1 | No
| 156196 | 2025-06-05 | 11:43 | 2025-06-05 | 14:03 | M34 | MENTONE | Urban | Planned |  | 34 | 4760 | 140 | 1 | No
| 156198 | 2025-06-05 | 8:00 | 2025-06-05 | 16:00 | M13 | MENTONE | Urban | Planned |  | 22 | 10560 | 480 | 1 | No
| 156199 | 2025-07-05 | 8:03 | 2025-07-05 | 14:15 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 29 | 10788 | 372 | 1 | No
| 156200 | 2025-01-05 | 8:40 | 2025-01-05 | 12:45 | SS24 | SPRINGVALE SOUTH | Urban | Planned |  | 3 | 735 | 245 | 1 | No
| 156206 | 2025-07-05 | 8:45 | 2025-07-05 | 13:10 | K31 | GARDINER | Urban | Planned |  | 38 | 10070 | 265 | 1 | No
| 156207 | 2025-07-05 | 8:00 | 2025-07-05 | 16:00 | CFD22 | CAULFIELD | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 156207 | 2025-07-05 | 8:40 | 2025-07-05 | 13:37 | CFD22 | CAULFIELD | Urban | Planned |  | 137 | 40689 | 297 | 1 | No
| 156214 | 29/04/2025 | 8:02 | 29/04/2025 | 12:59 | HGS23 | HASTINGS | Rural Short | Planned |  | 38 | 11286 | 297 | 1 | No
| 156216 | 2025-08-05 | 21:02 | 2025-09-05 | 2:33 | MC12 | MORDIALLOC | Urban | Planned |  | 89 | 29459 | 331 | 1 | No
| 156218 | 15/06/2025 | 8:00 | 15/06/2025 | 11:26 | NP12 | NOBLE PARK | Urban | Planned |  | 38 | 7828 | 206 | 1 | No
| 156219 | 15/05/2025 | 8:00 | 15/05/2025 | 14:00 | MC12 | MORDIALLOC | Urban | Planned |  | 49 | 17640 | 360 | 1 | No
| 156221 | 2025-09-05 | 8:33 | 2025-09-05 | 13:52 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 7 | 2233 | 319 | 1 | No
| 156222 | 2025-06-05 | 8:10 | 2025-06-05 | 10:45 | MTN31 | MORNINGTON | Urban | Planned |  | 226 | 35030 | 155 | 1 | No
| 156227 | 31/05/2025 | 7:35 | 31/05/2025 | 10:35 | MGE14 | MULGRAVE | Urban | Planned |  | 34 | 6120 | 180 | 1 | No
| 156228 | 2025-08-05 | 8:45 | 2025-08-05 | 13:00 | MTN34 | MORNINGTON | Urban | Planned |  | 44 | 11220 | 255 | 1 | No
| 156230 | 28/06/2025 | 6:03 | 28/06/2025 | 21:02 | CDA21 | CLARINDA | Urban | Planned |  | 2 | 1798 | 899 | 1 | No
| 156232 | 31/05/2025 | 12:35 | 31/05/2025 | 13:20 | MGE13 | MULGRAVE | Urban | Planned |  | 1 | 45 | 45 | 1 | No
| 156234 | 25/05/2025 | 8:00 | 25/05/2025 | 18:10 | MC12 | MORDIALLOC | Urban | Planned |  | 120 | 73200 | 610 | 1 | No
| 156235 | 22/06/2025 | 8:09 | 22/06/2025 | 12:06 | M32 | MENTONE | Urban | Planned |  | 46 | 10902 | 237 | 1 | No
| 156237 | 2025-09-05 | 8:00 | 2025-09-05 | 10:15 | MTN23 | MORNINGTON | Urban | Planned |  | 24 | 3240 | 135 | 1 | No
| 156238 | 2025-09-05 | 10:50 | 2025-09-05 | 14:10 | MTN31 | MORNINGTON | Urban | Planned |  | 50 | 10000 | 200 | 1 | No
| 156246 | 30/05/2025 | 8:15 | 30/05/2025 | 12:47 | DC7 | DONCASTER | Urban | Planned |  | 60 | 16320 | 272 | 1 | No
| 156248 | 28/05/2025 | 8:00 | 28/05/2025 | 16:00 | BU21 | BULLEEN | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 156248 | 28/05/2025 | 8:10 | 28/05/2025 | 14:56 | BU21 | BULLEEN | Urban | Planned |  | 46 | 18676 | 406 | 1 | No
| 156249 | 29/05/2025 | 8:48 | 29/05/2025 | 13:26 | BU21 | BULLEEN | Urban | Planned |  | 26 | 7228 | 278 | 1 | No
| 156252 | 27/05/2025 | 8:02 | 27/05/2025 | 13:02 | M35 | MENTONE | Urban | Planned |  | 185 | 55500 | 300 | 1 | No
| 156259 | 30/05/2025 | 8:01 | 30/05/2025 | 10:33 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 39 | 5928 | 152 | 1 | No
| 156267 | 15/06/2025 | 8:00 | 15/06/2025 | 12:13 | CDA23 | CLARINDA | Urban | Planned |  | 34 | 8602 | 253 | 1 | No
| 156268 | 2025-08-05 | 9:45 | 2025-08-05 | 11:45 | SH22 | SURREY HILLS | Urban | Planned |  | 1 | 120 | 120 | 1 | No
| 156273 | 21/05/2025 | 8:06 | 21/05/2025 | 12:30 | M34 | MENTONE | Urban | Planned |  | 91 | 24024 | 264 | 1 | No
| 156276 | 2025-06-05 | 8:05 | 2025-06-05 | 15:50 | KBH32 | KEYSBOROUGH | Urban | Planned |  | 1 | 465 | 465 | 1 | No
| 156285 | 2025-08-05 | 8:00 | 2025-08-05 | 15:25 | SS23 | SPRINGVALE SOUTH | Urban | Planned |  | 49 | 21805 | 445 | 1 | No
| 156286 | 2025-08-05 | 10:40 | 2025-08-05 | 14:20 | EB14 | EAST BURWOOD | Urban | Planned |  | 21 | 4620 | 220 | 1 | No
| 156287 | 2025-07-05 | 8:28 | 2025-07-05 | 16:36 | OAK32 | OAKLEIGH | Urban | Planned |  | 29 | 14152 | 488 | 1 | No
| 156289 | 2025-09-05 | 9:00 | 2025-09-05 | 11:22 | K33 | GARDINER | Urban | Planned |  | 12 | 1704 | 142 | 1 | No
| 156299 | 2025-09-05 | 8:00 | 2025-09-05 | 12:09 | WD15 | WEST DONCASTER | Urban | Planned |  | 129 | 32121 | 249 | 1 | No
| 156303 | 2025-05-06 | 10:32 | 2025-05-06 | 13:06 | BU21 | BULLEEN | Urban | Planned |  | 44 | 6776 | 154 | 1 | No
| 156304 | 15/05/2025 | 11:56 | 15/05/2025 | 14:45 | MTN22 | MORNINGTON | Rural Short | Planned |  | 22 | 3718 | 169 | 1 | No
| 156305 | 29/06/2025 | 8:01 | 29/06/2025 | 16:20 | MR12 | MOORABBIN | Urban | Planned |  | 31 | 15469 | 499 | 1 | No
| 156305 | 29/06/2025 | 8:01 | 29/06/2025 | 16:20 | MR13 | MOORABBIN | Urban | Planned |  | 114 | 56886 | 499 | 1 | No
| 156305 | 29/06/2025 | 8:01 | 29/06/2025 | 16:20 | MR21 | MOORABBIN | Urban | Planned |  | 24 | 11976 | 499 | 1 | No
| 156306 | 15/05/2025 | 12:20 | 15/05/2025 | 14:52 | MTN22 | MORNINGTON | Rural Short | Planned |  | 56 | 8512 | 152 | 1 | No
| 156308 | 2025-12-05 | 11:30 | 2025-12-05 | 13:00 | MTN32 | MORNINGTON | Rural Short | Planned |  | 3 | 270 | 90 | 1 | No
| 156309 | 2025-09-05 | 8:00 | 2025-09-05 | 12:25 | DC1 | DONCASTER | Urban | Planned |  | 8 | 2120 | 265 | 1 | No
| 156310 | 2025-05-06 | 7:50 | 2025-05-06 | 8:55 | BU21 | BULLEEN | Urban | Planned |  | 1 | 65 | 65 | 1 | No
| 156312 | 2025-12-05 | 9:30 | 2025-12-05 | 13:48 | DN21 | DANDENONG | Urban | Planned |  | 9 | 2322 | 258 | 1 | No
| 156316 | 15/05/2025 | 8:03 | 15/05/2025 | 9:58 | SR24 | SANDRINGHAM | Urban | Planned |  | 6 | 690 | 115 | 1 | No
| 156321 | 15/05/2025 | 12:01 | 15/05/2025 | 13:03 | OR25 | ORMOND | Urban | Planned |  | 13 | 806 | 62 | 1 | No
| 156322 | 2025-08-05 | 8:00 | 2025-08-05 | 16:00 | OAK33 | OAKLEIGH | Urban | Planned |  | 2 | 960 | 480 | 1 | No
| 156322 | 2025-08-05 | 8:15 | 2025-08-05 | 12:50 | OAK33 | OAKLEIGH | Urban | Planned |  | 139 | 38225 | 275 | 1 | No
| 156327 | 2025-12-05 | 9:08 | 2025-12-05 | 14:22 | WD23 | WEST DONCASTER | Urban | Planned |  | 51 | 16014 | 314 | 1 | No
| 156328 | 2025-12-05 | 8:24 | 2025-12-05 | 10:55 | HT4 | HEATHERTON | Urban | Planned |  | 26 | 3926 | 151 | 1 | No
| 156335 | 13/05/2025 | 8:07 | 13/05/2025 | 15:15 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 137 | 58636 | 428 | 1 | No
| 156338 | 18/05/2025 | 8:01 | 18/05/2025 | 13:22 | STO13 | SORRENTO | Urban | Planned |  | 21 | 6746.6007 | 321.2667 | 1 | No
| 156343 | 2025-02-06 | 8:32 | 2025-02-06 | 11:15 | BU21 | BULLEEN | Urban | Planned |  | 11 | 1793 | 163 | 1 | No
| 156345 | 2025-06-06 | 8:00 | 2025-06-06 | 10:40 | BU25 | BULLEEN | Urban | Planned |  | 32 | 5120 | 160 | 1 | No
| 156347 | 2025-12-05 | 9:19 | 2025-12-05 | 10:50 | HGS33 | HASTINGS | Rural Short | Planned |  | 1 | 91 | 91 | 1 | No
| 156354 | 23/04/2025 | 9:06 | 23/04/2025 | 9:32 | MTN24 | MORNINGTON | Rural Short | Planned |  | 2 | 52 | 26 | 1 | No
| 156360 | 13/05/2025 | 8:20 | 13/05/2025 | 13:34 | MR33 | MOORABBIN | Urban | Planned |  | 24 | 7536 | 314 | 1 | No
| 156361 | 14/05/2025 | 8:30 | 14/05/2025 | 14:20 | CRM23 | CARRUM | Urban | Planned |  | 149 | 52150 | 350 | 2 | No
| 156361 | 14/05/2025 | 8:30 | 14/05/2025 | 15:30 | CRM23 | CARRUM | Urban | Planned |  | 2 | 840 | 420 | 1 | No
| 156363 | 13/05/2025 | 14:11 | 13/05/2025 | 16:00 | NB36 | NORTH BRIGHTON | Urban | Planned |  | 33 | 3597 | 109 | 1 | No
| 156377 | 13/05/2025 | 8:00 | 13/05/2025 | 14:00 | M13 | MENTONE | Urban | Planned |  | 7 | 2520 | 360 | 1 | No
| 156379 | 15/05/2025 | 10:40 | 15/05/2025 | 11:37 | CFD16 | CAULFIELD | Urban | Planned |  | 2 | 114 | 57 | 1 | No
| 156380 | 15/05/2025 | 12:20 | 15/05/2025 | 13:20 | CFD16 | CAULFIELD | Urban | Planned |  | 2 | 120 | 60 | 1 | No
| 156381 | 18/05/2025 | 7:46 | 18/05/2025 | 10:14 | NW11 | NUNAWADING | Urban | Planned |  | 13 | 1924 | 148 | 1 | No
| 156384 | 18/05/2025 | 8:05 | 18/05/2025 | 16:15 | EB21 | EAST BURWOOD | Urban | Planned |  | 95 | 46550 | 490 | 1 | No
| 156385 | 14/05/2025 | 8:00 | 14/05/2025 | 10:17 | M13 | MENTONE | Urban | Planned |  | 60 | 8220 | 137 | 1 | No
| 156387 | 13/05/2025 | 12:25 | 13/05/2025 | 15:40 | M13 | MENTONE | Urban | Planned |  | 145 | 28275 | 195 | 1 | No
| 156388 | 20/05/2025 | 21:30 | 21/05/2025 | 2:20 | NO2 | NOTTING HILL | Urban | Planned |  | 7 | 2030 | 290 | 1 | No
| 156388 | 20/05/2025 | 21:30 | 21/05/2025 | 2:20 | NO6 | NOTTING HILL | Urban | Planned |  | 1 | 290 | 290 | 1 | No
| 156390 | 14/05/2025 | 8:13 | 14/05/2025 | 14:35 | DC4 | DONCASTER | Urban | Planned |  | 54 | 20628 | 382 | 1 | No
| 156392 | 2025-12-05 | 9:35 | 2025-12-05 | 9:51 | LWN35 | LANGWARRIN | Urban | Planned |  | 49 | 784 | 16 | 1 | No
| 156393 | 14/05/2025 | 10:18 | 14/05/2025 | 10:58 | CRM22 | CARRUM | Urban | Planned |  | 47 | 1880 | 40 | 1 | No
| 156401 | 22/05/2025 | 2:30 | 22/05/2025 | 2:36 | CFD13 | CAULFIELD | Urban | Planned |  | 3 | 18 | 6 | 1 | No
| 156409 | 22/05/2025 | 4:00 | 22/05/2025 | 4:02 | MR32 | MOORABBIN | Urban | Planned |  | 22 | 44 | 2 | 1 | No
| 156416 | 13/05/2025 | 8:20 | 13/05/2025 | 14:30 | EB31 | EAST BURWOOD | Urban | Planned |  | 5 | 1850 | 370 | 1 | No
| 156417 | 2025-12-05 | 13:13 | 2025-12-05 | 16:45 | NW22 | NUNAWADING | Urban | Planned |  | 97 | 20564 | 212 | 1 | No
| 156420 | 16/05/2025 | 8:40 | 16/05/2025 | 12:32 | WD23 | WEST DONCASTER | Urban | Planned |  | 42 | 9744 | 232 | 1 | No
| 156425 | 21/05/2025 | 8:00 | 21/05/2025 | 11:57 | SR34 | SANDRINGHAM | Urban | Planned |  | 71 | 16827 | 237 | 1 | No
| 156428 | 21/05/2025 | 11:26 | 21/05/2025 | 14:55 | SR34 | SANDRINGHAM | Urban | Planned |  | 70 | 14630 | 209 | 1 | No
| 156429 | 2025-12-05 | 8:01 | 2025-12-05 | 14:18 | NW13 | NUNAWADING | Urban | Planned |  | 67 | 25264.5811 | 377.0833 | 1 | No
| 156430 | 20/05/2025 | 8:16 | 20/05/2025 | 10:48 | SV33 | SPRINGVALE | Urban | Planned |  | 33 | 5016 | 152 | 1 | No
| 156433 | 21/05/2025 | 11:52 | 21/05/2025 | 13:17 | SR24 | SANDRINGHAM | Urban | Planned |  | 48 | 4080 | 85 | 1 | No
| 156435 | 21/05/2025 | 8:42 | 21/05/2025 | 11:10 | HT2 | HEATHERTON | Urban | Planned |  | 56 | 8288 | 148 | 1 | No
| 156436 | 19/05/2025 | 8:30 | 19/05/2025 | 8:58 | HT11 | HEATHERTON | Urban | Planned |  | 188 | 5264 | 28 | 1 | No
| 156439 | 2025-12-05 | 13:26 | 2025-12-05 | 15:06 | NW22 | NUNAWADING | Urban | Planned |  | 3 | 300 | 100 | 1 | No
| 156440 | 2025-12-05 | 10:01 | 2025-12-05 | 14:01 | NW22 | NUNAWADING | Urban | Planned |  | 11 | 2640 | 240 | 1 | No
| 156445 | 2025-12-05 | 10:30 | 2025-12-05 | 11:00 | NW22 | NUNAWADING | Urban | Planned |  | 3 | 90 | 30 | 1 | No
| 156449 | 29/05/2025 | 10:30 | 29/05/2025 | 16:30 | BU22 | BULLEEN | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 156449 | 29/05/2025 | 11:31 | 29/05/2025 | 14:55 | BU14 | BULLEEN | Urban | Planned |  | 107 | 21828 | 204 | 1 | No
| 156449 | 29/05/2025 | 11:31 | 29/05/2025 | 14:55 | BU22 | BULLEEN | Urban | Planned |  | 50 | 10200 | 204 | 1 | No
| 156452 | 28/05/2025 | 8:00 | 28/05/2025 | 14:00 | FSH34 | FRANKSTON SOUTH | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 156452 | 28/05/2025 | 8:40 | 28/05/2025 | 15:22 | FSH34 | FRANKSTON SOUTH | Urban | Planned |  | 249 | 100098 | 402 | 1 | No
| 156453 | 17/05/2025 | 8:00 | 17/05/2025 | 16:30 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 1 | 510 | 510 | 1 | No
| 156453 | 17/05/2025 | 8:40 | 17/05/2025 | 14:31 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 62 | 21762 | 351 | 1 | No
| 156454 | 25/05/2025 | 8:01 | 25/05/2025 | 16:31 | SV32 | SPRINGVALE | Urban | Planned |  | 10 | 5100 | 510 | 1 | No
| 156454 | 25/05/2025 | 8:12 | 25/05/2025 | 15:45 | SV32 | SPRINGVALE | Urban | Planned |  | 609 | 275877 | 453 | 1 | No
| 156457 | 22/05/2025 | 10:02 | 22/05/2025 | 13:22 | MR15 | MOORABBIN | Urban | Planned |  | 90 | 18000 | 200 | 1 | No
| 156458 | 27/05/2025 | 8:00 | 27/05/2025 | 13:15 | HGS33 | HASTINGS | Rural Short | Planned |  | 35 | 11025 | 315 | 1 | No
| 156462 | 13/05/2025 | 6:00 | 13/05/2025 | 16:45 | SR21 | SANDRINGHAM | Urban | Planned |  | 63 | 40635 | 645 | 1 | No
| 156463 | 15/05/2025 | 8:00 | 15/05/2025 | 15:30 | EM5 | EAST MALVERN | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 156463 | 15/05/2025 | 8:05 | 15/05/2025 | 15:15 | EM5 | EAST MALVERN | Urban | Planned |  | 33 | 14190 | 430 | 1 | No
| 156463 | 15/05/2025 | 8:05 | 15/05/2025 | 15:15 | RD10 | RIVERSDALE | Urban | Planned |  | 63 | 27090 | 430 | 1 | No
| 156464 | 13/05/2025 | 17:35 | 13/05/2025 | 21:47 | GW10 | GLEN WAVERLEY | Urban | Planned |  | 8 | 2016 | 252 | 1 | No
| 156465 | 22/05/2025 | 8:12 | 22/05/2025 | 11:22 | KBH32 | KEYSBOROUGH | Urban | Planned |  | 1 | 190 | 190 | 1 | No
| 156468 | 19/05/2025 | 11:00 | 19/05/2025 | 13:10 | NP16 | NOBLE PARK | Urban | Planned |  | 30 | 3900 | 130 | 1 | No
| 156478 | 25/05/2025 | 7:47 | 25/05/2025 | 10:15 | NW22 | NUNAWADING | Urban | Planned |  | 21 | 3108 | 148 | 1 | No
| 156485 | 18/05/2025 | 8:00 | 18/05/2025 | 16:00 | SV16 | SPRINGVALE | Urban | Planned |  | 3 | 1440 | 480 | 1 | No
| 156485 | 18/05/2025 | 8:05 | 18/05/2025 | 13:00 | SS11 | SPRINGVALE SOUTH | Urban | Planned |  | 28 | 8260 | 295 | 1 | No
| 156485 | 18/05/2025 | 8:05 | 18/05/2025 | 13:00 | SV16 | SPRINGVALE | Urban | Planned |  | 150 | 44250 | 295 | 1 | No
| 156487 | 16/05/2025 | 8:00 | 16/05/2025 | 13:53 | DC4 | DONCASTER | Urban | Planned |  | 51 | 18003 | 353 | 1 | No
| 156488 | 13/05/2025 | 8:00 | 13/05/2025 | 16:30 | FTN14 | FRANKSTON | Urban | Planned |  | 8 | 4080 | 510 | 1 | No
| 156490 | 16/05/2025 | 8:10 | 16/05/2025 | 12:08 | LD32 | LYNDALE | Urban | Planned |  | 246 | 58548 | 238 | 1 | No
| 156492 | 14/05/2025 | 21:36 | 15/05/2025 | 7:00 | OR24 | ORMOND | Urban | Planned |  | 1 | 564 | 564 | 1 | No
| 156497 | 26/05/2025 | 8:02 | 26/05/2025 | 15:57 | DC1 | DONCASTER | Urban | Planned |  | 46 | 21850 | 475 | 1 | No
| 156497 | 26/05/2025 | 8:02 | 26/05/2025 | 15:57 | DC2 | DONCASTER | Urban | Planned |  | 34 | 16150 | 475 | 1 | No
| 156497 | 26/05/2025 | 8:02 | 26/05/2025 | 15:57 | DC4 | DONCASTER | Urban | Planned |  | 75 | 35625 | 475 | 1 | No
| 156501 | 20/05/2025 | 8:06 | 20/05/2025 | 13:26 | MTN24 | MORNINGTON | Rural Short | Planned |  | 32 | 10240 | 320 | 1 | No
| 156502 | 16/05/2025 | 8:23 | 16/05/2025 | 9:50 | DC4 | DONCASTER | Urban | Planned |  | 1 | 87 | 87 | 1 | No
| 156503 | 14/05/2025 | 8:40 | 14/05/2025 | 14:55 | OR24 | ORMOND | Urban | Planned |  | 6 | 2250 | 375 | 1 | No
| 156504 | 15/05/2025 | 8:35 | 15/05/2025 | 10:15 | EB33 | EAST BURWOOD | Urban | Planned |  | 26 | 2600 | 100 | 1 | No
| 156505 | 21/05/2025 | 8:25 | 21/05/2025 | 14:05 | FSH12 | FRANKSTON SOUTH | Rural Short | Planned |  | 9 | 3060 | 340 | 1 | No
| 156506 | 28/05/2025 | 8:15 | 28/05/2025 | 14:16 | HGS22 | HASTINGS | Rural Short | Planned |  | 198 | 71478 | 361 | 1 | No
| 156509 | 19/05/2025 | 9:00 | 19/05/2025 | 11:15 | BU14 | BULLEEN | Urban | Planned |  | 43 | 5805 | 135 | 1 | No
| 156510 | 19/05/2025 | 12:20 | 19/05/2025 | 14:00 | DC3 | DONCASTER | Urban | Planned |  | 25 | 2500 | 100 | 1 | No
| 156539 | 28/05/2025 | 9:35 | 28/05/2025 | 17:20 | EM2 | EAST MALVERN | Urban | Planned |  | 117 | 54405 | 465 | 1 | No
| 156545 | 29/05/2025 | 8:52 | 29/05/2025 | 12:37 | RBD22 | ROSEBUD | Urban | Planned |  | 7 | 1575 | 225 | 1 | No
| 156546 | 29/05/2025 | 11:30 | 29/05/2025 | 16:00 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 1 | 270 | 270 | 1 | No
| 156546 | 29/05/2025 | 13:30 | 29/05/2025 | 15:00 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 58 | 5220 | 90 | 1 | No
| 156550 | 20/05/2025 | 8:27 | 20/05/2025 | 15:47 | GW8 | GLEN WAVERLEY | Urban | Planned |  | 141 | 62040 | 440 | 1 | No
| 156553 | 21/05/2025 | 9:00 | 21/05/2025 | 18:18 | LD6 | LYNDALE | Urban | Planned |  | 117 | 65286 | 558 | 1 | No
| 156566 | 30/05/2025 | 8:36 | 30/05/2025 | 16:58 | WD26 | WEST DONCASTER | Urban | Planned |  | 77 | 38654 | 502 | 1 | No
| 156567 | 24/05/2025 | 10:17 | 24/05/2025 | 13:14 | CRM14 | CARRUM | Rural Short | Planned |  | 25 | 4425 | 177 | 1 | No
| 156572 | 24/05/2025 | 8:00 | 24/05/2025 | 11:00 | DSH32 | DANDENONG SOUTH | Urban | Planned |  | 47 | 8460 | 180 | 1 | No
| 156573 | 23/05/2025 | 8:04 | 23/05/2025 | 10:10 | HGS22 | HASTINGS | Rural Short | Planned |  | 6 | 756 | 126 | 1 | No
| 156574 | 2025-06-06 | 8:30 | 2025-06-06 | 13:10 | DN25 | DANDENONG | Urban | Planned |  | 16 | 4480 | 280 | 1 | No
| 156575 | 23/05/2025 | 11:07 | 23/05/2025 | 13:10 | HGS22 | HASTINGS | Rural Short | Planned |  | 3 | 369 | 123 | 1 | No
| 156578 | 31/05/2025 | 9:28 | 31/05/2025 | 14:15 | K33 | GARDINER | Urban | Planned |  | 180 | 51660 | 287 | 1 | No
| 156579 | 23/05/2025 | 8:01 | 23/05/2025 | 16:31 | NW31 | NUNAWADING | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 156579 | 23/05/2025 | 9:40 | 23/05/2025 | 12:50 | NW31 | NUNAWADING | Urban | Planned |  | 15 | 2850 | 190 | 1 | No
| 156580 | 2025-03-05 | 0:00 | 2025-03-05 | 19:10 | MGE22 | MULGRAVE | Urban | Planned |  | 1 | 1150 | 1150 | 1 | No
| 156582 | 26/05/2025 | 9:17 | 26/05/2025 | 12:12 | LD1 | LYNDALE | Urban | Planned |  | 51 | 8925 | 175 | 1 | No
| 156583 | 26/05/2025 | 13:00 | 26/05/2025 | 15:28 | LD2 | LYNDALE | Urban | Planned |  | 58 | 8584 | 148 | 1 | No
| 156588 | 15/05/2025 | 8:10 | 15/05/2025 | 11:05 | MTN22 | MORNINGTON | Rural Short | Planned |  | 50 | 8750 | 175 | 1 | No
| 156592 | 18/06/2025 | 8:05 | 18/06/2025 | 10:43 | SR24 | SANDRINGHAM | Urban | Planned |  | 60 | 9480 | 158 | 1 | No
| 156593 | 29/05/2025 | 9:16 | 29/05/2025 | 12:10 | CFD15 | CAULFIELD | Urban | Planned |  | 29 | 5046 | 174 | 1 | No
| 156599 | 23/05/2025 | 8:24 | 23/05/2025 | 9:52 | OR33 | ORMOND | Urban | Planned |  | 79 | 6952 | 88 | 1 | No
| 156600 | 27/05/2025 | 8:35 | 27/05/2025 | 12:58 | M23 | MENTONE | Urban | Planned |  | 48 | 12624 | 263 | 1 | No
| 156602 | 2025-01-06 | 7:35 | 2025-01-06 | 15:40 | FSH32 | FRANKSTON SOUTH | Rural Short | Planned |  | 1 | 485 | 485 | 1 | No
| 156603 | 2025-03-06 | 10:01 | 2025-03-06 | 11:08 | STO21 | SORRENTO | Rural Short | Planned |  | 1 | 67 | 67 | 1 | No
| 156610 | 27/05/2025 | 8:09 | 27/05/2025 | 15:43 | WD23 | WEST DONCASTER | Urban | Planned |  | 88 | 39952 | 454 | 1 | No
| 156614 | 22/05/2025 | 8:07 | 22/05/2025 | 14:04 | BT12 | BENTLEIGH | Urban | Planned |  | 31 | 11067 | 357 | 1 | No
| 156615 | 23/05/2025 | 11:28 | 23/05/2025 | 12:20 | M32 | MENTONE | Urban | Planned |  | 6 | 312 | 52 | 1 | No
| 156616 | 25/05/2025 | 6:45 | 25/05/2025 | 14:20 | M23 | MENTONE | Urban | Planned |  | 5 | 2275 | 455 | 1 | No
| 156633 | 2025-01-06 | 8:02 | 2025-01-06 | 13:10 | SV34 | SPRINGVALE | Urban | Planned |  | 95 | 29260 | 308 | 1 | No
| 156634 | 2025-11-06 | 8:52 | 2025-11-06 | 11:10 | BU15 | BULLEEN | Urban | Planned |  | 36 | 4968 | 138 | 1 | No
| 156638 | 28/05/2025 | 9:15 | 28/05/2025 | 12:05 | BT13 | BENTLEIGH | Urban | Planned |  | 27 | 4590 | 170 | 1 | No
| 156639 | 2025-08-06 | 8:06 | 2025-08-06 | 13:20 | DSH23 | DANDENONG SOUTH | Urban | Planned |  | 3 | 942 | 314 | 1 | No
| 156641 | 27/05/2025 | 8:33 | 27/05/2025 | 15:13 | EB12 | EAST BURWOOD | Urban | Planned |  | 5 | 2000 | 400 | 1 | No
| 156642 | 18/06/2025 | 9:05 | 18/06/2025 | 12:45 | AR6 | ARMADALE | Urban | Planned |  | 100 | 22000 | 220 | 1 | No
| 156654 | 28/05/2025 | 8:09 | 28/05/2025 | 9:07 | BT15 | BENTLEIGH | Urban | Planned |  | 29 | 1682 | 58 | 1 | No
| 156665 | 30/05/2025 | 8:05 | 30/05/2025 | 11:42 | DC3 | DONCASTER | Urban | Planned |  | 48 | 10416 | 217 | 1 | No
| 156667 | 25/05/2025 | 7:34 | 25/05/2025 | 11:50 | HT7 | HEATHERTON | Urban | Planned |  | 40 | 10240 | 256 | 1 | No
| 156672 | 25/05/2025 | 10:50 | 25/05/2025 | 11:04 | NW23 | NUNAWADING | Urban | Planned |  | 1 | 14 | 14 | 1 | No
| 156673 | 2025-04-06 | 8:43 | 2025-04-06 | 14:40 | RBD14 | ROSEBUD | Urban | Planned |  | 41 | 14637 | 357 | 1 | No
| 156674 | 2025-04-06 | 11:38 | 2025-04-06 | 13:14 | RBD21 | ROSEBUD | Rural Short | Planned |  | 1 | 96 | 96 | 1 | No
| 156679 | 25/05/2025 | 7:33 | 25/05/2025 | 10:35 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 3 | 546 | 182 | 1 | No
| 156682 | 28/05/2025 | 8:30 | 28/05/2025 | 10:25 | DN11 | DANDENONG | Urban | Planned |  | 59 | 6785 | 115 | 1 | No
| 156684 | 16/06/2025 | 8:37 | 16/06/2025 | 11:07 | MTN31 | MORNINGTON | Urban | Planned |  | 35 | 5250 | 150 | 1 | No
| 156689 | 2025-04-06 | 8:40 | 2025-04-06 | 13:10 | LWN35 | LANGWARRIN | Urban | Planned |  | 62 | 16740 | 270 | 1 | No
| 156690 | 2025-04-06 | 11:30 | 2025-04-06 | 16:00 | FSH34 | FRANKSTON SOUTH | Urban | Planned |  | 52 | 14040 | 270 | 1 | No
| 156692 | 27/05/2025 | 9:05 | 27/05/2025 | 12:19 | NW33 | NUNAWADING | Urban | Planned |  | 9 | 1746 | 194 | 1 | No
| 156693 | 23/05/2025 | 8:15 | 23/05/2025 | 13:08 | NP16 | NOBLE PARK | Urban | Planned |  | 153 | 44829 | 293 | 1 | No
| 156694 | 27/05/2025 | 12:44 | 27/05/2025 | 14:45 | NW33 | NUNAWADING | Urban | Planned |  | 35 | 4235 | 121 | 1 | No
| 156698 | 29/05/2025 | 9:00 | 29/05/2025 | 15:30 | MR13 | MOORABBIN | Urban | Planned |  | 1 | 390 | 390 | 1 | No
| 156698 | 29/05/2025 | 9:50 | 29/05/2025 | 13:35 | MR13 | MOORABBIN | Urban | Planned |  | 178 | 40050 | 225 | 1 | No
| 156699 | 2025-03-06 | 8:45 | 2025-03-06 | 15:25 | SR25 | SANDRINGHAM | Urban | Planned |  | 119 | 47600 | 400 | 1 | No
| 156700 | 2025-05-06 | 8:15 | 2025-05-06 | 11:18 | FSH34 | FRANKSTON SOUTH | Urban | Planned |  | 33 | 6039 | 183 | 1 | No
| 156703 | 27/05/2025 | 20:48 | 28/05/2025 | 3:39 | WD15 | WEST DONCASTER | Urban | Planned |  | 4 | 1644 | 411 | 1 | No
| 156703 | 27/05/2025 | 20:48 | 28/05/2025 | 3:39 | WD23 | WEST DONCASTER | Urban | Planned |  | 1 | 411 | 411 | 1 | No
| 156707 | 2025-01-06 | 8:30 | 2025-01-06 | 14:45 | EM11 | EAST MALVERN | Urban | Planned |  | 74 | 27750 | 375 | 1 | No
| 156708 | 29/05/2025 | 8:18 | 29/05/2025 | 14:44 | CDA22 | CLARINDA | Urban | Planned |  | 20 | 7720 | 386 | 1 | No
| 156710 | 29/05/2025 | 11:12 | 29/05/2025 | 13:50 | SVW53 | SPRINGVALE WEST | Urban | Planned |  | 14 | 2212 | 158 | 1 | No
| 156712 | 30/05/2025 | 8:00 | 30/05/2025 | 11:30 | HT11 | HEATHERTON | Urban | Planned |  | 1 | 210 | 210 | 1 | No
| 156712 | 30/05/2025 | 8:02 | 30/05/2025 | 9:22 | HT11 | HEATHERTON | Urban | Planned |  | 53 | 4240 | 80 | 1 | No
| 156714 | 30/05/2025 | 9:00 | 30/05/2025 | 13:35 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 21 | 5775 | 275 | 1 | No
| 156719 | 27/05/2025 | 8:00 | 27/05/2025 | 16:00 | MTN31 | MORNINGTON | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 156719 | 27/05/2025 | 8:18 | 27/05/2025 | 13:50 | MTN31 | MORNINGTON | Urban | Planned |  | 153 | 50796 | 332 | 1 | No
| 156725 | 2025-04-06 | 8:20 | 2025-04-06 | 12:27 | GW7 | GLEN WAVERLEY | Urban | Planned |  | 2 | 494 | 247 | 1 | No
| 156726 | 19/06/2025 | 9:31 | 19/06/2025 | 12:42 | DMA14 | DROMANA | Urban | Planned |  | 36 | 6876 | 191 | 1 | No
| 156733 | 15/06/2025 | 8:02 | 15/06/2025 | 17:20 | KBH32 | KEYSBOROUGH | Urban | Planned |  | 68 | 37944 | 558 | 1 | No
| 156742 | 27/05/2025 | 8:07 | 27/05/2025 | 15:43 | STO13 | SORRENTO | Urban | Planned |  | 56 | 25536 | 456 | 1 | No
| 156745 | 2025-04-06 | 8:05 | 2025-04-06 | 11:20 | DC1 | DONCASTER | Urban | Planned |  | 78 | 15210 | 195 | 1 | No
| 156746 | 26/05/2025 | 8:56 | 26/05/2025 | 13:27 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 41 | 11111 | 271 | 1 | No
| 156747 | 17/06/2025 | 8:00 | 17/06/2025 | 14:42 | HGS32 | HASTINGS | Urban | Planned |  | 222 | 89244 | 402 | 1 | No
| 156748 | 25/05/2025 | 7:00 | 25/05/2025 | 15:30 | OR32 | ORMOND | Urban | Planned |  | 3 | 1530 | 510 | 1 | No
| 156751 | 2025-02-06 | 10:56 | 2025-02-06 | 15:58 | EM11 | EAST MALVERN | Urban | Planned |  | 89 | 26878 | 302 | 1 | No
| 156753 | 2025-05-06 | 8:10 | 2025-05-06 | 14:40 | MC12 | MORDIALLOC | Urban | Planned |  | 47 | 18330 | 390 | 1 | No
| 156756 | 25/05/2025 | 20:30 | 26/05/2025 | 0:30 | EM5 | EAST MALVERN | Urban | Planned |  | 27 | 6480 | 240 | 1 | No
| 156759 | 30/05/2025 | 9:12 | 30/05/2025 | 12:46 | SR31 | SANDRINGHAM | Urban | Planned |  | 9 | 1926 | 214 | 1 | No
| 156761 | 2025-06-06 | 10:10 | 2025-06-06 | 13:55 | DMA13 | DROMANA | Rural Short | Planned |  | 3 | 675 | 225 | 1 | No
| 156762 | 31/05/2025 | 8:20 | 31/05/2025 | 11:55 | FTN13 | FRANKSTON | Urban | Planned |  | 36 | 7740 | 215 | 1 | No
| 156770 | 23/06/2025 | 12:26 | 23/06/2025 | 13:57 | FTN25 | FRANKSTON | Urban | Planned |  | 113 | 10283 | 91 | 1 | No
| 156777 | 2025-08-06 | 8:00 | 2025-08-06 | 16:30 | GW10 | GLEN WAVERLEY | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 156777 | 2025-08-06 | 8:15 | 2025-08-06 | 16:30 | GW10 | GLEN WAVERLEY | Urban | Planned |  | 73 | 36135 | 495 | 1 | No
| 156778 | 17/06/2025 | 8:50 | 17/06/2025 | 15:10 | K31 | GARDINER | Urban | Planned |  | 159 | 60420 | 380 | 1 | No
| 156787 | 16/06/2025 | 10:07 | 16/06/2025 | 14:46 | MGE23 | MULGRAVE | Urban | Planned |  | 62 | 17298 | 279 | 1 | No
| 156796 | 2025-11-06 | 8:00 | 2025-11-06 | 15:48 | SVW41 | SPRINGVALE WEST | Urban | Planned |  | 108 | 50544 | 468 | 1 | No
| 156796 | 2025-11-06 | 8:00 | 2025-11-06 | 15:48 | SVW56 | SPRINGVALE WEST | Urban | Planned |  | 18 | 8424 | 468 | 1 | No
| 156799 | 2025-01-06 | 8:10 | 2025-01-06 | 12:41 | OE5 | OAKLEIGH EAST | Urban | Planned |  | 17 | 4607 | 271 | 1 | No
| 156800 | 29/05/2025 | 11:05 | 29/05/2025 | 14:10 | CRM22 | CARRUM | Urban | Planned |  | 14 | 2590 | 185 | 1 | No
| 156801 | 29/05/2025 | 8:40 | 29/05/2025 | 10:35 | CRM13 | CARRUM | Urban | Planned |  | 45 | 5175 | 115 | 1 | No
| 156805 | 2025-07-06 | 8:15 | 2025-07-06 | 11:05 | SVW53 | SPRINGVALE WEST | Urban | Planned |  | 23 | 3910 | 170 | 1 | No
| 156808 | 2025-06-06 | 8:32 | 2025-06-06 | 13:25 | MR24 | MOORABBIN | Urban | Planned |  | 87 | 25491 | 293 | 1 | No
| 156810 | 2025-06-06 | 9:30 | 2025-06-06 | 11:30 | DMA21 | DROMANA | Urban | Planned |  | 4 | 480 | 120 | 1 | No
| 156815 | 30/05/2025 | 8:58 | 30/05/2025 | 10:31 | BH31 | BOX HILL | Urban | Planned |  | 50 | 4650 | 93 | 1 | No
| 156827 | 2025-05-06 | 8:02 | 2025-05-06 | 8:25 | DVY34 | DANDENONG VALLEY | Urban | Planned |  | 9 | 207 | 23 | 1 | No
| 156828 | 2025-05-06 | 8:03 | 2025-05-06 | 12:50 | GW7 | GLEN WAVERLEY | Urban | Planned |  | 2 | 574 | 287 | 1 | No
| 156829 | 2025-05-06 | 8:01 | 2025-05-06 | 16:00 | MR22 | MOORABBIN | Urban | Planned |  | 110 | 52690 | 479 | 1 | No
| 156830 | 2025-05-06 | 9:35 | 2025-05-06 | 11:00 | MC23 | MORDIALLOC | Urban | Planned |  | 3 | 255 | 85 | 1 | No
| 156833 | 30/05/2025 | 8:12 | 30/05/2025 | 10:37 | CM22 | CHELTENHAM | Urban | Planned |  | 77 | 11165 | 145 | 1 | No
| 156836 | 2025-12-06 | 8:00 | 2025-12-06 | 14:43 | HGS22 | HASTINGS | Rural Short | Planned |  | 79 | 31837 | 403 | 1 | No
| 156838 | 2025-01-06 | 8:00 | 2025-01-06 | 16:45 | SR21 | SANDRINGHAM | Urban | Planned |  | 56 | 29400 | 525 | 1 | No
| 156851 | 23/05/2025 | 7:30 | 23/05/2025 | 13:50 | MGE12 | MULGRAVE | Urban | Planned |  | 24 | 9114 | 379.75 | 1 | No
| 156853 | 2025-03-06 | 8:10 | 2025-03-06 | 13:45 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 13 | 4355 | 335 | 1 | No
| 156853 | 2025-03-06 | 8:10 | 2025-03-06 | 13:45 | LWN34 | LANGWARRIN | Urban | Planned |  | 28 | 9380 | 335 | 1 | No
| 156854 | 2025-01-06 | 8:00 | 2025-01-06 | 11:00 | EL24 | ELSTERNWICK | Urban | Planned |  | 11 | 1980 | 180 | 1 | No
| 156859 | 26/05/2025 | 0:53 | 26/05/2025 | 1:56 | AR6 | ARMADALE | Urban | Planned |  | 18 | 1134 | 63 | 1 | No
| 156861 | 2025-04-06 | 8:00 | 2025-04-06 | 15:20 | MR24 | MOORABBIN | Urban | Planned |  | 3 | 1320 | 440 | 1 | No
| 156864 | 2025-12-06 | 9:03 | 2025-12-06 | 13:53 | EB22 | EAST BURWOOD | Urban | Planned |  | 56 | 16240 | 290 | 1 | No
| 156865 | 2025-01-06 | 8:00 | 2025-01-06 | 10:35 | HT2 | HEATHERTON | Urban | Planned |  | 109 | 16895 | 155 | 1 | No
| 156866 | 29/05/2025 | 8:15 | 29/05/2025 | 14:55 | HT8 | HEATHERTON | Urban | Planned |  | 1 | 400 | 400 | 1 | No
| 156867 | 2025-03-06 | 8:00 | 2025-03-06 | 11:30 | GW2 | GLEN WAVERLEY | Urban | Planned |  | 1 | 210 | 210 | 1 | No
| 156870 | 2025-01-06 | 8:00 | 2025-01-06 | 15:11 | CDA23 | CLARINDA | Urban | Planned |  | 24 | 10344 | 431 | 1 | No
| 156871 | 2025-01-06 | 8:02 | 2025-01-06 | 16:43 | CDA23 | CLARINDA | Urban | Planned |  | 8 | 4168 | 521 | 1 | No
| 156873 | 29/05/2025 | 9:14 | 29/05/2025 | 12:56 | MR13 | MOORABBIN | Urban | Planned |  | 8 | 1776 | 222 | 1 | No
| 156874 | 2025-01-06 | 11:00 | 2025-01-06 | 13:35 | SV34 | SPRINGVALE | Urban | Planned |  | 12 | 1860 | 155 | 1 | No
| 156879 | 22/06/2025 | 8:00 | 22/06/2025 | 16:00 | MC21 | MORDIALLOC | Urban | Planned |  | 1 | 480 | 480 | 1 | No
| 156879 | 22/06/2025 | 8:20 | 22/06/2025 | 18:41 | MC21 | MORDIALLOC | Urban | Planned |  | 33 | 20493 | 621 | 1 | No
| 156880 | 2025-04-06 | 8:35 | 2025-04-06 | 13:02 | DMA14 | DROMANA | Urban | Planned |  | 16 | 4272 | 267 | 1 | No
| 156883 | 2025-03-06 | 8:55 | 2025-03-06 | 12:10 | FSH11 | FRANKSTON SOUTH | Urban | Planned |  | 6 | 1170 | 195 | 1 | No
| 156885 | 2025-03-06 | 12:45 | 2025-03-06 | 15:25 | HGS22 | HASTINGS | Rural Short | Planned |  | 68 | 10880 | 160 | 1 | No
| 156888 | 2025-03-06 | 8:00 | 2025-03-06 | 11:58 | SR31 | SANDRINGHAM | Urban | Planned |  | 74 | 17612 | 238 | 1 | No
| 156889 | 2025-03-06 | 8:40 | 2025-03-06 | 11:30 | SV34 | SPRINGVALE | Urban | Planned |  | 21 | 3570 | 170 | 1 | No
| 156891 | 2025-03-06 | 12:42 | 2025-03-06 | 14:35 | CM25 | CHELTENHAM | Urban | Planned |  | 54 | 6102 | 113 | 1 | No
| 156893 | 2025-03-06 | 9:57 | 2025-03-06 | 12:14 | EM9 | EAST MALVERN | Urban | Planned |  | 18 | 2466 | 137 | 1 | No
| 156894 | 2025-10-06 | 9:47 | 2025-10-06 | 14:55 | DN11 | DANDENONG | Urban | Planned |  | 39 | 12012 | 308 | 1 | No
| 156895 | 2025-04-06 | 11:00 | 2025-04-06 | 15:34 | MR33 | MOORABBIN | Urban | Planned |  | 59 | 16166 | 274 | 1 | No
| 156897 | 2025-03-06 | 10:00 | 2025-03-06 | 15:00 | K35 | GARDINER | Urban | Planned |  | 4 | 1200 | 300 | 1 | No
| 156898 | 2025-05-06 | 8:00 | 2025-05-06 | 11:10 | SR26 | SANDRINGHAM | Urban | Planned |  | 61 | 11590 | 190 | 1 | No
| 156899 | 2025-05-06 | 13:00 | 2025-05-06 | 16:30 | MR12 | MOORABBIN | Urban | Planned |  | 131 | 27510 | 210 | 1 | No
| 156904 | 17/06/2025 | 8:00 | 17/06/2025 | 13:40 | STO13 | SORRENTO | Urban | Planned |  | 201 | 68340 | 340 | 2 | No
| 156904 | 17/06/2025 | 8:00 | 17/06/2025 | 15:30 | STO13 | SORRENTO | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 156905 | 18/06/2025 | 8:49 | 18/06/2025 | 12:13 | STO23 | SORRENTO | Urban | Planned |  | 11 | 2244 | 204 | 1 | No
| 156907 | 2025-06-06 | 8:00 | 2025-06-06 | 16:30 | MR32 | MOORABBIN | Urban | Planned |  | 1 | 510 | 510 | 1 | No
| 156907 | 2025-06-06 | 8:03 | 2025-06-06 | 14:03 | MR32 | MOORABBIN | Urban | Planned |  | 61 | 21960 | 360 | 1 | No
| 156909 | 2025-11-06 | 9:15 | 2025-11-06 | 13:16 | LD7 | LYNDALE | Urban | Planned |  | 71 | 17111 | 241 | 1 | No
| 156911 | 2025-03-06 | 8:10 | 2025-03-06 | 12:15 | STO21 | SORRENTO | Rural Short | Planned |  | 2 | 490 | 245 | 1 | No
| 156912 | 2025-11-06 | 14:30 | 2025-11-06 | 15:00 | LD4 | LYNDALE | Urban | Planned |  | 1 | 30 | 30 | 1 | No
| 156914 | 2025-12-06 | 20:35 | 13/06/2025 | 3:20 | CRM13 | CARRUM | Urban | Planned |  | 255 | 103275 | 405 | 1 | No
| 156915 | 13/06/2025 | 9:29 | 13/06/2025 | 14:16 | OAK26 | OAKLEIGH | Urban | Planned |  | 80 | 22960 | 287 | 1 | No
| 156920 | 2025-01-06 | 7:38 | 2025-01-06 | 14:20 | BU14 | BULLEEN | Urban | Planned |  | 20 | 8040 | 402 | 1 | No
| 156928 | 16/06/2025 | 8:01 | 16/06/2025 | 10:15 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 54 | 7236 | 134 | 1 | No
| 156930 | 16/06/2025 | 8:00 | 16/06/2025 | 10:35 | CDA11 | CLARINDA | Urban | Planned |  | 40 | 6200 | 155 | 1 | No
| 156934 | 2025-04-06 | 9:05 | 2025-04-06 | 14:20 | CFD12 | CAULFIELD | Urban | Planned |  | 32 | 10080 | 315 | 1 | No
| 156943 | 2025-11-06 | 8:10 | 2025-11-06 | 11:43 | HGS33 | HASTINGS | Rural Short | Planned |  | 28 | 5964 | 213 | 1 | No
| 156944 | 2025-11-06 | 10:00 | 2025-11-06 | 15:31 | HGS31 | HASTINGS | Rural Short | Planned |  | 136 | 45016 | 331 | 1 | No
| 156948 | 2025-04-06 | 8:55 | 2025-04-06 | 13:20 | HGS23 | HASTINGS | Rural Short | Planned |  | 2 | 530 | 265 | 1 | No
| 156950 | 2025-12-06 | 8:20 | 2025-12-06 | 12:05 | MGE24 | MULGRAVE | Urban | Planned |  | 112 | 25200 | 225 | 1 | No
| 156961 | 2025-03-06 | 8:30 | 2025-03-06 | 13:45 | MTN21 | MORNINGTON | Urban | Planned |  | 2 | 630 | 315 | 1 | No
| 156961 | 2025-03-06 | 8:30 | 2025-03-06 | 13:45 | MTN23 | MORNINGTON | Urban | Planned |  | 9 | 2835 | 315 | 1 | No
| 156964 | 14/05/2025 | 18:00 | 15/05/2025 | 2:42 | NO31 | NOTTING HILL | Urban | Planned |  | 2 | 1044 | 522 | 1 | No
| 156972 | 2025-05-06 | 8:11 | 2025-05-06 | 15:32 | GW3 | GLEN WAVERLEY | Urban | Planned |  | 138 | 60858 | 441 | 1 | No
| 156976 | 17/06/2025 | 9:25 | 17/06/2025 | 13:14 | NW21 | NUNAWADING | Urban | Planned |  | 28 | 6412 | 229 | 1 | No
| 156988 | 21/06/2025 | 6:31 | 21/06/2025 | 15:44 | LD5 | LYNDALE | Urban | Planned |  | 4 | 2213.5332 | 553.3833 | 1 | No
| 156990 | 2025-11-06 | 7:50 | 2025-11-06 | 13:30 | SV20 | SPRINGVALE | Urban | Planned |  | 1 | 340 | 340 | 1 | No
| 156995 | 2025-10-06 | 3:42 | 2025-10-06 | 4:22 | BT25 | BENTLEIGH | Urban | Planned |  | 25 | 1000 | 40 | 1 | No
| 156999 | 2025-06-06 | 8:01 | 2025-06-06 | 9:05 | DMA23 | DROMANA | Rural Short | Planned |  | 75 | 4800 | 64 | 1 | No
| 157002 | 19/06/2025 | 3:38 | 19/06/2025 | 4:30 | EW2 | ELWOOD | Urban | Planned |  | 8 | 416 | 52 | 1 | No
| 157007 | 13/06/2025 | 8:02 | 13/06/2025 | 10:30 | CDA24 | CLARINDA | Urban | Planned |  | 35 | 5180 | 148 | 1 | No
| 157009 | 13/06/2025 | 12:30 | 13/06/2025 | 15:43 | MR14 | MOORABBIN | Urban | Planned |  | 5 | 965 | 193 | 1 | No
| 157009 | 13/06/2025 | 12:30 | 13/06/2025 | 15:43 | MR22 | MOORABBIN | Urban | Planned |  | 34 | 6562 | 193 | 1 | No
| 157023 | 2025-10-06 | 9:07 | 2025-10-06 | 11:39 | CRM33 | CARRUM | Urban | Planned |  | 74 | 11248 | 152 | 1 | No
| 157024 | 2025-11-06 | 8:54 | 2025-11-06 | 11:55 | CRM33 | CARRUM | Urban | Planned |  | 73 | 13213 | 181 | 1 | No
| 157026 | 22/06/2025 | 8:00 | 22/06/2025 | 11:27 | CRM24 | CARRUM | Urban | Planned |  | 9 | 1863 | 207 | 1 | No
| 157029 | 2025-12-06 | 9:04 | 2025-12-06 | 15:20 | EM6 | EAST MALVERN | Urban | Planned |  | 54 | 20304 | 376 | 1 | No
| 157031 | 13/06/2025 | 8:52 | 13/06/2025 | 11:47 | K27 | GARDINER | Urban | Planned |  | 29 | 5075 | 175 | 1 | No
| 157038 | 20/06/2025 | 9:53 | 20/06/2025 | 14:04 | LD32 | LYNDALE | Urban | Planned |  | 50 | 12550 | 251 | 1 | No
| 157040 | 20/06/2025 | 11:01 | 20/06/2025 | 15:01 | OAK26 | OAKLEIGH | Urban | Planned |  | 2 | 480 | 240 | 1 | No
| 157044 | 18/06/2025 | 11:00 | 18/06/2025 | 15:23 | STO23 | SORRENTO | Urban | Planned |  | 37 | 9731 | 263 | 1 | No
| 157047 | 25/06/2025 | 8:00 | 25/06/2025 | 10:42 | MR11 | MOORABBIN | Urban | Planned |  | 39 | 6318 | 162 | 1 | No
| 157048 | 2025-11-06 | 12:30 | 2025-11-06 | 13:30 | CRM33 | CARRUM | Urban | Planned |  | 36 | 2150.3988 | 59.7333 | 1 | No
| 157051 | 14/06/2025 | 8:20 | 14/06/2025 | 13:02 | HT8 | HEATHERTON | Urban | Planned |  | 2 | 564 | 282 | 1 | No
| 157052 | 2025-10-06 | 10:59 | 2025-10-06 | 14:00 | CDA24 | CLARINDA | Urban | Planned |  | 18 | 3258 | 181 | 1 | No
| 157058 | 2025-10-06 | 8:54 | 2025-10-06 | 11:03 | MR12 | MOORABBIN | Urban | Planned |  | 54 | 6966 | 129 | 1 | No
| 157066 | 25/06/2025 | 23:18 | 26/06/2025 | 4:00 | K23 | GARDINER | Urban | Planned |  | 291 | 82062 | 282 | 1 | No
| 157069 | 18/06/2025 | 8:10 | 18/06/2025 | 14:05 | STO14 | SORRENTO | Rural Short | Planned |  | 478 | 169690 | 355 | 1 | No
| 157080 | 16/06/2025 | 3:30 | 16/06/2025 | 5:35 | HT8 | HEATHERTON | Urban | Planned |  | 8 | 1000 | 125 | 1 | No
| 157081 | 2025-10-06 | 12:09 | 2025-10-06 | 13:25 | MR32 | MOORABBIN | Urban | Planned |  | 19 | 1444 | 76 | 1 | No
| 157083 | 2025-11-06 | 11:10 | 2025-11-06 | 13:15 | LWN34 | LANGWARRIN | Urban | Planned |  | 52 | 6500 | 125 | 1 | No
| 157096 | 25/06/2025 | 8:10 | 25/06/2025 | 12:25 | CDA11 | CLARINDA | Urban | Planned |  | 34 | 8670 | 255 | 1 | No
| 157097 | 25/06/2025 | 8:14 | 25/06/2025 | 12:25 | DMA24 | DROMANA | Rural Short | Planned |  | 23 | 5773 | 251 | 1 | No
| 157098 | 25/06/2025 | 13:28 | 25/06/2025 | 15:05 | CDA23 | CLARINDA | Urban | Planned |  | 43 | 4171 | 97 | 1 | No
| 157099 | 26/06/2025 | 8:45 | 26/06/2025 | 10:38 | CDA21 | CLARINDA | Urban | Planned |  | 2 | 226 | 113 | 1 | No
| 157101 | 13/06/2025 | 8:20 | 13/06/2025 | 11:45 | MR11 | MOORABBIN | Urban | Planned |  | 64 | 13120 | 205 | 1 | No
| 157103 | 27/06/2025 | 8:00 | 27/06/2025 | 10:26 | BU25 | BULLEEN | Urban | Planned |  | 33 | 4818 | 146 | 1 | No
| 157106 | 30/06/2025 | 8:00 | 30/06/2025 | 12:28 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 30 | 8040 | 268 | 1 | No
| 157107 | 30/06/2025 | 8:02 | 30/06/2025 | 11:45 | DMA24 | DROMANA | Rural Short | Planned |  | 121 | 26983 | 223 | 1 | No
| 157109 | 2025-11-06 | 9:16 | 2025-11-06 | 14:36 | MTN22 | MORNINGTON | Rural Short | Planned |  | 82 | 26240 | 320 | 1 | No
| 157111 | 20/06/2025 | 11:00 | 20/06/2025 | 12:20 | RBD23 | ROSEBUD | Urban | Planned |  | 122 | 9760 | 80 | 1 | No
| 157114 | 26/06/2025 | 8:35 | 26/06/2025 | 12:30 | DMA14 | DROMANA | Urban | Planned |  | 23 | 5405 | 235 | 1 | No
| 157116 | 24/06/2025 | 8:18 | 24/06/2025 | 10:19 | BU21 | BULLEEN | Urban | Planned |  | 18 | 2178 | 121 | 1 | No
| 157118 | 2025-11-06 | 8:03 | 2025-11-06 | 13:34 | WD36 | WEST DONCASTER | Urban | Planned |  | 211 | 69841 | 331 | 1 | No
| 157122 | 13/06/2025 | 8:00 | 13/06/2025 | 13:32 | M23 | MENTONE | Urban | Planned |  | 166 | 55112 | 332 | 2 | No
| 157122 | 13/06/2025 | 8:00 | 13/06/2025 | 15:30 | M23 | MENTONE | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 157125 | 13/06/2025 | 12:40 | 13/06/2025 | 15:40 | MR24 | MOORABBIN | Urban | Planned |  | 13 | 2340 | 180 | 1 | No
| 157131 | 2025-11-06 | 11:45 | 2025-11-06 | 14:20 | NB34 | NORTH BRIGHTON | Urban | Planned |  | 69 | 10695 | 155 | 1 | No
| 157137 | 2025-12-06 | 8:35 | 2025-12-06 | 10:20 | DC1 | DONCASTER | Urban | Planned |  | 16 | 1680 | 105 | 1 | No
| 157138 | 2025-12-06 | 10:45 | 2025-12-06 | 12:00 | DC1 | DONCASTER | Urban | Planned |  | 46 | 3450 | 75 | 1 | No
| 157140 | 17/06/2025 | 9:00 | 17/06/2025 | 10:50 | WD36 | WEST DONCASTER | Urban | Planned |  | 2 | 220 | 110 | 1 | No
| 157145 | 2025-11-06 | 8:30 | 2025-11-06 | 10:45 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 56 | 7560 | 135 | 1 | No
| 157149 | 18/06/2025 | 9:30 | 18/06/2025 | 12:00 | DC8 | DONCASTER | Urban | Planned |  | 58 | 8700 | 150 | 1 | No
| 157150 | 17/06/2025 | 8:35 | 17/06/2025 | 15:58 | MR14 | MOORABBIN | Urban | Planned |  | 45 | 19935 | 443 | 1 | No
| 157150 | 17/06/2025 | 8:35 | 17/06/2025 | 15:58 | MR22 | MOORABBIN | Urban | Planned |  | 62 | 27466 | 443 | 1 | No
| 157158 | 2025-12-06 | 12:10 | 2025-12-06 | 13:17 | DC3 | DONCASTER | Urban | Planned |  | 46 | 3082 | 67 | 1 | No
| 157166 | 2025-12-06 | 3:30 | 2025-12-06 | 4:16 | MGE32 | MULGRAVE | Urban | Planned |  | 187 | 8517.85 | 45.55 | 1 | No
| 157167 | 16/06/2025 | 8:40 | 16/06/2025 | 12:25 | MTN32 | MORNINGTON | Rural Short | Planned |  | 63 | 14175 | 225 | 1 | No
| 157172 | 2025-10-06 | 8:44 | 2025-10-06 | 11:00 | FSH13 | FRANKSTON SOUTH | Urban | Planned |  | 147 | 19992 | 136 | 1 | No
| 157186 | 2025-12-06 | 12:04 | 2025-12-06 | 14:28 | CRM33 | CARRUM | Urban | Planned |  | 38 | 5472 | 144 | 1 | No
| 157187 | 2025-12-06 | 8:30 | 2025-12-06 | 13:30 | CRM33 | CARRUM | Urban | Planned |  | 1 | 300 | 300 | 1 | No
| 157187 | 2025-12-06 | 8:57 | 2025-12-06 | 10:55 | CRM33 | CARRUM | Urban | Planned |  | 35 | 4130 | 118 | 1 | No
| 157188 | 13/06/2025 | 8:58 | 13/06/2025 | 11:45 | CRM23 | CARRUM | Urban | Planned |  | 34 | 5678 | 167 | 1 | No
| 157201 | 26/06/2025 | 8:35 | 26/06/2025 | 12:30 | SV16 | SPRINGVALE | Urban | Planned |  | 4 | 940 | 235 | 1 | No
| 157205 | 13/06/2025 | 8:31 | 13/06/2025 | 14:56 | MTN34 | MORNINGTON | Urban | Planned |  | 97 | 37345 | 385 | 1 | No
| 157207 | 2025-12-06 | 8:00 | 2025-12-06 | 15:07 | SVW55 | SPRINGVALE WEST | Urban | Planned |  | 7 | 2989 | 427 | 1 | No
| 157213 | 2025-12-06 | 13:08 | 2025-12-06 | 14:10 | CDA22 | CLARINDA | Urban | Planned |  | 1 | 62 | 62 | 1 | No
| 157217 | 18/06/2025 | 8:13 | 18/06/2025 | 12:37 | MTN32 | MORNINGTON | Rural Short | Planned |  | 17 | 4488 | 264 | 1 | No
| 157218 | 13/06/2025 | 8:02 | 13/06/2025 | 10:05 | CDA22 | CLARINDA | Urban | Planned |  | 3 | 369 | 123 | 1 | No
| 157219 | 17/06/2025 | 22:55 | 18/06/2025 | 2:50 | NB35 | NORTH BRIGHTON | Urban | Planned |  | 104 | 24440 | 235 | 1 | No
| 157223 | 2025-12-06 | 8:35 | 2025-12-06 | 15:45 | EB32 | EAST BURWOOD | Urban | Planned |  | 51 | 21930 | 430 | 1 | No
| 157225 | 18/06/2025 | 13:08 | 18/06/2025 | 13:56 | DMA23 | DROMANA | Rural Short | Planned |  | 6 | 288 | 48 | 1 | No
| 157228 | 13/06/2025 | 12:32 | 13/06/2025 | 13:41 | SS21 | SPRINGVALE SOUTH | Urban | Planned |  | 22 | 1518 | 69 | 1 | No
| 157230 | 23/06/2025 | 9:21 | 23/06/2025 | 13:21 | DN11 | DANDENONG | Urban | Planned |  | 130 | 31200 | 240 | 1 | No
| 157231 | 18/06/2025 | 8:03 | 18/06/2025 | 13:15 | M32 | MENTONE | Urban | Planned |  | 96 | 29952 | 312 | 1 | No
| 157241 | 18/06/2025 | 8:17 | 18/06/2025 | 13:28 | MC21 | MORDIALLOC | Urban | Planned |  | 37 | 11507 | 311 | 1 | No
| 157252 | 20/06/2025 | 8:00 | 20/06/2025 | 14:00 | NP33 | NOBLE PARK | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 157252 | 20/06/2025 | 8:25 | 20/06/2025 | 13:25 | NP33 | NOBLE PARK | Urban | Planned |  | 100 | 30000 | 300 | 1 | No
| 157252 | 20/06/2025 | 8:25 | 20/06/2025 | 13:25 | SS22 | SPRINGVALE SOUTH | Urban | Planned |  | 87 | 26100 | 300 | 1 | No
| 157253 | 21/06/2025 | 7:30 | 21/06/2025 | 12:25 | DSH21 | DANDENONG SOUTH | Urban | Planned |  | 180 | 53100 | 295 | 1 | No
| 157261 | 20/06/2025 | 8:57 | 20/06/2025 | 11:04 | NB35 | NORTH BRIGHTON | Urban | Planned |  | 29 | 3683 | 127 | 1 | No
| 157262 | 20/06/2025 | 8:00 | 20/06/2025 | 10:55 | NP36 | NOBLE PARK | Urban | Planned |  | 32 | 5600 | 175 | 1 | No
| 157266 | 17/06/2025 | 8:38 | 17/06/2025 | 10:36 | MR11 | MOORABBIN | Urban | Planned |  | 50 | 5900 | 118 | 1 | No
| 157267 | 20/06/2025 | 11:05 | 20/06/2025 | 13:40 | LD4 | LYNDALE | Urban | Planned |  | 223 | 34565 | 155 | 1 | No
| 157268 | 24/06/2025 | 8:00 | 24/06/2025 | 15:15 | DC3 | DONCASTER | Urban | Planned |  | 16 | 6960 | 435 | 1 | No
| 157271 | 14/06/2025 | 7:43 | 15/06/2025 | 1:20 | MGE24 | MULGRAVE | Urban | Planned |  | 1 | 1057 | 1057 | 1 | No
| 157274 | 14/06/2025 | 7:42 | 14/06/2025 | 15:15 | LD1 | LYNDALE | Urban | Planned |  | 4 | 1812 | 453 | 1 | No
| 157274 | 14/06/2025 | 7:42 | 14/06/2025 | 15:15 | NP16 | NOBLE PARK | Urban | Planned |  | 1 | 453 | 453 | 1 | No
| 157281 | 24/06/2025 | 8:03 | 24/06/2025 | 14:35 | SR24 | SANDRINGHAM | Urban | Planned |  | 175 | 68600 | 392 | 1 | No
| 157283 | 18/06/2025 | 8:00 | 18/06/2025 | 15:00 | OR23 | ORMOND | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 157283 | 18/06/2025 | 8:10 | 18/06/2025 | 10:39 | OR23 | ORMOND | Urban | Planned |  | 109 | 16241 | 149 | 1 | No
| 157288 | 20/06/2025 | 8:14 | 20/06/2025 | 10:55 | MC23 | MORDIALLOC | Urban | Planned |  | 27 | 4347 | 161 | 1 | No
| 157297 | 20/06/2025 | 8:15 | 20/06/2025 | 13:15 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 38 | 11400 | 300 | 1 | No
| 157305 | 18/06/2025 | 8:30 | 18/06/2025 | 17:05 | BW23 | BURWOOD | Urban | Planned |  | 30 | 15450 | 515 | 1 | No
| 157305 | 18/06/2025 | 8:30 | 18/06/2025 | 17:05 | BW34 | BURWOOD | Urban | Planned |  | 2 | 1030 | 515 | 1 | No
| 157306 | 14/06/2025 | 6:00 | 14/06/2025 | 14:00 | EW3 | ELWOOD | Urban | Planned |  | 22 | 10560 | 480 | 1 | No
| 157308 | 27/06/2025 | 8:00 | 27/06/2025 | 11:57 | RBD12 | ROSEBUD | Rural Short | Planned |  | 23 | 5451 | 237 | 1 | No
| 157309 | 27/06/2025 | 13:20 | 27/06/2025 | 14:52 | DMA23 | DROMANA | Rural Short | Planned |  | 101 | 9292 | 92 | 1 | No
| 157310 | 26/06/2025 | 8:55 | 26/06/2025 | 13:10 | FTN14 | FRANKSTON | Urban | Planned |  | 19 | 4845 | 255 | 1 | No
| 157314 | 19/06/2025 | 9:38 | 19/06/2025 | 12:27 | BT12 | BENTLEIGH | Urban | Planned |  | 52 | 8788 | 169 | 1 | No
| 157335 | 17/06/2025 | 20:45 | 18/06/2025 | 0:00 | MGE12 | MULGRAVE | Urban | Planned |  | 3 | 585 | 195 | 1 | No
| 157338 | 20/06/2025 | 8:44 | 20/06/2025 | 13:53 | SR24 | SANDRINGHAM | Urban | Planned |  | 88 | 27192 | 309 | 1 | No
| 157351 | 17/06/2025 | 9:06 | 17/06/2025 | 14:00 | OAK32 | OAKLEIGH | Urban | Planned |  | 42 | 12348 | 294 | 1 | No
| 157353 | 19/06/2025 | 8:12 | 19/06/2025 | 14:00 | MTN34 | MORNINGTON | Urban | Planned |  | 31 | 10788 | 348 | 1 | No
| 157362 | 21/06/2025 | 7:00 | 21/06/2025 | 15:30 | DVY31 | DANDENONG VALLEY | Urban | Planned |  | 6 | 3057.6 | 509.6 | 1 | No
| 157363 | 26/06/2025 | 8:27 | 26/06/2025 | 13:55 | BU24 | BULLEEN | Urban | Planned |  | 90 | 29520 | 328 | 1 | No
| 157368 | 25/06/2025 | 8:00 | 25/06/2025 | 9:16 | SR24 | SANDRINGHAM | Urban | Planned |  | 47 | 3572 | 76 | 1 | No
| 157372 | 20/06/2025 | 13:03 | 20/06/2025 | 16:06 | FSH33 | FRANKSTON SOUTH | Urban | Planned |  | 14 | 2562 | 183 | 1 | No
| 157381 | 24/06/2025 | 8:00 | 24/06/2025 | 10:55 | OR32 | ORMOND | Urban | Planned |  | 42 | 7350 | 175 | 1 | No
| 157392 | 17/06/2025 | 11:10 | 17/06/2025 | 14:00 | EB33 | EAST BURWOOD | Urban | Planned |  | 60 | 10200 | 170 | 1 | No
| 157394 | 17/06/2025 | 8:29 | 17/06/2025 | 11:41 | MTN34 | MORNINGTON | Urban | Planned |  | 79 | 15168 | 192 | 1 | No
| 157395 | 16/06/2025 | 10:25 | 16/06/2025 | 12:20 | FSH22 | FRANKSTON SOUTH | Urban | Planned |  | 26 | 2990 | 115 | 1 | No
| 157396 | 24/06/2025 | 8:02 | 24/06/2025 | 11:29 | OR33 | ORMOND | Urban | Planned |  | 185 | 38295 | 207 | 1 | No
| 157399 | 24/06/2025 | 10:07 | 24/06/2025 | 15:12 | GW10 | GLEN WAVERLEY | Urban | Planned |  | 10 | 3050 | 305 | 1 | No
| 157410 | 20/06/2025 | 9:31 | 20/06/2025 | 15:53 | FTN12 | FRANKSTON | Urban | Planned |  | 1 | 382 | 382 | 1 | No
| 157411 | 29/06/2025 | 7:30 | 29/06/2025 | 16:21 | LD1 | LYNDALE | Urban | Planned |  | 1 | 531 | 531 | 1 | No
| 157412 | 2025-04-06 | 7:04 | 2025-04-06 | 7:08 | RWT23 | RINGWOOD | Urban | Planned |  | 2 | 8 | 4 | 1 | No
| 157415 | 24/06/2025 | 8:02 | 24/06/2025 | 9:57 | OR23 | ORMOND | Urban | Planned |  | 20 | 2300 | 115 | 1 | No
| 157415 | 24/06/2025 | 8:02 | 24/06/2025 | 9:57 | OR32 | ORMOND | Urban | Planned |  | 35 | 4025 | 115 | 1 | No
| 157418 | 24/06/2025 | 11:00 | 24/06/2025 | 15:30 | OR23 | ORMOND | Urban | Planned |  | 1 | 270 | 270 | 1 | No
| 157418 | 24/06/2025 | 12:10 | 24/06/2025 | 14:52 | OR23 | ORMOND | Urban | Planned |  | 163 | 26406 | 162 | 1 | No
| 157425 | 19/06/2025 | 8:05 | 19/06/2025 | 11:05 | NP33 | NOBLE PARK | Urban | Planned |  | 24 | 4320 | 180 | 1 | No
| 157435 | 22/06/2025 | 8:01 | 22/06/2025 | 17:37 | NO2 | NOTTING HILL | Urban | Planned |  | 259 | 149184 | 576 | 1 | No
| 157435 | 22/06/2025 | 8:01 | 22/06/2025 | 17:37 | NO32 | NOTTING HILL | Urban | Planned |  | 8 | 4608 | 576 | 1 | No
| 157435 | 22/06/2025 | 8:01 | 22/06/2025 | 17:37 | NO5 | NOTTING HILL | Urban | Planned |  | 3 | 1728 | 576 | 1 | No
| 157438 | 22/06/2025 | 10:25 | 22/06/2025 | 11:43 | NO32 | NOTTING HILL | Urban | Planned |  | 1 | 78 | 78 | 1 | No
| 157443 | 19/06/2025 | 10:45 | 19/06/2025 | 13:15 | NP33 | NOBLE PARK | Urban | Planned |  | 140 | 21000 | 150 | 1 | No
| 157446 | 22/06/2025 | 8:05 | 22/06/2025 | 12:36 | CRM24 | CARRUM | Urban | Planned |  | 23 | 6233 | 271 | 1 | No
| 157448 | 27/06/2025 | 8:57 | 27/06/2025 | 12:35 | OAK33 | OAKLEIGH | Urban | Planned |  | 53 | 11554 | 218 | 1 | No
| 157449 | 25/06/2025 | 8:00 | 25/06/2025 | 12:15 | EM8 | EAST MALVERN | Urban | Planned |  | 13 | 3315 | 255 | 1 | No
| 157451 | 19/06/2025 | 8:30 | 19/06/2025 | 15:45 | K31 | GARDINER | Urban | Planned |  | 78 | 33930 | 435 | 1 | No
| 157467 | 22/06/2025 | 8:00 | 22/06/2025 | 15:30 | SVW42 | SPRINGVALE WEST | Urban | Planned |  | 1 | 450 | 450 | 1 | No
| 157474 | 26/06/2025 | 8:10 | 26/06/2025 | 11:02 | HT4 | HEATHERTON | Urban | Planned |  | 61 | 10492 | 172 | 1 | No
| 157487 | 26/06/2025 | 8:15 | 26/06/2025 | 11:15 | HT4 | HEATHERTON | Urban | Planned |  | 15 | 2700 | 180 | 1 | No
| 157492 | 27/06/2025 | 8:14 | 27/06/2025 | 10:43 | OR23 | ORMOND | Urban | Planned |  | 30 | 4470 | 149 | 1 | No
| 157495 | 29/06/2025 | 8:08 | 29/06/2025 | 14:48 | WD26 | WEST DONCASTER | Urban | Planned |  | 39 | 15600 | 400 | 1 | No
| 157495 | 29/06/2025 | 8:08 | 29/06/2025 | 14:48 | WD36 | WEST DONCASTER | Urban | Planned |  | 124 | 49600 | 400 | 1 | No
| 157505 | 25/06/2025 | 10:15 | 25/06/2025 | 13:33 | FTN12 | FRANKSTON | Urban | Planned |  | 63 | 12474 | 198 | 1 | No
| 157515 | 29/06/2025 | 8:15 | 29/06/2025 | 14:15 | NO2 | NOTTING HILL | Urban | Planned |  | 1 | 360 | 360 | 1 | No
| 157521 | 24/06/2025 | 8:30 | 24/06/2025 | 13:40 | DC4 | DONCASTER | Urban | Planned |  | 143 | 44330 | 310 | 1 | No
| 157522 | 30/06/2025 | 9:05 | 30/06/2025 | 17:15 | DVY24 | DANDENONG VALLEY | Rural Short | Planned |  | 26 | 12740 | 490 | 1 | No
| 157524 | 27/06/2025 | 8:37 | 27/06/2025 | 10:45 | BU24 | BULLEEN | Urban | Planned |  | 38 | 4864 | 128 | 1 | No
| 157528 | 26/06/2025 | 8:02 | 26/06/2025 | 11:00 | NP25 | NOBLE PARK | Urban | Planned |  | 99 | 17622 | 178 | 1 | No
| 157535 | 24/06/2025 | 8:45 | 24/06/2025 | 13:40 | CRM35 | CARRUM | Urban | Planned |  | 27 | 7965 | 295 | 1 | No
| 157540 | 22/06/2025 | 8:06 | 22/06/2025 | 13:20 | BH33 | BOX HILL | Urban | Planned |  | 1 | 314 | 314 | 1 | No
| 157545 | 13/06/2025 | 8:15 | 13/06/2025 | 14:00 | EB32 | EAST BURWOOD | Urban | Planned |  | 20 | 6900 | 345 | 1 | No
| 157547 | 13/06/2025 | 8:00 | 13/06/2025 | 15:00 | EB22 | EAST BURWOOD | Urban | Planned |  | 1 | 420 | 420 | 1 | No
| 157547 | 13/06/2025 | 8:25 | 13/06/2025 | 11:50 | EB22 | EAST BURWOOD | Urban | Planned |  | 22 | 4510 | 205 | 1 | No
| 157568 | 24/06/2025 | 8:29 | 24/06/2025 | 14:29 | FSH31 | FRANKSTON SOUTH | Urban | Planned |  | 56 | 20160 | 360 | 1 | No
| 157571 | 27/06/2025 | 8:05 | 27/06/2025 | 11:15 | SS13 | SPRINGVALE SOUTH | Urban | Planned |  | 18 | 3420 | 190 | 1 | No
| 157572 | 27/06/2025 | 8:10 | 27/06/2025 | 11:45 | SVW55 | SPRINGVALE WEST | Urban | Planned |  | 78 | 16770 | 215 | 1 | No
| 157573 | 27/06/2025 | 11:00 | 27/06/2025 | 12:26 | NP33 | NOBLE PARK | Urban | Planned |  | 10 | 860 | 86 | 1 | No
| 157598 | 29/06/2025 | 8:04 | 29/06/2025 | 13:43 | MTN21 | MORNINGTON | Urban | Planned |  | 79 | 26781 | 339 | 1 | No
| 157605 | 24/06/2025 | 9:05 | 24/06/2025 | 14:47 | HGS22 | HASTINGS | Rural Short | Planned |  | 2 | 684 | 342 | 1 | No
| 157605 | 24/06/2025 | 9:05 | 24/06/2025 | 14:47 | MTN32 | MORNINGTON | Rural Short | Planned |  | 12 | 4104 | 342 | 1 | No
| 157615 | 27/06/2025 | 8:10 | 27/06/2025 | 10:16 | MC21 | MORDIALLOC | Urban | Planned |  | 17 | 2142 | 126 | 1 | No
| 157623 | 24/06/2025 | 9:00 | 24/06/2025 | 15:20 | BU22 | BULLEEN | Urban | Planned |  | 6 | 2280 | 380 | 1 | No
| 157624 | 25/06/2025 | 9:03 | 25/06/2025 | 14:15 | BU15 | BULLEEN | Urban | Planned |  | 119 | 37128 | 312 | 1 | No
| 157639 | 26/06/2025 | 8:50 | 26/06/2025 | 14:50 | BT22 | BENTLEIGH | Urban | Planned |  | 80 | 28800 | 360 | 1 | No
| 157647 | 29/06/2025 | 8:00 | 29/06/2025 | 9:50 | MTN21 | MORNINGTON | Urban | Planned |  | 18 | 1980 | 110 | 1 | No
| 157661 | 25/06/2025 | 8:18 | 25/06/2025 | 11:01 | OR32 | ORMOND | Urban | Planned |  | 40 | 6520 | 163 | 1 | No
| 157666 | 24/06/2025 | 8:30 | 24/06/2025 | 11:30 | BU14 | BULLEEN | Urban | Planned |  | 8 | 1440 | 180 | 1 | No
| 157728 | 27/06/2025 | 9:00 | 27/06/2025 | 13:42 | MGE33 | MULGRAVE | Urban | Planned |  | 10 | 2820 | 282 | 1 | No
| 157731 | 29/06/2025 | 6:00 | 29/06/2025 | 14:00 | OAK22 | OAKLEIGH | Urban | Planned |  | 61 | 29280 | 480 | 1 | No
| 157760 | 29/06/2025 | 8:30 | 29/06/2025 | 11:14 | K35 | GARDINER | Urban | Planned |  | 5 | 820 | 164 | 1 | No
| 157818 | 29/06/2025 | 10:25 | 29/06/2025 | 12:30 | MTN21 | MORNINGTON | Urban | Planned |  | 16 | 2000 | 125 | 1 | No

## 3.1 Revenue
| ANNUAL INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| EB RIN 3.1 REVENUE |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC09 - Revenue and financial statements ¦ Standard control
DC09 - Revenue and financial statements ¦ Alternative control
Disaggregated revenue
3.1.1 - REVENUE GROUPING BY CHARGEABLE QUANTITY
Disaggregated revenue
| REVENUE GROUPING BY CHARGEABLE QUANTITY | Units | Standard control | Alternative control
DREV0101 | Fixed customer charges | $ | 61927642.87
DREV0102 | Energy delivery charges where time of use is not a determinant | $ | 198955915.86
DREV0103 | On–peak energy delivery charges | $ | 95751986.67
DREV0104 | Shoulder period energy delivery charges | $ | 0
DREV0105 | Off–peak energy delivery charges | $ | 31110986.18
DREV0106 | Controlled load customer charges | $ | 1217186.11
DREV0107 | Unmetered supplies | $ | 4381412.92
DREV0108 | Contracted maximum demand charges | $ | 0
DREV0109 | Measured maximum demand charges | $ | 107471635
DREV0110 | Metering charges | $ | 0 | 35292388.3
DREV0111 | Connection charges | $ | 0 | 8339660.58
DREV0112 | Public lighting charges | $ | 0 | 7875988.22
DREV0113 | Other sources | $ | 0 | 9958289
DREV01 | Total revenue | $ | 500816765.61 | 61466326.1
3.1.2 - REVENUE GROUPING BY CUSTOMER TYPE OR CLASS
Disaggregated revenue
| REVENUE GROUPING BY CUSTOMER TYPE OR CLASS | Units | Standard control | Alternative control
DREV0201 | Residential customers | $ | 308263653.4 | 0
DREV0202 | Non residential customers not on demand tariffs | $ | 25644100.2 | 0
DREV0203 | Non-residential low voltage demand tariff customers | $ | 145537086.73 | 0
DREV0204 | Non-residential high voltage demand tariff customers | $ | 16990511.93 | 0
DREV0205 | Unmetered customers | $ | 4381412.92 | 7875988.22
DREV0206 | Other customers | $ | 0 | 53590337.57
DREV02 | Total revenue | $ | 500816765.18 | 61466325.79
3.1.3 - REVENUE (penalties) ALLOWED (deducted) THROUGH INCENTIVE SCHEMES
Disaggregated revenue
| REVENUE REWARDS AND PENALTIES - INCENTIVE SCHEMES | Units | Standard control
DREV0301 | EBSS | $ | 16798782
DREV0306 | CESS | $ | 12899173
DREV0302 | STPIS | $ | 4393622
DREV0307 | CSIS | $ | 2364501
DREV0308 | ESIS | $ | 0
DREV0309 | DMIS/DMIA/DMIAM | $ | 703300
DREV0303 | F-Factor | $ | 182400
DREV0305 | Other incentive schemes | $ | -1086011
DREV03 | Total revenue rewards and penalties - incentive schemes | $ | 36255767

## 3.2 Operating expenditure
| ANNUAL INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| EB RIN 3.2 OPERATING EXPENDITURE |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC06 - Operating expenditure ¦ Standard control
DC06 - Operating expenditure ¦ Alternative control
Economic benchmarking categories
3.2.1 - OPEX CATEGORIES
Economic benchmarking categories
| CURRENT OPEX CATEGORIES | Units | Standard control | Alternative control
DOPEX0101 | Debt raising expenditure | $ | 0
DOPEX0102 | Maintenance | $ | 25597214.35 | 0
DOPEX0103 | Vegetation management | $ | 18091097.65 | 0
DOPEX0104 | Emergency response | $ | 12221255.01 | 0
DOPEX0105 | Network operating costs | $ | 14989604.9 | 0
DOPEX0106 | GSL payments | $ | 420375.1 | 0
DOPEX0107 | IT | $ | 32989304.15 | 4064585.81
DOPEX0108 | Non-network operating costs | $ | 47893118.84 | 3566739.32
DOPEX0109 | Public lighting | $ | 0 | 3296568.54
DOPEX0110 | Metering | $ | 0 | 1845620.11
DOPEX0111 | Fee-based and Quoted | $ | 0 | 12386464.65
3.2.2 - OPEX CONSISTENCY
Economic benchmarking categories
| CURRENT COST ALLOCATION APPROACH |  | Standard control
DOPEX0201 | Opex for network services | $ | 147334627
DOPEX0202 | Opex for metering | $ | 0
DOPEX0203 | Opex for connection services | $ | 4867343
DOPEX0204 | Opex for public lighting | $ | 0
DOPEX0205 | Opex for amounts payable for easement levy or similar direct charges on DNSP | $ | 0
DOPEX0206 | Opex for transmission connection point planning | $ | 0
| Total | $ | 152201970

## 3.2.3 Provisions
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| EB RIN 3.2.3 PROVISIONS |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC09 - Revenue and financial statements ¦ Provisions
Provisions
DOPEX03A | TOTAL PROVISIONS | Units | Standard control
DOPEX0301A | Opening balance (the carrying amount at the beginning of the period) | $ | -4746065
Additional provisions made in the period, including increases to existing provisions
DOPEX0302A | Opex component | $ | -3721641
DOPEX0303A | Capex component | $ | 0
DOPEX0304A | Other component | $ | 0
Amounts used (that is, incurred and charged against the provision) during the period
DOPEX0305A | Opex component | $ | 3571838
DOPEX0306A | Capex component | $ | 0
DOPEX0307A | Other component | $ | 0
Unused amounts reversed during the period
DOPEX0308A | Opex component | $ | 186853
DOPEX0309A | Capex component | $ | 0
DOPEX0310A | Other component | $ | 0
The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate
DOPEX0311A | Opex component | $ | 0
DOPEX0312A | Capex component | $ | 0
DOPEX0313A | Other component | $ | 0
DOPEX0314A | Closing balance (carrying amount at the end of the period) | $ | -4709015
3.2.3 - PROVISIONS
|  | Units | Standard control
DOPEX03A | Provision for Environment
DOPEX0301A | Opening balance (the carrying amount at the beginning of the period) | $ | -3273737
Additional provisions made in the period, including increases to existing provisions
DOPEX0302A | Opex component | $ | -1617532
DOPEX0303A | Capex component | $ | 0
DOPEX0304A | Other component | $ | 0
Amounts used (that is, incurred and charged against the provision) during the period
DOPEX0305A | Opex component | $ | 1978483
DOPEX0306A | Capex component | $ | 0
DOPEX0307A | Other component | $ | 0
Unused amounts reversed during the period
DOPEX0308A | Opex component | $ | 0
DOPEX0309A | Capex component | $ | 0
DOPEX0310A | Other component | $ | 0
The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate
DOPEX0311A | Opex component | $ | 0
DOPEX0312A | Capex component | $ | 0
DOPEX0313A | Other component | $ | 0
DOPEX0314A | Closing balance (carrying amount at the end of the period) | $ | -2912786
DOPEX03B | Provision for Doubtful Debts
DOPEX0301B | Opening balance (the carrying amount at the beginning of the period) | $ | -609908
Additional provisions made in the period, including increases to existing provisions
DOPEX0302B | Opex component | $ | -1104109
DOPEX0303B | Capex component | $ | 0
DOPEX0304B | Other component | $ | 0
Amounts used (that is, incurred and charged against the provision) during the period
DOPEX0305B | Opex component | $ | 1111497
DOPEX0306B | Capex component | $ | 0
DOPEX0307B | Other component | $ | 0
Unused amounts reversed during the period
DOPEX0308B | Opex component | $ | 0
DOPEX0309B | Capex component | $ | 0
DOPEX0310B | Other component | $ | 0
The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate
DOPEX0311B | Opex component | $ | 0
DOPEX0312B | Capex component | $ | 0
DOPEX0313B | Other component | $ | 0
DOPEX0314B | Closing balance (carrying amount at the end of the period) | $ | -602520
DOPEX03C | Provision for Claims
DOPEX0301C | Opening balance (the carrying amount at the beginning of the period) | $ | -862420
Additional provisions made in the period, including increases to existing provisions
DOPEX0302C | Opex component | $ | -1000000
DOPEX0303C | Capex component | $ | 0
DOPEX0304C | Other component | $ | 0
Amounts used (that is, incurred and charged against the provision) during the period
DOPEX0305C | Opex component | $ | 481858
DOPEX0306C | Capex component | $ | 0
DOPEX0307C | Other component | $ | 0
Unused amounts reversed during the period
DOPEX0308C | Opex component | $ | 186853
DOPEX0309C | Capex component | $ | 0
DOPEX0310C | Other component | $ | 0
The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate
DOPEX0311C | Opex component | $ | 0
DOPEX0312C | Capex component | $ | 0
DOPEX0313C | Other component | $ | 0
DOPEX0314C | Closing balance (carrying amount at the end of the period) | $ | -1193709

## 3.3 Assets (RAB)
| ANNUAL INFORMATION ORDER |  |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  |  | 12.5% Grey | Amended
| EB RIN 3.3 ASSETS (RAB) |  |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC08 - Asset base values ¦ Standard control
DC08 - Asset base values ¦ Alternative control
DC08 - Asset base values ¦ Network services
Asset base values
3.3.1 - REGULATORY ASSET BASE VALUES
| BENCHMARKING ASSET BASE | Units | Network Services | Standard control | Alternative control
DRAB0101 | Opening value | $ | 2680463778 | 2769371938 | 135991971
DRAB0102 | Inflation addition | $ | 108624073 | 112214611 | 4354085
DRAB0103 | Actual straight line depreciation | $ | 193893844 | 198849562 | 22442197
DRAB0104 | Gross capex | $ | 294234074 | 302842659 | 13467327
DRAB0108 | Capital contributions included in gross capex | $ | 86701053 | 89899367 | 1831535
DRAB0106 | Disposals | $ | 257198 | 260456 | 0
DRAB0109 | Capex timing adjustment | $ | 6956860 | 7138337 | 189859
DRAB0107 | Closing value | $ | 2809426690 | 2902558160 | 129729510
3.3.2 - ASSET VALUE ROLL FORWARD
| OVERHEAD NETWORK ASSETS LESS THAN 33KV | Units | Network Services | Standard control | Alternative control
DRAB0201 | Opening value | $ | 1023948131 | 1061851563
DRAB0202 | Inflation addition | $ | 41495373 | 43026095
DRAB0203 | Actual straight line depreciation | $ | 57272577 | 59385305
DRAB0204 | Gross capex | $ | 99488267 | 103158290
DRAB0208 | Capital contributions included in gross capex | $ | 36962495 | 38326005
DRAB0206 | Disposals | $ | 37662 | 39051
DRAB0209 | Capex timing adjustment | $ | 2097307 | 2174675
DRAB0207 | Closing value | $ | 1072756344 | 1112460262
UNDERGROUND NETWORK ASSETS LESS THAN 33KV
DRAB0301 | Opening value | $ | 459684151 | 476700255
DRAB0302 | Inflation addition | $ | 18628644 | 19315836
DRAB0303 | Actual straight line depreciation | $ | 25711552 | 26660026
DRAB0304 | Gross capex | $ | 44663571 | 46311165
DRAB0308 | Capital contributions included in gross capex | $ | 16593686 | 17205810
DRAB0306 | Disposals | $ | 16908 | 17531
DRAB0309 | Capex timing adjustment | $ | 941551 | 976283
DRAB0307 | Closing value | $ | 481595771 | 499420172
DISTRIBUTION SUBSTATIONS AND TRANSFORMERS
DRAB0401 | Opening value | $ | 224551461 | 232863670
DRAB0402 | Inflation addition | $ | 9099920 | 9435607
DRAB0403 | Actual straight line depreciation | $ | 12559856 | 13023176
DRAB0404 | Gross capex | $ | 21817742 | 22622576
DRAB0408 | Capital contributions included in gross capex | $ | 8105862 | 8404879
DRAB0406 | Disposals | $ | 8259 | 8564
DRAB0409 | Capex timing adjustment | $ | 459939 | 476905
DRAB0407 | Closing value | $ | 235255085 | 243962139
OVERHEAD NETWORK ASSETS 33KV AND ABOVE
DRAB0501 | Opening value | $ | 400281820 | 415099030
DRAB0502 | Inflation addition | $ | 16221372 | 16819762
DRAB0503 | Actual straight line depreciation | $ | 22388997 | 23214904
DRAB0504 | Gross capex | $ | 38891955 | 40326640
DRAB0508 | Capital contributions included in gross capex | $ | 14449379 | 14982402
DRAB0506 | Disposals | $ | 14723 | 15266
DRAB0509 | Capex timing adjustment | $ | 819879 | 850124
DRAB0507 | Closing value | $ | 419361927 | 434882984
UNDERGROUND NETWORK ASSETS 33KV AND ABOVE
DRAB0601 | Opening value | $ | 106786974 | 110739901
DRAB0602 | Inflation addition | $ | 4327529 | 4487167
DRAB0603 | Actual straight line depreciation | $ | 5972925 | 6193260
DRAB0604 | Gross capex | $ | 10375575 | 10758320
DRAB0608 | Capital contributions included in gross capex | $ | 3854798 | 3996997
DRAB0606 | Disposals | $ | 3928 | 4073
DRAB0609 | Capex timing adjustment | $ | 218727 | 226796
DRAB0607 | Closing value | $ | 111877154 | 116017854
ZONE SUBSTATIONS AND TRANSFORMERS
DRAB0701 | Opening value | $ | 186570734 | 193477012
DRAB0702 | Inflation addition | $ | 7560756 | 7839665
DRAB0703 | Actual straight line depreciation | $ | 10435477 | 10820431
DRAB0704 | Gross capex | $ | 18127480 | 18796184
DRAB0708 | Capital contributions included in gross capex | $ | 6734833 | 6983274
DRAB0706 | Disposals | $ | 6862 | 7115
DRAB0709 | Capex timing adjustment | $ | 382144 | 396241
DRAB0707 | Closing value | $ | 195463942 | 202698282
EASEMENTS
DRAB0801 | Opening value | $ | 0 | 0
DRAB0802 | Inflation addition | $ | 0 | 0
DRAB0804 | Gross capex | $ | 0 | 0
| Capital contributions included in gross capex | $ | 0 | 0
DRAB0806 | Disposals | $ | 0 | 0
DRAB0809 | Capex timing adjustment | $ | 0 | 0
DRAB0807 | Closing value | $ | 0 | 0
METERS
DRAB0901 | Opening value | $ | 0 | 0 | 107455539
DRAB0902 | Inflation addition | $ | 0 | 0 | 4354085
DRAB0903 | Actual straight line depreciation | $ | 0 | 0 | 20623482
DRAB0904 | Gross capex | $ | 0 | 0 | 5656745
DRAB0908 | Capital contributions included in gross capex | $ | 0 | 0 | 0
DRAB0906 | Disposals | $ | 0 | 0 | 0
DRAB0909 | Capex timing adjustment | $ | 0 | 0 | 189859
DRAB0907 | Closing value | $ | 0 | 0 | 97032746
OTHER ASSET ITEMS WITH LONG LIVES
DRAB1001 | Opening value | $ | 107556050 | 107556050 | 28536432
DRAB1002 | Inflation addition | $ | 4358158 | 4358158 | 0
DRAB1003 | Actual straight line depreciation | $ | 19731228 | 19731228 | 1818715
DRAB1004 | Gross capex | $ | 5160843 | 5160843 | 7810582
DRAB1008 | Capital contributions included in gross capex | $ | 0 | 0 | 1831535
DRAB1006 | Disposals | $ | 0 | 0 | 0
DRAB1009 | Capex timing adjustment | $ | 173215 | 173215 | 0
DRAB1007 | Closing value | $ | 97517038 | 97517038 | 32696764
OTHER ASSET ITEMS WITH SHORT LIVES
DRAB1101 | Opening value | $ | 171084457 | 171084457 | 0
DRAB1102 | Inflation addition | $ | 6932321 | 6932321 | 0
DRAB1103 | Actual straight line depreciation | $ | 39821232 | 39821232 | 0
DRAB1104 | Gross capex | $ | 55708641 | 55708641 | 0
DRAB1108 | Capital contributions included in gross capex | $ | 0 | 0 | 0
DRAB1106 | Disposals | $ | 168856 | 168856 | 0
DRAB1109 | Capex timing adjustment | $ | 1864098 | 1864098 | 0
DRAB1107 | Closing value | $ | 195599429 | 195599429 | 0
DC03 - Network metrics ¦ Asset metrics
Asset lives
3.3.4 - ASSET LIVES
| ESTIMATED SERVICE LIFE OF NEW ASSETS | Units | Network Services | Standard control | Alternative control
DRAB1401 | Overhead network assets less than 33kV (wires and poles) | years | 37.2 | 37.2
DRAB1402 | Underground network assets less than 33kV (cables) | years | 37.2 | 37.2
DRAB1403 | Distribution substations including transformers | years | 37.2 | 37.2
DRAB1404 | Overhead network assets 33kV and above (wires and towers / poles etc) | years | 37.2 | 37.2
DRAB1405 | Underground network assets 33kV and above (cables, ducts etc) | years | 37.2 | 37.2
DRAB1406 | Zone substations and transformers | years | 37.2 | 37.2
DRAB1407 | Meters | years | 0 |  | 14
DRAB1408 | Other assets with long lives | years | 7.5 | 7.5 | 25.3
DRAB1409 | Other assets with short lives | years | 5 | 5 | 0
ESTIMATED RESIDUAL SERVICE LIFE
DRAB1501 | Overhead network assets less than 33kV (wires and poles) | years | 18.6 | 18.6
DRAB1502 | Underground network assets less than 33kV (cables) | years | 18.6 | 18.6
DRAB1503 | Distribution substations including transformers | years | 18.6 | 18.6
DRAB1504 | Overhead network assets 33kV and above (wires and towers / poles etc) | years | 18.6 | 18.6
DRAB1505 | Underground network assets 33kV and above (cables, ducts etc) | years | 18.6 | 18.6
DRAB1506 | Zone substations and transformers | years | 18.6 | 18.6
DRAB1507 | Meters | years | 0 |  | 5.4
DRAB1508 | Other assets with long lives | years | 5.7 | 5.7 | 16.3
DRAB1509 | Other assets with short lives | years | 4.5 | 4.5 | 0

## 3.4 Operational data
| ANNUAL INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| EB RIN 3.4 OPERATIONAL DATA |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC02 - Operational outputs ¦ Energy delivered¦received
Energy delivered / received
Energy delivered / received
3.4.1 - ENERGY DELIVERY
3.4.1.1 - ENERGY GROUPING - DELIVERY BY CHARGEABLE QUANTITY
| ENERGY DELIVERY BY TIME OF DELIVERY | Units | Energy
DOPED0201 | Energy delivery where time of use is not a determinant | MWh | 2687275
DOPED0202 | Energy delivery at On-peak times | MWh | 2344955
DOPED0203 | Energy delivery at Shoulder times | MWh | 0
DOPED0204 | Energy delivery at Off-peak times | MWh | 2477264
DOPED0205 | Controlled load energy deliveries | MWh | 47921
DOPED0206 | Energy delivery to unmetered supplies | MWh | 58214
DOPED01 | Total energy delivery by time of delivery | MWh | 7615629
3.4.1 - ENERGY DELIVERY
3.4.1.2 - ENERGY - RECEIVED FROM TNSP AND OTHER DNSPS BY TIME OF RECEIPT
| ENERGY RECEIVED BY TIME OF RECEIPT | Units | Energy
DOPED0301 | Energy into DNSP network at On-peak times | MWh | 0
DOPED0302 | Energy into DNSP network at Shoulder times | MWh | 0
DOPED0303 | Energy into DNSP network at Off-peak times | MWh | 0
DOPED0304 | Energy received from TNSP and other DNSPs not included in the above categories | MWh | 7061.02
3.4.1 - ENERGY DELIVERY
3.4.1.3 - ENERGY - RECEIVED INTO DNSP SYSTEM FROM EMBEDDED GENERATION BY TIME OF RECEIPT
| ENERGY RECEIVED FROM EMBEDDED GENERATION BY TIME OF RECEIPT | Units | Energy
DOPED0401 | Energy into DNSP network at On-peak times from non-residential embedded generation | MWh | 0
DOPED0402 | Energy into DNSP network at Shoulder times from non-residential embedded generation | MWh | 0
DOPED0403 | Energy into DNSP network at Off-peak times from non-residential embedded generation | MWh | 0
DOPED0404 | Energy received from embedded generation not included in above categories from non-residential embedded generation | MWh | 279.67
DOPED0405 | Energy into DNSP network at On-peak times from residential embedded generation | MWh | 0
DOPED0406 | Energy into DNSP network at Shoulder times from residential embedded generation | MWh | 0
DOPED0407 | Energy into DNSP network at Off-peak times from residential embedded generation | MWh | 0
DOPED0408 | Energy received from embedded generation not included in above categories from residential embedded generation | MWh | 577.22
3.4.1 - ENERGY DELIVERY
3.4.1.4 - ENERGY GROUPING - CUSTOMER TYPE OR CLASS
| ENERGY DELIVERED BY CUSTOMER (BENCHMARKING) | Units | Energy
DOPED0501 | Residential customers | MWh | 3000285
DOPED0502 | Non residential customers not on demand tariffs | MWh | 729946
DOPED0503 | Non-residential low voltage demand tariff customers | MWh | 2824843
DOPED0504 | Non-residential high voltage demand tariff customers | MWh | 1002341
DOPED0505 | Other customer class energy deliveries | MWh | 58214
DC04 - Customer numbers ¦ Benchmarking
Customers (benchmarking)
Customers (benchmarking)
3.4.2 - CUSTOMER NUMBERS
3.4.2.1 - DISTRIBUTION CUSTOMER NUMBERS BY CUSTOMER TYPE OR CLASS
Total Customers (Benchmarking)
| CUSTOMER NUMBERS BY CUSTOMER TYPE OR CLASS | Units | as at 1 July (start of year) | as at 30 June (end of year)
DOPCN0101 | Residential customer numbers | number of customers | 647066 | 649502
DOPCN0102 | Non residential customers not on demand tariff customer numbers | number of customers | 51603 | 51836
DOPCN0103 | Low voltage demand tariff customer numbers | number of customers | 11202 | 11212
DOPCN0104 | High voltage demand tariff customer numbers | number of customers | 106 | 110
DOPCN0105 | Unmetered Customer Numbers | number of customers | 7717 | 7494
DOPCN0106 | Other Customer Numbers | number of customers | 0 | 0
DOPCN01 | Total customers |  | 717694 | 720154
3.4.2 - CUSTOMER NUMBERS
3.4.2.2 - DISTRIBUTION CUSTOMER NUMBERS BY LOCATION ON THE NETWORK
Total Customers (Benchmarking)
| CUSTOMER NUMBERS BY FEEDER TYPE | Units | as at 1 July (start of year) | as at 30 June (end of year)
DOPCN0201 | CBD | number of customers | 0 | 0
DOPCN0202 | Urban | number of customers | 652367 | 654838
DOPCN0203 | Short Rural | number of customers | 65327 | 65316
DOPCN0204 | Long Rural | number of customers | 0 | 0
DOPCN02 | Total customers |  | 717694 | 720154
DC02 - Operational outputs ¦ Maximum demand
System maximum demand
System maximum demand
3.4.3 - SYSTEM DEMAND
3.4.3.1 - ANNUAL SYSTEM MAXIMUM DEMAND CHARACTERISTICS AT THE ZONE SUBSTATION LEVEL – MW MEASURE
| ANNUAL SYSTEM MAXIMUM DEMAND CHARACTERISTICS AT THE ZONE SUBSTATION LEVEL | Units | Demand
DOPSD0101 | Non-coincident summated raw system annual maximum demand | MW | 2125
DOPSD0102 | Non–coincident summated weather adjusted system annual maximum demand 10% POE | MW | 2374
DOPSD0103 | Non–coincident summated weather adjusted system annual maximum demand 50% POE | MW | 2153
DOPSD0104 | Coincident raw system annual maximum demand | MW | 1964
DOPSD0105 | Coincident weather adjusted system annual maximum demand 10% POE | MW | 2189
DOPSD0106 | Coincident weather adjusted system annual maximum demand 50% POE | MW | 1986
3.4.3 - SYSTEM DEMAND
3.4.3.2 - ANNUAL SYSTEM MAXIMUM DEMAND CHARACTERISTICS AT THE TRANSMISSION CONNECTION POINT – MW MEASURE
| ANNUAL SYSTEM MAXIMUM DEMAND CHARACTERISTICS AT THE TRANSMISSION CONNECTION POINT | Units | Demand
DOPSD0107 | Non-coincident summated raw system annual maximum demand | MW | 2013
DOPSD0108 | Non–coincident summated weather adjusted system annual maximum demand 10% POE | MW | 2210
DOPSD0109 | Non–coincident summated weather adjusted system annual maximum demand 50% POE | MW | 2031
DOPSD0110 | Coincident raw system annual maximum demand | MW | 1953
DOPSD0111 | Coincident weather adjusted system annual maximum demand 10% POE | MW | 2141
DOPSD0112 | Coincident weather adjusted system annual maximum demand 50% POE | MW | 1969
3.4.3 - SYSTEM DEMAND
3.4.3.3 - ANNUAL SYSTEM MAXIMUM DEMAND CHARACTERISTICS AT THE ZONE SUBSTATION LEVEL – MVA MEASURE
| ANNUAL SYSTEM MAXIMUM DEMAND CHARACTERISTICS AT THE ZONE SUBSTATION LEVEL | Units | Demand
DOPSD0201 | Non–coincident summated raw system annual maximum demand | MVA | 2137
DOPSD0202 | Non–coincident summated weather adjusted system annual maximum demand 10% POE | MVA | 2386
DOPSD0203 | Non–coincident summated weather adjusted system annual maximum demand 50% POE | MVA | 2163
DOPSD0204 | Coincident raw system annual maximum demand | MVA | 1974
DOPSD0205 | Coincident weather adjusted system annual maximum demand 10% POE | MVA | 2200
DOPSD0206 | Coincident weather adjusted system annual maximum demand 50% POE | MVA | 1996
3.4.3 - SYSTEM DEMAND
3.4.3.4 - ANNUAL SYSTEM MAXIMUM DEMAND CHARACTERISTICS AT THE TRANSMISSION CONNECTION POINT – MVA MEASURE
| ANNUAL SYSTEM MAXIMUM DEMAND CHARACTERISTICS AT THE TRANSMISSION CONNECTION POINT | Units | Demand
DOPSD0207 | Non-coincident Summated Raw System Annual Maximum Demand | MVA | 2056
DOPSD0208 | Non–coincident summated weather adjusted system annual maximum demand 10% POE | MVA | 2265
DOPSD0209 | Non–coincident summated weather adjusted system annual maximum demand 50% POE | MVA | 2076
DOPSD0210 | Coincident raw system annual maximum demand | MVA | 1988
DOPSD0211 | Coincident weather adjusted system annual maximum demand 10% POE | MVA | 2179
DOPSD0212 | Coincident weather adjusted system annual maximum demand 50% POE | MVA | 2003

## 3.5 Physical assets
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| EB RIN 3.5 PHYSICAL ASSETS |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC03 - Network metrics ¦ Length
Circuit length
3.5.1 - NETWORK CAPACITIES
3.5.1.1 - OVERHEAD NETWORK LENGTH OF CIRCUIT AT EACH VOLTAGE
| Circuit length | Units | Length
DPA0101 | Overhead low voltage distribution | km | 5789.96
DPA0102 | Overhead 2.2 kV | km | 0
DPA0103 | Overhead 6.6kv | km | 18.43
DPA0104 | Overhead 7.6 kV | km | 0
DPA0105 | Overhead 11 kV | km | 636.9
DPA0106 | Overhead SWER | km | 34.96
DPA0107 | Overhead 22 kV | km | 2906.91
DPA0108 | Overhead 33 kV | km | 0
DPA0109 | Overhead 44 kV | km | 0
DPA0110 | Overhead 66 kV | km | 609.57
DPA0111 | Overhead 110kV | km | 0
DPA0112 | Overhead 132 kV | km | 0
DPA0113 | Overhead 220kV | km | 0
DPA0114 | Other | km | 0
DPA01 | Total overhead circuit km | km | 9996.73
3.5.1 - NETWORK CAPACITIES
3.5.1.2 - UNDERGROUND NETWORK CIRCUIT LENGTH AT EACH VOLTAGE
| Circuit length | Units | Length
DPA0201 | Underground low voltage distribution | km | 2303.8
DPA0202 | Underground 5 kV | km | 0
DPA0203 | Underground 6.6 Kv | km | 2.18
DPA0204 | Underground 7.6 kV | km | 0
DPA0205 | Underground 11 kV | km | 251.67
DPA0206 | Underground SWER | km | 0.98
DPA0207 | Underground 22 kV | km | 994.46
DPA0208 | Underground 33 kV | km | 0
DPA0209 | Underground 66 kV | km | 3.66
DPA0210 | Underground 110 kV | km | 0
DPA0211 | Underground 132 kV | km | 0
DPA0212 | Other | km | 0
DPA02 | Total underground circuit km |  | 3556.75
DC03 - Network metrics ¦ Capacity
Circuit capacity MVA
3.5.1 - NETWORK CAPACITIES
3.5.1.3 - ESTIMATED OVERHEAD NETWORK WEIGHTED AVERAGE MVA CAPACITY BY VOLTAGE CLASS
| Circuit capacity MVA | Units | Volume
DPA0301 | Overhead low voltage distribution | MVA | 0.276
DPA0302 | Overhead 6.6 kV | MVA | 2.997
DPA0303 | Overhead 7.6 kV | MVA | 0
DPA0304 | Overhead 11 kV | MVA | 5.75
DPA0305 | Overhead SWER | MVA | 0.1
DPA0306 | Overhead 22 kV | MVA | 11.925
DPA0307 | Overhead 33 kV | MVA | 0
DPA0308 | Overhead 44 kV | MVA | 0
DPA0309 | Overhead 66 kV | MVA | 101.678
DPA0310 | Overhead 110 kV | MVA | 0
DPA0311 | Overhead 132 kV | MVA | 0
DPA0312 | Overhead 220 kV | MVA | 0
DPA0313 | Other | MVA | 0
3.5.1 - NETWORK CAPACITIES
3.5.1.4 - ESTIMATED UNDERGROUND NETWORK WEIGHTED AVERAGE MVA CAPACITY BY VOLTAGE CLASS
| Circuit capacity MVA | Units | Volume
DPA0401 | Underground low voltage distribution | MVA | 0.276
DPA0402 | Underground 5 kV | MVA | 0
DPA0403 | Underground 6.6 kV | MVA | 3.119
DPA0404 | Underground 7.6 kV | MVA | 0
DPA0405 | Underground 11 kV | MVA | 5.985
DPA0406 | Underground SWER | MVA | 0.1
DPA0407 | Underground 12.7 kV | MVA | 0
DPA0408 | Underground 22 kV | MVA | 12.412
DPA0409 | Underground 33 kV | MVA | 0
DPA0410 | Underground 66 kV | MVA | 133.925
DPA0411 | Underground 110 kV | MVA | 0
DPA0412 | Underground 132 kV | MVA | 0
DPA0413 | Other | MVA | 0
DC03 - Network metrics ¦ Capacity
Transformer capacities
3.5.2 - TRANSFORMER CAPACITIES
3.5.2.1 - DISTRIBUTION TRANSFORMER TOTAL INSTALLED CAPACITY
3.5.2.2 - ZONE SUBSTATION TRANSFORMER CAPACITY
3.5.2.3 - DISTRIBUTION - OTHER TRANSFORMER CAPACITY
Transformer capacities
| DISTRIBUTION TRANSFORMER TOTAL INSTALLED CAPACITY | Units | Volume
DPA0501 | Distribution transformer capacity owned by utility | MVA | 5943
DPA0503 | Cold spare capacity included in 'Distribution transformer capacity owned by utility' | MVA | 17
ZONE SUBSTATION TRANSFORMER CAPACITY
DPA0601 | Total installed capacity for first step transformation where there are two steps to reach distribution voltage | MVA | 0
DPA0602 | Total installed capacity for second step transformation where there are two steps to reach distribution voltage | MVA | 0
DPA0603 | Total zone substation transformer capacity where there is only a single step transformation to reach distribution voltage | MVA | 3466
DPA0604 | Total zone substation transformer capacity | MVA | 3466
DPA0605 | Cold spare capacity of zone substation transformers included in Total zone substation transformer capacity | MVA | 0
DISTRIBUTION - OTHER TRANSFORMER CAPACITY
DPA0606 | Distribution other - transformer capacity owned by utility | MVA | 0
DC03 - Network metrics ¦Networks assets - volumes
Public lighting
3.5.3 - PUBLIC LIGHTING
| Public lighting | Units | Volume
DPA0701 | Public lighting luminaires | Number of assets | 123868
DPA0702 | Public lighting poles | Number of assets | 35218
DPA0703 | Public lighting columns | Number of assets | 0

## 3.6 Quality of service
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| EB RIN 3.6 QUALITY OF SERVICE DATA |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC05 - Service performance ¦ Service outcomes
Reliability
3.6.1 - RELIABILITY
| Service target performance incentive scheme (STPIS) |  | STPIS V1
| Reliability | Units | Service Performance
INCLUSIVE OF MEDs
DQS0101 | Whole of network unplanned SAIDI | minutes/customer | 53.8963
DQS0102 | Whole of network unplanned SAIDI excluding excluded outages | minutes/customer | 53.8963
DQS0103 | Whole of network unplanned SAIFI | interruptions/customer | 0.53053
DQS0104 | Whole of network unplanned SAIFI excluding excluded outages | interruptions/customer | 0.53053
EXCLUSIVE OF MEDs
DQS0105 | Whole of network unplanned SAIDI | minutes/customer | 35.2161
DQS0106 | Whole of network unplanned SAIDI excluding excluded outages | minutes/customer | 35.2161
DQS0107 | Whole of network unplanned SAIFI | interruptions/customer | 0.43384
DQS0108 | Whole of network unplanned SAIFI excluding excluded outages | interruptions/customer | 0.43384
DC05 - Service performance ¦ Service outcomes
Energy not supplied
3.6.2 - ENERGY NOT SUPPLIED
| Energy not supplied | Units | Service Performance
DQS0201 | Energy not supplied (planned) | GWh | 1.0608
DQS0202 | Energy not supplied (unplanned) | GWh | 0.822
DQS02 | Total energy not supplied | GWh | 1.8828
DC05 - Service performance ¦ Service outcomes
System losses
3.6.3 - SYSTEM LOSSES
| System losses | Units | Service Performance
DQS03 | System losses | % | 3.81%
DC05 - Service performance ¦ Service outcomes
Capacity utilisation
3.6.4 - CAPACITY UTILISATION
| Capacity utilisation | Units | Service Performance
DQS04 | Overall utilisation | % | 61.7%

## 3.7 - Operating Environment
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| EB RIN 3.7 OPERATING ENVIRONMENT FACTORS |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC03 - Network metrics ¦ Terrain factors
Terrain factors
3.7.2 - TERRAIN FACTORS
| Terrain factors | Units | Asset Volume
DOEF0201 | Rural proportion | % | 18.22%
DOEF0202 | Urban and CBD vegetation maintenance spans | Number of spans | 21882
DOEF0203 | Rural vegetation maintenance spans | Number of spans | 10807
DOEF0204 | Total vegetation maintenance spans | Number of spans | 32689
DOEF0205 | Total number of spans | Number of spans | 188235
DOEF0206 | Average urban and CBD vegetation maintenance span cycle | Years | 2.46
DOEF0207 | Average rural vegetation maintenance span cycle | Years | 2.04
DOEF0208 | Average number of trees per urban and CBD vegetation maintenance span | Trees | 20.1
DOEF0209 | Average number of trees per rural vegetation maintenance span | Trees | 16.57
DOEF0210 | Average number of defects per urban and CBD vegetation maintenance span | Defects | 1.02
DOEF0211 | Average number of defects per rural vegetation maintenance span | Defects | 1.06
DOEF0212 | Tropical proportion | Spans | 0
DOEF0213 | Standard vehicle access | km | 68.03
DOEF0214 | Bushfire risk | Spans | 17377
DC03 - Network metrics ¦ Length
Service area factors
3.7.3 - SERVICE AREA FACTORS
| Service area factors | Units | Length
DOEF0301 | Route Line length | km | 6802.5735

## 6.2.4 STPIS Customer summary
| ANNUAL INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| AR RIN 3.6.8 NETWORK FEEDER RELIABILITY |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC04 - Customer numbers ¦ STPIS
6.2.4 - STPIS Customer summary data
Customers (STPIS)
|  | as at 1 July (start of year) | as at 30 June (end of year) | Average customer numbers
| CBD | 0 | 0 | 0
| Urban | 651024 | 654837 | 652930.5
| Rural Short | 65192 | 65316 | 65254
| Rural Long | 0 | 0 | 0
| Whole Network | 716216 | 720153 | 718184.5

## 6.6 STPIS Customer Service
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| AR RIN 6.6 STPIS CUSTOMER SERVICE |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC05 - Service performance ¦ Other service measures
Inadequately served customers (STPIS)
6.6.2 - INADEQUATELY SERVED CUSTOMERS
| Inadequately served customers (STPIS) | Units | Service performance
SAIDI VALUES
| Threshold SAIDI value for inadequately served customers | SAIDI | 384.22
| Average unplanned SAIDI of inadequately served customers | SAIDI | 704.68
| Highest unplanned SAIDI of inadequately served customers | SAIDI | 8658.7
SAIFI VALUES
| Average unplanned SAIFI of inadequately served customers | SAIFI | 2.27
| Highest unplanned SAIFI of inadequately served customers | SAIFI | 7
TOP 5 FEEDERS WITH MOST INADEQUATELY SERVED CUSTOMERS
SAIDI VALUES
| EM1 | SAIDI | 8658.7
| RBD14 | SAIDI | 4065.96
| MGE24 | SAIDI | 4028.95
| LWN24 | SAIDI | 3698.82
| BU24 | SAIDI | 3534.1
SAIFI VALUES
| GW7 | SAIFI | 6.15
| NP16 | SAIFI | 5.44
| RBD12 | SAIFI | 5.08
| CFD12 | SAIFI | 4.94
| HT9 | SAIFI | 4.8
NUMBER OF INADQUATELY SERVED CUSTOMERS
| FSH11 | number of customers | 1353
| NW21 | number of customers | 1236
| BR13 | number of customers | 1188
| DMA23 | number of customers | 721
| MTN32 | number of customers | 667
TOP 5 ZONE SUBSTATIONS WITH MOST INADEQUATELY SERVED CUSTOMERS
SAIDI VALUES
| <DNSP specified> | SAIDI
SAIDI
SAIDI
SAIDI
SAIDI
SAIFI VALUES
| <DNSP specified> | SAIFI
SAIFI
SAIFI
SAIFI
SAIFI
NUMBER OF INADQUATELY SERVED CUSTOMERS
| <DNSP specified> | number of customers
number of customers
number of customers
number of customers
number of customers

## 6.7 STPIS Daily performance
| ANNUAL INFORMATION ORDER | [14 empty] | #25C6FF | Protected (SOCI)
| United Energy | [14 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [14 empty] | 12.5% Grey | Amended
| AR RIN 6.7 STPIS DAILY PERFORMANCE | [14 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
DC05 - Service performance ¦ Call centre
Daily performance data - unplanned
DC05 - Service performance ¦ Momentary interruptions
MAIFI impact
6.7.1 - DAILY PERFORMANCE DATA - UNPLANNED
| Identify the service target performance incentive scheme (STPIS) that applied in the reporting period |  |  |  | STPIS V2
| Identify the Momentary interruptions parameter that applies in the reporting year (None, MAIFI, MAIFIe) |  |  |  | MAIFI
MAIFI / MAIFIe
| Call centre & Momentary interruptions |  | Call centre daily performance |  |  | CBD |  | Urban |  | Short rural |  | Long rural |  | Network
|  | Units | Total number of calls received (calls to call centre fault line) | Number of calls received (after removing excluded events) | Number of calls answered in 30 seconds (after removing excluded events) | All events | After removing excluded events | All events | After removing excluded events | All events | After removing excluded events | All events | After removing excluded events | All events | After removing excluded events
| 2024-07-01 | number of calls | 226 | 121 | 79 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-02 | number of calls | 348 | 205 | 154 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-03 | number of calls | 366 | 241 | 141 |  |  | 0.0048 | 0.0048 | 0 | 0 |  |  | 0.0043 | 0.0043
| 2024-07-04 | number of calls | 231 | 142 | 120 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-05 | number of calls | 222 | 119 | 109 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-06 | number of calls | 124 | 74 | 67 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-07 | number of calls | 129 | 80 | 75 |  |  | 0.0013 | 0.0013 | 0 | 0 |  |  | 0.0012 | 0.0012
| 2024-07-08 | number of calls | 238 | 127 | 108 |  |  | 0.002 | 0.002 | 0 | 0 |  |  | 0.0018 | 0.0018
| 2024-07-09 | number of calls | 211 | 116 | 91 |  |  | 0.001 | 0.001 | 0 | 0 |  |  | 0.0009 | 0.0009
| 2024-07-10 | number of calls | 220 | 117 | 89 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-11 | number of calls | 222 | 126 | 103 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-12 | number of calls | 177 | 107 | 93 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-13 | number of calls | 149 | 87 | 78 |  |  | 0.0019 | 0.0019 | 0 | 0 |  |  | 0.0017 | 0.0017
| 2024-07-14 | number of calls | 76 | 48 | 41 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-15 | number of calls | 403 | 238 | 164 |  |  | 0.0054 | 0.0054 | 0.0187 | 0.0187 |  |  | 0.0066 | 0.0066
| 2024-07-16 | number of calls | 603 | 331 | 201 |  |  | 0.0022 | 0.0022 | 0 | 0 |  |  | 0.002 | 0.002
| 2024-07-17 | number of calls | 311 | 158 | 109 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-18 | number of calls | 266 | 144 | 108 |  |  | 0.0005 | 0.0005 | 0 | 0 |  |  | 0.0005 | 0.0005
| 2024-07-19 | number of calls | 349 | 173 | 129 |  |  | 0.001 | 0.001 | 0.0041 | 0.0041 |  |  | 0.0012 | 0.0012
| 2024-07-20 | number of calls | 247 | 155 | 122 |  |  | 0.0073 | 0.0073 | 0.0041 | 0.0041 |  |  | 0.007 | 0.007
| 2024-07-21 | number of calls | 83 | 50 | 42 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-22 | number of calls | 255 | 140 | 112 |  |  | 0.0037 | 0.0037 | 0 | 0 |  |  | 0.0034 | 0.0034
| 2024-07-23 | number of calls | 286 | 158 | 114 |  |  | 0.003 | 0.003 | 0 | 0 |  |  | 0.0027 | 0.0027
| 2024-07-24 | number of calls | 324 | 191 | 129 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-25 | number of calls | 209 | 116 | 67 |  |  | 0.0056 | 0.0056 | 0 | 0 |  |  | 0.005 | 0.005
| 2024-07-26 | number of calls | 246 | 140 | 127 |  |  | 0.0028 | 0.0028 | 0 | 0 |  |  | 0.0026 | 0.0026
| 2024-07-27 | number of calls | 182 | 107 | 89 |  |  | 0.0073 | 0.0073 | 0 | 0 |  |  | 0.0066 | 0.0066
| 2024-07-28 | number of calls | 145 | 84 | 79 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-29 | number of calls | 293 | 149 | 102 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-30 | number of calls | 214 | 114 | 87 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-07-31 | number of calls | 329 | 181 | 135 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-01 | number of calls | 184 | 107 | 84 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-02 | number of calls | 225 | 141 | 123 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-03 | number of calls | 140 | 85 | 70 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-04 | number of calls | 91 | 58 | 50 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-05 | number of calls | 242 | 143 | 111 |  |  | 0 | 0 | 0.0409 | 0.0409 |  |  | 0.0037 | 0.0037
| 2024-08-06 | number of calls | 195 | 128 | 112 |  |  | 0.0009 | 0.0009 | 0 | 0 |  |  | 0.0008 | 0.0008
| 2024-08-07 | number of calls | 170 | 105 | 96 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-08 | number of calls | 265 | 140 | 113 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-09 | number of calls | 166 | 77 | 71 |  |  | 0.0019 | 0.0019 | 0 | 0 |  |  | 0.0017 | 0.0017
| 2024-08-10 | number of calls | 82 | 50 | 44 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-11 | number of calls | 96 | 53 | 50 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-12 | number of calls | 186 | 110 | 92 |  |  | 0.0009 | 0.0009 | 0 | 0 |  |  | 0.0008 | 0.0008
| 2024-08-13 | number of calls | 244 | 112 | 89 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-14 | number of calls | 181 | 101 | 85 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-15 | number of calls | 168 | 87 | 83 |  |  | 0.001 | 0.001 | 0 | 0 |  |  | 0.0009 | 0.0009
| 2024-08-16 | number of calls | 174 | 104 | 85 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-17 | number of calls | 64 | 32 | 25 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-18 | number of calls | 78 | 43 | 41 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-19 | number of calls | 188 | 97 | 81 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-20 | number of calls | 166 | 82 | 73 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-21 | number of calls | 186 | 93 | 83 |  |  | 0.0006 | 0.0006 | 0 | 0 |  |  | 0.0006 | 0.0006
| 2024-08-22 | number of calls | 159 | 79 | 78 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-23 | number of calls | 179 | 88 | 76 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-24 | number of calls | 96 | 58 | 51 |  |  | 0.002 | 0.002 | 0 | 0 |  |  | 0.0018 | 0.0018
| 2024-08-25 | number of calls | 124 | 71 | 59 |  |  | 0.0055 | 0.0055 | 0 | 0 |  |  | 0.005 | 0.005
| 2024-08-26 | number of calls | 213 | 115 | 95 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-08-27 | number of calls | 268 | 147 | 122 |  |  | 0.0137 | 0.0137 | 0.0284 | 0.0284 |  |  | 0.0151 | 0.0151
| 2024-08-28 | number of calls |  | 0 |  |  |  | 0.0315 | 0.0315 | 0.1146 | 0.1146 |  |  | 0.039 | 0.039
| 2024-08-29 | number of calls | 349 | 191 | 151 |  |  | 0 | 0 | 0.0049 | 0.0049 |  |  | 0.0004 | 0.0004
| 2024-08-30 | number of calls | 410 | 254 | 204 |  |  | 0.0068 | 0.0068 | 0.0199 | 0.0199 |  |  | 0.008 | 0.008
| 2024-08-31 | number of calls | 189 | 113 | 81 |  |  | 0.0033 | 0.0033 | 0 | 0 |  |  | 0.003 | 0.003
| 2024-09-01 | number of calls | 145 | 82 | 76 |  |  | 0.0026 | 0.0026 | 0.0146 | 0.0146 |  |  | 0.0036 | 0.0036
| 2024-09-02 | number of calls |  | 0 |  |  |  | 0.0212 | 0.0212 | 0.1702 | 0.1702 |  |  | 0.0347 | 0.0347
| 2024-09-03 | number of calls | 664 | 383 | 276 |  |  | 0 | 0 | 0.0009 | 0.0009 |  |  | 0.0001 | 0.0001
| 2024-09-04 | number of calls | 367 | 212 | 172 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-05 | number of calls | 339 | 154 | 119 |  |  | 0.0041 | 0.0041 | 0 | 0 |  |  | 0.0038 | 0.0038
| 2024-09-06 | number of calls | 259 | 134 | 100 |  |  | 0.001 | 0.001 | 0 | 0 |  |  | 0.0009 | 0.0009
| 2024-09-07 | number of calls | 147 | 100 | 71 |  |  | 0 | 0 | 0.0325 | 0.0325 |  |  | 0.003 | 0.003
| 2024-09-08 | number of calls | 100 | 54 | 48 |  |  | 0.0053 | 0.0053 | 0 | 0 |  |  | 0.0048 | 0.0048
| 2024-09-09 | number of calls | 303 | 151 | 104 |  |  | 0.0022 | 0.0022 | 0 | 0 |  |  | 0.002 | 0.002
| 2024-09-10 | number of calls | 185 | 107 | 87 |  |  | 0.0077 | 0.0077 | 0 | 0 |  |  | 0.007 | 0.007
| 2024-09-11 | number of calls | 173 | 98 | 91 |  |  | 0.0051 | 0.0051 | 0 | 0 |  |  | 0.0046 | 0.0046
| 2024-09-12 | number of calls | 170 | 97 | 93 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-13 | number of calls | 199 | 97 | 86 |  |  | 0.0023 | 0.0023 | 0 | 0 |  |  | 0.0021 | 0.0021
| 2024-09-14 | number of calls | 131 | 74 | 62 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-15 | number of calls | 214 | 76 | 64 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-16 | number of calls | 205 | 106 | 87 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-17 | number of calls | 206 | 111 | 95 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-18 | number of calls | 177 | 100 | 94 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-19 | number of calls | 203 | 101 | 96 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-20 | number of calls | 222 | 93 | 90 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-21 | number of calls | 85 | 61 | 53 |  |  | 0.0079 | 0.0079 | 0 | 0 |  |  | 0.0072 | 0.0072
| 2024-09-22 | number of calls | 104 | 52 | 48 |  |  | 0.0017 | 0.0017 | 0 | 0 |  |  | 0.0015 | 0.0015
| 2024-09-23 | number of calls | 204 | 110 | 94 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-24 | number of calls | 212 | 100 | 73 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-25 | number of calls | 290 | 146 | 123 |  |  | 0.0084 | 0.0084 | 0 | 0 |  |  | 0.0076 | 0.0076
| 2024-09-26 | number of calls | 260 | 140 | 94 |  |  | 0.0024 | 0.0024 | 0 | 0 |  |  | 0.0022 | 0.0022
| 2024-09-27 | number of calls | 164 | 100 | 83 |  |  | 0.0029 | 0.0029 | 0 | 0 |  |  | 0.0027 | 0.0027
| 2024-09-28 | number of calls | 74 | 46 | 44 |  |  | 0.0027 | 0.0027 | 0 | 0 |  |  | 0.0025 | 0.0025
| 2024-09-29 | number of calls | 61 | 38 | 35 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-09-30 | number of calls | 205 | 114 | 80 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-01 | number of calls | 184 | 92 | 64 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-02 | number of calls | 182 | 95 | 74 |  |  | 0 | 0 | 0.0409 | 0.0409 |  |  | 0.0037 | 0.0037
| 2024-10-03 | number of calls | 239 | 130 | 104 |  |  | 0.0043 | 0.0043 | 0 | 0 |  |  | 0.0039 | 0.0039
| 2024-10-04 | number of calls | 247 | 129 | 83 |  |  | 0.0374 | 0.0374 | 0.2198 | 0.2198 |  |  | 0.054 | 0.054
| 2024-10-05 | number of calls | 148 | 80 | 65 |  |  | 0.0099 | 0.0099 | 0 | 0 |  |  | 0.009 | 0.009
| 2024-10-06 | number of calls | 74 | 45 | 45 |  |  | 0.0028 | 0.0028 | 0 | 0 |  |  | 0.0025 | 0.0025
| 2024-10-07 | number of calls | 227 | 120 | 105 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-08 | number of calls | 230 | 110 | 96 |  |  | 0.002 | 0.002 | 0 | 0 |  |  | 0.0018 | 0.0018
| 2024-10-09 | number of calls | 176 | 78 | 64 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-10 | number of calls | 198 | 112 | 76 |  |  | 0 | 0 | 0.0689 | 0.0689 |  |  | 0.0063 | 0.0063
| 2024-10-11 | number of calls | 200 | 100 | 76 |  |  | 0.0004 | 0.0004 | 0 | 0 |  |  | 0.0004 | 0.0004
| 2024-10-12 | number of calls | 112 | 43 | 39 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-13 | number of calls | 78 | 41 | 41 |  |  | 0.0024 | 0.0024 | 0 | 0 |  |  | 0.0021 | 0.0021
| 2024-10-14 | number of calls | 206 | 92 | 88 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-15 | number of calls | 231 | 110 | 87 |  |  | 0.0022 | 0.0022 | 0 | 0 |  |  | 0.002 | 0.002
| 2024-10-16 | number of calls | 242 | 115 | 89 |  |  | 0 | 0 | 0.0409 | 0.0409 |  |  | 0.0037 | 0.0037
| 2024-10-17 | number of calls | 211 | 97 | 78 |  |  | 0.0072 | 0.0072 | 0 | 0 |  |  | 0.0065 | 0.0065
| 2024-10-18 | number of calls | 324 | 159 | 123 |  |  | 0.0036 | 0.0036 | 0 | 0 |  |  | 0.0033 | 0.0033
| 2024-10-19 | number of calls | 151 | 88 | 75 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-20 | number of calls | 100 | 41 | 41 |  |  | 0.0043 | 0.0043 | 0.0025 | 0.0025 |  |  | 0.0041 | 0.0041
| 2024-10-21 | number of calls | 241 | 139 | 97 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-22 | number of calls | 374 | 157 | 100 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-23 | number of calls | 190 | 90 | 83 |  |  | 0 | 0 | 0.0179 | 0.0179 |  |  | 0.0016 | 0.0016
| 2024-10-24 | number of calls | 223 | 112 | 81 |  |  | 0.0024 | 0.0024 | 0 | 0 |  |  | 0.0022 | 0.0022
| 2024-10-25 | number of calls | 229 | 117 | 105 |  |  | 0.0038 | 0.0038 | 0 | 0 |  |  | 0.0035 | 0.0035
| 2024-10-26 | number of calls | 111 | 48 | 42 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-27 | number of calls | 132 | 69 | 60 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-28 | number of calls | 212 | 122 | 110 |  |  | 0.0029 | 0.0029 | 0 | 0 |  |  | 0.0027 | 0.0027
| 2024-10-29 | number of calls | 215 | 109 | 84 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-10-30 | number of calls | 262 | 144 | 127 |  |  | 0.0011 | 0.0011 | 0 | 0 |  |  | 0.001 | 0.001
| 2024-10-31 | number of calls | 202 | 103 | 72 |  |  | 0.0009 | 0.0009 | 0 | 0 |  |  | 0.0009 | 0.0009
| 2024-11-01 | number of calls | 158 | 89 | 60 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-02 | number of calls | 72 | 50 | 48 |  |  | 0.0041 | 0.0041 | 0 | 0 |  |  | 0.0038 | 0.0038
| 2024-11-03 | number of calls | 69 | 45 | 45 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-04 | number of calls | 146 | 68 | 62 |  |  | 0.0014 | 0.0014 | 0 | 0 |  |  | 0.0013 | 0.0013
| 2024-11-05 | number of calls | 88 | 50 | 45 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-06 | number of calls | 196 | 128 | 91 |  |  | 0.0047 | 0.0047 | 0 | 0 |  |  | 0.0042 | 0.0042
| 2024-11-07 | number of calls | 163 | 83 | 64 |  |  | 0.0006 | 0.0006 | 0 | 0 |  |  | 0.0005 | 0.0005
| 2024-11-08 | number of calls | 129 | 75 | 59 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-09 | number of calls | 71 | 45 | 44 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-10 | number of calls | 48 | 33 | 33 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-11 | number of calls | 161 | 78 | 72 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-12 | number of calls | 155 | 74 | 68 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-13 | number of calls | 223 | 112 | 86 |  |  | 0.0013 | 0.0013 | 0 | 0 |  |  | 0.0012 | 0.0012
| 2024-11-14 | number of calls | 199 | 102 | 76 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-15 | number of calls | 189 | 102 | 81 |  |  | 0.0027 | 0.0027 | 0 | 0 |  |  | 0.0025 | 0.0025
| 2024-11-16 | number of calls | 145 | 85 | 65 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-17 | number of calls | 146 | 73 | 61 |  |  | 0.0081 | 0.0081 | 0.0139 | 0.0139 |  |  | 0.0086 | 0.0086
| 2024-11-18 | number of calls | 445 | 225 | 192 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-19 | number of calls | 279 | 179 | 151 |  |  | 0.0047 | 0.0047 | 0 | 0 |  |  | 0.0043 | 0.0043
| 2024-11-20 | number of calls | 219 | 110 | 80 |  |  | 0.0052 | 0.0052 | 0 | 0 |  |  | 0.0047 | 0.0047
| 2024-11-21 | number of calls | 350 | 146 | 107 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-22 | number of calls | 256 | 166 | 143 |  |  | 0.0027 | 0.0027 | 0.0487 | 0.0487 |  |  | 0.0068 | 0.0068
| 2024-11-23 | number of calls | 192 | 113 | 101 |  |  | 0.0119 | 0.0119 | 0 | 0 |  |  | 0.0108 | 0.0108
| 2024-11-24 | number of calls | 115 | 66 | 57 |  |  | 0.0078 | 0.0078 | 0 | 0 |  |  | 0.0071 | 0.0071
| 2024-11-25 | number of calls | 243 | 111 | 83 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-26 | number of calls | 244 | 133 | 129 |  |  | 0.0002 | 0.0002 | 0 | 0 |  |  | 0.0002 | 0.0002
| 2024-11-27 | number of calls | 463 | 260 | 172 |  |  | 0.0031 | 0.0031 | 0.0292 | 0.0292 |  |  | 0.0054 | 0.0054
| 2024-11-28 | number of calls | 377 | 191 | 154 |  |  | 0.0028 | 0.0028 | 0 | 0 |  |  | 0.0025 | 0.0025
| 2024-11-29 | number of calls | 239 | 140 | 126 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-11-30 | number of calls | 151 | 77 | 69 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-01 | number of calls | 97 | 67 | 63 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-02 | number of calls | 240 | 157 | 138 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-03 | number of calls | 264 | 151 | 118 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-04 | number of calls | 274 | 120 | 101 |  |  | 0.0067 | 0.0067 | 0.0063 | 0.0063 |  |  | 0.0066 | 0.0066
| 2024-12-05 | number of calls | 211 | 111 | 87 |  |  | 0 | 0 | 0.0025 | 0.0025 |  |  | 0.0002 | 0.0002
| 2024-12-06 | number of calls | 264 | 133 | 127 |  |  | 0.003 | 0.003 | 0 | 0 |  |  | 0.0027 | 0.0027
| 2024-12-07 | number of calls | 123 | 76 | 60 |  |  | 0.0216 | 0.0216 | 0 | 0 |  |  | 0.0196 | 0.0196
| 2024-12-08 | number of calls | 139 | 54 | 50 |  |  | 0.0053 | 0.0053 | 0.0409 | 0.0409 |  |  | 0.0085 | 0.0085
| 2024-12-09 | number of calls | 230 | 114 | 100 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-10 | number of calls | 209 | 116 | 97 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-11 | number of calls | 162 | 89 | 81 |  |  | 0.001 | 0.001 | 0 | 0 |  |  | 0.0009 | 0.0009
| 2024-12-12 | number of calls | 188 | 105 | 83 |  |  | 0 | 0 | 0.0003 | 0.0003 |  |  | 0 | 0
| 2024-12-13 | number of calls | 212 | 93 | 80 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-14 | number of calls | 125 | 72 | 54 |  |  | 0 | 0 | 0.0199 | 0.0199 |  |  | 0.0018 | 0.0018
| 2024-12-15 | number of calls | 351 | 89 | 65 |  |  | 0.0023 | 0.0023 | 0 | 0 |  |  | 0.0021 | 0.0021
| 2024-12-16 | number of calls | 1215 | 409 | 287 |  |  | 0.0052 | 0.0052 | 0 | 0 |  |  | 0.0047 | 0.0047
| 2024-12-17 | number of calls | 293 | 160 | 122 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-18 | number of calls | 259 | 122 | 95 |  |  | 0.0079 | 0.0079 | 0 | 0 |  |  | 0.0071 | 0.0071
| 2024-12-19 | number of calls | 231 | 119 | 100 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-20 | number of calls | 216 | 105 | 92 |  |  | 0 | 0 | 0.0199 | 0.0199 |  |  | 0.0018 | 0.0018
| 2024-12-21 | number of calls | 107 | 55 | 44 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-22 | number of calls | 96 | 54 | 46 |  |  | 0.0046 | 0.0046 | 0 | 0 |  |  | 0.0042 | 0.0042
| 2024-12-23 | number of calls | 254 | 145 | 134 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-24 | number of calls | 242 | 86 | 82 |  |  | 0.016 | 0.016 | 0 | 0 |  |  | 0.0145 | 0.0145
| 2024-12-25 | number of calls | 139 | 53 | 51 |  |  | 0.0056 | 0.0056 | 0.0057 | 0.0057 |  |  | 0.0056 | 0.0056
| 2024-12-26 | number of calls | 118 | 62 | 62 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-27 | number of calls | 133 | 74 | 72 |  |  | 0.0059 | 0.0059 | 0 | 0 |  |  | 0.0053 | 0.0053
| 2024-12-28 | number of calls | 107 | 57 | 48 |  |  | 0.0007 | 0.0007 | 0.0409 | 0.0409 |  |  | 0.0044 | 0.0044
| 2024-12-29 | number of calls | 54 | 31 | 30 |  |  | 0.0006 | 0.0006 | 0 | 0 |  |  | 0.0006 | 0.0006
| 2024-12-30 | number of calls | 104 | 55 | 55 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2024-12-31 | number of calls | 102 | 54 | 54 |  |  | 0.0007 | 0.0007 | 0 | 0 |  |  | 0.0006 | 0.0006
| 2025-01-01 | number of calls | 150 | 59 | 50 |  |  | 0.0026 | 0.0026 | 0 | 0 |  |  | 0.0023 | 0.0023
| 2025-01-02 | number of calls | 143 | 76 | 76 |  |  | 0.0006 | 0.0006 | 0 | 0 |  |  | 0.0005 | 0.0005
| 2025-01-03 | number of calls | 128 | 71 | 70 |  |  | 0.0059 | 0.0059 | 0.064 | 0.064 |  |  | 0.0111 | 0.0111
| 2025-01-04 | number of calls | 177 | 102 | 96 |  |  | 0.0013 | 0.0013 | 0 | 0 |  |  | 0.0012 | 0.0012
| 2025-01-05 | number of calls | 335 | 173 | 158 |  |  | 0.0025 | 0.0025 | 0 | 0 |  |  | 0.0023 | 0.0023
| 2025-01-06 | number of calls | 336 | 164 | 137 |  |  | 0.009 | 0.009 | 0 | 0 |  |  | 0.0081 | 0.0081
| 2025-01-07 | number of calls | 269 | 147 | 125 |  |  | 0.0042 | 0.0042 | 0 | 0 |  |  | 0.0038 | 0.0038
| 2025-01-08 | number of calls | 210 | 119 | 100 |  |  | 0.0017 | 0.0017 | 0 | 0 |  |  | 0.0015 | 0.0015
| 2025-01-09 | number of calls | 311 | 127 | 110 |  |  | 0.0011 | 0.0011 | 0 | 0 |  |  | 0.001 | 0.001
| 2025-01-10 | number of calls | 180 | 98 | 87 |  |  | 0.0048 | 0.0048 | 0 | 0 |  |  | 0.0043 | 0.0043
| 2025-01-11 | number of calls | 163 | 76 | 63 |  |  | 0.0114 | 0.0114 | 0.0067 | 0.0067 |  |  | 0.011 | 0.011
| 2025-01-12 | number of calls | 580 | 260 | 199 |  |  | 0.0236 | 0.0236 | 0.0169 | 0.0169 |  |  | 0.023 | 0.023
| 2025-01-13 | number of calls | 324 | 165 | 139 |  |  | 0.0079 | 0.0079 | 0 | 0 |  |  | 0.0072 | 0.0072
| 2025-01-14 | number of calls | 196 | 91 | 82 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-01-15 | number of calls | 214 | 93 | 77 |  |  | 0.0041 | 0.0041 | 0 | 0 |  |  | 0.0037 | 0.0037
| 2025-01-16 | number of calls | 196 | 112 | 100 |  |  | 0.0036 | 0.0036 | 0 | 0 |  |  | 0.0033 | 0.0033
| 2025-01-17 | number of calls | 198 | 118 | 110 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-01-18 | number of calls | 226 | 96 | 73 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-01-19 | number of calls | 101 | 62 | 61 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-01-20 | number of calls | 238 | 132 | 122 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-01-21 | number of calls | 196 | 139 | 123 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-01-22 | number of calls | 189 | 101 | 90 |  |  | 0.0025 | 0.0025 | 0 | 0 |  |  | 0.0023 | 0.0023
| 2025-01-23 | number of calls | 302 | 148 | 138 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-01-24 | number of calls | 198 | 90 | 84 |  |  | 0 | 0 | 0.0473 | 0.0473 |  |  | 0.0043 | 0.0043
| 2025-01-25 | number of calls | 168 | 70 | 63 |  |  | 0.0042 | 0.0042 | 0 | 0 |  |  | 0.0038 | 0.0038
| 2025-01-26 | number of calls | 63 | 32 | 28 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-01-27 | number of calls | 277 | 126 | 120 |  |  | 0.0063 | 0.0063 | 0.0634 | 0.0634 |  |  | 0.0115 | 0.0115
| 2025-01-28 | number of calls | 280 | 138 | 111 |  |  | 0.0044 | 0.0044 | 0 | 0 |  |  | 0.004 | 0.004
| 2025-01-29 | number of calls | 239 | 112 | 96 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-01-30 | number of calls | 187 | 85 | 73 |  |  | 0.0076 | 0.0076 | 0.0321 | 0.0321 |  |  | 0.0098 | 0.0098
| 2025-01-31 | number of calls | 199 | 105 | 92 |  |  | 0.0026 | 0.0026 | 0 | 0 |  |  | 0.0024 | 0.0024
| 2025-02-01 | number of calls | 161 | 74 | 57 |  |  | 0.001 | 0.001 | 0 | 0 |  |  | 0.0009 | 0.0009
| 2025-02-02 | number of calls | 1282 | 577 | 262 |  |  | 0.0072 | 0.0072 | 0.055 | 0.055 |  |  | 0.0115 | 0.0115
| 2025-02-03 | number of calls | 1292 | 633 | 436 |  |  | 0.0068 | 0.0068 | 0 | 0 |  |  | 0.0062 | 0.0062
| 2025-02-04 | number of calls | 378 | 214 | 182 |  |  | 0.0054 | 0.0054 | 0 | 0 |  |  | 0.005 | 0.005
| 2025-02-05 | number of calls | 256 | 98 | 83 |  |  | 0.0167 | 0.0167 | 0 | 0 |  |  | 0.0151 | 0.0151
| 2025-02-06 | number of calls | 263 | 162 | 126 |  |  | 0.0029 | 0.0029 | 0 | 0 |  |  | 0.0026 | 0.0026
| 2025-02-07 | number of calls | 314 | 143 | 128 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-02-08 | number of calls | 97 | 49 | 47 |  |  | 0.0002 | 0.0002 | 0 | 0 |  |  | 0.0002 | 0.0002
| 2025-02-09 | number of calls | 321 | 180 | 143 |  |  | 0.0078 | 0.0078 | 0 | 0 |  |  | 0.0071 | 0.0071
| 2025-02-10 | number of calls | 328 | 169 | 151 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-02-11 | number of calls | 266 | 136 | 101 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-02-12 | number of calls | 274 | 160 | 138 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-02-13 | number of calls | 359 | 202 | 164 |  |  | 0.0055 | 0.0055 | 0 | 0 |  |  | 0.005 | 0.005
| 2025-02-14 | number of calls | 187 | 103 | 81 |  |  | 0.0042 | 0.0042 | 0 | 0 |  |  | 0.0038 | 0.0038
| 2025-02-15 | number of calls | 181 | 111 | 97 |  |  | 0.0058 | 0.0058 | 0.0431 | 0.0431 |  |  | 0.0092 | 0.0092
| 2025-02-16 | number of calls | 78 | 45 | 44 |  |  | 0.0025 | 0.0025 | 0 | 0 |  |  | 0.0023 | 0.0023
| 2025-02-17 | number of calls | 245 | 140 | 133 |  |  | 0.0072 | 0.0072 | 0.0354 | 0.0354 |  |  | 0.0098 | 0.0098
| 2025-02-18 | number of calls | 182 | 89 | 73 |  |  | 0.0052 | 0.0052 | 0 | 0 |  |  | 0.0047 | 0.0047
| 2025-02-19 | number of calls | 346 | 242 | 175 |  |  | 0.001 | 0.001 | 0 | 0 |  |  | 0.0009 | 0.0009
| 2025-02-20 | number of calls | 219 | 139 | 134 |  |  | 0.0023 | 0.0023 | 0 | 0 |  |  | 0.0021 | 0.0021
| 2025-02-21 | number of calls | 180 | 112 | 109 |  |  | 0.0134 | 0.0134 | 0 | 0 |  |  | 0.0122 | 0.0122
| 2025-02-22 | number of calls | 258 | 158 | 132 |  |  | 0.0027 | 0.0027 | 0 | 0 |  |  | 0.0025 | 0.0025
| 2025-02-23 | number of calls | 191 | 113 | 102 |  |  | 0.001 | 0.001 | 0 | 0 |  |  | 0.0009 | 0.0009
| 2025-02-24 | number of calls | 266 | 157 | 150 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-02-25 | number of calls | 187 | 110 | 92 |  |  | 0.0025 | 0.0025 | 0 | 0 |  |  | 0.0023 | 0.0023
| 2025-02-26 | number of calls | 196 | 109 | 99 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-02-27 | number of calls | 164 | 104 | 95 |  |  | 0.0016 | 0.0016 | 0 | 0 |  |  | 0.0015 | 0.0015
| 2025-02-28 | number of calls | 179 | 89 | 87 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-03-01 | number of calls | 146 | 82 | 59 |  |  | 0.0027 | 0.0027 | 0.021 | 0.021 |  |  | 0.0044 | 0.0044
| 2025-03-02 | number of calls | 54 | 35 | 34 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-03-03 | number of calls | 172 | 110 | 97 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-03-04 | number of calls | 308 | 156 | 136 |  |  | 0.0045 | 0.0045 | 0 | 0 |  |  | 0.0041 | 0.0041
| 2025-03-05 | number of calls | 186 | 102 | 97 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-03-06 | number of calls | 179 | 92 | 77 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-03-07 | number of calls | 179 | 109 | 95 |  |  | 0.0034 | 0.0034 | 0 | 0 |  |  | 0.0031 | 0.0031
| 2025-03-08 | number of calls | 98 | 55 | 51 |  |  | 0.0056 | 0.0056 | 0 | 0 |  |  | 0.0051 | 0.0051
| 2025-03-09 | number of calls | 110 | 64 | 57 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-03-10 | number of calls | 210 | 108 | 88 |  |  | 0.0026 | 0.0026 | 0 | 0 |  |  | 0.0024 | 0.0024
| 2025-03-11 | number of calls | 343 | 180 | 132 |  |  | 0.0043 | 0.0043 | 0 | 0 |  |  | 0.0039 | 0.0039
| 2025-03-12 | number of calls | 266 | 162 | 103 |  |  | 0.0118 | 0.0118 | 0 | 0 |  |  | 0.0108 | 0.0108
| 2025-03-13 | number of calls | 178 | 115 | 85 |  |  | 0 | 0 | 0.0141 | 0.0141 |  |  | 0.0013 | 0.0013
| 2025-03-14 | number of calls | 224 | 120 | 85 |  |  | 0.0015 | 0.0015 | 0 | 0 |  |  | 0.0013 | 0.0013
| 2025-03-15 | number of calls | 209 | 107 | 95 |  |  | 0.0034 | 0.0034 | 0 | 0 |  |  | 0.0031 | 0.0031
| 2025-03-16 | number of calls | 232 | 141 | 135 |  |  | 0.0039 | 0.0039 | 0.0499 | 0.0499 |  |  | 0.0081 | 0.0081
| 2025-03-17 | number of calls | 260 | 149 | 125 |  |  | 0.0025 | 0.0025 | 0 | 0 |  |  | 0.0022 | 0.0022
| 2025-03-18 | number of calls | 184 | 102 | 82 |  |  | 0.0011 | 0.0011 | 0 | 0 |  |  | 0.001 | 0.001
| 2025-03-19 | number of calls | 176 | 95 | 83 |  |  | 0.0076 | 0.0076 | 0.0336 | 0.0336 |  |  | 0.0099 | 0.0099
| 2025-03-20 | number of calls | 279 | 176 | 136 |  |  | 0.0017 | 0.0017 | 0 | 0 |  |  | 0.0015 | 0.0015
| 2025-03-21 | number of calls | 171 | 97 | 79 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-03-22 | number of calls | 101 | 58 | 54 |  |  | 0.004 | 0.004 | 0.0487 | 0.0487 |  |  | 0.0081 | 0.0081
| 2025-03-23 | number of calls | 62 | 41 | 41 |  |  | 0.0043 | 0.0043 | 0 | 0 |  |  | 0.0039 | 0.0039
| 2025-03-24 | number of calls | 287 | 147 | 124 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-03-25 | number of calls | 180 | 103 | 83 |  |  | 0.0037 | 0.0037 | 0 | 0 |  |  | 0.0034 | 0.0034
| 2025-03-26 | number of calls | 190 | 101 | 92 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-03-27 | number of calls | 190 | 103 | 92 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-03-28 | number of calls | 155 | 85 | 74 |  |  | 0.0036 | 0.0036 | 0 | 0 |  |  | 0.0033 | 0.0033
| 2025-03-29 | number of calls | 109 | 61 | 55 |  |  | 0.0078 | 0.0078 | 0 | 0 |  |  | 0.0071 | 0.0071
| 2025-03-30 | number of calls | 342 | 131 | 120 |  |  | 0.0045 | 0.0045 | 0 | 0 |  |  | 0.0041 | 0.0041
| 2025-03-31 | number of calls | 197 | 114 | 107 |  |  | 0.006 | 0.006 | 0 | 0 |  |  | 0.0055 | 0.0055
| 2025-04-01 | number of calls | 162 | 101 | 89 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-04-02 | number of calls | 207 | 107 | 96 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-04-03 | number of calls | 221 | 109 | 101 |  |  | 0.0094 | 0.0094 | 0 | 0 |  |  | 0.0085 | 0.0085
| 2025-04-04 | number of calls | 221 | 116 | 89 |  |  | 0 | 0 | 0.021 | 0.021 |  |  | 0.0019 | 0.0019
| 2025-04-05 | number of calls | 116 | 69 | 64 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-04-06 | number of calls | 71 | 40 | 37 |  |  | 0.0036 | 0.0036 | 0 | 0 |  |  | 0.0033 | 0.0033
| 2025-04-07 | number of calls | 215 | 111 | 103 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-04-08 | number of calls | 166 | 86 | 80 |  |  | 0.0012 | 0.0012 | 0 | 0 |  |  | 0.0011 | 0.0011
| 2025-04-09 | number of calls | 189 | 89 | 61 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-04-10 | number of calls | 164 | 110 | 106 |  |  | 0 | 0 | 0.0379 | 0.0379 |  |  | 0.0034 | 0.0034
| 2025-04-11 | number of calls | 154 | 91 | 79 |  |  | 0.0013 | 0.0013 | 0 | 0 |  |  | 0.0012 | 0.0012
| 2025-04-12 | number of calls | 94 | 57 | 55 |  |  | 0.0029 | 0.0029 | 0 | 0 |  |  | 0.0027 | 0.0027
| 2025-04-13 | number of calls | 58 | 38 | 36 |  |  | 0.0059 | 0.0059 | 0.0507 | 0.0507 |  |  | 0.01 | 0.01
| 2025-04-14 | number of calls | 176 | 96 | 82 |  |  | 0.0002 | 0.0002 | 0 | 0 |  |  | 0.0002 | 0.0002
| 2025-04-15 | number of calls | 180 | 103 | 85 |  |  | 0.0016 | 0.0016 | 0 | 0 |  |  | 0.0014 | 0.0014
| 2025-04-16 | number of calls | 189 | 121 | 112 |  |  | 0.0055 | 0.0055 | 0 | 0 |  |  | 0.005 | 0.005
| 2025-04-17 | number of calls | 137 | 78 | 66 |  |  | 0.0132 | 0.0132 | 0 | 0 |  |  | 0.012 | 0.012
| 2025-04-18 | number of calls | 100 | 60 | 57 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-04-19 | number of calls | 47 | 33 | 33 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-04-20 | number of calls | 61 | 39 | 35 |  |  | 0.0011 | 0.0011 | 0 | 0 |  |  | 0.001 | 0.001
| 2025-04-21 | number of calls | 67 | 43 | 42 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-04-22 | number of calls | 195 | 92 | 77 |  |  | 0.0054 | 0.0054 | 0 | 0 |  |  | 0.0049 | 0.0049
| 2025-04-23 | number of calls | 183 | 94 | 93 |  |  | 0.0046 | 0.0046 | 0 | 0 |  |  | 0.0042 | 0.0042
| 2025-04-24 | number of calls | 186 | 118 | 100 |  |  | 0.002 | 0.002 | 0 | 0 |  |  | 0.0018 | 0.0018
| 2025-04-25 | number of calls | 96 | 49 | 48 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-04-26 | number of calls | 70 | 45 | 42 |  |  | 0.0001 | 0.0001 | 0 | 0 |  |  | 0.0001 | 0.0001
| 2025-04-27 | number of calls | 80 | 49 | 45 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-04-28 | number of calls | 196 | 111 | 84 |  |  | 0.0008 | 0.0008 | 0 | 0 |  |  | 0.0008 | 0.0008
| 2025-04-29 | number of calls | 241 | 141 | 100 |  |  | 0.0006 | 0.0006 | 0 | 0 |  |  | 0.0006 | 0.0006
| 2025-04-30 | number of calls | 188 | 97 | 81 |  |  | 0.0029 | 0.0029 | 0 | 0 |  |  | 0.0026 | 0.0026
| 2025-05-01 | number of calls | 160 | 89 | 72 |  |  | 0.0013 | 0.0013 | 0 | 0 |  |  | 0.0012 | 0.0012
| 2025-05-02 | number of calls | 153 | 71 | 63 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-03 | number of calls | 100 | 77 | 76 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-04 | number of calls | 71 | 39 | 37 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-05 | number of calls | 269 | 132 | 105 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-06 | number of calls | 179 | 95 | 84 |  |  | 0.0055 | 0.0055 | 0 | 0 |  |  | 0.005 | 0.005
| 2025-05-07 | number of calls | 271 | 131 | 106 |  |  | 0.0003 | 0.0003 | 0.079 | 0.079 |  |  | 0.0074 | 0.0074
| 2025-05-08 | number of calls | 216 | 104 | 73 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-09 | number of calls | 127 | 67 | 59 |  |  | 0.0069 | 0.0069 | 0 | 0 |  |  | 0.0063 | 0.0063
| 2025-05-10 | number of calls | 123 | 55 | 45 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-11 | number of calls | 62 | 44 | 42 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-12 | number of calls | 193 | 114 | 107 |  |  | 0 | 0 | 0.0487 | 0.0487 |  |  | 0.0044 | 0.0044
| 2025-05-13 | number of calls | 143 | 79 | 72 |  |  | 0.0031 | 0.0031 | 0 | 0 |  |  | 0.0028 | 0.0028
| 2025-05-14 | number of calls | 136 | 68 | 58 |  |  | 0.0024 | 0.0024 | 0 | 0 |  |  | 0.0022 | 0.0022
| 2025-05-15 | number of calls | 134 | 75 | 70 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-16 | number of calls | 150 | 90 | 81 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-17 | number of calls | 121 | 82 | 70 |  |  | 0.0038 | 0.0038 | 0 | 0 |  |  | 0.0035 | 0.0035
| 2025-05-18 | number of calls | 132 | 79 | 75 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-19 | number of calls | 309 | 151 | 133 |  |  | 0.004 | 0.004 | 0 | 0 |  |  | 0.0036 | 0.0036
| 2025-05-20 | number of calls | 238 | 153 | 124 |  |  | 0.0009 | 0.0009 | 0 | 0 |  |  | 0.0009 | 0.0009
| 2025-05-21 | number of calls | 201 | 119 | 92 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-22 | number of calls | 211 | 108 | 76 |  |  | 0.0113 | 0.0113 | 0.0076 | 0.0076 |  |  | 0.011 | 0.011
| 2025-05-23 | number of calls | 181 | 125 | 106 |  |  | 0.0054 | 0.0054 | 0 | 0 |  |  | 0.0049 | 0.0049
| 2025-05-24 | number of calls | 88 | 67 | 63 |  |  | 0.0007 | 0.0007 | 0 | 0 |  |  | 0.0006 | 0.0006
| 2025-05-25 | number of calls | 185 | 70 | 67 |  |  | 0.0068 | 0.0068 | 0 | 0 |  |  | 0.0062 | 0.0062
| 2025-05-26 | number of calls | 299 | 170 | 107 |  |  | 0.0117 | 0.0117 | 0 | 0 |  |  | 0.0106 | 0.0106
| 2025-05-27 | number of calls | 221 | 141 | 106 |  |  | 0.0044 | 0.0044 | 0 | 0 |  |  | 0.004 | 0.004
| 2025-05-28 | number of calls | 227 | 117 | 70 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-29 | number of calls | 176 | 106 | 82 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-30 | number of calls | 173 | 106 | 87 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-05-31 | number of calls | 191 | 90 | 79 |  |  | 0.0003 | 0.0003 | 0 | 0 |  |  | 0.0003 | 0.0003
| 2025-06-01 | number of calls | 86 | 58 | 56 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-02 | number of calls | 182 | 94 | 79 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-03 | number of calls | 238 | 107 | 89 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-04 | number of calls | 241 | 138 | 99 |  |  | 0.0034 | 0.0034 | 0 | 0 |  |  | 0.0031 | 0.0031
| 2025-06-05 | number of calls | 200 | 131 | 104 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-06 | number of calls | 149 | 84 | 63 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-07 | number of calls | 149 | 69 | 60 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-08 | number of calls | 74 | 54 | 51 |  |  | 0.0001 | 0.0001 | 0 | 0 |  |  | 0.0001 | 0.0001
| 2025-06-09 | number of calls | 113 | 68 | 60 |  |  | 0.0039 | 0.0039 | 0 | 0 |  |  | 0.0035 | 0.0035
| 2025-06-10 | number of calls | 258 | 156 | 134 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-11 | number of calls | 251 | 140 | 122 |  |  | 0.0025 | 0.0025 | 0 | 0 |  |  | 0.0023 | 0.0023
| 2025-06-12 | number of calls | 243 | 129 | 113 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-13 | number of calls | 236 | 145 | 123 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-14 | number of calls | 131 | 75 | 59 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-15 | number of calls | 121 | 80 | 76 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-16 | number of calls | 418 | 234 | 158 |  |  | 0.0022 | 0.0022 | 0 | 0 |  |  | 0.002 | 0.002
| 2025-06-17 | number of calls | 233 | 145 | 109 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-18 | number of calls | 322 | 175 | 112 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-19 | number of calls | 235 | 129 | 113 |  |  | 0 | 0 | 0.039 | 0.039 |  |  | 0.0035 | 0.0035
| 2025-06-20 | number of calls | 226 | 117 | 103 |  |  | 0 | 0 | 0.0327 | 0.0327 |  |  | 0.003 | 0.003
| 2025-06-21 | number of calls | 89 | 52 | 47 |  |  | 0.0034 | 0.0034 | 0.0354 | 0.0354 |  |  | 0.0063 | 0.0063
| 2025-06-22 | number of calls | 97 | 59 | 58 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-23 | number of calls | 244 | 127 | 106 |  |  | 0.0026 | 0.0026 | 0 | 0 |  |  | 0.0024 | 0.0024
| 2025-06-24 | number of calls | 265 | 161 | 137 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-25 | number of calls | 245 | 142 | 115 |  |  | 0.0026 | 0.0026 | 0 | 0 |  |  | 0.0024 | 0.0024
| 2025-06-26 | number of calls | 233 | 146 | 105 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-27 | number of calls | 214 | 122 | 95 |  |  | 0.0012 | 0.0012 | 0 | 0 |  |  | 0.0011 | 0.0011
| 2025-06-28 | number of calls | 217 | 91 | 83 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-29 | number of calls | 86 | 58 | 56 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2025-06-30 | number of calls | 294 | 160 | 138 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0

## 6.9 STPIS GSL
| ANNUAL INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| AR RIN 6.9 STPIS - GUARANTEED SERVICE LEVEL |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC05 - Service performance ¦ Other service measures
Guaranteed service levels
Instances where GSL not met
DC06 - Operating expenditure ¦ Distribution business
Guaranteed service levels - payments
6.9.1.1 - GUARANTEED SERVICE LEVELS
| GSL REQUIREMENTS | Units | Service Performance
| Scheme administrator |  | Essential Services Commission
| Specification of scheme |  | Section 14 of the Electricity Distribution Code of Practice
6.9.1.2 - GUARANTEED SERVICE LEVELS - JURISDICTIONAL GSL SCHEME
|  |  | Instances where GSL not met | GSL - payments
| GUARANTEED SERVICE LEVELS |  | Service Performance | Distribution business
| Appointments | Units | Number of instances | $
| Customer arranged appointments Central - number |  | 9812 | 0
| Appointments not met within 15 minutes of agreed time |  | 4 | 140
| Appointments - GSL payments |  | 4 | 140
Connections
| Connections made |  | 42953 | 0
| Connections not made on agreed date |  | 45 | 14880
| Connections - GSL payments - 1-4 day delay |  | 14 | 2480
| Connections - GSL payments - 5+ day delay |  | 31 | 12400
Reliability of supply
| >8 Sustained Interruptions |  | 0 | 0
| >18hrs Duration |  | 624 | 81120
| >30hrs Duration |  | 73 | 13870
| >60hrs Duration |  | 89 | 33820
| Major Event Day > 12 hours |  | 2802 | 252180
Street lights
| Street lights |  | 123868 | 0
| Street lights "out" during period |  | 8368 | 0
| Street lights not repaired by "fix by" date |  | 16 | 0
| Street lights not repaired in 2 business days |  | 16 | 0
| Street lights - number of business days to repair |  | 2 | 0
| Street lights - GSL payments |  | 16 | 400
Planned interruptions
| Planned interruptions 4 business days not given |  | 11 | 0

## 7.10 Juris Scheme
| ANNUAL INFORMATION ORDER | [5 empty] | #25C6FF | Protected (SOCI)
| United Energy | [5 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [5 empty] | 12.5% Grey | Amended
| AR RIN 7.10 JURISDICTIONAL SCHEMES | [5 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
DC09 - Revenue and financial statements ¦ Distribution business
Jurisdictional scheme payments
7.10.1 - JURISDICTIONAL SCHEME PAYMENTS
Jurisdictional scheme payments
| Jurisdictional Scheme Name | Description | Date DNSP Became Subject to Scheme | Description of Cost Recovery Method |  | Distribution Business
|  |  | DD/MM/YYYY |  | Units
| PFIT | Solar Rebate | 2009-01-11 | Full recovery via tariff submission | $ | 3656114.1
| ESV Levy | ESV Levy | 2021-01-07 | Full recovery via tariff submission | $ | 4465252.45

## 7.11 DMIS-DMIAM
| ANNUAL INFORMATION ORDER |  |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  |  | 12.5% Grey | Amended
| AR RIN 7.11 DEMAND MANAGEMENT INCENTIVE SCHEME |  |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC06 - Operating expenditure ¦ Distribution business
Demand management
DC07 - Capital expenditure ¦ Distribution business
Demand management
DC09 - Revenue and financial statements ¦ Distribution business
Demand management - relevant net benefit
7.11.1 DMIS - PROJECTS SUBMITTED FOR APPROVAL
Distribution Business
| DMIS - PROJECTS SUBMITTED FOR APPROVAL - EXPENDITURE AND BENEFITS FOR REPORTING YEAR | Units | Operating expenditure | Capital expenditure | Relevant net benefit
| Lower Mornington Peninsula demand management program | $ | 985553 | 0 | 0
| Total DMIS expenditure | $ | 985553 | 0 | 0
7.11.2 - DMIAM - PROJECTS SUBMITTED FOR APPROVAL
Distribution Business
| DMIAM - PROJECTS SUBMITTED FOR APPROVAL - EXPENDITURE FOR REPORTING YEAR |  | Operating expenditure | Capital expenditure
| Carrum Downs BESS | $ | 0 | 106643
| Total DMIAM expenditure | $ | 0 | 106643

## 8.1 Income
| ANNUAL INFORMATION ORDER | [10 empty] | #25C6FF | Protected (SOCI)
| United Energy | [10 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [10 empty] | 12.5% Grey | Amended
| AR RIN 8.1 INCOME STATEMENT | [10 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
DC09 - Revenue and financial statements ¦ Distribution business
DC09 - Revenue and financial statements ¦ Standard control
Income statement
8.1.1 - INCOME STATEMENT
8.1.1.1 - REVENUE
Standard Control
| TOTAL REVENUE | Units | Audited statutory accounts | Regulatory adjustments | Distribution Business | Total | Excluding dual function assets | Dual function assets
| Distribution revenue (excluding DFA revenues) | $ | 489481210.45 | 46438974.09 | 535920184.54 | 500816765.17 | 500816765.17
| Dual function asset revenue | $ | 0 | 0 | 0 | 0 | 0
| TUOS revenue | $ | 170549114.15 | 4739266.91 | 175288381.06 | 0 | 0
| Cross boundary revenue | $ | 0 | 4559519.08 | 4559519.08
| Other TUOS revenue | $ | 170549114.15 | 179747.83 | 170728861.98
| Jurisdictional scheme revenue | $ | 6945201.45 | 1302810.96 | 8248012.41
| Shared asset revenue | $ | 8989145.33 | -8989145.33 | 0
| Other revenue | $ | 179773026.19 | -150645186.28 | 29127839.91 | 2764933.49 | 2764933.49 | 0
| contributions | $ | 114387140.3 | -114387140.3 | 0 | 0 | 0
| profit from sale of fixed ASSETS | $ | 98538.69 | 0 | 98538.69 | 98538.69 | 98538.69
| Interest Income | $ | 2594255.06 | -575282.61 | 2018972.45 | 2018972.45 | 2018972.45 | 0
| All other revenue | $ | 62693092.14 | -35682763.37 | 27010328.77 | 647422.35 | 647422.35 | 0
| total revenue | $ | 855737697.57 | -107153279.65 | 748584417.92 | 503581698.66 | 503581698.66 | 0
8.1.1 - INCOME STATEMENT
8.1.1.2 - EXPENDITURE
Standard Control
| EXPENDITURE | Units | Audited statutory accounts | Regulatory adjustments | Distribution Business | Total | Excluding dual function assets | Dual function assets
| TUOS expenditure | $ | 170549114.15 | -370233.31 | 170178880.84 | 0 | 0
| Cross boundary expenditure | $ | 0 | 7591339.46 | 7591339.46 |  | 0
| Other TUOS expenditure | $ | 170549114.15 | -7961572.77 | 162587541.38 |  | 0
| Jurisdictional scheme payments | $ | 6945001.45 | 1206120.91 | 8151122.36 |  | 0
| Maintenance expenditure | $ | 56810908.4 | 8413896.1 | 65224804.5 | 55909567.01 | 55909567.01
| Operating expenditure excluding maintenance expenditure | $ | 105158310.05 | 6978833.88 | 112137143.93 | 96292403 | 96292403
| Other expenditure | $ | 277470781.24 | 24141572.35 | 301612353.59 | 274446308.25 | 274446308.25 | 0
| Depreciation | $ | 182344348.53 | 25412293.41 | 207756641.94 | 184992625.65 | 184992625.65
| Debt raising costs | $ | 0 | 0 | 0 | 0 | 0
| Loss from disposal of fixed assets | $ | 0 | 0 | 0 | 0 | 0
| Other Expenditure | $ | -190911.69 | 0 | -190911.69 | -190911.69 | -190911.69 | 0
| SAAS | $ | 1270721.06 | -1270721.06 | 0 | 0 | 0 | 0
| Finance charges | $ | 94046623.34 | 0 | 94046623.34 | 89644594.29 | 89644594.29 | 0
| total expenditure | $ | 616934115.29 | 40370189.93 | 657304305.22 | 426648278.26 | 426648278.26 | 0
DC09 - Revenue and financial statements ¦ Alternative control
Income statement
8.1.1 - INCOME STATEMENT
8.1.1.1 - REVENUE - ALTERNATIVE CONTROL SERVICES
Alternative Control Services
|  |  | Total | Public Lighting |  |  | Metering |  |  | Fee based services | Quoted services
| TOTAL REVENUE | Units |  | Total | Energy Efficient | Non-energy efficient | Total | Smart | Legacy
| Distribution revenue | $ | 35103419.37 | 0 | 0 | 0 | 35103419.37 | 35103419.37 |  | 0 | 0
| Connection charges | $ | 8339660.58 | [6 empty] | 6106756.21 | 2232904.37
| Other ACS revenue | $ | 18023245.84 | 7875988.22 | 3912394.02 | 3963594.2 | 188968.93 | 188968.93 | 0 | 3909613.76 | 6048674.93
| contributions | $ | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| profit from sale of fixed ASSETS | $ | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| all other revenue | $ | 18023245.84 | 7875988.22 | 3912394.02 | 3963594.2 | 188968.93 | 188968.93 |  | 3909613.76 | 6048674.93
| total revenue | $ | 61466325.79 | 7875988.22 | 3912394.02 | 3963594.2 | 35292388.3 | 35292388.3 | 0 | 10016369.97 | 8281579.3
8.1.1 - INCOME STATEMENT
8.1.1.2 - EXPENDITURE - ALTERNATIVE CONTROL SERVICES
Alternative Control Services
|  |  | Total | Public Lighting |  |  | Metering |  |  | Fee based services | Quoted services
| EXPENDITURE | Units |  | Total | Energy Efficient | Non-energy efficient | Total | Smart | Legacy
| Maintenance expenditure | $ | 9315237.49 | 3296568.54 | 1666074.96 | 1630493.58 | 0 | 0 |  | 668431.29 | 5350237.66
| Operating expenditure excluding maintenance expenditure | $ | 15844740.94 | 985095.55 | 490117.74 | 494977.81 | 6205464.09 | 6205464.09 |  | 5839409.85 | 2814771.45
| Other expenditure | $ | 27166045.33 | 2697399.64 | 1341964.79 | 1355434.85 | 24468645.69 | 24468645.69 |  | 0 | 0
| total expenditure | $ | 52326023.76 | 6979063.73 | 3498157.49 | 3480906.24 | 30674109.78 | 30674109.78 | 0 | 6507841.14 | 8165009.11
DC09 - Revenue and financial statements ¦ Other services
Income statement
8.1.1 - INCOME STATEMENT
8.1.1.1 - REVENUE - OTHER SERVICES
| TOTAL REVENUE | Units | Negotiated services | Unregulated services
| Distribution revenue (excluding DFA revenues) | $ |  | 0
| Dual function asset revenue | $ |  | 0
| TUOS revenue | $ | 0 | 175288381.06
| Cross boundary revenue | $ |  | 4559519.08
| Other TUOS revenue | $ |  | 170728861.98
| Jurisdictional scheme revenue | $ |  | 8248012.41
| Shared asset revenue | $ |  | 0
| Other revenue | $ | 0 | 0
| contributions | $ |  | 0
| profit from sale of fixed ASSETS | $ |  | 0
| all other revenue | $ |  | 0
| total revenue | $ | 0 | 183536393.47
8.1.1 - INCOME STATEMENT
8.1.1.2 - EXPENDITURE - OTHER SERVICES
| EXPENDITURE | Units | Negotiated services | Unregulated services
| TUOS expenditure | $ | 0 | 170178880.84
| Cross boundary expenditure | $ |  | 7591339.46
| Other TUOS expenditure | $ |  | 162587541.38
| Jurisdictional scheme payments | $ |  | 8151122.36
| Maintenance expenditure | $ |  | 0
| Operating expenditure excluding maintenance expenditure | $ |  | 0
| Other expenditure | $ |  | 0
| total expenditure | $ | 0 | 178330003.2

## 8.2 Capex
| ANNUAL INFORMATION ORDER | [11 empty] | #25C6FF | Protected (SOCI)
| United Energy | [11 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [11 empty] | 12.5% Grey | Amended
| AR RIN 8.2 CAPEX | [11 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
DC07 - Capital expenditure ¦ Standard control
Capex by purpose
8.2.1 - CAPEX BY PURPOSE - STANDARD CONTROL SERVICES - INCLUDING TOTAL CAPITAL CONTRIBUTIONS
Direct Expenditure
| CAPEX BY PURPOSE (INCLUDING TYPE 1 AND TYPE 2 CAPITAL CONTRIBUTIONS) | Units | Standard Control | SCS - Excluding dual function assets | Dual function assets
| Replacement | $ | 110911181.1 | 110911181.1 | 0
| Export services | $ | 7681766.4 | 7681766.4 | 0
| Augmentation | $ | 16126097.1 | 16126097.1 | 0
| Connection | $ | 126597836.2 | 126597836.2 | 0
| Non Network IT | $ | 32338235.3 | 32338235.3 | 0
| Property | $ | 13340892.6 | 13340892.6 | 0
| Fleet | $ | 6223561.9 | 6223561.9 | 0
| SAAS | $ | 1270721.1 | 1270721.1 | 0
| Non network other | $ | 14306 | 14306 | 0
| Total | $ | 314504597.7 | 314504597.7 | 0
8.2.1 - CAPEX BY PURPOSE - STANDARD CONTROL SERVICES - INCLUDING TOTAL CAPITAL CONTRIBUTIONS - RELATED PARTY MARGIN
Direct Expenditure
| RELATED PARTY MARGIN | Units | Standard Control | SCS - Excluding dual function assets | Dual function assets
| Replacement | $
| Export services | $
| Augmentation | $
| Connection | $
| Non Network IT | $
| Property | $
| Fleet | $
| SAAS | $
| Non network other | $
| Total | $ | 0 | 0 | 0
DC07 - Capital expenditure ¦ Standard control
Capex by asset class
8.2.4 - CAPEX BY ASSET CLASS - including only type 1 capital contributions and PWC undergrounding capex (equity funded)
Total Expenditure
| CAPEX BY ASSET CLASS - Including only Type 1 capital contributions and PWC undergrounding capex (equity funded) | Units | Standard Control | SCS - Excluding dual function assets | Dual function assets
| Subtransmission | $ | 9935329.85 | 9935329.85 | 0
| Distribution system assets | $ | 232037845.62 | 232037845.62 | 0
| SCADA | $ | 0 | 0 | 0
| Non network - IT | $ | 5160842.53 | 5160842.53 | 0
| Non network - other | $ | 19578760.45 | 19578760.45 | 0
| In-house software | $ | 36129880.27 | 36129880.27 | 0
| Total | $ | 302842658.72 | 302842658.72 | 0
8.2.4 - MOVEMENT IN PROVISIONS ALLOCATED TO AS INCURRED CAPEX
Total Expenditure
| MOVEMENTS IN PROVISIONS ALLOCATED TO as incurred CAPEX |  | Standard Control | SCS - Excluding dual function assets | Dual function assets
| Subtransmission | $ | 0 | 0 | 0
| Distribution system assets | $ | 0 | 0 | 0
| SCADA | $ | 0 | 0 | 0
| Non network - IT | $ | 0 | 0 | 0
| Non network - other | $ | 0 | 0 | 0
| In-house software | $ | 0 | 0 | 0
| Total | $ | 0 | 0 | 0
DC07 - Capital expenditure ¦ Standard control
Capex by asset class
Total Expenditure
| CAPEX ADDITIONS TO THE RAB AND TAB |  | Standard Control | SCS - Excluding dual function assets | Dual function assets
| Subtransmission | $ | 9935329.85 | 9935329.85 | 0
| Distribution system assets | $ | 232037845.62 | 232037845.62 | 0
| SCADA | $ | 0 | 0 | 0
| Non network - IT | $ | 5160842.53 | 5160842.53 | 0
| Non network - other | $ | 19578760.45 | 19578760.45 | 0
| In-house software | $ | 36129880.27 | 36129880.27 | 0
| Total | $ | 302842658.72 | 302842658.72 | 0
8.2.6 - DISPOSALS BY ASSET CLASS
Total Expenditure
| DISPOSALS BY ASSET CLASS |  | Standard Control | SCS - Excluding dual function assets | Dual function assets
| Subtransmission | $ | 39100 | 39100 | 0
| Distribution system assets | $ | 52500 | 52500 | 0
| SCADA | $ | 0 | 0 | 0
| Non network - IT | $ | 0 | 0 | 0
| Non network - other | $ | 168856.08 | 168856.08 | 0
| In-house software | $ | 0 | 0 | 0
| Total | $ | 260456.08 | 260456.08 | 0
8.2.7 - IMMEDIATE EXPENSING OF CAPEX
Total Expenditure
| IMMEDIATE EXPENSING OF CAPEX |  | Standard Control | SCS - Excluding dual function assets | Dual function assets
| Subtransmission | $ | 4492148 | 4492148 | 0
| Distribution system assets | $ | 104913312 | 104913312 | 0
| SCADA | $ | 0 | 0 | 0
| Non network - IT | $ | 719791 | 719791 | 0
| Non network - other | $ | 0 | 0 | 0
| In-house software | $ | 5370218 | 5370218 | 0
| Total | $ | 115495469 | 115495469 | 0
DC07 - Capital expenditure ¦ Standard control
Capital contributions by asset class
8.2.5 - CAPITAL CONTRIBUTIONS BY ASSET CLASS
Total Expenditure
| CAPITAL CONTRIBUTIONS BY ASSET CLASS | Units | Standard Control | SCS - Excluding dual function assets | Dual function assets
| Type 1 capital contributions | $ | 89899368.33 | 89899368.33
| Type 2 capital contributions | $ | 11661939 | 11661939
| PWC undergrounding capex (equity funded) | $ | 0 | 0
| Total | $ | 101561307.33 | 101561307.33 | 0
TYPE 1 CAPITAL CONTRIBUTION BY ASSET CLASS
| Subtransmission | $ | 0 | 0 | 0
| Distribution system assets | $ | 89899368.33 | 89899368.33 | 0
| SCADA | $ | 0 | 0 | 0
| Non network - IT | $ | 0 | 0 | 0
| Non network - other | $ | 0 | 0 | 0
| In-house software | $ | 0 | 0 | 0
| Total | $ | 89899368.33 | 89899368.33 | 0
TYPE 2 CAPITAL CONTRIBUTION BY ASSET CLASS
| Subtransmission | $ | 38469 | 38469 | 0
| Distribution system assets | $ | 11623470 | 11623470 | 0
| SCADA | $ | 0 | 0 | 0
| Non network - IT | $ | 0 | 0 | 0
| Non network - other | $ | 0 | 0 | 0
| In-house software | $ | 0 | 0 | 0
| Total | $ | 11661939 | 11661939 | 0
8.2.8 - CAPITAL CONTRIBUTIONS BY ASSET CLASS - PWC UNDERGROUNDING CAPEX (equity funded)
Total Expenditure
| CAPITAL CONTRIBUTIONS BY ASSET CLASS - PWC UNDERGROUNDING CAPEX (EQUITY FUNDED) | Units | Standard Control | SCS - Excluding dual function assets | Dual function assets
| Subtransmission | $ | 0 | 0 | 0
| Distribution system assets | $ | 0 | 0 | 0
| SCADA | $ | 0 | 0 | 0
| Non network - IT | $ | 0 | 0 | 0
| Non network - other | $ | 0 | 0 | 0
| In-house software | $ | 0 | 0 | 0
| Total | $ | 0 | 0 | 0
DC07 - Capital expenditure ¦ Alternative control
Capex by purpose
8.2.3 - CAPEX OTHER - INCLUDING TOTAL CAPITAL CONTRIBUTIONS
Alternative Control Services
|  |  | Total | Direct | [7 empty] | Indirect
|  |  |  | Public Lighting |  |  | Metering |  |  | Fee based services | Quoted services
| CAPEX - OTHER SERVICES (INCLUDING CAPITAL CONTRIBUTIONS) | Units |  | Total | Energy Efficient | Non-energy efficient | Total | Smart | Legacy
| Public Lighting | $ | 18804880.33 | 18804880.33 | 18790357.92 | 14522.41 | 0 | 0 |  | 0 | 0 | 0
| Metering - Meters | $ | 4926356.27 | 0 | 0 | 0 | 4926356.27 | 4926356.27 |  | 0 | 0 | 0
| Metering - IT | $ | 43159.94 | 0 | 0 | 0 | 43159.94 | 43159.94 |  | 0 | 0 | 0
| Metering - Communications | $ | 687228.96 | 0 | 0 | 0 | 687228.96 | 687228.96 |  | 0 | 0 | 0
| Metering - Other | $ | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| RELATED PARTY MARGIN | Units
| Public Lighting | $
| Metering - Meters | $
| Metering - IT | $
| Metering - Communications | $
| Metering - Other | $
DC07 - Capital expenditure ¦ Alternative control
Capex by asset class
8.2.5(B) - CAPITAL CONTRIBUTIONS BY TYPE
Alternative Control Services
|  |  | Total | Direct
|  |  |  | Public Lighting |  |  | Metering |  |  | Fee based services | Quoted services
| CAPITAL CONTRIBUTIONS BY TYPE | Units |  | Total | Energy Efficient | Non-energy efficient | Total | Smart | Legacy
| Type 1 capital contributions | $ |  | 1831535.45 | 1831535.45 | 0 | 0 | 0 |  | 0 | 0
| Type 2 capital contributions | $ |  | 10994298 | 10994298 | 0 | 0 | 0 |  | 0 | 0
DC07 - Capital expenditure ¦ Other services
Capex by purpose
8.2.3 - CAPEX OTHER - INCLUDING TOTAL CAPITAL CONTRIBUTIONS
| CAPEX BY PURPOSE (INCLUDING CAPITAL CONTRIBUTIONS) | Units | Negotiated distribution services
$
RELATED PARTY MARGINS
$

## 8.4 Opex
| ANNUAL INFORMATION ORDER | [16 empty] | #25C6FF | Protected (SOCI)
| United Energy | [16 empty] | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 | [16 empty] | 12.5% Grey | Amended
| AR RIN 8.4 OPEX | [16 empty] | #FFCCCC & 12.5% Grey | Amended Confidential
DC06 - Operating expenditure ¦ Distribution business
DC06 - Operating expenditure ¦ Standard control
DC06 - Operating expenditure ¦ Alternative control
DC06 - Operating expenditure ¦ Other services
Opex category
8.4.1 - OPERATING & MAINTENANCE EXPENDITURE - BY PURPOSE
8.4.2 - OPERATING & MAINTENANCE EXPENDITURE - BY PURPOSE - MARGINS ONLY
|  |  | Audited Statutory Accounts | Regulatory Adjustments | Distribution Business | Standard Control Services | Alternative Control Services | [9 empty] | Negotiated services
[7 empty] | Total | Direct | [7 empty] | Indirect
[8 empty] | Public Lighting |  |  | Metering |  |  | Fee based services | Quoted services
| OPEX CATEGORY | Units | [5 empty] | Total | Energy Efficient | Non-energy efficient | Total | Smart | Legacy
| Debt raising expenditure | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Maintenance | $ | 0 | 25597214.35 | 25597214.35 | 25597214.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vegetation management | $ | 0 | 18091097.65 | 18091097.65 | 18091097.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Emergency response | $ | 0 | 12221255.01 | 12221255.01 | 12221255.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network operating costs | $ | 71189475.12 | -56199870.22 | 14989604.9 | 14989604.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSL payments | $ | 420375.1 | 0 | 420375.1 | 420375.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IT | $ | 38324611.01 | -1270721.06 | 37053889.95 | 32989304.15 | 4064585.81 | 528057.42 | 262976.45 | 265080.97 | 2311646.62 | 2311646.62 | 0 | 670379.97 | 554501.8 | 0 | 0
| Non-network operating costs | $ | 51459858.17 | 0 | 51459858.17 | 47893118.84 | 3566739.32 | 457038.13 | 227141.29 | 229896.84 | 2048197.36 | 2048197.36 | 0 | 581051.09 | 480452.74 | 0 | 0
| Public lighting | $ | 0 | 3296568.54 | 3296568.54 | 0 | 3296568.54 | 3296568.54 | 1666074.96 | 1630493.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Metering | $ | 1845620.11 | 0 | 1845620.11 | 0 | 1845620.11 | 0 | 0 | 0 | 1845620.11 | 1845620.11 | 0 | 0 | 0 | 0 | 0
| Fee-based and Quoted | $ | 0 | 12386464.65 | 12386464.65 | 0 | 12386464.65 | 0 | 0 | 0 | 0 | 0 | 0 | 5256410.08 | 7130054.57 | 0 | 0
| Total | $ | 163239939.51 | 14122008.92 | 177361948.43 | 152201970 | 25159978.43 | 4281664.09 | 2156192.7 | 2125471.39 | 6205464.09 | 6205464.09 | 0 | 6507841.14 | 8165009.11 | 0 | 0
RELATED PARTY MARGINS
| Debt raising expenditure | $
| Maintenance | $
| Vegetation management | $
| Emergency response | $
| Network operating costs | $
| GSL payments | $
| IT | $
| Non-network operating costs | $
| Public lighting | $
| Metering | $
| Fee-based and Quoted | $

## 9.5 TUoS
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| AR RIN 9.5 TUoS AUDIT (t-2) |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC09 - Revenue and financial statements ¦ Distribution business
TUOS expenditure
9.5.1 - TUOS CHARGES (AEMO)
| TUOS CHARGES | Units | Distribution Business
| Payments to TNSP/AEMO (Prescribed TUOS Services) | $ | 26287337
| Payments to TNSP/AEMO (Prescribed common transmission services) | $ | 126877428
| Grid equalisation | $ | 0
| Other TUOS charges | $ | 0
| TUOS charges | $ | 153164765
9.5.2 - TRANSMISSION CONNECTION FEES
| TRANSMISSION CONNECTION FEES | Units | Distribution Business
| AusNet (Connection) | $ | 9295047
| Transmission connection fees |  | 9295047
9.5.4 - PAYMENTS TO EMBEDDED GENERATORS
PAYMENTS TO EMBEDDED GENERATORS
| Avoided transmission costs | Units | Distribution Business
| Avoided Transmission Cost | $ | 127730
| Avoided transmission costs |  | 127730
Avoided TUOS
| <DNSP specified> | $
$
$
| Avoided TUOS |  | 0
| Payments to embedded generators |  | 127730

## P1.1 Cost reflective tariffs
| REGULATORY INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| AR RIN P1. COST REFLECTIVE TARIFF AND METERING |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
ENERGY DELIVERED
DC02 - Operational outputs ¦ Energy delivered by CR tariff
Customers (tariff) by meter type
P1.1.1 - ENERGY DELIVERED BY METER TYPE - COST REFLECTIVE TARIFF CUSTOMERS
| RESIDENTIAL CUSTOMERS | Units | Total energy delivered
| Meter Type 1-3 | MWh | 183
| Meter Type 4 | MWh | 2643
| Meter Type 5 | MWh | 573665
| Meter Type 6 | MWh | 338
| Meter Type 7 | MWh | 0
| Total residential customers | MWh | 576829
LOW VOLTAGE SMALL BUSINESS CUSTOMERS
| Meter Type 1-3 | MWh | 6516
| Meter Type 4 | MWh | 151898
| Meter Type 5 | MWh | 307683
| Meter Type 6 | MWh | 29
| Meter Type 7 | MWh | 58214
| Total low voltage small business customers | MWh | 524340
LOW VOLTAGE NON RESIDENTIAL CUSTOMERS (excluding small business)
| Meter Type 1-3 | MWh | 1148007
| Meter Type 4 | MWh | 1415101
| Meter Type 5 | MWh | 261736
| Meter Type 6 | MWh | 0
| Meter Type 7 | MWh | 0
| Total low voltage non residential customers | MWh | 2824844
HIGH VOLTAGE NON RESIDENTIAL CUSTOMERS
| Meter Type 1-3 | MWh | 668604
| Meter Type 4 | MWh | 333738
| Total high voltage non residential customers | MWh | 1002342
| Customers (tariff) by meter type TOTAL | MWh | 4928355
DC02 - Operational outputs ¦ Energy delivered by CR tariff
Customers (tariff) by tariff
P1.1.2 - ENERGY DELIVERED BY TARIFF TYPE - COST REFLECTIVE TARIFF CUSTOMERS
| TARIFF NAME | TARIFF CODE
| RESIDENTIAL CUSTOMERS |  | Units | Total energy delivered
| Residential ToU | URTOU | MWh | 521216
| Residential Demand | RESKW1R | MWh | 3190
| Dedicated Circuit | LVDed | MWh | 47921
| Residential daytime saver | URDS | MWh | 4502
| Total residential customers |  | MWh | 576829
LOW VOLTAGE SMALL BUSINESS CUSTOMERS
| Small Business ToU | LVTOU | MWh | 465865
| Unmetered supplies | UnMet | MWh | 58214
| Community battery time of use | LVNDBB | MWh | 261
| Total low voltage small business customers |  | MWh | 524340
LOW VOLTAGE NON RESIDENTIAL CUSTOMERS (excluding small business)
| Small Business demand | LVMKW1R | MWh | 580335
| Large low voltage | LVKVATOU | MWh | 2243643
| Generator trial tariff | GT2 | MWh | 866
| Total low voltage non residential customers |  | MWh | 2824844
HIGH VOLTAGE NON RESIDENTIAL CUSTOMERS
| High Voltage | HVKVATOU | MWh | 979608
| Sub-transmission | SUBTKVATOU | MWh | 22734
| Total high voltage non residential customers |  | MWh | 1002342
| Total customers on cost reflective tariffs |  | MWh | 4928355
DC04 - Customer numbers ¦ Cost reflective tariffs
Customers by meter
P1.1.3 - NUMBER CUSTOMERS BY METER TYPE - COST REFLECTIVE TARIFF CUSTOMERS
| RESIDENTIAL CUSTOMERS | Units | as at 30 June (end of year)
| Meter Type 1-3 | number of customers | 1
| Meter Type 4 | number of customers | 89
| Meter Type 5 | number of customers | 114869
| Meter Type 6 | number of customers | 0
| Meter Type 7 | number of customers | 0
| Total residential customers |  | 114959
LOW VOLTAGE SMALL BUSINESS CUSTOMERS
| Meter Type 1-3 | number of customers | 14
| Meter Type 4 | number of customers | 1455
| Meter Type 5 | number of customers | 20889
| Meter Type 6 | number of customers | 0
| Meter Type 7 | number of customers | 7494
| Total low voltage small business customers |  | 29852
LOW VOLTAGE NON RESIDENTIAL CUSTOMERS (excluding small business)
| Meter Type 1-3 | number of customers | 686
| Meter Type 4 | number of customers | 4623
| Meter Type 5 | number of customers | 5962
| Meter Type 6 | number of customers | 0
| Meter Type 7 | number of customers | 0
| Total low voltage non residential customers |  | 11271
HIGH VOLTAGE NON RESIDENTIAL CUSTOMERS
| Meter Type 1-3 | number of customers | 75
| Meter Type 4 | number of customers | 36
| Total high voltage non residential customers | number of customers | 111
| Customers (tariff) by meter type TOTAL | number of customers | 156193
DC04 - Customer numbers ¦ Cost reflective tariffs
Customers by tariffs
P1.1.4 - NMI COUNT BY TARIFF TYPE - COST REFLECTIVE TARIFF CUSTOMERS
| TARIFF NAME | TARIFF CODE
| RESIDENTIAL CUSTOMERS |  | Units | as at 30 June (end of year)
| Residential ToU | URTOU | number of customers | 113084
| Residential Demand | RESKW1R | number of customers | 577
| Dedicated Circuit | URDS | number of customers | 1298
| Total residential customers |  |  | 114959
LOW VOLTAGE SMALL BUSINESS CUSTOMERS
| Small Business ToU | LVTOU | number of customers | 22356
| Unmetered supplies | UnMet | number of customers | 7494
| Community battery time of use | LVNDBB | number of customers | 2
| Total low voltage small business customers |  |  | 29852
LOW VOLTAGE NON RESIDENTIAL CUSTOMERS (excluding small business)
| Small Business demand | LVMKW1R | number of customers | 8236
| Large low voltage | LVKVATOU | number of customers | 3031
| Generator trial tariff | GT2 | number of customers | 4
| Total low voltage non residential customers |  |  | 11271
HIGH VOLTAGE NON RESIDENTIAL CUSTOMERS
| High Voltage | HVKVATOU | Number of customers | 110
| Sub-transmission | SUBTKVATOU | Number of customers | 1
| Total high voltage non residential customers |  | number of customers | 111
| Total customers on cost reflective tariffs |  | number of customers | 156193

## P1.2 NCR tariffs
| REGULATORY INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| AR RIN P1. NON-COST REFLECTIVE TARIFF AND METERING |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
ENERGY DELIVERED
DC02 - Operational outputs ¦ Energy delivered by NCR tariff
Customers (tariff) by meter type
P1.2.1 - ENERGY DELIVERED BY METER TYPE - NON-COST REFLECTIVE TARIFF CUSTOMERS
| RESIDENTIAL CUSTOMERS | Units | Total energy delivered
| Meter Type 1-3 | MWh | 0
| Meter Type 4 | MWh | 1837
| Meter Type 5 | MWh | 2417684
| Meter Type 6 | MWh | 3933
| Meter Type 7 | MWh | 0
| Total residential customers | MWh | 2423454
LOW VOLTAGE SMALL BUSINESS CUSTOMERS
| Meter Type 1-3 | MWh | 208
| Meter Type 4 | MWh | 7746
| Meter Type 5 | MWh | 252257
| Meter Type 6 | MWh | 3609
| Meter Type 7 | MWh | 0
| Total low voltage small business customers | MWh | 263820
LOW VOLTAGE NON RESIDENTIAL CUSTOMERS (excluding small business)
| Meter Type 1-3 | MWh
| Meter Type 4 | MWh
| Meter Type 5 | MWh
| Meter Type 6 | MWh
| Meter Type 7 | MWh
| Total low voltage non residential customers | MWh | 0
HIGH VOLTAGE NON RESIDENTIAL CUSTOMERS
| Meter Type 1-3 | MWh
| Meter Type 4 | MWh
| Total high voltage non residential customers | MWh | 0
| Customers (tariff) by meter type TOTAL | MWh | 2687274
DC02 - Operational outputs ¦ Energy delivered by NCR tariff
Customers (tariff) by tariff
P1.2.2 - ENERGY DELIVERED BY TARIFF TYPE - NON-COST REFLECTIVE TARIFF CUSTOMERS
| TARIFF NAME | TARIFF CODE
| RESIDENTIAL CUSTOMERS |  | Units | Total energy delivered
| Residential Single Rate | LVS1R | MWh | 2423454
| Total residential customers |  | MWh | 2423454
LOW VOLTAGE SMALL BUSINESS CUSTOMERS
| Small Business single rate | LVM1R | MWh | 263820
| Total low voltage small business customers |  | MWh | 263820
LOW VOLTAGE NON RESIDENTIAL CUSTOMERS (excluding small business)
| <DNSP specified> | <DNSP specified> | MWh
MWh
MWh
| Total low voltage non residential customers |  | MWh | 0
HIGH VOLTAGE NON RESIDENTIAL CUSTOMERS
| <DNSP specified> | <DNSP specified> | MWh
MWh
MWh
| Total high voltage non residential customers |  | MWh | 0
| Total customers on non-cost reflective tariffs |  | MWh | 2687274
DC04 - Customer numbers ¦ Non-cost reflective tariffs
Customers by meter
P1.2.3 - NUMBER CUSTOMERS BY METER TYPE - NON-COST REFLECTIVE TARIFF CUSTOMERS
| RESIDENTIAL CUSTOMERS | Units | as at 30 June (end of year)
| Meter Type 1-3 | number of customers | 0
| Meter Type 4 | number of customers | 133
| Meter Type 5 | number of customers | 530491
| Meter Type 6 | number of customers | 1140
| Meter Type 7 | number of customers | 0
| Total residential customers |  | 531764
LOW VOLTAGE SMALL BUSINESS CUSTOMERS
| Meter Type 1-3 | number of customers | 2
| Meter Type 4 | number of customers | 257
| Meter Type 5 | number of customers | 30287
| Meter Type 6 | number of customers | 268
| Meter Type 7 | number of customers | 0
| Total low voltage small business customers |  | 30814
LOW VOLTAGE NON RESIDENTIAL CUSTOMERS (excluding small business)
| Meter Type 1-3 | number of customers
| Meter Type 4 | number of customers
| Meter Type 5 | number of customers
| Meter Type 6 | number of customers
| Meter Type 7 | number of customers
| Total low voltage non residential customers |  | 0
HIGH VOLTAGE NON RESIDENTIAL CUSTOMERS
| Meter Type 1-3 | number of customers
| Meter Type 4 | number of customers
| Total high voltage non residential customers | number of customers | 0
| Customers (tariff) by meter type TOTAL | number of customers | 562578
DC04 - Customer numbers ¦ Non-cost reflective tariffs
Customers by tariffs
P1.2.4 - DISTRIBUTION CUSTOMER NUMBERS BY TARIFF TYPE - NON-COST REFLECTIVE TARIFFS
Customers by tariffs
| TARIFF NAME | TARIFF CODE
| RESIDENTIAL CUSTOMERS |  | Units | as at 30 June (end of year)
| Residential Single Rate | LVS1R | number of customers | 531764
| Total residential customers |  |  | 531764
LOW VOLTAGE SMALL BUSINESS CUSTOMERS
| Small Business single rate | LVM1R | number of customers | 30814
| Total low voltage small business customers |  |  | 30814
LOW VOLTAGE NON RESIDENTIAL CUSTOMERS (excluding small business)
| <DNSP specified> | <DNSP specified> | number of customers
number of customers
number of customers
| Total low voltage non residential customers |  |  | 0
HIGH VOLTAGE NON RESIDENTIAL CUSTOMERS
| <DNSP specified> | <DNSP specified> | Number of customers
Number of customers
number of customers
| Total high voltage non residential customers |  | number of customers | 0
| Total customers on non-cost reflective tariffs |  | number of customers | 562578

## 7.4 Shared Assets
| ANNUAL INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| RESET RIN 7.4 SHARED ASSETS |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC09 - Revenue and financial statements ¦ Other services
Unregulated service revenue earned with shared assets
7.4.1 - TOTAL UNREGULATED REVENUE EARNED WITH SHARED ASSETS
Unregulated service revenue earned with shared assets
| Shared asset | Type of asset used to provide service | Units | Unregulated services
| Pole Rental | Poles | $ | 8989145

## P1.3 Secondary tariffs
| REGULATORY INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| P1.3 SECONDARY TARIFFS |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC04 - Customer numbers ¦ Secondary tariffs
Customers (tariffs) with secondary tariffs
P1.3.3 - CUSTOMER NUMBERS BY METER TYPE - SECONDARY TARIFF CUSTOMERS
| RESIDENTIAL CUSTOMERS | Units | as at 30 June (end of year)
| Meter Type 1-3 | number of customers | 0
| Meter Type 4 | number of customers | 2
| Meter Type 5 | number of customers | 48583
| Meter Type 6 | number of customers | 389
| Meter Type 7 | number of customers | 0
| Total residential customers |  | 48974
LOW VOLTAGE SMALL BUSINESS CUSTOMERS
| Meter Type 1-3 | number of customers | 0
| Meter Type 4 | number of customers | 0
| Meter Type 5 | number of customers | 99
| Meter Type 6 | number of customers | 5
| Meter Type 7 | number of customers | 0
| Total low voltage small business customers |  | 104
LOW VOLTAGE NON RESIDENTIAL CUSTOMERS (excluding small business)
| Meter Type 1-3 | number of customers
| Meter Type 4 | number of customers
| Meter Type 5 | number of customers
| Meter Type 6 | number of customers
| Meter Type 7 | number of customers
| Total low voltage non residential customers |  | 0
HIGH VOLTAGE NON RESIDENTIAL CUSTOMERS
| Meter Type 1-3 | number of customers
| Meter Type 4 | number of customers
| Total high voltage non residential customers | number of customers | 0
| Customers (tariff) by meter type TOTAL | number of customers | 49078
DC04 - Customer numbers ¦ Secondary tariffs
Customers (tariffs) with secondary tariffs
P1.3.4 - CUSTOMER NUMBERS BY TARIFF TYPE - SECONDARY TARIFFS
| TARIFF NAME | TARIFF CODE
| RESIDENTIAL CUSTOMERS |  | Units | as at 30 June (end of year)
| Dedicated Circuit | LVDED | number of customers | 48974
| Total residential customers |  |  | 48974
LOW VOLTAGE SMALL BUSINESS CUSTOMERS
| Dedicated Circuit | LVDED | number of customers | 104
| Total low voltage small business customers |  |  | 104
LOW VOLTAGE NON RESIDENTIAL CUSTOMERS (excluding small business)
| <DNSP specified> | <DNSP specified> | number of customers
number of customers
number of customers
| Total low voltage non residential customers |  |  | 0
HIGH VOLTAGE NON RESIDENTIAL CUSTOMERS
| <DNSP specified> | <DNSP specified> | Number of customers
Number of customers
number of customers
| Total high voltage non residential customers |  | number of customers | 0
| Total customers on secondary tariffs |  | number of customers | 49078

## 3.4B Total customers
| ANNUAL INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| 3.4B TOTAL CUSTOMERS |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC04 - Customer numbers ¦ Total customers
Customers (distribution services)
3.4.2.3 - TOTAL CUSTOMERS BY METERING AND CONNECTION TYPE
| TOTAL CUSTOMERS |  | as at 30 June
| Breakdown 1 | Units | NMI | No NMI
| Metered customer | number of customers | 711277 | 0
| Unmetered customers | number of customers | 7494 | 0
Breakdown 2
| Energised connection points | number of customers | 717388 | 0
| Un-energised connection points | number of customers | 1383 | 0
| Total customers | Number of customers | 718771 | 0
DC04 - Customer numbers ¦ Total customers
Customers (distribution services) by meter status
3.4.2.4 - TOTAL CUSTOMERS BY METERING STATUS
as at 30 June
| METER PROVISION | Units | Total Customers
| Customers where meter is provided by retailer or other party | number of customers | 7496
| Customers where meter is provided by DNSP | number of customers | 703781
UNMETERED CUSTOMERS BY CLASS
| Residential | number of customers | 0
| Non residential LV | number of customers | 7494
| Non residential HV | number of customers | 0

## 3.9 Export services
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| Information request - 3.9 EXPORT SERVICES |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC02 - Operational outputs ¦ Export services
Export volumes
3.9.1 - NET METERED VOLUME OF ENERGY EXPORTED BY CUSTOMERS WITH SMART METERS
| FEEDER CLASSIFICATION | Units | Energy
| CBD | MWh | 0
| Urban | MWh | 591733
| Short rural | MWh | 87894
| Long rural | MWh | 0
DC03 - Network metrics ¦ Export services
Export capacity requested
3.9.2.1 - EXPORT CAPACITY REQUESTED BY CUSTOMER TYPE/FEEDER CLASSIFICATION
| CUSTOMER (EXPORT SERVICES) TYPE | Units | Volume
| Total customers | kVA | 64672.77
| Residential | kVA | 42621.53
| Non residential HV | kVA | 3754
| Non residential LV | kVA | 18297.24
| Low voltage small business | kVA | 7534.78
| Low voltage non residential (excluding small business) | kVA | 10762.46
FEEDER CLASSIFICATION
| CBD | kVA | 0
| Urban | kVA | 57482
| Short rural | kVA | 6830.77
| Long rural | kVA | 0
DC03 - Network metrics ¦ Export services
Export capacity approved
3.9.2.2 - EXPORT CAPACITY APPROVED BY CUSTOMER TYPE/FEEDER CLASSIFICATION
| EXPORT CUSTOMER TYPE | Units | Volume
| Total customers | kVA | 58049.41
| Residential | kVA | 39680.55
| Non residential HV | kVA | 1627
| Non residential LV | kVA | 16741.86
| Low voltage small business | kVA | 6878.54
| Low voltage non residential (excluding small business) | kVA | 9863.32
FEEDER CLASSIFICATION
| CBD | kVA | 0
| Urban | kVA | 52083.01
| Short rural | kVA | 5966.4
| Long rural | kVA | 0
DC03 - Network metrics ¦ Export services
Average Static Export
3.9.2.3 - AVERAGE STATIC EXPORT LIMIT AT YEAR END (NON-ZERO)
| CUSTOMER (EXPORT SERVICES) TYPE | Units | Volume
| Total customers | kVA | 6
| Residential | kVA | 5
| Non residential HV | kVA | 5602
| Non residential LV | kVA | 33
| Low voltage small business | kVA | 20
| Low voltage non residential (excluding small business) | kVA | 62
FEEDER CLASSIFICATION
| CBD | kVA | 0
| Urban | kVA | 7
| Short rural | kVA | 6
| Long rural | kVA | 0
DC03 - Network metrics ¦ Export services
Metrics related to utilised and curtailed energy
3.9.3 - UTILISATION AND CURTAILED ENERGY
| TOTAL POTENTIAL GENERATION | Units | Volume
| Total potential customer generation | KWh | 1089108812
| Potential customer generation - customers with smart meters | KWh | 1054974196
| Potential customer generation - customers without smart meters | KWh | 34134616
CONSUMER ENERGY RESOURCE CURTAILMENT
| Total curtailment | KWh | 46654582
| Curtailment due to inverter voltage response | KWh | 470188
| Curtailment due to static export limits | KWh | 46184394
| Curtailment due to dynamic export limits | KWh | 0
| Curtailment directed for system security | KWh | 0
| Other curtailment | KWh | 0
DC03 - Network metrics ¦ Export services
Exporting customer capacity
3.9.4.1 - EXPORTING CUSTOMER CAPACITY BY CUSTOMER (EXPORT SERVICES) TYPE
TOTAL INSTALLED CAPACITY
| SOLAR PV ONLY | Units | Volume
| Residential | kVA | 600930
| Non residential HV | kVA | 34506
| Non residential LV | kVA | 195938
| Low voltage small business | kVA | 104279
| Low voltage non residential (excluding small business) | kVA | 91659
SOLAR PV AND BATTERY
| Residential | kVA | 29098
| Non residential HV | kVA | 3067
| Non residential LV | kVA | 4188
| Low voltage small business | kVA | 2329
| Low voltage non residential (excluding small business) | kVA | 1859
BATTERY ONLY
| Residential | kVA | 798
| Non residential HV | kVA | 0
| Non residential LV | kVA | 30
| Low voltage small business | kVA | 30
| Low voltage non residential (excluding small business) | kVA | 0
| Total installed capacity | kVA | 868555
DC03 - Network metrics ¦ Export services
Exporting customer capacity
3.9.4.2 - EXPORTING CUSTOMER CAPACITY BY FEEDER CLASSIFICATION
TOTAL INSTALLED CAPACITY
| SOLAR PV ONLY | Units | Volume
| CBD | kVA | 0
| Urban | kVA | 721011
| Short rural | kVA | 110363
| Long rural | kVA | 0
SOLAR PV AND BATTERY
| CBD | kVA | 0
| Urban | kVA | 29779
| Short rural | kVA | 6575
| Long rural | kVA | 0
BATTERY ONLY
| CBD | kVA | 0
| Urban | kVA | 690
| Short rural | kVA | 138
| Long rural | kVA | 0
| Total installed capacity | kVA | 868556
DC04 - Customer numbers ¦Export services
Export customers with smart meters
3.9.5.1 - EXPORTING CUSTOMERS WITH SMART METERS BY FEEDER CLASSIFICATION/EQUIPMENT TYPE
| FEEDER CLASSIFICATION | Units | as at 30 June - end of year
| CBD | Number of customers | 0
| Urban | Number of customers | 119220
| Short rural | Number of customers | 18130
| Long rural | Number of customers | 0
EQUIPMENT TYPE
| Customers with solar PV only | Number of customers | 133030
| Customers with batteries | Number of customers | 142
| Customers with solar PV and batteries | Number of customers | 4178
| Customers without solar PV or batteries | Number of customers | 0
| Total customers (export services) | Number of customers | 137350
DC04 - Customer numbers ¦Export services
Export customers without smart meters
3.9.5.2 - EXPORTING CUSTOMERS WITHOUT SMART METERS BY FEEDER CLASSIFICATION/EQUIPMENT TYPE
| FEEDER CLASSIFICATION | Units | as at 30 June - end of year
| CBD | Number of customers | 0
| Urban | Number of customers | 121
| Short rural | Number of customers | 15
| Long rural | Number of customers | 0
EQUIPMENT TYPE
| Customers with solar PV only | Number of customers | 136
| Customers with batteries | Number of customers | 0
| Customers with solar PV and batteries | Number of customers | 0
| Customers without solar PV or batteries | Number of customers | 0
| Total customers (export services) without smart meters | Number of customers | 136
DC04 - Customer numbers ¦Export services
Export customers with static zero export limits
3.9.5.3 - EXPORTING CUSTOMERS WITH STATIC ZERO LIMITS BY FEEDER CLASSIFICATION/EXPORT SERVICE TYPE
| FEEDER CLASSIFICATION | Units | as at 30 June - end of year
| CBD | Number of customers | 0
| Urban | Number of customers | 223
| Short rural | Number of customers | 60
| Long rural | Number of customers | 0
CUSTOMER (EXPORT SERVICES) TYPE
| Total customers with static zero exports | Number of customers | 283
| Residential | Number of customers | 263
| Non residential HV | Number of customers | 2
| Non residential LV | Number of customers | 18
| Low voltage small business | Number of customers | 13
| Low voltage non residential (excluding small business) | Number of customers | 5
DC04 - Customer numbers ¦Export services
Export customers with static non-zero export limits
3.9.5.4 - EXPORTING CUSTOMERS WITH STATIC NON-ZERO LIMITS BY FEEDER CLASSIFICATION/EXPORT SERVICE TYPE
| FEEDER CLASSIFICATION | Units | as at 30 June - end of year
| CBD | Number of customers | 0
| Urban | Number of customers | 114164
| Short rural | Number of customers | 17217
| Long rural | Number of customers | 0
CUSTOMER (EXPORT SERVICES) TYPE
| Total customers with static zero exports | Number of customers | 131381
| Residential | Number of customers | 125166
| Non residential HV | Number of customers | 11
| Non residential LV | Number of customers | 6204
| Low voltage small business | Number of customers | 4379
| Low voltage non residential (excluding small business) | Number of customers | 1825
DC04 - Customer numbers ¦Export services
Customers (export services) requesting export capacity
3.9.5.5 - EXPORTING CUSTOMERS REQUESTING CAPACITY BY FEEDER CLASSIFICATION/EXPORT SERVICE TYPE
| FEEDER CLASSIFICATION | Units | as at 30 June - end of year
| CBD | Number of customers | 0
| Urban | Number of customers | 6481
| Short rural | Number of customers | 798
| Long rural | Number of customers | 0
CUSTOMER (EXPORT SERVICES) TYPE
| Total customers requesting export capacity | Number of customers | 7279
| Residential | Number of customers | 6850
| Non residential HV | Number of customers | 3
| Non residential LV | Number of customers | 426
| Low voltage small business | Number of customers | 271
| Low voltage non residential (excluding small business) | Number of customers | 155
DC04 - Customer numbers ¦Export services
Export customers with flexible export limits
3.9.5.6 - EXPORTING CUSTOMERS WITH FLEXIBLE LIMITS BY FEEDER CLASSIFICATION/EXPORT SERVICE TYPE
| FEEDER CLASSIFICATION | Units | as at 30 June - end of year
| CBD | Number of customers | 0
| Urban | Number of customers | 0
| Short rural | Number of customers | 0
| Long rural | Number of customers | 0
CUSTOMER (EXPORT SERVICES) TYPE
| Total customers with flexible export limits | Number of customers | 0
| Residential | Number of customers | 0
| Non residential HV | Number of customers | 0
| Non residential LV | Number of customers | 0
| Low voltage small business | Number of customers | 0
| Low voltage non residential (excluding small business) | Number of customers | 0
| CUSTOMERS ON ISOLATED NETWORKS | Number of customers | 0
DC04 - Customer numbers ¦Export services
Customers (export services) with measured voltage data
3.9.5.7 - EXPORTING CUSTOMERS WITH MEASURED VOLTAGE DATA BY FEEDER CLASSIFICATION/EXPORT SERVICE TYPE
| FEEDER CLASSIFICATION | Units | as at 30 June - end of year
| CBD | Number of customers | 0
| Urban | Number of customers | 118238
| Short rural | Number of customers | 18020
| Long rural | Number of customers | 0
CUSTOMER (EXPORT SERVICES) TYPE
| Total customers with measured voltage data | Number of customers | 136258
| Residential | Number of customers | 131953
| Non residential HV | Number of customers | 141
| Non residential LV | Number of customers | 4164
| Low voltage small business | Number of customers | 4164
| Low voltage non residential (excluding small business) | Number of customers | 0
DC04 - Customer numbers ¦Export services
Customers (export services) measured as experiencing overvoltage
3.9.5.8 - EXPORTING CUSTOMERS WITH MEASURED OVERVOLTAGE BY FEEDER CLASSIFICATION/EXPORT SERVICE TYPE
| FEEDER CLASSIFICATION | Units | as at 30 June - end of year
| CBD | Number of customers | 0
| Urban | Number of customers | 3112
| Short rural | Number of customers | 312
| Long rural | Number of customers | 0
CUSTOMER (EXPORT SERVICES) TYPE
| Total customers with measured voltage data | Number of customers | 3424
| Residential | Number of customers | 3134
| Non residential HV | Number of customers | 0
| Non residential LV | Number of customers | 290
| Low voltage small business | Number of customers | 271
| Low voltage non residential (excluding small business) | Number of customers | 19
DC04 - Customer numbers ¦Export services
Customers (export services) estimated to have experienced overvoltage
3.9.5.9 - EXPORTING CUSTOMERS ESTIMATED WITH OVERVOLTAGE BY FEEDER CLASSIFICATION/EXPORT SERVICE TYPE
| FEEDER CLASSIFICATION | Units | as at 30 June - end of year
| CBD | Number of customers | 0
| Urban | Number of customers | 3251
| Short rural | Number of customers | 328
| Long rural | Number of customers | 0
CUSTOMER (EXPORT SERVICES) TYPE
| Total customers with measured voltage data | Number of customers | 3579
| Residential | Number of customers | 3186
| Non residential HV | Number of customers | 0
| Non residential LV | Number of customers | 393
| Low voltage small business | Number of customers | 322
| Low voltage non residential (excluding small business) | Number of customers | 71
DC04 - Customer numbers ¦Export services
Measures relating to AS4777.2 (2020) compliant inverters
3.9.6 - AS4777.2 MEASURES - COMPLIANT INVERTERS
|  | Units | as at 30 June - end of year
| Total export customers required to have AS4777.2 (2020) compliant inverters | Number of customers | 41479
| Total export customers not required to have AS4777.2 (2020) compliant inverters | Number of customers | 97814
| Estimated proportion of customers (export services) required to be compliant with AS4777.2 (2020) that are non-compliant | % | 20.79%
DC05 - Service performance ¦Export services
Average duration of full export access against the agreed limit
3.9.7.1 - AVERAGE DURATION OF FULL EXPORT TO AGREED LIMIT BY CUSTOMER (EXPORT SERVICES) TYPE
| SOLAR PV ONLY | Units | Service performance
| Residential | hh:mm | 8539:33
| Non residential HV | hh:mm | 8760:00
| Non residential LV | hh:mm | 8498:41
| Low voltage small business | hh:mm | 8510:14
| Low voltage non residential (excluding small business) | hh:mm | 8487:08
SOLAR PV AND BATTERY
| Residential | hh:mm | 8145:27
| Non residential HV | hh:mm | 8760:00
| Non residential LV | hh:mm | 7892:51
| Low voltage small business | hh:mm | 7974:36
| Low voltage non residential (excluding small business) | hh:mm | 7811:07
BATTERY ONLY
| Residential | hh:mm | 8735:60
| Non residential HV | hh:mm | NULL
| Non residential LV | hh:mm | 8760:00
| Low voltage small business | hh:mm | 8760:00
| Low voltage non residential (excluding small business) | hh:mm | NULL
DC05 - Service performance ¦Export services
Average duration of no export access
3.9.7.2 - AVERAGE DURATION OF NO EXPORT ACCESS BY CUSTOMER (EXPORT SERVICES) TYPE
| SOLAR PV ONLY | Units | Service performance
| Residential | hh:mm | 36:11
| Non residential HV | hh:mm | 4672:00
| Non residential LV | hh:mm | 152:41
| Low voltage small business | hh:mm | 121:06
| Low voltage non residential (excluding small business) | hh:mm | 184:16
SOLAR PV AND BATTERY
| Residential | hh:mm | 107:20
| Non residential HV | hh:mm | 0:00
| Non residential LV | hh:mm | 199:38
| Low voltage small business | hh:mm | 230:31
| Low voltage non residential (excluding small business) | hh:mm | 168:45
BATTERY ONLY
| Residential | hh:mm | 0:04
| Non residential HV | hh:mm | NULL
| Non residential LV | hh:mm | 0:00
| Low voltage small business | hh:mm | 0:00
| Low voltage non residential (excluding small business) | hh:mm | NULL
DC05 - Service performance ¦Export services
Average upper limit - customers with flexible export limits
3.9.7.3 - AVERAGE UPPER LIMIT - CUSTOMERS WITH FLEXIBLE LIMITS BY FEEDER CLASSIFICATION/EXPORT SERVICE TYPE
| FEEDER CLASSIFICATION | Units | Service performance
| CBD | kW | 0
| Urban | kW | 0
| Short rural | kW | 0
| Long rural | kW | 0
CUSTOMER (EXPORT SERVICES) TYPE
| Average flexible export upper limit | kW
| Residential | kW | 0
| Non residential HV | kW | 0
| Non residential LV | kW | 0
| Low voltage small business | kW | 0
| Low voltage non residential (excluding small business) | kW | 0
| CUSTOMERS ON ISOLATED NETWORKS | kW | 0
DC05 - Service performance ¦Export services
Average time upper limit unavailable - customers with flexible export limits
3.9.7.4 - AVERAGE TIME UPPER LIMIT UNAVAILABLE TO CUSTOMERS WITH FLEXIBLE LIMITS BY FEEDER CLASSIFICATION/EXPORT SERVICE TYPE
| FEEDER CLASSIFICATION | Units | Service performance
| CBD | hh:mm | NULL
| Urban | hh:mm | NULL
| Short rural | hh:mm | NULL
| Long rural | hh:mm | NULL
CUSTOMER (EXPORT SERVICES) TYPE
| Average time the flexible export upper limit was unavailable | hh:mm
| Residential | hh:mm | NULL
| Non residential HV | hh:mm | NULL
| Non residential LV | hh:mm | NULL
| Low voltage small business | hh:mm | NULL
| Low voltage non residential (excluding small business) | hh:mm | NULL
| CUSTOMERS ON ISOLATED NETWORKS | hh:mm | NULL
DC05 - Service performance ¦Export services
Export limit compliance
3.9.8.1 - EXPORT LIMIT COMPLIANCE
|  | Units | Service performance
| Compliance with static export limits | % | 20.63%
| Compliance with flexible export limits | % | 0%
DC05 - Service performance ¦Export services
Complaints relating to export services
3.9.8.2 - EXPORT SERVICE COMPLAINTS BY FEEDER CLASSIFICATION/EXPORT SERVICE TYPE
| FEEDER CLASSIFICATION | Units | Service performance
| CBD | Number of complaints | 0
| Urban | Number of complaints | 20
| Short rural | Number of complaints | 2
| Long rural | Number of complaints | 0
CUSTOMER (EXPORT SERVICES) TYPE
| Total complaints | Number of complaints | 22
| Residential | Number of complaints | 20
| Non residential HV | Number of complaints | 0
| Non residential LV | Number of complaints | 2
| Low voltage small business | Number of complaints | 2
| Low voltage non residential (excluding small business) | Number of complaints | 0
DC05 - Service performance ¦Export services
Complaints relating to overvoltage
3.9.8.3 - OVERVOLTAGE COMPLAINTS BY FEEDER CLASSIFICATION/EXPORT SERVICE TYPE
| FEEDER CLASSIFICATION | Units | Service performance
| CBD | Number of complaints | 0
| Urban | Number of complaints | 25
| Short rural | Number of complaints | 3
| Long rural | Number of complaints | 0
CUSTOMER (EXPORT SERVICES) TYPE
| Total complaints relating to overvoltage | Number of complaints | 28
| Residential | Number of complaints | 25
| Non residential HV | Number of complaints | 0
| Non residential LV | Number of complaints | 3
| Low voltage small business | Number of complaints | 2
| Low voltage non residential (excluding small business) | Number of complaints | 1
DC05 - Service performance ¦Export services
Average time to provide an offer
3.9.9 - AVERAGE TIME OF OFFER
| AVERAGE TIME TO PROVIDE AN OFFER TO CONNECT SMALL GENERATING UNITS TO THE DISTRIBUTION NETWORK | Units | Service performance
| Model standing offer or equivalent | Days | 0
| Low voltage connections outside model standing offers | Days | 11
| High voltage connections | Days | 38
DC06 - Operating expenditure ¦ Export services
Opex for provision of export services
3.9.10 - EXPORT SERVICES OPEX
|  | Units | Total Standard Control Services
| Overvoltage complaint management | $ | 45150.07
| Other export services opex | $ | 0
DC07 - Capital expenditure ¦ Export services
Capex for provision of export services
3.9.11 - EXPORT SERVICES CAPEX
| CAPEX FOR PROVISION OF EXPORT SERVICES | Units | Total Standard Control Services
| ICT capex | $ | 7076848.07
| Recurrent expenditure | $ | 0
| <DNSP specified> | $
$
$
| Non-recurrent expenditure | $ | 7076848.07
| UE NAP Technology Transition | $ | 975080.24
| UE Network Data Platform | $ | 1258428.61
| LV DERMS Phase 1 | $ | 3404626.5
| Energy Workbench for UE | $ | 1438712.72
| Network monitoring capex | $ | 0
| Other export services capex | $ | 0
| Capex for provision of export services | $ | 7076848.07

## 7.5 Large projects
| ANNUAL INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| 7.5 LARGE PROJECTS |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC06 - Operating expenditure ¦ Large projects
DC07 - Capital expenditure ¦ Large projects
Large project expenditure
7.5.1 - LARGE PROJECT EXPENDITURE
Large project expenditure
Standard control services (Total expenditure)
| PROJECT NAME/ID | Units | Operating Expenditure | Capital Expenditure
| <DNSP specified> | $ | 0
$
$
| Total | $ | 0 | 0

## 8.6 Ind Asset Base Roll Fwd
| ANNUAL INFORMATION ORDER |  |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  |  | 12.5% Grey | Amended
| 8.6 INDICATIVE ASSET BASE ROLL FORWARD |  |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC08 - Asset base values ¦ standard control
Asset base roll forward
8.6.1 ASSET BASE ROLL FORWARD - SCS
Standard control services
| INDICATIVE TOTAL REGULATORY ASSET BASE ROLL FORWARD (WITHIN PERIOD) | Units | Excluding dual function assets | Dual function assets
| Opening value | $ | 2769371939
| Inflation addition | $ | 112214612
| Forecast straight line depreciation | $ | 198849563
| Gross capex | $ | 302842659
| Capital contributions included in gross capex | $ | 89899368
| Disposals | $ | 260456
| Capex timing adjustment | $ | 7138338
| Closing value | $ | 2902558161 | 0
INDICATIVE TOTAL TAX ASSET BASE ROLL FORWARD (WITHIN PERIOD)
| Opening value | $ | 2222088673
| Actual tax depreciation | $ | 173044908
| Gross capex | $ | 302842659
| Disposals | $ | 260456
| Closing value | $ | 2351625968 | 0
DC08 - Asset base values ¦ Alternative control
Asset base roll forward
8.6.2 ASSET BASE ROLL FORWARD - ACS
| INDICATIVE METERING ASSET BASE ROLL FORWARD (WITHIN PERIOD) | Units | Alternative Control Services
| Opening Value | $ | 107455539
| Inflation addition | $ | 4354085
| Forecast straight line depreciation | $
| Actual straight line depreciation | $ | 20623482
| Gross capex | $ | 5656745
| Capital contributions included in gross capex | $ | 0
| Disposals | $ | 0
| Capex timing adjustment | $ | 189859
| Closing Value | $ | 97032746
INDICATIVE PUBLIC LIGHTING ASSET BASE ROLL FORWARD (WITHIN PERIOD)
| Opening Value | $ | 28536432
| Inflation addition | $ | 0
| Forecast straight line depreciation | $
| Actual straight line depreciation | $ | 1818715
| Gross capex | $ | 7810582
| Capital contributions included in gross capex | $ | 1831535
| Disposals | $ | 0
| Capex timing adjustment | $ | 0
| Closing Value | $ | 32696764

## 8.7 Profitability - tax data
| ANNUAL INFORMATION ORDER |  |  | #25C6FF | Protected (SOCI)
| United Energy |  |  | #FFCCCC | Confidential
| REPORTING STATEMENT: 2024-25 |  |  | 12.5% Grey | Amended
| Financial performance information request - 8.7 PROFITABILITY TAX DATA |  |  | #FFCCCC & 12.5% Grey | Amended Confidential
DC09 - Revenue and financial statements ¦ Standard control
Profitability - tax data
8.7.1 - PROFITABILITY TAX DATA
| OWNERSHIP STRUCTURE | Units | Standard Control Services
| Ownership Structure | text | Private sector entity which is taxed as a company
| Proportion of holding interest in flow-through vehicle attributable to a NTER or government owned non-NTER entity | % | 0%
| Tax rate applicable to holding interest attributable to a NTER or government-owned non-NTER entity | % | 0%
| Proportion of holding interest in flow-through vehicle not attributable to a NTER or government owned non-NTER entity | % | 0%
| Tax rate applicable to holding interest not attributable to a NTER or government owned non-NTER entity | % | 0%
| Flow-though blended tax rate | % | 0%
TAX RELATED INFORMATION
| Tax asset base depreciation | $ | 178439064
| Tax rate | % | 30%
Taxable income adjustments
| Tax loss carried forward | $ | 0
| Total taxable revenue and/or income for customer contributions and/or gifted assets | $ | 101561307
| Permanent differences due to disallowed interest expense | $ | 3772150
| Permanent differences due to adjustments to prior year returns | $ | -384000
INTEREST EXPENSE
Debt and Equity
| Interest bearing liabilities | $ | 1782188144
| Related party interest expense | $ | 20858941
| Interest expense | $ | 63272880

## NSP additional information
This sheet may be used to identify amendments made to data resubmitted to the AER. It may also be used to provide additional information not captured in this workbook.
NSP data amendments
Worksheet | Table | Comments