## Changes summary
Data category 03: Network metrics
Changes from December 2023 Consultation workbooks
Data requirements
Worksheet | Table | Change | Rationale
Checks and Totals |  | The following checks and Totals were removed: Overhead network length of circuit at each voltage = Overhead conductors by feeder type Overhead network length of circuit at each voltage = Overhead conductors by material type Underground cable network length of circuit at each voltage = Underground cables by cable length by feeder type | Conductor length is reported based on the length of all the conductors, for example the three lines of conductor will be reported for a three-phase circuit. Therefore, these lengths will not reconcile as provided within the Checks and Totals.
Network Assets - Volume | Total poles by feeder type | New row added "Feeders other" | To allow for reconciliation between data reporting requirements (Total poles by feeder type and Asset age profile) where subtransmission/transmission feeders are not assigned a feeder category.
Definitions |  | Definition added "Feeders other" | New data item referred to in workbooks.

## Introduction
AER Network information requirements review
Project Overview
The network information requirements review project is being undertaken to streamline regulated electricity networks' annual reporting obligations, and facilitate improvements in the AER’s information management maturity. The project will allow for consolidation of existing information requests, ongoing integration of new information requirements, and clearer documentation of our underlying data structure. In sum, this project will help improve data quality and deliver efficiencies to both the AER and the regulated businesses.
Data category 03: Network metrics
Network metrics describe the physical characteristics of the network, including the volume, capacity, location and age of assets, and information about the environment in which the network operates.
Network metrics data used to assess expenditure forecasts, and inform specific analysis (such as benchmarking analysis). It also provides insights to the operating environment of the network, that may impact the operational and investment decisions of the network business.
This workbook defines the data requirements related to network metrics. Requirements are set out in tables on each worksheet, and are defined by multiple elements of the workbook including: - worksheet name - table and sub-table names - column headings and - row descriptors. The workbook also includes validation rules for input cells (shaded green), cross checks where disaggregated data must equal the same total and definitions of the terms used.

## Definitions
Data category 03: Network metrics
Definitions have been provided for each column descriptor as well as each row descriptor of the data tabs in this workbook. To find the full meaning of a data element, please consider all relevant column, row and table heading definitions provided in the table below.
Compounding Definitions
Where you are seeking to discern the meaning of a row or column descriptor with multiple terms, you may need to look up the terms individually below and consider the definitions together to discern the full meaning of the row or column descriptor.
Term | Definition
Network assets - public lighting
Public lighting - light type | A description/name/identifier for the lights (lamps) used to deliver public lighting services.
Business specified tariff category | Tariff category used to charge for public lighting services.
Public lighting services | The installation, operation, repair, replacement and maintenance of public lighting assets whether owned by the NSP or by another party. This also includes alteration and relocation of existing public lighting assets.
Public lighting assets | Include luminaires, brackets, lamps and dedicated public lighting poles (not poles that deliver network services).
Luminaire | A complete electric light unit.
Network assets - meter population
Current transformer connected meter | A meter installed on a connection with a load greater than 100 Amps. They measure a fraction of the amps (current) passing through the connection and a multiplier is applied to this reading to reflect the actual amps.
Direct connect meter | A meter connected to the network without current or voltage transformers.
Meter | A meter is a device complying with Australian Standards which measures and records the production or consumption of electrical energy. Meter types 1-7 must be consistent with the requirements in Schedule 7.4 of NER.
Meter type 1-3 | High voltage meter.
Meter type 4 | Remotely read interval meter with communications functionality. It must meet the minimum services specification for type 4 meters set out in schedule 7.5 of the NER.
Meter type 5 | Manually read interval meter that records interval energy data, which is not a remotely read interval meter.
Meter type 6 | Manually read accumulation meter.
Multi phase meter | A meter used at a multi phase connection, where electricity is supplied through more than one conductor.
Single phase meter | A meter used at a single phase connection, where electricity is supplied through a single conductor.
Network assets - poles by feeder type
CBD feeder | A feeder in the CBD area of State or Territory capital that has been determined by the relevant participating jurisdiction as supplying electricity to predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas.
Urban feeder | Has the meaning as defined in the STPIS scheme and Distribution Reliability Measures Guideline.
Long rural feeder | A feeder with a total feeder route length greater than 200 km, which is not a CBD feeder or urban feeder.
Short rural feeder | A feeder with a total feeder route length less than 200 km, which is not a CBD feeder or urban feeder.
TAS - Critical Infrastructure | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - High density commercial | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - High density rural | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - Low density rural | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - Urban | Consistent with the requirements of the Tasmanian Electricity Code.
Feeders other | Feeders that are subtransmission or transmission feeders that can not be assigned to the distribution feeder categories (CBD, Urban, Short rural and Long rural).
Non-network assets
Car | Cars are motor vehicles other than those that comply with the definition of Light commercial vehicle, Heavy commercial vehicle, Elevated work platform (LCV), or Elevated work platform (HCV).
Device | Hardware devices that access services made available by a server. May include desktop computers, laptops, tablets and thin client interfaces and handheld end user computing devices including smart phones, tablets and laptops.
Elevated work platform (HCV) | Motor Vehicles that have permanently attached elevating work platforms that would be HCVs but for the exclusion of elevated work platforms from the definition of HCV.
Elevated work platform (LCV) | (LCV) are Motor Vehicles that have permanently attached elevating work platforms that are not Elevated work platforms (HCV).
Heavy Commercial Vehicle | Heavy commercial vehicles (HCVs) are Motor Vehicles that are registered for use on public roads excluding Elevated Work Platform (HCV)s that: have a gross vehicle mass greater than 4.5 tonnes; or are articulated Vehicles; or are buses with a gross vehicle mass exceeding 4.5 tonnes.
Light commercial vehicle | Motor Vehicles that are registered for use on public roads excluding elevated work platforms that: are rigid trucks or load carrying vans or utilities having a gross vehicle mass greater than 1.5 tonnes but not exceeding 4.5 tonnes; or have cab-chassis construction, and a gross vehicle mass greater than 1.5 tonnes but not exceeding 4.5 tonnes; or are buses with a gross vehicle mass not exceeding 4.5 tonnes.
Motor vehicle | Any motor vehicle registered for use on public roads excluding motor vehicles not generally moved large distances on public roads under their own power (e.g. excluding tractors, forklifts, backhoes, bobcats and any other road registered mobile plant).
Length
Circuit length | Circuit length is calculated from the route length (measured in kilometres) of lines in service (the total length of feeders including all spurs), where each SWER line, single-phase line, and three-phase line counts as one line. A double circuit line counts as twice the length. The length does not take into account vertical components such as sag.
Overhead conductor | Overhead conductor / line Assets located above ground used for the primary function of transmitting power in a transmission network or distributing power in a distribution network. Excludes assets that are included in any other asset category or asset group.
Underground asset (cable) | An asset with the primary function of distributing power, below ground. This includes cables, cable joints and other assets used to connect the underground network to the overhead system. It excludes any pole mounted assets that are included in any other asset group. This does not include underground substations and transformers.
CBD feeder | A feeder in the CBD area of State or Territory capital that has been determined by the relevant participating jurisdiction as supplying electricity to predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas.
Urban feeder | Has the meaning as defined in the STPIS scheme and Distribution Reliability Measures Guideline.
Long rural feeder | A feeder with a total feeder route length greater than 200 km, which is not a CBD feeder or urban feeder.
Short rural feeder | A feeder with a total feeder route length less than 200 km, which is not a CBD feeder or urban feeder.
TAS - Critical Infrastructure | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - High density commercial | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - High density rural | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - Low density rural | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - Urban | Consistent with the requirements of the Tasmanian Electricity Code.
Feeders other | Feeders that are subtransmission or transmission feeders that can not be assigned to the distribution feeder categories (CBD, Urban, Short rural and Long rural).
Feeder ID | The unique code or feeder identifier that the NSP uses internally to identify the feeder.
Feeder service area description | A description of the location of the feeder.
Feeder classification | Classification of feeder based on location on network or type of load served (network type as defined in the STPIS). Non Tasmanian feeder classifications are: CBD, Urban; Short rural and Long Rural. Tasmanian feeder classifications are consistent with the requirements of the Tasmanian Electricity Code: Critical infrastructure; Urban; High density commercial, High density rural and Low density rural.
Asset replacement | The replacement of an asset with its modern equivalent where the asset has reached the end of its economic life.
Capacity
Circuit capacity | The maximum apparent power (MVA).
Cold spare capacity | The capacity of spare transformers owned by NSP but not currently in use. Cold Spare Capacity incorporates both spare capacity and cold capacity. Cold capacity is equipment which is already on site, with connections already in place so that the device can be brought into service merely by switching operations but which is not normally load carrying. Spare capacity also includes spare assets, on site, or in the store, where physical movement and / or making of connections would require manual intervention at the site of use.
Distribution other - transformer capacity owned by utility | Transformer capacity not reported as distribution transformer capacity or zone substation transformer capacity.
Distribution transformer total installed capacity | The transformer capacity involved in the final level of transformation, stepping down the voltage used in the distribution lines to the level used by the customer. It does not include intermediate transformation capacity (e.g. 132 kV or 66 kV to the 22 kV or 11 kV distribution level). The capacity measure is the normal nameplate continuous capacity / rating (including forced cooling and other factors used to improve capacity). This measure includes Cold Spare Capacity of Distribution Transformers and excludes the capacity of all zone substation transformers, voltage transformers (potential transformers) and current transformers.
Estimated overhead network weighted average MVA capacity by voltage class | For overhead network, estimated typical or weighted average capacities for each of the listed voltage classes under normal circumstances taking account of limits imposed by thermal or by voltage drop considerations as relevant.
Estimated underground network weighted average MVA capacity by voltage class | For underground network, estimated typical or weighted average capacities for each of the listed voltage classes under normal circumstances taking account of limits imposed by thermal or by voltage drop considerations as relevant.
Overhead conductor | Overhead conductor / line Assets located above ground used for the primary function of transmitting power in a transmission network or distributing power in a distribution network. Excludes assets that are included in any other asset category or asset group.
Total installed capacity for second step transformation where there are two steps to reach distribution voltage | Where a second step transformation is applied before reaching the distribution voltage. For example 66 kV or 33 kV to 22 kV or 11 kV where there has already been a step of transformation above this at higher voltages within DNSP’s system.
Total installed capacity for first step transformation where there are two steps to reach distribution voltage | Includes, for example, 66 kV or 33 kV to 22 kV or 11 kV where there will be a second step transformation before reaching the distribution voltage.
Total zone substation transformer capacity where there is only a single step transformation to reach distribution voltage | Where only a single step of transformation is applied before reaching the distribution voltage. This variable is only relevant where there is only a single step of transformation to reach distribution voltage.
Transformer | Assets used to transform voltage levels within the network. This includes all its components such as the cooling systems and tap changing equipment (where installed). It excludes any pole mounted assets that are included in any other asset category. For the avoidance of doubt, this does not include instrument transformers as defined in the National Electricity Rules. It also does not include auxiliary transformers.
Underground asset (cable) | An asset with the primary function of distributing power, below ground. This includes cables, cable joints and other assets used to connect the underground network to the overhead system. It excludes any pole mounted assets that are included in any other asset group. This does not include underground substations and transformers.
Zone substation | A substation on a distribution network that transforms any voltage above 33 kV to levels at or below 33 kV but above 1 kV. As a guide, assets included within a zone substation include all equipment, buildings, structures, civil works and other assets that are located permanently within the substation boundary fence; but excluding the landing spans of incoming or outgoing overhead lines, and excluding incoming or outgoing cables and associated cable terminations (cables includes all power, communications and control cables).
Assets decommissioned | The removal of the asset from service.
Asset age profile
Pole | Vertically oriented assets that provide load bearing structural support for overhead conductors or other lines assets. This also includes associated pole top structures, such as cross-arms and insulators where these are replaced in conjunction with a pole replacement project. It excludes other pole mounted assets that are included in any other asset group, notably pole mounted substations and pole mounted switchgear such as links, fuses, air break switches etc.
Composite pole | A pole developed using a combination of materials, such as timber and concrete.
Pole - other technology | Stobie poles, or poles made of materials not included elsewhere in the asset category.
Staking of /staked wooden pole | A wooden pole that is staked; or the activity of staking a wooden pole.
Overhead conductor | Overhead conductor / line Assets located above ground used for the primary function of transmitting power in a transmission network or distributing power in a distribution network. Excludes assets that are included in any other asset category or asset group.
Underground asset (cable) | An asset with the primary function of distributing power, below ground. This includes cables, cable joints and other assets used to connect the underground network to the overhead system. It excludes any pole mounted assets that are included in any other asset group. This does not include underground substations and transformers.
Service lines | Includes assets that provide a physical link and associated assets between the distribution network and a customer’s premises. It excludes any pole mounted assets and meters that are included in any other asset group.
Residential connection | Work connecting any customer who purchases energy principally for personal, household or domestic use at premises.
Commercial/industrial connection | Work connecting any customer who is not a residential or unmetered customer.
Subdivision connection | Work connecting un-reticulated lots or areas to the distribution network for residential subdivisions.
Transformer | Assets used to transform voltage levels within the network. This includes all its components such as the cooling systems and tap changing equipment (where installed). It excludes any pole mounted assets that are included in any other asset category. For the avoidance of doubt, this does not include instrument transformers as defined in the National Electricity Rules. It also does not include auxiliary transformers.
Switchgear | These are assets used to control, protect and isolate segments of the network. This includes disconnect switches, fuses, circuit breakers, links, reclosers, sectionalisers, ring main units, oil insulated fuses etc. It excludes any pole mounted assets that are included in any other asset category.
Public lighting assets | Include luminaires, brackets, lamps and dedicated public lighting poles (not poles that deliver network services).
Luminaire | A complete electric light unit.
Major road | Road on which the visual requirements of motorists are dominant (e.g. traffic routes). Typically the responsibility of a state or territory road authority.
Minor road | Road on which the visual requirements of pedestrians are dominant (e.g. local roads and lighting that is applicable to areas other than roads outdoor public areas, e.g. outdoor shopping). Typically the responsibility of a local Government authority.
Pole | Vertically oriented assets that provide load bearing structural support for overhead conductors or other lines assets. This also includes associated pole top structures, such as cross-arms and insulators where these are replaced in conjunction with a pole replacement project. It excludes other pole mounted assets that are included in any other asset group, notably pole mounted substations and pole mounted switchgear such as links, fuses, air break switches etc.
Column | A vertical structure of any appropriate material, which, is designed to support luminaires either directly or by use of outreach arms or mounting frames.
SCADA and network control and protection systems | SCADA and network control hardware, software and associated IT systems. Includes protection and control systems and communication systems. Excludes SCADA and Network Control systems that exist within gateway devices (routers, bridges etc.) at corporate offices. Protection systems has the meaning prescribed in the National Electricity Rules.
Installed assets - quantity currently in commission by year | The number of assets currently in commission and the year they were installed.
Asset metrics - asset lives
Alternative Control Services | A distribution service that is a direct control service but not a standard control service (as defined in the NER). By way of context, Alternative Control Services are intended to capture distribution services provided at the request of, or for the benefit of, specific customers with regulatory oversight of prices.
Standard Control Services | As defined in the National Electricity Rules. For clarity, Standard Control Services are intended to capture services available only through DNSP’s network typically provided to all customers or a broad class of customers recovered through general network tariffs.
Network services | Services provided over the shared network used to service all network users connected to it. Such services may include the construction, maintenance, operation, planning and design of the shared network. Network Services are delivered through the provision and operation of apparatus, equipment, plant and/or buildings (excluding connection assets) used to convey, and control the conveyance of, electricity to customers. Network Services also include the provision of emergency response and administrative support for other Network Services. Network Services are a subset of Standard Control Services that excludes Connection Services, Metering services, Fee Based and Quoted Services and Public Lighting Services. The Opex and capex of connection assets that become part of the shared network are part of Network Services. This only applies to the Opex and capex for connection assets subsequent to their installation and excludes Opex and capex associated with the provision of Connection Services. For the avoidance of doubt, Network Services includes the construction, maintenance, operation, planning and design of Dual Function Assets where these assets are part of the shared network.
Distribution substation | A substation on a distribution network that transforms voltage of levels at or below 33 kV but above 1 kV to levels below 1 kV. As a guide, assets included within a distribution substation include all equipment permanently installed within the distribution substation boundary. Where applicable (such as indoor and outdoor substations), this includes any enclosures, structures, civil works, poles and associated hardware, cabling and other assets that are located permanently within the distribution substation boundary, but excludes any incoming or outgoing lines or cables. For the avoidance of doubt this does not include any building, structure, equipment, cabling, etc. located within the substation boundary that is the property or responsibility of third parties. Where applicable (such as for pole mounted substations), this also includes any poles, pole hardware, pole structures, links, surge diverters, fuses or protective devices, cabling and other assets forming part of the substation or its supports, but excluding incoming or outgoing overhead mains, cables and associated cable terminations (cables in this context includes all power, communications and control cables).
Estimated service life of new assets | The expected service life of new assets is the estimated period after installation of a new asset during which the asset will be capable of delivering the same effective service as it could at its installation date.
Other assets with long lives | Assets with expected asset lives greater than or equal to 10 years that are not: (a) Overhead Assets (b) Underground Assets (c) Substations, switchyards and transformer (d) Zone Substations And Transformers (e) Easements (f) Meters Note: For transmission, assets must be used for provision of Prescribed Transmission Services only. Includes secondary substation equipment (protection, telecommunication and control systems) where these assets have lives of ten years or greater.
Other assets with short lives | Assets with expected asset lives less than 10 years that are not: (a) Overhead Assets (b) Underground Assets (c) Substations, switchyards and transformer (d) Zone Substations And Transformers (e) Easements (f) Meters Note: For transmission, assets must be used for provision of Prescribed Transmission Services only. Includes secondary substation equipment (protection, telecommunication and control systems) where these assets have lives less than 10 years.
Overhead network assets | Assets used to conduct electricity from one point to another above ground. These include poles, pole-top structures and overhead conductors. This does not include pole top substations and transformers.
Transformer | Assets used to transform voltage levels within the network. This includes all its components such as the cooling systems and tap changing equipment (where installed). It excludes any pole mounted assets that are included in any other asset category. For the avoidance of doubt, this does not include instrument transformers as defined in the National Electricity Rules. It also does not include auxiliary transformers.
Underground asset (cable) | An asset with the primary function of distributing power, below ground. This includes cables, cable joints and other assets used to connect the underground network to the overhead system. It excludes any pole mounted assets that are included in any other asset group. This does not include underground substations and transformers.
Zone substation | A substation on a distribution network that transforms any voltage above 33 kV to levels at or below 33 kV but above 1 kV. As a guide, assets included within a zone substation include all equipment, buildings, structures, civil works and other assets that are located permanently within the substation boundary fence; but excluding the landing spans of incoming or outgoing overhead lines, and excluding incoming or outgoing cables and associated cable terminations (cables includes all power, communications and control cables).
Meter | A meter is a device complying with Australian Standards which measures and records the production or consumption of electrical energy. Meter types 1-7 must be consistent with the requirements in Schedule 7.4 of NER.
Estimated residual service life | The remaining time an asset class is expected to deliver the same effective service as that asset class did at its installation date.
Asset metrics - inspection and maintenance cycles
Pole top structure | These are horizontally oriented structures and their components that provide support for overhead conductors and related assets to be supported on a pole and provide adequate clearances. A pole top structure is independently of the pole it is located on. This includes cross-arms and insulators. It excludes any pole mounted assets that are included in any other asset group, notably pole mounted substations and pole mounted switchgear such as links, fuses, air break switches etc.
Pole | Vertically oriented assets that provide load bearing structural support for overhead conductors or other lines assets. This also includes associated pole top structures, such as cross-arms and insulators where these are replaced in conjunction with a pole replacement project. It excludes other pole mounted assets that are included in any other asset group, notably pole mounted substations and pole mounted switchgear such as links, fuses, air break switches etc.
Staking of /staked wooden pole | A wooden pole that is staked; or the activity of staking a wooden pole.
Overhead conductor | Overhead conductor / line Assets located above ground used for the primary function of transmitting power in a transmission network or distributing power in a distribution network. Excludes assets that are included in any other asset category or asset group.
Underground asset (cable) | An asset with the primary function of distributing power, below ground. This includes cables, cable joints and other assets used to connect the underground network to the overhead system. It excludes any pole mounted assets that are included in any other asset group. This does not include underground substations and transformers.
Service lines | Includes assets that provide a physical link and associated assets between the distribution network and a customer’s premises. It excludes any pole mounted assets and meters that are included in any other asset group.
Transformer | Assets used to transform voltage levels within the network. This includes all its components such as the cooling systems and tap changing equipment (where installed). It excludes any pole mounted assets that are included in any other asset category. For the avoidance of doubt, this does not include instrument transformers as defined in the National Electricity Rules. It also does not include auxiliary transformers.
Switchgear | These are assets used to control, protect and isolate segments of the network. This includes disconnect switches, fuses, circuit breakers, links, reclosers, sectionalisers, ring main units, oil insulated fuses etc. It excludes any pole mounted assets that are included in any other asset category.
Public light maintenance | The repair and inspection of the following public lighting assets on a major or minor road: Luminaires; Brackets; Lamps; Poles dedicated to public lighting services; and Underground or overhead cabling dedicated to public lighting services.
Public lighting assets | Include luminaires, brackets, lamps and dedicated public lighting poles (not poles that deliver network services).
SCADA and network control and protection systems | SCADA and network control hardware, software and associated IT systems. Includes protection and control systems and communication systems. Excludes SCADA and Network Control systems that exist within gateway devices (routers, bridges etc.) at corporate offices. Protection systems has the meaning prescribed in the National Electricity Rules.
Terrain factors
Average number of trees per vegetation Maintenance span | The average number of trees within the NSP’s vegetation maintenance spans. This includes only trees that require active vegetation management to meet its vegetation management obligations. This excludes trees that only require Inspections and no other vegetation management activities required to comply with the NSP’s vegetation obligations.
CBD feeder | A feeder in the CBD area of State or Territory capital that has been determined by the relevant participating jurisdiction as supplying electricity to predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas.
Urban feeder | Has the meaning as defined in the STPIS scheme and Distribution Reliability Measures Guideline.
Bushfire Risk | The number of Maintenance Spans in high bushfire risk areas as classified by a person or organisation with appropriate expertise on fire risk. This includes but is not limited to: (a) the NSP’s jurisdictional fire authority (b) local councils (c) insurance companies (d) NSP’s consultants (e) local fire experts.
Cutting cycle | The average planned number of years (including fractions of years) between which cyclic vegetation maintenance is performed within vegetation management zones.
Defects (vegetation) | Any recorded incidence of noncompliance with a NSP’s vegetation clearance standard. This also includes vegetation outside a NSP’s standard clearance zone that is recognised as hazardous vegetation and which would normally be reported as requiring management under the NSP's inspection practices.
Route line length | The aggregate length in kilometres of lines, measured as the length of each span between poles and/or towers, and where the length of each span is considered only once irrespective of how may circuits it contains. This is the distance between line segments and does not include vertical components such as line sag.
Long rural feeder | A feeder with a total feeder route length greater than 200 km, which is not a CBD feeder or urban feeder.
Short rural feeder | A feeder with a total feeder route length less than 200 km, which is not a CBD feeder or urban feeder.
Standard Vehicle Access | Route Line Length areas with Standard Vehicle Access are serviced through made roads, gravel roads and open paddocks (including gated and fenced paddocks). An area with no Standard Vehicle Access would not be accessible by a two wheel drive vehicle.
Total number of spans | The total count of spans in the network in the relevant year. If NSP records towers rather than spans, the number of spans is the number of towers less one.
Tropical Proportion | The approximate total number of urban and rural maintenance spans in the Hot Humid Summer and Warm Humid Summer regions as defined by the Australian Bureau of Meteorology Australian Climatic Zones map (based on temperature and humidity).
Vegetation maintenance span | A span within the NSP’s network that is subject to active vegetation management practices in the relevant year. Active vegetation management practices do not include inspection of vegetation maintenance spans.
Export Services
Battery | A device that reserves energy.
Curtailment | The amount of energy that is prevented from being generated by export customers due to a planned or unplanned network constraint.
Customer (export services) | Metered customers with a NMI.
Export customer | A customer (export services) that receives export services
Export services | Export services are services provided by distribution networks to accept and distribute energy generated within its network either behind the meter or front of meter.
Export capacity | The maximum amount of electricity a customer's system is capable of exporting to the distribution network in accordance with the connection agreement.
Non-residential HV customer | Non-residential customer who is connected at higher than 415 volts.
Non-residential LV customer | Non-residential customer who is connected at 240 or 415 volts.
Residential customer | A customer or customer (gas) who purchases energy principally for personal, household or domestic use at premises.
Solar photovoltaic (PV) | A system for generating electricity that converts sunlight into electrical energy.
CBD feeder | A feeder in the CBD area of State or Territory capital that has been determined by the relevant participating jurisdiction as supplying electricity to predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas.
Approved capacity | The maximum amount of export capacity a distribution network agrees to accept from a customer.
Export capacity request | The maximum amount of export capacity a customer requests when requesting export services from a distribution network.
Feeder | A power line, including underground cables, that is part of a distribution network.
Feeder classification | Classification of feeder based on location on network or type of load served (network type as defined in the STPIS). Non Tasmanian feeder classifications are: CBD, Urban; Short rural and Long Rural. Tasmanian feeder classifications are consistent with the requirements of the Tasmanian Electricity Code: Critical infrastructure; Urban; High density commercial, High density rural and Low density rural.
High voltage customer | Customer connected at higher than 415 volts.
Long rural feeder | A feeder with a total feeder route length greater than 200 km, which is not a CBD feeder or urban feeder.
Low voltage customer | Customer connected at 240 or 415 volts.
Non-residential customer | A customer who purchases energy not principally for personal, household or domestic use at premises.
Short rural feeder | A feeder with a total feeder route length less than 200 km, which is not a CBD feeder or urban feeder.
TAS - Critical infrastructure | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - High density commercial | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - High density rural | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - Low density rural | Consistent with the requirements of the Tasmanian Electricity Code.
TAS - Urban | Consistent with the requirements of the Tasmanian Electricity Code.
Urban feeder | Has the meaning as defined in the STPIS scheme and Distribution Reliability Measures Guideline.
Small business | A small customer that is not a residential customer, whose tariff is classified as a small business tariff, or otherwise identified as a small business in the NSP's customer database.
Small customer | A customer, usually residential or small business, whose annual usage falls under the relevant jurisdictional threshold (generally 100MWh).

## Validations
Data category 03: Network metrics
Data validation is a process to improve data quality by checking the accuracy and quality of source data before using, importing or otherwise processing the data. Data validation rules provide the first level of data cleansing in the data quality process. They decrease the likelihood of errors at the point of data entry. Data validation rules cannot, however, guarantee data entry is correct, only that it has passed a pre-specified set of rules.
Validation Rules
Worksheet | Tables | input cells | Rules applying
Network assets - volume | Public lighting | Number of assets | Whole number
≥0
NULL invalid if prescribed or business defined row descriptor exists
|  | Business specified | Free text, must align with previous years descriptors, or changes explained
NULL invalid
| Meter population | Number of assets | Whole number
≥0
NULL invalid
| Total poles by feeder type | Number of assets | Whole number
≥0
NULL invalid
Non-network assets - volume | IT & Communications | Number of devices | ≥0
NULL invalid
| Motor vehicles | Number of vehicles | ≥0
NULL invalid
Length | Circuit Length | km | ≥0
NULL invalid
| Service area factors | km | ≥0
NULL invalid
| Maintenance spans | km | ≥0
NULL invalid
| High voltage distribution lines | Business specified (Feeder ID) | Free text - must match descriptors used in data category 05 - service performance
NULL is valid
|  | Business specified (Feeder service area description) | Free text - must match descriptors used in data category 05 - service performance
NULL invalid
|  | Businesses selection (Feeder classification) | Valid responses are only: CBD / Urban / Short rural / Long rural
Tasnetworks valid responses are only: CBD / critical infrastructure / high density commercial / high density rural / low density rural
NULL invalid
|  | km | ≥0
NULL invalid
| Selected asset characteristics | km | ≥0
NULL invalid
Capacity | Circuit capacity MVA | MVA | ≥0
NULL invalid
| Transformer capacities | MVA | ≥0
NULL invalid
| Selected asset characteristics - Capacity data | MVA | ≥0
NULL invalid
Asset age profile | Installed assets - quantity currently in commission by year | Number of assets | Whole number
≥0
NULL invalid
|  | km | ≥0
NULL invalid
|  | Business specified | Free text - must match categories specified in Data category 07 - capital expenditure
NULL is valid
Asset metrics | Asset lives | Years | ≥0
NULL invalid
| Inspection and maintenance cycles | Years | ≥0
NULL invalid
|  | Business specified | Free text - must match categories specified in Data category 07 - capital expenditure
NULL Valid
Terrain factors | Terrain factors | Years | ≥0
NULL invalid
|  | Number of spans | ≥0
NULL invalid
|  | km | ≥0
NULL invalid
Export Services | Export capacity requested | Residential (kVA) | ≥0
NULL invalid
|  | Low voltage small business (kVA) | ≥0
NULL valid if data provided at "Low voltage non residential", else NULL invalid
|  | Low voltage non residential (excluding small business) (kVA) | ≥0
NULL valid if data provided at "Low voltage non residential", else NULL invalid
|  | Low voltage non residential (kVA) | ≥0
NULL valid if data provided at "Low voltage small business" & "Low voltage non residential (excluding small business)", else NULL invalid
|  | High voltage non residential (kVA) | ≥0
NULL invalid
|  | by feeder classification (kVA) | ≥0
NULL invalid
| Export service - approved capacity | Residential (kVA) | ≥0
NULL invalid
|  | Low voltage small business (kVA) | ≥0
NULL valid if data provided at "Low voltage non residential", else NULL invalid
|  | Low voltage non residential (excluding small business) (kVA) | ≥0
NULL valid if data provided at "Low voltage non residential", else NULL invalid
|  | Low voltage non residential (kVA) | ≥0
NULL valid if data provided at "Low voltage small business" & "Low voltage non residential (excluding small business)", else NULL invalid
|  | High voltage non residential (kVA) | ≥0
NULL invalid
|  | by feeder classification (kVA) | ≥0
NULL invalid
| Average non-zero static export limit at year-end | Residential (kVA) | ≥0
NULL invalid
|  | Low voltage small business (kVA) | ≥0
NULL valid if data provided at "Low voltage non residential", else NULL invalid
|  | Low voltage non residential (excluding small business) (kVA) | ≥0
NULL valid if data provided at "Low voltage non residential", else NULL invalid
|  | Low voltage non residential (kVA) | ≥0
NULL valid if data provided at "Low voltage small business" & "Low voltage non residential (excluding small business)", else NULL invalid
|  | High voltage non residential (kVA) | ≥0
NULL invalid
|  | by feeder classification (kVA) | ≥0
NULL invalid
| Metrics related to utilised and curtailed energy | KWh | ≥0
NULL valid
| Exporting customer capacity by customer (export services) type | Residential (kVA) | ≥0
NULL invalid
|  | Low voltage small business (kVA) | ≥0
NULL valid if data provided at "Low voltage non residential", else NULL invalid
|  | Low voltage non residential (excluding small business) (kVA) | ≥0
NULL valid if data provided at "Low voltage non residential", else NULL invalid
|  | Low voltage non residential (kVA) | ≥0
NULL valid if data provided at "Low voltage small business" & "Low voltage non residential (excluding small business)", else NULL invalid
|  | High voltage non residential (kVA) | ≥0
NULL invalid
|  | by feeder classification (kVA) | ≥0
NULL invalid
| Export customer capacity by feeder classification | kVA | ≥0
NULL valid if feeder classification does not apply to the distribution network.

## Checks and Totals
Data category 03: Network metrics
Totals and Data Hierarchies
Worksheet | Table | Sub table | Reference |  | Worksheet | Table | Sub table | Reference | Check
Network Assets - Volume | Meter Population | Meter 4 | Single phase meter population | = | Network Assets - Volume | Meter Population | Meter 4 | Current transformer connected meter population | TRUE
|  |  | + |  |  |  |  | +
|  |  | Multi phase meter population |  |  |  |  | Direct connect meter population
Network Assets - Volume | Meter Population | Meter 5 | Single phase meter population | = | Network Assets - Volume | Meter Population | Meter 5 | Current transformer connected meter population | TRUE
|  |  | + |  |  |  |  | +
|  |  | Multi phase meter population |  |  |  |  | Direct connect meter population
Network Assets - Volume | Meter Population | Meter 6 | Single phase meter population | = | Network Assets - Volume | Meter Population | Meter 6 | Current transformer connected meter population | TRUE
|  |  | + |  |  |  |  | +
|  |  | Multi phase meter population |  |  |  |  | Direct connect meter population
Export Services | Export capacity requested | Customer (export services) type (Total customers) | Total | = | Export Services | Export capacity requested | Feeder classification (Total) | Total | TRUE
Export Services | Export services - approved capacity | Export customer type (Total customers) | Total | = | Export Services | Export services - approved capacity | Feeder classification (Total) | Total | TRUE
Export Services | Average non-zero static export limit at year-end | Customer (export services) type (Total customers) | Total | = | Export Services | Average non-zero static export limit at year-end | Feeder classification (Total) | Total | TRUE
Export Services | Exporting customer capacity by customer (export services) type |  | Total installed capacity | = | Export Services | Exporting customer capacity by feeder classification |  | Total installed capacity | TRUE
Export Services | Exporting customer capacity by customer (export services) type |  | Solar PV only | = | Export Services | Exporting customer capacity by feeder classification |  | Solar PV only | TRUE
Export Services | Exporting customer capacity by customer (export services) type |  | Solar PV and Battery | = | Export Services | Exporting customer capacity by feeder classification |  | Solar PV and Battery | TRUE
Export Services | Exporting customer capacity by customer (export services) type |  | Battery only | = | Export Services | Exporting customer capacity by feeder classification |  | Battery only | TRUE

## Network assets - volume
Data category 03: Network metrics
Network assets - volume
|  | Units |  | Current RIN reference | Assurance standard - Non-Financial data
Public lighting |  |  | Volume
Public lighting luminaires |  | Number of assets |  | EB3.5.3 | ASAE3000
Public lighting poles |  | Number of assets |  | EB3.5.3 | ASAE3000
Public lighting columns |  | Number of assets |  | EB3.5.3 | ASAE3000
PUBLIC LIGHTING BY LIGHT TYPE |  |  |  | CA4.1.1
<business specified> |  | Number of assets |  | CA4.1.1 | ASAE3000
<business specified> |  | Number of assets |  | CA4.1.1 | ASAE3000
<business specified> |  | Number of assets |  | CA4.1.1 | ASAE3000
<business specified> |  | Number of assets |  | CA4.1.1 | ASAE3000
<business specified> |  | Number of assets |  | CA4.1.1 | ASAE3000
<additional rows allowed>
| Total assets | Number of assets | 0
PUBLIC LIGHTING BY TARIFF |  |  |  | ARR4.1.4
<business specified> |  | Number of assets |  | ARR4.1.4 | ASAE3000
<business specified> |  | Number of assets |  | ARR4.1.4 | ASAE3000
<business specified> |  | Number of assets |  | ARR4.1.4 | ASAE3000
<business specified> |  | Number of assets |  | ARR4.1.4 | ASAE3000
<business specified> |  | Number of assets |  | ARR4.1.4 | ASAE3000
<additional rows allowed>
| Total assets | Number of assets | 0
Meter population |  |  | Volume
Meter Type 1-3
Single phase meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Multi phase meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Current transformer connected meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Direct connect meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Meter Type 4
Single phase meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Multi phase meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Current transformer connected meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Direct connect meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Meter Type 5
Single phase meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Multi phase meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Current transformer connected meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Direct connect meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Meter Type 6
Single phase meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Multi phase meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Current transformer connected meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Direct connect meters |  | Number of assets |  | CA4.2.1 | ASAE3000
Total poles by feeder type |  |  | Assets currently in Commission
CBD feeder |  | Number of assets |  | CA2.2.2 | ASAE3000
Urban feeder / TAS - Urban |  | Number of assets |  | CA2.2.2 | ASAE3000
Long rural feeder |  | Number of assets |  | CA2.2.2 | ASAE3000
Short rural feeder |  | Number of assets |  | CA2.2.2 | ASAE3000
TAS - Critical Infrastructure |  | Number of assets |  | CA2.2.2 | ASAE3000
TAS - High density commercial |  | Number of assets |  | CA2.2.2 | ASAE3000
TAS - High density rural |  | Number of assets |  | CA2.2.2 | ASAE3000
TAS - Low density rural |  | Number of assets |  | CA2.2.2 | ASAE3000
Feeders other |  | Number of assets |  | CA2.2.2 | ASAE3000

## Non-network assets - volume
Data category 03: Network metrics
Non-network assets - volume
| Units | Volume | Current RIN reference | Assurance standard - Non-Financial data
IT & communications
Number of devices | Number of devices |  | CA2.6.2 | ASAE3000
Motor vehicles
Car | Number of vehicles |  | CA2.6.3 | ASAE3000
Light Commercial Vehicle | Number of vehicles |  | CA2.6.3 | ASAE3000
Elevated Work Platform (LCV) | Number of vehicles |  | CA2.6.3 | ASAE3000
Elevated Work Platform (HCV) | Number of vehicles |  | CA2.6.3 | ASAE3000
Heavy Commercial Vehicle | Number of vehicles |  | CA2.6.3 | ASAE3000

## Length
Data category 03: Network metrics
Length
|  |  | Units |  |  | Current RIN reference | Assurance standard - Non-Financial data
Circuit length |  |  |  |  | Length
OVERHEAD NETWORK LENGTH OF CIRCUIT AT EACH VOLTAGE
Overhead low voltage distribution |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead 2.2 kV |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead 6.6 kV |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead 7.6 kV |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead 11 kV |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead SWER |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead 22 kV |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead 33 kV |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead 44 kV |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead 66 kV |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead 110 kV |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead 132 kV |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Overhead 220 kV |  |  | km |  |  | EB3.5.1.1 | ASAE3000
Other |  |  | km |  |  | EB3.5.1.1 | ASAE3000
|  | Total overhead network length | km |  | 0 | EB3.5.1.1
UNDERGROUND NETWORK LENGTH OF CIRCUIT AT EACH VOLTAGE
Underground low voltage distribution |  |  | km |  |  | EB3.5.1.2 | ASAE3000
Underground 5 kV |  |  | km |  |  | EB3.5.1.2 | ASAE3000
Underground 6.6 kV |  |  | km |  |  | EB3.5.1.2 | ASAE3000
Underground 7.6 kV |  |  | km |  |  | EB3.5.1.2 | ASAE3000
Underground 11 kV |  |  | km |  |  | EB3.5.1.2 | ASAE3000
Underground SWER |  |  | km |  |  | EB3.5.1.2 | ASAE3000
Underground 22 kV |  |  | km |  |  | EB3.5.1.2 | ASAE3000
Underground 33 kV |  |  | km |  |  | EB3.5.1.2 | ASAE3000
Underground 66 kV |  |  | km |  |  | EB3.5.1.2 | ASAE3000
Underground 110 kV |  |  | km |  |  | EB3.5.1.2 | ASAE3000
Underground 132 kV |  |  | km |  |  | EB3.5.1.2 | ASAE3000
Other |  |  | km |  |  | EB3.5.1.2 | ASAE3000
|  | Total underground network length | km |  | 0 | EB3.5.1.2
Service area factors |  |  |  |  | Length
Total route line length
Route line length - Urban and CBD feeders |  |  | km |  |  | CA2.7.1 | ASAE3000
Route line length - Rural feeders |  |  | km |  |  | CA2.7.1 | ASAE3000
|  | Total route line length | km |  | 0 | EB3.7.3
Maintenance spans |  |  |  |  | Length
Total length of maintenance spans
Length of maintenance spans - Urban and CBD feeders |  |  | km |  |  | CA2.7.1 | ASAE3000
Length of maintenance spans - Rural feeders |  |  | km |  |  | CA2.7.1 | ASAE3000
|  | Total length of maintenance spans | km |  | 0
High voltage distribution lines |  |  |  | Length
Feeder ID | Feeder service area description | Feeder classification |  | Overhead | Underground
<business specified> | <business specified> | <business selection> | km |  |  | ARR3.6.8 | ASAE3000
<business specified> | <business specified> | <business selection> | km |  |  | ARR3.6.8 | ASAE3000
<business specified> | <business specified> | <business selection> | km |  |  | ARR3.6.8 | ASAE3000
<business specified> | <business specified> | <business selection> | km |  |  | ARR3.6.8 | ASAE3000
<business specified> | <business specified> | <business selection> | km |  |  | ARR3.6.8 | ASAE3000
<additional rows allowed>
Feeder Classification Options
CBD
Urban
Short Rural
Long Rural
TAS - Critical Infrastructure
TAS - High density commercial
TAS - High density rural
TAS - Low density rural
TAS - Urban
Selected asset characteristics |  |  |  | Length
|  |  |  | Assets in Commission | Asset Replacements
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH BY FEEDER TYPE
CBD feeder |  |  | km |  |  | CA2.2.2 | ASAE3000
Urban feeder / TAS - Urban |  |  | km |  |  | CA2.2.2 | ASAE3000
Short rural feeder |  |  | km |  |  | CA2.2.2 | ASAE3000
Long rural feeder |  |  | km |  |  | CA2.2.2 | ASAE3000
TAS - Critical Infrastructure |  |  | km |  |  | CA2.2.2 | ASAE3000
TAS - High density commercial |  |  | km |  |  | CA2.2.2 | ASAE3000
TAS - High density rural |  |  | km |  |  | CA2.2.2 | ASAE3000
TAS - Low density rural |  |  | km |  |  | CA2.2.2 | ASAE3000
Feeders other |  |  | km |  |  | CA2.2.2 | ASAE3000
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH MATERIAL TYPE
Overhead conductor LV ABC |  |  | km |  |  | CA2.2.2 | ASAE3000
Overhead conductor steel |  |  | km |  |  | CA2.2.2 | ASAE3000
Overhead conductor ACSR |  |  | km |  |  | CA2.2.2 | ASAE3000
Overhead conductor AAAC |  |  | km |  |  | CA2.2.2 | ASAE3000
Overhead conductor AAC |  |  | km |  |  | CA2.2.2 | ASAE3000
Overhead conductor HDBC |  |  | km |  |  | CA2.2.2 | ASAE3000
Other material |  |  | km |  |  | CA2.2.2 | ASAE3000
UNDERGROUND CABLES BY: CABLE LENGTH BY FEEDER TYPE
CBD feeder |  |  | km |  |  | CA2.2.2 | ASAE3000
Urban feeder / TAS - Urban |  |  | km |  |  | CA2.2.2 | ASAE3000
Short rural feeder |  |  | km |  |  | CA2.2.2 | ASAE3000
Long rural feeder |  |  | km |  |  | CA2.2.2 | ASAE3000
TAS - Critical Infrastructure |  |  | km |  |  | CA2.2.2 | ASAE3000
TAS - High density commercial |  |  | km |  |  | CA2.2.2 | ASAE3000
TAS - High density rural |  |  | km |  |  | CA2.2.2 | ASAE3000
TAS - Low density rural |  |  | km |  |  | CA2.2.2 | ASAE3000
Feeders other |  |  | km |  |  | CA2.2.2 | ASAE3000

## Capacity
Data category 03: Network metrics
Capacity
[5 empty] | Current RIN reference | Assurance standard - Non-Financial data
Circuit capacity MVA | Units |  |  | Volume
ESTIMATED OVERHEAD NETWORK WEIGHTED AVERAGE MVA CAPACITY BY VOLTAGE CLASS
Overhead low voltage distribution | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Overhead 6.6 kV | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Overhead 7.6 kV | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Overhead 11 kV | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Overhead SWER | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Overhead 22 kV | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Overhead 33 kV | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Overhead 44 kV | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Overhead 66 kV | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Overhead 110 kV | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Overhead 132 kV | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Overhead 220 kV | MVA |  |  |  | EB3.5.1.3 | ASAE3000
Other | MVA |  |  |  | EB3.5.1.3 | ASAE3000
ESTIMATED UNDERGROUND NETWORK WEIGHTED AVERAGE MVA CAPACITY BY VOLTAGE CLASS
Underground low voltage distribution | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Underground 5 kV | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Underground 6.6 kV | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Underground 7.6 kV | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Underground 11 kV | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Underground SWER | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Underground 12.7 kV | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Underground 22 kV | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Underground 33 kV | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Underground 66 kV | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Underground 110 kV | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Underground 132 kV | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Other | MVA |  |  |  | EB3.5.1.4 | ASAE3000
Transformer capacities |  |  |  | Volume
DISTRIBUTION TRANSFORMER TOTAL INSTALLED CAPACITY
Distribution transformer capacity owned by utility | MVA |  |  |  | EB3.5.2 | ASAE3000
Cold spare capacity included in Distribution transformer capacity owned by utility | MVA |  |  |  | EB3.5.2 | ASAE3000
ZONE SUBSTATION TRANSFORMER CAPACITY
Total installed capacity for first step transformation where there are two steps to reach distribution voltage | MVA |  |  |  | EB3.5.2 | ASAE3000
Total installed capacity for second step transformation where there are two steps to reach distribution voltage | MVA |  |  |  | EB3.5.2 | ASAE3000
Total zone substation transformer capacity where there is only a single step transformation to reach distribution voltage | MVA |  |  |  | EB3.5.2 | ASAE3000
Total zone substation transformer capacity | MVA |  |  |  | EB3.5.2 | ASAE3000
Cold spare capacity of zone substation transformers included in Total zone substation transformer capacity | MVA |  |  |  | EB3.5.2 | ASAE3000
DISTRIBUTION - OTHER TRANSFORMER CAPACITY
Distribution other - transformer capacity owned by utility | MVA |  |  |  | EB3.5.2 | ASAE3000
Selected asset characteristics - capacity data |  | Assets in Commission | Asset replacements | Assets decommissioned
TRANSFORMERS
Transformer capacity | MVA |  |  |  | CA2.2.2 | ASAE3000
Transformer capacity decommissioned | MVA |  |  |  | CA2.2.2 | ASAE3000

## Asset age profile
Data category 03: Network metrics
Asset age profile
|  | Units |  |  |  |  | Current RIN reference | Assurance standard - Non-Financial data
Installed assets - quantity currently in commission by year |  |  | Current reporting year | Previous reporting year | … | 1935
POLES BY: HIGHEST OPERATING VOLTAGE; MATERIAL TYPE | [6 empty] | Replaces CA2.8.1
˂ = 1 kV; Wood |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 1 kV & < = 11 kV; Wood |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˃ 11 kV & < = 22 kV; Wood |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 22 kV & < = 66 kV; Wood |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV; Wood |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 132 kV; Wood |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˂ = 1 kV; Concrete |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 1 kV & < = 11 kV; Concrete |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˃ 11 kV & < = 22 kV; Concrete |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 22 kV & < = 66 kV; Concrete |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV; Concrete |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 132 kV; Concrete |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˂ = 1 kV; Steel |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 1 kV & < = 11 kV; Steel |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˃ 11 kV & < = 22 kV; Steel |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 22 kV & < = 66 kV; Steel |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV; Steel |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 132 kV; Steel |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˂ = 1 kV; Composite pole |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 1 kV & < = 11 kV; Composite pole |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
˃ 11 kV & < = 22 kV; Composite pole |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 22 kV & < = 66 kV; Composite pole |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV; Composite pole |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 132 kV; Composite pole |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
˂ = 1 kV; Pole - other technology |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 1 kV & < = 11 kV; Pole - other technology |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
˃ 11 kV & < = 22 kV; Pole - other technology |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 22 kV & < = 66 kV; Pole - other technology |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV; Pole - other technology |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 132 kV; Pole - other technology |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
Other |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
| Total poles | Number of assets | 0
STAKING OF / STAKED WOODEN POLES BY: HIGHEST OPERATING VOLTAGE
˂ = 1 kV |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 1 kV & < = 11 kV |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
˃ 11 kV & < = 22 kV |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 22 kV & < = 66 kV |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
> 132 kV |  | Number of assets |  |  | … |  | Amends CA 5.2.1 | ASAE3000
| Total wooden poles | Number of assets | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | [6 empty] | Replaces CA2.8.1
˂ = 1 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
> 1 kV & < = 11 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
˃ 11 kV & < = 22 kV; SWER |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
˃ 11 kV & < = 22 kV; Single-Phase |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
˃ 11 kV & < = 22 kV; Multiple-Phase |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
> 22 kV & < = 66 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
> 132 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
Other |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
| Total overhead conductors | km | 0
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | [6 empty] | Replaces CA2.8.1
˂ = 1 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
> 1 kV & < = 11 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
> 11 kV & < = 22 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
> 22 kV & < = 33 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
> 33 kV & < = 66 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
> 132 kV |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
Other |  | km |  |  | … |  | CA 5.2.1 | ASAE3000
| Total underground cables | km | 0
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | [6 empty] | Replaces CA2.8.1
˂ = 11 kV; Residential; Overhead conductor |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˂ = 11 kV; Commercial & Industrial; Overhead conductor |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˂ = 11 kV; Residential; Underground cable |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˂ = 11 kV; Commercial & Industrial; Underground cable |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˂ = 11 kV; Subdivision; Underground cable |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 11 kV & < = 22 kV; Commercial & Industrial |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 11 kV & < = 22 kV; Subdivision |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 22 kV & < = 33 kV; Commercial & Industrial |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 22 kV & < = 33 kV; Subdivision |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 33 kV & < = 66 kV; Commercial & Industrial |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 33 kV & < = 66 kV; Subdivision |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV; Commercial & Industrial |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV; Subdivision |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 132 kV; Commercial & Industrial |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 132 kV; Subdivision |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Other |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
| Total service lines | Number of assets | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE; AMPERE RATING; NUMBER OF PHASES (AT LV) | [6 empty] | Replaces CA2.8.1
Pole Mounted; < = 22kV; < = 60 kVA; Single Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Pole Mounted; < = 22kV; > 60 kVA and < = 600 kVA; Single Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Pole Mounted; < = 22kV; > 600 kVA; Single Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Pole Mounted; < = 22kV; < = 60 kVA; Multiple Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Pole Mounted; < = 22kV; > 60 kVA and < = 600 kVA; Multiple Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Pole Mounted; < = 22kV; > 600 kVA; Multiple Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Kiosk Mounted; < = 22kV; < = 60 kVA; Single Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Kiosk Mounted; < = 22kV; > 60 kVA and < = 600 kVA; Single Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Kiosk Mounted; < = 22kV; > 600 kVA; Single Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Kiosk Mounted; < = 22kV; < = 60 kVA; Multiple Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Kiosk Mounted; < = 22kV; > 60 kVA and < = 600 kVA; Multiple Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Kiosk Mounted; < = 22kV; > 600 kVA; Multiple Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV; < = 60 kVA; Single Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV; > 60 kVA and < = 600 kVA; Single Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV; > 600 kVA; Single Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV; < = 60 kVA; Multiple Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV; > 60 kVA and < = 600 kVA; Multiple Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV; > 600 kVA; Multiple Phase |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV; < = 15 MVA |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV; > 15 MVA and < = 40 MVA |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV; > 40 MVA |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV; < = 15 MVA |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV; > 15 MVA and < = 40 MVA |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV; > 40 MVA |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV; < = 100 MVA |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV; > 100 MVA |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; > 132 kV; < = 100 MVA |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Ground Outdoor / Indoor Chamber Mounted; > 132 kV; > 100 MVA |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Other |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
| Total transformers | Number of assets | 0
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE; SWITCH FUNCTION | [6 empty] | Replaces CA2.8.1
˂ = 11 kV; Fuse |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˂ = 11 kV; Switch |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
˂ = 11 kV; Circuit Breaker |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 11 kV & < = 22 kV; Switch |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 11 kV & < = 22 kV; Circuit Breaker |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 22 kV & < = 33 kV; Switch |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 22 kV & < = 33 kV; Circuit Breaker |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 33 kV & < = 66 kV; Switch |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 33 kV & < = 66 kV; Circuit Breaker |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV; Switch |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 66 kV & < = 132 kV; Circuit Breaker |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 132 kV; Switch |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
> 132 kV; Circuit Breaker |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Other |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
| Total switchgear | Number of assets | 0
PUBLIC LIGHTING BY: ASSET TYPE; LIGHTING OBLIGATION | [6 empty] | Replaces CA2.8.1
Luminaires; Major Road |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Luminaires; Minor Road |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Brackets; Major Road |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Brackets; Minor Road |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Lamps; Major Road |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Lamps; Minor Road |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Poles / Columns; Major Road |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Poles / Columns; Minor Road |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Other |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
| Total public lighting | Number of assets | 0
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | [6 empty] | Replaces CA2.8.1
Field Devices |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Local Network Wiring Assets |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Communications Network Assets |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Master Station Assets |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Communications Site Infrastructure |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Communications Linear Assets |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
AFLC |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
Other |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
| Total SCADA, network control and protection systems | Number of assets | 0
OTHER BY: BUSINESS SPECIFIED CATEGORIES | [6 empty] | Replaces CA2.8.1
<business specified> |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
<business specified> |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
<business specified> |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
<business specified> |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
<business specified> |  | Number of assets |  |  | … |  | CA 5.2.1 | ASAE3000
<additional rows allowed>
| Total assets - other by business specified categories | Number of assets | 0

## Asset metrics
Data category 03: Network metrics
Asset metrics
[5 empty] | Current RIN reference | Assurance standard - Non-Financial data
Asset lives |  | Standard Control Services | Alternative Control Services | Network Services |  | Standard Control Services | Alternative Control Services | Network Services
ESTIMATED SERVICE LIFE OF NEW ASSETS
Overhead network assets less than 33kV (wires and poles) | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Underground network assets less than 33kV (cables) | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Distribution substations including transformers | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Overhead network assets 33kV and above (wires and towers / poles etc) | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Underground network assets 33kV and above (cables, ducts etc) | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Zone substations and transformers | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Meters | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Other assets with long lives | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Other assets with short lives | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
ESTIMATED RESIDUAL SERVICE LIFE
Overhead network assets less than 33kV (wires and poles) | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Underground network assets less than 33kV (cables) | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Distribution substations including transformers | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Overhead network assets 33kV and above (wires and towers / poles etc) | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Underground network assets 33kV and above (cables, ducts etc) | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Zone substations and transformers | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Meters | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Other assets with long lives | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Other assets with short lives | Years |  |  |  | EB3.3.4 |  |  | ASAE3000
Inspection and maintenance cycles |  |  | Inspection cycle | Maintenance cycle |  | Inspection cycle | Maintenance cycle
Poles | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
Pole top structures | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
Staked wooden poles | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
Overhead conductors | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
Underground cables | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
Service lines | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
Transformers | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
Switchgear | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
Public lighting | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
SCADA, network control and protection systems | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
Other assets
<business specified> | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
<business specified> | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
<business specified> | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
<business specified> | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
<business specified> | Years |  |  |  | Replaces CA2.8.1 | ASAE3000 | ASAE3000
<additional rows allowed>

## Terrain factors
Data category 03: Network metrics
Terrain factors
| Units | Asset volume | Current RIN reference | Assurance standard - Non-Financial data
TOTAL URBAN AND CBD
Average frequency of cutting cycle | Years |  | CA2.7.1 | ASAE3000
Number of maintenance spans | Number of spans |  | CA2.7.1 | ASAE3000
Number of vegetation maintenance spans | Number of spans |  | EB3.7.2 | ASAE3000
Average number of defects per vegetation maintenance span | Number of spans |  | EB3.7.2 | ASAE3000
Average number of trees per vegetation maintenance span | Number of spans |  | EB3.7.2 | ASAE3000
TOTAL RURAL
Average frequency of cutting cycle | Years |  | CA2.7.1 | ASAE3000
Number of maintenance spans | Number of spans |  | CA2.7.1 | ASAE3000
Number of vegetation maintenance spans | Number of spans |  | EB3.7.2 | ASAE3000
Average number of defects per vegetation maintenance span | Number of spans |  | EB3.7.2 | ASAE3000
Average number of trees per vegetation maintenance span | Number of spans |  | EB3.7.2 | ASAE3000
OTHER
Total number of spans | Number of spans |  | EB3.7.2 | ASAE3000
Tropical Proportion (number of spans) | Number of spans |  | EB3.7.2 | ASAE3000
Bushfire Risk (number of spans) | Number of spans |  | EB3.7.2 | ASAE3000
Standard Vehicle Access | km |  | EB3.7.2 | ASAE3000

## Export services
Data category 03: Network metrics
Export Services
| Units | Volume | Current RIN reference | Assurance standard - Non-Financial data
Export capacity requested
CUSTOMER (EXPORT SERVICES) TYPE
Total customers | kVA | 0
Residential | kVA |  | ES Info Req 3.2.1
Non residential LV | kVA |  | ES Info Req 3.2.1
Low voltage small business | kVA |  | NEW
Low voltage non residential (excluding small business) | kVA |  | NEW
Non residential HV | kVA |  | ES Info Req 3.2.1
FEEDER CLASSIFICATION
CBD | kVA |  | ES Info Req 3.2.2
Urban / TAS - Urban | kVA |  | ES Info Req 3.2.2
Short rural | kVA |  | ES Info Req 3.2.2
Long rural | kVA |  | ES Info Req 3.2.2
TAS - Low density rural | kVA |  | ES Info Req 3.2.2
TAS - High density rural | kVA |  | ES Info Req 3.2.2
TAS - High density commercial | kVA |  | ES Info Req 3.2.2
TAS - Critical infrastructure | kVA |  | ES Info Req 3.2.2
Export service - approved capacity
EXPORT CUSTOMER TYPE
Total customers | kVA | 0
Residential | kVA |  | ES Info Req 3.2.1
Non residential LV | kVA |  | ES Info Req 3.2.1
Low voltage small business | kVA |  | NEW
Low voltage non residential (excluding small business) | kVA |  | NEW
Non residential HV | kVA |  | ES Info Req 3.2.1
FEEDER CLASSIFICATION
CBD | kVA |  | ES Info Req 3.2.2
Urban / TAS - Urban | kVA |  | ES Info Req 3.2.2
Short rural | kVA |  | ES Info Req 3.2.2
Long rural | kVA |  | ES Info Req 3.2.2
TAS - Low density rural | kVA |  | ES Info Req 3.2.2
TAS - High density rural | kVA |  | ES Info Req 3.2.2
TAS - High density commercial | kVA |  | ES Info Req 3.2.2
TAS - Critical infrastructure | kVA |  | ES Info Req 3.2.2
Average non-zero static export limit at year-end
CUSTOMER (EXPORT SERVICES) TYPE
Total customers | kVA | 0
Residential | kVA |  | ES Info Req 3.6.1
Low voltage non residential | kVA |  | ES Info Req 3.6.1
Low voltage small business | kVA |  | NEW
Low voltage non residential (excluding small business) | kVA |  | NEW
Non residential HV | kVA |  | ES Info Req 3.6.1
FEEDER CLASSIFICATION
CBD | kVA |  | ES Info Req 3.6.2
Urban / TAS - Urban | kVA |  | ES Info Req 3.6.2
Short rural | kVA |  | ES Info Req 3.6.2
Long rural | kVA |  | ES Info Req 3.6.2
TAS - Low density rural | kVA |  | ES Info Req 3.6.2
TAS - High density rural | kVA |  | ES Info Req 3.6.2
TAS - High density commercial | kVA |  | ES Info Req 3.6.2
TAS - Critical infrastructure | kVA |  | ES Info Req 3.6.2
Metrics related to utilised and curtailed energy
TOTAL POTENTIAL GENERATION
Total potential customer generation | KWh |  | ES Info Req 4.8.1
Potential customer generation - customers with smart meters | KWh |  | ES Info Req 4.8.1
Potential customer generation - customers without smart meters | KWh |  | ES Info Req 4.8.1
CONSUMER ENERGY RESOURCE CURTAILMENT
Total curtailment | KWh |  | ES Info Req 4.8.2
Curtailment due to inverter voltage response | KWh |  | ES Info Req 4.8.2
Curtailment due to static export limits | KWh |  | ES Info Req 4.8.2
Curtailment due to dynamic export limits | KWh |  | ES Info Req 4.8.2
Curtailment directed for system security | KWh |  | ES Info Req 4.8.2
Other curtailment | KWh |  | ES Info Req 4.8.2
Exporting customer capacity by customer (export services) type
TOTAL INSTALLED CAPACITY
SOLAR PV ONLY
Residential | kVA |  | ES Info Req 1.4
Low voltage non residential | kVA |  | ES Info Req 1.4
Low voltage small business | kVA |  | NEW
Low voltage non residential (excluding small business) | kVA |  | NEW
Non residential HV | kVA |  | ES Info Req 1.4
SOLAR PV AND BATTERY
Residential | kVA |  | ES Info Req 1.4
Low voltage non residential | kVA |  | ES Info Req 1.4
Low voltage small business | kVA |  | NEW
Low voltage non residential (excluding small business) | kVA |  | NEW
Non residential HV | kVA |  | ES Info Req 1.4
BATTERY ONLY
Residential | kVA |  | ES Info Req 1.4
Low voltage non residential | kVA |  | ES Info Req 1.4
Low voltage small business | kVA |  | NEW
Low voltage non residential (excluding small business) | kVA |  | NEW
Non residential HV | kVA |  | ES Info Req 1.4
Total installed capacity | kVA | 0
Export customer capacity by feeder classification
TOTAL INSTALLED CAPACITY
SOLAR PV ONLY
CBD | kVA |  | ES Info Req 1.5
Urban / TAS - Urban | kVA |  | ES Info Req 1.5
Short rural | kVA |  | ES Info Req 1.5
Long rural | kVA |  | ES Info Req 1.5
TAS - Low density rural | kVA |  | ES Info Req 1.5
TAS - High density rural | kVA |  | ES Info Req 1.5
TAS - High density commercial | kVA |  | ES Info Req 1.5
TAS - Critical infrastructure | kVA |  | ES Info Req 1.5
SOLAR PV AND BATTERY
CBD | kVA |  | ES Info Req 1.5
Urban / TAS - Urban | kVA |  | ES Info Req 1.5
Short rural | kVA |  | ES Info Req 1.5
Long rural | kVA |  | ES Info Req 1.5
TAS - Low density rural | kVA |  | ES Info Req 1.5
TAS - High density rural | kVA |  | ES Info Req 1.5
TAS - High density commercial | kVA |  | ES Info Req 1.5
TAS - Critical infrastructure | kVA |  | ES Info Req 1.5
BATTERY ONLY
CBD | kVA |  | ES Info Req 1.5
Urban / TAS - Urban | kVA |  | ES Info Req 1.5
Short rural | kVA |  | ES Info Req 1.5
Long rural | kVA |  | ES Info Req 1.5
TAS - Low density rural | kVA |  | ES Info Req 1.5
TAS - High density rural | kVA |  | ES Info Req 1.5
TAS - High density commercial | kVA |  | ES Info Req 1.5
TAS - Critical infrastructure | kVA |  | ES Info Req 1.5
Total installed capacity | kVA | 0