## DNA
Existing Designated Network Assets - as at 19 June 2026
Parent | Name of DNA | Existing DNA Description | Location and Route of Existing DNA | Capacity | Owner/Controller/Operator of DNA
Lumea | Riverina DNA | The DNA comprises the Riverina BESS 132/33kV substation and approximately 200m of 132kV underground cable. 132 kV Underground Single Circuit cable from Darlington Point substation to Riverina BESS substation (approx. 200 m); 132 kV feeder switch bay without breaker including 132kV cable termination structure; One of 132/33 kV 180 MVA Transformer; One switchgear building including; 5 x 33 kV indoor switchboards (Transformer incomer excludes the CB); One Aux Services Building (ASB) with secondary systems equipment installed; One earthing/auxiliary Transformer; Site amenities and storage shed. The Designated Assets includes the Primary and Secondary works associated with the above. | Adjacent to TG's Darlington Point Substation in the Murrumbidgee Shire, New South Wales | The capacity of the DNA is 150MW and there is currently no spare capacity. There are space limitations to increasing capacity. | Lumea Pty Limited (ACN 626 136 865) as trustee for Lumea Trust (ABN 94 121 353 950)
ElectraNet | Redhill to Clements Gap North DNA | Redhill-Clements Gap North 132 kV transmissions line (Redhill F1887); and Clements Gap North Substation. | The Designated Network Asset owned by ElectraNet connects the Clements Gap Wind Farm and a development to construct a battery energy storage system (BESS). The battery will connect to the Transmission Network by nearly 13 kilometres of 132kV cable. | The maximum capacity of the DNA is 105 MVA being the summer thermal rating of the DNA. The maximum capacity of ElectraNet’s transmission network at the Transmission Network Connection Point under summer system normal operating conditions is 141 MVA and is associated with network thermal limitations. | ElectraNet Pty Limited ACN 094 482 416.
Powerlink | MacIntyre DNA | The DNA owned by Powerlink is comprised of: • the 330kV Tummaville Switching Station • the 330kV MacIntyre Intermediate Switching Station • the 330kV transmission line between Tummaville Switching Station and MacIntyre Intermediate Switching Station • cut-in-works and related assets. | The MacIntyre DNA connects the MacIntyre Wind Precinct, located south-west of Warwick, Queensland, to the Transmission Network via the MacIntyre Intermediate Switching Station and the Tummaville Switching Station. | In a Satisfactory Operating State, 1,826 MVA. A Runback Scheme will trip up to 750 MVA initially following a contingency. Current details of the MacIntyre DNA Capacity are available at Powerlink’s MacIntyre DNA webpage https://www.powerlink.com.au/dna-macintyre. The webpage also lists the capacity of generating plants and load facilities for Existing Connected Parties and Conditional Proponents, in relation to the MacIntyre DNA. | Queensland Electricity Transmission Corporation Limited ABN 82 078 849 233, trading as Powerlink, in its capacity as owner of the MacIntyre DNA.
Powerlink | Western Downs DNA | The DNA owned by Powerlink is comprised of: • DNA Component 1, made up of 48.5km of 275kV double circuit transmission line between Halys Substation to the Diamondy Switching and associated easements; and • DNA Component 2, made up of the 275kV Diamondy Switching Station and associated access easement. | The Western Downs DNA connects the Wambo Wind Farm, located near Jandowae, Queensland, to the Transmission Network via the Halys Substation. | As at 8 April 2025, under normal operating conditions, the Western Downs DNA has a limiting transfer capacity of 750 MVA. Current details of the Western Downs DNA capacity are available at Powerlink's Western Downs DNA webpage. The webpage also lists the capacity of generating plants and load facilities for Existing Connected Parties and Conditional Proponents, in relation to the Western Downs DNA. | Queensland Electricity Transmission Corporation Limited ABN 82 078 849 233, trading as Powerlink, in its capacity as owner of the Western Downs DNA.
Lumea | Limondale DNA | 2.21. The main components of Limondale DNA are: • Underground cable o Approximately 1.1km of 220kV single circuit underground cable between Balranald and the Limondale substation. o Duplicated 72F single mode underground fibre cable for control and protection communications between Balranald substation and the Limondale substation. • Limondale 220/33kV substation (including the Primary and Secondary works associated with the below) o One combined 220kV line and transformer switchbay with all required HV plant and associated secondary systems o One 220/33kV 250MVA transformer o One 33/0.415kV Auxiliary/Earthing Transformer o One 33KV BESS connection switchbay o One 33KV Harmonic Filter connection switchbay o An additional secondary services building (SSB) | The DNA comprises two underground cables connecting the Balranald and Limondale substations, as well as the Limondale substation itself. | The capacity of the DNA is 250MVA and there is currently no spare capacity. There are physical space limitations to augmenting the DNA and this prevents the ability to upgrade the DNA within the bounds of the current property to provide any new capacity to users beyond existing facilities owned by Foundation Users. | Lumea Pty Limited (ACN 626 136 865)
Powerlink | Kidston DNA | The Kidston DNA owned by Powerlink is comprised of: • A 275kV single circuit transmission line between Guybal Munjan Substation and Aurumfield Switching Station and associated easements • The 275kV Aurumfield Switching Station and associated access easement • DNA Component 2 (Shared) – 275kV Aurumfiled Switching Station and associated access easement, less the DNA Component 2 (Dedicated) Connection Bays • DNA Component 2 (Dedicated Connection Bays) – the connection bays used to connect Existing Connected Parties to the Aurumfield Switching Station | The DNA will connect to the Transmission Network via the Guybal Munjan Substation. The capacity of the DNA is 576 MWA. | The capacity of the DNA is 576 MWA. Following an upgrade of the second circuit, capacity within both circuits will be 899 MVA. | Queensland Electricity Transmission Corporation Limited ABN 82 078 849 233, trading as Powerlink, in its capacity as owner of the Kidston DNA.