## Insights
Count of MSSS_CAUSE_DESCRIPTION | Column Labels
Row Labels | Steel Pole Beyond 2m | Wood Pole Below Ground | Wood Pole Beyond 2m | Wood Pole Up To 2m | Grand Total
EASTERN/COASTAL | 1 | 7 | 9 | 4 | 21
Corrosion | 1 |  |  |  | 1
Footing Failure |  |  |  | 1 | 1
Rot/Decay |  | 3 | 6 |  | 9
Rot/Decay External |  | 3 | 2 |  | 5
Termites |  | 1 | 1 | 1 | 3
Unknown - Wind |  |  |  | 1 | 1
Rot/Decay Internal |  |  |  | 1 | 1
WESTERN | 1 | 33 | 23 | 24 | 81
Footing Failure |  |  |  | 1 | 1
Lightning |  |  | 1 |  | 1
Rot/Decay |  | 10 | 10 | 8 | 28
Rot/Decay External |  | 8 | 4 | 4 | 16
Termites |  | 10 | 4 | 5 | 19
Unknown - Wind |  | 5 | 3 | 6 | 14
Wrap Stay |  |  | 1 |  | 1
Temporary Pole | 1 |  |  |  | 1
Grand Total | 2 | 40 | 32 | 28 | 102
[8 empty] | Pole failure data shows that the majority of pole failures occur in Western Areas (>80%). The largest causes of failure in the all areas are Rot/Decay and Termites. Majority of failures occur below ground (some below the depth of the inspection zone). | This graph shows that the majority of the poles that fail are in Western areas and also from the 1980s and earlier. This also shows that many of the poles that fail in the Western areas have a working strength of 3kN. | The dominant species of poles that have failed are either unknown (due to no disc being present on the pole) and Spotted Gum. Spotted Gum poles make up approximately 51% of the total population. Unknown species are generally natural poles pre-1970's or older poles were the disc has popped out of the pole.
Count of YOM Grouping | Column Labels
Row Labels | 3 kiloNewton | 5 kiloNewton | 8 kiloNewton | 12 kiloNewton | 20 kiloNewton | Unknown | Grand Total
EASTERN/COASTAL | 1 | 8 | 6 | 3 |  | 3 | 21
1950s | 1 | 2 | 1 |  |  |  | 4
1960s |  | 1 | 1 | 2 |  |  | 4
1970s |  | 1 |  |  |  | 1 | 2
1980s |  | 4 | 3 | 1 |  | 1 | 9
1990s |  |  | 1 |  |  | 1 | 2
WESTERN | 29 | 25 | 18 | 4 | 1 | 4 | 81
1950s | 1 | 1 | 3 | 1 |  |  | 6
1960s | 7 | 4 | 3 | 1 |  | 2 | 17
1970s | 3 | 6 | 1 | 1 |  | 1 | 12
1980s | 14 | 10 | 5 | 1 | 1 |  | 31
1990s | 4 | 1 | 4 |  |  | 1 | 10
2000s |  | 3 | 2 |  |  |  | 5
Grand Total | 30 | 33 | 24 | 7 | 1 | 7 | 102
[8 empty] | Smaller sized poles dominate the poles that are deemed unserviceable. 3kN poles were used extensitvely in rural areas and particularly on SWER intermediate poles (as indicated in the adjacent graph) as they were sufficient to support the load of a single light SWER conductor. Unfortunately, due to their low length, strength and girth dimensions, there is less margin for the pole to deteriorate while still being able to effectively support the pole tip load. | SWER intermediate poles are the largest population of pole structure types found in the Ergon Energy network and are also the most common type of pole structure to fail. These are typically 3kN poles and located in Western areas. There is no dominant type of pole structure in Eastern areas. | Many of the poles that fail are in rural Western areas and situated in grazing and crop properties.
Count of Failed equip | Column Labels
Row Labels | 1950s | 1960s | 1970s | 1980s | 1990s | 2000s | Grand Total
ZZ NO DISC - UNKNOWN | 8 | 13 | 6 | 13 | 5 | 3 | 48
SG SPOTTED GUM | 1 | 5 | 7 | 12 | 3 | 2 | 30
WS WHITE STRINGYBARK |  |  |  | 4 |  |  | 4
RI RED IRONBARK |  |  |  | 4 |  |  | 4
BB BLACKBUTT | 1 |  | 1 | 1 | 1 |  | 4
GI GREY IRONBARK |  | 1 |  | 1 |  |  | 2
GG GREY GUM |  |  |  |  | 1 |  | 1
RW RED BLOODWOOD |  |  |  | 1 |  |  | 1
RM RED MAHOGANY |  | 1 |  |  |  |  | 1
DS DARWIN STRINGYBAR |  |  |  | 1 |  |  | 1
GB GREY BOX |  |  |  |  | 1 |  | 1
NI NARROW LEAF RED I |  | 1 |  |  |  |  | 1
GM GYMPIE MESSMATE |  |  |  | 1 |  |  | 1
ZR UNKNOWN RED SPECI |  |  |  | 1 |  |  | 1
FR FOREST RED GUM |  |  |  | 1 |  |  | 1
HS HOLLOW/TUBULAR ST |  |  |  |  | 1 |  | 1
Grand Total | 10 | 21 | 14 | 40 | 12 | 5 | 102
Count of Failed equip | Column Labels
Row Labels | WESTERN | EASTERN/COASTAL | Grand Total
3 kiloNewton | 28.43% | 0.9804% | 29.41%
5 kiloNewton | 24.51% | 7.843% | 32.35%
8 kiloNewton | 17.65% | 5.882% | 23.53%
12 kiloNewton | 3.922% | 2.941% | 6.863%
20 kiloNewton | 0.9804% | 0% | 0.9804%
Unknown | 3.922% | 2.941% | 6.863%
Grand Total | 79.41% | 20.59% | 100%
Count of Failed equip | Column Labels
Row Labels | WESTERN | EASTERN/COASTAL | Grand Total
SWER inter | 46 | 1 | 47
Rrl inter spn <200m | 5 | 4 | 9
SWER sty term | 5 | 1 | 6
SWER sty angle | 5 |  | 5
HV fully suppd |  | 4 | 4
Rrl sty term 1 cct | 3 | 1 | 4
Rrl inter spn >200m | 4 |  | 4
Urb service pole | 2 | 1 | 3
Urb LV inter | 2 |  | 2
Urb unsty trm>=2cct | 2 |  | 2
66kV rrl inter | 1 |  | 1
Rrl unsty trm 1 cct |  | 1 | 1
Rrl inter 3 cct | 1 |  | 1
Bllrd unsty <=2 cct |  | 1 | 1
Streetlight only |  | 1 | 1
Light serv pole | 1 |  | 1
HV partly suppd |  | 1 | 1
Urb inter sub pole | 1 |  | 1
Rrl inter 2 cct |  | 1 | 1
Urb LV ABC inter |  | 1 | 1
Duplex SWER |  | 1 | 1
Rrl sty term 2 cct |  | 1 | 1
Urb sty term 1 cct | 1 |  | 1
Rrl inter sub pole | 1 |  | 1
66kV inter & 1 cct | 1 |  | 1
Rrl sty ang20-30o |  | 1 | 1
Grand Total | 81 | 21 | 102
Count of Failed equip | Column Labels
Row Labels | WESTERN | EASTERN/COASTAL | Grand Total
Paddock Grazing | 55 | 8 | 63
Road Reserve | 11 | 5 | 16
Footpath | 7 | 2 | 9
Paddock Crop | 2 | 2 | 4
Crop Harvester | 3 |  | 3
Sugar Cane |  | 3 | 3
Road | 1 |  | 1
Front Yard |  | 1 | 1
Backyard | 1 |  | 1
Inaccessible to heavy vehicles | 1 |  | 1
Grand Total | 81 | 21 | 102
Count of Failed equip | Column Labels
Row Labels | 3 kiloNewton | 5 kiloNewton | 8 kiloNewton | 12 kiloNewton | 20 kiloNewton | Unknown | Grand Total
WESTERN | 29 | 25 | 18 | 4 | 1 | 4 | 81
SWER inter | 23 | 14 | 8 |  |  | 1 | 46
SWER sty term |  | 2 | 2 |  |  | 1 | 5
SWER sty angle | 2 | 2 |  | 1 |  |  | 5
Rrl inter spn <200m | 1 | 1 | 2 |  |  | 1 | 5
Rrl inter spn >200m | 2 |  | 1 | 1 |  |  | 4
Rrl sty term 1 cct |  | 1 | 2 |  |  |  | 3
Urb service pole |  | 2 |  |  |  |  | 2
Urb unsty trm>=2cct |  |  | 2 |  |  |  | 2
Urb LV inter |  | 2 |  |  |  |  | 2
Urb inter sub pole | 1 | [5 empty] | 1
66kV inter & 1 cct |  | 1 |  |  |  |  | 1
Rrl inter 3 cct |  |  |  | 1 |  |  | 1
Urb sty term 1 cct |  |  |  | 1 |  |  | 1
66kV rrl inter |  |  |  |  | 1 |  | 1
Rrl inter sub pole |  |  | 1 |  |  |  | 1
Light serv pole | [5 empty] | 1 | 1
EASTERN/COASTAL | 1 | 8 | 6 | 3 |  | 3 | 21
HV fully suppd |  | 2 | 2 |  |  |  | 4
Rrl inter spn <200m |  | 2 | 1 | 1 |  |  | 4
Rrl unsty trm 1 cct |  |  |  | 1 |  |  | 1
Bllrd unsty <=2 cct | [5 empty] | 1 | 1
SWER inter |  | 1 |  |  |  |  | 1
HV partly suppd | [5 empty] | 1 | 1
Rrl sty term 2 cct |  |  | 1 |  |  |  | 1
Rrl inter 2 cct |  |  | 1 |  |  |  | 1
Streetlight only | [5 empty] | 1 | 1
SWER sty term |  |  |  | 1 |  |  | 1
Duplex SWER |  | 1 |  |  |  |  | 1
Urb LV ABC inter |  |  | 1 |  |  |  | 1
Urb service pole |  | 1 |  |  |  |  | 1
Rrl sty ang20-30o |  | 1 |  |  |  |  | 1
Rrl sty term 1 cct | 1 | [5 empty] | 1
Grand Total | 30 | 33 | 24 | 7 | 1 | 7 | 102

## Unassisted Pole Failures
DSTRCT_CODE | WORK_ORDER | WO_TYPE_DESCRIPTION | WO_DESC | RAISED_DATE | YYYY-MM | CLOSED_DT | COMP_CODE_DESCRIPTION | MSSS_OBJECT_FAILURE_DESCRIPTION | MSSS_DAMAGE_APPARENT_CAUSE_DESCRIPTION | MSSS_CAUSE_DESCRIPTION | CONSEQUENCE_DESCRIPTION | VOLTAGE_DESCRIPTION | WORK_ORDER_EXTENDED_DESCRIPTION | COMPLETION_COMMENTS | COMPLETED_BY_DESC | EQUIP_NO | FISCAL_YEAR | OUTAGE_NAME | OUTAGE_DATE | END_DATE | MSS_MAJOR_EVENT_DAY_EVENT_CODE | STPIS_MAJOR_EVENT_DAY_EVENT_CODE | OUTAGE_EXEMPTION_DESCRIPTION | OUTAGE_WEATHER_DESCRIPTION | SUB_REGION_NAME | OUTAGE_ACTUAL_START_TIMESTAMP | OUTAGE_CREATED_DATE_TIMESTAMP | OUTAGE_STATUS_DESCRIPTION | OUTAGE_TYPE_DESCRIPTION | OUTAGE_TRIGGER_DESCRIPTION | OUTAGE_STANDARD_REASON_DESCRIPTION | OUTAGE_REASON_DESCRIPTION | OUTAGE_PRIMARY_ASSET_HIER_TYPE_ID | DEFECT_CAUSE_DESCRIPTION | OUTAGE_DESCRIPTION | OUTAGE_COMMENTARY | OUTAGE_LOG_DETAILS | RNUM | EQUIP_2 | ITEM_NAME_1 | PARENT_EQUIP | PARENT_ITEM_NAME_1 | EQUIPMENT NUMBER | DATE_LAST_INSPECTED | FAULT_INDICATOR_FITTED | INSPECTED_BY | INSPECTION_CONTRACTOR | LENGTH_OF_POLE | NUMBER_OF_HV_ARMS | NUMBER_OF_LV_ARMS | POLE_CONDITION_DESCRIPTION | POLE_EARTH | POLE_STRUCTURE_TYPE_DESCRIPTION | POLE_CHEMICAL_TREATMENT_DESCRIPTION | POLE_SITE_CHARACTERISTICS_DESCRIPTION | UNDERGROUND_SITE_ENVIRONMENT_DESCRIPTION | SPECIES_DESCRIPTION | STRENGTH_DESCRIPTION | DSTRCT_CODE2 | EQUIPMENT_NUMBER | EQUIPMENT_CLASS | CALC_STRENGTH | EXTERNAL_DECAY | FINAL_SECTION_MOD | INSPECTION_HOLE_A | INSPECTION_HOLE_B | INSPECTION_HOLE_C | INSPECTION_HOLE_D | INSPECTION_HOLE_E | INSPECTION_HOLE_F | INSPECTION_HOLE_G | INSPECTION_HOLE_H | LOCATION_WEAKEST_POINT | MAX_DEPTH_SURFACE_ROT | MAX_EFFECTIVE_DIAMETER | MIN_DEPTH_SURFACE_ROT | POLE_CALC_CONSTRUCTION | POLE_DIAMETER | POLE_GIRTH | POLE_STRUCTURE | SOUND_WOOD_1_METER | SOUND_WOOD_STAKES | SOUND_WOOD_GL | SUM_WIDTH_SPLITS | LAT | LON | INFERRED_YOM | Plant number | Failed equip | YOM Grouping | Location
EECL | OT189746 | Operational |  | 2023-07-20 | 202307 | 2024-01-30 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay | 0 | 19kV |  |  |  | 1149526 | 2024 | 23SW9699 | 2023-07-20 | 2023-07-20 13:41 |  |  | Normal Event |  | South West | 2023-07-20 09:32 | 2023-07-20 09:35 | Completed | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FC |  | YOWAH: BLUE BONNET BVD, BLUFF RD, BOOBIALLA ST, BOUGANVILLEA ST, GIDYEA CL, HARLEQUIN DR, MATRIX DR, WHITEWOOD DR, WREN LANE | 19.1kV SWER Recloser CB596838. Opened on WGL request due to lines down call crews have confirmed that a pole is on the ground Crew stood temporary pole. SL 3148918. REDACTED | 19.1kV SWER Recloser CB596838. Opened on WGL request due to lines down call Crew have advised there is a pole down at 3148919 HV Wires Down Pole/s Down Sending Asset Event to FFA FFA Order Created F-AE23SW9699-1-0 DfltHost cuncmfr03 - REDACTED Sending Asset Event to FFA Fault Call 2352568 Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW9699-1-0 cuncmfr03 REDACTED FFA Order En Route F-AE23SW9699-1-0 cuncmfr03 FFA Order On Site F-AE23SW9699-1-0 cuncmfr03 Restoration Comments for F-AE23SW9699-1-0 by cuncmfr03: temporary pole stood at s/l 3148918 FFA Order F-AE23SW9699-1-0 Completed by technician REDACTED with code A-F-C - Completed Action Taken : temporary pole stood Site Label : 3148918 Crew confirmed made safe form 17 completed Time On modified from 23:59 20-Jul to 13:41 20-Jul Added notes to Reasons tab. | 1 | 2030928 | 10 NW CB6862 11150 Bulloo Dev' Rd Yowah | 1149526 | 3148918 | 2030928 | 2021-09-08 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Rock | Paddock Grazing | GG GREY GUM | 3 kiloNewton | EECL | 2030928 | PO | 9.987 | 0 | 1181.8103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 6 | 0 | 720 | 16 | 0 | 0 | 115 | 0 | -28.0759 | 144.6217 | 1991 | PO3148918 | 000002030928 | 1990s | WESTERN
EECL | OT188621 | Operational |  | 2023-07-08 | 202307 | 2023-07-09 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay External | 0 | 11kV |  |  |  | 1011179 | 2024 | 23CA8180 | 2023-07-08 | 2023-07-09 14:52 |  |  | Normal Event | Fine | Capricornia | 2023-07-08 14:34 | 2023-07-08 15:21 | Completed | Unplanned Outage | HV-Conductor Connection Failure | Fallen Power Lines | due to fallen power lines. | FC |  | CALLIOPE: RIVERVIEW DR | Crew require HV access to 11kV Load Break AB X1044 to repair broken HV conductor load side of X595276. F-1627-q | Crew require HV access to 11kV Load Break AB X1044 to repair broken HV conductor load side of X595276. HV Wires Down F-1627-q Sending Asset Event to FFA FFA Order Created F-AE23CA8180-1-0 DfltHost Time On modified from 23:59 08-Jul to 21:00 08-Jul Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Crew will return to replace pole at 8am on the 09/07/23 Time On modified from 21:00 08-Jul to 23:59 09-Jul Sending Asset Event to FFA Time On modified from 23:59 09-Jul to 14:00 09-Jul Sending Asset Event to FFA Time On modified from 14:00 09-Jul to 15:00 09-Jul Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA8180-1-0 pcoc01 REDACTED FFA Order En Route F-AE23CA8180-1-0 pcoc01 FFA Order On Site F-AE23CA8180-1-0 pcoc01 FFA Order F-AE23CA8180-1-0 Completed by technician REDACTED with code A-T-304 - HV-Conductor Connection Failure Action Taken : replaced pole due to splitting and conductor coming to ground Site Label : 2149318 Time On modified from 15:00 09-Jul to 14:52 09-Jul | 1 | 9292917 | 3p/w of sub152961 riverview dr CALLIOPE | 1011179 | 2149318 | 9292917 | 2022-05-18 |  |  | 0 | 11 | 2 | 0 | Serviceable | N | Rrl sty ang20-30o | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | EECL | 9292917 | PO | 22.253 | 0 | 2874.3491 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 10 | 0 | 969 | 26 | 0 | 0 | 154 | 0 | -23.9845 | 151.1508 | 1986 | PO2149318 | 000002336763 | 1980s | EASTERN/COASTAL
EECL | OT188078 | Operational |  | 2023-07-04 | 202307 | 2023-07-04 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay External | 0 | 19kV |  |  |  | 1076729 | 2024 | 23SW9086 | 2023-07-04 | 2023-07-04 14:20 |  |  | Normal Event | Storm | South West | 2023-07-04 05:39 | 2023-07-04 09:28 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | QUILPIE: DIAMANTINA DEVELOPMENTAL RD, KEEROONGOOLOO RD WINDORAH: HAMMOND DOWNS RD | 19.1kV SWER Recloser CB7113 - found OPEN by crew (Comm's Failure) FFA Order F-AE23SW9086-1-0 Completed by technician REDACTED in crew REDACTED with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Pole unassisted pole failure. DL8123 top of pole has snapped off causing HV wires to go to ground. Wires were taken off pole, spliced together and Temporary pole has been stood. DL8123 is currently not operational and is obviously by-passed till access to borer to stand new Disk Link Pole. Site Label : 3089379 | 19.1kV SWER Recloser CB7113 - found OPEN by crew (Comm's Failure) Sending Asset Event to FFA FFA Order Created F-AE23SW9086-1-0 DfltHost Manual Reclose Checklist Sending Asset Event to FFA clearance given to reclose CB7113 (No Comms) @1100 after sectionalising Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA sectionalised upto DL585360 @ 1100 Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 04-Jul to 14:20 04-Jul Sending Asset Event to FFA DSO Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW9086-1-0 quloc02 REDACTED FFA Order En Route F-AE23SW9086-1-0 quloc02 FFA Order On Site F-AE23SW9086-1-0 quloc02 FFA Order F-AE23SW9086-1-0 Completed by technician REDACTED with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Pole unassisted pole failure. DL8123 top of pole has snapped off causing HV wires to go to ground. Wires were taken off pole, spliced together and Temporary pole has been stood. DL8123 is currently not operational and is obviously by-passed till access to borer to stand new Disk Link Pole. Site Label : 3089379 Reason for Event changed from Unknown | 1 | 2931635 | DL8123 via 191 Hammond Dwns Rd Windora | 1076729 | 3089379 | 2931635 | 2021-04-28 | N |  | 0 | 14 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | SG SPOTTED GUM | 3 kiloNewton | EECL | 2931635 | PO | 8.34 | 0 | 1389.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 9 | 0 | 760 | 16 | 0 | 0 | 121 | 0 | -25.3928 | 142.828 | 1993 | PO3089379 | 000002931635 | 1990s | WESTERN
EECL | OT192808 | Operational |  | 2023-08-20 | 202308 | 2023-08-20 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | 0 | 12.7kV |  |  |  | 1191416 | 2024 | 23SW16258 | 2023-08-20 | 2023-08-20 15:17 |  |  | Normal Event |  | South West | 2023-08-20 10:32 | 2023-08-20 10:16 | Completed | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | WANDOAN: BUNDI RD, L RD, MCALLISTERS RD, MOUNT ORGAN RD | Crew advise SWER pole snapped at SL - 3131626, crew require access from 12.7kV SWER Recloser CB7240 | Crew advise SWER pole snapped at SL - 3131626, crew require access from 12.7kV SWER Recloser CB7240 HV Wires Down REDACTED, wndoc01. Switching Sheet ID updated from to J-272934-g. Sending Asset Event to FFA FFA Order Created F-AE23SW16258-1-0 DfltHost FFA Order Acknowledged F-AE23SW16258-1-0 wndoc01 REDACTED 0429848619 Sending Asset Event to FFA Time Off modified from 10:30 20-Aug to 10:32 20-Aug Sending Asset Event to FFA FFA Order En Route F-AE23SW16258-1-0 wndoc01 FFA Order On Site F-AE23SW16258-1-0 wndoc01 Time On modified from 15:00 20-Aug to 17:00 20-Aug Sending Asset Event to FFA Time On modified from 17:00 20-Aug to 15:17 20-Aug Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23SW16258-1-0 Completed by technician REDACTED with code A-F-C - Completed Action Taken : Ergon crew found pole had snapped off 1m down from top of pole Site Label : 3131626 | 1 | 9305389 | 2 Sth Grosmont Rd on L Rd Wondoan | 1191416 | 3131626 | 9305389 | 2020-08-25 |  |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 3 kiloNewton | EECL | 9305389 | PO | 10.634 | 0 | 1572.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -130 | 0 | 252 | 0 | 10 | 0 | 792 | 16 | 0 | 0 | 126 | 0 | -26.0841 | 149.8037 | 1981 | PO3131626 | 000003142289 | 1980s | WESTERN
EECL | OT194761 | Operational |  | 2023-09-07 | 202309 | 2023-09-08 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | 0 | 22kV |  |  |  | 1557977 | 2024 | 23CA13126 | 2023-09-07 | 2023-09-07 12:46 |  |  | Normal Event | Fine | Capricornia | 2023-09-07 02:57 | 2023-09-07 03:00 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FE |  | ANAKIE, CAPELLA, EMERALD, RUBYVALE, SAPPHIRE, SAPPHIRE CENTRAL, SPRINGSURE, THE GEMFIELDS, WILLOWS GEMFIELDS | EMERALD 22kV Ruby-Cape Fdr CB S256 tripped. SCADA Interface automated outage. Pole snapped with wires still in the air - Crew replaced HV strain with tee off pole. SL 4010485. REDACTED | entered from the SCADA Interface OCEF Trip to lockout F-1810-q. MR to be attempted Depot Co-ord Advised emlcs03 Sending Asset Event to FFA FFA Order Created F-AE23CA13126-1-0 DfltHost unable to to back feed as RC879588 comms is failed Sending Asset Event to FFA Sectionalising upto X614310 Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA13126-1-0 emlcs03 REDACTED FFA Order En Route F-AE23CA13126-1-0 emlcs03 FFA Order On Site F-AE23CA13126-1-0 emlcs03 pole 4010485 snapped with wires still in the air Time On modified from 23:59 07-Sep to 16:00 07-Sep Pole/s Down Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 16:00 07-Sep to 12:46 07-Sep Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA13126-1-0 emlll01 REDACTED FFA Order En Route F-AE23CA13126-1-0 emlll01 FFA Order On Site F-AE23CA13126-1-0 emlll01 FFA Order F-AE23CA13126-1-0 Completed by technician REDACTEDwith code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Replaced 14/8 HV strain with tee off pole with 14/12 HV strain with tee off. Site Label : 4010485 Updated Reasons tab. Reason for Event changed from Unknown | 1 | 9320600 | 1 SW of 26794 Capricorn Hwy Emerald | 1557977 | 4010485 | 9320600 | 2022-01-24 |  |  | 0 | 12.5 | 2 | 0 | Serviceable | N | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | ZZ NO DISC - UNKNOWN | 8 kiloNewton | EECL | 9320600 | PO | 0 | 10 | 1925.2742 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -85 | 15 | 271 | 5 | 7 | 0 | 915 | 28 | 0 | 0 | 100 | 0 | -23.5265 | 148.1388 | 1990 | PO4010485 | 000002449897 | 1990s | WESTERN
EECL | OT197332 | Operational |  | 2023-09-30 | 202309 | 2023-09-30 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | 0 | 11kV |  |  |  | 1102944 | 2024 | 23WB13094 | 2023-09-30 | 2023-09-30 12:25 |  |  | Normal Event | Fine | Wide Bay | 2023-09-30 04:40 | 2023-09-30 15:33 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | 143 GASTONS RD;BULLYARD QLD 4671 | Fault occurred at:30/09/2023 04:37; REDACTED; >SPARKS --> SparksLocation:Wires: Pole to Pole -- SparksDimFlickering:NO<; Incident Details:loud explosions and sparks from lines going through property. Supply went off briefly but back on now.; Warnings[sparksSafety]: ADVISED |  | 1 | 9322138 | 143 Gastons Rd Bullyard | 1102944 | ... | 9322138 | 2019-04-16 | N |  | 0 | 12.5 | 2 | 2 | Serviceable | N | Rrl sty term 2 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | EECL | 9322138 | PO | 21.04 | 0 | 3112.1759 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 10 | 0 | 995 | 36 | 0 | 0 | 158 | 0 | -24.9449 | 152.0802 | 1991 | PO3026498 | 000002633641 | 1990s | EASTERN/COASTAL
EECL | OT199501 | Operational |  | 2023-10-18 | 202310 | 2023-10-27 | Pole-Wood | Wood Pole Beyond 2m | Broken | Termites | 0 | 19kV |  |  |  | 1170153 | 2024 | 23FN13857 | 2023-10-18 | 2023-10-19 10:21 |  |  | Normal Event | Hot | Far North | 2023-10-18 13:44 | 2023-10-18 13:47 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to a SCADA Automated Event | FC |  | GEORGETOWN: ABINGDON RD | GEORGETOWN 19kV Ironhurst IH3R ACR CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface IH3R tripped to lockout OC F-2086-s GRTCS02 Sending Asset Event to FFA FFA Order Created F-AE23FN13857-1-0 DfltHost REDACTED Sending Asset Event to FFA Crew advised that there is a fire in the area. Pole has been burnt down at IH.86. Crews to isolate at Reg IH54 load and bypass Sending Asset Event to FFA HV Wires Down Pole/s Down Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN13857-1-0 grtcsfr03 REDACTED FFA Order En Route F-AE23FN13857-1-0 grtcsfr03 FFA Order On Site F-AE23FN13857-1-0 grtcsfr03 Customers Back on upto Reg IH.54 Asset selection modified Sending Asset Event to FFA Crews will attend in the morning to make repairs Time On modified from 23:59 18-Oct to 23:59 19-Oct Sending Asset Event to FFA Sending Asset Event to FFA reversing switching Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 19-Oct to 12:00 19-Oct Sending Asset Event to FFA Time On modified from 12:00 19-Oct to 10:21 19-Oct Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23FN13857-1-0 grtcsfr03 FFA Order On Site F-AE23FN13857-1-0 grtcsfr03 FFA Order F-AE23FN13857-1-0 Completed by technician REDACTED with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : Pole failed due to bad termite damage. Site Label : 5085213 | 1 | 9330972 | 1spns NE ironhurst stn georgetown | 1170153 | IH86 | 9330972 | 2019-06-02 |  |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | RW RED BLOODWOOD | 8 kiloNewton | EECL | 9330972 | PO | 22.283 | 0 | 4056.5648 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 9 | 0 | 1100 | 16 | 0 | 0 | 100 | 0 | -18.2226 | 143.0539 | 1982 | PO5085231 | 000002913072 | 1980s | WESTERN
EECL | OT199758 | Operational |  | 2023-10-20 | 202310 | 2023-10-21 | Pole-Wood | Wood Pole Below Ground | No Damage | Termites | 0 | 11kV |  |  |  | 1642407 | 2024 | 23SW18638 | 2023-10-21 | 2023-10-21 15:30 |  |  | Normal Event |  | South West | 2023-10-21 07:48 | 2023-10-20 19:07 | Completed | Forced Outage |  | Lines Emergency Maintenance | to allow maintenance of the electricity network | SZ |  | CHARLEVILLE | Partridge Street 11kV Feeder Feeder Section from load side of 11kV Disc Links DL604937 and DO604938 1 Margret St Charleville Work/Test Details: Emergency Repair of failed TX Pole PW02256 | via package wizard Switching Sheet ID updated from to J-282141-g. Time Off modified from 06:00 21-Oct to 07:48 21-Oct Sending Asset Event to FFA FFA Order Created F-AE23SW18638-1-0 DfltHost FFA Order Acknowledged F-AE23SW18638-1-0 chrcdwgl1 REDACTED FFA Order En Route F-AE23SW18638-1-0 chrcdwgl1 FFA Order On Site F-AE23SW18638-1-0 chrcdwgl1 Restoration Comments for F-AE23SW18638-1-0 by chrcdwgl1: continued working Time On modified from 14:00 21-Oct to 15:00 21-Oct Sending Asset Event to FFA Time On modified from 15:00 21-Oct to 16:00 21-Oct Sending Asset Event to FFA Time On modified from 16:00 21-Oct to 15:30 21-Oct Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23SW18638-1-0 Completed by technician REDACTED with code A-F-C - Completed Action Taken : replaced TX pole Site Label : 3202754 | 1 | 9350766 | PW2256 1 Margret st Charleville | 1642407 | 3202754 | 9350766 | 2021-08-06 |  |  | 0 | 11 | 1 | 1 | Serviceable | Y | Urb inter sub pole | WOOD UNTREATED ROUND | Grass | Road Reserve | NI NARROW LEAF RED I | 3 kiloNewton | EECL | 9350766 | PO | 65.354 | 0 | 8441.6075 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -50 | 0 | 457 | 0 | 9 | 0 | 1437 | 4 | 0 | 0 | 100 | 0 | -26.4118 | 146.2409 | 1963 | PO3202754 | 000002350743 | 1960s | WESTERN
EECL | OT200544 | Operational |  | 2023-10-26 | 202310 | 2023-10-27 | Pole-Wood | Wood Pole Beyond 2m | Broken | Termites | 0 | 19kV |  |  |  | 934575 | 2024 | 23NQ12755 | 2023-10-26 | 2023-10-27 13:50 |  |  | Normal Event | Fine | North Queensland | 2023-10-26 11:17 | 2023-10-26 14:05 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Protective Device Operated | due to the operating of protective equipment. | FC |  | PRAIRIE: KOOROOINYA RACE COURSE, LAMMERMOOR STATION, VENTCHER STATION | F-28560-g Lammermoore No. 1 has opened due to fault downstream. | F-28560-g Lammermoore No. 1 has opened due to fault downstream. Issued to REDACTED Sending Asset Event to FFA FFA Order Created F-AE23NQ12755-1-0 DfltHost Pole 5022043 has fallen over crews isolating via LL clamps on pole 5022042 towards hus299. Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ12755-1-0 huhcmfr01 HV Wires Down Pole/s Down Sending Asset Event to FFA FFA Order En Route F-AE23NQ12755-1-0 huhcmfr01 FFA Order On Site F-AE23NQ12755-1-0 huhcmfr01 Restoration Comments for F-AE23NQ12755-1-0 by huhcmfr01: site made safe by isolating and earthing Restoration Comments for F-AE23NQ12755-1-0 by huhcmfr01: site made safe by isolating and earthing Asset selection reset Asset selection modified Sending Asset Event to FFA Crew advised Pole Dist Sub HUS299 is beyond 19.1kV SWER Recloser LAMMERMOORE NO.1. Crews have isolated and earthed at LL Clamps Pole 5022042 towards HUS299. All customers except HUS299 restored @ 1500. Crew are returning tomorrow morning 27/10/2023 to replace fallen pole. Asset selection modified Time On modified from 23:59 26-Oct to 13:00 27-Oct Sending Asset Event to FFA Sending Asset Event to FFA Outage area extended to remake broken bridge. Asset selection modified Sending Asset Event to FFA Replay sequence time changed from 27-OCT-23 12:05:09 to 27-Oct-23 12:01:00 Reason for Event changed from Unknown Sending Asset Event to FFA Time On modified from 13:00 27-Oct to 14:00 27-Oct Sending Asset Event to FFA Lammermoore No.1 Closed Asset selection modified Sending Asset Event to FFA Supply Restored Time On modified from 14:00 27-Oct to 13:50 27-Oct Sending Asset Event to FFA FFA Order F-AE23NQ12755-1-0 Completed by technician REDACTED with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced tx pole and tx and restored supply Site Label : 5022043 | 1 | 9331204 | (bore pump) Ashton Station | 934575 | 5022043 | 9331204 | 2019-10-21 |  |  | 0 | 12.5 | 0 | 0 | Serviceable | Y | SWER sty term | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | RI RED IRONBARK | 5 kiloNewton | EECL | 9331204 | PO | 14.727 | 0 | 2178.345 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -100 | 0 | 285 | 0 | 13 | 0 | 910 | 18 | 0 | 0 | 100 | 15 | -21.2305 | 144.6812 | 1980 | PO5022043 | 000002566538 | 1980s | WESTERN
EECL | OT201360 | Operational |  | 2023-10-31 | 202310 | 2023-11-02 | Pole-Wood | Wood Pole Beyond 2m | Broken | Termites | 0 | 19kV |  |  |  | 1212272 | 2024 | 23FN14249 | 2023-10-31 | 2023-11-01 15:28 |  |  | Normal Event | Fine | Far North | 2023-10-31 18:23 | 2023-10-31 18:26 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to a SCADA Automated Event | FC |  | N/A | F-2160-s NORMANTON 19kV AugustsDwnLO107 ACR CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface REDACTEDadvised will get chopper patrol in the morning . REDACTED advised will get chopper patrol in the morning Time On modified from 23:59 31-Oct to 23:59 01-Nov Sending Asset Event to FFA FFA Order Created F-AE23FN14249-1-0 DfltHost Crews boarding chopper to patrol. Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN14249-1-0 nrmoc01 REDACTED FFA Order En Route F-AE23FN14249-1-0 nrmoc01 FFA Order On Site F-AE23FN14249-1-0 nrmoc01 Time On modified from 23:59 01-Nov to 15:28 01-Nov Manual Reclose Checklist Sending Asset Event to FFA Restoration Comments for F-AE23FN14249-1-0 by nrmoc01: isolated and earthed approx 1100 Sending Asset Event to FFA FFA Order F-AE23FN14249-1-0 Completed by technician REDACTED with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : replaced swer pin pole LO219 Site Label : 5258034 | 1 | 9331729 | 2 poles nth augustus/nardoo boundary | 1212272 | LO219 | 9331729 | 2018-08-10 |  |  | 0 | 14 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | RI RED IRONBARK | 8 kiloNewton | EECL | 9331729 | PO | 0 | 0 | 4869.9265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 6 | 0 | 1155 | 16 | 0 | 0 | 184 | 0 | -18.719 | 139.8434 | 1989 | PO5258034 | 000003440680 | 1980s | WESTERN
EECL | OT201961 | Operational |  | 2023-11-04 | 202311 | 2023-11-05 | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay External | 0 | 19kV |  |  |  | 756443 | 2024 | 23CA15342 | 2023-11-04 | 2023-11-05 14:02 |  |  | Normal Event | Storm Electrical | Capricornia | 2023-11-04 18:08 | 2023-11-04 19:34 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to damage requiring emergency repairs. Fault finding is in progress. | SZ |  | CLERMONT: BARRYLAR RD, FLEURS RD, MOUNT DONALD RD, NEW CORRY RD, PEAK DOWNS HWY, WOLFANG ACCESS RD WOLFANG: BETOOTA RD, WOLFANG ACCESS RD | X8452 is in bypass , Calls suggest 19.1kV SWER Recloser X8452 has opened Pole down at site 2093833 | X8452 is in bypass , Calls suggest 19.1kV SWER Recloser X8452 has opened clmcm03 Sending Asset Event to FFA FFA Order Created F-AE23CA15342-1-0 DfltHost Manual Reclose Checklist Sending Asset Event to FFA MRC failed crew to helli patrol in the AM Sending Asset Event to FFA Time On modified from 23:59 04-Nov to 23:59 05-Nov Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA15342-1-0 clmfr01 REDACTED FFA Order En Route F-AE23CA15342-1-0 clmfr01 Sending Asset Event to FFA Pole down at site 2093833 Sending Asset Event to FFA Pole/s Down Sending Asset Event to FFA FFA Order On Site F-AE23CA15342-1-0 clmfr01 Time On modified from 23:59 05-Nov to 14:02 05-Nov Sending Asset Event to FFA FFA Order En Route F-AE23CA15342-1-0 clmfr01 FFA Order On Site F-AE23CA15342-1-0 clmfr01 FFA Order F-AE23CA15342-1-0 Completed by technician REDACTED with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : pole failure at ground level. Pole was defected by inspectors and due to be changed in the coming weeks. stood temp pole and re energised Site Label : 2093873 | 1 | 2227750 | 1 W SP338100 1158 Wolfang Acc Rd C'mont | 756443 | 2093873 | 2227750 | 2023-04-02 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD UNTREATED DRESSED | Grass | Crop Harvester | ZZ NO DISC - UNKNOWN | 8 kiloNewton | EECL | 2227750 | PO | 17.349 | 5 | 2566.2456 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -80 | 8 | 299 | 2 | 6 | 0 | 970 | 16 | 0 | 0 | 95 | 0 | -22.6799 | 147.8063 | 1952 | PO2093873 | 000002227750 | 1950s | WESTERN
EECL | OT202168 | Operational |  | 2023-11-05 | 202311 | 2023-11-07 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay External | 0 | 12.7kV |  |  |  | 1978609 | 2024 | 23SW19594 | 2023-11-05 | 2023-11-06 18:10 |  |  | Normal Event | Storm Electrical | South West | 2023-11-05 19:52 | 2023-11-05 19:56 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Lightning / Storm | due to damage caused by storm activity. | FC |  | ROMA, SURAT, WALLUMBILLA, WALLUMBILLA SOUTH | F-1154-r ROMA 12kV Sut Grnge CB773263 ACR CB tripped. SCADA Interface automated outage. Crew replaced broken pin pole. SL 3103388. REDACTED | entered from the SCADA Interface OC trip Crews out of hours, will fly line first in morning. Crew to call for dispatch Time On modified from 23:59 05-Nov to 23:59 06-Nov Depot Co-ord Advised . Please send to ROMCM700. Sending Asset Event to FFA FFA Order Created F-AE23SW19594-1-0 DfltHost FFA Order Acknowledged F-AE23SW19594-1-0 romcm700 REDACTED 0427485694 FFA Order En Route F-AE23SW19594-1-0 romcm700 Lines down Beyond DL6392. Chopper Crew to isolate and Earth. OCC to energise ACR CB773263 Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Please dispatch to romcm709 Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW19594-1-0 romcm709 REDACTED FFA Order En Route F-AE23SW19594-1-0 romcm709 FFA Order On Site F-AE23SW19594-1-0 romcm709 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 06-Nov to 18:10 06-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23SW19594-1-0 Completed by technician REDACTED with code A-T-317 - Severe Weather Action Taken : replaced broken pin pole Site Label : 3103388 Updated Reasons tab. Updated Event Trigger from Lightning to HV-Unassisted failure. Reason for Event changed from Unknown | 1 | 9335022 | btwn 1415-2034 Dunkeld rd Roma | 1978609 | 3103388 | 9335022 | 2020-01-23 |  |  | 0 | 11 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 9335022 | PO | 5.015 | 0 | 647.7709 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | 0 | 188 | 0 | 6 | 0 | 590 | 16 | 0 | 0 | 100 | 0 | -26.9603 | 148.8183 | 1969 | PO3103388 | 000003004372 | 1960s | WESTERN
EECL | OT203393 | Operational |  | 2023-11-13 | 202311 | 2023-11-13 | Pole-Wood | Wood Pole Up To 2m | Broken | Termites | 0 | 22kV |  |  |  | 1200342 | 2024 | 23FN14668 | 2023-11-13 | 2023-11-13 17:35 |  |  | Normal Event |  | Far North | 2023-11-13 13:01 | 2023-11-13 13:11 | Completed | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | KARUMBA | F-2236-s Feeder Tripped for Safety after Report from Farmer of Low Wires and Dead Cattle Crew replaced pole KW58. SL 5159056. REDACTED | Feeder Tripped for Safety after Report from Farmer of Low Wires and Dead Cattle F-2236-s Issued to REDACTED, nrmcsfr01. Sending Asset Event to FFA FFA Order Created F-AE23FN14668-1-0 DfltHost FFA Order Acknowledged F-AE23FN14668-1-0 nrmcsfr01 REDACTED FFA Order En Route F-AE23FN14668-1-0 nrmcsfr01 FFA Order On Site F-AE23FN14668-1-0 nrmcsfr01 Restoration Comments for F-AE23FN14668-1-0 by nrmcsfr01: replace pole kw58 in progress Time On modified from 23:59 13-Nov to 17:35 13-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23FN14668-1-0 Completed by technician REDACTED with code A-F-C - Completed Action Taken : replaced pole kw58 on the Karumba line Site Label : 5159056 Added notes to Reasons tab. | 1 | 9343412 | 37 spn past ss10862 pipeline rd Normanto | 1200342 | KW58 | 9343412 | 2021-06-21 |  |  | 0 | 15.5 | 1 | 0 | Serviceable | Y | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Soil | Road Reserve | WS WHITE STRINGYBARK | 8 kiloNewton | EECL | 9343412 | PO | 15.293 | 0 | 3489.8772 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -100 | 0 | 344 | 0 | 6 | 0 | 1080 | 22 | 0 | 0 | 70 | 0 | -17.6758 | 140.9807 | 1986 | PO5159056 | 000003274438 | 1980s | EASTERN/COASTAL
EECL | OT204075 | Operational |  | 2023-11-17 | 202311 | 2023-11-19 | Pole-Wood | Wood Pole Below Ground | Broken | Termites | 0 | 19kV |  |  |  | 1928808 | 2024 | 23NQ13636 | 2023-11-17 | 2023-11-19 10:15 |  |  | Normal Event | Wind | North Queensland | 2023-11-17 17:45 | 2023-11-17 17:52 | Completed | Unplanned Outage | Animal Insects (termites/borers/white ants) | Protective Device Operated | due to the operating of protective equipment. | FC |  | HUGHENDEN, MUTTABURRA, PRAIRIE | F-2255-s OC x 4 to lockout | OC x 4 to lockout see F-2255-s. Dispatch crew please Time Off modified from 17:48 17-Nov to 17:45 17-Nov Sending Asset Event to FFA FFA Order Created F-AE23NQ13636-1-0 DfltHost Sending Asset Event to FFA Crew attending REDACTED Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ13636-1-0 huhcdwgl1 REDACTED FFA Order En Route F-AE23NQ13636-1-0 huhcdwgl1 CXrew advised will fly line Saturday Morning Sending Asset Event to FFA Time On modified from 23:59 17-Nov to 23:59 18-Nov Sending Asset Event to FFA Sending Asset Event to FFA Crew patrolled up to Waterview Sec No.1 - no fault found Sending Asset Event to FFA Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA Crew found pole down towards HUS359 Pole/s Down Sending Asset Event to FFA Crew will return to complete repairs on the 19/11/2023 Time On modified from 23:59 18-Nov to 15:00 19-Nov Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 15:00 19-Nov to 10:15 19-Nov Sending Asset Event to FFA FFA Order En Route F-AE23NQ13636-1-0 huhcdwgl1 FFA Order On Site F-AE23NQ13636-1-0 huhcdwgl1 FFA Order F-AE23NQ13636-1-0 Completed by technician REDACTED with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : replace pole due to termites and high winds Site Label : 5234433 | 1 | 9350758 | 3pNW homestead sub eastfield stn MB | 1928808 | 5234433 | 9350758 | 2023-09-06 |  |  | 0 | 12.5 | 0 | 0 | Unserviceable - P2 | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 9350758 | PO | 5.72 | 5 | 846.1134 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | -40 | 8 | 248 | 2 | 6 | 0 | 810 | 16 | 0 | 0 | 24 | 0 | -22.0742 | 144.7365 | 1982 | PO5234433 | 000003414163 | 1980s | WESTERN
EECL | OT205003 | Operational |  | 2023-11-23 | 202311 |  | Pole-Wood | Wood Pole Beyond 2m | Broken | Unknown - Wind | 0 | 19kV |  |  |  | 1256298 | 2024 | 23SW20617 | 2023-11-23 | 2024-01-05 14:19 |  |  | Normal Event | Storm Electrical | South West | 2023-11-23 10:19 | 2023-11-23 10:22 | Completed | Unplanned Outage | Lightning | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | CHARLEVILLE, CUNNAMULLA, WYANDRA | F-1288-r - CUNNAMULLA 22kV Wyandra RC822709 ACR CB tripped. SCADA Interface automated outage. Transformer pole replaced REDACTED | entered from the SCADA Interface 22kV Recloser RC822709 - Tripped on EF WGL ADVISED - Chasing a chopper for a line patrol Depot Co-ord Advised chrcmfr01 Sending Asset Event to FFA FFA Order Created F-AE23SW20617-1-0 DfltHost Removing Asset Event from FFA FFA Order cancelled.F-AE23SW20617-1-0 chrcmfr03 Sending Asset Event to FFA FFA Order Created F-AE23SW20617-1-1 DfltHost FFA Order Acknowledged F-AE23SW20617-1-1 chrcmfr03 REDACTED FFA Order En Route F-AE23SW20617-1-1 chrcmfr03 Chopper has found PW03115 burnt to the ground, crew leaving Cunnamulla now CUNCMFR03 Sending Asset Event to FFA Sending Asset Event to FFA Restored up to 22kV Disc Links DL6930 at 1517. Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 23-Nov to 23:59 24-Nov Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW20617-1-1 cuncmfr03 REDACTED FFA Order En Route F-AE23SW20617-1-1 cuncmfr03 FFA Order On Site F-AE23SW20617-1-1 cuncmfr03 The section that is isolated and earthed has zero cust. Sending Asset Event to FFA Time On modified from 23:59 24-Nov to 23:59 01-Dec Sending Asset Event to FFA FFA Order En Route F-AE23SW20617-1-1 cuncmfr03 FFA Order On Site F-AE23SW20617-1-1 cuncmfr03 FFA Order F-AE23SW20617-1-1 Completed by technician REDACTED with code A-T-62 - Lightning Action Taken : Tx pole to change Site Label : 6010234 Time On modified from 23:59 01-Dec to 23:59 08-Dec Time On modified from 23:59 08-Dec to 23:59 15-Dec Country wet again ,no access to heavy vehicles please extend out to 25/1/23, no LOS to customers Time On modified from 23:59 15-Dec to 23:59 25-Jan Time On modified from 23:59 25-Jan to 12:00 25-Jan Time On modified from 12:00 25-Jan to 14:19 05-Jan Updated Reasons tab. Updated Event Trigger from Transmission to Distribution. Reason for Event changed from Unknown | 1 | 2981014 | PW3273, 1153 Western Warrego Rd Wyandra | 1256298 | 6010234 | 2981014 | 2023-06-14 | N |  | 0 | 12.5 | 4 | 0 | Serviceable | Y | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | EECL | 2981014 | PO | 16.988 | 0 | 2512.8636 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | 0 | 296 | 0 | 13 | 0 | 930 | 28 | 0 | 0 | 100 | 0 | -27.3772 | 145.9142 | 2000 | PO6010234 | 000002981014 | 2000s | WESTERN
EECL | OT205337 | Operational |  | 2023-11-25 | 202311 | 2024-01-16 | Pole-Wood | Wood Pole Below Ground | Broken | Termites | 0 | 19kV |  |  |  | 1179481 | 2024 | 23FN15148 | 2023-11-25 | 2023-11-28 17:10 |  |  | Normal Event | Hot | Far North | 2023-11-25 17:43 | 2023-11-25 17:46 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FE |  | NORMANTON: IFFLEY RD, BURKETOWN RD, BURKE DEVELOPMENT RD, NEU MAYER VALLEY STATION | NORMANTON 22kV Burketown Fdr CB tripped. SCADA Interface automated outage. 2 poles down and a broken cross-arm - Crew replaced TM8. SL 5223427. REDACTED | entered from the SCADA Interface OC trip Storm in Area Reason for Event changed from Unknown Close fail Sending Asset Event to FFA FFA Order Created F-AE23FN15148-1-0 DfltHost FFA Order Acknowledged F-AE23FN15148-1-0 nrmoc01 REDACTED FFA Order En Route F-AE23FN15148-1-0 nrmoc01 FFA Order On Site F-AE23FN15148-1-0 nrmoc01 Crew to fly line tomorrow Time On modified from 23:59 25-Nov to 23:59 26-Nov Sending Asset Event to FFA FFA Order Suspended F-AE23FN15148-1-0 by REDACTED feeder needs to be patrolled in daylight hours using helicopter Crew on site patrolling feeder. Asset selection modified Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Pole down 5223427 Sending Asset Event to FFA 2 poles down and a broken crossarm. Tomorrows job now Time On modified from 23:59 26-Nov to 23:59 27-Nov Sending Asset Event to FFA Pole TT66 will be replaced tomorrow and isolation pont point moved to there for the reminder of work to be completed Tuesday Time On modified from 23:59 27-Nov to 18:00 28-Nov Sending Asset Event to FFA Sending Asset Event to FFA Crew under a permit now to replace broken cross arm. Once that is done we can get Iffley SWER away and crew will return tomorrow to replace down poles. HV Wires Down Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 18:00 28-Nov to 17:10 28-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23FN15148-1-0 nrmoc01 FFA Order On Site F-AE23FN15148-1-0 nrmoc01 Restoration Comments for F-AE23FN15148-1-0 by nrmoc01: all complete, supply restored around 1800 today. details to come tomorrow. to buggered FFA Order F-AE23FN15148-1-0 Completed by technician REDACTED in crew nrmoc01(0409450233) with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : replace TM8 fault was beyond B533 but Burketown feeder CB tripped isolating fault Site Label : 5223427 Actual Power Restoration for F-AE23FN15148-1-0: 28-NOV-2023 18:00:00 Reason for Event changed from Lightning / Storm Updated Reasons tab. Updated Event Trigger from Lightning to HV-Unassisted failure. | 1 | 9352387 | NEUMAYER VALLEY 8 poles Sth of 3 way | 1179481 | TM8 | 9352387 | 2018-08-16 |  |  | 0 | 14 | 2 | 0 | Serviceable | N | SWER sty term | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | WS WHITE STRINGYBARK | 12 kiloNewton | EECL | 9352387 | PO | 0 | 0 | 3895.8453 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 347 | 0 | 13 | 0 | 1090 | 18 | 0 | 0 | 100 | 0 | -18.2979 | 140.3679 | 1989 | PO5223427 | 000003379335 | 1980s | EASTERN/COASTAL
EECL | OT205465 | Operational |  | 2023-11-26 | 202311 | 2023-12-28 | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay External | 0 | 19kV |  |  |  | 1056148 | 2024 | 23CA16557 | 2023-11-26 | 2023-11-27 13:14 |  |  | Normal Event | Wet / Rain | Capricornia | 2023-11-26 18:53 | 2023-11-26 18:56 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | ARAMAC: BOWEN DOWNS RD, TORRENS CREEK RD, OFF BOWEN DOWNS RD, ARAMAC-MUTTABURRA RD | F-2219-q BARCALDINE 19kV Ashra Downs X606266 CB tripped. SCADA Interface automated outage. Crew erected temporary pole at SL 4135044 REDACTED | entered from the SCADA Interface Depot Co-ord Advised Brac crew confirm feeder not in built area - no fault calls recieved Sending Asset Event to FFA FFA Order Created F-AE23CA16557-1-0 DfltHost Removing Asset Event from FFA FFA Order cancelled.F-AE23CA16557-1-0 MRC failed crew to patrol in the morning Time On modified from 23:59 26-Nov to 23:59 27-Nov Manual Reclose Checklist Restored on F-2219 Time On modified from 23:59 27-Nov to 13:14 27-Nov HV Wires Down Sending Asset Event to FFA FFA Order Created F-AE23CA16557-1-1 DfltHost FFA Order Acknowledged F-AE23CA16557-1-1 brccs02 REDACTED FFA Order En Route F-AE23CA16557-1-1 brccs02 FFA Order On Site F-AE23CA16557-1-1 brccs02 FFA Order F-AE23CA16557-1-1 Completed by technician REDACTED in crew brccs02(0437746018) with code A-T-317 - Severe Weather Action Taken : Erected Temp pole at Bowen Down’s Site Label # 4135044 Site Label : 4135044 Updated Reasons tab. Reason for Event changed from Unknown | 1 | 3160567 | 7 NE X1897 4470 Aramac Torrens Crk Rd | 1056148 | 4135044 | 3160567 | 2021-02-01 | N |  | 0 | 11 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 3160567 | PO | 5.313 | 0 | 686.2189 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 6 | 0 | 645 | 16 | 0 | 0 | 40 | 15 | -22.4684 | 145.006 | 2009 | PO4135044 | 000003160567 | 2000s | WESTERN
EECL | OT205726 | Operational |  | 2023-11-28 | 202311 | 2023-11-28 | Pole-Wood | Wood Pole Below Ground | Broken | Termites | 0 | 19kV |  |  |  | 1622205 | 2024 | 23NQ14096 | 2023-11-28 | 2023-11-28 15:33 |  |  | Normal Event | Storm Electrical | North Queensland | 2023-11-28 05:51 | 2023-11-28 08:15 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to damage requiring emergency repairs. Fault finding is in progress. | FC |  | HUGHENDEN: DELBESSIE STATION, GLENMOAN STATION, GLENTOR STATION, KOON KOOL STATION, MONAVALE STATION, MOUNTAIN VIEW STATION, MT BECKFORD STATION, WARWOMBIE STATION, WONGALEE STATION PRAIRIE: GLENDOWER STATION | F-2360-s HANN HWY NO.1.FC - Multiple calls beyond | HANN HWY NO.1.FC - Multiple calls beyond Sending Asset Event to FFA FFA Order Created F-AE23NQ14096-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ14096-1-0 huhcs01 REDACTED 0437738649 FFA Order En Route F-AE23NQ14096-1-0 huhcs01 Sending Asset Event to FFA FFA Order On Site F-AE23NQ14096-1-0 huhcs01 Restoration Comments for F-AE23NQ14096-1-0 by huhcs01: requires temp pole to be stood Time On modified from 23:59 28-Nov to 15:33 28-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23NQ14096-1-0 Completed by technician REDACTED in crew huhcs01(0437738649) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : stood temp pole Site Label : 5058252 | 1 | 2780047 | Monavale Station Flinders Rvr Hughenden | 1622205 | 5058252 | 2780047 | 2021-03-03 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Inaccessible to heavy vehicles | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 2780047 | PO | 11.731 | 0 | 1735.2224 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 50 | 0 | 264 | 0 | 6 | 0 | 830 | 16 | 0 | 0 | 100 | 0 | -20.8464 | 144.3831 | 1995 | PO5058252 | 000002780047 | 1990s | WESTERN
EECL | OT205881 | Operational |  | 2023-11-28 | 202311 | 2023-11-29 | Pole-Wood | Wood Pole Up To 2m | Broken | Unknown - Wind | 0 | 19kV |  |  |  | 1093372 | 2024 | 23SW20887 | 2023-11-28 | 2023-11-29 15:57 |  |  | Normal Event | Storm Electrical | South West | 2023-11-28 21:12 | 2023-11-28 21:14 | Completed | Unplanned Outage | Lightning | Fallen Power Lines | due to fallen power lines. | FC |  | CHARLEVILLE, CHEEPIE, COOLADDI, QUILPIE, | F-1323-r QUILPIE 19kV Cheepie Dup CB7036 CB tripped. SCADA Interface automated outage. Wind and lightning caused three SWER pin poles to fall down - Three temporary poles installed. SL 3222291. REDACTED | entered from the SCADA Interface OC Trip Storm in Area MRC failed Depot Co-ord Advised Crews to start at 0600 tomorrow. Crew to update for dispatch Time On modified from 23:59 28-Nov to 23:59 29-Nov . Reason for Event changed from Unknown QULOC03 Sending Asset Event to FFA FFA Order Created F-AE23SW20887-1-0 DfltHost FFA Order Acknowledged F-AE23SW20887-1-0 quloc03 REDACTED 0429373407 Crew are heading for line patrol then first sectionalise at SD7038 Sending Asset Event to FFA Reclose Attempt on CB7036 with SD7038 open at 0725 Manual Reclose Checklist Sending Asset Event to FFA Successful, line patrolling up to S7114 then reclose attempt with S7114 open Sending Asset Event to FFA crew to open DL8128 and attempt reclose failed Sending Asset Event to FFA Isolated and earthed at S7114 - reclose attempt at 0904 Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Crew found poles down beyond S7114. carrying out repairs now HV Wires Down Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order En Route F-AE23SW20887-1-0 quloc03 FFA Order On Site F-AE23SW20887-1-0 quloc03 Crews made repairs restored at 1557 Time On modified from 23:59 29-Nov to 15:57 29-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23SW20887-1-0 Completed by technician REDACTED in crew QULOC03(0429373407) with code A-T-62 - Lightning Action Taken : wind/lightning caused 3 swer pin poles to fall down, 3 temp poles installed Site Label : 3222291 Added notes to Reasons tab. Updated Event Trigger from HV-CCF to Lightning. | 1 | 9372394 | 10SpnWStPw4087Colac1010ColacRdQuilpii | 1093372 | 3222291 | 9372394 | 2023-09-14 |  |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 9372394 | PO | 11.68 | 0 | 1727.6995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -150 | 0 | 271 | 0 | 6 | 0 | 850 | 16 | 0 | 0 | 60 | 0 | -26.4645 | 144.6325 | 1986 | PO3222291 | 000002469896 | 1980s | WESTERN
EECL | OT206016 | Operational |  | 2023-11-29 | 202311 | 2023-11-30 | Pole-Wood | Wood Pole Below Ground | Broken | Unknown - Wind | 0 | 12.7kV |  |  |  | 1229938 | 2024 | 23SW21062 | 2023-11-29 | 2023-11-30 11:42 | M |  | Normal Event | Storm | South West | 2023-11-29 14:48 | 2023-11-29 15:55 | Completed | Unplanned Outage | Severe Weather | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | WANDOAN: NATHAN RD | F-1339-r - WAND - TAROOM FDR - Bungaban nth SWER - REDACTED ADVISED THAT CB2462 HAS TRIPPED Crew found faulty recloser and pole down at SL 4227187 with a broken conductor - Crew replaced CB and installed temporary pole. REDACTED | REDACTED ADVISED THAT CB2462 HAS TRIPPED Sending Asset Event to FFA FFA Order Created F-AE23SW21062-1-0 DfltHost Crew are replacing faulty Recloser. Not sure if there is a fault on the line as well. Sending Asset Event to FFA Time On modified from 23:59 29-Nov to 23:59 30-Nov Sending Asset Event to FFA Faulty recloser replaced. There is a Fault on the line. Crew are out of hours. Sending Asset Event to FFA Sending Asset Event to FFA REDACTED to commence feeder SWER patrol Sending Asset Event to FFA Crew advised that they patrolled the first half of the feeder and want to liven up to sectionaliser S1968 Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW21062-1-0 wndoc01 REDACTED 0429848619 FFA Order En Route F-AE23SW21062-1-0 wndoc01 FFA Order On Site F-AE23SW21062-1-0 wndoc01 Time On modified from 23:59 30-Nov to 11:42 30-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23SW21062-1-0 Completed by technician REDACTED in crew wndoc01(0429848619) with code A-T-62 - Lightning Action Taken : Ergon crew found faulty recloser and a pole down at S/L 4227187 with broken conductor crew replaced CB and installed temp pole Site Label : 4227187 Reason for Event changed from Lightning / Storm Updated Reasons tab. Updated Event Trigger from Lightning to Severe Weather. | 1 | 9364168 | 3 Sth T to PC5726 1977 Nathan Rd Wandoan | 1229938 | 4227187 | 9364168 | 2020-03-15 |  |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Crop | BB BLACKBUTT | 3 kiloNewton | EECL | 9364168 | PO | 11.345 | 0 | 1678.1073 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 0 | 6 | 0 | 810 | 16 | 0 | 0 | 129 | 0 | -25.927 | 150.0108 | 1972 | PO4227187 | 000003116649 | 1970s | WESTERN
EECL | OT206028 | Operational |  | 2023-11-29 | 202311 | 2023-12-12 | Pole-Wood | Wood Pole Up To 2m | Broken | Footing Failure | Replace | 12.7kV |  |  |  | 1893513 | 2024 | 23SW21011 | 2023-11-29 | 2023-11-29 20:45 | M |  | Normal Event | Storm Electrical | South West | 2023-11-29 14:50 | 2023-11-29 14:53 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | BRIGALOW, CANAGA, CHINCHILLA, EARLE, PELICAN, WYCHIE | F-2248-q - CHINCHILLA 22kV WyhieCanga CB609548 ACR CB tripped. SCADA Interface automated outage. SWER pin pole blew over in windy storm. Temporary pole stood. SL 3078887. REDACTED | entered from the SCADA Interface Storm in Area MRC to be carried out Depot Co-ord Advised Manual Reclose Checklist MRC unsuccessful chnfr02 Sending Asset Event to FFA FFA Order Created F-AE23SW21011-1-0 DfltHost FFA Order Acknowledged F-AE23SW21011-1-0 chnfr02 REDACTED 0400201688 FFA Order En Route F-AE23SW21011-1-0 chnfr02 FFA Order On Site F-AE23SW21011-1-0 chnfr02 Asset selection modified Sending Asset Event to FFA Replay sequence/s deleted after 29-NOV-23 14:49:40 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA HV Pole down at SL 3078887 HV Wires Down Pole/s Down Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 29-Nov to 20:45 29-Nov Sending Asset Event to FFA Sending Asset Event to FFA Restoration Comments for F-AE23SW21011-1-0 by chnfr02: SWER pin pole blown over in a windy storm, pole was an old hardwood stood temporary pole and made safe renergised 12.5/5 3/12 in cultivation paddock Restoration Comments for F-AE23SW21011-1-0 by chnfr02: SWER pin pole blown over in a windy storm, pole was an old hardwood stood temporary pole and made safe renergised 12.5/5 3/12 in cultivation paddock FFA Order F-AE23SW21011-1-0 Completed by technician REDACTED in crew chnfr02(0400201688) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : SWER pin pole blown over in a windy storm stood temporary pole and made safe renergised 12.5/5 3/12 in cultivation paddock Site Label : 3078887 Restoration Comments for F-AE23SW21011-1-0 by chnfr02: SWER pin pole blown over in a windy storm, pole was an old hardwood stood temporary pole and made safe renergised 12.5/5 3/12 in cultivation paddock Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Created F-AE23SW21011-1-1 DfltHost Updated Reasons tab. Updated Event Trigger from Lightning to HV-Unassisted failure. Sending Asset Event to FFA FFA Order cancelled.F-AE23SW21011-1-1 | 1 | 9353677 | acc 1027 Brigalow - Canaga Rd Brigalow | 1893513 | 3078887 | 9353677 | 2020-05-18 |  |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Crop | SG SPOTTED GUM | 3 kiloNewton | EECL | 9353677 | PO | 5.083 | 0 | 751.8715 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -80 | 0 | 197 | 0 | 6 | 0 | 640 | 16 | 0 | 0 | 99 | 20 | -26.7537 | 150.8268 | 1963 | PO3078887 | 000002889601 | 1960s | WESTERN
EECL | OT206017 | Operational |  | 2023-11-29 | 202311 | 2023-11-29 | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay Internal |  | 11kV |  |  |  | 927467 | 2024 | 23CA16684 | 2023-11-29 | 2023-11-29 07:50 | [17 empty] | 1 | [5 empty] | 2021-03-10 |  |  | 0 | 12.5 | 1 | 3 | Serviceable | N | Rrl inter spn <200m | WOOD UNTREATED ROUND | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 12 kiloNewton | EECL | 0 | PO | 22.073 | 3 | 3264.9926 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | -25 | 5 | 331 | 1 | 9 | 0 | 1100 | 22 | 0 | 0 | 96 | 40 | -23.1192 | 150.7233 | 1961 | PO4069303 | 000002807450 | 1960s | EASTERN/COASTAL
EECL | OT206775 | Operational |  | 2023-12-02 | 202312 | 2023-12-02 | Pole-Wood | Wood Pole Up To 2m | Broken | Unknown - Wind | 0 | 19kV |  |  |  | 1951724 | 2024 | 23SW21254 | 2023-12-01 | 2023-12-02 21:53 |  |  | Normal Event | Storm Electrical | South West | 2023-12-01 18:20 | 2023-12-01 18:23 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FC |  | AMBY, MITCHELL | F - 2282-q - ROMA - 19kV Nth Amby CB776441 ACR CB tripped. SCADA Interface automated outage. Pole grounded and conductors broken at SL 3070764, pole grounded at SL 3101149, and broken insulator disc at SL 3101014. Repairs made as required. REDACTED | entered from the SCADA Interface Crew will call when avaliable. MRC unsuccessful at 19:36 crew to fly morning 02/12/23 Time On modified from 23:59 01-Dec to 23:59 02-Dec . . romcm700 Sending Asset Event to FFA FFA Order Created F-AE23SW21254-1-0 DfltHost FFA Order Acknowledged F-AE23SW21254-1-0 romcm700 REDACTED o 0427485694 FFA Order En Route F-AE23SW21254-1-0 romcm700 FFA Order On Site F-AE23SW21254-1-0 romcm700 Time On modified from 23:59 02-Dec to 16:00 02-Dec Reason for Event changed from Unknown Sending Asset Event to FFA crew to install temp pole at SL3070764 Sending Asset Event to FFA Pole/s Down Sending Asset Event to FFA Time On modified from 16:00 02-Dec to 22:00 02-Dec Sending Asset Event to FFA Restoration Comments for F-AE23SW21254-1-0 by romcm700: isolated and repsired Restoration Comments for F-AE23SW21254-1-0 by romcm700: isolated and repsired FFA Order F-AE23SW21254-1-0 Completed by technician REDACTED o in crew romcm700(0427485694) with code A-T-62 - Lightning Action Taken : pole down and conductors broken at sl 3070764, also pole down at sl 3101149, broken insulator disc at sl 3101014 Site Label : 3070764 Time On modified from 22:00 02-Dec to 21:53 02-Dec Updated notes in Reasons tab. Updated Event Trigger from Lightning to Severe Weather. | 1 | 9353335 | Carinya 14 Epw1090 52424WarregoHwyMitch | 1951724 | 3070764 | 9353335 | 2019-09-01 |  |  | 0 | 11 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 9353335 | PO | 5.523 | 0 | 713.3584 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 6 | 0 | 610 | 16 | 0 | 0 | 100 | 0 | -26.4833 | 148.1307 | 1971 | PO3070764 | 000002854143 | 1970s | WESTERN
EECL | OT206776 | Operational |  | 2023-12-02 | 202312 | 2024-02-28 | Pole-Wood | Wood Pole Up To 2m | Broken | Termites | 0 | 19kV |  |  |  | 1628920 | 2024 | 23CA16938 | 2023-12-02 | 2023-12-03 11:41 |  |  | Normal Event | Hot | Capricornia | 2023-12-02 11:32 | 2023-12-02 11:34 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | SZ |  | CLERMONT: EPPING FOREST RD, OFF GREGORY DEVEL RD | F-2295-q - CLER - 19.1kV SWER Recloser X8695 sugested fault point Crew stood temporary pole and spliced conductor. SL 4068835. REDACTED | 19.1kV SWER Recloser X8695 sugested fault point Sending Asset Event to FFA FFA Order Created F-AE23CA16938-1-0 DfltHost Depot Co-ord Advised Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA16938-1-0 clmwgo01 REDACTED 0438317946 FFA Order En Route F-AE23CA16938-1-0 clmwgo01 Time On modified from 23:59 02-Dec to 23:59 03-Dec Sending Asset Event to FFA . Sending Asset Event to FFA Crew reports lines/poles down between X3160 & 338580 Sending Asset Event to FFA HV Wires Down Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23CA16938-1-0 clmwgo01 Time On modified from 23:59 03-Dec to 11:41 03-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order On Site F-AE23CA16938-1-0 clmwgo01 FFA Order F-AE23CA16938-1-0 Completed by technician REDACTED in crew CLMWGO01(0438317946) with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : Crew stood temp Pole and spliced conductor Site Label : 4068835 Reason for Event changed from Lightning / Storm Updated Reasons tab. Updated Event Trigger from Animal Other to HV-Unassisted failure. | 1 | 2804466 | 6pSW SP338579 ElginDownsRdBelyando | 1628920 | 4068835 | 2804466 | 2023-07-23 | N |  | 0 | 12.5 | 0 | 0 | Unserviceable - P1 | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 3 kiloNewton | EECL | 2804466 | PO | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 269 | 0 | 6 | 0 | 845 | 16 | 0 | 0 | 0 | 0 | -22.0167 | 146.9144 | 1987 | PO4068835 | 000002804466 | 1980s | WESTERN
EECL | OT208256 | Operational |  | 2023-12-09 | 202312 | 2023-12-10 | Pole-Wood | Wood Pole Beyond 2m | Broken | Wrap Stay | 0 | 33kV |  |  |  | 1977875 | 2024 | 23SW21666 | 2023-12-09 | 2023-12-10 15:18 |  |  | Normal Event | Fine | South West | 2023-12-09 18:50 | 2023-12-09 18:52 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FE |  | MITCHELL, MORVEN, MUNGALLALA, | F-2346-q - MITCHELL 33kV Mungalla Fdr CB 6190 tripped. SCADA Interface automated outage. Crew replaced broken pole at SL 3193847 REDACTED | entered from the SCADA Interface ROMCM718 Sending Asset Event to FFA FFA Order Created F-AE23SW21666-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW21666-1-0 romcm718 REDACTED 0400201688 FFA Order En Route F-AE23SW21666-1-0 romcm718 OC then EF trip to LO Depot Co-ord Advised Sending Asset Event to FFA crew advise snapped pole at SL3193847, isolation and earthing underway HV Wires Down Pole/s Down Reason for Event changed from Unknown Sending Asset Event to FFA Sending Asset Event to FFA supply restored up to AB6065 @ 2138 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 09-Dec to 23:59 10-Dec Sending Asset Event to FFA FFA Order On Site F-AE23SW21666-1-0 romcm718 Asset selection modified Sending Asset Event to FFA T-off to PW00160 de-bridged under access and back bone restored 2343, crews require access from AB6065 tomorrow to replace pole and re-connect T-off Asset selection modified Sending Asset Event to FFA . Time On modified from 23:59 10-Dec to 17:00 10-Dec Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW21666-1-0 romcm703 Jferguson 0436279486 FFA Order En Route F-AE23SW21666-1-0 romcm703 FFA Order On Site F-AE23SW21666-1-0 romcm703 FFA Order F-AE23SW21666-1-0 Completed by technician REDACTED in crew romcm703(0436279486) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replace broken pole Site Label : 3193847 Asset selection modified Asset selection modified Time On modified from 17:00 10-Dec to 15:18 10-Dec Added notes to Reasons tab. Updated Asset Event Type from Sub Transmission to Distribution. | 1 | 2286705 | DL6269 Warrego Hwy Mitchell | 1977875 | 3193847 | 2286705 | 2020-04-22 | N |  | 0 | 11 | 3 | 0 | Serviceable | N | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | EECL | 2286705 | PO | 9.065 | 0 | 1170.8517 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 10 | 0 | 720 | 28 | 0 | 0 | 115 | 0 | -26.482 | 147.7645 | 1969 | PO3193847 | 000002286705 | 1960s | WESTERN
EECL | OT209916 | Operational |  | 2023-12-16 | 202312 | 2023-12-17 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay | 0 | 19kV |  |  |  | 828459 | 2024 | 23NQ14866 | 2023-12-16 | 2023-12-17 13:38 | M | A | Normal Event | Wind | North Queensland | 2023-12-16 21:35 | 2023-12-17 07:26 | Completed | Unplanned Outage | Animal Insects (termites/borers/white ants) | Unknown | due to damage requiring emergency repairs. Fault finding is in progress. | FC |  | CLONCURRY | F-2598-s Multiple fault calls suggest Jessivale No.1 has tripped | Multiple fault calls suggest Jessivale No.1 has tripped REDACTED advised crews are flying the line this morning Sending Asset Event to FFA FFA Order Created F-AE23NQ14866-1-0 DfltHost Sending Asset Event to FFA Crews have confirmed lines down near CLS80, awaiting pole number HV Wires Down Sending Asset Event to FFA Pole/s Down Sending Asset Event to FFA REDACTED advised pole down is 5035015. Sending Asset Event to FFA Time On modified from 23:59 17-Dec to 13:38 17-Dec Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ14866-1-0 clccs02 REDACTED 0400893092 FFA Order En Route F-AE23NQ14866-1-0 clccs02 FFA Order On Site F-AE23NQ14866-1-0 clccs02 FFA Order F-AE23NQ14866-1-0 Completed by technician REDACTED in crew clccs02(0400893092) with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : Patrolled line from Jessivale recloser located pole down(due to termites) on Tyndal Stn (5035015) isolated earthed and replaced pole Site Label : 5035015 auto-completed | 1 | 2649326 | 3 e homestead 3way tyndool stn CC | 828459 | 5035015 | 2649326 | 2019-07-15 | N |  | 0 | 12.5 | 0 | 0 | Unserviceable - P2 | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 2649326 | PO | 10.365 | 0 | 1533.1272 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -80 | 0 | 264 | 0 | 6 | 0 | 845 | 16 | 100 | 0 | 50 | 15 | -20.2502 | 140.5656 | 1982 | PO5035015 | 000002649326 | 1980s | WESTERN
EECL | OT210888 | Operational |  | 2023-12-19 | 202312 | 2023-12-20 | Pole-Wood | Wood Pole Below Ground | Broken | Termites | 0 | LV |  |  |  | 1671256 | 2024 | 23NQ14971 | 2023-12-19 | 2023-12-20 11:36 | M | A | Normal Event | Fine | North Queensland | 2023-12-19 20:18 | 2023-12-20 11:38 | Completed | Unplanned Outage | LV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | 22 GRAY ST HUGHENDEN QLD 4821 | QPS advise Lines on road aty this location. P1 Call Flag Re-logged to correct NMI.. P1 Call Flag |  | 1 | 9355313 | 22 Gray St Hughenden | 1671256 | 5115655 | 9355313 | 2019-07-18 | N |  | 0 | 11 | 0 | 0 | Serviceable | N | Urb service pole | WOOD (GREEN) SALT IMPREG CCA | Concrete Pre Cut | Footpath | SG SPOTTED GUM | 5 kiloNewton | EECL | 9355313 | PO | 7.218 | 3 | 932.2693 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | -150 | 5 | 215 | 1 | 14 | 0 | 695 | 3 | 0 | 0 | 97 | 0 | -20.8433 | 144.2003 | 1979 | PO5115655 | 000003084059 | 1970s | WESTERN
EECL | OT211510 | Operational |  | 2023-12-21 | 202312 | 2024-02-12 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay External | Made Safe | 19kV |  |  |  | 1786802 | 2024 | 23NQ15081 | 2023-12-21 | 2023-12-27 15:20 |  |  | Normal Event | Storm Electrical | North Queensland | 2023-12-21 18:20 | 2023-12-21 18:23 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FE |  | LONGREACH, WINTON | F-2701-s WINT - 19kV Apsley Fdr CB A652 tripped. SCADA Interface automated outage. Crew found HV pole adjacent to SL 5227205 grounded - Fault isolated and other customers restored. Crew replaced pole. REDACTED | entered from the SCADA Interface Sending Asset Event to FFA FFA Order Created F-AE23NQ15081-1-0 DfltHost crew will fly the line tomorow Sending Asset Event to FFA Time On modified from 23:59 21-Dec to 23:59 22-Dec Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ15081-1-0 wntcdwgl1 REDACTED 0427893349 Sending Asset Event to FFA Sending Asset Event to FFA Crew have found Pole adj to 5227205 down. REDACTED to isolate & earth at LLC Pole 5089500 towards WIS232 & then continue aerial line patrol. Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Reclose successfull at Fdr CB A652. Isolated & Earthed at Pole 5089500 LLC towards Dist Sub WIS232 to replace fallen HV pole. Asset selection modified Pole/s Down Sending Asset Event to FFA Borer required for job. Currently being repaired. Customer does not require power at site, so will be attended to after Christmas when borer available. Time On modified from 23:59 22-Dec to 16:00 28-Dec Sending Asset Event to FFA FFA Order En Route F-AE23NQ15081-1-0 wntcdwgl1 FFA Order On Site F-AE23NQ15081-1-0 wntcdwgl1 FFA Order F-AE23NQ15081-1-0 Completed by technician REDACTED in crew wntcdwgl1(0427893349) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : isolated fault and restored supply to remaining customers Site Label : 5227205 Time On modified from 16:00 28-Dec to 18:00 27-Dec Time On modified from 18:00 27-Dec to 15:20 27-Dec send to REDACTED to complete Sending Asset Event to FFA FFA Order Created F-AE23NQ15081-1-1 DfltHost FFA Order cancelled.F-AE23NQ15081-1-1 auto-completed Updated Reasons tab. Reason for Event changed from Unknown | 1 | 3389682 | (bore pump) Vindex Station | 1786802 | 5227207 | 3389682 | 2024-02-21 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | Y | SWER sty term | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | EECL | 3389682 | PO | 16.275 | 6 | 2407.4057 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | 10 | 291 | 1 | 13 | 0 | 948 | 18 | 0 | 0 | 145 | 0 | -22.538 | 143.3187 | 1991 | PO5227207 | 000003389682 | 1990s | WESTERN
EECL | OT211642 | Operational |  | 2023-12-22 | 202312 | 2023-12-22 | Pole-Wood | Wood Pole Up To 2m | Broken | Termites | 0 | 19kV |  |  |  | 1016576 | 2024 | 23CA18028 | 2023-12-21 | 2023-12-22 16:11 |  |  | Normal Event | Storm | Capricornia | 2023-12-21 17:28 | 2023-12-21 17:31 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | ARAMAC: REEDY CK RD, STAGMOUNT RD, ALBIONVALE RD, REEDY CREEK RD, TORRENS CREEK RD, ARAMAC-FLEETWOOD RD, OFF TORRENS CREEK RD | F-29529-g BARCALDINE 19.1kV Fleetwood CB S7022 tripped. SCADA Interface automated outage. Grounded pole - Crew erected temporary pole. SL 4139592. REDACTED | entered from the SCADA Interface Downstream Outages excluded from asset selection: 23CA17964 S1936 (4 assets) F-29529-g AHC REDACTED calling back with further instructions Depot Co-ord Advised No Frequented areas that require patrolling Unsucessfulreclose attempt Will Push job out to tomorrow Advised by AHC Crew advised helicopter patrol to be conducted in daylight hours Time On modified from 23:59 21-Dec to 23:59 22-Dec . DSO brccs01 Sending Asset Event to FFA FFA Order Created F-AE23CA18028-1-0 DfltHost FFA Order Acknowledged F-AE23CA18028-1-0 brccs01 REDACTED 0428110442 FFA Order En Route F-AE23CA18028-1-0 brccs01 supply restored up to 19.1kV SWER Sectionaliser X1735 at 1249 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 22-Dec to 16:11 22-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order On Site F-AE23CA18028-1-0 brccs01 FFA Order F-AE23CA18028-1-0 Completed by technician REDACTED in crew brccs01(0428110442) with code A-T-317 - Severe Weather Action Taken : pole found on the ground 4 span past barcoorah tee off. temp pole erected under access. Site Label : 4139592 19.1kV SWER Sectionaliser S1936 removed from Asset Selection as cust mins already captured under 23CA17964. Reason for Event changed from Unknown Updated Reasons tab. Updated Event Trigger from Severe Weather to HV-Unassisted failure. | 1 | 3190451 | 17 N x7024 glenavon stagmount rd aramac | 1016576 | 4139592 | 3190451 | 2020-07-12 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 3 kiloNewton | EECL | 3190451 | PO | 15.567 | 0 | 2302.5912 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -30 | 0 | 286 | 0 | 6 | 0 | 900 | 16 | 0 | 0 | 143 | 0 | -22.5711 | 145.3988 | 1988 | PO4139592 | 000003190451 | 1980s | WESTERN
EECL | OT212898 | Operational |  | 2023-12-25 | 202312 | 2023-12-28 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay | 0 | 66kV |  |  |  | 1783387 | 2024 | 23NQ15315 | 2023-12-28 | 2023-12-28 11:05 |  |  | Normal Event |  | North Queensland | 2023-12-28 08:00 | 2023-12-27 09:31 | Completed | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE |  | N/A | Replace nailed aerial stay bollard pole S/L2142824 on Harper road. This is the second bollard pole supporting 66Kv angle pole S/L5142825.(The other bollard pole S/L5142823 broke on 25-12-23) | Other Incident Time On modified from 13:00 28-Dec to 11:05 28-Dec | 1 | 9356725 | HarperRd]OatsRd to RockyNedRd HomeHilll | 1783387 | 5142824 | 9356725 | 2021-05-05 |  |  | 0 | 8.5 | 0 | 0 | Serviceable | N | Bllrd unsty <=2 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Sugar Cane | ZZ NO DISC - UNKNOWN | Unknown | EECL | 9356725 | PO | 25.18 | 0 | 2115.8129 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 14 | 0 | 887 | 12 | 0 | 100 | 0 | 0 | -19.7475 | 147.4267 | 1975 | PO5142824 | 000003237316 | 1970s | EASTERN/COASTAL
EECL | OT214953 | Operational |  | 2023-12-31 | 202312 | 2024-01-02 | Pole-Wood | Wood Pole Below Ground | Broken | Termites | 0 | 19kV |  |  |  | 1217714 | 2024 | 23FN16982 | 2023-12-30 | 2024-01-01 11:19 | M | A | Normal Event | Storm Electrical | Far North | 2023-12-30 19:39 | 2023-12-30 19:41 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FC |  | N/A | F-949-t - NORMANTON 19kV AugustsDwnLO107 ACR CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface Crew adv will arrange chopper to fly in the morning. Time On modified from 23:59 30-Dec to 23:59 31-Dec . Crews patrolling as of 0800hrs. REDACTED as contact. Sending Asset Event to FFA FFA Order Created F-AE23FN16982-1-0 DfltHost FFA Order Acknowledged F-AE23FN16982-1-0 nrmoc01 REDACTED 0409450233 FFA Order En Route F-AE23FN16982-1-0 nrmoc01 FFA Order On Site F-AE23FN16982-1-0 nrmoc01 Sending Asset Event to FFA REDACTED adv Pole down SL 5258205. Isol & Earthed. Crews to return tomorrow to continue repairs. ETA on site tomorrow 1100hrs Asset selection modified Time On modified from 23:59 31-Dec to 15:00 01-Jan HV Wires Down Pole/s Down Manual Reclose Checklist Reason for Event changed from Unknown Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23FN16982-1-0 nrmoc01 FFA Order On Site F-AE23FN16982-1-0 nrmoc01 Time On modified from 15:00 01-Jan to 11:19 01-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23FN16982-1-0 Completed by technician REDACTED in crew nrmoc01(0409450233) with code A-T-317 - Severe Weather Action Taken : replace MO112 Site Label : 5258205 Actual Power Restoration for F-AE23FN16982-1-0: 01-JAN-2024 11:30:00 Updated Asset Event Type from Transmission to Distribution. | 1 | 9356859 | 54 poles South nardoo stn hstead | 1217714 | MO112 | 9356859 | 2018-08-06 |  |  | 0 | 15.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | WS WHITE STRINGYBARK | 8 kiloNewton | EECL | 9356859 | PO | 0 | 15 | 2951.6642 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -120 | 20 | 336 | 10 | 6 | 0 | 1150 | 16 | 0 | 0 | 70 | 0 | -18.9051 | 139.6206 | 1989 | PO5258205 | 000003441683 | 1980s | WESTERN
EECL | OT215086 | Operational |  | 2023-12-31 | 202312 |  | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay | 0 | 11kV |  |  |  | 949862 | 2024 | 23WB17030 | 2023-12-31 | 2023-12-31 18:33 |  |  | Normal Event | Wind | Wide Bay | 2023-12-31 11:57 | 2023-12-31 19:36 | Cancelled | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | 309 COONAMBULA-EIDSVOLD RD;MUNDUBBERA QLD 4626 | 3rd Party->Fault occurred at:31/12/2023 11:50; REDACTED;>WDPP --> AffectingTraffic:NO -- StillHavePower:UNSURE<;Incident Details:Pole down in paddock at R080 Riversleigh School Bus Road which is about 80 meters from TCE address, wires are still attached;COVID-19:UNKNOWN;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N | outage cancelled via Clash Wizard | 1 | 2777345 | R080 RIVERLEIGH SCHOOLBUS RD MUNDUBBERA | 949862 | 3312487 | 2777345 | 2020-02-02 | N |  | 0 | 12.5 | 1 | 0 | Serviceable | N | Rrl inter spn <200m | WOOD UNTREATED ROUND | Rock | Paddock Grazing | ZZ NO DISC - UNKNOWN | 8 kiloNewton | EECL | 2777345 | PO | 21.56 | 0 | 3189.0627 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 6 | 0 | 1010 | 22 | 0 | 0 | 100 | 0 | -25.5815 | 151.2674 | 1957 | PO3312487 | 000002777345 | 1950s | WESTERN
EECL | OT212946 | Operational |  | 2023-12-26 | 202312 | 2023-12-26 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay External | 0 | 11kV |  |  |  | 1445763 | 2024 | 23MK10249 | 2023-12-26 | 2023-12-26 18:56 | M | A | Normal Event | Storm Electrical | Mackay | 2023-12-26 03:37 | 2023-12-26 03:40 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | ETON: ELVINS RD, TREVETHANS RD, JOHN TEMPLE DR, PEAK DOWNS HWY, STONY CREEK RD NEBO: PEAK DOWNS HWY BLUE MOUNTAIN: BLUE MOUNTAIN RD | Fault Sheet F-923-t ETON 11kV Eton Range RC878030 ACR CB tripped. SCADA Interface automated outage. P2 pole failed, broke in half below 11kV tee-off arm. SL 4097064. REDACTED | entered from the SCADA Interface O/C trip Fault Sheet F-923-t Sending Asset Event to FFA FFA Order Created F-AE23MK10249-1-0 DfltHost FFA Order Acknowledged F-AE23MK10249-1-0 mckoc02 REDACTED 0438412657 FFA Order En Route F-AE23MK10249-1-0 mckoc02 FFA Order On Site F-AE23MK10249-1-0 mckoc02 Crew currently completely cursory patrol Sending Asset Event to FFA Fault call reports lines dowqn adjacent Sub 4626. Crews to head to site Sending Asset Event to FFA Depot Co-ord Advised Sending Asset Event to FFA FFA Order Pending F-AE23MK10249-1-0 FFA Order Acknowledged F-AE23MK10249-1-0 mckoc03 REDACTED 0430777796 FFA Order En Route F-AE23MK10249-1-0 mckoc03 FFA Order On Site F-AE23MK10249-1-0 mckoc03 Time On modified from 23:59 26-Dec to 18:00 26-Dec Sending Asset Event to FFA Time On modified from 18:00 26-Dec to 20:00 26-Dec Sending Asset Event to FFA Time On modified from 20:00 26-Dec to 18:56 26-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23MK10249-1-0 mckoc03 FFA Order On Site F-AE23MK10249-1-0 mckoc03 FFA Order F-AE23MK10249-1-0 Completed by technician REDACTED with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : P2 pole failed, broken in half below 11kv T-off arm Site Label : 4097064 auto-completed Updated Reasons tab. Reason for Event changed from Unknown | 1 | 9356638 | S/W of lks718, 23632 peak downs hwy eton | 1445763 | 4097064 | 9356638 | 2023-08-11 |  |  | 0 | 12.5 | 5 | 0 | Unserviceable - P2 | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | GI GREY IRONBARK | 5 kiloNewton | EECL | 9356638 | PO | 18.188 | 2 | 2152.3056 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -140 | 3 | 281 | 1 | 1 | 0 | 895 | 45 | 0 | 0 | 98 | 0 | -21.2887 | 148.9495 | 1965 | PO4097064 | 000002936534 | 1960s | EASTERN/COASTAL
EECL | OT207060 | Operational |  | 2023-12-03 | 202312 | 2023-12-05 | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay External | 0 | 66kV |  |  |  | 834933 | 2024 | 23NQ14359 | 2023-12-03 | 2023-12-05 16:09 |  |  | Normal Event | Storm Electrical | North Queensland | 2023-12-03 17:42 | 2023-12-03 17:45 | Completed | Unplanned Outage | HV-Conductor Connection Failure | Unknown | due to damage requiring emergency repairs. Fault finding is in progress. | FE |  | N/A | F-2412-s Feeder trip to L/O, distance 55km from Hughenden, 96km from Cape River | Feeder trip to L/O, distance 55km from Hughenden, 96km from Cape River Sending Asset Event to FFA FFA Order Created F-AE23NQ14359-1-0 DfltHost Crews Attending: REDACTED Sending Asset Event to FFA Crews have gotten bogged and are having further vehicle issues, they are abanding tonights effort and will fly in the morning. Time On modified from 23:59 03-Dec to 23:59 04-Dec Sending Asset Event to FFA . Sending Asset Event to FFA Sending Asset Event to FFA 4 X poles down on 66/19.1kV Fdr. REDACTED advsed they will attempt to get the SWER onto temp poles to get supply restored to customers and once the 66 poles are replaced another access will be required to bring SWER back onto 66 poles Asset selection modified 4 X poles down on 66/19.1kV Fdr. REDACTED advsed they will attempt to get the SWER onto temp poles to get supply restored to customers and once the 66 poles are replaced another access will be required to bring SWER back onto 66 poles Asset selection modified Sending Asset Event to FFA Access to area is restricted due to ground conditions. REDACTED is trying to source machinery to replace 66kV poles tomorrow Sending Asset Event to FFA Time On modified from 23:59 04-Dec to 23:59 05-Dec Sending Asset Event to FFA Crews have advised that SWER is ok to turn back on. 66kV Will be staying off overnight as they cannot get to poles due to weather to replace. Sending Asset Event to FFA Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Time On modified from 23:59 05-Dec to 16:09 05-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ14359-1-0 huhcdwgl1 REDACTED 0429797319 FFA Order En Route F-AE23NQ14359-1-0 huhcdwgl1 FFA Order On Site F-AE23NQ14359-1-0 huhcdwgl1 FFA Order F-AE23NQ14359-1-0 Completed by technician REDACTED in crew huhcdwgl1(0429797319) with code A-T-317 - Severe Weather Action Taken : 4x 66/19.1kv poles down due to wind storm also killed 3 head of cattle Site Label : 5095698 | 1 | 9353110 | 23 P W T-Off 2 Penrice Stn Laurelvale St | 834933 | 5095701 | 9353110 | 2021-11-19 |  |  | 0 | 15.5 | 0 | 0 | Serviceable | Y | 66kV inter & 1 cct | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 9353110 | PO | 9.792 | 15 | 1815.6024 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | -50 | 20 | 291 | 10 | 6 | 0 | 1090 | 31 | 0 | 0 | 45 | 80 | -20.8363 | 144.6974 | 1976 | PO5095701 | 000002955689 | 1970s | WESTERN
EECL | OT207208 | Operational |  | 2023-12-04 | 202312 |  | Crossarm | Wood Pole Below Ground | Broken | Rot/Decay | 0 | 11kV |  |  |  | 1861790 | 2024 | 23NQ14399 | [5 empty] | Hot | North Queensland | 2023-12-04 11:35 | 2023-12-04 15:16 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ |  | BOWEN: COLLINSVILLE RD, MOUNT BUCKLEY RD, PETER DELAMOTHE RD | F-2418-s MERI - 03 HV fuses down at Mt Dangar No.10. Broken xarm next pole down. | F-2418-s MERI - 03 HV fuses down at Mt Dangar No.10. Broken xarm next pole down. Sending Asset Event to FFA FFA Order Created F-AE23NQ14399-1-0 DfltHost Sending Asset Event to FFA Time On modified from 23:59 04-Dec to 19:00 04-Dec Sending Asset Event to FFA Reverse switching commenced. Time On modified from 19:00 04-Dec to 18:00 04-Dec Sending Asset Event to FFA Time On modified from 18:00 04-Dec to 17:25 04-Dec Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ14399-1-0 clvcs01 REDACTED 0418739194 FFA Order En Route F-AE23NQ14399-1-0 clvcs01 FFA Order On Site F-AE23NQ14399-1-0 clvcs01 FFA Order F-AE23NQ14399-1-0 Completed by technician REDACTED in crew clvcs01(0418739194) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced broken crossarm Site Label : 5200646 auto-completed | 1 | 3299212 | accessOpp1568 peter delmonthe rd bowen | 1861790 | 5200646 | 3299212 | 2020-01-14 | Y |  | 0 | 11 | 1 | 0 | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | EECL | 3299212 | PO | 14.722 | 10 | 1901.5963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -120 | 15 | 270 | 5 | 6 | 0 | 910 | 22 | 0 | 0 | 90 | 0 | -20.1195 | 148.1305 | 1980 | PO5200646 | 000003299212 | 1980s | EASTERN/COASTAL
EECL | OT209961 | Operational |  | 2023-12-17 | 202312 | 2023-12-19 | Pole-Wood | Wood Pole Up To 2m | Broken | Footing Failure | 0 | 12.7kV |  |  |  | 1691542 | 2024 | 23CA17678 | 2023-12-17 | 2023-12-17 10:46 | M | A | Normal Event | Storm Electrical | Capricornia | 2023-12-17 06:20 | 2023-12-17 07:23 | Completed | Unplanned Outage | Lightning | Fallen Power Lines | due to fallen power lines. | FC |  | MONTO: CANNINDAH RD, CRANKS AVE, MOUNTAIN VIEW RD, NORMANS RD, SCHIMKES RD MULGILDIE: BRIANS RD, BROWN'S RD, BURNETT HWY | F-2392-q - Suggest fault point 12.7kV SWER Recloser 7553 - lines down call recieved | Suggest fault point 12.7kV SWER Recloser 7553 - lines down call recieved HV Wires Down Sending Asset Event to FFA FFA Order Created F-AE23CA17678-1-0 DfltHost Crew advise snapped pole beyond S2566, isolation and earthing being moved and will get supply back on to S2566 Pole/s Down Sending Asset Event to FFA supply restored up to S2566 0854 Time On modified from 23:59 17-Dec to 12:00 17-Dec Sending Asset Event to FFA Time On modified from 12:00 17-Dec to 10:46 17-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA17678-1-0 moncdwgl1 REDACTED 0429055889 FFA Order En Route F-AE23CA17678-1-0 moncdwgl1 FFA Order On Site F-AE23CA17678-1-0 moncdwgl1 FFA Order F-AE23CA17678-1-0 Completed by technician REDACTED in crew moncdwgl1(0429055889) with code A-T-317 - Severe Weather Action Taken : 12.5 meter. 5 KN swer pin pole failed in storm. replaced with new 12.5 mtr 5 kn swer pole Site Label : 4226153 | 1 | 9355972 | E opp 436 Normans Rd Monto | 1691542 | 4226153 | 9355972 | 2021-04-13 |  |  | 0 | 11 | 0 | 0 | Serviceable | N | SWER inter | WOOD UNTREATED ROUND | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 9355972 | PO | 9.301 | 4 | 1201.3213 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -160 | 5 | 231 | 3 | 6 | 0 | 750 | 16 | 0 | 0 | 96 | 0 | -24.9495 | 151.2455 | 1955 | PO4226153 | 000003293045 | 1950s | EASTERN/COASTAL
EECL | OT211141 | Operational |  | 2023-12-20 | 202312 | 2024-01-02 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | 0 | 19kV |  |  |  | 1794015 | 2024 | 23NQ15005 | 2023-12-20 | 2023-12-21 12:00 |  |  | Normal Event | Storm Electrical | North Queensland | 2023-12-20 14:57 | 2023-12-20 15:00 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FC |  | CLONCURRY, JULIA CREEK, MCKINLAY, OORINDI, | F-2679-s JUCR - JC11 FDR - Carjoon No.1 Recloser OC trip x 4 to lockout. Fallen HV pole 5157876 - Temporary pole installed. REDACTED | entered from the SCADA Interface REDACTEDadvised storms in area and will attend in daylight hours tomorrow 21/12/23. Time On modified from 23:59 20-Dec to 23:59 21-Dec . Sending Asset Event to FFA FFA Order Created F-AE23NQ15005-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ15005-1-0 jckcmcs01 REDACTED 0473859801 FFA Order En Route F-AE23NQ15005-1-0 jckcmcs01 Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA Crew adv found fallen HV Pole 5157876. Isolated at Longford No.1 & successfull reclose at Carjoon No.1 Recloser. Sending Asset Event to FFA Crew to check downstream Sectionalisers (x3) via chopper. Sending Asset Event to FFA Time On modified from 23:59 21-Dec to 12:00 21-Dec Pole/s Down Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order On Site F-AE23NQ15005-1-0 jckcmcs01 FFA Order F-AE23NQ15005-1-0 Completed by technician REDACTED in crew jckcmcs01(0473859801) with code A-T-317 - Severe Weather Action Taken : perform aerial patrol on jc11 feeder beyond Carjoon no.1, located pole down and replaced with temporary pole at site label 5157876 Site Label : 5157816 auto-completed Added notes to Reasons tab. | 1 | 3271664 | 5 sth bore sub272 3way elrose stn JC | 1794015 | 5157877 | 3271664 | 2022-11-15 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | Y | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | Unknown | EECL | 3271664 | PO | 14.121 | 8 | 2088.7323 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | -80 | 15 | 285 | 2 | 6 | 0 | 950 | 16 | 0 | 0 | 92 | 0 | -20.9066 | 141.0611 | 1990 | PO5157876 | 000003271662 | 1990s | WESTERN
EECL | OT211199 | Operational |  | 2023-12-20 | 202312 | 2023-12-22 | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay | 0 | 19kV |  |  |  | 1056357 | 2024 | 23CA17964 | 2023-12-20 | 2023-12-22 16:11 |  |  | Normal Event | Storm | Capricornia | 2023-12-20 21:51 | 2023-12-21 05:58 | Completed | Unplanned Outage | Severe Weather | Lightning / Storm | due to damage caused by storm activity. | SZ |  | ARAMAC: TORRENS CREEK RD | F-2462-q Fault calls indicate 19.1kV SWER Sectionaliser S1936 | Fault calls indicate 19.1kV SWER Sectionaliser S1936 Crews will call in for job ETA 1500 waiting for chopper to fly the line. Time On modified from 23:59 21-Dec to 23:59 22-Dec Sending Asset Event to FFA FFA Order Created F-AE23CA17964-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA17964-1-0 brccmfr01 REDACTED 0427965190 Crews advise 2 poles are down past 19.1kV SWER Sectionaliser S1936 BRCCS01. Sending Asset Event to FFA HV Wires Down Pole/s Down Storm in Area Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Time On modified from 23:59 22-Dec to 16:11 22-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA17964-1-0 brccs01 REDACTED 0428110442 FFA Order En Route F-AE23CA17964-1-0 brccs01 FFA Order On Site F-AE23CA17964-1-0 brccs01 FFA Order F-AE23CA17964-1-0 Completed by technician REDACTED in crew brccs01(0428110442) with code A-T-317 - Severe Weather Action Taken : 2 poles found broken off at base of pole after storm, 14 poles past sectionilser x1735. 2x temp poles erected under access, supply restored 16:11 22/12/23 Site Label : 4146905 | 1 | 3227712 | 12NW X7135 albion vale rd aramac | 1056357 | 4146905 | 3227712 | 2020-08-17 | N |  | 0 | 11 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 3227712 | PO | 7.514 | 0 | 970.5429 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 6 | 0 | 675 | 16 | 0 | 0 | 100 | 0 | -22.2905 | 145.3337 | 1968 | PO4146905 | 000003227712 | 1960s | WESTERN
EECL | OT211717 | Operational |  | 2023-12-22 | 202312 | 2023-12-24 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | <null> | 22kV |  |  |  | 1294244 | 2024 | 23FN16641 | 2023-12-22 | 2023-12-22 20:22 |  |  | Normal Event | Cyclonic | Far North | 2023-12-22 13:22 | 2023-12-22 13:24 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FE |  | JULATTEN, MARYFARMS, MOUNT MOLLOY | MT MOLLOY 22kV Carbine Fdr CB tripped. SCADA Interface automated outage. Crew replaced fallen HV pin pole. SL 5008430. REDACTED | entered from the SCADA Interface Crew attending REDACTED ETA 1445 ignore above comments wrong outage. Asset selection modified Crew adv found fallen pole at 5008929. Crew to isolate and make repairs. Crew advised are attempting to have resatored tonight but are having severe access issues. REDACTED on site Supply restored at 2022 Time On modified from 23:59 22-Dec to 20:22 22-Dec Sending Asset Event to FFA FFA Order Created F-AE23FN16641-1-0 DfltHost Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN16641-1-0 mbaco10 REDACTED 123 FFA Order En Route F-AE23FN16641-1-0 mbaco10 FFA Order On Site F-AE23FN16641-1-0 mbaco10 FFA Order F-AE23FN16641-1-0 Completed by technician REDACTED in crew mbaco10(123) with code A-T-233 - Other Natural Disaster Action Taken : Replace Fallen HV Pin Pole Site Label : 5008430 Added notes to Reasons tab. | 1 | 9356345 | 2381 Mossman Mt Molloy Rd Julatten | 1294244 | J138 | 9356345 | 2022-09-15 |  |  | 0 | 12.5 | 1 | 0 | Serviceable | N | Rrl inter spn <200m | WOOD UNTREATED ROUND | Grass | Sugar Cane | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 9356345 | PO | 11.646 | 1 | 1722.6422 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | 1 | 261 | 1 | 6 | 0 | 825 | 22 | 0 | 0 | 99 | 0 | -16.6199 | 145.3261 | 1956 | PO5008430 | 000002486889 | 1950s | EASTERN/COASTAL
EECL | OT212083 | Operational |  | 2023-12-24 | 202312 | 2023-12-25 | Pole-Wood | Wood Pole Below Ground | Broken | Unknown - Wind | 0 | LV |  |  |  | 1563919 | 2024 | 23SW23189 | 2023-12-24 | 2023-12-25 15:27 |  |  | Normal Event | Storm Electrical | South West | 2023-12-24 10:34 | 2023-12-25 17:33 | Completed | Unplanned Outage | Severe Weather | Unknown | Single Fault Call | GT |  | 83 NORTH ST;HARLAXTON QLD 4350 | 3rd Party->Fault occurred at:24/12/2023 10:31; REDACTED;>WDPP --> AffectingTraffic:YES -- StillHavePower:NO<;Incident Details:Customer advises a Pole has fallen, and cars are trying to drive under the wire at the road;COVID-19:N/A;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N |  | 1 | 2418299 | 81 North St,Toowoomba | 1563919 | 2137455 | 2418299 | 2023-12-04 | N |  | 0 | 18.5 | 4 | 0 | Serviceable | Y | Rrl inter 3 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 12 kiloNewton | EECL | 2418299 | PO | 24.129 | 2 | 5378.7859 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 388 | 0 | 6 | 0 | 1235 | 35 | 0 | 0 | 98 | 0 | -27.5423 | 151.9567 | 1970 | PO2137455 | 000002418299 | 1970s | WESTERN
EECL | OT212101 | Operational |  | 2023-12-24 | 202312 | 2024-01-05 | Pole-Wood | Wood Pole Up To 2m | Broken | Unknown - Wind | 0 | 11kV |  |  |  | 1474060 | 2024 | 23SW22874 | 2023-12-24 | 2023-12-29 11:22 |  |  | Normal Event | Storm Electrical | South West | 2023-12-24 09:20 | 2023-12-24 09:23 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FE |  | BROOKSTEAD, PAMPAS | F-1853-r PAMPAS 11kV Yandilla Fdr CB CB4007 tripped. SCADA Interface automated outage. F-1668-r Original sheet Crew replaced 3 x HV poles and restrung HV conductors. SL 2054583. REDACTED | entered from the SCADA Interface Storm in Area Toowoomba call Foreman 4616 2637 - Left Message REDACTED No Fault Calls. Manual Reclose Checklist Reclose Unsuccessful Fysh Rd ACR CB591867 also tripped and Reclosed on OC Opened Fysh Rd. No Fault calls - Try Energise up to Fysh Rd Un Successful Asset selection reset customer beyond AB769059 fed from lemontree load shift Asset selection modified miloc01 Sending Asset Event to FFA FFA Order Created F-AE23SW22874-1-0 DfltHost Assets extracted from CB591867 (FYSH RD RECLOSER) into event 23SW22981 Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW22874-1-0 twmcs11 REDACTED 0427601845 FFA Order En Route F-AE23SW22874-1-0 twmcs11 FFA Order On Site F-AE23SW22874-1-0 twmcs11 Restoration Comments for F-AE23SW22874-1-0 by TWMCS11: isolated and earthed Time On modified from 23:59 24-Dec to 18:10 24-Dec Sending Asset Event to FFA HV Wires Down Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order F-AE23SW22874-1-0 Completed by technician REDACTED in crew TWMCS11(0427601845) with code A-T-317 - Severe Weather Action Taken : isolated and earthed . Site Label : 2054677 Asset selection modified Time On modified from 18:10 24-Dec to 23:59 24-Dec Line de-bridged @ SL2054677 and 3 TX's left off. unable to access due to water. Left isolated and earthed lines down beyond Time On modified from 23:59 24-Dec to 23:59 27-Dec . Time On modified from 23:59 27-Dec to 23:59 28-Dec Crew on site now to replace 3 HV poles TWMCM06 Sending Asset Event to FFA FFA Order Created F-AE23SW22874-1-1 DfltHost Poles Replaced. upstream outage to remake tee off tomorrow Time On modified from 23:59 28-Dec to 17:00 29-Dec Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Replay sequence/s deleted after 24-DEC-23 09:19:58 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 17:00 29-Dec to 11:43 29-Dec Sending Asset Event to FFA Time On modified from 11:43 29-Dec to 11:22 29-Dec Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW22874-1-1 twmcm06 REDACTED 0427704018 FFA Order En Route F-AE23SW22874-1-1 twmcm06 FFA Order On Site F-AE23SW22874-1-1 twmcm06 FFA Order F-AE23SW22874-1-1 Completed by technician REDACTED in crew twmcm06(0427704018) with code A-T-317 - Severe Weather Action Taken : Replaced 3 Hv poles and re strung HV conductors Site Label : 2054583 Updated Reasons tab. Reason for Event changed from Lightning / Storm | 1 | 9357104 | 2plS cnr Gilgai Ln/Gore Hwy,Pampas | 1474060 | 2054583 | 9357104 | 2021-10-28 |  |  | 0 | 12.5 | 1 | 0 | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Soil | Road Reserve | GB GREY BOX | 3 kiloNewton | EECL | 9357104 | PO | 12.107 | 0 | 1790.8813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 0 | 6 | 0 | 827 | 21 | 0 | 0 | 132 | 0 | -27.8009 | 151.3882 | 1992 | PO2054583 | 000002175084 | 1990s | WESTERN
EECL | OT212242 | Operational |  | 2023-12-24 | 202312 | 2023-12-27 | Pole-Wood | Wood Pole Up To 2m | Broken | Unknown - Wind | 0 | 19kV |  |  |  | 1140188 | 2024 | 23NQ15158 | 2023-12-24 | 2023-12-28 10:08 |  |  | Normal Event | Storm Electrical | North Queensland | 2023-12-24 16:44 | 2023-12-24 16:46 | Completed | Unplanned Outage | Lightning | Fallen Power Lines | due to fallen power lines. | FE |  | WINTON | F-2748-s - WINTON 19kV Elderslie Fdr CB B652 tripped. SCADA Interface automated outage. Pole and wire grounded after lightning strike. SL 5089499. REDACTED | entered from the SCADA Interface REDACTED will organise chopper for the AM, patrol at first lighrt. Issue to wntcdwgl1 Sending Asset Event to FFA FFA Order Created F-AE23NQ15158-1-0 DfltHost Sending Asset Event to FFA to be flown tomorrow morining. Time On modified from 23:59 24-Dec to 23:59 25-Dec Sending Asset Event to FFA Sending Asset Event to FFA REDACTED is currently in chopper patroling Sending Asset Event to FFA Pole down beyond DL800966 crews to isolate and earth . Sending Asset Event to FFA Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA Crews have other faults in the area, will need to come back to reapir pole down. fault isolated and earthed . Time On modified from 23:59 25-Dec to 23:59 26-Dec Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ15158-1-0 wntcdwgl1 REDACTED 0427893349 Time On modified from 23:59 26-Dec to 23:59 28-Dec Sending Asset Event to FFA FFA Order En Route F-AE23NQ15158-1-0 wntcdwgl1 FFA Order On Site F-AE23NQ15158-1-0 wntcdwgl1 FFA Order F-AE23NQ15158-1-0 Completed by technician REDACTED in crew wntcdwgl1(0427893349) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : pole down and broken wire from lightning strike Site Label : 5089499 Time On modified from 23:59 28-Dec to 10:08 28-Dec Reason for Event changed from Unknown Updated Reasons tab. Updated Event Trigger from HV-Unassisted failure to Lightning. | 1 | 9356647 | Bore t-off 6spns NW vindex hmstd winton | 1140188 | 5089499 | 9356647 | 2019-05-23 |  |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 9356647 | PO | 14.254 | 0 | 2108.3386 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -50 | 0 | 282 | 0 | 6 | 0 | 885 | 16 | 0 | 0 | 80 | 0 | -22.5355 | 143.3198 | 1979 | PO5089499 | 000003389679 | 1970s | WESTERN
EECL | OT212513 | Operational |  | 2023-12-25 | 202312 | 2024-02-12 | Pole-Wood | Wood Pole Up To 2m | Broken | Unknown - Wind | Made Safe | 19kV |  |  |  | 6877379 | 2024 | 23NQ15193 | 2023-12-25 | 2023-12-27 10:15 | M | A | Normal Event | Storm Electrical | North Queensland | 2023-12-25 00:49 | 2023-12-25 00:42 | Completed | Unplanned Outage | Lightning | Lightning / Storm | due to damage caused by storm activity. | FC |  | N/A | F-2751-s - Transient Fault of Unknown Origin on GLENELG 19kV RC797915 ACR CB Crew isolated and earthed feeder, crews to install temporary poles. SL 5060221. REDACTED | entered from the SCADA Interface Recloser tripped and locked out. Left for daylight hrs. issued to REDACTED 0427 893 349 crew ID - wntcdwgl1 Fault job F-2751-s created. Time Off modified from 00:39 25-Dec to 00:49 25-Dec Time On modified from 00:39 25-Dec to 23:59 25-Dec Reason for Event changed from Transient Fault of Unknown Origin Sending Asset Event to FFA FFA Order Created F-AE23NQ15193-1-0 DfltHost Sending Asset Event to FFA Crew to fly the line in daylight hrs Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ15193-1-0 wntcdwgl1 REDACTED 0427893349 Time On modified from 23:59 25-Dec to 23:59 26-Dec Sending Asset Event to FFA REDACTED advised pole down near WIS217 Sending Asset Event to FFA Pole/s Down Sending Asset Event to FFA REDACTED Sending Asset Event to FFA . Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA crews will attend in morning to finish repairs Time On modified from 23:59 26-Dec to 23:59 27-Dec Sending Asset Event to FFA FFA Order En Route F-AE23NQ15193-1-0 wntcdwgl1 FFA Order On Site F-AE23NQ15193-1-0 wntcdwgl1 FFA Order F-AE23NQ15193-1-0 Completed by technician REDACTED in crew wntcdwgl1(0427893349) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : isolated and earthed feeder crews to install temp poles Site Label : 5060221 Time On modified from 23:59 27-Dec to 23:59 28-Dec Time On modified from 23:59 28-Dec to 10:15 27-Dec auto-completed Added notes to Reasons tab. WIS23 removed via Clash Wizard as is captured in 23NQ15420 WIS176 removed via Clash Wizard as is captured in 23NQ15330 | 1 | 6877380 | 3 W TX217 930 Olio Faiview Rd Corfield | 6877379 | 5060221 | 6877380 | 2021-08-24 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | Y | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 3 kiloNewton | EECL | 6877380 | PO | 5.498 | 12 | 813.1873 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -340 | 20 | 203 | 5 | 6 | 0 | 715 | 16 | 0 | 0 | 88 | 0 | -21.8449 | 143.0598 | 1980 | PO5060221 | 000006877380 | 1980s | WESTERN
EECL | OT212527 | Operational |  | 2023-12-25 | 202312 | 2024-02-12 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay External | Made Safe | 19kV |  |  |  | 1791947 | 2024 | 23NQ15203 | 2023-12-25 | 2023-12-26 13:32 | M | A | Normal Event | Storm Electrical | North Queensland | 2023-12-25 01:23 | 2023-12-25 01:26 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FE |  | CORFIELD, WINTON, | F-2752-s - WINTON 19kV Rangelnds Fdr CB C652 tripped. SCADA Interface automated outage. Crew installed temporary pole due to wet weather. SL 5065891. REDACTED | entered from the SCADA Interface Recloser tripped and locked out. Left for daylight hrs. issuec to REDACTED 0427 893 349 Crew ID - wntcdwgl1 Fault job F-2752-s created. Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Created F-AE23NQ15203-1-0 DfltHost Crew to fly the line in depot hrs. Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ15203-1-0 wntcdwgl1 REDACTED 0427893349 Succesful reclose at 1232 after opening Temp Links at 5153600 towards Sub WIS233 Asset selection modified Sending Asset Event to FFA . Sending Asset Event to FFA Time On modified from 23:59 25-Dec to 23:59 26-Dec Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 26-Dec to 17:00 26-Dec Sending Asset Event to FFA Crews under access Sending Asset Event to FFA Time On modified from 17:00 26-Dec to 13:32 26-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23NQ15203-1-0 wntcdwgl1 FFA Order On Site F-AE23NQ15203-1-0 wntcdwgl1 FFA Order F-AE23NQ15203-1-0 Completed by technician REDACTED in crew wntcdwgl1(0427893349) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : installed temp pole due to wet weather Site Label : 5065891 Updated Reasons tab. Reason for Event changed from Lightning / Storm | 1 | 2822950 | 4spns e of webb stn hstd winton | 1791947 | 5065891 | 2822950 | 2020-10-17 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 2822950 | PO | 7.397 | 5 | 1094.0931 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8 | 224 | 2 | 6 | 0 | 746 | 16 | 0 | 0 | 95 | 12 | -22.0345 | 142.9511 | 1987 | PO5065891 | 000002822950 | 1980s | WESTERN
EECL | OT212557 | Operational |  | 2023-12-25 | 202312 | 2024-02-15 | Pole-Wood | Wood Pole Beyond 2m | Broken | Unknown - Wind | Made Safe | 19kV |  |  |  | 1185094 | 2024 | 23NQ15232 | 2023-12-25 | 2023-12-26 20:22 | M | A | Normal Event | Storm Electrical | North Queensland | 2023-12-25 05:08 | 2023-12-25 05:25 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FE |  | CORFIELD: CAMBERWARRA STATION, KENNEDY DEVELOPMENT HWY, KOONDI STATION, MANUKA ST, MANUKA STATION, RACECOURSE RES, RAILWAY STATION WINTON: CORFIELD SDNG, ESCOMBE STATION, KOONDI STATION | F-2757-s - Transient Fault of Unknown Origin on GLENELG 19kV Corfield ACR CB A652 Crew reported lots of damage found during aerial patrol. Crew installed temporary pole. SL 5063209. REDACTED | entered from the SCADA Interface Downstream Outages excluded from asset selection: 23NQ15193 CORFIELD SWER.PC (34 assets) Time Off modified from 05:21 25-Dec to 05:07 25-Dec Time On modified from 05:21 25-Dec to 05:20 25-Dec Recloser tripped to lock out. crews to fly the line in daylight hrs. Time On modified from 05:20 25-Dec to 23:59 25-Dec Storm in Area Sending Asset Event to FFA FFA Order Created F-AE23NQ15232-1-0 DfltHost issued to REDACTED 0437 738 649 huhcmfr01 Fault job F-2757-s created. Reason for Event changed from Transient Fault of Unknown Origin Sending Asset Event to FFA Crew reports a lot of damage found on aerial patrol. Will come back tomorrow as pilot has headed home Time On modified from 23:59 25-Dec to 23:59 26-Dec Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ15232-1-0 huhcs01 REDACTED 0437738649 Issue to Winton Sending Asset Event to FFA Assets extracted from RC797910 into event 23NQ15293 Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Closed A652- RC797910 and RC797915 open Sending Asset Event to FFA Replay sequence/s deleted after 25-DEC-23 05:07:42 Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ15232-1-0 wntcdwgl1 REDACTED 0427893349 FFA Order En Route F-AE23NQ15232-1-0 wntcdwgl1 FFA Order On Site F-AE23NQ15232-1-0 wntcdwgl1 FFA Order F-AE23NQ15232-1-0 Completed by technician REDACTED in crew wntcdwgl1(0427893349) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : installed temporary pole Site Label : 5063209 Time On modified from 23:59 26-Dec to 17:00 27-Dec Time On modified from 17:00 27-Dec to 10:15 27-Dec Reason for Event changed from Unknown Updated Reasons tab. Updated Event Trigger from Lightning to Severe Weather. To clear clashing events and duplicated customer minutes, Replay updated to reflect supply restoration at 2022 hrs 26/12 when Closed A652- RC797910 and RC797915 open, as customer minutes in relation to RC797915 caputured under original SCADA event 23NQ15193. Replay sequence/s deleted after 25-DEC-23 05:07:42 Time On modified from 10:15 27-Dec to 20:22 26-Dec | 1 | 2808180 | 7SthManukaSec1,12981KennedyDevRdCorfield | 1185094 | 5063209 | 2808180 | 2021-08-05 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 3 kiloNewton | EECL | 2808180 | PO | 11.006 | 4 | 1627.9538 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -50 | 6 | 256 | 2 | 6 | 0 | 828 | 16 | 0 | 0 | 96 | 0 | -21.7226 | 143.3881 | 1981 | PO5063209 | 000002808180 | 1980s | WESTERN
EECL | OT212823 | Operational |  | 2023-12-25 | 202312 | 2023-12-25 | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay | 0 | 19kV |  |  |  | 1046873 | 2024 | 23CA18467 | 2023-12-25 | 2023-12-25 21:05 | M | A | Normal Event | Storm Electrical | Capricornia | 2023-12-25 17:08 | 2023-12-25 17:11 | Completed | Unplanned Outage | Lightning | Fallen Power Lines | due to fallen power lines. | FC |  | ARAMAC: BOWEN DOWNS RD, TORRENS CREEK RD, OFF BOWEN DOWNS RD, ARAMAC-MUTTABURRA RD | F-2539-q BARCALDINE 19kV Ashra Downs X606266 CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface tripped to LO on OC crew advise electrical storm in the area Depot Co-ord Advised Storm in Area MRC unsuccessful crew advise to delay outage to tomorrow brccs01 Sending Asset Event to FFA FFA Order Created F-AE23CA18467-1-0 DfltHost Sending Asset Event to FFA Crew advised lines down 14 span past ACR. HV Wires Down Sending Asset Event to FFA Pole/s Down Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA18467-1-0 brccs01 REDACTED 0428110442 FFA Order En Route F-AE23CA18467-1-0 brccs01 FFA Order On Site F-AE23CA18467-1-0 brccs01 Time On modified from 23:59 25-Dec to 21:05 25-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23CA18467-1-0 Completed by technician REDACTED in crew brccs01(0428110442) with code A-T-317 - Severe Weather Action Taken : found pole snapped at ground level 14 span from start of ashra swer. erected temp pole under access to get power back on Site Label : 4133828 | 1 | 3152554 | 12 N X606266 1491 Muttaburra Aramac Rd | 1046873 | 4133828 | 3152554 | 2021-01-23 | N |  | 0 | 11 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 3152554 | PO | 7.583 | 6 | 979.4227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -400 | 10 | 215 | 2 | 6 | 0 | 714 | 16 | 0 | 0 | 108 | 0 | -22.6897 | 144.764 | 1966 | PO4133828 | 000003152554 | 1960s | WESTERN
EECL | OT212968 | Operational |  | 2023-12-26 | 202312 | 2023-12-27 | Pole-Wood | Wood Pole Up To 2m | Split | Unknown - Wind | 0 | 19kV |  |  |  | 1183355 | 2024 | 23FN16800 | 2023-12-25 | 2023-12-26 17:43 | M | A | Normal Event | Storm | Far North | 2023-12-25 19:03 | 2023-12-25 19:05 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FC |  | NORMANTON: IFFLEY RD, BURKETOWN RD, BURKE DEVELOPMENT RD, NEU MAYER VALLEY STATION | NORMANTON 33kV Poingdestre B533 ACR CB tripped. SCADA Interface automated outage. Crew replaced pole TM67 and installed temporary pole at CO34. SL 5223361. REDACTED | entered from the SCADA Interface Crew to fly tomorrow morning Time On modified from 23:59 25-Dec to 23:59 26-Dec Sending Asset Event to FFA FFA Order Created F-AE23FN16800-1-0 DfltHost FFA Order Acknowledged F-AE23FN16800-1-0 nrmcsfr01 REDACTED 0409450233 FFA Order En Route F-AE23FN16800-1-0 nrmcsfr01 FFA Order On Site F-AE23FN16800-1-0 nrmcsfr01 Crew have started patrol with helicopter Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Wires down beyond TT66.1 and TT66 Sending Asset Event to FFA Time On modified from 23:59 26-Dec to 17:43 26-Dec Sending Asset Event to FFA Restoration Comments for F-AE23FN16800-1-0 by nrmcsfr01: repaired ok earthed at 1058 26/12/23 supply restored 1743 paperwork to be completed tomorrow Restoration Comments for F-AE23FN16800-1-0 by nrmcsfr01: repaired ok earthed at 1058 26/12/23 supply restored 1743 paperwork to be completed tomorrow FFA Order F-AE23FN16800-1-0 Completed by technician REDACTED in crew nrmcsfr01(0409450233) with code A-T-317 - Severe Weather Action Taken : replaced 1 pole TM67 installed 1 temporary pole CO34 Site Label : 5223361 Actual Power Restoration for F-AE23FN16800-1-0: 26-DEC-2023 17:43:00 auto-completed Updated Reasons tab. Reason for Event changed from Unknown | 1 | 9356640 | 54 pole nth of t off to neumayer homeste | 1183355 | TM67 | 9356640 | 2018-08-17 |  |  | 0 | 14 | 1 | 0 | Serviceable | N | Duplex SWER | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | DS DARWIN STRINGYBAR | 5 kiloNewton | EECL | 9356640 | PO | 0 | 0 | 2708.2012 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 6 | 0 | 955 | 38 | 0 | 0 | 100 | 0 | -18.3552 | 140.2295 | 1988 | PO5223361 | 000003379141 | 1980s | EASTERN/COASTAL
EECL | OT214302 | Operational |  | 2023-12-29 | 202312 |  | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay | 0 | 22kV |  |  |  | 2719747 | 2024 | 23CA18939 | 2023-12-29 | 2023-12-29 19:57 |  |  | Normal Event | [5 empty] | Forced Outage | HV-Unassisted failure(Apparent defect) | Unknown | [6 empty] | 1 | [5 empty] | 2023-12-10 |  |  | 0 | 15.5 | 2 | 1 | Unserviceable - P2 | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | SG SPOTTED GUM | 8 kiloNewton | EECL | 0 | PO | 9.259 | 4 | 1716.8363 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -120 | 6 | 263 | 2 | 6 | 0 | 850 | 23 | 100 | 0 | 76 | 0 | -23.5046 | 148.155 | 1977 | PO4054596 | 000002719747 | 1970s | WESTERN
EECL | OT215318 | Operational |  | 2024-01-01 | 202401 | 2024-01-01 | Pole-Wood | Wood Pole Below Ground | Broken | Unknown - Wind | 0 | 33kV |  |  |  | 1905619 | 2024 | 23SW24121 | 2023-12-31 | 2024-01-01 14:10 | M | A | Normal Event | Storm Electrical | South West | 2023-12-31 23:00 | 2023-12-31 23:02 | Completed | Unplanned Outage | Severe Weather | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FE |  | BOLLON, ST GEORGE | F-2715-q ST GEORGE 33kV Stg Meatworks Fdr CB EB02Q00 tripped. SCADA Interface automated outage. 33kV pole grounded during storm. SL 6010809. REDACTED | entered from the SCADA Interface OC trip to L/O. F-2715-q Storm in Area AHC REDACTED advised storm overhead, wait til passes and attempt reclose Depot Co-ord Advised MRC unsucessful. AHC REDACTED advised delay until morning Time On modified from 23:59 31-Dec to 23:59 01-Jan stgcmfr03 Sending Asset Event to FFA FFA Order Created F-AE23SW24121-1-0 DfltHost FFA Order Acknowledged F-AE23SW24121-1-0 stgcmfr03 REDACTED 0448557051 Sending Asset Event to FFA supply restored up to 33kV Load Break AB AB586674 at 0613. Crew advised very wet, unable to patrol via vehicle, trying to arrange heli. Todd will call back with an update soon Asset selection modified Sending Asset Event to FFA Located pole down ETA 16.00 Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 01-Jan to 14:10 01-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23SW24121-1-0 stgcmfr03 FFA Order On Site F-AE23SW24121-1-0 stgcmfr03 FFA Order F-AE23SW24121-1-0 Completed by technician REDACTED in crew stgcmfr03(0448557051) with code A-T-317 - Severe Weather Action Taken : 33kv pole grounded from storm in area. Site Label : 6010809 Updated Reasons tab. Reason for Event changed from Unknown | 1 | 3029141 | 9 wst dl20403 acc via wagoo rd st george | 1905619 | 6010809 | 3029141 | 2020-09-29 | N |  | 0 | 12.5 | 1 | 0 | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 3029141 | PO | 9.471 | 3 | 1400.9386 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -200 | 4 | 243 | 2 | 6 | 0 | 782 | 22 | 0 | 0 | 97 | 0 | -28.0008 | 148.602 | 1967 | PO6010809 | 000003029141 | 1960s | WESTERN
EECL | OT215507 | Operational |  | 2024-01-01 | 202401 | 2024-01-01 | Pole-Wood | Wood Pole Below Ground | Broken | Unknown - Wind | 0 | 19kV |  |  |  | 1468981 | 2024 | 23SW24114 | 2023-12-31 | 2024-01-01 17:12 | M | A | Normal Event | Storm Electrical | South West | 2023-12-31 22:29 | 2023-12-31 22:32 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to a SCADA Automated Event | FC |  | CONDAMINE, GLENMORGAN, YULEBA, YULEBA CREEK | F-2714-q ROMA 19kV Combarngo CB765542 ACR CB tripped. SCADA Interface automated outage. Crew erected temporary pole. SL 4230599. REDACTED | entered from the SCADA Interface F-2714-q OC trip to L/O AHC REDACTED advised no issues with MRC Depot Co-ord Advised Time On modified from 23:59 31-Dec to 23:59 01-Jan AHC REDACTED advised delay intil morning romcm703 Sending Asset Event to FFA FFA Order Created F-AE23SW24114-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW24114-1-0 romcm703 REDACTED 0436279486 FFA Order En Route F-AE23SW24114-1-0 romcm703 Line down at Pole 4230599 Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA FFA Order On Site F-AE23SW24114-1-0 romcm703 Std Reason Changed from Unknown by REDACTED 0436279486 Restoration Comments for F-AE23SW24114-1-0 by romcm703: isolated and earth repairs under way Sending Asset Event to FFA Time On modified from 23:59 01-Jan to 17:12 01-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23SW24114-1-0 Completed by technician REDACTED in crew romcm703(0436279486) with code A-T-62 - Lightning Action Taken : erect temp pole Site Label : 4230599 Updated Reasons tab. Updated Event Trigger from Lightning to HV-Unassisted failure. | 1 | 9372204 | 10SpnWstPW1423,1298Lynn'sCrkRdCondamine | 1468981 | 4230599 | 9372204 | 2023-09-13 |  |  | 0 | 11 | 0 | 0 | Unserviceable - P2 | N | SWER inter | WOOD UNTREATED ROUND | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 9372204 | PO | 4.357 | 0 | 562.8229 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 6 | 0 | 578 | 16 | 0 | 0 | 92 | 0 | -26.9964 | 149.6263 | 1959 | PO4230599 | 000002968549 | 1950s | WESTERN
EECL | OT215565 | Operational |  | 2024-01-01 | 202401 | 2024-01-02 | Pole-Wood | Wood Pole Below Ground | Broken | Termites | 0 | 19kV |  |  |  | 1778999 | 2024 | 24NQ0051 | 2024-01-01 | 2024-01-02 12:26 |  |  | Normal Event | Storm | North Queensland | 2024-01-01 13:14 | 2024-01-01 16:22 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FC |  | BELYANDO CROSSING: CAERPHILLY STATION, DANDENONG STATION, JUMBA STATION CHARTERS TOWERS: GREGORY DEVELOPMENTAL RD SEVENTY MILE RANGE: GREGORY DEVELOPMENTAL RD | Pole Down adjacent MOONLIGHT CRK NO. crww to isolate & earth | Pole Down adjacent MOONLIGHT CRK NO. crww to isolate & earth Pole/s Down Sending Asset Event to FFA FFA Order Created F-AE24NQ0051-1-0 DfltHost issued to REDACTED chtfco01 Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ0051-1-0 chtfco01 REDACTED 0418735767 FFA Order En Route F-AE24NQ0051-1-0 chtfco01 FFA Order On Site F-AE24NQ0051-1-0 chtfco01 Restoration Comments for F-AE24NQ0051-1-0 by chtfco01: isolated and earthed at caerphilly recloser. repairs to be completed tomorrow works to be done tomorrow Sending Asset Event to FFA please allocate switching sheet and FFA job to REDACTED, CHTCS03 Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Pending F-AE24NQ0051-1-0 FFA Order Acknowledged F-AE24NQ0051-1-0 chtcs03 REDACTED 0418767751 FFA Order En Route F-AE24NQ0051-1-0 chtcs03 FFA Order On Site F-AE24NQ0051-1-0 chtcs03 FFA Order F-AE24NQ0051-1-0 Completed by technician REDACTED in crew CHTCS03(0418767751) with code A-T-317 - Severe Weather Action Taken : temp pole installed Site Label : 5214059 Time On modified from 23:59 02-Jan to 12:26 02-Jan | 1 | 3344697 | 3spns SW caerphilly homestead t-off | 1778999 | 5214059 | 3344697 | 2018-12-08 |  |  | 0 | 11 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 3344697 | PO | 0 | 0 | 854.4241 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -50 | 0 | 212 | 0 | 6 | 0 | 665 | 16 | 0 | 0 | 50 | 0 | -21.036 | 146.5813 | 1981 | PO5214059 | 000003344697 | 1980s | WESTERN
EECL | OT215662 | Operational |  | 2024-01-01 | 202401 | 2024-01-02 | Pole-Wood | Wood Pole Below Ground | Broken | Unknown - Wind | ? | 19kV |  |  |  | 1687383 | 2024 | 24NQ0058 | 2024-01-01 | 2024-01-02 15:23 |  |  | Normal Event | Storm Electrical | North Queensland | 2024-01-01 16:57 | 2024-01-01 17:00 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FE |  | CORFIELD, HUGHENDEN, STAMFORD | F-2851-s - GLENELG 19kV Vellum Downs ACR CB B652 tripped. SCADA Interface automated outage.\r\nCrew replaced pole that was grounded in storm. SL 524377. REDACTED | entered from the SCADA Interface\r\nOn Call Supervisor advised that line will be flown morning of Jan 2.\r\nTime On modified from 23:59 01-Jan to 23:59 02-Jan\r\nDelayed\r\n5242377 pole down as per FCL 2394676\r\nPole/s Down\r\nhuhcmfr03\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE24NQ0058-1-0 DfltHost\r\nFFA Order Acknowledged F-AE24NQ0058-1-0 huhcmfr03 REDACTED 0429969325\r\nFFA Order En Route F-AE24NQ0058-1-0 huhcmfr03\r\nFFA Order On Site F-AE24NQ0058-1-0 huhcmfr03\r\nRestoration Comments for F-AE24NQ0058-1-0 by huhcmfr03: needs new pole\r\nIsol & Earthed at Sect Roscavan No.1. Remainder of fdr restored. AP issued\r\nAsset selection modified\r\nTime On modified from 23:59 02-Jan to 16:00 02-Jan\r\nManual Reclose Checklist\r\nSending Asset Event to FFA\r\nHV Wires Down\r\nReason for Event changed from Unknown\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nTime On modified from 16:00 02-Jan to 15:23 02-Jan\r\nSending Asset Event to FFA\r\nFFA Order En Route F-AE24NQ0058-1-0 huhcmfr03\r\nFFA Order On Site F-AE24NQ0058-1-0 huhcmfr03\r\nFFA Order F-AE24NQ0058-1-0 Completed by technician REDACTED in crew huhcmfr03(0429969325) with code A-T-317 - Severe Weather\r\nAction Taken : replaced pole \r\nSite Label : 5242377\r\nauto-completed\r\nAdded notes to Reasons tab. | 1 | 9356996 | 6 pole NE cracrin homestead to vuna stn | 1687383 | 5242377 | 9356996 | 2020-11-27 |  |  | ? | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 9356996 | PO | 5.503 | 0 | 814.0369 | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | -40 | 0 | 209 | 0 | 6 | 0 | 718 | 16 | 0 | 0 | 100 | 60 | -21.445 | 143.4389 | 1998 | PO5242377 | 000002853399 | 1990s | WESTERN
EECL | OT215946 | Operational |  | 2024-01-02 | 202401 | 2024-01-03 | Pole-Wood | Wood Pole Beyond 2m | Split | Unknown - Wind | ? | 19kV |  |  |  | 1656370 | 2024 | 24NQ0099 | 2024-01-02 | 2024-01-03 14:09 |  |  | Normal Event | Storm Electrical | North Queensland | 2024-01-02 14:54 | 2024-01-02 14:57 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FC |  | MCKINLAY: | SANDILA STATION, CANNINGTON STATION\r\nJULIA CREEK: | CUKADOO STATION, TOOLEBUC STATION, GLENHOLME STATION, CANNINGTON STATION, DING A DING STATION, ANSWER DOWNS STATION F-2861-s\r\nJULIA CK 19kV Percol Plains No1 ACR CB tripped. SCADA Interface automated outage.\r\nCrew replaced pole due to pole top damage. Also installed temporary poles at SLs 2068155 and 2068152 due to broken poles. REDACTED entered from the SCADA Interface\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE24NQ0099-1-0 DfltHost\r\nFFA Order Acknowledged F-AE24NQ0099-1-0 jckcmcs01 REDACTED 0473859801\r\n REDACTED 0473 859 801 JCKCMCS01, Will orgaised a chopper 1st thing tomorrow\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 02-Jan to 23:59 03-Jan\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE24NQ0099-1-0 jckcmcs02 REDACTED 0473859801\r\nFFA Order En Route F-AE24NQ0099-1-0 jckcmcs02\r\n REDACTED 0473 859 801 advised he commencing line patrol.\r\nSending Asset Event to FFA\r\nCrews advised that there is 19.1kV Poles down SL 2068155, 2068152 and 2068055\r\nSending Asset Event to FFA\r\nPole/s Down\r\nReason for Event changed from Unknown\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nCrews are currently reverse switching\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 03-Jan to 14:09 03-Jan\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order On Site F-AE24NQ0099-1-0 jckcmcs02\r\nRestoration Comments for F-AE24NQ0099-1-0 by jckcmcs02: installed replacement pole at site label 2068055 and installed temporary pole at site label 2068155 & 2068152\r\nRestoration Comments for F-AE24NQ0099-1-0 by jckcmcs02: installed replacement pole at site label 2068055 and installed temporary pole at site label 2068155 & 2068152\r\nRestoration Comments for F-AE24NQ0099-1-0 by jckcmcs02: installed replacement pole at site label 2068055 and installed temporary pole at site label 2068155 & 2068152\r\nRestoration Comments for F-AE24NQ0099-1-0 by jckcmcs02: installed replacement pole at site label 2068055 and installed temporary pole at site label 2068155 & 2068152\r\nRestoration Comments for F-AE24NQ0099-1-0 by jckcmcs02: installed replacement pole at site label 2068055 and installed temporary pole at site label 2068155 & 2068152\r\nFFA Order F-AE24NQ0099-1-0 Completed by technician REDACTED in crew jckcmcs02(0473859801) with code A-T-317 - Severe Weather\r\nAction Taken : replace pole due to pole top damage, also installed temporary poles at s/l 2068155 & 2068152 due to broken poles\r\nSite Label : 2068055\r\nActual Power Restoration for F-AE24NQ0099-1-0: 03-JAN-2024 15:16:00\r\nauto-completed\r\nAdded notes to Reasons tab. | 1 | 9357014 | 5 nth homestead 3way cannington stn MCK | 1656370 | 2068055 | 9357014 | 2020-05-13 |  |  | ? | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 9357014 | PO | 9.542 | 0 | 1411.4057 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 0 | 6 | 0 | 795 | 16 | 0 | 0 | 100 | 20 | -21.8967 | 140.8992 | 1983 | PO2068055 | 000002194643 | 1980s | WESTERN
EECL | OT216005 | Operational |  | 2024-01-02 | 202401 |  | Pole-Wood | Wood Pole Up To 2m | Broken | Unknown - Wind | 0 | 19kV |  |  |  | 826575 | 2024 | 24NQ0110 | 2024-01-02 | 2024-01-04 20:18 |  |  | Normal Event | Wind | North Queensland | 2024-01-02 18:41 | 2024-01-02 18:43 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FE |  | CLONCURRY, KAJABBI | F-2883-s NTH CLONCURY 11kV NC02 Fdr CB B252 tripped. SCADA Interface automated outage. Crew installed temporary pole due to grounded pole. SL 5026047. Crew also fixed blown insulators at SLs 5026029 and 10985692. REDACTED. | entered from the SCADA Interface Sending Asset Event to FFA FFA Order Created F-AE24NQ0110-1-0 DfltHost Storm in Area Sending Asset Event to FFA Kajabbi Gen turned on @ 1959 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Fault believed to be in the SWER's which failure of Cloncurry SWER NO.1 failing to operate tripping back at Sub Time On modified from 23:59 02-Jan to 23:59 03-Jan Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ0110-1-0 clccmcs01 REDACTED 0427701876 FFA Order En Route F-AE24NQ0110-1-0 clccmcs01 FFA Order On Site F-AE24NQ0110-1-0 clccmcs01 FFA Order En Route F-AE24NQ0110-1-0 clccmcs01 FFA Order On Site F-AE24NQ0110-1-0 clccmcs01 FFA Order F-AE24NQ0110-1-0 Completed by technician REDACTED in crew clccmcs01(0427701876) with code A-T-317 - Severe Weather Action Taken : scoped line isolated and made safe fault and re energised Site Label : B252 Depot Co-ord Advised Crews to fly line this morning Crew advised trhat there is 2 poles down at 5025979 andjacent CLS40. Crew to Isolate and earth 19.1kV Link Cloncurry West No.1 and 19.1kV Link New Jersey Plains No.1 . HV Wires Down Reason for Event changed from Unknown Cloncurry Nth SWER ACR had no comms to close in after repairs. crews attended to close in locally but weather was too unsafe to complete. to be continiued in the AM 4/1 Asset selection modified Asset selection modified Time On modified from 23:59 03-Jan to 17:00 04-Jan Suspected blown bypass fuse to the Mindie ACR, crews are running low on hours and large storm in the area. to attend in the AM 4/1 Asset selection modified Suspected blown by pass fuse on the Cloncurry east leg Asset selection modified Centre fuse was still closed, which is the Cloncurry North line. Reclose attempt on Cloncurry North recloser successful Asset selection modified Kurt advised test prove de-energised on the load side of Cloncurry SWER No.1, the last bypass fuse must have blown Asset selection modified Clooncurry North Recloser Closed at 1301 Asset selection modified Asset selection modified 19.1kV Mindie Recloser Failed on attempt to close. Crews to fly line beyond to find fault 19.1kV Carsland Recloser closed at 1609 Asset selection modified Crew advise that there is a Pole down adjacent CLS42, and broken insulator on pole 10985692. Isolation and access to be taken beyond 19.1kV Mindie Recloser Time On modified from 17:00 04-Jan to 21:00 04-Jan Mindie Recloser Closed after repairs made @ 2018 Time On modified from 21:00 04-Jan to 20:18 04-Jan Sending Asset Event to FFA FFA Order Created F-AE24NQ0110-1-1 DfltHost FFA Order Acknowledged F-AE24NQ0110-1-1 clccmcs01 REDACTED 0427701876 FFA Order En Route F-AE24NQ0110-1-1 clccmcs01 FFA Order On Site F-AE24NQ0110-1-1 clccmcs01 FFA Order F-AE24NQ0110-1-1 Completed by technician REDACTED in crew clccmcs01(0427701876) with code A-T-317 - Severe Weather Action Taken : pole down installed temp pole to re energise also fixed the following 5026029 blown insulator 10985692 blown insulator Site Label : 5026047 Actual Power Restoration for F-AE24NQ0110-1-1: 04-JAN-2024 20:30:00 Added notes to Reasons tab. | 1 | 2593059 | 19p E Mindi rec1 on ilkley stn Cloncurry | 826575 | 5026047 | 2593059 | 2019-07-04 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | Y | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | EECL | 2593059 | PO | 15.605 | 0 | 2308.2232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 6 | 0 | 900 | 16 | 0 | 0 | 143 | 0 | -20.6172 | 140.6259 | 2001 | PO5026047 | 000002593059 | 2000s | WESTERN
EECL | OT216286 | Operational |  | 2024-01-03 | 202401 | 2024-01-04 | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay External | 0 | 19kV |  |  |  | 1070789 | 2024 | 24SW0281 | 2024-01-03 | 2024-01-04 18:57 |  |  | Normal Event | Storm Electrical | South West | 2024-01-03 19:40 | 2024-01-04 07:52 | Completed | Unplanned Outage | Lightning | Fallen Power Lines | due to fallen power lines. | SZ |  | QUILPIE: CONGIE RD, COOPER DEVELOPMENTAL RD | F-2790-q - Crew found 19.1kV SWER Recloser CB7102 has opened during a single fault call investigation FFA Order F-AE24SW0281-1-0 Completed by technician REDACTED with code A-T-62 - Lightning Action Taken : 7 swer poles broken cause of wind. 7 temporary poles stood, REDACTED has photos if required Site Label : 6025085 | Crew found 19.1kV SWER Recloser CB7102 has opened during a single fault call investigation quloc03 Sending Asset Event to FFA FFA Order Created F-AE24SW0281-1-0 DfltHost MRC unsuccessful at 08:19 Sending Asset Event to FFA crew to sectionalise Sending Asset Event to FFA Sending Asset Event to FFA Crews found poles down and broken conductors past DL8107 HV Wires Down Pole/s Down Reason for Event changed from Unknown Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 04-Jan to 18:57 04-Jan Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW0281-1-0 quloc03 REDACTED 0429373407 FFA Order En Route F-AE24SW0281-1-0 quloc03 FFA Order On Site F-AE24SW0281-1-0 quloc03 FFA Order F-AE24SW0281-1-0 Completed by technician REDACTED in crew QULOC03(0429373407) with code A-T-62 - Lightning Action Taken : 7 swer poles broken cause of wind. 7 temporary poles stood, REDACTED has photos if required Site Label : 6025085 | 1 | 2965360 | 1 NW PW4308 acc Congie Rd Eromanga | 1070789 | 6025085 | 2965360 | 2021-09-06 | N |  | 0 | 11 | 0 | 0 | Serviceable | Y | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 2965360 | PO | 10.817 | 8 | 1397.2426 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -80 | 10 | 243 | 5 | 6 | 0 | 810 | 16 | 0 | 0 | 92 | 0 | -26.7422 | 143.592 | 1984 | PO6025085 | 000002965360 | 1980s | WESTERN
EECL | OT216365 | Operational |  | 2024-01-04 | 202401 | 2024-01-04 | Pole-Wood | Wood Pole Below Ground | Broken | Termites | ? | 19kV |  |  |  | 925750 | 2024 | 24NQ0260 | 2024-01-04 | 2024-01-04 15:18 |  |  | Normal Event |  | North Queensland | 2024-01-04 09:22 | 2024-01-04 09:26 | Completed | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FE |  | CLONCURRY | Cloncurry South Noi.1 opened for public safety. REDACTED sent photo from public SWER line 1m from ground\r\nCrew replaced SWER pole. SL 2142894. REDACTED | Cloncurry South Noi.1 opened for public safety. REDACTED sent photo from public SWER line 1m from ground\r\nTime Off modified from 11:22 04-Jan to 09:22 04-Jan\r\nHV Wires Down\r\nA/WGL REDACTED 0400 893 092 advised depot is waiting for helicopter to become available, once arrived patrols will commence.\r\nCrew device ID will be updated when known.\r\nDepot Co-ord Advised\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE24NQ0260-1-0 DfltHost\r\nFFA Order Acknowledged F-AE24NQ0260-1-0 clccs02 REDACTED 0400893092\r\nFFA Order En Route F-AE24NQ0260-1-0 clccs02\r\nFFA Order On Site F-AE24NQ0260-1-0 clccs02\r\nFFA Order F-AE24NQ0260-1-0 Completed by technician REDACTED in crew clccs02(0400893092) with code A-F-C - Completed\r\nAction Taken : replace SWER pole\r\nSite Label : 2142894\r\nTime On modified from 23:59 04-Jan to 15:18 04-Jan\r\nauto-completed\r\nAdded notes to Reasons tab. | 1 | 9357063 | 23 sp Sth Bore CLS216 Round Oak Station | 925750 | 2142894 | 9357063 | 2020-08-15 |  |  | ? | 11 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Rock | Paddock Grazing | GI GREY IRONBARK | 3 kiloNewton | EECL | 9357063 | PO | 10.083 | 0 | 1153.9328 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | -120 | 0 | 236 | 0 | 6 | 0 | 741 | 16 | 0 | 0 | 58 | 0 | -20.7921 | 140.5263 | 1981 | PO2142894 | 000002364406 | 1980s | WESTERN
EECL | OT216498 | Operational |  | 2024-01-04 | 202401 | 2024-01-06 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | ? | 19kV |  |  |  | 829517 | 2024 | 24FN0149 | 2024-01-04 | 2024-01-06 17:33 |  |  | Normal Event | Storm Electrical | Far North | 2024-01-04 19:50 | 2024-01-04 19:52 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | SZ |  | NORMANTON: | IFFLEY RD | NORM - Burketown Fdr - Recloser IF240 Opened for public safety due to lines down call F/C - 2395615\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE24FN0149-1-0 DfltHost\r\nCrews advised they wont be attending untill morning 5/1/23 due to storms and 2 hr drive.\r\nSending Asset Event to FFA\r\nIsol & earthed at Sect IF421. Rest of cust restored\r\nAsset selection modified\r\nHV Wires Down\r\nManual Reclose Checklist\r\nSending Asset Event to FFA\r\nReplay sequence time changed from 05-JAN-24 10:05:50 to 05-Jan-24 10:49:00\r\nSending Asset Event to FFA\r\nCrews have advised job pushed out until tomorrow due to weather conditions\r\nTime On modified from 23:59 05-Jan to 16:00 06-Jan\r\nSending Asset Event to FFA\r\n.\r\nSending Asset Event to FFA\r\nREDACTEDadv poor access due to wet weather. Maybe access later today\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nTime On modified from 16:00 06-Jan to 16:00 07-Jan\r\nSending Asset Event to FFA\r\nTime On modified from 16:00 07-Jan to 17:33 06-Jan\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE24FN0149-1-0 nrmoc01 REDACTED 0428153642\r\nFFA Order En Route F-AE24FN0149-1-0 nrmoc01\r\nFFA Order On Site F-AE24FN0149-1-0 nrmoc01\r\nFFA Order F-AE24FN0149-1-0 Completed by technician REDACTED in crew nrmoc01(0428153642) with code A-T-306 - HV-Unassisted failure(Apparent defect)\r\nAction Taken : Replaced pole after pole top snapped off\r\nSite Label : 5041994\r\nAdded notes to Reasons tab. | 1 | 9357143 | iffley station homestead | 829517 | IF563 | 9357143 | 2022-07-25 |  |  | ? | 14 | 0 | 0 | Serviceable | N | SWER sty angle | WOOD (GREEN) SALT IMPREG CCA | Soil | Backyard | FR FOREST RED GUM | 12 kiloNewton | EECL | 9357143 | PO | 21.901 | 0 | 4492.5063 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | -150 | 0 | 363 | 0 | 1 | 0 | 1160 | 64 | 0 | 0 | 100 | 20 | -18.8707 | 141.2044 | 1989 | PO5041994 | 000002686389 | 1980s | WESTERN
EECL | OT216767 | Operational |  | 2024-01-06 | 202401 | 2024-01-06 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay External | ? | 11kV |  |  |  | 1596099 | 2024 | 24SW0434 | 2024-01-05 | 2024-02-29 10:58 |  |  | Normal Event |  | South West | 2024-01-05 19:34 | 2024-01-05 19:36 | Completed | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | WARWICK | F-2808-q - 11kV Gas Switch AB614371 - Crew request feeder be tripped due to pole failure at DL579686\r\n | 11kV Gas Switch AB614371 - Crew request feeder be tripped due to pole failure at DL579686\r\nTime Off modified from 20:00 05-Jan to 19:33 05-Jan\r\nCrew advise pole has now fallen over, isolation and earthing underway\r\nHV Wires Down\r\nLV Wires Down\r\nPole/s Down\r\nSupply restored up to AB14350 2018\r\nAsset selection modified\r\nBackfeed to GE00196 2040\r\nAsset selection modified\r\nCrew plan to stand new pole tonight and leave HV Cable Disconnected, will return next week to reconnect HV Cable\r\nTime On modified from 23:59 05-Jan to 05:00 06-Jan\r\nAsset selection modified\r\ncrwe to return to install HV cable and Links DL579686\r\nTime On modified from 05:00 06-Jan to 16:00 06-Jan\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE24SW0434-1-0 DfltHost\r\nFFA Order Acknowledged F-AE24SW0434-1-0 waroc01 REDACTED 0431073082\r\nFFA Order En Route F-AE24SW0434-1-0 waroc01\r\nFFA Order On Site F-AE24SW0434-1-0 waroc01\r\nFFA Order F-AE24SW0434-1-0 Completed by technician REDACTED in crew waroc01(0431073082) with code A-F-C - Completed\r\nAction Taken : Replaced 11kv pole that fell to the ground due to rot.\r\nSite Label : 3201281\r\nas above\r\nTime On modified from 16:00 06-Jan to 16:00 08-Jan\r\nTime On modified from 16:00 08-Jan to 16:00 12-Jan\r\nCrew to return to repair cable\r\nTime On modified from 16:00 12-Jan to 12:00 31-Jan\r\nTime On modified from 12:00 31-Jan to 12:00 01-Feb\r\nTime On modified from 12:00 01-Feb to 12:00 27-Feb\r\nTime On modified from 12:00 27-Feb to 14:30 27-Feb\r\nTime On modified from 14:30 27-Feb to 14:30 27-Mar\r\nThis Forced event has been completed. \r\nPlanned Outage 24SW5478 is scheduled for repairs to be made \r\non 18/03/24.\r\nF-2808-q has been terminated at Operation 34 to allow Planned \r\nSchedule / AFW to proceed.\r\n.\r\nNOTE: Links DL579686 are not installed currently and will be erected by crew under Planned Outage 24SW5478. Undeground cable is on ground and earthed and baricaded. Also GE00196 is fed from normally open point SD19414.\r\nTime On modified from 14:30 27-Mar to 10:57 29-Feb\r\nUpdated Asset Event Type from Transmission to Distribution. | 1 | 9357223 | 17 Golf Links Ave Warwick | 1596099 | 3201281 | 9357223 | 2021-03-09 |  |  | ? | 12.5 | 2 | 1 | Serviceable | Y | Urb unsty trm>=2cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 8 kiloNewton | EECL | 9357223 | PO | 16.967 | 0 | 2509.7274 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 14 | 0 | 939 | 10 | 0 | 0 | 100 | 0 | -28.1952 | 152.0321 | 1982 | PO3201281 | 000002341020 | 1980s | WESTERN
EECL | OT216812 | Operational |  | 2024-01-06 | 202401 |  | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay External | 0 | 12.7kV |  |  |  | 1995424 | 2024 | 24SW0455 | 2024-01-06 | 2024-01-06 14:19 |  |  | Normal Event | Storm Electrical | South West | 2024-01-06 06:20 | 2024-01-06 06:23 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | BLYTHDALE, ROMA | F-2111-r - ROMA 12kV Warooby RC807108 ACR CB tripped. SCADA Interface automated outage. Broken wire and broken pole at SL 3308307 REDACTED | entered from the SCADA Interface Advised by WGL - do not attempt reclose unitil line patrol performed. Line patrol performed as advised by crew Sending Asset Event to FFA FFA Order Created F-AE24SW0455-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW0455-1-0 romcm713 REDACTED 0437386198 FFA Order En Route F-AE24SW0455-1-0 romcm713 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 06-Jan to 14:18 06-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order On Site F-AE24SW0455-1-0 romcm713 FFA Order F-AE24SW0455-1-0 Completed by technician REDACTED in crew romcm713(0437386198) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : broken wire, and broken pole at 3308307. access too difficult to proceed. de bridged and earthed at 3308303 Site Label : 3308307 Reason for Event changed from Unknown Updated Reasons tab. Updated Event Trigger from Lightning to HV-Unassisted failure. | 1 | 9367124 | Tee to tower,1222 Burtons Rd,Blythdale | 1995424 | 3308307 | 9367124 | 2021-03-09 |  |  | 0 | 12.5 | 2 | 1 | Serviceable | Y | Urb unsty trm>=2cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 8 kiloNewton | EECL | 9367124 | PO | 16.967 | 0 | 2509.7274 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 14 | 0 | 939 | 10 | 0 | 0 | 100 | 0 | -28.1952 | 152.0321 | 1958 | PO3308307 | 000002752454 | 1950s | WESTERN
EECL | OT216979 | Operational |  | 2024-01-07 | 202401 | 2024-01-13 | Pole-Wood | Wood Pole Beyond 2m | Broken | Termites | ? | 33kV |  |  |  | 928138 | 2024 | 24NQ0427 | 2024-01-07 | 2024-01-12 17:09 |  |  | Normal Event | Wet / Rain | North Queensland | 2024-01-07 16:50 | 2024-01-07 16:52 | Completed | Unplanned Outage | Animal Insects (termites/borers/white ants) | Fallen Power Lines | due to fallen power lines. | FC |  | COLLINSVILLE: | MYUNA STATION, KERALE STATION, BIRRALEE STATION, GLEN BOWEN STATION | entered from the SCADA Interface\r\nREDACTED advised will organise chopper and attend in morning\r\nTime On modified from 23:59 07-Jan to 23:59 08-Jan\r\nEF/OC Trip to Lockout\r\nIssued to REDACTED 0437 504 343, bwnoh04.\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE24NQ0427-1-0 DfltHost\r\nFFA Order Acknowledged F-AE24NQ0427-1-0 bwnoh04 REDACTED 0437504343\r\nFFA Order En Route F-AE24NQ0427-1-0 bwnoh04\r\nCrew are heading Collinsville.\r\nSending Asset Event to FFA\r\nFFA Order On Site F-AE24NQ0427-1-0 bwnoh04\r\ncrews found pole snapped and wires down at 5076128 - isolating and earthing at Bowen River no.11 and Bowen River nmo.3- access very difficult - may be out for some time\r\nSending Asset Event to FFA\r\REDACTED adv due to poor access conditions - will reassess by Fri 12/1.\r\nTime On modified from 23:59 08-Jan to 23:59 12-Jan\r\nSending Asset Event to FFA\r\nHV Wires Down\r\nReason for Event changed from Unknown\r\nSending Asset Event to FFA\r\nFFA Order Suspended F-AE24NQ0427-1-0 by REDACTED 0437504343\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 12-Jan to 18:30 12-Jan\r\nSending Asset Event to FFA\r\nCrews adv will be commencing reverse switching later this afternoon.\r\nManual Reclose Checklist\r\nSending Asset Event to FFA\r\nTime On modified from 18:30 12-Jan to 17:09 12-Jan\r\nSending Asset Event to FFA\r\nFFA Order En Route F-AE24NQ0427-1-0 bwnoh04\r\nFFA Order On Site F-AE24NQ0427-1-0 bwnoh04\r\nFFA Order F-AE24NQ0427-1-0 Completed by technician REDACTED in crew bwnoh04(0437504343) with code A-T-299 - Animal Insects (termites/borers/white ants)\r\nAction Taken : pole full of white ants snapped\r\nSite Label : 5076127\r\nauto-completed\r\nAdded notes to Reasons tab. | 1 | 9358502 | Near Biralee HVL1 Myuna Rd CollinsVille | 928138 | 5076127 | 9358502 | 2020-11-29 |  |  | ? | 14 | 3 | 0 | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | RI RED IRONBARK | 8 kiloNewton | EECL | 9358502 | PO | 31.032 | 0 | 5171.9406 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | -50 | 0 | 382 | 0 | 10 | 0 | 1220 | 45 | 0 | 0 | 100 | 20 | -20.6158 | 147.6493 | 1981 | PO5076127 | 000002875506 | 1980s | EASTERN/COASTAL
EECL | OT217578 | Operational |  | 2024-01-10 | 202401 | 2024-02-06 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | 0 | 22kV |  |  |  | 1132241 | 2024 | 24SW0760 | 2024-01-10 | 2024-01-11 09:38 |  |  | Normal Event | Storm Electrical | South West | 2024-01-10 17:02 | 2024-01-10 17:05 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FE |  | CUNNAMULLA, EULO, HUNGERFORD, THARGOMINDAH, YOWAH | F-2156-r CUNNAMULLA 22kV Eulo Fdr CB 7864 tripped. SCADA Interface automated outage. 22kV pole broken off at SL 4251516 during storm - Crew stood temporary pole. REDACTED | entered from the SCADA Interface Crew to commence line patrol Depot Co-ord Advised Storm in Area F-2156-r Manual Reclose Checklist REDACTED advised 22kV pole broken off at SL 4251516, Crews to install temp poles to restore supply HV Wires Down Pole/s Down Reason for Event changed from Unknown cuncmfr03 Sending Asset Event to FFA FFA Order Created F-AE24SW0760-1-0 DfltHost FFA Order Acknowledged F-AE24SW0760-1-0 cuncmfr03 REDACTED 0436486711 FFA Order En Route F-AE24SW0760-1-0 cuncmfr03 FFA Order On Site F-AE24SW0760-1-0 cuncmfr03 REDACTED adised delayed until Time On modified from 23:59 10-Jan to 12:00 11-Jan Sending Asset Event to FFA Crew advised that they will return in the morning as it is too wet at the moment Sending Asset Event to FFA Time On modified from 12:00 11-Jan to 23:59 11-Jan Sending Asset Event to FFA Time On modified from 23:59 11-Jan to 09:38 11-Jan Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE24SW0760-1-0 cuncmfr03 FFA Order On Site F-AE24SW0760-1-0 cuncmfr03 FFA Order F-AE24SW0760-1-0 Completed by technician REDACTED in crew cuncmfr03(0436486711 ) with code A-T-317 - Severe Weather Action Taken : pole broke off above 2m during storm, stood temp pole Site Label : 4251516 Reason for Event changed from Lightning / Storm Updated Reasons tab. Updated Event Trigger from Lightning to Severe Weather. | 1 | 3023977 | 3 W DL15166 Bulloo Dev' Rd Cunnamulla | 1132241 | 4251516 | 3023977 | 2021-11-09 | N |  | 0 | 14 | 1 | 0 | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | BB BLACKBUTT | 8 kiloNewton | EECL | 3023977 | PO | 16.134 | 0 | 2689.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 6 | 0 | 947 | 22 | 0 | 0 | 151 | 0 | -28.0652 | 145.6655 | 1997 | PO4251516 | 000003023977 | 1990s | WESTERN
EECL | OT217714 | Operational |  | 2024-01-11 | 202401 | 2024-01-11 | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay | 0 | 19kV |  |  |  | 1843571 | 2024 | 24NQ0620 | 2024-01-11 | 2024-01-11 20:49 |  |  | Normal Event | Storm Electrical | North Queensland | 2024-01-11 12:17 | 2024-01-11 12:21 | Completed | Unplanned Outage | Lightning | Fallen Power Lines | due to fallen power lines. | FC |  | PRAIRIE, TORRENS CREEK | F-2955-s - HUGHENDEN 19kV PrairieSth 1 SWERACR CB tripped. SCADA Interface automated outage. Crew stood temporary poles at SLs 5022087 and 5022088 REDACTED | entered from the SCADA Interface OC Trip x 3 to lockout Sending Asset Event to FFA FFA Order Created F-AE24NQ0620-1-0 DfltHost Sending Asset Event to FFA Crew advised two poles down 5022087 and 5022088 updated estimated completion time. Time On modified from 23:59 11-Jan to 20:00 11-Jan Pole/s Down Sending Asset Event to FFA FFA Order Pending F-AE24NQ0620-1-0 FFA Order Acknowledged F-AE24NQ0620-1-0 huhcdwgl1 REDACTED 0437738649 FFA Order Acknowledged F-AE24NQ0620-1-0 huhcmfr01 REDACTED 0437489468 FFA Order En Route F-AE24NQ0620-1-0 huhcmfr01 FFA Order On Site F-AE24NQ0620-1-0 huhcmfr01 Reverse switching commenced. Time On modified from 20:00 11-Jan to 21:00 11-Jan Reason for Event changed from Unknown Sending Asset Event to FFA Restoration Comments for F-AE24NQ0620-1-0 by huhcmfr01: isolated and earthed then stood temp pole top restore supply Manual Reclose Checklist Sending Asset Event to FFA Time On modified from 21:00 11-Jan to 20:49 11-Jan Sending Asset Event to FFA FFA Order F-AE24NQ0620-1-0 Completed by technician REDACTED in crew huhcmfr01(0437489468) with code A-T-62 - Lightning Action Taken : stood temp poles at S/l 5022087 and 5022088 Site Label : 5022087 auto-completed Added notes to Reasons tab. | 1 | 2566832 | 10 sth of nth boundry curragilla stn PR | 1843571 | 5022088 | 2566832 | 2019-10-08 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 2566832 | PO | 6.201 | 8 | 917.258 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -130 | 10 | 213 | 5 | 6 | 0 | 715 | 16 | 0 | 0 | 92 | 0 | -21.0715 | 144.6239 | 1982 | PO5022088 | 000002566832 | 1980s | WESTERN
EECL | OT217720 | Operational |  | 2024-01-11 | 202401 | 2024-01-23 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay | 0 | 19kV |  |  |  | 1164191 | 2024 | 24SW0823 | 2024-01-11 | 2024-01-12 14:01 |  |  | Normal Event | Storm Electrical | South West | 2024-01-11 13:08 | 2024-01-11 13:11 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | EULO: YERREL RD, TOOMPINE RD, BULLOO DEVELOPMENTAL RD YOWAH: BLUFF RD CUNNAMULLA: YOWAH RD, MITCHELL HWY, BULLOO DEVELOPMENTAL RD, QUILPIE-THARGOMINDAH RD THARGOMINDAH: QUILPIE-THARGOMINDAH RD | F-2164-r CUNNAMULLA 19kV Eulo North CB596828 CB tripped. SCADA Interface automated outage. Crew installed temporary pole. SL 6061496. REDACTED | entered from the SCADA Interface Tripped to lockout, OC Depot Co-ord Advised Storm in Area Message left for REDACTED F-2164-r Sending Asset Event to FFA FFA Order Created F-AE24SW0823-1-0 DfltHost FFA Order Acknowledged F-AE24SW0823-1-0 cuncmfr01 REDACTED 0448688742 crew request to perform a MRC and atempt a close - Fail Manual Reclose Checklist Sending Asset Event to FFA Chopper to fly the line cuncmfr02. Sending Asset Event to FFA . Time On modified from 23:59 11-Jan to 23:59 12-Jan Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW0823-1-0 cuncmfr02 REDACTED 0417579960 FFA Order En Route F-AE24SW0823-1-0 cuncmfr02 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 12-Jan to 14:01 12-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order On Site F-AE24SW0823-1-0 cuncmfr02 FFA Order F-AE24SW0823-1-0 Completed by technician REDACTED in crew cuncmfr02(0417579960) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : temp pole installed Site Label : 6061496 Reason for Event changed from Unknown Updated Reasons tab. Updated Event Trigger from Lightning to HV-Unassisted failure. | 1 | 2637589 | pw3316-pw3239 toompine rd eulo | 1164191 | 6061496 | 2637589 | 2019-11-14 | N |  | 0 | 11 | 0 | 0 | Serviceable | Y | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 2637589 | PO | 14.433 | 0 | 1864.2897 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -100 | 0 | 267 | 0 | 6 | 0 | 840 | 16 | 0 | 0 | 100 | 0 | -27.9046 | 144.785 | 1975 | PO6061496 | 000002637589 | 1970s | WESTERN
EECL | OT217796 | Operational |  | 2024-01-11 | 202401 | 2024-01-12 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | ? | 19kV |  |  |  | 1653943 | 2024 | 24CA0719 | 2024-01-11 | 2024-01-12 15:46 |  |  | Normal Event | Fine | Capricornia | 2024-01-11 18:12 | 2024-01-11 18:14 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to a SCADA Automated Event | FC |  | BLACKALL: | MIMOSA ST, FRAMES LANE, RAVENSBOURNE RD, EMMET-BLACKALL RD, ISISFORD BLACKALL RD, OFF LANDSBOROUGH HWY, OFF ISISFORD-B'ALL RD | entered from the SCADA Interface\r\nDepot Co-ord Advised\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE24CA0719-1-0 DfltHost\r\nPtrolling 1st section through populated area before reclose attempt\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE24CA0719-1-0 bklcdwgl1 REDACTED 0455518385\r\nFFA Order En Route F-AE24CA0719-1-0 bklcdwgl1\r\nline finished posable sectionalising, crew now patrolling\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 11-Jan to 23:59 12-Jan\r\nSending Asset Event to FFA\r\nCrews to return in daylight\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 12-Jan to 15:00 12-Jan\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nCrew advised bklp201.\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE24CA0719-1-0 bklp201 REDACTED 0436293991\r\nFFA Order En Route F-AE24CA0719-1-0 bklp201\r\nFFA Order On Site F-AE24CA0719-1-0 bklp201\r\nStd Reason Changed from Unknown by REDACTED 0436293991\r\nRestoration Comments for F-AE24CA0719-1-0 by bklp201: Swer pin toff pole- poles snapped off at stay area.\r\nTime On modified from 15:00 12-Jan to 16:00 12-Jan\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nTime On modified from 16:00 12-Jan to 15:45 12-Jan\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order F-AE24CA0719-1-0 Completed by technician REDACTED in crew bklp201(0436293991) with code A-T-306 - HV-Unassisted failure(Apparent defect)\r\nAction Taken : isolated earthed fault and replaced pole\r\nSite Label : 4006739\r\nAdded notes to Reasons tab. Updated Event Trigger from HV-CCF to HV-Unassisted failure. | 1 | 9358509 | 9Se Sp432499 BlackallIsisfordRd Blackall | 1653943 | 4006739 | 9358509 | 2023-08-31 |  |  | ? | 11 | 0 | 0 | Serviceable | N | SWER sty angle | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 9358509 | PO | 7.809 | 5 | 1008.683 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -100 | 8 | 218 | 2 | 10 | 0 | 717 | 64 | 0 | 0 | 80 | 0 | -24.4596 | 145.4466 | 1980 | PO4006739 | 000002427455 | 1980s | WESTERN
EECL | OT218035 | Operational |  | 2024-01-13 | 202401 | 2024-01-13 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay | ? | 11kV |  |  |  | 978362 | 2024 | 24SW0981 | 2024-01-13 | 2024-01-13 17:20 |  |  | Normal Event | Fine | South West | 2024-01-13 13:18 | 2024-01-13 13:23 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ |  | KELVINHAUGH, KINGSTHORPE, OAKEY | F-2179-r - OAKE - Lanewood FDR - 11kV Disc Links DL3342 POle replacement required | 11kV Disc Links DL3342 POle replacement required\r\nTWMOC03\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE24SW0981-1-0 DfltHost\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE24SW0981-1-0 twmoc03 REDACTED 0427365393\r\nFFA Order En Route F-AE24SW0981-1-0 twmoc03\r\nFFA Order On Site F-AE24SW0981-1-0 twmoc03\r\nTime On modified from 23:59 13-Jan to 16:13 13-Jan\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nTime On modified from 16:13 13-Jan to 18:00 13-Jan\r\nSending Asset Event to FFA\r\nTime On modified from 18:00 13-Jan to 17:20 13-Jan\r\nSending Asset Event to FFA\r\nFFA Order F-AE24SW0981-1-0 Completed by technician REDACTED in crew twmoc03(0427365393) with code A-T-65 - Wind borne object\r\nAction Taken : crew found pole broken and leaning\r\nSite Label : 3069228\r\nUpdated Event Trigger from Wind borne object to HV-Unassisted failure. | 1 | 9358902 | 9PS PTD1789 gte nr 360 4AK RdOakey | 978362 | 3069228 | 9358902 | 2019-07-08 |  |  | ? | 11 | 1 | 0 | Serviceable | N | Rrl inter spn <200m | WOOD UNTREATED ROUND | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | Unknown | EECL | 9358902 | PO | 13.234 | 0 | 1709.4059 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -300 | 0 | 259 | 0 | 6 | 0 | 815 | 22 | 0 | 0 | 130 | 0 | -27.4651 | 151.7548 | 1963 | PO3069228 | 000002846974 | 1960s | WESTERN
EECL | OT219050 | Operational |  | 2024-01-19 | 202401 | 2024-01-19 | Pole-Wood | Wood Pole Below Ground | No Damage | Rot/Decay | 0 | LV |  |  |  | 1134146 | 2024 | 24MK0493 | 2024-01-19 | 2024-01-19 13:29 |  |  | Normal Event | Hot | Mackay | 2024-01-19 07:38 | 2024-01-19 13:35 | Completed | Unplanned Outage | LV-Conductor Connection Failure | Unknown | Single Fault Call | GT |  | 303 THOROGOOD RD;KELSEY CREEK QLD 4800 | Electrician->Fault occurred at:19/01/2024 07:34; REDACTED;>UPH --> Details:Other-WiresExposed:NO,TripHazard:NO<;Incident Details:Pole is leaning away from house and mains connection box has pulled away from House. line is still connected. EC has pulled fuse on pole to isolate house but pole is neeeds securing.;COVID-19:N/A;Warnings[uphSafety]: ADVISED;Sensitive Load:N |  | 1 | 9365165 | 303 Thorogood rd Kelsey ck Prosy | 1134146 | 4145835 | 9365165 | 2020-04-03 |  |  | 0 | 9.5 | 0 | 0 | Serviceable | N | Urb service pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Front Yard | SG SPOTTED GUM | 5 kiloNewton | EECL | 9365165 | PO | 9.978 | 2 | 1101.7817 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -70 | 5 | 227 | 0 | 8 | 0 | 730 | 3 | 0 | 0 | 98 | 0 | -20.4212 | 148.4405 | 1970 | PO4145835 | 000003224038 | 1970s | EASTERN/COASTAL
EECL | OT219202 | Operational |  | 2024-01-19 | 202401 | 2024-02-15 | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay | Replace | 19kV |  |  |  | 1759924 | 2024 | 24CA1098 | 2024-01-19 | 2024-01-20 13:19 |  |  | Normal Event | Storm | Capricornia | 2024-01-19 16:57 | 2024-01-19 17:44 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | BLACKALL: OFF ISISFORD-B'ALL RD | F-2227-r Crew advise 19.1kV SWER Recloser S6913 has operated. Crew erected temporary pole. SL 2074150. REDACTED | Calls suggest 19.1kV SWER Sectionaliser S2239 has operated. REDACTED bklp202 Sending Asset Event to FFA FFA Order Created F-AE24CA1098-1-0 DfltHost Sending Asset Event to FFA Asset selection reset Crew advise 19.1kV SWER Recloser S6913 has operated. Asset selection modified Sending Asset Event to FFA No Life Threaten Fault calls. Reclose attempt approved. Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA No life threaten calls Reclose up to S2239. Sending Asset Event to FFA Reclose Unsuccessful. Too wet to drive. Crews to attend in the morning with Chopper Sending Asset Event to FFA Time On modified from 23:59 19-Jan to 23:59 20-Jan Sending Asset Event to FFA Crews heading to the area now with a helicopter Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA1098-1-0 bklp202 REDACTED 0488331670 FFA Order En Route F-AE24CA1098-1-0 bklp202 Crew has found 2 SWER poles down at Clarendon. Work underway to make repairs. Time On modified from 23:59 20-Jan to 16:00 20-Jan Sending Asset Event to FFA Time On modified from 16:00 20-Jan to 13:18 20-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order On Site F-AE24CA1098-1-0 bklp202 FFA Order F-AE24CA1098-1-0 Completed by technician REDACTED in crew bklp202(0488331670) with code A-T-317 - Severe Weather Action Taken : temp pole erected Site Label : 2074150 Actual Power Restoration for F-AE24CA1098-1-0: 20-JAN-2024 13:11:00 Updated Reasons tab. Reason for Event changed from Unknown | 1 | 9370492 | 1PleWSp446542\1418AvingtonRdBlackall | 1759924 | 2074150 | 9370492 | 2023-09-15 |  |  | 0 | 11 | 0 | 0 | Unserviceable - P2 | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 9370492 | PO | 3.838 | 8 | 495.7297 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -100 | 13 | 172 | 3 | 6 | 0 | 670 | 16 | 0 | 0 | 86 | 80 | -24.2417 | 145.2148 | 2003 | PO2074150 | 000002184632 | 2000s | WESTERN
EECL | OT219262 | Operational |  | 2024-01-20 | 202401 | 2024-01-20 | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay | 0 | 11kV |  |  |  | 1038071 | 2024 | 24SW1418 | 2024-01-19 | 2024-01-20 17:30 |  |  | Normal Event | Fine | South West | 2024-01-19 23:55 | 2024-01-19 23:56 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | SZ |  | FORMARTIN: JONDARYAN ST RUTH RD, SNELLING RD, WAINUI SOLDIERS RD JONDARYAN: JONDARYAN ST RUTH RD | F-2232-r 11kV Sectionaliser S19490, Opened on Fault Crew replaced broken HV pole. SL 6006159. REDACTED | 11kV Sectionaliser S19490, Opened on Fault F-2232-r Time On modified from 23:59 19-Jan to 23:59 20-Jan TWMOC03 Depot Co-ord Advised Storm in Area Sending Asset Event to FFA FFA Order Created F-AE24SW1418-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW1418-1-0 twmoc04 REDACTED 0413497233 FFA Order Acknowledged F-AE24SW1418-1-0 twmoc07 REDACTED 0427704018 FFA Order En Route F-AE24SW1418-1-0 twmoc07 FFA Order On Site F-AE24SW1418-1-0 twmoc07 FFA Order F-AE24SW1418-1-0 Completed by technician REDACTED in crew twmoc07(0427704018 ) with code A-T-62 - Lightning Action Taken : Replaced broking hv pole Site Label : 6006159 Time On modified from 23:59 20-Jan to 17:30 20-Jan Reason for Event changed from Lightning / Storm Updated Reasons tab. Updated Event Trigger from Lightning to HV-Unassisted failure. | 1 | 9365311 | 3 opp896 jondaryan st ruth rd formartin | 1038071 | 6006159 | 9365311 | 2019-11-20 |  |  | 0 | 12.5 | 1 | 0 | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Soil | Crop Harvester | SG SPOTTED GUM | 3 kiloNewton | EECL | 9365311 | PO | 6.133 | 0 | 907.204 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 210 | 0 | 6 | 0 | 660 | 21 | 0 | 0 | 105 | 0 | -27.4016 | 151.4719 | 1968 | PO6006159 | 000005400792 | 1960s | WESTERN
EECL | OT219940 | Operational |  | 2024-01-23 | 202401 | 2024-02-22 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay External | Replace | 19kV |  |  |  | 1023219 | 2024 | 24CA1231 | 2024-01-23 | 2024-01-23 14:34 |  |  | Normal Event | Fine | Capricornia | 2024-01-23 09:55 | 2024-01-23 10:00 | Completed | Unplanned Outage | HV-Conductor Connection Failure | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | N/A | F-2262-r - BARC - Fleetwood SWER - reported broken pole downstream of 19.1kV SWER Dropout Fuse X12089 on de-energised network | reported broken pole downstream of 19.1kV SWER Dropout Fuse X12089 on de-energised network brccmfr02 Sending Asset Event to FFA FFA Order Created F-AE24CA1231-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA1231-1-0 brccmfr02 REDACTED 0437739195 FFA Order En Route F-AE24CA1231-1-0 brccmfr02 Time On modified from 23:59 23-Jan to 14:34 23-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order On Site F-AE24CA1231-1-0 brccmfr02 FFA Order F-AE24CA1231-1-0 Completed by technician REDACTED in crew brccmfr02(0437739195) with code A-T-317 - Severe Weather Action Taken : pole fell down in storm on denigised line Fleetwood swer as per photos attached. Site Label : 4147043 | 1 | 3228019 | 7W X12089 reedy creek rd aramac | 1023219 | 4147043 | 3228019 | 2020-07-15 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER sty term | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | EECL | 3228019 | PO | 29.16 | 0 | 4313.3184 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -50 | 0 | 353 | 0 | 4 | 0 | 1110 | 18 | 0 | 0 | 177 | 0 | -22.4464 | 145.0837 | 1968 | PO4147043 | 000003228019 | 1960s | WESTERN
EECL | OT220486 | Operational |  | 2024-01-25 | 202401 | 2024-02-13 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay External | Made Safe | 19kV |  |  |  | 1549930 | 2024 | 24NQ2880 | 2024-01-25 | 2024-01-25 19:29 | M | A | Normal Event | Storm Electrical | North Queensland | 2024-01-25 14:53 | 2024-01-25 14:55 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to a SCADA Automated Event | FE |  | CLONCURRY, JULIA CREEK, MCKINLAY, OORINDI, | F-2950-q - JULIA CK 19kV JC11 SWER Fdr CB K652 tripped. SCADA Interface automated outage. | entered from the SCADA Interface JCKCDWGL1 Sending Asset Event to FFA FFA Order Created F-AE24NQ2880-1-0 DfltHost crew advised pole down near JCS327, isolated and earthed, power restored up to 19.1kV SWER Disc Links CLIFTON PARK NO.1 at 1828 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 25-Jan to 19:29 25-Jan Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ2880-1-0 jckcdwgl1 REDACTED 0427033991 FFA Order En Route F-AE24NQ2880-1-0 jckcdwgl1 FFA Order On Site F-AE24NQ2880-1-0 jckcdwgl1 FFA Order F-AE24NQ2880-1-0 Completed by technician REDACTED in crew JCKCDWGL1(0427033991) with code A-T-317 - Severe Weather Action Taken : pole down in electrical storm Made safe stood temp pole under 24NQ2880 Site Label : 5067652 FFA Order F-AE24NQ2880-1-0 Completed by technician REDACTED in crew JCKCDWGL1(0427033991) with code A-T-317 - Severe Weather Action Taken : pole down in electrical storm Made safe stood temp pole under 24NQ2880 Site Label : 5067652 FFA Order F-AE24NQ2880-1-0 Completed by technician REDACTED in crew JCKCDWGL1(0427033991) with code A-T-317 - Severe Weather Action Taken : pole down in electrical storm Made safe stood temp pole under 24NQ2880 Site Label : 5067652 | 1 | 2832727 | 2 sth QR track bindooran stn JC | 1549930 | 5067652 | 2832727 | 2022-10-19 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | Y | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 8 kiloNewton | EECL | 2832727 | PO | 6.837 | 0 | 1011.332 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | -40 | 0 | 223 | 0 | 9 | 0 | 750 | 16 | 0 | 0 | 100 | 50 | -20.7075 | 141.3985 | 1969 | PO5067652 | 000002832727 | 1960s | WESTERN
EECL | OT221357 | Operational |  | 2024-01-27 | 202401 | 2024-01-26 | Pole-Wood | Wood Pole Beyond 2m | Broken | Termites | 0 | 19kV |  |  |  | 1210281 | 2024 | 24FN2066 | 2024-01-27 | 2024-01-27 12:25 |  |  | Normal Event | Wet / Rain | Far North | 2024-01-27 08:02 | 2024-01-27 10:38 | Completed | Unplanned Outage | Animal Insects (termites/borers/white ants) | Fallen Power Lines | due to fallen power lines. | FC |  | NORMANTON: BURKE DEVELOPMENT RD | F-3139-s NORM - Burketown Feeder Co188 sectionaliser open - pole down beyond at 5223658 - wire still intact | F-3139-s NORM - Burketown Feeder Co188 sectionaliser open - pole down beyond at 5223658 - wire still intact HV Wires Down Pole/s Down Storm in Area Sending Asset Event to FFA FFA Order Created F-AE24FN2066-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Time On modified from 23:59 27-Jan to 12:25 27-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24FN2066-1-0 nrmoc01 REDACTED 0427136340 FFA Order En Route F-AE24FN2066-1-0 nrmoc01 FFA Order On Site F-AE24FN2066-1-0 nrmoc01 Restoration Comments for F-AE24FN2066-1-0 by nrmoc01: pole failure due to termite damage, stood temp pole FFA Order F-AE24FN2066-1-0 Completed by technician REDACTED in crew nrmoc01(0427136340) with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : pole failure due to termite damage, stood temp pole Site Label : 5223658 | 1 | 3379952 | 18poles N of cowan downs stn homestead | 1210281 | CO263 | 3379952 | 2018-08-20 | N |  | 0 | 14 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | WS WHITE STRINGYBARK | 5 kiloNewton | EECL | 3379952 | PO | 0 | 0 | 3502.1022 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 6 | 0 | 1060 | 16 | 0 | 0 | 100 | 10 | -18.9083 | 140.5092 | 1989 | PO5223658 | 000003379952 | 1980s | WESTERN
EECL | OT221769 | Operational |  | 2024-01-26 | 202401 | 2024-01-30 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | 0 | 11kV |  |  |  | 1811591 | 2024 | 24NQ2889 | 2024-01-25 | 2024-01-29 13:42 | M | A | Normal Event | Cyclonic | North Queensland | 2024-01-25 15:51 | 2024-01-25 15:56 | Completed | Unplanned Outage | Severe Weather | Cyclone | due to damage caused by cyclone activity. | ST |  | CLUDEN, JULAGO, NOME, STUART | F-3100-s 11kV Stuart No.2 Feeder CB B252 - OC Trip to Lockout | 11kV Stuart No.2 Feeder CB B252 - OC Trip to Lockout Time On modified from 23:59 26-Jan to 23:59 27-Jan Generation placed on SP824784 unplanned generation event 24NQ2889 Asset selection modified Generation placed on SP824784 unplanned generation event 24NQ2889 as per restoration plan Time On modified from 23:59 27-Jan to 22:00 27-Jan Time On modified from 22:00 27-Jan to 22:00 29-Jan Asset selection modified Assets extracted from TVS454 into event 24NQ3480 Asset selection modified Asset selection modified Closed in B252 (ST-02), RC890369 indicated 8.0kV. Crew investigated found bad volts at TVS88 patrolled back to TVS3616 which also indicated bad volts. Isolated at Bruce HWY No.10 and Bruce HWY No.2 to eliminate brown out conditions. Also suspect the burnt off bridge is between these two locations. Asset selection modified Broken bridge repaired - closed in bruce hwy no2 Asset selection modified Closed in Bruce Hwy No.10 up to RC890369 Asset selection modified Closed RC890369 restoring remainder of feeder Time On modified from 22:00 29-Jan to 13:42 29-Jan | 1 | 3208609 | 7 Hunter St, Stuart, T'ville | 1811591 | 5135262 | 3208609 | 2022-04-06 | N |  | 0 | 12.5 | 1 | 1 | Serviceable | Y | Rrl inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | RI RED IRONBARK | 8 kiloNewton | EECL | 3208609 | PO | 22.517 | 3 | 3330.6713 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | 5 | 327 | 1 | 9 | 0 | 1046 | 20 | 0 | 0 | 97 | 0 | -19.3471 | 146.8519 | 1986 | PO5135262 | 000003208609 | 1980s | EASTERN/COASTAL
EECL | OT221796 | Operational |  | 2024-01-28 | 202401 | 2024-01-28 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay | 0 | 33kV |  |  |  | 1919341 | 2024 | 24SW3781 | 2024-01-28 | 2024-01-28 15:01 |  |  | Normal Event | Storm | South West | 2024-01-28 09:21 | 2024-01-28 09:23 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | our repair crews are attending. Fault finding is in progress. | FE |  | DRILLHAM, DULACCA, JACKSON, MILES, NORTH JACKSON, ULIMAROA | F-2331-r: MILES 33kV Dulacca Fdr CB CB3579 tripped. SCADA Interface automated outage. Crew replaced P2 pole that failed in storm. SL 2135592. REDACTED | entered from the SCADA Interface chnfr01 Sending Asset Event to FFA FFA Order Created F-AE24SW3781-1-0 DfltHost Sending Asset Event to FFA Depot Co-ord Advised Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW3781-1-0 chnfr01 REDACTED 0429419383 FFA Order En Route F-AE24SW3781-1-0 chnfr01 Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order On Site F-AE24SW3781-1-0 chnfr01 Std Reason Changed from Transient Fault of Unknown Origin by REDACTED 0429419383 Restoration Comments for F-AE24SW3781-1-0 by chnfr01: 2135592 Pole failed in storm pole is between Regs PC592739. and Junction of GS893072, DL612572 crews onsite planning on replacing pole Sending Asset Event to FFA Time On modified from 23:59 28-Jan to 15:01 28-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW3781-1-0 Completed by technician REDACTED in crew chnfr01(0429419383) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced P2 pole, failed in storm Site Label : 2135592 FFA Order F-AE24SW3781-1-0 Completed by technician REDACTED in crew chnfr01(0429419383) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced P2 pole, failed in storm Site Label : 2135592 Added notes to Reasons tab. Updated Event Trigger from HV-CCF to HV-Unassisted failure. Updated Asset Event Type from Sub Transmission to Distribution. | 1 | 9367210 | acc 31556 Warrego Hwy,Miles | 1919341 | 2135592 | 9367210 | 2024-01-17 |  |  | 0 | 12.5 | 1 | 0 | Unserviceable - P2 | N | Rrl inter spn <200m | WOOD UNTREATED ROUND | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 9367210 | PO | 4.222 | 8 | 624.5767 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 186 | 5 | 6 | 0 | 630 | 22 | 0 | 0 | 92 | 0 | -26.6496 | 150.1133 | 1962 | PO2135592 | 000002406047 | 1960s | WESTERN
EECL | OT215309 | Operational |  | 2024-01-01 | 202401 | 2024-01-24 | Pole-Steel | Steel Pole Beyond 2m | Broken | Corrosion |  | LV |  |  |  | 5343708 | 2024 |  | 2024-01-01 | [6 empty] | 2024-01-01 04:46 | 2024-01-01 04:46 | [10 empty] | 1 | [5 empty] | 2020-08-10 |  |  | 0 | 7.5 | 0 | 0 | Serviceable | N | Streetlight only | PUB LIGHT PLATE SET | Pavers | Footpath | HS HOLLOW/TUBULAR ST | Unknown | EECL | 0 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -19.2602 | 146.8193 | 1997 | PO5204452 | 000005343709 | 1990s | EASTERN/COASTAL
EECL | OT223730 | Operational |  | 2024-02-02 | 202402 | 2024-02-04 | Pole-Wood | Wood Pole Below Ground | Broken | Termites | 0 | 19kV |  |  |  | 751508 | 2024 | 24CA2656 | 2024-02-02 | 2024-02-02 20:19 |  |  | Normal Event | Fine | Capricornia | 2024-02-02 15:05 | 2024-02-02 15:56 | Completed | Unplanned Outage | Animal Insects (termites/borers/white ants) | Unknown | due to damage requiring emergency repairs. Fault finding is in progress. | FC |  | ALPHA: DEGULLA RD, OFF FORRESTER RD CLERMONT: ALBRO RD, OFF ALBRO RD, OFF FORRESTER RD | Crew advised that they suspect that OCR X7152 has tripped | Crew advised that they suspect that OCR X7152 has tripped No service. Being done as DSO F-2423-r Time On modified from 23:59 02-Feb to 20:19 02-Feb Sending Asset Event to FFA FFA Order Created F-AE24CA2656-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA2656-1-0 brccs01 REDACTED 0428110442 FFA Order En Route F-AE24CA2656-1-0 brccs01 FFA Order On Site F-AE24CA2656-1-0 brccs01 Restoration Comments for F-AE24CA2656-1-0 by brccs01: isolated and earthed wires down. temp pole erected under access FFA Order F-AE24CA2656-1-0 Completed by technician REDACTED in crew brccs01(0428110442) with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : SWER pin pole replaced with temp pole. Site Label : 2070331 | 1 | 2171034 | 2pW391215DegullaStnDegullaRdAlpha | 751508 | 2070331 | 2171034 | 2020-12-12 | N |  | 0 | 11 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 3 kiloNewton | EECL | 2171034 | PO | 10.364 | 2 | 1338.7274 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | 4 | 239 | 1 | 6 | 0 | 767 | 16 | 0 | 0 | 120 | 0 | -22.7902 | 146.5137 | 1976 | PO2070331 | 000002171034 | 1970s | WESTERN
EECL | OT223977 | Operational |  | 2024-02-04 | 202402 | 2024-02-08 | Pole-Wood | Wood Pole Up To 2m | Broken | Termites | Made Safe | 19kV |  |  |  | 1623210 | 2024 | 24NQ4121 | 2024-02-04 | 2024-02-05 17:10 |  |  | Normal Event | Wind | North Queensland | 2024-02-04 15:29 | 2024-02-04 15:31 | Completed | Unplanned Outage | Animal Insects (termites/borers/white ants) | Fallen Power Lines | due to fallen power lines. | FC |  | WINTON | WINTON 19kV Jarvisfield RC869744 ACR CB tripped. SCADA Interface automated outage. Termites had completely eaten out the middle of the pole and with strong winds, the pole failed. Repairs made as required. SL 5165200. REDACTED | entered from the SCADA Interface wntcdwgl1 REDACTED will organise a chopper to fly line in the morning Time On modified from 23:59 04-Feb to 23:59 05-Feb Sending Asset Event to FFA FFA Order Created F-AE24NQ4121-1-0 DfltHost F-3288-s Sending Asset Event to FFA Crews to attend in morning Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ4121-1-0 wntcdwgl1 REDACTED 0427893349 Crew adv Poles down on main line between Toff to WIS164 and Toff to WIS165 Sending Asset Event to FFA Time On modified from 23:59 05-Feb to 17:10 05-Feb Manual Reclose Checklist Sending Asset Event to FFA FFA Order En Route F-AE24NQ4121-1-0 wntcdwgl1 FFA Order On Site F-AE24NQ4121-1-0 wntcdwgl1 FFA Order F-AE24NQ4121-1-0 Completed by technician REDACTED in crew wntcdwgl1(0427893349) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : termites completely eaten out middle of the pole, with the strong winds pole has failed. Site Label : 5165200 Updated Reasons tab. Updated Event Trigger from HV-Unassisted failure to Animal Insects. Reason for Event changed from Unknown | 1 | 3287488 | 12pE Javisfield HVL 5 Suvla stn WI | 1623210 | 5165200 | 3287488 | 2018-11-21 |  |  | 0 | 12.5 | 0 | 0 | Serviceable | Y | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | GM GYMPIE MESSMATE | 3 kiloNewton | EECL | 3287488 | PO | 0 | 0 | 1044.4195 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | -100 | 0 | 224 | 0 | 6 | 0 | 705 | 16 | 0 | 0 | 100 | 0 | -22.5374 | 142.5966 | 1982 | PO5165200 | 000003287488 | 1980s | WESTERN
EECL | OT224658 | Operational |  | 2024-02-07 | 202402 | 2024-02-19 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay | 0 | 19kV |  |  |  | 1673444 | 2024 | 24NQ4404 | 2024-02-07 | 2024-02-08 11:55 |  |  | Normal Event | Wet / Rain | North Queensland | 2024-02-07 20:45 | 2024-02-07 21:20 | Data verification | Unplanned Outage | Overload | HV or LV Fuse blown | due to damage requiring emergency repairs. | FC |  | CLONCURRY | F-3317-s NOCL - NC02 Fdr: Suspect Blown Bypass Fuse at Cloncurry SWER No.4 feeding Cloncurry West SWER. | Suspect Blown Bypass Fuse at Cloncurry SWER No.4 feeding Cloncurry West SWER Sending Asset Event to FFA FFA Order Created F-AE24NQ4404-1-0 DfltHost Crew confirm Bypass Fuse is Down Lightning in the area will attempt MRC Manual Reclose Checklist Sending Asset Event to FFA MRC Failed Crew to Organise Chopper and Fly in the Morning Sending Asset Event to FFA Time On modified from 23:59 07-Feb to 23:59 09-Feb Sending Asset Event to FFA Time On modified from 23:59 09-Feb to 23:59 08-Feb Sending Asset Event to FFA Sending Asset Event to FFA Pole/s Down Sending Asset Event to FFA Crew adv have found Pole down SL5026011. Isolation & earthing between Switch Cloncurry West No.1 & New Jersey Plains No.1. Sending Asset Event to FFA Time On modified from 23:59 08-Feb to 15:00 08-Feb Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Reverse switching commenced. Sending Asset Event to FFA Replay sequence/s deleted after 07-FEB-24 20:45:00 Time On modified from 15:00 08-Feb to 11:55 08-Feb Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ4404-1-0 clccdwgl1 REDACTED 0437618725 FFA Order En Route F-AE24NQ4404-1-0 clccdwgl1 FFA Order On Site F-AE24NQ4404-1-0 clccdwgl1 FFA Order F-AE24NQ4404-1-0 Completed by technician REDACTED in crew clccdwgl1(0437618725) with code A-T-28 - Overload Action Taken : stood temp pole Site Label : 5026011 | 1 | 2592785 | 15p N QR mine rd on Mindie stn Cloncurry | 1673444 | 5026011 | 2592785 | 2019-07-03 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 2592785 | PO | 12.351 | 0 | 1826.9155 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -100 | 0 | 266 | 0 | 6 | 0 | 835 | 16 | 0 | 0 | 100 | 0 | -20.6211 | 140.5544 | 1981 | PO5026011 | 000002592785 | 1980s | WESTERN
EECL | OT224720 | Operational |  | 2024-02-08 | 202402 | 2024-02-08 | Pole-Wood | Wood Pole Below Ground | Broken | Termites | 0 | LV |  |  |  | 6234977 | 2024 | 24CA3006 | 2024-02-08 | 2024-02-08 15:50 |  |  | Normal Event |  | Capricornia | 2024-02-08 10:45 | 2024-02-08 16:31 | Completed | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 57 DARWIN ST;JERICHO QLD 4728 | 3rd Party->Fault occurred at:08/02/2024 09:04; REDACTED;>WDPP --> AffectingTraffic:YES -- StillHavePower:UNSURE<;Incident Details:line down across road out front of this premise;Access Details:no known access issues;COVID-19:N/A;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:L |  | 1 | 9371239 | opp 59 Darwin St Jericho | 6234977 | 2004979 | 9371239 | 2021-08-13 |  |  | 0 | 9.5 | 0 | 0 | Serviceable | N | Urb service pole | WOOD (GREEN) SALT IMPREG CCA | Soil | Footpath | SG SPOTTED GUM | 5 kiloNewton | EECL | 9371239 | PO | 13.734 | 0 | 1516.4687 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 254 | 0 | 14 | 0 | 798 | 3 | 0 | 0 | 127 | 0 | -23.6018 | 146.1241 | 1975 | PO2004979 | 000002416563 | 1970s | WESTERN
EECL | OT225489 | Operational |  | 2024-02-13 | 202402 | 2024-02-14 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | 0 | 19kV |  |  |  | 1069325 | 2024 | 24SW4860 | 2024-02-13 | 2024-02-14 13:05 |  |  | Normal Event | Wind | South West | 2024-02-13 20:15 | 2024-02-13 20:18 | Completed | Unplanned Outage | Lightning | Unknown | due to a SCADA Automated Event | FC |  | QUILPIE: KEEROONGOOLOO RD, DIAMANTINA DEVELOPMENTAL RD WINDORAH: HAMMOND DOWNS RD | F-2483-r QUILPIE 19kV Regleigh CB7113 ACR CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface F-2483-r OC trip. Reclose failed, crews to attend in morning qulcmcs02. Time On modified from 23:59 13-Feb to 23:59 14-Feb Depot Co-ord Advised Sending Asset Event to FFA FFA Order Created F-AE24SW4860-1-0 DfltHost . Sending Asset Event to FFA Pole/s Down Sending Asset Event to FFA Crew reports pole down past DL585360 Sending Asset Event to FFA Sending Asset Event to FFA Removing Asset Event from FFA FFA Order cancelled.F-AE24SW4860-1-0 Sending Asset Event to FFA FFA Order Created F-AE24SW4860-1-1 DfltHost Sent ot QULOC02 Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW4860-1-1 quloc02 REDACTED 0438157176 FFA Order En Route F-AE24SW4860-1-1 quloc02 FFA Order On Site F-AE24SW4860-1-1 quloc02 Restoration Comments for F-AE24SW4860-1-1 by quloc02: Isolated and earthed at DL585360, stand temporary pole to restore power ( 2.5 Hours Duration) Time On modified from 23:59 14-Feb to 13:05 14-Feb Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW4860-1-1 Completed by technician REDACTED in crew quloc02(0438157176) with code A-T-317 - Severe Weather Action Taken : Pole failed due to strong winds Site Label : 3086436 | 1 | 2919532 | 16 NW Jundah/Tenham/DiamantinaDev' Rd's | 1069325 | 3086436 | 2919532 | 2021-04-24 | N |  | 0 | 11 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Road Reserve | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 2919532 | PO | 11.364 | 0 | 1467.808 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 0 | 6 | 0 | 775 | 16 | 0 | 0 | 100 | 0 | -25.5835 | 142.9902 | 1987 | PO3086436 | 000002919532 | 1980s | WESTERN
EECL | OT225520 | Operational |  | 2024-02-14 | 202402 | 2024-02-15 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | 0 | 19kV |  |  |  | 1797997 | 2024 | 24NQ4667 | 2024-02-14 | 2024-02-15 15:49 |  |  | Normal Event | Fine | North Queensland | 2024-02-14 04:51 | 2024-02-14 04:54 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | WINTON | F- 3345-s WINTON 19kV Jarvisfield RC869744 ACR CB tripped. SCADA Interface automated outage. Crew replaced angle strain pole. SL 5165115. REDACTED | entered from the SCADA Interface Super arranging chopper ITM. Reason for Event changed from Unknown REDACTED advised to leave till depot hours to organise helicopter to patrol line. Contact REDACTED wntcsfr03 Sending Asset Event to FFA FFA Order Created F-AE24NQ4667-1-0 DfltHost FFA Order Acknowledged F-AE24NQ4667-1-0 wntcsfr03 REDACTED 0447761083 Sending Asset Event to FFA Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA Time On modified from 23:59 14-Feb to 18:00 15-Feb Sending Asset Event to FFA WIS169 still no supply Sending Asset Event to FFA Time On modified from 18:00 15-Feb to 15:49 15-Feb Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE24NQ4667-1-0 wntcsfr03 FFA Order On Site F-AE24NQ4667-1-0 wntcsfr03 FFA Order F-AE24NQ4667-1-0 Completed by technician REDACTED in crew wntcsfr03(0447761083) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Replaced angle strain pole Site Label : 5165115 Updated Reasons tab. Updated Event Trigger from Lightning to HV-Unassisted failure. Reason for Event changed from Lightning / Storm | 1 | 9371938 | 15pW whyrallah sec1 Tulmar stn WI | 1797997 | 5165115 | 9371938 | 2018-12-11 |  |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER sty term | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZR UNKNOWN RED SPECI | 5 kiloNewton | EECL | 9371938 | PO | 0 | 0 | 2454.3345 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -75 | 0 | 293 | 0 | 7 | 0 | 920 | 18 | 0 | 0 | 146 | 0 | -22.7234 | 142.3257 | 1982 | PO5165115 | 000003287316 | 1980s | WESTERN
EECL | OT225757 | Operational |  | 2024-02-15 | 202402 | 2024-02-23 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay External | 0 | LV |  |  |  | 1094883 | 2024 | 24SW5360 | 2024-02-15 | 2024-02-22 12:00 |  |  | Normal Event | Storm Electrical | South West | 2024-02-15 17:26 | 2024-02-23 12:10 | Cancelled | Unplanned Outage | Severe Weather | Unknown | Single Fault Call | GT |  | 55 DOWLING ST;THARGOMINDAH QLD 4492 | Fault occurred at:15/02/2024 17:22; REDACTED;>WDPP --> AffectingTraffic:NO -- StillHavePower:YES<;Incident Details:Pole has fallen down behind property in vacant block and is visibly sparking and pole on other end of line is leaning badly;COVID-19:NO;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N | outage cancelled via Clash Wizard | 1 | 9372201 | behind50 POWELL ST THARGO | 1094883 | 2083769 | 9372201 | 2023-07-13 |  |  | 0 | 11 | 0 | 1 | Serviceable | N | Urb LV inter | WOOD UNTREATED ROUND | Soil | Road Reserve | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 9372201 | PO | 9.119 | 0 | 1177.8711 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -50 | 0 | 229 | 0 | 6 | 0 | 720 | 1 | 0 | 0 | 100 | 0 | -27.9967 | 143.8242 | 1954 | PO2083769 | 000002277652 | 1950s | WESTERN
EECL | OT225948 | Operational |  | 2024-02-17 | 202402 | 2024-02-17 | Pole-Wood | Wood Pole Below Ground | Broken | Termites | 0 | LV |  |  |  | 1561890 | 2024 | 24SW5082 | 2024-02-17 | 2024-02-17 10:25 |  |  | Normal Event |  | South West | 2024-02-17 08:30 | 2024-02-17 08:20 | Completed | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | ROMA: CHARLES ST, COURTNEY ST, DERRY ST, IVY ST, ROBERTSON ST | 11kV Pole Dist Sub PW13250 crews need to replace an LV Pole, will be isolating at a Bundle Box on Pole S/L 2083160. LV Switching Only | 11kV Pole Dist Sub PW13250 crews need to replace an LV Pole, will be isolating at a Bundle Box on Pole S/L 2083160. LV Switchin Only romcm707 Sending Asset Event to FFA FFA Order Created F-AE24SW5082-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 12:30 17-Feb to 10:25 17-Feb Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW5082-1-0 romcm707 REDACTED 0428561525 FFA Order En Route F-AE24SW5082-1-0 romcm707 FFA Order On Site F-AE24SW5082-1-0 romcm707 FFA Order F-AE24SW5082-1-0 Completed by technician REDACTED in crew romcm707(0428561525) with code A-F-C - Completed Action Taken : replace lv pole Site Label : 2083170 Actual Power Restoration for F-AE24SW5082-1-0: 17-FEB-2024 10:59:00 | 1 | 2273156 | 18 ROBERTSON st, ROMA | 1561890 | 2083162 | 2273156 | 2024-01-17 | N |  | 0 | 9.5 | 0 | 1 | Serviceable | N | Urb LV inter | WOOD UNTREATED ROUND | Soil | Footpath | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 2273156 | PO | 12.854 | 4 | 1419.2961 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -200 | 6 | 244 | 1 | 6 | 0 | 790 | 1 | 0 | 0 | 96 | 0 | -26.5831 | 148.7908 | 1962 | PO2083162 | 000002273156 | 1960s | WESTERN
EECL | OT226457 | Operational |  | 2024-02-21 | 202402 |  | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay | 0 | 19kV |  |  |  | 1789862 | 2024 | 24NQ5069 | 2024-02-21 |  |  |  | Normal Event | Storm | North Queensland | 2024-02-21 13:12 | 2024-02-21 13:14 | Delayed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FE |  | LONGREACH, WINTON | F-1290-t - WINTON 19kV Apsley Fdr CB A652 tripped. SCADA Interface automated outage. | entered from the SCADA Interface REDACTED currently in Long reach on his way back to look at fault Sending Asset Event to FFA Sending Asset Event to FFA Chopper organised for Thursday AM Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Time On modified from 23:59 21-Feb to 23:59 22-Feb Sending Asset Event to FFA FFA Order Created F-AE24NQ5069-1-0 DfltHost Crew have found pole down Beyond Section H Link No.1 Isolating and Earthing For Repairs Sending Asset Event to FFA Manual Reclose Checklist Reason for Event changed from Protective Device Operated Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Crew adv WIS240 has NO Cust Connected and will be Delayed for a while Time On modified from 23:59 22-Feb to 23:59 27-Feb Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ5069-1-0 wntcsfr03 REDACTED 0447761083 FFA Order En Route F-AE24NQ5069-1-0 wntcsfr03 FFA Order On Site F-AE24NQ5069-1-0 wntcsfr03 FFA Order F-AE24NQ5069-1-0 Completed by technician REDACTED in crew wntcsfr03(0447761083) with code A-T-317 - Severe Weather Action Taken : Section H Link No.1 open and earthed on F-1290-t Pole 5213247 down. Pole is in swamp and TX at end of line has 0 customers. Left Isolated. Site Label : 5213247 Time On modified from 23:59 27-Feb to 23:59 01-Mar to be followed up in depot hrs, access issues as per above. Time On modified from 23:59 01-Mar to 10:00 04-Mar REDACTED advised access is still an issue so outage pushed out to the 15th March Time On modified from 10:00 04-Mar to 10:00 15-Mar | 1 | 3341193 | 2spns W off jundah rd winton | 1789862 | 5213247 | 3341193 | 2024-02-14 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | Y | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | EECL | 3341193 | PO | 25.218 | 0 | 3379.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 6 | 0 | 1022 | 16 | 0 | 163 | 0 | 0 | -22.4057 | 143.0341 | 1980 | PO5213247 | 000003341193 | 1980s | WESTERN
EECL | OT226546 | Operational |  | 2024-02-22 | 202402 | 2024-02-22 | Pole-Wood | Wood Pole Up To 2m | Broken | Rot/Decay | 0 | 19kV |  |  |  | 1511052 | 2024 | 24NQ5071 | 2024-02-21 | 2024-02-22 13:59 |  |  | Normal Event | Storm | North Queensland | 2024-02-21 13:51 | 2024-02-21 13:53 | Completed | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FE |  | WINTON | F-3402-s WINTON 19kV Elderslie Fdr CB B652 tripped. SCADA Interface automated outage. Pole grounded during storm - Temporary pole installed. SL 5094785. REDACTED | entered from the SCADA Interface Crews advised chopper organised for the morning Time On modified from 23:59 21-Feb to 23:59 22-Feb . Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Created F-AE24NQ5071-1-0 DfltHost Crew have Commenced Patrol Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Pole down beyond The Grove No.1 5094783 Sending Asset Event to FFA Time On modified from 23:59 22-Feb to 13:59 22-Feb Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ5071-1-0 wntcsfr03 REDACTED 0447761083 FFA Order En Route F-AE24NQ5071-1-0 wntcsfr03 FFA Order On Site F-AE24NQ5071-1-0 wntcsfr03 FFA Order En Route F-AE24NQ5071-1-0 wntcsfr03 FFA Order On Site F-AE24NQ5071-1-0 wntcsfr03 FFA Order F-AE24NQ5071-1-0 Completed by technician REDACTED in crew wntcsfr03(0447761083) with code A-T-317 - Severe Weather Action Taken : Pole 5094785 down after storm. Installed temp pole. Site Label : 5094785 auto-completed Updated Reasons tab. Reason for Event changed from Protective Device Operated | 1 | 2951502 | 1spn w of corkmail rd winton | 1511052 | 5094785 | 2951502 | 2020-10-02 | N |  | 0 | 12.5 | 0 | 0 | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 2951502 | PO | 12.647 | 0 | 1870.6712 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | 0 | 269 | 0 | 6 | 0 | 845 | 16 | 0 | 0 | 85 | 0 | -22.3335 | 142.6784 | 2004 | PO5094785 | 000002951502 | 2000s | WESTERN
EECL | OT226676 | Operational |  | 2024-02-23 | 202402 | 2024-02-23 | Pole-Wood | Wood Pole Up To 2m | Broken | Termites | 0 | 19kV |  |  |  | 1258820 | 2024 | 24NQ5073 | 2024-02-21 | 2024-02-23 14:37 |  |  | Normal Event | Storm | North Queensland | 2024-02-21 13:52 | 2024-02-21 13:54 | Completed | Unplanned Outage | Animal Insects (termites/borers/white ants) | Fallen Power Lines | due to fallen power lines. | FC |  | DAJARRA: BOULIA RD, DILLON ST, LETHAM ST, CARMODY ST, MATHESON ST DUCHESS: MAYFIELD STATION MOUNT ISA: STANBROKE STATION ALPURRURULAM: ATNYER ST | F-1291-t - DUCHESS RD 19kV Ashover No.1 ACR CB tripped. SCADA Interface automated outage. Crew replaced pole that fell due to termite damage. SL 5218831. REDACTED | entered from the SCADA Interface Crews advised to wet to go out today. Dajarra Gen started Asset selection modified . Time On modified from 23:59 21-Feb to 23:59 22-Feb . REDACTED advised that it is too wet to patrol, booking chopper for tomorrow 22/02/24 - will advise when in the air. Time On modified from 23:59 22-Feb to 09:15 22-Feb Reason for Event changed from Unknown Crew in Helicopter Patrol Time On modified from 09:15 22-Feb to 09:15 23-Feb Crew have found Pole Down Site Lab 5218831 Isolating and Earthing for Repairs Reason for Event changed from Protective Device Operated Time On modified from 09:15 23-Feb to 20:00 22-Feb Manual Reclose Checklist Repairs complete and Ashover ACR Closed at 1907. Dajarra to be left on Generation until tomorrow morning as remote operation sequences have not been operating and Dajarra has been off most of the day due to planned switching. Crew to return tomorrow with diesel delivery and return to normal supply if remote sequence doesn't operate. Asset selection modified Time On modified from 20:00 22-Feb to 12:00 23-Feb Time On modified from 12:00 23-Feb to 14:00 23-Feb Time On modified from 14:00 23-Feb to 16:00 23-Feb Sending Asset Event to FFA FFA Order Created F-AE24NQ5073-1-0 DfltHost FFA Order Acknowledged F-AE24NQ5073-1-0 mtifr05 REDACTED 0437715949 FFA Order En Route F-AE24NQ5073-1-0 mtifr05 FFA Order On Site F-AE24NQ5073-1-0 mtifr05 FFA Order F-AE24NQ5073-1-0 Completed by technician REDACTED in crew MTIFR05(0437715949) with code A-T-301 - Animal nesting/burrowing Action Taken : REPLACED POLE THAT FELL DOWN DUE TO TERMITE DAMAGE. Site Label : 5218831 FFA Order F-AE24NQ5073-1-0 Completed by technician REDACTED in crew MTIFR05(0437715949) with code A-T-301 - Animal nesting/burrowing Action Taken : REPLACED POLE THAT FELL DOWN DUE TO TERMITE DAMAGE. Site Label : 5218831 Asset selection modified Crew had to manually swittch Dajarra Township from generator to mains supply. Off at 1405 restored at 1437. Gen has 18% fuel, fuel yop up organised for 10AM tomorrow Time On modified from 16:00 23-Feb to 14:37 23-Feb auto-completed Added notes to Reasons tab. Updated Event Trigger from Animal nesting/burrowing to Animal Insects. | 1 | 9372211 | 27 se ashover rec ashover stn duchess | 1258820 | 5218831 | 9372211 | 2018-11-12 |  |  | 0 | 12.5 | 0 | 0 | Serviceable | Y | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | SG SPOTTED GUM | 3 kiloNewton | EECL | 9372211 | PO | 0 | 0 | 1224.7481 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 6 | 0 | 730 | 16 | 0 | 0 | 100 | 0 | -21.4977 | 139.7666 | 1984 | PO5218831 | 000003363965 | 1980s | WESTERN
EECL | OT227451 | Operational |  | 2024-02-29 | 202402 | 2024-02-29 | Pole-Wood | Wood Pole Up To 2m | Broken | Termites | Replace | 66kV |  |  |  | 1840873 | 2024 | 24NQ5511 | 2024-02-28 | 2024-02-29 13:02 |  |  | Normal Event |  | North Queensland | 2024-02-28 21:27 | 2024-02-28 21:29 | Data verification | Unplanned Outage |  | Unknown | due to a SCADA Automated Event | FE |  | SEVENTY MILE: ROCKY CREEK RD, MACOVIN RIDGE RD CHARTERS TOWERS: CLERMONT HWY SEVENTY MILE RANGE: MT LEYSHON RD, QUARTZBLOW RD | MILLCHESTER 66kV Mt Leyshn Fdr CB F152 tripped. SCADA Interface automated outage. | entered from the SCADA Interface Zone 2 Trip - 22.9km Depot Co-ord Advised Crews have located a pole that has snapped in half...5223813. A semi trailer has been arranged for first thing in the morning, mine has been advised of extended outage. Time On modified from 23:59 28-Feb to 14:00 29-Feb HV Wires Down Pole/s Down . . Pajingo Mine advised of ETR. Crew have left town with pole and expect to be on site within the hour and are hoping to have repairs completed by 14:00 Time On modified from 14:00 29-Feb to 13:02 29-Feb | 1 | 9373744 | 3spnW Sub-Mt Leyshon Rd-Chtrs twrs | 1840873 | 5223813 | 9373744 | 2023-03-02 |  |  | 0 | 20 | 0 | 0 | Serviceable | Y | 66kV rrl inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | BB BLACKBUTT | 20 kiloNewton | EECL | 9373744 | PO | 32.555 | 6 | 7867.4668 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | -100 | 8 | 469 | 5 | 6 | 0 | 1515 | 30 | 0 | 0 | 74 | 0 | -20.2981 | 146.2634 | 1988 | PO5223813 | 000003380471 | 1980s | WESTERN
EECL | OT227452 | Operational |  | 2024-02-29 | 202402 | 2024-03-01 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay External | 0 | 19kV |  |  |  | 1587080 | 2024 | 24CA3884 | 2024-02-29 | 2024-02-29 17:13 |  |  | Normal Event | Hot | Capricornia | 2024-02-29 07:25 | 2024-02-29 08:42 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | CAPELLA: ACCESS RD, GREGORY HWY, MAGENTA RD, MALTHOID RD, NUTHOLM RD, OFF RUBYVALE RD, RUBYVALE RD CLERMONT: RUBYVALE RD | F-2571-r - 19.1kV SWER Recloser X8443 - Crew Found Recloser Tripped Open due to pole down | 19.1kV SWER Recloser X8443 - Crew Found Recloser Tripped Open CLMWGO01 Sending Asset Event to FFA FFA Order Created F-AE24CA3884-1-0 DfltHost Crew Request reclose attempt Manual Reclose Checklist Sending Asset Event to FFA reclose unsuccesful crew tp carry out line patrol and advise Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA3884-1-0 clmwgo01 REDACTED 0438317946 FFA Order En Route F-AE24CA3884-1-0 clmwgo01 broken pole found downstream of Disc Link S3454 Reason for Event changed from Unknown Sending Asset Event to FFA Time On modified from 23:59 29-Feb to 16:30 29-Feb Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 16:30 29-Feb to 18:00 29-Feb Sending Asset Event to FFA Time On modified from 18:00 29-Feb to 17:13 29-Feb Sending Asset Event to FFA Pole/s Down Sending Asset Event to FFA FFA Order On Site F-AE24CA3884-1-0 clmwgo01 FFA Order F-AE24CA3884-1-0 Completed by technician REDACTED in crew Clmwgo01(0438317946) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Crew received multiple fault calls, X8443 operated, crew performed MRC on X8443 through OCC attempt unsuccessful, upon Ariel patrol crew found pole 4072571 had failed due to head wrap stay. Ioslated and earthed and made safe. crew to replace place that day Site Label : 4072571 | 1 | 9375311 | T2 SP338722 via 14000 Access Rd Capella | 1587080 | 4072571 | 9375311 | 2023-10-29 |  |  | 0 | 11 | 0 | 0 | Unserviceable - P2 | N | SWER sty angle | WOOD (GREEN) SALT IMPREG CCA | Grass | Road | SG SPOTTED GUM | 3 kiloNewton | EECL | 9375311 | PO | 8.554 | 4 | 1104.8915 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2 | 6 | 224 | 2 | 10 | 0 | 730 | 64 | 0 | 0 | 96 | 0 | -23.3113 | 147.8745 | 1985 | PO4072571 | 000002824804 | 1980s | WESTERN
EECL | OT227842 | Operational |  | 2024-03-03 | 202403 | 2024-03-03 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay External |  | 22kV |  |  |  | 1208094 | 2024 | 24FN3593 | 2024-03-03 | 2024-03-03 16:19 |  |  | Normal Event | Storm | Far North | 2024-03-03 09:48 | 2024-03-03 09:50 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FE |  | CLOHESY RIVER, DAVIES CREEK, EMERALD CREEK, KOAH, KURANDA, MAREEBA, SPEEWAH | F-3461-s - Pole 5151333 has rotted and snapped at base, pole and wires down Crew replaced HV strain pole REDACTED | entered from the SCADA Interface trip on OC REDACTED PH: 0437 580 443 Sending Asset Event to FFA FFA Order Created F-AE24FN3593-1-0 DfltHost OC trip - did not offer reclose Red / White phase 160A. Sending Asset Event to FFA FFA Order Acknowledged F-AE24FN3593-1-0 mbaco01 REDACTED 0437580443 FFA Order En Route F-AE24FN3593-1-0 mbaco01 HV Wires Down Pole/s Down Sending Asset Event to FFA Pole 5151333 has rotted and snapped at base, pole and wires down. Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Replay sequence/s deleted after 03-MAR-24 09:47:42 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 03-Mar to 18:00 03-Mar Sending Asset Event to FFA FFA Order En Route F-AE24FN3593-1-0 mbaco01 FFA Order On Site F-AE24FN3593-1-0 mbaco01 Time On modified from 18:00 03-Mar to 16:19 03-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24FN3593-1-0 Completed by technician REDACTED in crew MBACO01(0437580443) with code A-T-28 - Overload Action Taken : replace HV strain pole Site Label : 5151333 Reason for Event changed from Unknown Added notes to Reasons tab. Updated Event Trigger from Overload to HV-Unassisted failure. | 1 | 3258028 | 2spn E 97 Kovacic Rd Emerald Crk Mareeba | 1208094 | KOV2 | 3258028 | 2020-02-19 | N |  |  | 12.5 | 2 |  | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 1208094 | PO | 12.02 | 0 | 1777.9196 | [8 empty] | 0 |  | 263 |  | 7 |  | 825 | 45 |  |  | 131 |  | -16.9757 | 145.5031 | 1980 | PO5151333 | 000003258028 | 1980s | EASTERN/COASTAL
EECL | OT229744 | Operational |  | 2024-03-15 | 202403 | 2024-03-16 | Pole-Wood | Wood Pole Beyond 2m | Split | Rot/Decay |  | 12.7kV |  |  |  | 1684540 | 2024 | 24CA4493 | 2024-03-15 | 2024-03-16 13:12 |  |  | Normal Event | Fine | Capricornia | 2024-03-15 23:53 | 2024-03-16 00:02 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | SZ |  | BILOELA: CAMBOON RD, CROWSDALE RD, ZIEBARTHS RD | F-2638-r Calls Indicate 12.7kV SWER Dropout Fuse DO792665 Pole snapped, conductor gorunded - Crew replaced 12.7kV SWER pole. SL 4027697. REDACTED | Calls Indicate 12.7kV SWER Dropout Fuse DO792665 BILCM02 Sending Asset Event to FFA FFA Order Created F-AE24CA4493-1-0 DfltHost FFA Order Acknowledged F-AE24CA4493-1-0 bilcm02 REDACTED 0497111830 FFA Order En Route F-AE24CA4493-1-0 bilcm02 FFA Order On Site F-AE24CA4493-1-0 bilcm02 Restoration Comments for F-AE24CA4493-1-0 by BILCM02: pole snapped and conductor on the ground S/L 4027697, isolated and earthed . Sending Asset Event to FFA Sending Asset Event to FFA bilcs01 Sending Asset Event to FFA Time On modified from 23:59 16-Mar to 15:00 16-Mar Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA4493-1-0 bilcs01 REDACTED 0447924486 FFA Order En Route F-AE24CA4493-1-0 bilcs01 Sending Asset Event to FFA FFA Order On Site F-AE24CA4493-1-0 bilcs01 Time On modified from 15:00 16-Mar to 13:12 16-Mar Sending Asset Event to FFA HV Wires Down Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order En Route F-AE24CA4493-1-0 bilcs01 FFA Order On Site F-AE24CA4493-1-0 bilcs01 FFA Order F-AE24CA4493-1-0 Completed by technician REDACTED in crew BILCS01(0447924486) with code A-T-28 - Overload Action Taken : Crew replaced 12.7 kv SWER pole 4027697 Site Label : 4027697 Added notes to Reasons tab. | 1 | 9381147 | 361CamboonCrowsdaleRdBiloela-1SESP218474 | 1684540 | 4027697 | 9381147 | 2020-08-31 |  |  |  | 12.5 |  |  | Serviceable | N | SWER sty term | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | Unknown | EECL | 1684540 | PO | 12.434 | 2 | 1839.1308 | 1 | [7 empty] | '-180 | 3 | 266 | 1 | 7 |  | 849 | 18 |  |  | 98 |  | -24.4567 | 150.4463 | 1971 | PO4027697 | 000002555804 | 1970s | WESTERN
EECL | OT230186 | Operational |  | 2024-03-20 | 202403 | 2024-03-21 | Pole-Steel | Steel Pole Beyond 2m | Leaning | Temporary Pole |  | 19kV |  |  |  | 1236222 | 2024 | 24SW6576 | 2024-03-20 | 2024-03-20 13:00 |  |  | Normal Event |  | South West | 2024-03-20 11:06 | 2024-03-21 08:53 | Completed | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | MARKARENE;6058 LINDEN-NEBINE RD;CUNNAMULLA QLD 4490 | Fault occurred at:20/03/2024 08:11; REDACTED;>UPH --> Details:Other-WiresExposed:NO,TripHazard:NO<;Incident Details:Power pole on severe lean. newly replaced aluminium pole on property. No pole number.;COVID-19:NO;Warnings[uphSafety]: ADVISED;Dog restraint:YARD;Sensitive Load:N |  | 1 | 2268688 | MARKARENE, 10 poles nth of DL6987 | 1236222 | 5262419 | 2268688 | 2021-02-19 | N |  |  | 11 |  |  | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 8 kiloNewton | EECL | 1236222 | PO | 12.63 | 0 | 1631.3374 | 1 | [7 empty] | 0 |  | 256 |  | 6 |  | 803 | 16 |  |  | 100 |  | -27.8198 | 146.4863 | 1994 | PO5262419 | 000002268688 | 1990s | WESTERN
EECL | OT231478 | Operational |  | 2024-03-30 | 202403 | 2024-03-30 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay |  | 19kV |  |  |  | 1598019 | 2024 | 24NQ6868 | 2024-03-30 | 2024-03-30 12:52 |  |  | Normal Event | Hot | North Queensland | 2024-03-30 06:37 | 2024-03-30 06:39 | Data verification | Unplanned Outage | Overload | Unknown | due to a SCADA Automated Event | FC |  | CLONCURRY, KAJABBI | F-3639-s - NTH CLONCURY 19kV Cloncurry East ACR CB tripped. OC trip to lockout | entered from the SCADA Interface OC trip to lockout Left message with REDACTED 0400893092 Sending Asset Event to FFA FFA Order Created F-AE24NQ6868-1-0 DfltHost FFA Order Acknowledged F-AE24NQ6868-1-0 clccs03 REDACTED 0484029642 FFA Order En Route F-AE24NQ6868-1-0 clccs03 Sending Asset Event to FFA Time On modified from 23:59 30-Mar to 12:52 30-Mar Sending Asset Event to FFA FFA Order On Site F-AE24NQ6868-1-0 clccs03 FFA Order F-AE24NQ6868-1-0 Completed by technician REDACTED in crew CLCCS03(0484029642) with code A-T-28 - Overload Action Taken : stood temp pole Site Label : 5035259 | 1 | 3261306 | 5 n m-koff 3way fort constantine stn Cc | 1598019 | 5035259 | 3261306 | 2019-07-12 | N |  |  | 12.5 |  |  | Serviceable | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | EECL | 1598019 | PO | 13.012 | 0 | 1924.7312 | 2 |  | 1 | [5 empty] | '-80 |  | 274 |  | 6 |  | 860 | 16 |  |  | 100 |  | -20.4208 | 140.4798 | 1981 | PO5035259 | 000003261306 | 1980s | WESTERN
EECL | OT228388 | Operational |  | 2024-03-05 | 202403 | 2024-03-05 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay |  | LV |  |  |  | 1309501 | 2024 | 24WB3848 | 2024-03-05 | 2024-03-05 19:32 |  |  | Normal Event |  | Wide Bay | 2024-03-05 17:00 | 2024-03-05 19:33 | Completed | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 15 BEATRICE ST;WALKERVALE QLD 4670 | Fault occurred at:05/03/2024 15:00; REDACTED;>WDPB --> HasComeAway:POLE,AffectingTraffic:NO -- StillHavePower:YES<;Incident Details:pulled out of main pole - wire connecting from pole to house - wire to house is very low - they have removalist coming tomorrow and worried truck will hit the wire - 2 wires hanging down - windy weather also;COVID-19:NO;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N |  | 1 | 000009376614 | 15 BEATRICE ST, KEPNOCK b/berg | 000001309501 | 000009376614 | 000009376614 | 2024-03-27 | N |  |  | 11 |  |  | Serviceable | N | Urb LV ABC inter | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | BB BLACKBUTT | 8 kiloNewton | EECL |  | PO |  | 0 | 2697.5859 | [14 empty] | 948 | [5 empty] | -24.8798 | 152.3614 | 1958 | PO3053201 | 000002772309 | 1950s | EASTERN/COASTAL
EECL | OT233570 | Operational |  | 2024-04-18 | 202404 | 2024-04-18 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay External |  | 11kV |  |  |  | 1034993 | 2024 | 24SW7864 | 2024-04-18 | 2024-04-19 00:49 |  |  | Normal Event |  | South West | 2024-04-18 15:34 | 2024-04-18 14:17 | Completed | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | FORMARTIN: MICKLEBOROUGH RD, WEST PRAIRIE RD NORWIN: WEST PRAIRE RD WEST PRAIRIE: WEST PRAIRIE RD | F-31839-g : NORW Formartin Fdr : Crew require HV access to conductors beyond 11kV Sectionaliser SEC16888 to make repairs to damaged pole top at SL3083453, near TX PE03205. Associated with FC2423739. Crew confirm conductors above stat. height. | Crew require HV access to conductors beyond 11kV Sectionaliser SEC16888 to make repairs to damaged pole top at SL3083453, near TX PE03205. Associated with FC2423739. Crew confirm conductors above stat. height. MILOC01. Sending Asset Event to FFA FFA Order Created F-AE24SW7864-1-0 DfltHost F-31839-g Sending Asset Event to FFA Time Off modified from 15:00 18-Apr to 15:33 18-Apr Sending Asset Event to FFA Time Off modified from 15:33 18-Apr to 15:34 18-Apr Sending Asset Event to FFA Sending Asset Event to FFA Associated lines down fault call has been made safe. Isolated & Earthed under F-31839-g. Fault call linked to Asset Event. Sending Asset Event to FFA twmoc01 Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW7864-1-0 twmoc01 REDACTED 0427391214 FFA Order En Route F-AE24SW7864-1-0 twmoc01 FFA Order On Site F-AE24SW7864-1-0 twmoc01 Crew out of hours second crew coming to switch back in no ETA yet Sending Asset Event to FFA FFA Order F-AE24SW7864-1-0 Completed by technician REDACTED in crew twmoc01(0427391214) with code A-F-C - Completed Action Taken : Replaced pole due to old broken at stay wrap at head of pole. Site Label : 3083453 Time On modified from 23:59 18-Apr to 01:00 19-Apr Asset selection modified Time On modified from 01:00 19-Apr to 00:49 19-Apr | 1 | 9391198 | 2S PE3205 2640 WestPrairieRd Norwin | 1034993 | 3083453 | 9391198 | 2019-11-29 |  |  |  | 12.5 | 2 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 8 kiloNewton | EECL | 1034993 | PO | 15.327 | 0 | 2267.1161 | [7 empty] | 1 | 80 |  | 286 |  | 9 |  | 900 | 21 |  |  | 143 |  | -27.4333 | 151.3412 | 1968 | PO3083453 | 000002908395 | 1960s | WESTERN
EECL | OT233594 | Operational |  | 2024-04-18 | 202404 | 2024-04-18 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay |  | 22kV |  |  |  | 1264813 | 2024 | 24FN5382 | 2024-04-18 | 2024-04-18 14:52 |  |  | Normal Event |  | Far North | 2024-04-18 10:14 | 2024-04-18 08:55 | Completed | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | WALKAMIN: KENNEDY HWY, REX RD | Crew adv Req Access to Replace Pole 2145976 between SS11206 and C128 | Crew adv Req Access to Replace Pole 2145976 between SS11206 and C128 Time Off modified from 09:30 18-Apr to 10:14 18-Apr Time On modified from 15:59 18-Apr to 14:52 18-Apr Sending Asset Event to FFA FFA Order Created F-AE24FN5382-1-0 DfltHost FFA Order Acknowledged F-AE24FN5382-1-0 athfco03 REDACTED 0487669575 FFA Order En Route F-AE24FN5382-1-0 athfco03 FFA Order On Site F-AE24FN5382-1-0 athfco03 FFA Order F-AE24FN5382-1-0 Completed by technician REDACTED in crew athfco03(0487669575) with code A-F-C - Completed Action Taken : Replace Pole failed in service . Replaced with 14m 8KN Site Label : 2145976 auto-completed | 1 | 9391208 | 6853 Kennedy Hwy Rocky Cr, opp Rex Rd. | 1264813 | C113 | 9391208 | 2020-09-02 |  |  |  | 12.5 | 4 | 1 | Serviceable | N | HV fully suppd | WOOD UNTREATED ROUND | Soil | Paddock Crop | ZZ NO DISC - UNKNOWN | 8 kiloNewton | EECL | 1264813 | PO | 20.644 | 0 | 3053.663 | [8 empty] | 0 |  | 314 |  | 10 |  | 988 | 45 |  |  | 157 |  | -17.1801 | 145.4479 | 1960 | PO2145976 | 000002386375 | 1960s | EASTERN/COASTAL
EECL | OT233836 | Operational |  | 2024-04-21 | 202404 | 2024-04-21 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay |  | LV |  |  |  | 5289647 | 2024 | 24SW7977 | 2024-04-21 | 2024-04-21 21:44 |  |  | Normal Event |  | South West | 2024-04-21 21:15 | 2024-04-21 21:50 | Completed | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 4 LYNAGH ST;KAIMKILLENBUN QLD 4406 | Neighbour reported leaning pole - Crew found pole rotten at ground line. Crew replaced with 11/5BB, replaced service to house. SL 5254991. REDACTED | Updated notes in Reasons tab. | 1 | 9390711 | 2 lynagh st Kaimkillenbun | 5289647 | 5254991 | 9390711 | 2023-06-22 |  |  |  | 11 |  |  | Serviceable | N | Light serv pole | WOOD UNTREATED ROUND | Lawn | Road Reserve | ZZ NO DISC - UNKNOWN | Unknown | EECL | 5289647 | PO | 10.387 | 10 | 1341.6587 |  |  |  |  | 1 |  |  |  | '-230 | 15 | 243 | 5 | 14 |  | 825 | 78 |  |  | 90 |  | -27.0612 | 151.4352 | 1962 | PO5254991 | 000005289648 | 1960s | WESTERN
EECL | OT234293 | Operational |  | 2024-04-25 | 202404 | 2024-04-27 | Pole-Wood | Wood Pole Up To 2m | Split | Rot/Decay |  | 12.7kV |  |  |  | 1654725 | 2024 | 24SW8149 | 2024-04-26 | 2024-04-26 16:22 |  |  | Normal Event |  | South West | 2024-04-26 10:15 | 2024-04-26 09:16 | Completed | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | MEANDARRA: BENDEE RD | require access to replace pole near PC01786 | require access to replace pole near PC01786 DSO TARFRCS02 Sending Asset Event to FFA FFA Order Created F-AE24SW8149-1-0 DfltHost Switching Sheet ID updated from to J-307730-g. Sending Asset Event to FFA Time On modified from 13:30 26-Apr to 16:30 26-Apr Sending Asset Event to FFA Time On modified from 16:30 26-Apr to 16:22 26-Apr Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW8149-1-0 tarfrcs02 REDACTED 0427933822 FFA Order En Route F-AE24SW8149-1-0 tarfrcs02 FFA Order On Site F-AE24SW8149-1-0 tarfrcs02 FFA Order En Route F-AE24SW8149-1-0 tarfrcs02 FFA Order En Route F-AE24SW8149-1-0 tarfrcs02 FFA Order On Site F-AE24SW8149-1-0 tarfrcs02 FFA Order F-AE24SW8149-1-0 Completed by technician REDACTED in crew tarfrcs02(0427933822) with code A-F-C - Completed Action Taken : new pole and 2x stays Site Label : 3087423 | 1 | 9394182 | 5S tx, 501 bendee rd inglestone | 1654725 | 3087423 | 9394182 | 2020-11-17 |  |  |  | 11 |  |  | Serviceable | N | SWER sty angle | WOOD (GREEN) SALT IMPREG CCA | Grass | Crop Harvester | ZZ NO DISC - UNKNOWN | 5 kiloNewton | EECL | 1654725 | PO | 6.841 | 0 | 883.6702 |  |  |  |  | 1 |  | 1 |  | 0 |  | 208 |  | 1 |  | 655 | 64 |  |  | 104 |  | -27.8218 | 149.8658 | 1968 | PO3087423 | 000002923598 | 1960s | WESTERN
EECL | OT234497 | Operational |  | 2024-04-28 | 202404 |  | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay |  | 11kV |  |  |  | 1658451 | 2024 | 24CA6156 | 2024-04-28 | 2024-04-28 21:49 |  |  | Normal Event | Fine | Capricornia | 2024-04-28 11:22 | 2024-04-28 13:57 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ |  | BILOELA, THANGOOL | crew advise pole top of TX 218065 feeder to be tripped for safety Stay choked the top of the pole. Crew replaced pole. SL 4140580. REDACTED | crew advise pole top of TX 218065 feeder to be tripped for safety Asset selection modified Asset selection modified Sending Asset Event to FFA FFA Order Created F-AE24CA6156-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA approx 2200 restore time Time On modified from 23:59 28-Apr to 22:00 28-Apr Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 22:00 28-Apr to 21:49 28-Apr Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA6156-1-0 bilcm03 REDACTED 0409971593 Sending Asset Event to FFA FFA Order En Route F-AE24CA6156-1-0 bilcm03 FFA Order On Site F-AE24CA6156-1-0 bilcm03 FFA Order F-AE24CA6156-1-0 Completed by technician REDACTED in crew BILCM03(0409971593) with code A-T-33 - Design Fault Action Taken : choke stay choked the top of the poll off replaced pole Site Label : 4140580 Updated Reasons tab. | 1 | 3195778 | X2833 168 Lookerbie Rd Thangool | 1658451 | 4140580 | 3195778 | 2021-04-20 | N |  |  | 12.5 | 3 |  | Unserviceable - P2 | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | Unknown | EECL | 1658451 | PO | 11.261 | 0 | 1665.6956 |  |  |  |  | 1 |  |  |  | '-70 |  | 257 |  | 12 |  | 808 | 46 | 100 |  | 129 |  | -24.508 | 150.5759 | 1989 | PO4140580 | 000003195778 | 1980s | EASTERN/COASTAL
EECL | OT232307 | Operational |  | 2024-04-07 | 202404 |  | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay | Replace | 11kV |  |  |  | 1512185 | 2024 | 24SW7321 | 2024-04-07 | [5 empty] | South West | 2024-04-07 04:24 | 0.18303 |  | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | [9 empty] | 1512185 |  |  | 2024-01-19 | [6 empty] | Serviceable | Y | Urb sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | SG SPOTTED GUM | 12 kiloNewton | EECL | [25 empty] | -27.5139 | 151.3904 | 1966 | PO3145248 | 000003218543 | 1960s | WESTERN
EECL | OT236006 | Operational |  | 2024-05-14 | 202405 | 2024-05-15 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay External |  | 11kV |  |  |  | 1362655 | 2024 | 24WB5700 | 2024-05-15 | 2024-05-15 19:33 |  |  | Normal Event |  | Wide Bay | 2024-05-15 14:00 | 2024-05-15 08:08 | Completed | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE |  | ROSEDALE, WATALGAN, YANDARAN | Rotted off pole needs changing S/L 2091529 | Switching Sheet ID updated from to J-310446-g. S-14622-q Switching Sheet Written Switch Sheet Distributed Sending Asset Event to FFA FFA Order Created F-AE24WB5700-1-0 DfltHost FFA Order Acknowledged F-AE24WB5700-1-0 bndcsfr12 REDACTED 0419736136 FFA Order En Route F-AE24WB5700-1-0 bndcsfr12 FFA Order On Site F-AE24WB5700-1-0 bndcsfr12 FFA Order F-AE24WB5700-1-0 Completed by technician REDACTED in crew bndcsfr12(0419736136) with code A-F-C - Completed Action Taken : replaced pole Site Label : 2091529 Time On modified from 21:00 15-May to 19:33 15-May | 1 | 9400569 | 2plsWstSW2912pst244MattonsRdAvondale | 1362655 | 2091529 | 9400569 | 2019-05-13 |  |  |  | 14 | 2 |  | Serviceable | N | Rrl sty term 1 cct | WOOD UNTREATED ROUND | Grass | Paddock Crop | ZZ NO DISC - UNKNOWN | 3 kiloNewton | EECL | 1362655 | PO | 9.835 | 0 | 1502.5678 | [8 empty] | 0 |  | 248 |  | 10 |  | 780 | 28 |  | 124 |  |  | -24.7604 | 152.1059 | 1956 | PO2091529 | 000009400569 | 1950s | EASTERN/COASTAL
EECL | OT238042 | Operational |  | 2024-06-05 | 202406 | 2024-06-06 | Pole-Wood | Wood Pole Below Ground | Broken | Rot/Decay External |  | LV |  |  |  | 830435 | 2024 | 24NQ9511 | 2024-06-05 | 2024-06-06 15:11 |  |  | Normal Event |  | North Queensland | 2024-06-05 16:30 | 2024-06-06 15:27 | Completed | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 889 KIRKNIE RD;HOME HILL QLD 4806 | Fault occurred at:05/06/2024 15:38; REDACTED;>UPH --> Details:Low Hanging Wires-WiresExposed:NO,TripHazard:NO -- WireLocation:poleToPole -- WiresLowEnoughToTouch:YES >> WDPP --> AffectingTraffic:NO -- StillHavePower:YES<;Incident Details:Called to advise lines are a lot lower than it should be, harvester would hit lines when in the fields.;COVID-19:NO;Warnings[uphSafety]: ADVISED;Sensitive Load:N |  | 1 | 9407436 | T off at 887-889 Kirknie Rd.Home hill | 830435 | 5046573 | 9407436 | 2020-02-18 |  |  |  | 14 |  | 1 | Serviceable | Y | Rrl unsty trm 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | RM RED MAHOGANY | 12 kiloNewton | EECL | 830435 | PO | 23.259 | 0 | 3553.5224 |  |  |  | 1 |  |  |  | 1 | 50 |  | 334 |  | 14 |  | 1050 | 29 |  | 167 |  |  | -19.7073 | 147.3438 | 1967 | PO5046573 | 000009407436 | 1960s | EASTERN/COASTAL
EECL | OT237837 | Operational |  | 2024-06-04 | 202406 | 2024-06-04 | Pole-Wood | Wood Pole Beyond 2m | Broken | Lightning |  | 19kV |  |  |  | 775624 | 2024 | 24SW9638 | 2024-06-04 | 2024-06-04 17:11 |  |  | Normal Event | Fine | South West | 2024-06-04 06:12 | 2024-06-04 06:14 | Completed | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | BOLLON, DIRRANBANDI | ST GEORGE 33kV Bollan CB1552 CB tripped. SCADA Interface automated outage. F-2840-r | entered from the SCADA Interface Crew will leave depot at 7am Depot Co-ord Advised REDACTED advise he has called locals in area, no faults calls history of heavy spider webs and dew tripping line before. MRC completed mrc unsuccessful 0705 crew to patrol line from CB1552 stgcmfr01 Sending Asset Event to FFA FFA Order Created F-AE24SW9638-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW9638-1-0 stgcmfr01 REDACTED 0439250268 FFA Order En Route F-AE24SW9638-1-0 stgcmfr01 FFA Order On Site F-AE24SW9638-1-0 stgcmfr01 crews advise nothing obvious on remainder of 33kV line. further fault finding through remote switching to be carried out Sending Asset Event to FFA Crew have found HV pole down. Switching for repairs underway. Sending Asset Event to FFA Pole/s Down Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 04-Jun to 17:02 04-Jun Sending Asset Event to FFA Sending Asset Event to FFA Replay sequence/s deleted after 04-JUN-24 16:58:00 Asset selection modified Time On modified from 17:02 04-Jun to 19:02 04-Jun Sending Asset Event to FFA Replay sequence/s deleted after 04-JUN-24 16:58:00 Asset selection modified Sending Asset Event to FFA Bypass fuse at DO5444482 blown when re-energised, suspect cold load pickup, opened down stream reclosers and staggered closing, Bypass fuse held Time On modified from 19:02 04-Jun to 17:11 04-Jun Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW9638-1-0 Completed by technician REDACTED in crew stgcmfr01(0439250268) with code A-T-62 - Lightning Action Taken : replaced broken temporary pole Site Label : SL3092086 Actual Power Restoration for F-AE24SW9638-1-0: 04-JUN-2024 17:19:00 | 1 | 9406843 | PC4494 3685 Fernlee Rd Bollon | 775624 | 3092086 | 9406843 | 2020-05-03 |  |  |  | 12.5 |  |  | Serviceable | Y | SWER sty angle | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | EECL | 775624 | PO | 9.446 | 0 | 1397.2014 | 1 | [7 empty] | '-110 |  | 255 |  | 4 |  | 800 | 64 |  |  | 50 |  | -28.2422 | 147.2558 | 1970 | PO3092086 | 000009406843 | 1970s | WESTERN
EECL | OT237640 | Operational |  | 2024-06-01 | 202406 | 2024-06-02 | Pole-Wood | Wood Pole Beyond 2m | Broken | Rot/Decay External |  | 33kV |  |  |  | 1021935 | 2024 | 24SW9585 | 2024-06-01 | 2024-06-02 13:00 |  |  | Normal Event | Wet / Rain | South West | 2024-06-01 16:03 | 2024-06-01 16:13 | Completed | Unplanned Outage | SUBT-Unassisted failure(Apparent defect) | Unknown | due to damage requiring emergency repairs. Fault finding is in progress. | ZS |  | N/A | F-3416-q 33kV Circuit Breaker CB3012 - trip to lockout | 33kV Circuit Breaker CB3012 - trip to lockout TWMOC03 Sending Asset Event to FFA FFA Order Created F-AE24SW9585-1-0 DfltHost FFA Order Acknowledged F-AE24SW9585-1-0 twmoc03 FFA Order En Route F-AE24SW9585-1-0 twmoc03 FFA Order On Site F-AE24SW9585-1-0 twmoc03 Time On modified from 23:59 01-Jun to 12:00 02-Jun Sending Asset Event to FFA Pole replacement required, Isolated and Earthed, crew to take permit in the morning. Sending Asset Event to FFA Delayed. Sending Asset Event to FFA FFA Order En Route F-AE24SW9585-1-0 twmoc03 FFA Order On Site F-AE24SW9585-1-0 twmoc03 Time On modified from 12:00 02-Jun to 13:58 02-Jun Sending Asset Event to FFA Time On modified from 13:58 02-Jun to 13:00 02-Jun Sending Asset Event to FFA Pole/s Down Sending Asset Event to FFA FFA Order F-AE24SW9585-1-0 Completed by technician REDACTED in crew twmoc03() with code A-T-28 - Overload Action Taken : 33kv line tripped between postman’s ridge and north Toowoomba. Wires still above stat height, pole broken at base. Site Label : 2137684 | 1 | 9406250 | acc gate 300m SE 341 Jones Rd, Withcott | 1021935 | 2137684 | 9406250 | 2023-12-13 |  |  |  | 14 | 2 |  | Serviceable | N | Rrl inter spn >200m | WOOD UNTREATED ROUND | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 12 kiloNewton | EECL | 1021935 | PO | 30.724 | 8 | 5120.5977 |  |  |  |  | 1 |  |  |  | 0 | 15 | 383 | 0 | 6 |  | 1251 | 21 |  |  | 92 |  | -27.5336 | 152.0141 | 1954 | PO2137684 | 000009406250 | 1950s | WESTERN