## Insights
| Count of WORK_ORDER | Column Labels
| Row Labels | Corrosion | Incorrect Installation | Laminated | Leakage | Rot/Decay | Termites | Unknown | Vibration | Grand Total
| Xarm, Wood Intermediate |  |  |  | 1 | 89 | 6 | 1 | 1 | 98
| Xarm, Wood Termination |  |  |  |  | 77 | 4 |  | 1 | 82
| Xarm, Wood Strain | 1 |  | 1 |  | 57 | 4 |  | 1 | 64
| Xarm, Wood Dressing |  |  |  |  | 7 | 2 |  | 1 | 10
| Xarm Strap(S) | 1 | 1 | [5 empty] | 3 | 5
| Xarm Bracket Nuts | 2 | [5 empty] | 1 | 1 | 4
| Xarm Kingbolt | 3 | [7 empty] | 3
| Xarm, Steel Termination | 2 | [7 empty] | 2
| Grand Total | 9 | 1 | 1 | 1 | 230 | 16 | 2 | 8 | 268
| Count of WORK_ORDER | Column Labels
| Row Labels | Corrosion | Incorrect Installation | Laminated | Leakage | Rot/Decay | Termites | Unknown | Vibration | Grand Total
| Broken | 6 | 1 |  |  | 171 | 5 | 1 |  | 184
| Burnt Off |  |  |  | 1 | 1 |  |  |  | 2
| Deteriorated | 3 |  |  |  | 42 | 8 | 1 |  | 54
| Loose Fitting | [7 empty] | 7 | 7
The predominant type of crossarm that fails is wood which is still the most dominant material used in legacy constructions on the Ergon Energy network. Composite crossarms are now used for all maintenance, replacement and augmentation works. Majority of wood crossarms fail due to rot/decay. Often it is rot/decay that can't be seen from the groundline, hence why aerial inspection methods are now being used to capture deterioration on the top side of the crossarm. | Split |  |  | 1 |  | 16 | 3 |  | 1 | 21
| Grand Total | 9 | 1 | 1 | 1 | 230 | 16 | 2 | 8 | 268
| Count of WORK_ORDER | Column Labels
| Row Labels | Xarm Bracket Nuts | Xarm Kingbolt | Xarm Strap(S) | Xarm, Steel Termination | Xarm, Wood Dressing | Xarm, Wood Intermediate | Xarm, Wood Strain | Xarm, Wood Termination | Grand Total
| 11kV | 2 | 2 | 3 |  | 8 | 50 | 35 | 38 | 138
| LV |  | 1 |  | 2 | 2 | 15 | 20 | 34 | 74
| 22kV | [5 empty] | 16 | 8 | 9 | 33
| 66kV | 1 |  | 1 |  |  | 12 |  |  | 14
| 19kV | [5 empty] | 3 |  | 1 | 4
| 33kV |  |  | 1 |  |  | 1 | 1 |  | 3
Many of the crossarms that fail are 11kV, LV and 22kV, which are the 3 most common voltages that crossarms are used for in the distribution network. | 12.7kV | [5 empty] | 1 |  |  | 1
| 6.6kV | 1 | [7 empty] | 1
| Grand Total | 4 | 3 | 5 | 2 | 10 | 98 | 64 | 82 | 268

## Failure Detail Xarms
DSTRCT_CODE | WORK_ORDER | WO_TYPE | WO_TYPE_DESCRIPTION | WO_DESC | RAISED_DATE | YYYYMM | COMP_CODE_DESCRIPTION | MSSS_OBJECT_FAILURE_DESCRIPTION | MSSS_DAMAGE_APPARENT_CAUSE_DESCRIPTION | MSSS_CAUSE_DESCRIPTION | CONSEQUENCE_DESCRIPTION | VOLTAGE_DESCRIPTION | WORK_ORDER_EXTENDED_DESCRIPTION | COMPLETION_COMMENTS | COMPLETED_BY_DESC | EQUIP_NO | FISCAL_YEAR | OUTAGE_NAME | OUTAGE_ACTUAL_START_TIMESTAMP | OUTAGE_CREATED_DATE_TIMESTAMP | OUTAGE_STATUS_CODE | OUTAGE_STATUS_DESCRIPTION | MSS_MAJOR_EVENT_DAY_EVENT_CODE | OUTAGE_WEATHER_DESCRIPTION | SUB_REGION_NAME | OUTAGE_TYPE_DESCRIPTION | OUTAGE_TRIGGER_DESCRIPTION | OUTAGE_STANDARD_REASON_DESCRIPTION | OUTAGE_REASON_DESCRIPTION | OUTAGE_PRIMARY_ASSET_HIER_TYPE_ID | DEFECT_CAUSE_DESCRIPTION | OUTAGE_DESCRIPTION | OUTAGE_COMMENTARY | OUTAGE_LOG_DETAILS | RNUM | EQUIP_2 | ITEM_NAME_1 | PARENT_EQUIP | PARENT_ITEM_NAME_1 | EQUIPMENT_NUMBER | DATE_LAST_INSPECTED | DAYS BETWEEN INSPECTION AND FAILURE | FAULT_INDICATOR_FITTED | INSPECTED_BY | INSPECTION_CONTRACTOR | LENGTH_OF_POLE | NUMBER_OF_HV_ARMS | NUMBER_OF_LV_ARMS | POLE_CONDITION_DESCRIPTION | POLE_EARTH | POLE_STRUCTURE_TYPE_DESCRIPTION | POLE_CHEMICAL_TREATMENT_DESCRIPTION | POLE_SITE_CHARACTERISTICS_DESCRIPTION | UNDERGROUND_SITE_ENVIRONMENT_DESCRIPTION | SPECIES_DESCRIPTION | STRENGTH_DESCRIPTION | TREATMENT_YEAR_DESCRIPTION | Latitude | Longitude | Equip | RIN-COMM-DT
EECL | OT188322 | OP | Operational |  | 2023-07-05 | 202307 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 11kV |  | ? |  | 951925 | 2024 | 23WB7263 | 2023-07-05 13:30 | 2023-07-05 13:32 | COMP | Completed | ? | Fine | Wide Bay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC | ? | BARAMBAH, JOHNSTOWN, MOFFATDALE, NANANGO, SANDY RIDGES | F-717-r MURGON 11kV Barambah Rd S6028 ACR CB tripped. SCADA Interface automated outage.\r\n1350hrs Reclose Failed on OC Trip, REDACTED sendsing crew to sectionalise\r\nCrew repaired broken top arm on tee off pole. SL 3046409. REDACTED | entered from the SCADA Interface\r\nOC Trip to Lockout\r\nManual Reclose Checklist\r\nDepot Co-ord Advised\r\nReclose Failed on OC Trip, REDACTED sendsing crew to sectionalise\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23WB7263-1-0 DfltHost\r\nSectionalized to Links S1917\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23WB7263-1-0 mrgcm01 REDACTED 0428071189\r\nFFA Order En Route F-AE23WB7263-1-0 mrgcm01\r\nFFA Order On Site F-AE23WB7263-1-0 mrgcm01\r\nTime On modified from 23:59 05-Jul to 18:11 05-Jul\r\nSending Asset Event to FFA\r\nFFA Order F-AE23WB7263-1-0 Completed by technician REDACTED in crew MRGCM01(0428071189) with code A-T-306 - HV-Unassisted failure(Apparent defect)\r\nAction Taken : top arm on tee off pole broken and repaired\r\nSite Label : 3046409\r\nUpdated Reasons tab.\r\nReason for Event changed from Unknown | 1 | 2739541 | 2332 Burnett hwy, Wyalla. T to house | 951925 | 3046409 | 2739541 | 2019-03-25 | 1563 | ? |  |  | 14 | 2 | ? | Serviceable | N | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1983 | -26.4826 | 152.0601 | 000002739541 | 01/JAN/83
EECL | OT188323 | OP | Operational |  | 2023-07-05 | 202307 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay | ? | 22kV |  | ? |  | 1058255 | 2024 | 23CA8056 | 2023-07-05 15:01 | 2023-07-05 13:48 | COMP | Completed | ? | ? | Capricornia | Forced Outage | ? | P1 Lines works | to allow emergency maintenance of the electricity network. | FC | ? | BOROREN, FORESHORES, IVERAGH, TURKEY BEACH | 22kV Disc Links X778882 Outage required to repair broken Xarm.\r\n\r\n22kV Disc Links X778882\r\n22KV Droup out DO884619\r\n22KV Disc Links DL884618\r\nEarth at Junction of all\r\n\r\nCrew replaced broken HV flat pin cross-arm at SL 4155397 REDACTED | Switching Sheet ID updated from to J-266085-g.\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23CA8056-1-0 DfltHost\r\nPut on Pad PCOC07\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 05-Jul to 16:30 05-Jul\r\nSending Asset Event to FFA\r\nTime On modified from 16:30 05-Jul to 17:00 05-Jul\r\nSending Asset Event to FFA\r\nTime Off modified from 14:30 05-Jul to 14:46 05-Jul\r\nSending Asset Event to FFA\r\nTime Off modified from 14:46 05-Jul to 15:01 05-Jul\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23CA8056-1-0 pcoc07 REDACTED 0428577597\r\nFFA Order En Route F-AE23CA8056-1-0 pcoc07\r\nFFA Order On Site F-AE23CA8056-1-0 pcoc07\r\nFFA Order F-AE23CA8056-1-0 Completed by technician REDACTED in crew pcoc07(0428577597) with code A-F-C - Completed\r\nAction Taken : broken hv flat pin x arm, organised forced outage to replace arm, arm replaced. power restored\r\nSite Label : 4155397\r\nTime On modified from 17:00 05-Jul to 16:03 05-Jul\r\nAdded notes to Reasons tab. | 1 | 3248043 | 3 SE X11876 44799 Bruce Hwy Miriam Vale | 1058255 | 4155397 | 3248043 | 2019-08-07 | 1428 | N |  |  | 11 | 1 | ? | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1971 | -24.2973 | 151.5151 | 000003248043 | 01/JAN/71
EECL | OT188225 | OP | Operational |  | 2023-07-05 | 202307 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1018280 | 2024 | 23SW9113 | 2023-07-05 04:49 | 2023-07-05 04:55 | COMP | Completed | ? | ? | South West | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC | ? | CENTENARY HEIGHTS, MIDDLE RIDGE, RANGEVILLE, TOOWOOMBA | F-27607-g Recloser RC848099 tripped for safety due to sparking lines, broken crossarm- conductors hanging near LV\r\nCrew repaired broken HV angle arm at SL 3250563 REDACTED | Recloser RC848099 tripped for safety due to sparking lines, broken crossarm- conductors hanging near LV\r\nTime Off modified from 05:30 05-Jul to 04:49 05-Jul\r\nREDACTEDadvised he is getting to site in appox 10mins to confirm fault area and isolation. Backfeed to proceed once confirmed\r\nF-27607-g\r\ntwmoc01\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23SW9113-1-0 DfltHost\r\nswitching commenced to isolate/earth and backfeed\r\nREDACTEDadvised crews have run out of hrs. Day shift crew to start in 25mins and they will attend. REDACTED advise to leave switching as is.\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nSupply restored beyond DL890332 Via SD542244 at 06.46\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 05-Jul to 11:01 05-Jul\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23SW9113-1-0 twmoc01 REDACTED 0418712115\r\nFFA Order En Route F-AE23SW9113-1-0 twmoc01\r\nFFA Order On Site F-AE23SW9113-1-0 twmoc01\r\nFFA Order F-AE23SW9113-1-0 Completed by technician REDACTED in crew twmoc01(0418712115) with code A-F-C - Completed\r\nAction Taken : isolated earthed made safe\nrepaired broken hv angle arm SL3250563\nconductors above stat height upon arrival\r\nSite Label : 3250563\r\nAdded notes to Reasons tab. | 1 | 2644043 | 6 Dorge St,Toowoomba | 1018280 | 3250563 | 2644043 | 2022-05-30 | 401 | N |  |  | 14 | 1 | 1 | Serviceable | N | Rrl sty angle 5-20o | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 5 kiloNewton | 1981 | -27.6137 | 151.9676 | 000002644043 | 01/JAN/81
EECL | OT188546 | OP | Operational |  | 2023-07-07 | 202307 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1000232 | 2024 | 23WB7311 | 2023-07-07 13:25 | 2023-07-07 13:28 | COMP | Completed | ? | ? | Wide Bay | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ | ? | LOWER WONGA, UPPER WONGA, WIDGEE | 11kV Recloser S3181 - Crew requested ACR Trip as grass fire and low conductor.\r\nCrew repaired broken cross-arm at SL 3037141 REDACTED\r\n | 11kV Recloser S3181 - Crew requested ACR Trip as grass fire and low conductor.\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23WB7311-1-0 DfltHost\r\nAsset selection modified\r\nTime On modified from 23:59 07-Jul to 17:30 07-Jul\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nTime On modified from 17:30 07-Jul to 19:00 07-Jul\r\nSending Asset Event to FFA\r\nCrew have found a PG Clamp beside Switch 6381 faulty.\r\nSending Asset Event to FFA\r\nTime On modified from 19:00 07-Jul to 18:21 07-Jul\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23WB7311-1-0 kkvcs01 REDACTED 0427809497\r\nFFA Order En Route F-AE23WB7311-1-0 kkvcs01\r\nFFA Order On Site F-AE23WB7311-1-0 kkvcs01\r\nFFA Order Suspended F-AE23WB7311-1-0 by REDACTED 0427809497\r\nFFA Order En Route F-AE23WB7311-1-0 kkvcs01\r\nFFA Order On Site F-AE23WB7311-1-0 kkvcs01\r\nFFA Order F-AE23WB7311-1-0 Completed by technician REDACTED in crew kkvcs01(0427809497) with code A-F-C - Completed\r\nAction Taken : Repaired broken HV x-arm. SL 3037141\r\nSite Label : 3037141\r\nAdded notes to Reasons tab. | 1 | 2692599 | 6E Tx15049 39 Gibbs Rd, Widgee | 1000232 | 3037141 | 2692599 | 2019-07-25 | 1443 | N |  |  | 11 | 1 | ? | Serviceable | N | Rrl inter spn >200m | WOOD UNTREATED ROUND | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | ? | -26.1591 | 152.4426 | 000002692599 | 01/JAN/61
EECL | OT188565 | OP | Operational |  | 2023-07-07 | 202307 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 19kV |  | ? |  | 925906 | 2024 | 23NQ7236 | 2023-07-07 15:13 | 2023-07-07 15:16 | COMP | Completed | ? | Fine | North Queensland | Unplanned Outage | HV-Conductor Connection Failure | Unknown | due to a SCADA Automated Event | FC | ? | BOGIE: TABLETOP RD\r\nCOLLINSVILLE: | JOHNNY CAKE RD, TABLETOP STATION F1677-s COLLINSVILLE 19kV Table Top No.1 ACR CB tripped. SCADA Interface automated outage. entered from the SCADA Interface\r\nContacted oncall crew REDACTED and he spoke with REDACTED in relation to a line patrol.Chopper is booked for 07:30 for the patrol. Contacted REDACTED 0407 743 819 to advise of this arrangement.\r\nTime On modified from 23:59 07-Jul to 23:59 08-Jul\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23NQ7236-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23NQ7236-1-0 clvoh01 REDACTED 0428766675\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 08-Jul to 19:18 08-Jul\r\nSending Asset Event to FFA\r\nTime On modified from 19:18 08-Jul to 19:18 07-Jul\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order En Route F-AE23NQ7236-1-0 clvoh01\r\nFFA Order On Site F-AE23NQ7236-1-0 clvoh01\r\nFFA Order On Site F-AE23NQ7236-1-0 clvoh01\r\nFFA Order F-AE23NQ7236-1-0 Completed by technician REDACTED in crew CLVOH01(0428766675) with code A-T-304 - HV-Conductor Connection Failure\r\nAction Taken : re attached hv 3/12 to eyebolt on angle pole\r\nSite Label : 5058955 |  | 1 | 2783828 | Strathmore Station to Table top | 925906 | 5058955 | 2783828 | 2020-11-30 | 949 | N |  |  | 12.5 | 1 | ? | Serviceable | N | SWER sty angle | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | ? | -20.4159 | 147.6899 | 000002783828 | 01/JAN/82
EECL | OT188635 | OP | Operational |  | 2023-07-08 | 202307 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 22kV |  | ? |  | 880396 | 2024 | 23CA8185 | 2023-07-08 18:33 | 2023-07-08 22:54 | COMP | Completed | ? | ? | Capricornia | Forced Outage | ? | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT | ? | SONOMA NO. 2;1439 LOWMEAD RD;MIRIAM VALE QLD 4677 | Fault occurred at:08/07/2023 16:02; REDACTED, 0749745173; >WIRESDOWN-PP --> AffectingTraffic:NO -- StillHavePower:YES<; Incident Details:Line down pole to pole - Down on the ground in the paddock, there are deceased cows near the line. Power went off approx 5 minutes at lunch and come back on again.; Access Details:Access ok - No covid - dogs locked away.; Warnings[WiresDownSafety]: ADVISED | ? | 1 | 2899368 | Acc Via 1439 Lowmead Rd Lowmead | 880396 | 4087773 | 2899368 | 2020-07-02 | 1101 | N |  |  | 12.5 | 1 | ? | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | RI RED IRONBARK | 5 kiloNewton | 1973 | -24.4343 | 151.6655 | 000002899368 | 01/JAN/73
EECL | OT188664 | OP | Operational |  | 2023-07-09 | 202307 | Crossarm | Xarm Bracket Nuts | Deteriorated | Corrosion | ? | 6.6kV |  | ? |  | 1149621 | 2024 | 23FN8199 | 2023-07-09 11:01 | 2023-07-09 09:24 | COMP | Completed | ? | ? | Far North | Forced Outage | ? | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | GT | ? | THURSDAY ISLAND: LOBAN ST, SAILOR CRES, WAIBEN ESP F-479-t - SS1137, Crew confirmed broken hv bridging arm from edo to TX. Access edo's to tx. | SS1137, Crew confirmed broken hv bridging arm from edo to TX. Access edo's to tx.\r\nTime Off modified from 11:20 09-Jul to 09:20 09-Jul\r\nREDACTED 0439 490 124\r\nTime Off modified from 09:20 09-Jul to 10:00 09-Jul\r\nSwitching Sheet ID updated from to J-266533-g.\r\nTime Off modified from 10:00 09-Jul to 09:42 09-Jul\r\nTime Off modified from 09:42 09-Jul to 11:01 09-Jul\r\nTime On modified from 23:59 09-Jul to 11:48 09-Jul\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23FN8199-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23FN8199-1-0 thioc01 REDACTED 0439490124\r\nFFA Order En Route F-AE23FN8199-1-0 thioc01\r\nFFA Order On Site F-AE23FN8199-1-0 thioc01\r\nFFA Order F-AE23FN8199-1-0 Completed by technician REDACTED in crew thioc01(0439490124 ) with code A-F-C - Completed\r\nAction Taken : replace xarm hardware\r\nSite Label : 5086330\r\nActual Power Restoration for F-AE23FN8199-1-0: 09-JUL-2023 12:32:00 |  | 1 | 2917505 | 65 waiben esp thursday island | 1149621 | WA22 | 2917505 | 2019-07-20 | 1450 | N |  |  | 14 | 5 | 3 | Serviceable | Y | Rrl sty angle 5-20o | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | SG SPOTTED GUM | 5 kiloNewton | 1968 | -10.5698 | 142.225 | 000009355696
EECL | OT188738 | OP | Operational |  | 2023-07-10 | 202307 | Crossarm | Xarm, Wood Strain | Deteriorated | Rot/Decay | ? | LV |  | ? |  | 1346682 | 2024 | 23WB7353 | 2023-07-10 09:36 | 2023-07-10 13:03 | COMP | Completed | ? | Fine | Wide Bay | Unplanned Outage | VEG: Inside Urban Grow-in (NSP responsibility) | Unknown | Single Fault Call | GT | ? | 2 SOUTH HEATH RD;BURRUM RIVER QLD 4659 | Fault occurred at:10/07/2023 09:33; REDACTED, 0410483784; >UPH --> Details:Low Hanging Wires -- WireLocation:poleToPole -- WiresLowEnoughToTouch:NO<; Incident Details:Low hanging wire. Cross bar at top of pole P6045511 appears to be rotten and snapped. Service line in trees.; Access Details:gates are open for access; Warnings[uphSafety]: ADVISED | ? | 1 | 2627255 | 2 SOUTH HEATH RD, BURRUM RIVER | 1346682 | 3025355 | 2627255 | 2019-07-12 | 1459 | N |  |  | 12.5 | 1 | 2 | Serviceable | N | Rrl Toff | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1980 | -25.2917 | 152.5849 | 000002627255 | 01/JAN/80
EECL | OT189025 | OP | Operational |  | 2023-07-12 | 202307 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1444645 | 2024 | 23MK4893 | 2023-07-12 14:12 | 2023-07-12 15:39 | COMP | Completed | ? | Wet / Rain | Mackay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to damage requiring emergency repairs. Fault finding is in progress. | SZ | ? | GARGETT: GARGETT-MIA MIA RD, MARKS RD, PUP CREEK RD, SEPTIMUS RD | 11kV Dropout Fuse FLKS766190 - Crews advise one fuse down. Carrying out line patrol. | 11kV Dropout Fuse FLKS766190 - Crews advise one fuse down. Carrying out line patrol.\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23MK4893-1-0 DfltHost\r\nSending Asset Event to FFA\r\nManual Reclose Checklist\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23MK4893-1-0 pncoc01 REDACTED 0419471653\r\nFFA Order En Route F-AE23MK4893-1-0 pncoc01\r\nFFA Order On Site F-AE23MK4893-1-0 pncoc01\r\nRestoration Comments for F-AE23MK4893-1-0 by pncoc01: repaired x arm\r\nTime On modified from 23:59 12-Jul to 19:30 12-Jul\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order En Route F-AE23MK4893-1-0 pncoc01\r\nFFA Order On Site F-AE23MK4893-1-0 pncoc01\r\nFFA Order F-AE23MK4893-1-0 Completed by technician REDACTED in crew pncoc01(0419471653) with code A-T-304 - HV-Conductor Connection Failure\r\nAction Taken : replaced broken x arm \r\nSite Label : 2036512\r\nauto-completed | 1 | 5983641 | 675 gargett-mia mia rd gargett | 1444645 | 2036512 | 5983641 | 2019-12-06 | 1314 | N |  |  | 12.5 | 1 | ? | Serviceable | N | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1981 | -21.1875 | 148.7498 | 000005983641 | 01/JAN/81
EECL | OT189190 | OP | Operational |  | 2023-07-14 | 202307 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay | ? | LV |  | ? |  | 1556673 | 2024 | 23SW9459 | 2023-07-14 09:07 | 2023-07-14 08:19 | COMP | Completed | ? | ? | South West | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT | ? | DALBY: DAKOTA PL, MCQUEEN ST, NICHOLSON ST, PRATTEN ST, WAMBO ST, WEALE ST\r\nMAREEBA: | NOLAN ST 11kV Pole Dist Sub PC01171 - Crew need access to TX to repair faulty Xarm\r\nCrew replaced LV arm. SL 6014446. REDACTED | 11kV Pole Dist Sub PC01171 - Crew need access to TX to repair faulty Xarm\r\ndlbfrl02\r\nSending Asset Event to FFA\r\nTime Off modified from 08:45 14-Jul to 09:07 14-Jul\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nTime On modified from 10:30 14-Jul to 11:30 14-Jul\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23SW9459-1-0 DfltHost\r\nRemoving Asset Event from FFA\r\nFFA Order cancelled.F-AE23SW9459-1-0\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23SW9459-1-1 DfltHost\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23SW9459-1-1 dlbfrl02 REDACTED 0437799747\r\nFFA Order En Route F-AE23SW9459-1-1 dlbfrl02\r\nFFA Order On Site F-AE23SW9459-1-1 dlbfrl02\r\nTime On modified from 11:30 14-Jul to 11:40 14-Jul\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order F-AE23SW9459-1-1 Completed by technician REDACTED in crew dlbfrl02(0437799747) with code A-F-C - Completed\r\nAction Taken : LV arm replaced \r\nSite Label : 6014446\r\nTime On modified from 11:40 14-JUL to 11:31 14-JUL\r\nAdded notes to Reasons tab. | 1 | 2184175 | SS1171,acc by 125 Nicholson St,Dalby | 1556673 | 6014446 | 2184175 | 2023-07-14 | 0 | N |  |  | 11 | ? | 1 | Serviceable | Y | Tfr support pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 8 kiloNewton | ? | -27.1892 | 151.2462 | 000002184175 | 01/JAN/77
EECL | OT189569 | OP | Operational |  | 2023-07-18 | 202307 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay | ? | 66kV |  | ? |  | 1860880 | 2024 | 23MK5008 | 2023-07-18 10:18 | 2023-07-18 10:20 | COMP | Completed | ? | Fine | Mackay | Unplanned Outage | HV-Conductor Connection Failure | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | ZS | ? | CREDITON, DALRYMPLE HEIGHTS, EUNGELLA | F-1713-s PINNACLE 66kV Eungella Fdr CB EA04Q00 tripped. SCADA Interface automated outage. | entered from the SCADA Interface\r\nCrews to attend site to get distance to fault\r\nAsset selection modified\r\nCrews have advised 66kV Xarm has snapped on Teemburra recloser. All customers beyond this recloser now isolated to repair 66/11kV Pole\r\nAsset selection modified\r\nAsset selection modified\r\nReason for Event changed from Unknown\r\nTime On modified from 23:59 18-Jul to 15:00 18-Jul\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23MK5008-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23MK5008-1-0 pncoc01 REDACTED 0437597426\r\nFFA Order En Route F-AE23MK5008-1-0 pncoc01\r\nFFA Order On Site F-AE23MK5008-1-0 pncoc01\r\nTime On modified from 15:00 18-Jul to 20:00 18-Jul\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nFFA Order F-AE23MK5008-1-0 Completed by technician REDACTED in crew pncoc01(0437597426) with code A-T-304 - HV-Conductor Connection Failure\r\nAction Taken : replaced 66kv arm due to root causing it to break and land on the 11kv arm\r\nSite Label : 4142983\r\nAsset selection modified\r\nAsset selection modified\r\nTime On modified from 20:00 18-Jul to 17:57 18-Jul | 1 | 3208896 | ACR Lucas Paddock rd Pinnacle | 1860880 | 4142983 | 3208896 | 2020-05-05 | 1169 | N |  |  | 17 | 3 | ? | Serviceable | Y | 66kV inter & 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | GI GREY IRONBARK | 8 kiloNewton | 1994 | -21.1558 | 148.7068 | 000003208896 | 01/JAN/94
EECL | OT189976 | OP | Operational |  | 2023-07-22 | 202307 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1424162 | 2024 | 23WB11055 | 2023-07-22 14:22 | 2023-07-22 12:27 | COMP | Completed | ? | ? | Wide Bay | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ | ? | KINGAROY, TAABINGA | Repair Broken Crossarm at 6045 | Repair Broken Crossarm at 6045\r\nSwitching Sheet ID updated from to J-268753-g.\r\nTime Off modified from 13:00 22-Jul to 14:17 22-Jul\r\nTime Off modified from 14:17 22-Jul to 14:22 22-Jul\r\nReverse Switching in progress\r\nTime On modified from 23:59 22-Jul to 17:00 22-Jul\r\nTime On modified from 17:00 22-Jul to 15:38 22-Jul | 1 | 3150958 | Tx 10471 Bunya hwy, Kingaroy. rear-dam | 1424162 | 4241902 | 3150958 | 2021-10-01 | 659 | N |  |  | 12.5 | 4 | 1 | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Backyard | SG SPOTTED GUM | 8 kiloNewton | 1977 | -26.5809 | 151.8147 | 000003150958 | 01/JAN/77
EECL | OT190148 | OP | Operational |  | 2023-07-24 | 202307 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | LV |  | ? |  | 1429124 | 2024 | 23CA11417 | 2023-07-24 17:43 | 2023-07-24 17:33 | COMP | Completed | ? | ? | Capricornia | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT | ? | NORMAN GARDENS: GERMAN ST, HALLIGAN CRES, MARCELLIN CT, WRIGHT ST | Crew require LV outage on 11kV Pole Dist Sub 21593 to replace LV x-arm\r\n | Crew require LV outage on 11kV Pole Dist Sub 21593 to replace LV x-arm\r\n REDACTED, ccoc01\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23CA11417-1-0 DfltHost\r\nSending Asset Event to FFA\r\nTime Off modified from 17:45 24-Jul to 17:36 24-Jul\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23CA11417-1-0 ccoc01 REDACTED 0427525026\r\nFFA Order En Route F-AE23CA11417-1-0 ccoc01\r\nFFA Order On Site F-AE23CA11417-1-0 ccoc01\r\nFFA Order F-AE23CA11417-1-0 Completed by technician REDACTED in crew Ccoc01(0427525026) with code A-F-C - Completed\r\nAction Taken : Replace rotten LV intermediate cross arm\r\nSite Label : 4126371\r\nTime On modified from 21:00 24-JUL to 19:38 24-JUL\r\nTime Off modified from 17:36 24-Jul to 17:43 24-Jul | 1 | 3106311 | 3 marcellin ct rockhampton | 1429124 | No Description Provided | 3106311 | 2019-07-10 | 1475 | N |  |  | 11 | ? | 1 | Serviceable | N | Urb LV inter | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | ZZ NO DISC - UNKNOWN | 8 kiloNewton | ? | -23.3332 | 150.5352 | 000003106311 | 01/JAN/85
EECL | OT190160 | OP | Operational |  | 2023-07-24 | 202307 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay | ? | 22kV |  | ? |  | 1275955 | 2024 | 23FN10825 | 2023-07-24 20:00 | 2023-07-24 20:02 | COMP | Completed | ? | Cold | Far North | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC | ? | TOLGA: MARNANE RD\r\nARRIGA: KIPPIN DR\r\nWALKAMIN: DATI RD, CURRAN RD, HANSEN RD, CHANNEL RD, ALLWOOD LANE | F-1684-q ATHERTON 22kV Channel Rd Spur SC1 ACR CB tripped. SCADA Interface automated outage.\r\nCrew repaired broken HV termination arm. SL 2144681. REDACTED | entered from the SCADA Interface\r\nF-1684-q\r\nOC Trip.\r\nReason for Event changed from Unknown\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23FN10825-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23FN10825-1-0 athoc01 REDACTED 0400176065\r\nFFA Order En Route F-AE23FN10825-1-0 athoc01\r\nManual Reclose Checklist\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 24-Jul to 03:00 25-Jul\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nFFA Order En Route F-AE23FN10825-1-0 athoc01\r\nFFA Order On Site F-AE23FN10825-1-0 athoc01\r\nFFA Order F-AE23FN10825-1-0 Completed by technician REDACTED in crew athoc01(0407140682) with code A-T-306 - HV-Unassisted failure(Apparent defect)\r\nAction Taken : broken hv termination arm\r\nSite Label : 2144681\r\nTime On modified from 03:00 25-Jul to 00:52 25-Jul\r\nUpdated Reasons tab.\r\nReason for Event changed from Protective Device Operated | 1 | 2377401 | T-off 5 spns nth 603 Channel Rd Walkamin | 1275955 | SC52 | 2377401 | 2020-09-09 | 1048 | N |  |  | 12.5 | 2 | ? | Serviceable | N | HV fully suppd | WOOD UNTREATED ROUND | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 12 kiloNewton | 1961 | -17.1356 | 145.397 | 000002377401 | 01/JAN/61
EECL | OT190378 | OP | Operational |  | 2023-07-26 | 202307 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1815445 | 2024 | 23NQ9491 | 2023-07-26 11:04 | 2023-07-26 11:03 | COMP | Completed | ? | ? | North Queensland | Forced Outage | ? | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FE | ? | IDALIA, MUNDINGBURRA, OONOONBA, ROSSLEA | F-1742-s OONN-04 feeder tripped due to FC 2353993 - reportg of broken xarm. suspect HV sitting on LV xarm | OONN-04 feeder tripped due to FC 2353993 - reportg of broken xarm. suspect HV sitting on LV xarm\r\nTime Off modified from 11:30 26-Jul to 11:03 26-Jul\r\nTime Off modified from 11:03 26-Jul to 11:04 26-Jul\r\ncrew adv broken xarm at SL 2098408. waiting for switc op assist to open ABS Abbott ST No.1 and back feed\r\nall customers restored except TVS1990. switching for access\r\nAsset selection modified\r\nTime On modified from 23:59 26-Jul to 16:00 26-Jul\r\nTime On modified from 16:00 26-Jul to 14:57 26-Jul\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23NQ9491-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23NQ9491-1-0 twvfr07 REDACTED 0458215615\r\nFFA Order En Route F-AE23NQ9491-1-0 twvfr07\r\nFFA Order On Site F-AE23NQ9491-1-0 twvfr07\r\nFFA Order F-AE23NQ9491-1-0 Completed by technician REDACTED in crew twvfr07(0458215615) with code A-F-C - Completed\r\nAction Taken : replaced broken cross arm and defective cross arm\r\nSite Label : 2098408 & 2098407 | 1 | 2277701 | 128 ABBOTT ST oonoonba | 1815445 | 2098408 | 2277701 | 2019-12-18 | 1316 | N |  |  | 12.5 | 1 | 1 | Serviceable | N | Urb inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | ZZ NO DISC - UNKNOWN | 8 kiloNewton | ? | -19.3059 | 146.8203 | 000002277701 | 01/JAN/80
EECL | OT190648 | OP | Operational |  | 2023-07-28 | 202307 | Crossarm | Xarm, Wood Strain | Deteriorated | Rot/Decay | ? | 11kV |  | ? |  | 1105511 | 2024 | 23WB11256 | 2023-07-28 16:27 | 2023-07-28 16:13 | COMP | Completed | ? | ? | Wide Bay | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ | ? | DUCKINWILLA: BRUCE HWY\r\nMARYBOROUGH: BRUCE HWY\r\nTORBANLEA: BRUCE HWY | F-27780-g Crew require access part S498 to repair broken crossarm | Crew require access part S498 to repair broken crossarm\r\nF-27780-g\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23WB11256-1-0 DfltHost\r\nSending Asset Event to FFA\r\nTime Off modified from 16:30 28-Jul to 16:27 28-Jul\r\nSending Asset Event to FFA\r\nTime On modified from 18:30 28-Jul to 19:00 28-Jul\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23WB11256-1-0 hboc01 REDACTED 0436384632\r\nFFA Order En Route F-AE23WB11256-1-0 hboc01\r\nFFA Order On Site F-AE23WB11256-1-0 hboc01\r\nTime On modified from 19:00 28-Jul to 18:50 28-Jul\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order F-AE23WB11256-1-0 Completed by technician REDACTED in crew hboc01(0436384632) with code A-F-C - Completed\r\nAction Taken : replace broken crossarm.\nConductors at that height 7,1m \r\nSite Label : 3013878 | 1 | 2557266 | 1e sw6931a Churchill Mine Rd Torbanlea | 1105511 | 3013878 | 2557266 | 2022-05-18 | 436 | N |  |  | 12.5 | 3 | ? | Serviceable | N | HV partly suppd | WOOD UNTREATED ROUND | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 8 kiloNewton | ? | -25.3702 | 152.6438 | 000002557266 | 01/JAN/56
EECL | OT190615 | OP | Operational |  | 2023-07-28 | 202307 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay | ? | LV |  | ? |  | 784546 | 2024 | 23WB11251 | 2023-07-28 11:03 | 2023-07-28 14:35 | COMP | Completed | ? | Fine | Wide Bay | Unplanned Outage | LV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT | ? | 181 EATONVALE RD TINANA QLD 4650 | Fault occurred at:28/07/2023 11:00 | (name not given), (phone not given) >PILLARDAMAGED --> PillarDamagedReason:Other -- WiresExposed:NO< Incident Details:Crossarm Snapped and Powerlines are hanging low to the ground. 4m from ground. Access Details:Driveway Warnings[pillarDamaged]: ADVISED | 1 | 2714923 | 181 eatonvale rd,tinana | 784546 | 6044095 | 2714923 | 2022-10-24 | 277 | N |  |  | 11 | ? | 2 | Serviceable | N | LV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Front Yard | SG SPOTTED GUM | 8 kiloNewton | 1991 | -25.5374 | 152.6673 | 000002714923 | 01/JAN/91
EECL | OT190712 | OP | Operational |  | 2023-07-29 | 202307 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1840208 | 2024 | 23SW15583 | 2023-07-29 20:18 | 2023-07-29 19:16 | COMP | Completed | ? | Fine | South West | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC | ? | WELLCAMP: BARKLA RD | F-1698-q Calls indicate fault at 11kV Pole Dist Sub PE06909 82 Barkla Rd, Wellcamp\r\n\r\nFFA Order F-AE23SW15583-1-0 Completed by technician REDACTED in crew twmoc01(0409997610) with code A-T-306 - HV-Unassisted failure(Apparent defect)\r\nAction Taken : Replace 11kv strain arm broken \r\nSite Label : 3019183 | Calls indicate fault at 11kV Pole Dist Sub PE06909 82 Barkla Rd, Wellcamp\r\ntwmoc01\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23SW15583-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23SW15583-1-0 twmoc01 REDACTED 0409997610\r\nFFA Order En Route F-AE23SW15583-1-0 twmoc01\r\nFFA Order On Site F-AE23SW15583-1-0 twmoc01\r\nAsset selection modified\r\nTime Off modified from 19:08 29-Jul to 20:17 29-Jul\r\nSending Asset Event to FFA\r\nReplay sequence time changed from 29-JUL-23 20:18:54 to 29-Jul-23 21:13:00\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 29-Jul to 23:53 29-Jul\r\nSending Asset Event to FFA\r\nFFA Order F-AE23SW15583-1-0 Completed by technician REDACTED in crew twmoc01(0409997610) with code A-T-306 - HV-Unassisted failure(Apparent defect)\r\nAction Taken : Replace 11kv strain arm broken \r\nSite Label : 3019183\r\nReason for Event changed from Unknown | 1 | 5329976 | 82 Barkla Rd Wellcamp | 1840208 | 3019183 | 5329976 | 2023-07-20 | 9 | N |  |  | 14 | 2 | ? | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Rock | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1982 | -27.5755 | 151.8624 | 000005329976 | 01/JAN/82
EECL | OT190770 | OP | Operational |  | 2023-07-30 | 202307 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1684300 | 2024 | 23NQ9586 | 2023-07-30 19:45 | 2023-07-30 19:45 | COMP | Completed | ? | ? | North Queensland | Forced Outage | ? | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | SZ | ? | GIRU: BRUCE HWY, LINK RD, SARRI RD | Link Rd No.2, isolation point for broken Hv x-arm | Link Rd No.2, isolation point for broken Hv x-arm\r\nTime Off modified from 23:45 30-Jul to 19:45 30-Jul\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23NQ9586-1-0 DfltHost\r\nRemoving Asset Event from FFA\r\nFFA Order cancelled.F-AE23NQ9586-1-0\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23NQ9586-1-1 DfltHost\r\n.\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23NQ9586-1-1 hhlfr01 REDACTED 0427650719\r\nFFA Order En Route F-AE23NQ9586-1-1 hhlfr01\r\nFFA Order On Site F-AE23NQ9586-1-1 hhlfr01\r\nTime On modified from 23:59 30-Jul to 23:15 30-Jul\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order F-AE23NQ9586-1-1 Completed by technician REDACTEDin crew hhlfr01(0427650719) with code A-F-C - Completed\r\nAction Taken : replace broken angled strain x arm.\r\nSite Label : 5060825 | 1 | 2794580 | Bosel rd Giru | 1684300 | 5060825 | 2794580 | 2021-10-07 | 661 | N |  |  | 14 | 2 | ? | Unserviceable - P2 | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 12 kiloNewton | 1980 | -19.5287 | 147.0437 | 000002794580 | 01/JAN/80
EECL | OT190758 | OP | Operational |  | 2023-07-30 | 202307 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | LV |  | ? |  | 1749464 | 2024 | 23NQ9585 | 2023-07-30 18:08 | 2023-07-30 18:07 | COMP | Completed | ? | ? | North Queensland | Forced Outage | ? | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | GT | ? | ROSSLEA: BOWEN RD, CRAFTSMAN ST, LOVE LANE, O'CONNOR ST, SNELHAM ST, WELSH ST | TVS1895 forced outage to replace broken LV x-arm | TVS1895 forced outage to replace broken LV x-arm\r\nTime Off modified from 20:10 30-Jul to 18:08 30-Jul\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23NQ9585-1-0 DfltHost\r\nSending Asset Event to FFA\r\n.\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23NQ9585-1-0 twvoc01 REDACTED 0439478816\r\nFFA Order En Route F-AE23NQ9585-1-0 twvoc01\r\nFFA Order On Site F-AE23NQ9585-1-0 twvoc01\r\nFFA Order F-AE23NQ9585-1-0 Completed by technician REDACTED in crew twvoc01(0439478816) with code A-F-C - Completed\r\nAction Taken : replace broken LV cross arm on pole 5141442.\r\nSite Label : 5141442\r\nTime On modified from 23:59 30-JUL to 19:02 30-JUL | 1 | 3233815 | 78 bowen rd Rosslea | 1749464 | 5141442 | 3233815 | 2020-01-08 | 1299 | N |  |  | 15.5 | 2 | 2 | Unserviceable - P2 | N | Rrl Toff | WOOD (GREEN) SALT IMPREG CCA | Grass | Road | GB GREY BOX | 12 kiloNewton | 1972 | -19.2991 | 146.7993 | 000003233815 | 01/JAN/72
EECL | OT190923 | OP | Operational |  | 2023-08-01 | 202308 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay | ? | LV |  | ? |  | 1210197 | 2024 | 23WB11315 | 2023-08-01 10:40 | 2023-08-01 10:37 | COMP | Completed | ? | ? | Wide Bay | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT | ? | AVOCA: | DENNIS CT, GLENVIEW CRES, KENDALLS RD\r\nBUNDABERG: | Completed\r\nAction Taken : Replace cross arm\r\nSite Label : 2109434 | 1 | 2336315 | 49 glenview crescent avoca | 1210197 | 2109434 | 2336315 | 2020-04-20 | 1198 | N |  |  | 12.5 | ? | 1 | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 5 kiloNewton | 1973 | -24.8913 | 152.3047 | 000002336315 | 01/JAN/73
EECL | OT191165 | OP | Operational |  | 2023-08-03 | 202308 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 33kV |  | ? |  | 1989307 | 2024 | 23SW15776 | 2023-08-03 11:40 | 2023-08-03 16:36 | COMP | Completed | ? | Fine | South West | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT | ? | WILGAVALE | 60 LEES RD | RYWUNG QLD 4413 Fault occurred at:03/08/2023 11:37 REDACTED 0434142640 >UPH --> Details:Broken Cross-arm< Incident Details:Report a broken crossbars is broken, snapped, conductor is hanging by strap. Warnings[uphSafety]: ADVISED Time On modified from 16:30 03-Aug to 10:23 04-Aug | 1 | 2686258 | 8plW at 60 Lees Rd,Cameby | 1989307 | 3257999 | 2686258 | 2020-01-15 | 1296 | N |  |  | 15.5 | 1 | ? | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | RS RED STRINGYBARK | 8 kiloNewton | 1991 | -26.6838 | 150.4455 | 000002686258 | 01/JAN/91
EECL | OT191234 | OP | Operational |  | 2023-08-04 | 202308 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay | ? | LV |  | ? |  | 1109494 | 2024 | 23FN11221 | 2023-08-04 07:46 | 2023-08-04 07:45 | COMP | Completed | ? | ? | Far North | Forced Outage | ? | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FC | ? | GLEN ALLYN: | GERAGHTY RD, HAINES RD\r\nMALANDA: | GERAGHY RD, GLEN ALLYN RD, PEI RD, WALLACE RD F-1769-s ATHE - Peeramon Fdr: 12.7kV SWER Recloser GLS4 Opened for Public Safety due to Low Wires.\r\n 12.7kV SWER Recloser GLS4 5088692\r\nTime On modified from 12:30 04-Aug to 11:15 04-Aug\r\nauto-completed | 1 | 2926170 | 1304 Glen Allyn Rd Malanda | 1109494 | BA3 | 2926170 | 2020-05-27 | 1164 | N |  |  | 11 | ? | 2 | Serviceable | N | LV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | WS WHITE STRINGYBARK | 5 kiloNewton | 1994 | -17.383 | 145.6962 | 000002926170 | 01/JAN/94
EECL | OT191385 | OP | Operational |  | 2023-08-05 | 202308 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1277633 | 2024 | 23NQ9803 | 2023-08-05 16:00 | 2023-08-05 15:54 | COMP | Completed | ? | ? | North Queensland | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC | ? | BASALT, BLUEWATER SPRINGS, BREDDAN, CHARTERS TOWERS, EWAN, FLETCHER CREEK, MINGELA, SELLHEIM, SOUTHERN CROSS, | F-518-t Recloser tripped for Safety. Report of Low Wires down from Annabranch Rd No.1\r\nCrew replaced broken cross-arm. SL 2069604. REDACTED | 22kV Pole Dist Sub SS7883 - LV outage required to replace broken LV arm FC2356774 22kV Pole Dist Sub SS7883 - LV outage required to replace broken LV arm FC2356774\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23FN11349-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23FN11349-1-0 msmfr01 REDACTED 0409645525\r\nFFA Order En Route F-AE23FN11349-1-0 msmfr01\r\nFFA Order On Site F-AE23FN11349-1-0 msmfr01\r\nRestoration Comments for F-AE23FN11349-1-0 by msmfr01: Isolated LV at SS7883 - LV fuses open DNOB attached 0905 hrs 09/08/23\r\nFFA Order F-AE23FN11349-1-0 Completed by technician REDACTED in crew msmfr01(0409645525) with code A-F-C - Completed\r\nAction Taken : isolated LV SS7883 ,replaced Xarm ,restored supply carrried out test at customers switchboard to confirm safe , fault loop 0.45 ohms at 246 volts, 0.47 ohms at 244 volts, 0.47 ohms at 245 volts, neutral bar to independent earth 0.2 volts, tong test main neutral 2.4 amps - 0 amps in main earth conductor - not a reportable incident \r\nSite Label : 5033540\r\nTime On modified from 13:00 09-AUG to 11:10 09-AUG | 1 | 2208249 | Annabranch rd Annakin Park stn CT | 1277633 | 2069604 | 2208249 | 2022-03-17 | 506 | N |  |  | 14 | 2 | ? | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | GM GYMPIE MESSMATE | 12 kiloNewton | 1990 | -19.9129 | 146.2744 | 000002208249 | 01/JAN/90
EECL | OT191738 | OP | Operational |  | 2023-08-09 | 202308 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay | ? | LV |  | ? |  | 1139435 | 2024 | 23FN11349 | 2023-08-09 08:08 | 2023-08-09 09:06 | COMP | Completed | ? | ? | Far North | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT | ? | WHYANBEEL: | SCIACCA RD | Crew requires access to 22kV Pole Dist Sub 453697 LV only. Broken LV cross arm. Crew requires access to 22kV Pole Dist Sub 453697 LV only. Broken LV cross arm.\r\nDepot adv lgrcs03.\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23CA12143-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23CA12143-1-0 lgrcs03 REDACTED 0428781123\r\nFFA Order En Route F-AE23CA12143-1-0 lgrcs03\r\nSending Asset Event to FFA\r\nFFA Order On Site F-AE23CA12143-1-0 lgrcs03\r\nFFA Order F-AE23CA12143-1-0 Completed by technician REDACTED in crew lgrcs03(0428781123) with code A-F-C - Completed\r\nAction Taken : replace p1 lv x-arm\r\nSite Label : 4028174\r\nTime On modified from 23:59 11-AUG to 10:26 11-AUG | 1 | 2640218 | 49 Sciacci Rd off Mossman Daintree Rd | 1139435 | SC7 | 2640218 | 2019-09-11 | 1428 | N |  |  | 11 | ? | 1 | Serviceable | Y | Urb sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Backyard | BI BROAD LEAF IRONBARK | 5 kiloNewton | 2003 | -16.397 | 145.3908 | 000002640218 | 01/JAN/03
EECL | OT191975 | OP | Operational |  | 2023-08-11 | 202308 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay | ? | LV |  | ? |  | 1410998 | 2024 | 23CA12143 | 2023-08-11 08:20 | 2023-08-11 08:13 | COMP | Completed | ? | ? | Capricornia | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT | ? | LONGREACH: | GREBE ST, LARK ST, RAVEN RD, STILT ST | 22kV Pole Dist Sub SS10456, crew advise of broken LV x-arm 22kV Pole Dist Sub SS10456, crew advise of broken LV x-arm\r\nTime On modified from 23:59 12-Aug to 13:30 12-Aug\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23FN11499-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23FN11499-1-0 insoc01 REDACTED 0437899019\r\nFFA Order En Route F-AE23FN11499-1-0 insoc01\r\nFFA Order On Site F-AE23FN11499-1-0 insoc01\r\nFFA Order F-AE23FN11499-1-0 Completed by technician REDACTED in crew insoc01(0437899019) with code A-T-311 - LV-Unassisted failure(Apparent defect)\r\nAction Taken : replace lv arm\r\nSite Label : 5026650\r\nTime On modified from 13:30 12-AUG to 12:33 12-AUG | 1 | 2558735 | near 8 grebe st longreach | 1410998 | 4028174 | 2558735 | 2020-02-13 | 1275 | N |  |  | 9.5 | ? | 1 | Serviceable | Y | Urb LV inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1986 | -23.4471 | 144.2595 | 000002558735 | 01/JAN/86
EECL | OT192082 | OP | Operational |  | 2023-08-12 | 202308 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay | ? | LV |  | ? |  | 826646 | 2024 | 23FN11499 | 2023-08-12 10:02 | 2023-08-12 11:21 | COMP | Completed | ? | Wet / Rain | Far North | Unplanned Outage | LV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | GT | ? | HARVEYS CREEK: | HARVEY CREEK RD | F-17245-q - 11kV Pole Dist Sub PE01502, crews require access to replace transformer F-17245-q - 11kV Pole Dist Sub PE01502, crews require access to replace transformer\r\nWires hanging low\r\nLV Wires Down\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23SW16045-1-0 DfltHost\r\nwaroc01\r\nSending Asset Event to FFA\r\nTime Off modified from 06:47 13-Aug to 08:29 13-Aug\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 13-Aug to 14:11 13-Aug\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23SW16045-1-0 waroc01 REDACTED 0431073082\r\nFFA Order En Route F-AE23SW16045-1-0 waroc01\r\nFFA Order On Site F-AE23SW16045-1-0 waroc01\r\nSending Asset Event to FFA\r\nFFA Order F-AE23SW16045-1-0 Completed by technician REDACTED in crew waroc01(0431073082) with code A-T-311 - LV-Unassisted failure(Apparent defect)\r\nAction Taken : Replaced broken LV twin cross arms which failed causing oil leak on 63KV TX which was reapplied as well. Upgraded switch arm due to age.\r\nSite Label : 3076507 | 1 | 2597026 | 30 harvey cr rd bellender ker | 826646 | GB283 | 2597026 | 2022-05-31 | 438 | N |  |  | 14 | 1 | 2 | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 2003 | -17.2702 | 145.9222 | 000002597026 | 01/JAN/03
EECL | OT192164 | OP | Operational |  | 2023-08-13 | 202308 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 22kV |  | ? |  | 1587914 | 2024 | 23CA12204 | 2023-08-13 15:07 | 2023-08-13 14:23 | COMP | Completed | ? | ? | Capricornia | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ | ? | CLERMONT | F-1726-q\r\n22kV Air Break S3429 - Crew require Forced Outage to repair broken 22kV x-arm on Pole 4150965, between TX 338248 & Bathhampton T-off S8747 | THARGOMINDAH-HUNGERFORD RD\r\nTHARGOMINDAH: HUNGERFORD RD, THARGOMINDAH-HUNGERFORD RD, WERENILKE RD |  | 3237722 | 21spn NW x8432 Leo Flat Rd Clermont | 1587914 | 4150965 | 3237722 | 2022-12-09 | 247 |  |  |  | 12.5 | 1 | ? | Serviceable | N | Rrl inter spn >200m | WOOD UNTREATED DRESSED | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 3 kiloNewton | ? | -22.7573 | 147.5805 | 000003237722 | 01/JAN/54
EECL | OT192133 | OP | Operational |  | 2023-08-13 | 202308 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay | ? | LV |  | ? |  | 1616502 | 2024 | 23SW16045 | 2023-08-13 08:29 | 2023-08-13 08:00 | COMP | Completed | ? | Fine | South West | Unplanned Outage | HV-Conductor Connection Failure | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC | ? | JUNABEE: | JUNABEE RD, ROONA RD | BRUCE HWY Fault Job F-1820-s\r\n22kV Pole Dist Sub SS614 - REDACTED reported broken cross arm on LV. Crews require access to LV to repair cross arm | 1 | 2878930 | PExxx2,Junabee Rd,Junabee | 1616502 | 3076507 | 2878930 | 2018-10-25 | 1753 | ? |  |  | 12.5 | 2 | 2 | Serviceable | Y | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1964 | -28.236 | 152.0961 | 000002878930 | 01/JAN/64
EECL | OT192531 | OP | Operational |  | 2023-08-17 | 202308 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay | ? | 11kV |  | ? |  | 1570087 | 2024 | 23SW16162 | 2023-08-17 09:30 | 2023-08-17 09:34 | COMP | Completed | ? | ? | South West | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ | ? | FREESTONE, MOUNT STURT, SWAN CREEK, UPPER FREESTONE, YANGAN | F-817-r - 11kV Recloser CB4415 - Crew Require Acces doiwnstream for Broken Crossarm Repairs | F-1760-q 11kV Dropout Fuse X711016 isolation for broken X/arm\r\n 11kV Dropout Fuse X711016 isolation for broken X/arm\r\nTime Off modified from 19:00 27-Aug to 19:41 27-Aug\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23CA12649-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23CA12649-1-0 ccoc02 REDACTED 0455474160\r\nFFA Order En Route F-AE23CA12649-1-0 ccoc02\r\nFFA Order On Site F-AE23CA12649-1-0 ccoc02\r\nSending Asset Event to FFA\r\nFFA Order F-AE23CA12649-1-0 Completed by technician REDACTED in crew ccoc02(0455474160) with code A-F-C - Completed\r\nAction Taken : replaced single phase 11kv xarm that had broken\r\nSite Label : 4014854\r\nTime On modified from 22:00 27-Aug to 21:39 27-Aug | 1 | 2875807 | 2 N PE9-53 42 wiedmans rd yangan | 1570087 | 3075818 | 2875807 | 2020-03-18 | 1247 | N |  |  | 12.5 | 1 | ? | Serviceable | N | Rrl sty angle 5-20o | WOOD UNTREATED ROUND | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1968 | -28.1803 | 152.1569 | 000002875807 | 01/JAN/68
EECL | OT192898 | OP | Operational |  | 2023-08-21 | 202308 | Crossarm | Xarm, Wood Intermediate | Broken | Termites | ? | 19kV |  | ? |  | 1157155 | 2024 | 23SW16272 | 2023-08-21 09:54 | 2023-08-21 10:02 | COMP | Completed | ? | ? | South West | Forced Outage | ? | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | SZ | ? | CUNNAMULLA: | BULLOO DEVELOPMENTAL RD, WOMBULA-YENLORA RD\r\nHUNGERFORD: | THARGOMINDAH-HUNGERFORD RD\r\nTHARGOMINDAH: HUNGERFORD RD, THARGOMINDAH-HUNGERFORD RD, WERENILKE RD F-1742-q - Wongetta SWER - Forced outage required beyond Wongetta SWER ACR RC873559\r\nAssociated with fault call 2359019 repoerts of lines down WGL request trip for public safety\r\nCrew ETA 2.5hrs. Forced outage required beyond Wongetta SWER ACR RC873559\r\nAssociated with fault call 2359019 repoerts of lines down WGL request trip for public safety\r\nCrew ETA 2.5hrs.\r\nACR tripped for safety 0954\r\nTime Off modified from 10:30 21-Aug to 09:54 21-Aug\r\nF-1742-q\r\nTime On modified from 23:59 21-Aug to 15:10 21-Aug | 1 | 2218885 | pw5040-dl4338 thargo hungerford rd tharg | 1157155 | 3186308 | 2218885 | 2020-10-31 | 1024 | N |  |  | 12.5 | 1 | ? | Serviceable | N | Duplex SWER | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | ? | -28.2005 | 143.8258 | 000002218885 | 01/JAN/90
EECL | OT193042 | OP | Operational |  | 2023-08-22 | 202308 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay | ? | LV |  | ? |  | 1297231 | 2024 | 23FN11797 | 2023-08-22 09:18 | 2023-08-22 09:18 | COMP | Completed | ? | ? | Far North | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT | ? | DALLACHY CREEK: | NASH RD\r\nKENNEDY: | BRUCE HWY Fault Job F-1820-s\r\n22kV Pole Dist Sub SS614 - REDACTED reported broken cross arm on LV. Crews require access to LV to repair cross arm 22kV Pole Dist Sub SS614 - REDACTED reported broken cross arm on LV. Crews require access to LV to repair cross arm\r\nTime Off modified from 10:00 22-Aug to 09:18 22-Aug\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23FN11797-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23FN11797-1-0 tlycs03 REDACTED 0427627604\r\nFFA Order En Route F-AE23FN11797-1-0 tlycs03\r\nFFA Order On Site F-AE23FN11797-1-0 tlycs03\r\nFault Job F-1820-s\r\nSending Asset Event to FFA\r\nFFA Order F-AE23FN11797-1-0 Completed by technician REDACTED in crew tlycs03(0427627604) with code A-F-C - Completed\r\nAction Taken : Replaced Lv termination crossarm \r\nSite Label : 5045015\r\nTime On modified from 23:59 22-AUG to 11:49 22-AUG | 1 | 2703090 | Cnr Nash Rd /Bruce Hwy Bilanya | 1297231 | C251 | 2703090 | 2022-07-14 | 404 | N |  |  | 12.5 | 3 | 2 | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1991 | -18.1628 | 145.9316 | 000002703090 | 01/JAN/91
EECL | OT193242 | OP | Operational |  | 2023-08-24 | 202308 | Crossarm | Xarm, Wood Strain | Deteriorated | Rot/Decay | ? | 22kV |  | ? |  | 1225120 | 2024 | 23FN11885 | 2023-08-24 11:42 | 2023-08-24 09:40 | COMP | Completed | ? | ? | Far North | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ | ? | YARRABAH | F-554-t 22kV Recloser Pole PR183 - Emergency repairs, crews found broken xarm\r\nCrew replaced double HV strain cross-arms. SL 5034668. REDACTED \r\n | 22kV Recloser Pole PR183 - Emergency repairs, crews found broken xarm\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23FN11885-1-0 DfltHost\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23FN11885-1-0 cnscm04 REDACTED 0407331287\r\nFFA Order En Route F-AE23FN11885-1-0 cnscm04\r\nFFA Order On Site F-AE23FN11885-1-0 cnscm04\r\nTime Off modified from 10:31 24-Aug to 11:42 24-Aug\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 24-Aug to 13:47 24-Aug\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order F-AE23FN11885-1-0 Completed by technician REDACTED in crew cnscm04(0407331287 ) with code A-F-C - Completed\r\nAction Taken : Double HV Strain Xarms replaced\r\nSite Label : 5034668\r\nAdded notes to Reasons tab. | 1 | 2647206 | opp 2457 second beach yarrabah rd | 1225120 | PR195 | 2647206 | 2022-11-03 | 294 | N |  |  | 14 | 2 | 1 | Serviceable | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Rock | Road Reserve | WS WHITE STRINGYBARK | 8 kiloNewton | 1965 | -16.8895 | 145.8281 | 000002647206 | 01/JAN/65
EECL | OT193559 | OP | Operational |  | 2023-08-27 | 202308 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 11kV |  | ? |  | 931802 | 2024 | 23CA12649 | 2023-08-27 19:41 | 2023-08-27 18:07 | COMP | Completed | ? | ? | Capricornia | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ | ? | BOULDERCOMBE: | AREMBY RD | F-1760-q 11kV Dropout Fuse X711016 isolation for broken X/arm\r\n 11kV Dropout Fuse X711016 isolation for broken X/arm\r\nTime Off modified from 19:00 27-Aug to 19:41 27-Aug\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23CA12649-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23CA12649-1-0 ccoc02 REDACTED 0455474160\r\nFFA Order En Route F-AE23CA12649-1-0 ccoc02\r\nFFA Order On Site F-AE23CA12649-1-0 ccoc02\r\nSending Asset Event to FFA\r\nFFA Order F-AE23CA12649-1-0 Completed by technician REDACTED in crew ccoc02(0455474160) with code A-F-C - Completed\r\nAction Taken : replaced single phase 11kv xarm that had broken\r\nSite Label : 4014854\r\nTime On modified from 22:00 27-Aug to 21:39 27-Aug | 1 | 2477012 | acc via RM 482 Aremby Rd Bouldercombe | 931802 | 4014854 | 2477012 | 2021-07-10 | 778 | N |  |  | 11 | 1 | ? | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | NI NARROW LEAF RED I | 5 kiloNewton | 1984 | -23.571 | 150.5082 | 000002477012 | 01/JAN/84
EECL | OT194149 | OP | Operational |  | 2023-09-01 | 202309 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 11kV |  | ? |  | 928937 | 2024 | 23CA12883 | 0:32 | 0:25 | COMP | Completed | ? | ? | Capricornia | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE | ? | BANCROFT, KALPOWAR, MONTO, MUNGUNGO | Broken cross arm past X17776 on Kalpower fdr , Monto.\r\n\r\nWork on Goody Rd, Via Monto\r\n\r\nforced outage to replace X arm | HV Wires Down\r\nAsset selection reset\r\nAsset selection modified\r\nSwitching Sheet ID updated from to J-274807-g.\r\nTime Off modified from 12:30 01-Sep to 13:30 01-Sep\r\nTime Off modified from 13:30 01-Sep to 13:32 01-Sep\r\nTime On modified from 16:00 01-Sep to 14:48 01-Sep | 1 | 3194367 | acc 588 Goodys Rd Monto-1SW SP239307 | 928937 | 4140324 | 3194367 | 2019-07-20 | 1504 | N |  |  | 11 | 1 | ? | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton | ? | -24.6748 | 151.1861 | 000003194367 | 01/JAN/69
EECL | OT194485 | OP | Operational |  | 2023-09-05 | 202309 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | LV |  | ? |  | 1799511 | 2024 | 23NQ10858 | 0:35 | 0:35 | COMP | Completed | ? | ? | North Queensland | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT | ? | HEATLEY: ADAMS ST, FULHAM RD, RHODES ST, RYDER CT | 11kV Pole Dist Sub TVS2499 crew require outage to complete emergency repairs to broken LV crossarm. F/C 2361705.\r\nCrew replaced broken LV angle arm. SL 5039960. REDACTED | 11kV Pole Dist Sub TVS2499 crew require outage to complete emergency repairs to broken LV crossarm. F/C 2361705\r\nTime Off modified from 11:52 05-Sep to 09:35 05-Sep\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23NQ10858-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23NQ10858-1-0 twvfr04 REDACTED 0409137912\r\nFFA Order En Route F-AE23NQ10858-1-0 twvfr04\r\nFFA Order On Site F-AE23NQ10858-1-0 twvfr04\r\nFFA Order En Route F-AE23NQ10858-1-0 twvfr04\r\nFFA Order On Site F-AE23NQ10858-1-0 twvfr04\r\nFFA Order F-AE23NQ10858-1-0 Completed by technician REDACTED in crew twvfr04(0409137912) with code A-F-C - Completed\r\nAction Taken : Replaced Broken LV Angle arm.\r\nSite Label : 5039960\r\nTime On modified from 23:59 05-SEP to 13:08 05-SEP\r\nAdded notes to Reasons tab. | 1 | 2675883 | cnr ADAMS ST + fulham rd heatly | 1799511 |  | 5039960 | 2009-08-22 | 5127 |  |  |  | ? | 12.5 | 1 | Serviceable | Y | Urb unsty angle | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | RW RED BLOODWOOD | 8 kiloNewton |  | -19.2886 | 146.7515 | 000002675883 | 01/JAN/70
EECL | OT195132 | OP | Operational |  | 2023-09-10 | 202309 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay | ? | 66kV |  | ? |  | 942352 | 2024 | 23NQ11060 | 0:36 | 0:26 | ANAL | Data verification | ? | ? | North Queensland | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | ZS | ? | BEMERSIDE, CARDWELL RANGE, CORDELIA, FORREST HOME, HALIFAX, LUCINDA, MACKNADE, TAYLORS BEACH, VICTORIA ESTATE | Crews Advised 66kV Disc Insulators dropped from S/L 5077487 and hanging Low.Crews onsite. REDACTED 0439 112 473 Onsite Reported to OCCN by REDACTED 0437 760 945 | Crews Advised 66kV Disc Insulators dropped from S/L 5077487 and hanging Low.Crews onsite. REDACTED 0439 112 473 Onsite Reported to OCCN by REDACTED 0437 760 945\r\REDACTED 0473 145 674 ingcsfr01 attending\r\nDepot Co-ord Advised\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23NQ11060-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23NQ11060-1-0 ingcsfr01\r\REDACTED advised drop 66kV kV Network without performing load Transfers to reduce time to repair\r\nSending Asset Event to FFA\r\nREDACTEDwill be point of contact for work and second switching crew will be REDACTED \r\nSending Asset Event to FFA\r\nAR disabled @ 1019\r\nSending Asset Event to FFA\r\nFFA Order En Route F-AE23NQ11060-1-0 ingcsfr01\r\nFFA Order On Site F-AE23NQ11060-1-0 ingcsfr01\r\nSending Asset Event to FFA\r\nTime Off modified from 10:40 10-Sep to 12:36 10-Sep\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 10-Sep to 14:00 10-Sep\r\nSending Asset Event to FFA\r\nUnder access for repairs\r\nSending Asset Event to FFA\r\nFFA Order Pending F-AE23NQ11060-1-0\r\nTime On modified from 14:00 10-Sep to 14:45 10-Sep\r\nSending Asset Event to FFA\r\nClosed B152 Restoring Supply with exception of Vict EA04Q00 and MACN FB0252\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nClosed MACN FB0252 to Mill\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nClosed VICT EA04Q00 all supply restored\r\nTime On modified from 14:45 10-Sep to 14:34 10-Sep\r\nSending Asset Event to FFA\r\nHV Wires Down\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23NQ11060-1-0 mckmb02 REDACTED 0437760945\r\nFFA Order En Route F-AE23NQ11060-1-0 mckmb02\r\nFFA Order On Site F-AE23NQ11060-1-0 mckmb02\r\nFFA Order F-AE23NQ11060-1-0 Completed by technician REDACTED in crew mckmb02(0437760945) with code A-F-C - Completed\r\nAction Taken : New Composite Wishbone Crossarm installed\nNew Insulators and Hardware Installed \r\nSite Label : 5077487 | 1 | 2881793 | 8 Est of Ingham Zsub Ingham | 942352 | 5077487 | 2881793 | 2023-04-29 | 134 | N |  |  | 15.5 | 1 | ? | Serviceable | N | 66kV rrl inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | SG SPOTTED GUM | 8 kiloNewton | 1975 | -18.6658 | 146.1606 | 000002881793 | 01/JAN/75
EECL | OT195838 | OP | Operational |  | 2023-09-16 | 202309 | Crossarm | Xarm, Steel Termination | Broken | Corrosion | ? | LV |  | ? |  | 944543 | 2024 | 23NQ11267 | 0:25 | 0:45 | COMP | Completed | ? | Fine | North Queensland | Unplanned Outage | Animal Insects (termites/borers/white ants) | Brown Out | there are supply problems resulting in low voltage conditions. It is advisable to disconnect sensitive electrical appliances. | GT | ? | COLLINSVILLE: CONWAY ST, DAVIDSON ST, GRALTON ST, ISBELL CT, ISBELL ST, MURPHY ST, PELICAN CREEK RD, STATION HILL, STATION ST | 33kV Pole Dist Sub CVS94 (6 Isbell Street), multiple calls reporting fuse down at this location. | 33kV Pole Dist Sub CVS94 (6 Isbell Street), multiple calls reporting fuse down at this location.\r\nIssued to REDACTED 0428 766 675, clcoh01.\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23NQ11267-1-0 DfltHost\r\nAsset selection reset\r\nCrew advise broken LV termination cross arm at the intersection of Station Street and Murphy Street.\r\nAsset selection modified\r\nTime Off modified from 15:36 16-Sep to 15:25 16-Sep\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23NQ11267-1-0 clvoh01 Chappo 0428766675\r\nFFA Order En Route F-AE23NQ11267-1-0 clvoh01\r\nFFA Order On Site F-AE23NQ11267-1-0 clvoh01\r\nFFA Order F-AE23NQ11267-1-0 Completed by technician REDACTED in crew CLVOH01(0428766675) with code A-T-299 - Animal Insects (termites/borers/white ants)\r\nAction Taken : broken lv term arm\r\nSite Label : 2154669\r\nTime On modified from 23:59 16-SEP to 18:15 16-SEP | 1 | 2409849 | cnr murphy&Station sts collinsville | 944543 |  | 2154670 |  |  | ? |  |  | ? | 11 | ? | [5 empty] | Footpath | SG SPOTTED GUM | 5 kiloNewton |  | -20.5524 | 147.8514 | 000009372677
EECL | OT195821 | OP | Operational |  | 2023-09-16 | 202309 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1532627 | 2024 | 23SW17354 | 0:05 | 0:37 | COMP | Completed | ? | ? | South West | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ | ? | HIGHFIELDS: BARBER RD, BRADYS RD, JAMES BYRNE RD, RECREATION RESERVE RD | Crew require access past 11kV Dropout Fuse MDO19568 to repair broken crossarm at Pole 3089501 (near tx PE05176) | Crew require access past 11kV Dropout Fuse MDO19568 to repair broken crossarm at Pole 3089501 (near tx PE05176)\r\ntwmoc01\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23SW17354-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23SW17354-1-0 twmoc01 REDACTED 0409105958\r\nFFA Order En Route F-AE23SW17354-1-0 twmoc01\r\nFFA Order On Site F-AE23SW17354-1-0 twmoc01\r\nTime On modified from 14:00 16-Sep to 15:00 16-Sep\r\nSending Asset Event to FFA\r\nFFA Order En Route F-AE23SW17354-1-0 twmoc01\r\nFFA Order On Site F-AE23SW17354-1-0 twmoc01\r\nTime On modified from 15:00 16-Sep to 14:55 16-Sep\r\nSending Asset Event to FFA\r\nTime Off modified from 12:00 16-Sep to 13:05 16-Sep\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order F-AE23SW17354-1-0 Completed by technician REDACTED in crew twmoc01(0409105958) with code A-F-C - Completed\r\nAction Taken : isolated and earthed line and replaced broken strain arm \r\nSite Label : 3089502 | 1 | 2932383 | 35 recreation Reserve Rd Highfields | 1532627 |  | 3089502 | 2024-03-04 | -170 | ? |  |  | ? | 12.5 | 1 | Serviceable | N | Rrl inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | SG SPOTTED GUM | 5 kiloNewton |  | -27.484 | 151.9489 | 000002932383 | 01/JAN/75
EECL | OT195897 | OP | Operational |  | 2023-09-17 | 202309 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1779197 | 2024 | 23NQ11276 | 0:58 | 0:18 | COMP | Completed | ? | ? | North Queensland | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE | ? | RASMUSSEN: RIVERWAY DR | F-1952-s - Emergency Maint broken crossarm on pole 5136644\r\n | Emergency Maint broken crossarm on pole 5136644\r\nTime Off modified from 19:30 17-Sep to 20:57 17-Sep\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23NQ11276-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23NQ11276-1-0 twvoc01 REDACTED 0439478816\r\nFFA Order En Route F-AE23NQ11276-1-0 twvoc01\r\nFFA Order On Site F-AE23NQ11276-1-0 twvoc01\r\nTime On modified from 23:59 17-Sep to 23:59 18-Sep\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 18-Sep to 01:15 18-Sep\r\nSending Asset Event to FFA\r\nFFA Order F-AE23NQ11276-1-0 Completed by technician REDACTED in crew twvoc01(0439478816) with code A-F-C - Completed\r\nAction Taken : replace broken double strain cross arm on pole 5136644.\r\nSite Label : 5136644\r\nActual Power Restoration for F-AE23NQ11276-1-0: 18-SEP-2023 02:13:00 | 1 | 3216734 | opposite 1003 riverway drive rasmussen | 1779197 |  | 5136644 | 2023-05-27 | 113 | ? |  |  | ? | 15.5 | 1 | Serviceable | Y | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | GI GREY IRONBARK | 20 kiloNewton |  | -19.3426 | 146.7285 | 000003216734 | 01/JAN/97
EECL | OT196177 | OP | Operational |  | 2023-09-20 | 202309 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay | ? | LV |  | ? |  | 5451127 | 2024 | 23NQ11411 | 0:14 | 0:08 | COMP | Completed | ? | Fine | North Queensland | Unplanned Outage | LV-Conductor Connection Failure | Unknown | Single Fault Call | GT | ? | BOOTOOLOO RD BOWEN QLD 4805 | Fault occurred at:20/09/2023 08:58 | REDACTED, 0408407733. >WIRESDOWN-PP --> AffectingTraffic:NO -- StillHavePower:UNSURE< Incident Details:Wires down in the middle of the farm. Farm called Rugby or Morgan farm. Powerline running behind Don River in Bowen, Pole number 2094428. Wire 8 ft above the ground. Access Details:On the Bootooloo side on Rugby Farm Warnings[WiresDownSafety]: ADVISED\r\n\r\nP1 Call Flag | 1 |  | Access Whites Lane Bowen | 5451127 | 2085855 | 8701091 | 2022-02-22 | 575 |  |  |  | ? | 11 | ? | Serviceable | N | Rrl unsty ang 5-20o | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton |  | -20.067 | 148.1876 | 000002265362 | 01/JAN/77
EECL | OT196349 | OP | Operational |  | 2023-09-21 | 202309 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay | ? | 11kV |  | ? |  | 1465074 | 2024 | 23SW17550 | 0:10 | 0:20 | COMP | Completed | ? | Hot | South West | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC | ? | DALBY, KAIMKILLENBUN, MACLAGAN, MOOLA, RANGEMORE, YAMSION, | F-1858-q 11kV Recloser CB2293 tripped on OC\r\nCrew replaced rotten cross-arm. SL 6044504. REDACTED | 11kV Recloser CB2293 tripped on OC\r\nAsset selection reset\r\nAsset selection modified\r\nMRC unsuccessful after speaking with REDACTED. Crew ETA approx 1 hr from site as they are on other jobs\r\nDepot Co-ord Advised\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23SW17550-1-0 DfltHost\r\nCrew will be heading to sectionalise at temp links SL3105466 when they do arrive on site\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nManual Reclose Checklist\r\nSending Asset Event to FFA\r\n11kV Air Break AB2445 - OPEN\r\n11kV Recloser CB2293 - CLOSE @ 1632hrs.\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23SW17550-1-0 dlbfrl02 REDACTED 0437799747\r\nFFA Order En Route F-AE23SW17550-1-0 dlbfrl02\r\nFFA Order On Site F-AE23SW17550-1-0 dlbfrl02\r\nTime On modified from 23:59 21-Sep to 19:27 21-Sep\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order F-AE23SW17550-1-0 Completed by technician REDACTED in crew dlbfrl02(0437799747) with code A-T-30 - Vibration\r\nAction Taken : replace rotten arm\r\nSite Label : 6044504\r\nReason for Event changed from Unknown\r\nUpdated Reasons tab. Updated Event Trigger from SUBT-Unassisted failure to HV-Unassisted faiure. | 1 | 2318434 | 1plE 3488 Dalby/Cooyar Rd,Moola | 1465074 | 6044504 | 2318434 | 2019-12-04 | 1387 |  |  |  | 12.5 | 3 | ? | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1983 | -27.0873 | 151.5616 | 000002318434 | 01/JAN/83
EECL | OT196894 | OP | Operational |  | 2023-09-26 | 202309 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay | ? | 22kV |  | ? |  | 920878 | 2024 | 23CA13785 | 0:57 | 0:07 | COMP | Completed | ? | ? | Capricornia | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC | ? | THEODORE: ISLA-DELUSION RD | 22kV Disc Links DL819480 (X7720) - Crew Require Access Downstream of Links to Repair Broken Crossarm | 22kV Disc Links DL819480 (X7720) - Crew Require Access Downstream of Links to Repair Broken Crossarm\r\nCrew Confirmed DL819480 is actually X7720 which matched PON, Data discrepenancy form done.\r\nSwitching Sheet ID updated from to J-278400-g.\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23CA13785-1-0 DfltHost\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nTime Off modified from 12:00 27-Sep to 13:57 27-Sep\r\nSending Asset Event to FFA\r\nTime On modified from 18:00 27-Sep to 15:34 27-Sep\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23CA13785-1-0 morfr03 REDACTED 0438340683\r\nFFA Order En Route F-AE23CA13785-1-0 morfr03\r\nFFA Order On Site F-AE23CA13785-1-0 morfr03\r\nFFA Order F-AE23CA13785-1-0 Completed by technician REDACTED in crew morfr03(0438340683) with code A-F-C - Completed\r\nAction Taken : replaced arm with new fibreglass arm\r\nSite Label : 4151816 | 1 | 3239773 | 231 Isla Delusion Rd Theodore | 920878 |  | 4151816 | 2023-09-26 | 0 | ? |  |  | ? | 12.5 | 2 | Serviceable | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton |  | -25.1421 | 150.0598 | 000003239773 | 01/JAN/80
EECL | OT196909 | OP | Operational |  | 2023-09-26 | 202309 | Crossarm | Xarm, Wood Strain | Split | Vibration | ? | 11kV |  | ? |  | 980103 | 2024 | 23WB12955 | 0:51 | 0:30 | COMP | Completed | ? | ? | Wide Bay | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC | ? | GUNDIAH: EMERYS BRIDGE RD, JESSENS RD, LAMKES RD, THOMPSONS RD\r\nMOUNT URAH: THOMPSONS RD\r\nNETHERBY: DEBORAH RD\r\nST MARY: BAUPLEVIEW RD, FLINDERSIA RD, GLENBAR RD\r\nTIARO: GLENBAR RD | F-919-r - 11kV Disc Links S3196 - Crew Require Access to Repair Broken Crossarm\r\n | 11kV Disc Links S3196 - Crew Require Access to Repair Broken Crossarm\r\nF-919-r\r\nMRBCS02\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23WB12955-1-0 DfltHost\r\nSending Asset Event to FFA\r\nTime Off modified from 14:00 26-Sep to 14:51 26-Sep\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23WB12955-1-0 mrbcs02 REDACTED 0437583809\r\nFFA Order En Route F-AE23WB12955-1-0 mrbcs02\r\nFFA Order On Site F-AE23WB12955-1-0 mrbcs02\r\nAsset selection modified\r\nTime On modified from 18:00 26-Sep to 17:59 26-Sep\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order F-AE23WB12955-1-0 Completed by technician REDACTED in crew mrbcs02(0437583809) with code A-F-C - Completed\r\nAction Taken : replaced x arm\r\nSite Label : 2125980\r\nActual Power Restoration for F-AE23WB12955-1-0: 26-SEP-2023 18:15:00 | 1 |  |  | 980103 |  |  | 2023-09-27 | -1 |  |  |  | ######## | ######## | N | Serviceable | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | GB GREY BOX | 8 kiloNewton |  | -25.7995 | 152.489 | 000002380919 | 01/JAN/79
EECL | OT196898 | OP | Operational |  | 2023-09-26 | 202309 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1449086 | 2024 | 23MK7766 | 0:27 | 0:50 | COMP | Completed | ? | Fine | Mackay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ | ? | KUTTABUL: | MOUNT MARTIN RD\r\nMOUNT MARTIN: BRADSHAWS RD, MCFAULS RD, MOUNT MARTIN LOOP RD, MOUNT MARTIN RD, MOUNT TOBY RD, SUGARLOAF RD | 11kV Dropout Fuse FLKS610568, multiple calls of TLOS from beyond these fuses.\r\nHV term arm had failed at SL 4087547. Red wood arm snapped in centre on king bolt, no rot. Repairs made as required. REDACTED 11kV Dropout Fuse FLKS610568, multiple calls of TLOS from beyond these fuses.\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23MK7766-1-0 DfltHost\r\nCrew adv Broken Crossarn on Sub 541681 Req Access to Make Repairs\r\nSending Asset Event to FFA\r\nReason for Event changed from Unknown\r\nSending Asset Event to FFA\r\nManual Reclose Checklist\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order Acknowledged F-AE23MK7766-1-0 pncoc01 REDACTED 0408566761\r\nFFA Order En Route F-AE23MK7766-1-0 pncoc01\r\nFFA Order On Site F-AE23MK7766-1-0 pncoc01\r\nFFA Order F-AE23MK7766-1-0 Completed by technician REDACTED in crew pncoc01(0408566761) with code A-T-306 - HV-Unassisted failure(Apparent defect)\r\nAction Taken : HV TERM ARM HAS FAILED AT 4087547. RED WOOD ARM HAS SNAPPED IN CENTRE ON KINGBOLT. NO ROT ARM IS SOLID AND HEAVY\n\nHV STAYED ABOVE STAT HEIGHT CONDUCTORS WERE HELD ON BY BRIDGING\r\nSite Label : 4087547\r\nTime On modified from 23:59 26-Sep to 18:10 26-Sep\r\nPrimary Asset de-escalated from Langdon Recloser (FC)\r\nDe-escalated Primary Asset selection from Langdon Recloser (FC) to impacted 11kV Dropout Fuse FLKS610568.\r\nAdded notes to Reasons tab. | 1 | 2897883 | Tx781 81 McFauls rd Mirani | 2897883 |  |  | 2024-06-22 | -270 |  |  |  | N |  | ? | Serviceable | Y | Rrl sty sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | WOOD (GREEN) SALT IMPREG CCA | 5 kiloNewton |  | -21.0839 | 148.8067 | 000002897883 | 01/JAN/83
EECL | OT197050 | OP | Operational |  | 2023-09-27 | 202309 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1270969 | 2024 | 23SW17734 | 0:25 | 0:46 | COMP | Completed | ? | ? | South West | Forced Outage | ? | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ | ? | HIGHGROVE: DOWLING'S RD, KINGS HILL RD | 11kV Disc Links DL7584 required to isolate to replace broken cross arm access to TX PE06137 also req | 11kV Disc Links DL7584 required to isolate to replace broken cross arm\r\nSwitching Sheet ID updated from to J-278658-g.\r\ntwmoc03\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23SW17734-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23SW17734-1-0 twmoc03 REDACTED 0428879985\r\nFFA Order En Route F-AE23SW17734-1-0 twmoc03\r\nTime Off modified from 16:00 27-Sep to 18:25 27-Sep\r\nSending Asset Event to FFA\r\nTime On modified from 23:59 27-Sep to 22:36 27-Sep\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nFFA Order On Site F-AE23SW17734-1-0 twmoc03\r\nFFA Order F-AE23SW17734-1-0 Completed by technician REDACTED in crew twmoc03(0428879985) with code A-F-C - Completed\r\nAction Taken : replace broken x arm\r\nSite Label : 3146125 | 1 | 3222483 | PE6137 196 dowling rd highgrove | 1270969 |  | 3146125 | 2023-05-31 | 119 | ? |  |  | ? | 14 | 3 | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Backyard | SG SPOTTED GUM | 5 kiloNewton |  | -27.1462 | 151.8062 | 000003222483 | 01/JAN/80
EECL | OT197149 | OP | Operational |  | 2023-09-28 | 202309 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | ? | 22kV |  | ? |  | 1060152 | 2024 | 23CA13947 | 0:36 | 0:43 | COMP | Completed | ? | Fine | Capricornia | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT | ? | MIMOSA PARK DUARINGA 16368 BAUHINIA DOWNS RD BARALABA QLD 4702 | Fault occurred at:28/09/2023 14:34 REDACTED , 0428556419 | >DFL --> StartedWithinPastWeek:NO -- -- NeighboursAffected:NO -- OccursSameTimeEachDay:NO< Incident Details:Very dimming power to property. Also affecting water pumps for stocks. 3pN.Fr16368FitzroyDevelopmentRdWoorabind Warnings[dflSafety, dflTurnOffAppliances]: ADVISED | [11 empty] | 3015305 | ######## | ######## | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton |  | -24.1786 | 149.4944 | 000003015305 | 01/JAN/84
EECL | OT197241 | OP | Operational |  | 2023-09-29 | 202309 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay | ? | 11kV |  | ? |  | 1719707 | 2024 | 23NQ11807 | 0:36 | 0:39 | ANAL | Data verification | ? | Fine | North Queensland | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FE | ? | AYR: | CLARE RD, GIDDY RD, BRUCE HWY, KILRIE RD, HOME HILL RD, AYR DALBEG RD, OLD HOME HILL RD\r\nMCDESME: | MCDESME RD\r\n JARVISFIELD 11kV Jarv No.6 Fdr CB FB08Q00 tripped. SCADA Interface automated outage. entered from the SCADA Interface\r\nREDACTEDenroute\r\nSending Asset Event to FFA\r\nFFA Order Created F-AE23NQ11807-1-0 DfltHost\r\nFFA Order Acknowledged F-AE23NQ11807-1-0 hhlfr01 REDACTED 0438092091\r\nFFA Order En Route F-AE23NQ11807-1-0 hhlfr01\r\nFFA Order On Site F-AE23NQ11807-1-0 hhlfr01\r\ncrews patrolling/ sectionalising\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nSending Asset Event to FFA\r\nline down adj DL807466\r\nTime On modified from 23:59 29-Sep to 17:00 29-Sep\r\nHV Wires Down\r\nSending Asset Event to FFA\r\nReason for Event changed from Unknown\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nJA-06 tripped when closing Gilligans Rd No.4.\r\ncrew to investigate.\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nbroken xarm tee off to BDS1294\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nAsset selection modified\r\nSending Asset Event to FFA\r\nFFA Order En Route F-AE23NQ11807-1-0 hhlfr01\r\nTime On modified from 17:00 29-Sep to 16:16 29-Sep\r\nSending Asset Event to FFA\r\nFFA Order On Site F-AE23NQ11807-1-0 hhlfr01\r\nFFA Order F-AE23NQ11807-1-0 Completed by technician REDACTED in crew hhlfr01(0438092091) with code A-T-306 - HV-Unassisted failure(Apparent defect)\r\nAction Taken : Replaced broken HV crossarm\r\nSite Label : 2030556 | 1 | 2091364 | T.off109 Ayr-DalbegRd Plantation Ck Ayr | 1719707 |  |  | 2022-05-27 | 490 | ? |  |  | ADFS_ | ? | 14 | Serviceable | N | Serviceable | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | SG SPOTTED GUM | 12 kiloNewton |  | -19.6467 | 147.3833 | 000002091364 | 01/JAN/76
EECL | OT197553 | OP | Operational |  | 2023-10-02 | 202310 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 728612 | 2024 | 23NQ11879 | 45201.571 | 2023-10-02 13:45 | COMP | Completed |  | Wind | North Queensland | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | BLACKROCK, INGHAM, PALM CREEK | INGHAM 11kV Warrens Hill ACR CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface Sending Asset Event to FFA FFA Order Created F-AE23NQ11879-1-0 DfltHost Sending Asset Event to FFA Access is require to replace INS300. Time On modified from 23:59 02-Oct to 18:30 02-Oct HV Wires Down Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ11879-1-0 ingcsfr02 REDACTED 0407657024 FFA Order En Route F-AE23NQ11879-1-0 ingcsfr02 FFA Order On Site F-AE23NQ11879-1-0 ingcsfr02 Time On modified from 18:30 02-Oct to 17:02 02-Oct Sending Asset Event to FFA FFA Order F-AE23NQ11879-1-0 Completed by technician REDACTED in crew INGCSFR02(0407657024) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : HV X- ARM BROKEN AT SITE LABEL 2020379 CAUSING 11KV TO COME TO GROUND WARRENS HILL RECLOSER TRIPPED ON EF ISOLATED EARTHED AND CARRIED OUT REPAIRS Site Label : 2020379 auto-completed | 1 | 2054907 | Access 48 Danger Camp Rd. Ingham | 728612 | 2020379 | 2054907 | 2019-11-05 | 1427 | N |  |  | 12.5 | 1 |  | Serviceable | Y | Urb unsty sub pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Backyard | SG SPOTTED GUM | 12 kiloNewton | 2002 | -18.6846 | 146.2048 | 000002054907 | 01/JAN/02
EECL | OT199336 | OP | Operational |  | 2023-10-17 | 202310 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 955401 | 2024 | 23WB13637 | 45216.5347 | 2023-10-17 12:30 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | YANDARAN: DICKSONS RD | F-1009-r - 11kV Dropout Fuse DO852196 - Crew Require Access to Replace Broken Crossarm | 11kV Dropout Fuse DO852196 - Crew Require Access to Replace Broken Crossarm F-10009-r BNDCSFR05 Sending Asset Event to FFA FFA Order Created F-AE23WB13637-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23WB13637-1-0 bndcsfr05 REDACTED 0439991440 FFA Order En Route F-AE23WB13637-1-0 bndcsfr05 FFA Order On Site F-AE23WB13637-1-0 bndcsfr05 Sending Asset Event to FFA Time Off modified from 13:00 17-Oct to 12:50 17-Oct Sending Asset Event to FFA Sending Asset Event to FFA Restoration Comments for F-AE23WB13637-1-0 by bndcsfr05: replaced broken arm Sending Asset Event to FFA FFA Order En Route F-AE23WB13637-1-0 bndcsfr05 FFA Order On Site F-AE23WB13637-1-0 bndcsfr05 Time On modified from 18:00 17-Oct to 15:04 17-Oct Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23WB13637-1-0 Completed by technician REDACTED in crew bndcsfr05(0439991440) with code A-F-C - Completed Action Taken : replace HV broken cross arm Site Label : 2014459 | 1 | 2062558 | 303 dicksons road yandaran | 955401 | 2014459 | 2062558 | 2021-12-22 | 664 | N |  |  | 12.5 | 2 |  | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | IB IRONBARK | 12 kiloNewton | 1993 | -24.6809 | 152.0759 | 000002062558 | 01/JAN/93
EECL | OT199916 | OP | Operational |  | 2023-10-22 | 202310 | Crossarm | Xarm, Wood Dressing | Deteriorated | Termites |  | 11kV |  |  |  | 921403 | 2024 | 23NQ12604 | 45221.5047 | 2023-10-22 12:38 | CAN | Cancelled |  | Fine | North Queensland | Unplanned Outage | Animal Insects (termites/borers/white ants) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | AYR: AYR DALBEG RD, CLARE RD | 11kV Pole Dist Sub BDS2418, AYRZ Sub, AY06 Fdr: Repair Crossarm | 11kV Pole Dist Sub BDS2418, AYRZ Sub, AY06 Fdr: Repair Crossarm Sending Asset Event to FFA FFA Order Created F-AE23NQ12604-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 22-Oct to 15:00 22-Oct Sending Asset Event to FFA Time On modified from 15:00 22-Oct to 14:07 22-Oct Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ12604-1-0 hhlfr01 REDACTED 0419299921 FFA Order En Route F-AE23NQ12604-1-0 hhlfr01 FFA Order On Site F-AE23NQ12604-1-0 hhlfr01 FFA Order F-AE23NQ12604-1-0 Completed by technician REDACTED in crew hhlfr01(0419299921 ) with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : termite damage to cross arm. replaced arm. Site Label : 2030636 Outage incorrectly created as unplanned, Forced outage 23NQ12607 created to capture this event . | 1 | 2091997 | ToffBtwn.468 to 567 Ayr-Dalbeg Rd Ayr | 921403 | 2030636 | 2091997 | 2022-05-26 | 514 | N |  |  | 12.5 | 2 |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Soil |  | SG SPOTTED GUM | 12 kiloNewton | 1993 | -19.6624 | 147.3522 | 000009338329
EECL | OT198996 | OP | Operational |  | 2023-10-14 | 202310 | Crossarm | Xarm, Wood Strain | Deteriorated | Termites |  | LV |  |  |  | 980381 | 2024 | 23NQ12298 | 45213.1208 | 2023-10-14 14:54 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | BURKETOWN: BEAMES ST, BOWEN ST, LAGOON ST | 22kV Pole Dist Sub IGS599726 - REDACTED requesting outage for strain pole repairs on SL 2056798. | 22kV Pole Dist Sub IGS599726 - REDACTED requesting outage for strain pole repairs on SL 2056798. Time Off modified from 17:00 14-Oct to 02:54 14-Oct Sending Asset Event to FFA FFA Order Created F-AE23NQ12298-1-0 DfltHost FFA Order Acknowledged F-AE23NQ12298-1-0 bur01 REDACTED 0436418642 FFA Order En Route F-AE23NQ12298-1-0 bur01 FFA Order On Site F-AE23NQ12298-1-0 bur01 FFA Order F-AE23NQ12298-1-0 Completed by technician REDACTED in crew bur01(0436418642) with code A-F-C - Completed Action Taken : replaced rotten Lv term arm Site Label : 2056798 Time On modified from 18:00 14-OCT to 15:21 14-OCT | 1 | 2161689 | Bowen St 4 Spn E of Beames St Burketown | 980381 | 50113 | 2161689 | 2021-02-01 | 985 | N |  |  | 12.5 |  | 2 | Serviceable | Y | Rrl Toff | WOOD (GREEN) SALT IMPREG CCA | Grass |  | BI BROAD LEAF IRONBARK | 5 kiloNewton | 2002 | -17.745 | 139.5499 | 000009390667
EECL | OT199310 | OP | Operational |  | 2023-10-17 | 202310 | Crossarm | Xarm, Wood Termination | Split | Termites |  | LV |  |  |  | 1055552 | 2024 | 23FN13804 | 45216.41 | 2023-10-17 10:42 | COMP | Completed |  | Fine | Far North | Unplanned Outage | Animal Insects (termites/borers/white ants) | Unknown | due to damage requiring emergency repairs. Fault finding is in progress. | GT |  | DIMBULAH: PETFORD RD | LV outage only @ 22kV Pole Dist Sub SS1509 to replace LV crossarm | LV outage only @ 22kV Pole Dist Sub SS1509 to replace LV crossarm Sending Asset Event to FFA FFA Order Created F-AE23FN13804-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN13804-1-0 mbacsfr04 REDACTED 0428853807 FFA Order En Route F-AE23FN13804-1-0 mbacsfr04 FFA Order On Site F-AE23FN13804-1-0 mbacsfr04 FFA Order En Route F-AE23FN13804-1-0 mbacsfr04 FFA Order On Site F-AE23FN13804-1-0 mbacsfr04 FFA Order F-AE23FN13804-1-0 Completed by technician REDACTED in crew mbacsfr04(0428853807) with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : replaced broken cross arm due to termites Site Label : 2098757 Time On modified from 23:59 17-OCT to 13:31 17-OCT | 1 | 2281333 | 65773 Burke Development Rd Dimbulah | 1055552 | KA7 | 2281333 | 2020-01-23 | 1363 | N |  |  | 11 |  | 1 | Serviceable | N | Rrl sty term 1 cct | WOOD UNTREATED ROUND | Grass | Paddock Grazing | NI NARROW LEAF RED I | 5 kiloNewton | 1960 | -17.1708 | 145.0693 | 000002281333 | 01/JAN/60
EECL | OT199046 | OP | Operational |  | 2023-10-15 | 202310 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1368719 | 2024 | 23WB13548 | 45214.4062 | 2023-10-15 13:15 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 49 WEBBERS BRIDGE RD;WOOROONDEN QLD 4605 | Fault occurred at:15/10/2023 08:10; REDACTED , 0428985529; >UPH --> Details:Broken Cross-arm<; Incident Details:Broken xarm in paddock close to house. Wire 1m from ground and dam. No loss,; Access Details:Double gates will be open; Warnings[uphSafety]: ADVISED |  | 1 | 2287833 | 49 Webbers Bridge rd Wooroonden. beh hou | 1368719 | 2089024 | 2287833 | 2021-11-09 | 705 | N |  |  | 12.5 | 1 | 1 | Serviceable | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 2002 | -26.119 | 151.751 | 000002287833 | 01/JAN/02
EECL | OT199400 | OP | Operational |  | 2023-10-17 | 202310 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1473435 | 2024 | 23SW18552 | 45218.734 | 2023-10-19 17:26 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | MILLMERRAN: COMMODORE PEAK RD | F-1021-r - 11kV Pole Dist Sub PE05659 - Crew require access to repair broken cross arm | F-1021-r - 11kV Pole Dist Sub PE05659 - Crew require access to repair broken cross arm twmoc01 - REDACTED Sending Asset Event to FFA FFA Order Created F-AE23SW18552-1-0 DfltHost Sending Asset Event to FFA Time Off modified from 18:00 19-Oct to 17:37 19-Oct Sending Asset Event to FFA Time On modified from 23:59 19-Oct to 19:09 19-Oct Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW18552-1-0 twmoc01 REDACTED 0428221390 FFA Order En Route F-AE23SW18552-1-0 twmoc01 FFA Order On Site F-AE23SW18552-1-0 twmoc01 FFA Order F-AE23SW18552-1-0 Completed by technician REDACTED in crew twmoc01(0428221390) with code A-F-C - Completed Action Taken : Replaced EDO XArm Site Label : 3208556 | 1 | 2386581 | PE5659,276 Commodore Peak Rd,Clontarf | 1473435 | 3208556 | 2386581 | 2021-06-03 | 866 | N |  |  | 14 | 5 |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | BB BLACKBUTT | 8 kiloNewton | 1979 | -27.9454 | 151.2208 | 000002386581 | 01/JAN/79
EECL | OT200596 | OP | Operational |  | 2023-10-26 | 202310 | Crossarm | Xarm, Wood Intermediate | Broken | Unknown |  | 11kV |  |  |  | 1107910 | 2024 | 23SW18946 | 45225.6569 | 2023-10-26 15:12 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | CHINCHILLA | F-1054-r EE REDACTED advised that Conductor at SL3211120 is very Low and requires Access to rectify from 11kV Gas Switch AB783879 Broken cross-arm replaced. SL 3211120. REDACTED | EE Lachlan advised that Conductor at SL3211120 is very Low and requires Access to rectify from 11kV Gas Switch AB783879 Time On modified from 23:59 26-Oct to 18:00 26-Oct CHNFR01 Sending Asset Event to FFA FFA Order Created F-AE23SW18946-1-0 DfltHost FFA Order Acknowledged F-AE23SW18946-1-0 chnfr01 REDACTED 0429419383 FFA Order En Route F-AE23SW18946-1-0 chnfr01 F-1054-r Sending Asset Event to FFA Time Off modified from 15:30 26-Oct to 15:38 26-Oct Sending Asset Event to FFA FFA Order On Site F-AE23SW18946-1-0 chnfr01 FFA Order F-AE23SW18946-1-0 Completed by technician REDACTED in crew chnfr01(0429419383) with code A-F-C - Completed Action Taken : replaced broken xarm after lightning storm last night one conductor dropped to 2m from the ground Site Label : 3211120 Actual Power Restoration for F-AE23SW18946-1-0: 26-OCT-2023 17:00:00 Time Off modified from 15:38 26-Oct to 15:46 26-Oct Time On modified from 18:00 26-Oct to 17:00 26-Oct HV Wires Down Added notes to Reasons tab. | 1 | 2402813 | 3S Aerodrome Rd on RifleRange Rd Cchilla | 1107910 | 3211120 | 2402813 | 2020-11-22 | 1068 | N |  |  | 14 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1992 | -26.7748 | 150.6476 | 000002402813 | 01/JAN/92
EECL | OT201013 | OP | Operational |  | 2023-10-28 | 202310 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1643990 | 2024 | 23SW19071 | 45227.837 | 2023-10-28 20:08 | COMP | Completed |  | Fine | South West | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to a SCADA Automated Event | FC |  | AMIENS, DALVEEN | F-2012-q - cb tripped to lockout via OC prot STANTHORP TN 11kV Goldfeld ACR 20866 CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface F-2012-q - cb tripped to lockout via OC prot ah co-ord advised, crew to patrol feeder prior to reclose attempt sttoc01 Sending Asset Event to FFA FFA Order Created F-AE23SW19071-1-0 DfltHost crew advise broken crossarm above PE04871 Sending Asset Event to FFA sttoc01 Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW19071-1-0 sttoc01 REDACTED 0439186719 FFA Order En Route F-AE23SW19071-1-0 sttoc01 FFA Order On Site F-AE23SW19071-1-0 sttoc01 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 28-Oct to 23:57 28-Oct Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23SW19071-1-0 Completed by technician REDACTED in crew sttoc01(0439186719) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : hv switch , replace XARM, due to rot, 11kV, FDR operated Site Label : 2137007 | 1 | 2415171 | PE4871 2697 Goldfields Rd Dalveen | 1643990 | 2137007 | 2415171 | 2022-01-13 | 653 | N |  |  | 12.5 | 2 | 2 | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Rock | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1974 | -28.4162 | 151.7275 | 000002415171 | 01/JAN/74
EECL | OT200296 | OP | Operational |  | 2023-10-25 | 202310 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1058803 | 2024 | 23SW18809 | 45224.3403 | 2023-10-25 08:12 | COMP | Completed |  |  | South West | Forced Outage |  | Public Safety Isolation - Directed by Emerg Serv Authorised Agent | due to public safety concerns as directed by emergency services. | FC |  | CROWS NEST, GEHAM, GRAPETREE, GROOMSVILLE, HAMPTON, MERRITTS CREEK, PALMTREE, PECHEY, PERSEVERANCE, RAVENSBOURNE, WHICHELLO | F-1041-r - CRNE - PEACHEY CB16374 - Lines down report at PE08001 Lines down report from police station. Crew replaced broken HV pin arm. SL 3096127. REDACTED | Lines down report at PE8001 Time Off modified from 09:10 25-Oct to 08:10 25-Oct 11kV Recloser CB16374 opened at 08:10 due to lines down report. Grapetree Rd CB17662 currently bypassed Depot Co-ord Advised Broken X-arm at SL3096127. isolated at DL14102 Asset selection modified 11kV Disc Links DL861730 is DL14102 on PON Sending Asset Event to FFA FFA Order Created F-AE23SW18809-1-0 DfltHost twmoc05 Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW18809-1-0 twmoc05 REDACTED 0407646440 twmfr03 Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW18809-1-0 twmfr03 REDACTED 0418712115 FFA Order En Route F-AE23SW18809-1-0 twmfr03 Time On modified from 23:59 25-Oct to 15:30 25-Oct Sending Asset Event to FFA FFA Order On Site F-AE23SW18809-1-0 twmfr03 Asset selection modified Sending Asset Event to FFA Time On modified from 15:30 25-Oct to 14:22 25-Oct HV Wires Down Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23SW18809-1-0 Completed by technician REDACTED in crew twmfr03(0418712115) with code A-F-C - Completed Action Taken : replaced broken hv pin arm Site Label : 3096127 Updated Reasons tab. Reason for Event changed from Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | 1 | 2960114 | 1 NW PE8001 52 Beh Rd Crows Nest | 1058803 | 3096127 | 2960114 | 2022-09-15 | 405 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road | RI RED IRONBARK | 3 kiloNewton | 1989 | -27.2969 | 152.1415 | 000002960114 | 01/JAN/89
EECL | OT199536 | OP | Operational |  | 2023-10-18 | 202310 | Crossarm | Xarm, Wood Dressing | Broken | Rot/Decay |  | 11kV |  |  |  | 816070 | 2024 | 23SW18491 | 45217.7132 | 2023-10-18 17:09 | COMP | Completed |  |  | South West | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FE |  | CENTENARY HEIGHTS, SOUTH TOOWOOMBA, TOOWOOMBA | Macarthur St Feeder 11kV CB4095 - Tripped by OCC due to broken X-arm and possible ncroachment of 11kV mains into LV. Crew replaced broken HV pin arm. SL 4246329. REDACTED | Macarthur St Feeder 11kV CB4095 - Tripped by OCC due to broken X-arm and possible encroachment of 11kV mains into LV. Time Off modified from 17:30 18-Oct to 17:07 18-Oct Other Incident twmoc01 Sending Asset Event to FFA FFA Order Created F-AE23SW18491-1-0 DfltHost REDACTEDSending Asset Event to FFA F-1957-q Sending Asset Event to FFA Spoke to REDACTED 0417 793 146 about wether or not we back feed MaCarthey FDr or not he will get back to me in 5mins Sending Asset Event to FFA Time On modified from 23:59 18-Oct to 20:30 18-Oct Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW18491-1-0 twmoc01 REDACTED 0428221390 FFA Order En Route F-AE23SW18491-1-0 twmoc01 FFA Order On Site F-AE23SW18491-1-0 twmoc01 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 20:30 18-Oct to 19:51 18-Oct Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23SW18491-1-0 Completed by technician REDACTED in crew twmoc01(0428221390) with code A-F-C - Completed Action Taken : Replaced broken HV pin arm Site Label : 4246329 FFA Order F-AE23SW18491-1-0 Completed by technician REDACTED in crew twmoc01(0428221390) with code A-F-C - Completed Action Taken : Replaced broken HV pin arm Site Label : 4246329 auto-completed Added notes to Reasons tab. | 1 | 3165244 | 12 macarthur st sth toowoomba | 816070 | 4246329 | 3165244 | 2022-06-17 | 488 | N |  |  | 12.5 | 1 | 1 | Serviceable | N | Urb inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 5 kiloNewton | 1969 | -27.5726 | 151.9625 | 000003165244 | 01/JAN/69
EECL | OT199587 | OP | Operational |  | 2023-10-19 | 202310 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 22kV |  |  |  | 943035 | 2024 | 23CA14656 | 45218.4764 | 2023-10-19 11:13 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | OGMORE | F- 1018-r - 22kV Recloser X598902 - Crew Require Access to repair Broken Crossarm at TX100048 Crew replaced broken cross-arm. SL 4233501. REDACTED | 22kV Recloser X598902 - Crew Require Access to repair Broken Crossarm at TX100048 F-1018-r rokfr06 Sending Asset Event to FFA FFA Order Created F-AE23CA14656-1-0 DfltHost Sending Asset Event to FFA Time Off modified from 11:30 19-Oct to 11:26 19-Oct Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA14656-1-0 rokfr06 REDACTED 0409315226 Sending Asset Event to FFA Time On modified from 18:00 19-Oct to 19:00 19-Oct Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 19:00 19-Oct to 17:30 19-Oct Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23CA14656-1-0 rokfr06 FFA Order On Site F-AE23CA14656-1-0 rokfr06 FFA Order F-AE23CA14656-1-0 Completed by technician REDACTED in crew Rokfr06(0409315226) with code A-F-C - Completed Action Taken : Replace broken crossarm Site Label : 4233501 Added notes to Reasons tab. | 1 | 3299719 | SP100048 OGMORE CON RD OGMORE | 943035 | 4233501 | 3299719 | 2021-04-18 | 914 | N |  |  | 12.5 | 2 |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1978 | -22.6198 | 149.6049 | 000003299719 | 01/JAN/78
EECL | OT199455 | OP | Operational |  | 2023-10-18 | 202310 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 66kV |  |  |  | 6907338 | 2024 | 23NQ12426 | 45217.4014 | 2023-10-18 09:41 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | SUBT-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FE |  | BAMBAROO, COOLBIE, GREENVALE, MOUNT FOX, MOUNT GARNET, MUTARNEE, PALUMA | INGHAM 66kV Black Rv Fdr CB A152 tripped. SCADA Interface automated outage. Crew repaired broken 66kV cross-arm. SL 5241245. REDACTED | entered from the SCADA Interface Downstream Outages excluded from asset selection: 23NQ12410 Mt Fullstop No.1 (22 assets) Earth Fault trip Asset selection modified Sending Asset Event to FFA FFA Order Created F-AE23NQ12426-1-0 DfltHost fault indicators shows white phase on the Greenvale 66kV line. Sending Asset Event to FFA NEON and REDACTED advised chopper and ground crew are currently being organised . Sending Asset Event to FFA distance to faullt 78klm advised from REDACTED lots of thick smoke around. REDACTED advises that crew have just left depot. also REDACTED advises they cannot get a chopper and will have to brive to the faulted area. Sending Asset Event to FFA crew have advised approx 20 -30 to the IN-GR 1 Sending Asset Event to FFA crew - REDACTED contact for switching. delays was due to crew was working on other jobs and had to pack up and return to depot before being dispatched Sending Asset Event to FFA REDACTED advises IN-GRNo.1 ES is defective Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA All customers supply returned except Mt Fox and Greenvale Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ12426-1-0 ingcsfr02 REDACTED 0473145674 correct distance was 76.60klm Sending Asset Event to FFA Crews were able to patrol a section of line that SCADA indicated the fault might be but not the whole feeder. Due to a lot of fires in the area and the very dry conditions Crews will Isolate at IN-GR No.2 and Earth towards GREN Sub. Power will be restored upto MTFO Sub. Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Crews have arranged a chopper to patrol the rest of the 66kV Lines to GREN Sub first thing depot hrs 19/10/23 Time On modified from 23:59 18-Oct to 23:59 19-Oct Sending Asset Event to FFA REDACTED advised delays with the chopper this morning. Crews expect to continue line patrol around midday today when the chopper is available. REDACTED will provide an update if anything changes. Sending Asset Event to FFA crews have found broken 66kV wishbone arm 6 poles past the Mt Fox substation Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA The generator on CTS1003 has stopped, generation are now looking into the cause Sending Asset Event to FFA Generation on CTS1003 back online at 1157 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Crews have completed Repairs and to Safely Energise Line CB at Ingham has to be Opened Sending Asset Event to FFA Time On modified from 23:59 19-Oct to 14:23 19-Oct Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Pending F-AE23NQ12426-1-0 FFA Order Acknowledged F-AE23NQ12426-1-0 ingcm05 REDACTED 0407657024 FFA Order En Route F-AE23NQ12426-1-0 ingcm05 FFA Order On Site F-AE23NQ12426-1-0 ingcm05 FFA Order F-AE23NQ12426-1-0 Completed by technician REDACTED in crew INGCM05(0407657024) with code A-T-320 - SUBT-Unassisted failure(Apparent defect) Action Taken : 66 KV X ARM BROKEN AT 5241245 Site Label : 5241245 Reason for Event changed from Unknown Updated Event Trigger from Fire (External) to SUBT-Unassisted failure. CTS555 removed via Clash Wizard as is captured in 23NQ12689 | 1 | 5586005 | 3spn W of IN-GR No 2 Kangeroo Hills Stn | 6907338 | 5241245 | 5586005 | 2019-08-09 | 1531 | N |  |  | 15.5 |  |  | Serviceable | Y | 66kV rrl inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1973 | -18.8629 | 145.7097 | 000005586005 | 01/JAN/73
EECL | OT201591 | OP | Operational |  | 2023-11-02 | 202311 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1549608 | 2024 | 23SW19278 | 2023-11-02 23:50 | 2023-11-02 14:48 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | WILSONTON | 11kV Gas Switch AB612530 - Crew Require Access to replace Crossarm at Pole 3301872 | 11kV Gas Switch AB612530 - Crew Require Access to replace Crossarm at Pole 3301872 Switching Sheet ID updated from to J-284108-g. TWMOC01 Sending Asset Event to FFA FFA Order Created F-AE23SW19278-1-0 DfltHost Time Off modified from 23:30 02-Nov to 23:49 02-Nov Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 04:00 03-Nov to 02:00 03-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW19278-1-0 twmoc01 REDACTED 0409105958 FFA Order En Route F-AE23SW19278-1-0 twmoc01 FFA Order On Site F-AE23SW19278-1-0 twmoc01 FFA Order F-AE23SW19278-1-0 Completed by technician REDACTED in crew twmoc01(0409105958) with code A-F-C - Completed Action Taken : replaced 11 kv arms Site Label : 3301872 | 1 | 2715505 | 352B Bridge St,Toowoomba | 1549608 | 3301872 | 2715505 | 2021-09-21 | 772 | N |  |  | 14 | 2 | 2 | Serviceable | Y | HV lower cct Toff | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 12 kiloNewton | 1978 | -27.545 | 151.9258 | 000002715505 | 01/JAN/78
EECL | OT201637 | OP | Operational |  | 2023-11-02 | 202311 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | LV |  |  |  | 1493988 | 2024 | 23MK8726 | 2023-11-02 17:39 | 2023-11-02 17:43 | COMP | Completed |  |  | Mackay | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FC |  | CRYSTAL BROOK, FOXDALE, GREGORY, GREGORY RIVER, MYRTLEVALE, PROSERPINE, STRATHDICKIE | F-701-t: 11kV FOXDALE FDR CB opened for public safety due to reports of fallen powerlines, refer to F/C 2374072. LV cross-arm broken, customers restored. Cross-arm replaced under 23MK8729 REDACTED | 11kV FOXDALE FDR CB opened for public safety due to reports of fallen powerlines, refer to F/C 2374072. Time Off modified from 18:00 02-Nov to 17:39 02-Nov F-701-t Crew ETA 1755 hrs. Assets extracted from 6525 (FULLER) into event 23MK8729 Time On modified from 23:59 02-Nov to 18:29 02-Nov Added notes to Reasons tab. | 1 | 3270419 | sub6525 106 upriver rd proserpine | 1493988 | 4213504 | 3270419 | 2020-01-17 | 1385 | N |  |  | 14 | 3 | 1 | Serviceable | Y | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | BI BROAD LEAF IRONBARK | 5 kiloNewton | 1991 | -20.358 | 148.5458 | 000003270419 | 01/JAN/91
EECL | OT201883 | OP | Operational |  | 2023-11-04 | 202311 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1458237 | 2024 | 23SW19423 | 2023-11-04 11:00 | 2023-11-04 14:50 | COMP | Completed |  |  | South West | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 134 GEHAM STATION RD GEHAM QLD 4352 | Fault occurred at:04/11/2023 08:45; REDACTED, 0468516478; >UPH --> Details:Life Threatening<; Incident Details:No covid. Broken crossarm and bracket. 2 main lines lower than normal but over 4 meters from ground. Access ok. Dogs locked up. area clear.; Warnings[uphSafety]: ADVISED P1 Call Flag |  | 1 | 3098082 | 131 Geham Station Rd,Geham | 1458237 | 3124288 | 3098082 | 2019-11-10 | 1455 | N |  |  | 14 |  | 1 | Serviceable | N | Urb unsty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 12 kiloNewton |  | -27.4043 | 152.011 | 000003098082 | 01/JAN/76
EECL | OT203429 | OP | Operational |  | 2023-11-13 | 202311 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1536058 | 2024 | 23SW20062 | 2023-11-13 17:58 | 2023-11-13 15:45 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | DOUGLAS: DOUGLAS PLAINBY RD, GOMORAN DOUGLAS RD, GUY RD, PECHEY MACLAGAN RD, SCHMALING RD, STENZEL RD GOOMBUNGEE: GOMORAN-BERGEN RD, PECHEY MACLAGAN RD GROOMSVILLE: PECHEY MACLAGAN RD, SMOOTHY RD | 11kV Disc Links DL9788 - Suspect arm at 3136345 requires replacement. | 11kV Disc Links DL9788 - Suspect arm at 3136345 requires replacement. twmoc02 Sending Asset Event to FFA FFA Order Created F-AE23SW20062-1-0 DfltHost Sending Asset Event to FFA Time Off modified from 17:00 13-Nov to 17:58 13-Nov Time On modified from 23:59 13-Nov to 19:25 13-Nov Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW20062-1-0 twmoc02 REDACTED 0439388767 FFA Order En Route F-AE23SW20062-1-0 twmoc02 FFA Order On Site F-AE23SW20062-1-0 twmoc02 FFA Order F-AE23SW20062-1-0 Completed by technician REDACTED in crew twmoc02(0439388767) with code A-F-C - Completed Action Taken : replace hv term arm Site Label : 3136345 | 1 | 3170843 | 1NE DL9788 297G'mrenD'lasRdG'bungee | 1536058 | 3136345 | 3170843 | 2020-04-27 | 1295 | N |  |  | 12.5 | 2 |  | Serviceable | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | BB BLACKBUTT | 3 kiloNewton | 1977 | -27.3387 | 151.8978 | 000003170843 | 01/JAN/71
EECL | OT204542 | OP | Operational |  | 2023-11-21 | 202311 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | LV |  |  |  | 780555 | 2024 | 23SW20425 | 2023-11-21 02:33 | 2023-11-21 02:33 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | ATHOL: NEWTON RD, WEGENER RD | EE REDACTED requested LV Isolation due to Insultor pulled through XArm at 11kV Pole Dist Sub PE04032 | EE REDACTED requested LV Isolation due to Insultor pulled through XArm at 11kV Pole Dist Sub PE04032 twmoc04 Time Off modified from 02:40 21-Nov to 02:33 21-Nov Sending Asset Event to FFA FFA Order Created F-AE23SW20425-1-0 DfltHost Sending Asset Event to FFA Time On modified from 04:00 21-Nov to 05:00 21-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW20425-1-0 twmoc04 REDACTED 0459819951 Time On modified from 05:00 21-Nov to 07:00 21-Nov Sending Asset Event to FFA FFA Order En Route F-AE23SW20425-1-0 twmoc04 FFA Order On Site F-AE23SW20425-1-0 twmoc04 Time On modified from 07:00 21-Nov to 08:00 21-Nov Sending Asset Event to FFA FFA Order F-AE23SW20425-1-0 Completed by technician REDACTED in crew twmoc04(0459819951) with code A-F-C - Completed Action Taken : isolate supply, replace broken LV cross arm, restore supply Site Label : 3207177 Time On modified from 08:00 21-NOV to 07:05 21-NOV | 1 | 2377296 | 1pole N 35 Wegener rd Southbrook | 780555 | 3207177 | 2377296 | 2020-07-15 | 1224 | N |  |  | 12.5 | 2 |  | Serviceable | N | Rrl Toff | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 3 kiloNewton |  | -27.6136 | 151.7728 | 000002377296 | 01/JAN/80
EECL | OT204874 | OP | Operational |  | 2023-11-22 | 202311 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1399655 | 2024 | 23WB14862 | 2023-11-22 19:38 | 2023-11-22 19:28 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | KINGAROY: GRANT AVE, HARRIS RD, SORENSEN ST | Crews advise, require access to the LV to change a crossarm 11kV Pole Dist Sub 8457 LV switching only..Crews to open the LV isolation on both transformers. | Crews advise, require access to the LV to change a crossarm 11kV Pole Dist Sub 8457 . LV switching only.. KNGOC03. Sending Asset Event to FFA FFA Order Created F-AE23WB14862-1-0 DfltHost FFA Order Acknowledged F-AE23WB14862-1-0 kngoc03 REDACTED 0427816804 Primary Asset de-escalated from Doonkuna St Fdr Comp (FC) Sending Asset Event to FFA FFA Order En Route F-AE23WB14862-1-0 kngoc03 FFA Order On Site F-AE23WB14862-1-0 kngoc03 Sending Asset Event to FFA Time Off modified from 20:00 22-Nov to 19:38 22-Nov Sending Asset Event to FFA FFA Order En Route F-AE23WB14862-1-0 kngoc03 FFA Order On Site F-AE23WB14862-1-0 kngoc03 FFA Order F-AE23WB14862-1-0 Completed by technician REDACTED in crew kngoc03(0427816804) with code A-F-C - Completed Action Taken : LV switching completed and arm changed Site Label : 3109872 Time On modified from 23:00 22-NOV to 21:21 22-NOV | 1 | 3036481 | cnrSORENSEN ST & GRANT AVE KINGAROY HGTS | 1399655 | 3109872 | 3036481 | 2019-08-20 | 1555 | N |  |  | 12.5 | 2 | 2 | Serviceable | N | Rrl sty term 2 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | RI RED IRONBARK | 5 kiloNewton | 1983 | -26.559 | 151.87 | 000003036481 | 01/JAN/83
EECL | OT206104 | OP | Operational |  | 2023-11-29 | 202311 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 22kV |  |  |  | 944168 | 2024 | 23CA16724 | 2023-11-29 18:30 | 2023-11-29 18:36 | COMP | Completed | M |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | BARMOYA, THE CAVES, WATTLEBANK | F-1349-r 22kV Recloser RC777317. Opened at AHC request. Reports of lines down beyond | 22kV Recloser RC777317. Opened at AHC request. Reports of lines down beyond ccoc02 Sending Asset Event to FFA FFA Order Created F-AE23CA16724-1-0 DfltHost Sending Asset Event to FFA isolated at S5228 Asset selection modified Sending Asset Event to FFA rokfr02 Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA16724-1-0 rokfr02 REDACTED 0409315226 FFA Order En Route F-AE23CA16724-1-0 rokfr02 FFA Order On Site F-AE23CA16724-1-0 rokfr02 Crew have made safe by repairing downed conductors, confirmed with REDACTED work site is fit to energise Sending Asset Event to FFA Time On modified from 23:59 29-Nov to 23:06 29-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23CA16724-1-0 Completed by technician REDACTED in crew rokfr02(0409315226) with code A-F-C - Completed Action Taken : replaced broken 150x150 wood hv cross arm and repaired conductors Site Label : 4232126 FFA Order F-AE23CA16724-1-0 Completed by technician REDACTED in crew rokfr02(0409315226) with code A-F-C - Completed Action Taken : replaced broken 150x150 wood hv cross arm and repaired conductors Site Label : 4232126 FFA Order F-AE23CA16724-1-0 Completed by technician REDACTED in crew rokfr02(0409315226) with code A-F-C - Completed Action Taken : replaced broken 150x150 wood hv cross arm and repaired conductors Site Label : 4232126 | 1 | 3297826 | 74 ch barret rd the caves | 944168 | 4232126 | 3297826 | 2021-01-22 | 1041 | N |  |  | 12.5 | 2 |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Front Yard | IB IRONBARK | 8 kiloNewton | 1997 | -23.1442 | 150.5669 | 000003297826 | 01/JAN/97
EECL | OT206279 | OP | Operational |  | 2023-11-30 | 202311 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 779597 | 2024 | 23WB15109 | 2023-11-30 13:39 | 2023-11-30 19:29 | COMP | Completed |  | Fine | Wide Bay | Unplanned Outage | LV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | 8149 BURNETT HWY TANSEY QLD 4601 | Fault occurred at:30/11/2023 09:00; REDACTED, 0428760832;>WDPP --> AffectingTraffic:NO -- StillHavePower:UNSURE<;Incident Details:Insulator snapped end of crossarm off where bolt is located, powerline is on the ground.;Access Details:Wait at entrance and customer will come and direct them to the issue;COVID-19:NO;Warnings[wiresDownSafety]: ADVISED;Dog restraint:ARRIVAL;Sensitive Load:N P1 Call Flag |  | 1 | 2246867 | acc 8149 Burnett hwy, Tansey. rear pad' | 779597 | 3189439 | 2246867 | 2021-06-29 | 884 | N |  |  | 12.5 |  | 1 | Serviceable | Y | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Irrigation | SG SPOTTED GUM | 5 kiloNewton | 1996 | -26.018 | 152.0101 | 000002246867 | 01/JAN/96
EECL | OT202588 | OP | Operational |  | 2023-11-07 | 202311 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | LV |  |  |  | 1269654 | 2024 | 23WB14302 | 2023-11-07 17:16 | 2023-11-07 16:33 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | URANGAN: GIBBS ST, HOOP WAY, MITTA WAY, RICHARD ST, TRURO ST, WILLIAM ST | Crew advised outage required to repair broken cross arm. Crew replaced LV strain arm. SL 3149290. REDACTED | Crew advised outage required to repair broken cross arm. hboc01. Time Off modified from 17:00 07-Nov to 16:31 07-Nov LV only, crew waiting on a bucket. Sending Asset Event to FFA FFA Order Created F-AE23WB14302-1-0 DfltHost FFA Order Acknowledged F-AE23WB14302-1-0 hboc01 REDACTED 0447761083 FFA Order En Route F-AE23WB14302-1-0 hboc01 FFA Order On Site F-AE23WB14302-1-0 hboc01 Crew ready to start outage. Time Off modified from 16:31 07-Nov to 17:16 07-Nov Sending Asset Event to FFA Time On modified from 18:30 07-Nov to 18:50 07-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23WB14302-1-0 Completed by technician REDACTED In crew hboc01(0447761083) with code A-F-C - Completed Action Taken : Replaced LV strain arm Site Label : 3149290 Time On modified from 18:50 07-NOV to 20:01 07-NOV Added notes to Reasons tab. | 1 | 2032871 | 26 gibbs st urangan | 1269654 | 3149290 | 2032871 | 2019-11-15 | 1453 | N |  |  | 9.5 |  | 1 | Serviceable | N | Urb unsty angle | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | GB GREY BOX | 8 kiloNewton | 1977 | -25.2868 | 152.8904 | 000002032871 | 01/JAN/77
EECL | OT202989 | OP | Operational |  | 2023-11-10 | 202311 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1050493 | 2024 | 23SW19908 | 2023-11-10 09:09 | 2023-11-10 07:48 | COMP | Completed |  | Fine | South West | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ |  | CAMBOOYA: CUDMORE RD, GREENUP RD, HENRY RD, JAMES ST, TODD RD, TOOWOOMBA-KARARA RD, WESTS RD | Crew require forced outage to replace broken strain arm on T off 2059284 | Crew require forced outage to replace broken strain arm on T off 2059284 Sending Asset Event to FFA FFA Order Created F-AE23SW19908-1-0 DfltHost Sending Asset Event to FFA twmfrcm01 Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Time Off modified from 06:31 10-Nov to 09:08 10-Nov Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW19908-1-0 twmfrcm01 REDACTED 0419256307 FFA Order En Route F-AE23SW19908-1-0 twmfrcm01 FFA Order On Site F-AE23SW19908-1-0 twmfrcm01 FFA Order F-AE23SW19908-1-0 Completed by technician REDACTED in crew twmfrcm01(0419256307) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced 11kv strain arm Site Label : 2080106 Time On modified from 23:59 10-Nov to 12:05 10-Nov | 1 | 2249868 | 185 Henry rd Cambooya | 1050493 | 2080106 | 2249868 | 2022-11-13 | 362 | N |  |  | 14 | 1 |  | Serviceable | N | Rrl sty angle 5-20o | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1981 | -27.7326 | 151.8511 | 000002249868 | 01/JAN/81
EECL | OT203466 | OP | Operational |  | 2023-11-14 | 202311 | Crossarm | Xarm, Wood Strain | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1523262 | 2024 | 23CA15862 | 2023-11-14 09:42 | 2023-11-14 08:10 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | BONDOOLA: COBRABALL RD | F-28809-g Crews need access beyond 11kV Dropout Fuse DO786704 to replace HV arm | Crews need access beyond 11kV Dropout Fuse DO786704 to replace HV arm yepcm09 Sending Asset Event to FFA FFA Order Created F-AE23CA15862-1-0 DfltHost F-28809-g FFA Order Acknowledged F-AE23CA15862-1-0 yepcm09 REDACTED 0428835839 FFA Order En Route F-AE23CA15862-1-0 yepcm09 FFA Order On Site F-AE23CA15862-1-0 yepcm09 Time Off modified from 09:00 14-Nov to 09:42 14-Nov Sending Asset Event to FFA Time On modified from 14:00 14-Nov to 13:22 14-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23CA15862-1-0 Completed by technician REDACTED in crew yepcm09(0400743458) with code A-F-C - Completed Action Taken : Replaced damaged strain crossarm - severe white rot at kingbolt, almost snapped Raised incident notification for HV lines below 5.5m over paddock (Approx 4m) due to crossarm damage Site Label : 4128180 | 1 | 3115003 | 2587 yeppoon rd yeppoon | 1523262 | 4128180 | 3115003 | 2020-01-08 | 1406 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl sty angle 5-20o | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | NI NARROW LEAF RED I | 5 kiloNewton | 1982 | -23.1662 | 150.695 | 000003115003 | 01/JAN/82
EECL | OT203898 | OP | Operational |  | 2023-11-16 | 202311 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | LV |  |  |  | 1549437 | 2024 | 23SW20229 | 2023-11-16 18:45 | 2023-11-16 18:24 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | ATHOL: SHORT RD UMBIRAM: UMBIRAM SCHOOL RD, WAINWRIGHT RD, WYREEMA ATHOL RD | Crew require access to lin to replace X-arm at TX PE06017, crew to make repairs to LV in the morning | Crew require access to lin to replace X-arm at TX PE06017 Switching Sheet ID updated from to J-286306-g. twmcm07 Sending Asset Event to FFA FFA Order Created F-AE23SW20229-1-0 DfltHost FFA Order Acknowledged F-AE23SW20229-1-0 twmcm07 REDACTED 0407646440 FFA Order En Route F-AE23SW20229-1-0 twmcm07 crew to make repairs to the LV in the morning Time On modified from 23:59 16-Nov to 10:00 17-Nov Sending Asset Event to FFA FFA Order On Site F-AE23SW20229-1-0 twmcm07 Sending Asset Event to FFA Sending Asset Event to FFA Left Message with Ben for update Sending Asset Event to FFA Time On modified from 10:00 17-Nov to 16:00 17-Nov Sending Asset Event to FFA Time On modified from 16:00 17-Nov to 21:33 16-Nov Sending Asset Event to FFA Sending Asset Event to FFA crew advised HV outage is complete but TX PE06017 LV has been isolated due defects in the switchboard and form 3 has been issued Sending Asset Event to FFA FFA Order Pending F-AE23SW20229-1-0 FFA Order Acknowledged F-AE23SW20229-1-0 twmfr05 REDACTED 0427965369 FFA Order En Route F-AE23SW20229-1-0 twmfr05 FFA Order On Site F-AE23SW20229-1-0 twmfr05 FFA Order F-AE23SW20229-1-0 Completed by technician REDACTED in crew twmfr05(0427965369) with code A-F-C - Completed Action Taken : crew replaced lv arm at transformer under outage but crew did not reenergise due to form b defects but they were re connected later that same day Site Label : 3228103 | 1 | 2507633 | PE6017, acc 309 Wyreema-Athol Rd,Umbiram | 1549437 | 3228103 | 2507633 | 2020-07-13 | 1221 | N |  |  | 14 | 4 | 2 | Serviceable | Y | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1979 | -27.6306 | 151.7867 | 000002507633 | 01/JAN/79
EECL | OT204988 | OP | Operational |  | 2023-11-23 | 202311 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1339927 | 2024 | 23WB14877 | 2023-11-23 13:22 | 2023-11-23 11:59 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | ALLOWAY: BARAZZAS RD, DR MAYS CROSSING RD, NEW FARM RD, PAYNES RD, REXS RD CALAVOS: DR MAYS CROSSING RD, WOLFENDEN RD | F-28963-g Dr Mays Feeder. Broken Cross Arm Near RG 594494 | Dr Mays Feeder. Broken Cross Arm Near RG 594494 F-28963-g Time Off modified from 12:30 23-Nov to 13:22 23-Nov Sending Asset Event to FFA FFA Order Created F-AE23WB14877-1-0 DfltHost FFA Order Acknowledged F-AE23WB14877-1-0 bndcsfr09 REDACTED 0428753577 FFA Order En Route F-AE23WB14877-1-0 bndcsfr09 FFA Order On Site F-AE23WB14877-1-0 bndcsfr09 FFA Order F-AE23WB14877-1-0 Completed by technician REDACTED in crew bndcsfr09(0428753577) with code A-F-C - Completed Action Taken : Replaced broken x-arm on S/L 3311063 - white rot in x-arm - conductors hanging at 3.1m on arrival - Retensioned to 7.6m after repairs Site Label : 3311063 Time On modified from 23:59 23-Nov to 16:04 23-Nov | 1 | 2768964 | new farm rd/dr mays crossing rd calavos | 1339927 | 3311063 | 2768964 | 2020-12-17 | 1071 | N |  |  | 14 | 1 |  | Serviceable | N | Rrl unsty trm 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Railway Reserve | SG SPOTTED GUM | 12 kiloNewton | 1982 | -24.9426 | 152.4005 | 000002768964 | 01/JAN/82
EECL | OT205870 | OP | Operational |  | 2023-11-28 | 202311 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | LV |  |  |  | 1562977 | 2024 | 23SW20882 | 2023-11-28 19:15 | 2023-11-28 19:21 | COMP | Completed |  | Wet / Rain | South West | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FC |  | DALBY: ALFRED ST, CONDAMINE ST, COXEN ST, CUNNINGHAM ST, FORTESCUE ST, MORETON ST, MORRIS ST, PRATTEN ST, WOOD ST | Fault calls indicate problem at 11kV Pole Dist Sub PC01217. Lines down report 28 Wood St | Fault calls indicate problem at 11kV Pole Dist Sub PC01217. Lines down report 28 Wood St AHC advised dlbloc01 Sending Asset Event to FFA FFA Order Created F-AE23SW20882-1-0 DfltHost Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW20882-1-0 dlbloc01 REDACTED 0438751501 FFA Order En Route F-AE23SW20882-1-0 dlbloc01 FFA Order On Site F-AE23SW20882-1-0 dlbloc01 Asset selection modified Sending Asset Event to FFA FFA Order En Route F-AE23SW20882-1-0 dlbloc01 FFA Order On Site F-AE23SW20882-1-0 dlbloc01 Time On modified from 23:59 28-Nov to 23:55 28-Nov Sending Asset Event to FFA FFA Order F-AE23SW20882-1-0 Completed by technician REDACTEDin crew DLBLOC01(0438751501) with code A-T-317 - Severe Weather Action Taken : Bottom LV twin strain crossarm has broken. leaving conductors hanging low to ground held by bridging. replaced arm SL 3230209 Site Label : 3230209 auto-completed | 1 | 2521424 | CNR CONDAMINE AND WOOD STS DALBY | 1562977 | 3230209 | 2521424 | 2020-06-22 | 1254 | N |  |  | 11 |  | 4 | Serviceable | Y | LV fully suppd | WOOD UNTREATED ROUND | Lawn | Footpath | ZZ NO DISC - UNKNOWN | Unknown |  | -27.1864 | 151.2564 | 000002521424 | 01/JAN/54
EECL | OT206283 | OP | Operational |  | 2023-11-30 | 202311 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | LV |  |  |  | 1871841 | 2024 | 23NQ14202 | 2023-11-30 12:16 | 2023-11-30 12:35 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | LV-Conductor Connection Failure | Operational Incident | due to damage requiring emergency repairs. | GT |  | BOWEN: DENISON ST, HILL ST, JOHN ST, LEICHHARDT ST, PILCHER PL, SUNSET CRES, WEST ST | Multiple calls of LOS from 11kV Pole Dist Sub BNS224 | Multiple calls of LOS from 11kV Pole Dist Sub BNS224 Sending Asset Event to FFA FFA Order Created F-AE23NQ14202-1-0 DfltHost FFA Order Acknowledged F-AE23NQ14202-1-0 bwncs03 REDACTED 0418739194 FFA Order En Route F-AE23NQ14202-1-0 bwncs03 FFA Order On Site F-AE23NQ14202-1-0 bwncs03 Restoration Comments for F-AE23NQ14202-1-0 by bwncs03: broken Lv crossarm. isolated all Lv at transformer. new crossarm required FFA Order Pending F-AE23NQ14202-1-0 FFA Order Acknowledged F-AE23NQ14202-1-0 bwnoh03 REDACTED 0437768581 FFA Order En Route F-AE23NQ14202-1-0 bwnoh03 FFA Order On Site F-AE23NQ14202-1-0 bwnoh03 FFA Order F-AE23NQ14202-1-0 Completed by technician REDACTED in crew bwnoh03(0437768581) with code A-T-309 - LV-Conductor Connection Failure Action Taken : Lv x-arm broke. replaced arm and damaged bridging Site Label : 5065414 Time On modified from 23:59 30-NOV to 16:15 30-NOV | 1 | 2820446 | cnr john st /sunset crescent bowen | 1871841 | 5065414 | 2820446 | 2023-11-14 | 16 | N |  |  | 12.5 | 1 | 2 | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 8 kiloNewton | 1981 | -20.0034 | 148.2332 | 000002820446 | 01/JAN/81
EECL | OT201460 | OP | Operational |  | 2023-11-01 | 202311 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 757633 | 2024 | 23WB14128 | 2023-11-01 16:52 | 2023-11-01 16:21 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | ELLESMERE, HALY CREEK, KINGAROY | F-526-j 11kV Disc Links S6063 - Opened due to broken cross arm | 11kV Disc Links S6063 - Opened due to broken cross arm Time On modified from 23:59 01-Nov to 19:00 01-Nov Time On modified from 19:00 01-Nov to 19:30 01-Nov Time Off modified from 16:30 01-Nov to 16:52 01-Nov Time On modified from 19:30 01-Nov to 18:13 01-Nov | 1 | 2309891 | 596 stuart valley dr haly ck | 757633 | 2097728 | 2309891 | 2022-12-05 | 331 | N |  |  | 11 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | RG ROSE GUM | 5 kiloNewton | 1983 | -26.6445 | 151.7593 | 000002309891 | 01/JAN/83
EECL | OT205416 | OP | Operational |  | 2023-11-26 | 202311 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Termites |  | 11kV |  |  |  | 934992 | 2024 | 23NQ13973 | 2023-11-26 13:01 | 2023-11-26 13:03 | COMP | Completed |  | Wet / Rain | North Queensland | Unplanned Outage | Animal Insects (termites/borers/white ants) | Fallen Power Lines | due to fallen power lines. | FE |  | BROUGHTON, CHARTERS TOWERS, CHARTERS TOWERS CITY | F-2329-s CHART TWRS 11kV CT04 Fdr CB D252 tripped. SCADA Interface automated outage. | entered from the SCADA Interface F-2329-s Issued to REDACTED 0418 773 095, chtwgo01. Sending Asset Event to FFA FFA Order Created F-AE23NQ13973-1-0 DfltHost Depot Co-ord Advised Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ13973-1-0 chtwgo01 REDACTED 0418773095 FFA Order En Route F-AE23NQ13973-1-0 chtwgo01 FFA Order On Site F-AE23NQ13973-1-0 chtwgo01 Crew to patrol last section around Hospital and if Clear will attemot to backfeed from CHTO 05 Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Crew adv patrolled beyond LB791807 & successfull reclose at RMU SZ791799. Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Crews now attending to lines down near CTS966, beyond ACR Plumtree Ck No.3. HV Wires Down Reason for Event changed from Unknown Sending Asset Event to FFA Restored up to & isolated at LKS Gladstone Ck No.2 via ACR Plumtree Ck No.3 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 26-Nov to 18:30 26-Nov Sending Asset Event to FFA FFA Order F-AE23NQ13973-1-0 Completed by technician REDACTED in crew Chtwgo01(0418773095) with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : replace 11kv xarm eaten from white ants Site Label : 2068647 Time On modified from 18:30 26-Nov to 16:57 26-Nov auto-completed | 1 | 2200092 | 30 dunroamin rd ch towers | 934992 | 2068647 | 2200092 | 2021-02-26 | 1003 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | BB BLACKBUTT | 8 kiloNewton | 1995 | -20.0357 | 146.3117 | 000002200092 | 01/JAN/95
EECL | OT205602 | OP | Operational |  | 2023-11-27 | 202311 | Crossarm | Xarm, Wood Intermediate | Broken | Termites |  | 11kV |  |  |  | 1730775 | 2024 | 23NQ14044 | 2023-11-27 14:50 | 2023-11-27 14:53 | COMP | Completed |  | Wet / Rain | North Queensland | Unplanned Outage | Animal Insects (termites/borers/white ants) | Protective Device Operated | due to the operating of protective equipment. | FC |  | RYAN, SUNSET | F-2335-s - DUCHESS RD 11kV Sunset Dr No.1 ACR CB tripped on OC - 2 x trip to lockout | entered from the SCADA Interface Sending Asset Event to FFA FFA Order Created F-AE23NQ14044-1-0 DfltHost Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ14044-1-0 mtioc01 REDACTED 0437715949 Time On modified from 23:59 27-Nov to 20:00 27-Nov Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 20:00 27-Nov to 18:55 27-Nov Sending Asset Event to FFA FFA Order En Route F-AE23NQ14044-1-0 mtioc01 FFA Order On Site F-AE23NQ14044-1-0 mtioc01 FFA Order F-AE23NQ14044-1-0 Completed by technician REDACTED in crew MTIOC01(0437715949) with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : replaced broken crossarm Site Label : 5023883 auto-completed | 1 | 2578919 | 1 past Sub347 sports pde mt isa | 1730775 | 5023883 | 2578919 | 2022-03-06 | 631 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | GB GREY BOX | 12 kiloNewton | 2005 | -20.704 | 139.5145 | 000002578919 | 01/JAN/05
EECL | OT205843 | OP | Operational |  | 2023-11-28 | 202311 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1859712 | 2024 | 23NQ14070 | 2023-11-27 18:43 | 2023-11-27 19:28 | ANAL | Data verification |  | Storm Electrical | North Queensland | Unplanned Outage | VEG: Rural clearing clashed conductors | Unknown | due to damage requiring emergency repairs. Fault finding is in progress. | ZS |  | RAVENSWOOD: BURDEKIN DAM RD | F-2342-s BUDA - B252 Tripped to lockout on OC. Crew to patrol. | B252 Tripped to lockout on OC Crew advised due to weather and distance will patrol in the morning Time On modified from 23:59 27-Nov to 15:00 28-Nov Sending Asset Event to FFA FFA Order Created F-AE23NQ14070-1-0 DfltHost . Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Crews have flown lines. Tress growing up through 11kV at 5049847. Crews are heading out to clear trees but access is difficult Sending Asset Event to FFA Backhoe heading out for an outage tomorrow so may need to be delayed and done tomorrow if they can't get access today Sending Asset Event to FFA Crews still making repairs Time On modified from 15:00 28-Nov to 16:00 28-Nov Sending Asset Event to FFA Crew still making repairs Time On modified from 16:00 28-Nov to 18:00 28-Nov Sending Asset Event to FFA Crews will return tomorrow 29/11/2023 to complete repairs Time On modified from 18:00 28-Nov to 15:00 29-Nov Sending Asset Event to FFA Sending Asset Event to FFA Repairs completed. Customers are off under planned outage 23NQ13365. Supply to be restored on reversal of planned outage Time On modified from 15:00 29-Nov to 09:15 29-Nov Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ14070-1-0 chtwgo01 REDACTED 0418773095 FFA Order En Route F-AE23NQ14070-1-0 chtwgo01 FFA Order On Site F-AE23NQ14070-1-0 chtwgo01 FFA Order F-AE23NQ14070-1-0 Completed by technician REDACTED in crew Chtwgo01(0418773095) with code A-T-328 - VEG: Rural clearing clashed conductors Action Taken : replaced xarm after tree trimming from feeder fault trip from trees in lines Site Label : 5049847 | 1 | 2728610 | 4spns Wof burdekin dam rd burdekin dam | 1859712 | 5049847 | 2728610 | 2020-08-09 | 1206 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Soil | Inaccessible to heavy vehicles | SG SPOTTED GUM | 5 kiloNewton | 1987 | -20.6286 | 147.1431 | 000002728610 | 01/JAN/87
EECL | OT203657 | OP | Operational |  | 2023-11-15 | 202311 | Crossarm | Xarm, Wood Dressing | Broken | Rot/Decay |  | 11kV |  |  |  | 1507288 | 2024 | 23SW20163 | 2023-11-15 15:24 | 2023-11-15 15:09 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | DEVON PARK: SCHULLS RD | F-2139-q - crew require access to replace broken bridging arm | crew require access to replace broken bridging arm Time Off modified from 15:20 15-Nov to 15:24 15-Nov Time On modified from 23:59 15-Nov to 16:37 15-Nov Sending Asset Event to FFA FFA Order Created F-AE23SW20163-1-0 DfltHost TWMFRCM01 Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW20163-1-0 twmfrcm01 REDACTED 4292345642 FFA Order En Route F-AE23SW20163-1-0 twmfrcm01 FFA Order On Site F-AE23SW20163-1-0 twmfrcm01 FFA Order F-AE23SW20163-1-0 Completed by technician REDACTED in crew twmfrcm01(04292345642) with code A-F-C - Completed Action Taken : replaced broken bridging arm Site Label : 3090346 Time On modified from 16:37 15-NOV to 16:51 15-NOV FFA Order F-AE23SW20163-1-0 Completed by technician REDACTED In crew twmfrcm01(04292345642) with code A-F-C - Completed Action Taken : replaced broken bridging arm Site Label : 3090346 Time On modified from 16:37 15-NOV to 16:51 15-NOV FFA Order F-AE23SW20163-1-0 Completed by technician REDACTED in crew twmfrcm01(04292345642) with code A-F-C - Completed Action Taken : replaced broken bridging arm Site Label : 3090346 Time On modified from 16:37 15-NOV to 16:51 15-NOV | 1 | 2936047 | Tx, acc 48 Schulls Rd,Oakey | 1507288 | 3090346 | 2936047 | 2023-10-26 | 20 | N |  |  | 14 | 5 | 3 | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass |  | SG SPOTTED GUM | 12 kiloNewton | 1985 | -27.3764 | 151.6903 | 000009389305
EECL | OT203972 | OP | Operational |  | 2023-11-17 | 202311 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 727374 | 2024 | [23 empty] | 2023-11-17 | 0 | [6 empty] | Serviceable | N | HV fully suppd | WOOD UNTREATED ROUND | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | Unknown |  |  |  | 000005686791 | 01/JAN/51
EECL | OT208457 | OP | Operational |  | 2023-12-11 | 202312 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 22kV |  |  |  | 1728601 | 2024 | 23CA17382 | 2023-12-11 10:10 | 2023-12-11 10:12 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE |  | ALPHA | F-29223-g 22kV Recloser RC880475 opened do to low wire found Crew replaced broken cross-arm. SL 2000846. REDACTED | 22kV Recloser RC880475 openned do to low wire found Sending Asset Event to FFA FFA Order Created F-AE23CA17382-1-0 DfltHost Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 11-Dec to 16:38 11-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA17382-1-0 brccmfr02 REDACTED 0427033585 FFA Order En Route F-AE23CA17382-1-0 brccmfr02 FFA Order On Site F-AE23CA17382-1-0 brccmfr02 FFA Order F-AE23CA17382-1-0 Completed by technician REDACTED in crew brccmfr02(0427033585) with code A-F-C - Completed Action Taken : replace broken xarm Site Label : 2000846 Actual Power Restoration for F-AE23CA17382-1-0: 11-DEC-2023 16:01:00 Added notes to Reasons tab. | 1 | 2015809 | 3 Pls W X1977 54 Byron St Alpha | 1728601 | 2000846 | 2015809 | 2021-09-05 | 827 | N |  |  | 14 | 2 |  | Serviceable | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | Unknown |  | -23.6492 | 146.6289 | 000002015809 | 01/JAN/68
EECL | OT207885 | OP | Operational |  | 2023-12-07 | 202312 | Crossarm | Xarm, Wood Dressing | Broken | Rot/Decay |  | 11kV |  |  |  | 1771605 | 2024 | 23NQ14485 | 2023-12-07 07:22 | 2023-12-07 07:52 | COMP | Completed |  | Wind | North Queensland | Unplanned Outage | Distribution substation | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ |  | HELENS HILL: FONTANAS RD | F-2449-s Broken cross arm on INS1191 | Broken cross arm on INS1191 Sending Asset Event to FFA FFA Order Created F-AE23NQ14485-1-0 DfltHost FFA Order Acknowledged F-AE23NQ14485-1-0 ingcsfr01 REDACTED 0473145674 FFA Order En Route F-AE23NQ14485-1-0 ingcsfr01 FFA Order On Site F-AE23NQ14485-1-0 ingcsfr01 Restoration Comments for F-AE23NQ14485-1-0 by ingcsfr01: tranny was isolated initially at the edos to make safe Time On modified from 23:59 07-Dec to 10:00 07-Dec Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23NQ14485-1-0 Completed by technician REDACTED in crew ingcsfr01(0473145674) with code A-T-303 - Distribution substation Action Taken : broken HV bridging arm. Isolated and replaced Site Label : 2042612 auto-completed | 1 | 2118776 | end of fontanas rd helen hill | 1771605 | 2042612 | 2118776 | 2020-12-16 | 1086 | N |  |  | 12.5 | 2 |  | Serviceable | Y | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Front Yard | ZZ NO DISC - UNKNOWN | 12 kiloNewton |  | -18.7534 | 146.1329 | 000002118776 | 01/JAN/95
EECL | OT206429 | OP | Operational |  | 2023-12-01 | 202312 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1243462 | 2024 | 23WB15136 | 2023-12-01 08:15 | 2023-12-01 15:38 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 452 BOUGHTONS RD;BUCCA QLD 4670 | Fault occurred at:01/12/2023 05:37; REDACTED, 0422071594;>WDPB --> HasComeAway:UNSURE,AffectingTraffic:NO -- StillHavePower:YES<;Incident Details:very low service line at property, line is low enough to reach; possible damage at top of pole, unsure if property pole or Ergon pole; cust adv cross arm appears rotten; power still working;;COVID-19:UNKNOWN;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N |  | 1 | 2218059 | 452 boughtons rd avondale | 1243462 | 2071192 | 2218059 | 2019-05-22 | 1654 | N |  |  | 11 |  | 1 | Serviceable | Y | Urb service pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Front Yard | SG SPOTTED GUM | 8 kiloNewton | 1985 | -24.7868 | 152.101 | 000002218059 | 01/JAN/85
EECL | OT207124 | OP | Operational |  | 2023-12-04 | 202312 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 779597 | 2024 | 23WB15096 | 2023-11-30 13:39 | 2023-11-30 13:45 | COMP | Completed |  | Fine | Wide Bay | Unplanned Outage | Lightning | Fallen Power Lines | due to fallen power lines. | GT |  | TANSEY: BURNETT HWY | Crew report LV X-Arm broken wire on the ground, need LV isolation @11kV Pole Dist Sub 14117 | Crew report LV X-Arm broken wire on the ground, need LV isolation @11kV Pole Dist Sub 14117 mrgcm02 Sending Asset Event to FFA FFA Order Created F-AE23WB15096-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 30-Nov to 17:00 30-Nov Sending Asset Event to FFA mrgcm01 REDACTED 0428 071 189 Time On modified from 17:00 30-Nov to 18:00 30-Nov Sending Asset Event to FFA REDACTED Time On modified from 18:00 30-Nov to 17:50 30-Nov Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23WB15096-1-0 mrgcm01 REDACTED 0428071189 FFA Order En Route F-AE23WB15096-1-0 mrgcm01 FFA Order On Site F-AE23WB15096-1-0 mrgcm01 FFA Order F-AE23WB15096-1-0 Completed by technician REDACTED in crew mrgcm01(0428071189) with code A-T-311 - LV-Unassisted failure(Apparent defect) Action Taken : arm broken and replaced Site Label : 3189439 Time On modified from 17:50 30-NOV to 15:11 05-DEC | 1 | 2246867 | acc 8149 Burnett hwy, Tansey. rear pad' | 779597 | 3189439 | 2246867 | 2021-06-29 | 888 | N |  |  | 12.5 |  | 1 | Serviceable | Y | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Irrigation | SG SPOTTED GUM | 5 kiloNewton | 1996 | -26.018 | 152.0101 | 000002246867 | 01/JAN/96
EECL | OT206952 | OP | Operational |  | 2023-12-03 | 202312 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1499702 | 2024 | 23SW21389 | 2023-12-03 10:21 | 2023-12-03 08:32 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | GOOMBUNGEE: CENTENARY RD, GOOMBUNGEE-MT DARRY RD, LEBSANFTS RD, PECHEY MACLAGAN RD, RUMMELLS RD KILBIRNIE: GOOMBUNGEE KILBURNIE RD, GOOMBUNGEE MOUNT DARRY RD, MT DARRY RD | 11kV Gas Switch AB19535, Outage required to replace HV strain arm at SL 2080694 | 11kV Gas Switch AB19535, Outage required to replace HV strain arm at SL 2080694 Time Off modified from 08:45 03-Dec to 10:21 03-Dec Time On modified from 23:59 03-Dec to 18:00 03-Dec Time On modified from 18:00 03-Dec to 12:43 03-Dec | 1 | 2254279 | opp3s 93 LEBSANFTS RD goombungee | 1499702 | 2080694 | 2254279 | 2019-11-29 | 1465 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1968 | -27.2891 | 151.8196 | 000002254279 | 01/JAN/68
EECL | OT211058 | OP | Operational |  | 2023-12-20 | 202312 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 766433 | 2024 | 23NQ15009 | 2023-12-20 15:42 | 2023-12-20 15:46 | COMP | Completed |  | Hot | North Queensland | Unplanned Outage | Service Asset Fault | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FE |  | BROUGHTON | F-2680-s Suspect HV Fuses at Bus Rd No.2 have blown. REDACTED called to advise broken cross arm and 11kV twisted together near CTS 750, and low HV across a driveway close by. Opened up Woodchopper Rd No.1 for safety | Suspect HV Fuses at Bus Rd No.2 havce blown. REDACTED called to advise broken cross arm and 11kV twisted together near CTS 750, and low HV across a driveway close by. Opened up Woodchopper Rd No.1 for safety REDACTED Asset selection modified broken xarm on 2153915 Time On modified from 23:59 20-Dec to 19:00 20-Dec Sending Asset Event to FFA FFA Order Created F-AE23NQ15009-1-0 DfltHost FFA Order Acknowledged F-AE23NQ15009-1-0 chtcs07 REDACTED 0428161062 FFA Order En Route F-AE23NQ15009-1-0 chtcs07 FFA Order On Site F-AE23NQ15009-1-0 chtcs07 Asset selection modified Sending Asset Event to FFA Time On modified from 19:00 20-Dec to 18:39 20-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23NQ15009-1-0 Completed by technician REDACTED in crew chtcs07(0428161062) with code A-T-315 - Service Asset Fault Action Taken : isolated line replaced broken cross arm Site Label : 2153915 auto-completed | 1 | 2404906 | 308 Bus Rd Charters Towers | 766433 | 2153915 | 2404906 | 2021-11-29 | 751 | N |  |  | 12.5 | 2 |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | BI BROAD LEAF IRONBARK | 8 kiloNewton | 1990 | -20.152 | 146.3204 | 000002404906 | 01/JAN/90
EECL | OT207822 | OP | Operational |  | 2023-12-06 | 202312 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1628368 | 2024 | 23SW21528 | 2023-12-06 16:57 | 2023-12-06 16:23 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | STORM KING: EUKEY RD, NIELSENS RD, OBRIEN LANE, PYRAMIDS RD, SHATTE LANE | F-1482-r Fault Call For Broken Cross arm Between PE04997 and PE04996 | Fault Call For Broken Cross arm Between PE04997 and PE04996 Time Off modified from 17:00 06-Dec to 16:57 06-Dec Time On modified from 23:59 06-Dec to 18:22 06-Dec | 1 | 2423161 | South of 632 eukey rd stanthorpe | 1628368 | 3214339 | 2423161 | 2021-09-20 | 807 | N |  |  | 14 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | IB IRONBARK | 3 kiloNewton | 1974 | -28.7274 | 151.9817 | 000002423161 | 01/JAN/74
EECL | OT207715 | OP | Operational |  | 2023-12-06 | 202312 | Crossarm | Xarm, Wood Strain | Deteriorated | Termites |  | LV |  |  |  | 1109709 | 2024 | 23SW21510 | 2023-12-06 14:58 | 2023-12-06 12:23 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | CHINCHILLA: BELL ST, BLANCHARD ST, CONDAMINE ST, FIRST AVE, GORMLEYS RD, HEENEY ST, HELENA ST, HYPATIA ST, MIDDLE ST | LV Cross Arm Broken requiring Forced Outage of 11kV Pole Dist Sub PC01127 and 11kV Ground Dist Sub GC588690 Crew replaced cross-arm that broke due to termites. SL 3217933. REDACTED | LV Cross Arm Broken requiring Forced Outage of 11kV Pole Dist Sub PC01127 and 11kV Ground Dist Sub GC588690 REDACTED 0467 721 443 Sending Asset Event to FFA FFA Order Created F-AE23SW21510-1-0 DfltHost CHNFR01 Sending Asset Event to FFA Sending Asset Event to FFA Time Off modified from 15:00 06-Dec to 14:58 06-Dec Sending Asset Event to FFA REDACTED 0467 721 443 Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW21510-1-0 chnfr01 REDACTED 0428776314 FFA Order En Route F-AE23SW21510-1-0 chnfr01 FFA Order On Site F-AE23SW21510-1-0 chnfr01 1652 restored Time On modified from 18:00 06-Dec to 16:52 06-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23SW21510-1-0 Completed by technician REDACTED in crew chnfr01(0428776314) with code A-F-C - Completed Action Taken : broken arm due to termites replaced Site Label : 3217933 Added notes to Reasons tab. | 1 | 2442644 | cnrMiddle/Helena st Chinchilla | 1109709 | 3217933 | 2442644 | 2021-12-15 | 721 | N |  |  | 12.5 | 3 | 3 | Serviceable | Y | HV fully suppd | WOOD UNTREATED ROUND | Concrete Pre Cut | Footpath | ZZ NO DISC - UNKNOWN | Unknown |  | -26.7402 | 150.622 | 000002442644 | 01/JAN/51
EECL | OT211308 | OP | Operational |  | 2023-12-18 | 202312 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | LV |  |  |  | 1303623 | 2024 | 23FN16552 | 2023-12-13 16:07 | 2023-12-20 17:36 | COMP | Completed | M |  | Far North | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FE |  | JULATTEN: CLACHERTY RD | SS5428 event extracted from 23FN15867 SS5428, LV TX isolation open and DNOB due to LV open wire down, Broken LV x-arm | Event extracted from 23FN15867 SS5428, LV TX isolation open and DNOB due to LV open wire down, Broken LV x-arm LV Wires Down Crews advised outage on SS761388 LV only to make repairs as it involves the open point between subs. REDACTED 0455 541 674 Asset selection modified confirm ok to energise please send to MBACO19 Assets extracted from SS761388 (Clacherty Rd) into event 23FN16617 FFA Order F-AE23FN16617-1-0 Completed by technician REDACTED in crew mbaco19(0409300987) with code A-F-C - Completed Action Taken : replaced LV Xarms at SL 5005370. Site Label : 5005370 Time On modified from 19:00 23-DEC to 19:41 21-DEC Time On modified from 19:00 23-Dec to 19:41 21-Dec | 1 | 2467604 | 219 CLACHERTY RD JULATTEN | 1303623 | NO1 | 2467604 | 2022-07-19 | 517 | N |  |  | 14 | 4 | 3 | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZR UNKNOWN RED SPECI | 12 kiloNewton | 1988 | -16.5759 | 145.3647 | 000002467604 | 01/JAN/88
EECL | OT211094 | OP | Operational |  | 2023-12-20 | 202312 | Crossarm | Xarm, Wood Intermediate | Split | Rot/Decay |  | 22kV |  |  |  | 1080236 | 2024 | 23FN16530 | 2023-12-20 13:34 | 2023-12-20 13:37 | COMP | Completed |  |  | Far North | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | ST |  | MANUNDA, WESTCOURT | F-2676-s Fdr open due to broken cross arm on 5015389, REDACTED advise of the fault | Fdr open due to broken cross arm on 5015389, REDACTED advise of the fault Time Off modified from 14:36 20-Dec to 13:34 20-Dec please dispatch to cnsoc03 Sending Asset Event to FFA FFA Order Created F-AE23FN16530-1-0 DfltHost Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN16530-1-0 cnsoc03 REDACTED 0428665969 FFA Order En Route F-AE23FN16530-1-0 cnsoc03 FFA Order On Site F-AE23FN16530-1-0 cnsoc03 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 20-Dec to 16:16 20-Dec Sending Asset Event to FFA FFA Order F-AE23FN16530-1-0 Completed by technician REDACTED in crew cnsoc03(0428665969 ) with code A-F-C - Completed Action Taken : Replace hv pin arm Site Label : 5017426 auto-completed | 1 | 2535070 | 263 AUMULLER ST MANUNDA | 1080236 | GMT4S | 2535070 | 2022-10-13 | 433 | N |  |  | 11 |  |  | Serviceable | Y | Urb LV ABC inter | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 8 kiloNewton | 2013 | -16.9266 | 145.755 | 000002535070 | 01/JAN/13
EECL | OT211689 | OP | Operational |  | 2023-12-22 | 202312 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 22kV |  |  |  | 1124420 | 2024 | 23FN16653 | 2023-12-22 13:01 | 2023-12-22 17:01 | COMP | Completed |  | Wet / Rain | Far North | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | LOT 101 UPPER DARADGEE RD;UPPER DARADGEE QLD 4860 | Fault occurred at:22/12/2023 12:57; REDACTED, 0427633816;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details:Cross arm broken and power lines hanging, insulator pulled out - HV wires. POLE 5027714;Access Details:Pole on roadside. Clear access.;COVID-19:N/A;Warnings[uphSafety]: ADVISED;Sensitive Load:N |  | 1 | 2604006 | 3spn S of 265 Upper Daragee rd Daragee | 1124420 | B2.43 | 2604006 | 2021-03-09 | 1018 | N |  |  | 12.5 | 4 | 1 | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1985 | -17.5155 | 145.9787 | 000002604006 | 01/JAN/85
EECL | OT210538 | OP | Operational |  | 2023-12-18 | 202312 | Crossarm | Xarm Bracket Nuts | Loose Fitting | Vibration |  | 11kV |  |  |  | 1541950 | 2024 | 23SW22089 | 2023-12-18 18:59 | 2023-12-18 17:52 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | FELTON SOUTH: CLIFTON PITTSWORTH RD, TOOWOOMBA-KARARA RD PITTSWORTH: CLIFTON RD | F-2418-q 11kV Disc Links DL8591, Outage required to replace broken cross-arm at SL 3032480 | 11kV Disc Links DL8591, Outage required to replace broken cross-arm at SL 3032480 F-2418-q Coord request upstream Recloser RC856855 be tripped until crew arrives to make safe Asset selection reset Asset selection reset Asset selection reset Asset selection reset Asset selection modified Asset selection modified Asset selection reset Asset selection modified Time Off modified from 18:15 18-Dec to 18:59 18-Dec Asset selection modified Time On modified from 23:59 18-Dec to 21:14 18-Dec Sending Asset Event to FFA FFA Order Created F-AE23SW22089-1-0 DfltHost FFA Order Acknowledged F-AE23SW22089-1-0 twmoc02 REDACTED 429859851 FFA Order En Route F-AE23SW22089-1-0 twmoc02 FFA Order On Site F-AE23SW22089-1-0 twmoc02 FFA Order F-AE23SW22089-1-0 Completed by technician REDACTED in crew twmoc02(0429859851) with code A-F-C - Completed Action Taken : coach screw fell out of arm braces causing cross arm to wind will, isolated, earthed and made safe, then replaced cross arm and restored power Site Label : 3032480 | 1 | 2666734 | acc 1723 Clifton-Pittsworth Rd,Felton | 1541950 | 3032480 | 2666734 | 2023-03-07 | 286 | N |  |  | 15.5 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Crop | SG SPOTTED GUM | 8 kiloNewton | 1969 | -27.8758 | 151.7064 | 000002666734 | 01/JAN/69
EECL | OT208431 | OP | Operational |  | 2023-12-11 | 202312 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | LV |  |  |  | 1497175 | 2024 | 23SW21710 | 2023-12-11 12:00 | 2023-12-11 11:56 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | RANGEVILLE: ALDERLEY ST, EVONRISE ST, HIGH ST, LOVEDAY ST, OTT ST, STOCKWELL ST | LV Only- Crew require LV outage on 11kV Pole Dist Sub PE00686 Due to broken crossarm. Customers on Loveday St are affected. Crew replaced LV strain arm. SL 3257331. REDACTED | LV Only- Crew require LV outage on 11kV Pole Dist Sub PE00686 Due to broken crossarm. Customers on Loveday St are affected. Time Off modified from 12:15 11-Dec to 12:00 11-Dec twmfrsl01 REDACTED- 0418712115 Sending Asset Event to FFA FFA Order Created F-AE23SW21710-1-0 DfltHost Sending Asset Event to FFA crew require more time due to difficulties Time On modified from 14:00 11-Dec to 16:00 11-Dec Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW21710-1-0 twmfrsl01 REDACTED 0418712115 FFA Order En Route F-AE23SW21710-1-0 twmfrsl01 FFA Order On Site F-AE23SW21710-1-0 twmfrsl01 Restoration Comments for F-AE23SW21710-1-0 by twmfrsl01: replaced broken lv strain arm Time On modified from 16:00 11-Dec to 16:30 11-Dec Sending Asset Event to FFA Time On modified from 16:30 11-Dec to 17:00 11-Dec Sending Asset Event to FFA Time On modified from 17:00 11-Dec to 16:40 11-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23SW21710-1-0 Completed by technician REDACTED in crew twmfrsl01(0418712115) with code A-F-C - Completed Action Taken : replaced lv strain arm Site Label : 3257331 Time On modified from 16:40 11-DEC to 16:40 11-DEC Added notes to Reasons tab. | 1 | 2682536 | opp 42 loveday street toowoomba | 1497175 | 3257331 | 2682536 | 2022-03-07 | 644 | N |  |  | 11 |  | 1 | Serviceable | N | Urb LV inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | SG SPOTTED GUM | 5 kiloNewton | 1968 | -27.5867 | 151.9766 | 000002682536 | 01/JAN/68
EECL | OT209374 | OP | Operational |  | 2023-12-15 | 202312 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1140327 | 2024 | 23FN15989 | 2023-12-15 07:19 | 2023-12-15 07:21 | COMP | Completed |  |  | Far North | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | SZ |  | HULL HEADS, LOWER TULLY, ROCKINGHAM, TULLY HEADS | 22kV Recloser Pole LT2 Opened for safety Lines Down FC 2385489 | 22kV Recloser Pole LT2 Opened for safety Lines Down FC 2385489 Time Off modified from 10:00 15-Dec to 07:19 15-Dec crew attending REDACTED Crew have made safe and isolated sub ss6739 Asset selection modified Sending Asset Event to FFA FFA Order Created F-AE23FN15989-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN15989-1-0 tlyfr01 REDACTED 0427627604 FFA Order En Route F-AE23FN15989-1-0 tlyfr01 FFA Order On Site F-AE23FN15989-1-0 tlyfr01 FFA Order F-AE23FN15989-1-0 Completed by technician REDACTED in crew tlyfr01(0427627604) with code A-F-C - Completed Action Taken : Replaced Lv termination arm Site Label : 5056724 Actual Power Restoration for F-AE23FN15989-1-0: 15-DEC-2023 09:00:00 Time On modified from 23:59 15-Dec to 09:00 15-Dec | 1 | 2771279 | 86 vipiana dr tully heads | 1140327 | VIP12 | 2771279 | 2022-10-18 | 423 | N |  |  | 14 | 3 | 2 | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1993 | -18.0095 | 146.0499 | 000002771279 | 01/JAN/93
EECL | OT207869 | OP | Operational |  | 2023-12-07 | 202312 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1436732 | 2024 | 23MK9712 | 2023-12-07 00:59 | 2023-12-07 01:02 | COMP | Completed |  | Fine | Mackay | Unplanned Outage | Service Asset Fault | Unknown | due to a SCADA Automated Event | FC |  | OWENS CREEK: OWENS CREEK RD FINCH HATTON: GORGE RD, PRIMROSES RD, THURGOODS RD, WILSONS PADDOCK RD, OWENS CREEK LOOP RD FINCH HATTON GORGE: ARGENTS RD, JOHNSTONS RD, VAN HOUWENINGE RD | F-2447-s - PINNACLE 11kV Gorge Rd RC616412 ACR CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface EF trip to lockout F-2447-s. Sending Asset Event to FFA FFA Order Created F-AE23MK9712-1-0 DfltHost Sending Asset Event to FFA Broken crossarm found between Sub 8053 & tee-off pole 4130142. Isolation required at LKS161. Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA FFA Order Acknowledged F-AE23MK9712-1-0 mckoc01 REDACTED 0409913086 FFA Order En Route F-AE23MK9712-1-0 mckoc01 FFA Order On Site F-AE23MK9712-1-0 mckoc01 Time On modified from 23:59 07-Dec to 06:20 07-Dec Sending Asset Event to FFA FFA Order F-AE23MK9712-1-0 Completed by technician REDACTED in crew mckoc01(0409913086) with code A-T-315 - Service Asset Fault Action Taken : replaced broken 11kv pin xarm at pole 4106909 Site Label : 4106909 auto-completed | 1 | 2990457 | 1 pole west of sub8053 kowari-gorge rd | 1436732 | 4106909 | 2990457 | 2020-04-26 | 1320 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | SG SPOTTED GUM | 5 kiloNewton | 1993 | -21.1322 | 148.6131 | 000002990457 | 01/JAN/93
EECL | OT208793 | OP | Operational |  | 2023-12-12 | 202312 | Crossarm | Xarm, Wood Termination | Split | Rot/Decay |  | 11kV |  |  |  | 982201 | 2024 | 23WB15657 | 2023-12-12 18:21 | 2023-12-12 20:33 | COMP | Completed |  | Fine | Wide Bay | Unplanned Outage | HV-Conductor Connection Failure | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ |  | COOYAR, KOORALGIN, MOUNT BINGA, UPPER YARRAMAN | 11kV Recloser S3591 - Outage required from ACR to repair lines | 11kV Recloser S3591 - Outage required from ACR to repair lines yrmcs01 Sending Asset Event to FFA FFA Order Created F-AE23WB15657-1-0 DfltHost Asset selection modified Sending Asset Event to FFA 2052: S3591 - Open Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 12-Dec to 21:56 12-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23WB15657-1-0 yrmcs01 FFA Order En Route F-AE23WB15657-1-0 yrmcs01 FFA Order On Site F-AE23WB15657-1-0 yrmcs01 FFA Order F-AE23WB15657-1-0 Completed by technician REDACTED in crew yrmcs01() with code A-T-304 - HV-Conductor Connection Failure Action Taken : hv reterminated Site Label : 3118277 | 1 | 3067293 | tx 1882 on SANDERS RD KOORALGIN | 982201 | 3118277 | 3067293 | 2020-02-03 | 1408 | N |  |  | 14 | 4 | 2 | Serviceable | Y | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1972 | -26.8997 | 151.9625 | 000003067293 | 01/JAN/72
EECL | OT208863 | OP | Operational |  | 2023-12-13 | 202312 | Crossarm | Xarm, Wood Strain | Broken | Termites |  | 11kV |  |  |  | 836960 | 2024 | 23NQ14672 | 2023-12-13 08:55 | 2023-12-13 08:34 | COMP | Completed | M |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | NOME: BENTLEY DR, PAUL JAMES DR | F-2486-s STUA - ST-05 Fdr - Broken xarm beyond ABS Paul James Dr No.1. SL 5130805 | STUA - ST-05 Fdr - Broken xarm beyond ABS Paul James Dr No.1. SL 5130805 Time Off modified from 09:00 13-Dec to 09:00 13-Dec Time Off modified from 09:00 13-Dec to 08:54 13-Dec issued to REDACTED twvfr07 Sending Asset Event to FFA FFA Order Created F-AE23NQ14672-1-0 DfltHost FFA Order Acknowledged F-AE23NQ14672-1-0 twvfr07 REDACTED 0455524351 FFA Order En Route F-AE23NQ14672-1-0 twvfr07 FFA Order On Site F-AE23NQ14672-1-0 twvfr07 Time On modified from 13:00 13-Dec to 13:45 13-Dec Sending Asset Event to FFA Time On modified from 13:45 13-Dec to 13:32 13-Dec Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23NQ14672-1-0 Completed by technician REDACTED in crew twvfr07(0455524351) with code A-F-C - Completed Action Taken : Replaced broken 11kV strain arm from termite damage. Site Label : 5130805 | 1 | 3184936 | 83 Paul James Dr Nome T'ville | 836960 | 5130805 | 3184936 | 2020-09-23 | 1176 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Crop | SG SPOTTED GUM | 8 kiloNewton | 1990 | -19.3419 | 146.928 | 000003184936 | 01/JAN/90
EECL | OT211554 | OP | Operational |  | 2023-12-21 | 202312 | Crossarm | Xarm Kingbolt | Broken | Corrosion |  | 11kV |  |  |  | 1805039 | 2024 | 23NQ15086 | 2023-12-22 00:23 | 2023-12-22 00:32 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | HORSESHOE BAY | Ergon Crew advie they found a broke HV crossarm at S/L5135018 | Ergon Crew advie they found a broke HV crossarm at S/L5135018 Time Off modified from 00:45 22-Dec to 00:22 22-Dec Time On modified from 23:59 22-Dec to 05:00 22-Dec Asset selection modified Time On modified from 05:00 22-Dec to 03:16 22-Dec Sending Asset Event to FFA FFA Order Created F-AE23NQ15086-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ15086-1-0 mgics01 REDACTED 0437664723 FFA Order En Route F-AE23NQ15086-1-0 mgics01 FFA Order On Site F-AE23NQ15086-1-0 mgics01 FFA Order F-AE23NQ15086-1-0 Completed by technician REDACTED in crew mgics01(0437664723) with code A-F-C - Completed Action Taken : switched network 11kv off to replace broken xarm/hardware. Site Label : 5135018 | 1 | 3207228 | cnr gifford st & horseshoe bay rd Hshoe | 1805039 | 5135018 | 3207228 | 2020-03-17 | 1374 | N |  |  | 12.5 | 2 | 2 | Serviceable | Y | HV fully suppd | STEEL | Grass | Footpath | HS HOLLOW/TUBULAR ST | Unknown |  | -19.1267 | 146.8626 | 000003207228 | 01/JAN/04
EECL | OT206589 | OP | Operational |  | 2023-12-01 | 202312 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1558454 | 2024 | 23CA16866 | 2023-12-01 17:33 | 2023-12-01 17:37 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | FERNLEES, GINDIE, SPRINGSURE, | 22kV Recloser RC790613 - tripped due to Broken X-Arm | 22kV Recloser RC790613 - tripped due to Broken X-Arm supply restored up to 22kV Dropout Fuse S8065 Asset selection modified Time On modified from 23:59 01-Dec to 21:30 01-Dec Time On modified from 21:30 01-Dec to 20:34 01-Dec | 1 | 3230153 | X8065 Gregory Hwy Gindie | 1558454 | 4147865 | 3230153 | 2023-12-11 | -10 | N |  |  | 12.5 | 2 |  | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1983 | -23.7535 | 148.1385 | 000003230153 | 01/JAN/83
EECL | OT209747 | OP | Operational |  | 2023-12-16 | 202312 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 22kV |  |  |  | 1247811 | 2024 | 23FN16101 | 2023-12-16 12:03 | 2023-12-16 12:08 | COMP | Completed |  | Wet / Rain | Far North | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | TRINITY BEACH: CONNEMARA CL, CORINDA CL, KATANDRA CL, MARARNA ST, MOORE ST, VASEY ESP, WILMA ST | KAMERUNGA 22kV Cook 2 TB2 ACR CB tripped. SCADA Interface automated outage. Crew found disc insulator near SS3401 had pulled through; RMU SS5834 had cracked bushings so moved isolation point back to RMU SS776694. Crew replaced HV cross-arm. SL 5166609. REDACTED | entered from the SCADA Interface Tripped on EF Sending Asset Event to FFA FFA Order Created F-AE23FN16101-1-0 DfltHost SS649277 - FI up on SD1. patrolled to SS8743 - no FI up. closed ACR TB2 up to SS8743. checking FI downstream Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA crew found disc insulator near SS3401 pulled through. RMU SS5834 has cracked bushings so moved isolation point back to RMU SS776694. restored up to SS776694 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 16-Dec to 18:00 16-Dec Sending Asset Event to FFA Assets extracted from SS3401 (10 Connemara Cl) into event 23FN16127 FFA Order Acknowledged F-AE23FN16101-1-0 cnsoc26 REDACTED 0439256942 FFA Order En Route F-AE23FN16101-1-0 cnsoc26 FFA Order On Site F-AE23FN16101-1-0 cnsoc26 Asset selection modified Sending Asset Event to FFA Time On modified from 18:00 16-Dec to 17:16 16-Dec Sending Asset Event to FFA FFA Order F-AE23FN16101-1-0 Completed by technician REDACTED in crew CNSOC26(0439256942) with code A-T-304 - HV-Conductor Connection Failure Action Taken : REPLACED HV ARM Site Label : 5166609 Actual Power Restoration for F-AE23FN16101-1-0: 16-DEC-2023 17:31:00 auto-completed Reason for Event changed from Unknown Updated Reasons tab. Updated Event Trigger from HV-CCF to HV-Unassisted failure. | 1 | 3290629 | 2 connemara cl,trinity beach | 1247811 | CON1 | 3290629 | 2020-04-23 | 1332 | N |  |  | 14 | 2 | 1 | Serviceable | N | Urb Toff | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 12 kiloNewton | 1977 | -16.7807 | 145.6948 | 000003290629 | 01/JAN/77
EECL | OT211913 | OP | Operational |  | 2023-12-23 | 202312 | Crossarm | Xarm, Wood Intermediate | Broken | Termites |  | 22kV |  |  |  | 1721067 | 2024 | 23CA18165 | 2023-12-23 18:50 | 2023-12-23 18:19 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE |  | N/A | Foced Outage required to start of DYSART TOWN No2 Feeder due to broken x-arm | Foced Outage required to start of DYSART TOWN No2 Feeder due to broken x-arm Switching Sheet ID updated from to J-291330-g. Broken X-arm at SL 4234473 mdmcm02 Sending Asset Event to FFA FFA Order Created F-AE23CA18165-1-0 DfltHost Time Off modified from 18:45 23-Dec to 18:50 23-Dec Sending Asset Event to FFA Time On modified from 23:59 23-Dec to 23:59 24-Dec Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 24-Dec to 23:59 23-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA18165-1-0 mdmcm02 REDACTED 0428783428 FFA Order En Route F-AE23CA18165-1-0 mdmcm02 FFA Order On Site F-AE23CA18165-1-0 mdmcm02 FFA Order F-AE23CA18165-1-0 Completed by technician REDACTED in crew mdmcm02(0428783428) with code A-F-C - Completed Action Taken : Found snapped x-arm, isolated and replaced. Site Label : 4234473 | 1 | 3301668 | 4 SW of X3673 acc Golden Mile Rd Dysart | 1721067 | 4234473 | 3301668 | 2019-10-11 | 1534 | N |  |  | 15.5 | 1 |  | Serviceable | Y | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1988 | -22.5512 | 148.3991 | 000003301668 | 01/JAN/88
EECL | OT215181 | OP | Operational |  | 2023-12-31 | 202312 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay |  | LV |  |  |  | 1707371 | 2024 | 24CA0067 | 2023-12-31 17:18 | 2024-01-01 14:12 | COMP | Completed |  | Storm Electrical | Capricornia | Unplanned Outage | Severe Weather | Unknown | Single Fault Call | GT |  | 11 GARNHAM DR;DYSART QLD 4745 | Fault occurred at:31/12/2023 17:15; REDACTED, 0419703844;>WDPP --> AffectingTraffic:NO -- StillHavePower:YES<;Incident Details:A wire has come loose above TX & is hanging. It's now wrapped/resting on the TX itself. No LOS. Thinking this could be the earth wire.;COVID-19:N/A;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N |  | 1 | 3317947 | SP359591 11 Garnham Dr Dysart | 1707371 | 4245058 | 3317947 | 2019-10-17 | 1536 | N |  |  | 12.5 | 3 | 2 | Serviceable | Y | Urb unsty sub pole | WOOD UNTREATED DRESSED | Grass | Footpath | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -22.5881 | 148.3455 | 000003317947 | 01/JAN/60
EECL | OT207832 | OP | Operational |  | 2023-12-06 | 202312 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1373723 | 2024 | 23WB15456 | 2023-12-06 19:09 | 2023-12-06 18:02 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | CHELMSFORD, FAIRDALE, GREENVIEW, MP CREEK | fault calls advise broken Crossarm on the ee off towards pole sub 1184 crew require access to replace arm | fault calls advise broken Crossarm on the ee off towards pole sub 1184 crew require access to replace arm Sending Asset Event to FFA FFA Order Created F-AE23WB15456-1-0 DfltHost Time Off modified from 18:30 06-Dec to 18:15 06-Dec Sending Asset Event to FFA Time Off modified from 18:15 06-Dec to 19:09 06-Dec Sending Asset Event to FFA FFA Order Acknowledged F-AE23WB15456-1-0 mrgoc02 REDACTED 0411032982 FFA Order En Route F-AE23WB15456-1-0 mrgoc02 FFA Order On Site F-AE23WB15456-1-0 mrgoc02 Restoration Comments for F-AE23WB15456-1-0 by mrgoc02: under access replacing hv strain x arm Time On modified from 23:59 06-Dec to 21:08 06-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23WB15456-1-0 Completed by technician REDACTED in crew mrgoc02(0411032982) with code A-F-C - Completed Action Taken : replaced broken 1 ph 11kv strain timber x arm, retensioned 11kv conductors ( 3/12 steel ). heights 7m p4231020- p4231021, 7.5m p4231020- p4231019 Site Label : 4231020 Actual Power Restoration for F-AE23WB15456-1-0: 06-DEC-2023 21:00:00 | 1 | 6224868 | outfront 152 Red Hill Rd Chelmsford | 1373723 | 4231020 | 6224868 | 2021-09-07 | 820 | N |  |  | 11 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD UNTREATED ROUND | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | Unknown |  | -26.2839 | 151.821 | 000006224868 | 01/JAN/53
EECL | OT208148 | OP | Operational |  | 2023-12-08 | 202312 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | 22kV |  |  |  | 1001613 | 2024 | 23CA17314 | 2023-12-08 19:06 | 2023-12-08 21:08 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 2005 GLENORINA RD;GINDIE QLD 4702 | Fault occurred at:08/12/2023 15:40; REDACTED, 0427844046;>UPH --> Details:Low Hanging Wires-WiresExposed:NO,TripHazard:NO -- WireLocation:poleToPole -- WiresLowEnoughToTouch:NO<;Incident Details:Pole 4105112 & SP272443 wire hanging lower between Ergon poles. Cross arm has twisted & moved. Cust supply ok cust ok clear access;COVID-19:NO;Warnings[uphSafety]: ADVISED;Sensitive Load:N |  | 1 | 8739273 | 2005 Glenoria Rd Gindie-at SP272443 | 1001613 | 4105112 | 8739273 | 2021-05-19 | 933 | N |  |  | 12.5 |  |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Front Yard | SG SPOTTED GUM | 8 kiloNewton | 1973 | -23.8112 | 148.2969 | 000008739273 | 01/JAN/13
EECL | OT207684 | OP | Operational |  | 2023-12-06 | 202312 | Crossarm | Xarm Strap(S) | Broken | Incorrect Installation |  | 66kV |  |  |  | 1862756 | 2024 | 23WB15435 | 2023-12-06 09:45 | 2023-12-06 11:33 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 226 KLASS AND TOWNES RD;KINGAROY QLD 4610 | Fault occurred at:06/12/2023 06:35; REDACTED, 0427626159;>UPH --> Details:Life Threatening-WiresExposed:NO,TripHazard:NO<;Incident Details:66,000 V pole, bolt is broken and wire is touching the stay and pole. No wires down at this stage.;COVID-19:N/A;Warnings[uphSafety]: ADVISED;Sensitive Load:N |  | 1 | 2047366 | 3plN,McDonald/Klass-Townes Rd,Memerambi | 1862756 | 2010147 | 2047366 | 2022-07-29 | 495 | N |  |  | 15.5 |  |  | Serviceable | N | 66kV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | GI GREY IRONBARK | 8 kiloNewton | 1993 | -26.4637 | 151.8478 | 000002047366 | 01/JAN/93
EECL | OT214482 | OP | Operational |  | 2023-12-30 | 202312 | Crossarm | Xarm Strap(S) | Loose Fitting | Vibration |  | 33kV |  |  |  | 879974 | 2024 | 23SW23825 | 2023-12-30 11:14 | 2023-12-30 11:17 | COMP | Completed |  | Wind | South West | Unplanned Outage | Severe Weather | Unknown | due to a SCADA Automated Event | FE |  | BONGEEN, BOWENVILLE, BRANCHVIEW, BROOKSTEAD, CECIL PLAINS, FORMARTIN, JONDARYAN, NORWIN, ST RUTH, TIPTON, WEST PRAIRIE, | F-1886-r YARRANLEA 33kV Norwin Fdr CB EB05Q00 tripped. SCADA Interface automated outage. | entered from the SCADA Interface Reclose adv. Rural circuit. Depot Co-ord Advised Storm in Area Coord adv to hold off. Unlisted customer reported lines down in area. Patrol required Spoke wagain with Coord and reclose adv. Reclose unsuccessful Coord to adv of dispatch twmoc01 Sending Asset Event to FFA FFA Order Created F-AE23SW23825-1-0 DfltHost Resotred up to 33kV Gas Switch AB7594 at 1843 Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW23825-1-0 twmoc05 REDACTED 0451002449 FFA Order En Route F-AE23SW23825-1-0 twmoc05 FFA Order On Site F-AE23SW23825-1-0 twmoc05 FFA Order F-AE23SW23825-1-0 Completed by technician REDACTED in crew twmoc05(0451002449) with code A-T-317 - Severe Weather Action Taken : 33kv X-arm lost coach screw from arm braces and windmilled round. Site Label : 2051021 Time On modified from 23:59 30-Dec to 23:59 31-Dec Time On modified from 23:59 31-Dec to 00:17 31-Dec PE14271 removed via Clash Wizard as is captured in 23SW24025 | 1 | 2165307 | 1pl S/W 1717 Oakey/Pttswrth Rd/Aubigny | 879974 | 2051021 | 2165307 | 2023-01-30 | 334 | N |  |  | 15.5 | 3 | 1 | Serviceable | N | Urb unsty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1986 | -27.5498 | 151.6174 | 000002165307 | 01/JAN/86
EECL | OT211133 | OP | Operational |  | 2023-12-20 | 202312 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 779889 | 2024 | 23SW22374 | 2023-12-20 17:19 | 2023-12-20 22:03 | CAN | Cancelled |  | Fine | South West | Unplanned Outage | HV-Conductor Connection Failure | Unknown | Single Fault Call | GT |  | 2 RAINBOW RD;HIGHFIELDS QLD 4352 | 3rd Party->Fault occurred at:20/12/2023 17:15; REDACTED, 0439308193;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details:Broken Crossarm at the cnr of Sunray Dr & Rainbow Rd.;Access Details:Clear access;COVID-19:UNKNOWN;Warnings[uphSafety]: ADVISED;Sensitive Load:N | outage cancelled via Clash Wizard | 1 | 2258452 | 1 Sunray Dr Highfields | 779889 | 3190723 | 2258452 | 2021-02-03 | 1050 | N |  |  | 12.5 | 1 | 1 | Serviceable | N | Rrl unsty ang 5-20o | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | SG SPOTTED GUM | 8 kiloNewton | 1979 | -27.4628 | 151.945 | 000002258452 | 01/JAN/79
EECL | OT211818 | OP | Operational |  | 2023-12-23 | 202312 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1422251 | 2024 | 23SW22738 | 2023-12-23 14:54 | 2023-12-23 17:03 | COMP | Completed |  |  | South West | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 48 TOURIST RD;EAST TOOWOOMBA QLD 4350 | 3rd Party->Fault occurred at:23/12/2023 12:02; REDACTED, 0427027975;>UPH --> Details:Low Hanging Wires-WiresExposed:NO,TripHazard:NO -- WireLocation:poleToPole -- WiresLowEnoughToTouch:NO<;Incident Details:Pole number 3207814 - wire down pole to pole, low hanging and broken away from crossarm.;Access Details:Clear access;COVID-19:NO;Warnings[uphSafety]: ADVISED;Sensitive Load:N |  | 1 | 2381808 | crn tourist rd & ipswich st toowoomba | 1422251 | 3207814 | 2381808 | 2020-02-20 | 1402 | N |  |  | 11 |  | 2 | Serviceable | N | Urb Toff | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | SG SPOTTED GUM | 8 kiloNewton | 1982 | -27.5702 | 151.9766 | 000002381808 | 01/JAN/82
EECL | OT209645 | OP | Operational |  | 2023-12-16 | 202312 | Crossarm | Xarm, Wood Intermediate | Burnt Off | Leakage |  | 66kV |  |  |  | 1869227 | 2024 | 23CA17621 | 2023-12-16 01:21 | 2023-12-16 01:31 | COMP | Completed | M | Fine | Capricornia | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FE |  | BLACKWATER: ARDURAD RD, BLACKWATER-R'STON RD, PENROSE RD COMET: COMET ROLLESTON RD, HUMBOLDT RD, OFF COMET-R'STON RD ROLLESTON: COMET-ROLLESTON RD, OFF COMET-R'STON RD, SIRIUS RD, SUNLIGHT RD | F-2378-q : 6014 BLAC - SOBL 66kV Feeder Distance Z1 Trip to Lockout. Unplanned Outage to SBSS South Blackwater. | 6014 BLAC - SOBL 66kV Feeder Distance Z1 Trip to Lockout. Unplanned Outage to SBSS South Blackwater. F-2378-q 66kV change-over attempted. SOBL supplied via 6061 feeder from LEIC. Asset selection modified LEIC LC-S615 tripped on load. No remote control of 66kV CB at LEIC. Local crew to attend to restore supply. Asset selection modified 0131hrs - CB SB-S605 close at SOBL following clearance from REDACTED of BMA Mine (0420 749 367). 0132hrs - CB LH-S615 tripped at LEIC. 0133hrs - REDACTED advo=ises one of their subs have blown up onsite.. . 0143hrs - Clearance obtained from REDACTED of Cook Coal that feeder can be re-energised. . blwoc01 Sending Asset Event to FFA FFA Order Created F-AE23CA17621-1-0 DfltHost Replay sequence time changed from 16-DEC-23 01:32:17 to 16-Dec-23 01:31:28 0205hrs - Clearance obtained from Jacob BMA that their faulted sub has been isolated and request reclose of feeder. Sending Asset Event to FFA 0208hrs - Manual reclose of CB EA14Q00 proved unsuccessful - Fault locator = 23.29 km from BLAC Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Manual reclose successful on site from LEIC substation. Supply restored to SOBL & COCO at 02:27:48 SOBL BMA mine advised that they have been restricted to 16.4MW load. Sending Asset Event to FFA Replay sequence/s deleted after 16-DEC-23 02:24:25 Replay sequence/s deleted after 16-DEC-23 01:31:28 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Crew carrying out line patrol of 6014 66kV feeder. Protection relay fault indicator indicates fault location of 23km from BLAC substation. Sending Asset Event to FFA Sending Asset Event to FFA Crew advise broken crossarm Time On modified from 23:59 16-Dec to 12:03 16-Dec Reason for Event changed from Unknown Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA17621-1-0 blwoc01 REDACTED 0467388353 FFA Order En Route F-AE23CA17621-1-0 blwoc01 FFA Order On Site F-AE23CA17621-1-0 blwoc01 FFA Order F-AE23CA17621-1-0 Completed by technician REDACTED in crew BLWOC01(0467388353) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replace burnt off crossarm. conductor was on ground. 1.5km x 500m paddock burnt out Site Label : 4027178 | 1 | 2552779 | 46 s Cook Washery TannyfoilRd Blackwater | 1869227 | 4027178 | 2552779 | 2022-09-07 | 465 | N |  |  | 18.5 |  |  | Serviceable | Y | 66kV rrl inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 20 kiloNewton | 1977 | -23.7872 | 148.9062 | 000002552779 | 01/JAN/77
EECL | OT212032 | OP | Operational |  | 2023-12-24 | 202312 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1632036 | 2024 | 23SW23020 | 2023-12-24 07:13 | 2023-12-24 16:15 | COMP | Completed |  | Storm Electrical | South West | Unplanned Outage | HV-Conductor Connection Failure | Unknown | Single Fault Call | GT |  | 2031 RIVERTREE RD;RIVERTREE NSW 2372 | Fault occurred at:24/12/2023 07:53; REDACTED, 0746861085;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details:Customer advises cross arms are rotten and 1 has fallen off and the second looks like its about to;COVID-19:NO;Warnings[uphSafety]: ADVISED;Dog restraint:ARRIVAL;Sensitive Load:N | via Clash Wizard Time Off modified from 07:55 24-Dec to 07:13 24-Dec | 1 | 2621833 | acc opp 2031 Rivertree Rd,Rivertree NSW | 1632036 | 3247024 | 2621833 | 2020-11-26 | 1123 | N |  |  | 14 | 3 |  | Serviceable | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 12 kiloNewton | 1979 | -28.6201 | 152.2367 | 000002621833 | 01/JAN/79
EECL | OT213275 | OP | Operational |  | 2023-12-26 | 202312 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 22kV |  |  |  | 1955321 | 2024 | 23SW23503 | 2023-12-26 17:36 | 2023-12-26 17:39 | COMP | Completed |  | Storm Electrical | South West | Unplanned Outage | Lightning | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | EUROMBAH, INJUNE, KANGAROO CREEK, TAROOM, WANDOAN, YULEBA | F-2590-q - WANDOAN 22kV Windrush ACR CB 17096 tripped. SCADA Interface automated outage. Crew found grounded conductor due to broken insulator and tie - Repaired as required. SL 3074921. REDACTED | entered from the SCADA Interface Depot Co-ord Advised Storm in Area MRC unsuccessful, crew to open DL19170 wndoc01 Sending Asset Event to FFA FFA Order Created F-AE23SW23503-1-0 DfltHost Sending Asset Event to FFA 1945: CB1417 Close - Backfeed in place to AB1416 Asset selection modified Sending Asset Event to FFA Crew advised delayed until tomorrow due to weather. Time On modified from 23:59 26-Dec to 23:59 27-Dec Sending Asset Event to FFA Crew believe that they have found two seperate faults. Switching underway to isoalte and earth and restore what we can. Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Restored up to 22kV Dropout Fuse DO1219 at 1153. Hoping to have final customers restored at 1700. Time On modified from 23:59 27-Dec to 17:00 27-Dec Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Assets extracted from PC05841 into event 23SW23616 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 17:00 27-Dec to 19:00 27-Dec Sending Asset Event to FFA Replay sequence time changed from 27-DEC-23 16:42:46 to 27-Dec-23 17:10:46 Replay sequence time changed from 27-DEC-23 16:42:25 to 27-Dec-23 17:06:00 Replay sequence time changed from 27-DEC-23 17:10:46 to 27-Dec-23 17:08:00 Time On modified from 19:00 27-Dec to 17:18 27-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW23503-1-0 wndoc01 REDACTED 0429848619 FFA Order En Route F-AE23SW23503-1-0 wndoc01 FFA Order On Site F-AE23SW23503-1-0 wndoc01 FFA Order F-AE23SW23503-1-0 Completed by technician REDACTED in crew wndoc01(0429848619) with code A-T-62 - Lightning Action Taken : Ergon crew found conductor on the ground due to broken insulator and tie crew repaired defect Site Label : 3074921 Updated Reasons tab. 22kV Pole Dist Sub PC05139 removed from Asset Selection as cust mins captured under 23SW23627 | 1 | 2870824 | 1 NW PC5841 179 Annamaroo Rd Taroom | 1955321 | 3074929 | 2870824 | 2023-10-24 | 63 | N |  |  | 14 | 1 |  | Serviceable | N | Rrl sty angle 5-20o | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1994 | -25.7564 | 149.8813 | 000002870824 | 01/JAN/94
EECL | OT213074 | OP | Operational |  | 2023-12-26 | 202312 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1892210 | 2024 | 23MK10251 | 2023-12-26 11:26 | 2023-12-26 11:28 | COMP | Completed |  | Wet / Rain | Mackay | Unplanned Outage | Severe Weather | Fallen Power Lines | due to fallen power lines. | FC |  | NEBO: WALSHS RD, BRAESIDE RD, CEMETERY RD, SALEYARD DR, COCKENZIE RD, DONNELLAN RD, PEAK DOWNS HWY, OXFORD-DOWNS SARINA RD | F-2772-s - NEBO - Braeside FDR - Braesside ACR EF x 3 to lockout Crew adv have found broken xarms at Pole 4082909 & 4082910. Crew currenlty isolating and then will back feed beyond Regs 4419 from Nebo Feeder. Crew replaced 11kV cross-arm after storm REDACTED | entered from the SCADA Interface Sending Asset Event to FFA FFA Order Created F-AE23MK10251-1-0 DfltHost Crew attending REDACTED 0408 610 830 Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23MK10251-1-0 mnboc01 REDACTED 0484692981 FFA Order En Route F-AE23MK10251-1-0 mnboc01 FFA Order On Site F-AE23MK10251-1-0 mnboc01 REDACTED advised has patrolled from Braeside recloser to ABS601507 No faults found will attempt reclose up to ABS601507. Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Crews have advised bad storm rolling through the area, poor visibility and access issues are making a line patrol difficult..Chopper organised for tomorrow morning Sending Asset Event to FFA Chopper organised for 0630 weather permitting Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA moved open point to put 10291 on as they have 500 guests Sending Asset Event to FFA Time On modified from 23:59 26-Dec to 23:59 27-Dec Sending Asset Event to FFA Crew no organizing a helicopter to continue patrol. Will call back once they are in the air. Sending Asset Event to FFA Crew in the air patrolling Sending Asset Event to FFA FFA Order En Route F-AE23MK10251-1-0 mnboc01 FFA Order On Site F-AE23MK10251-1-0 mnboc01 Crew adv have found broken xarms at Pole 4082909 & 4082910. Crew currenlty isolating and then will back feed beyond Regs 4419 from Nebo Feeder. Unsure of restore time as yet. Lots of access issues due to weather. Crew currently using a helicopter. Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Crew under access and adv restore time 1900 at this stage Time On modified from 23:59 27-Dec to 19:30 27-Dec Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 19:30 27-Dec to 21:30 27-Dec Sending Asset Event to FFA Time On modified from 21:30 27-Dec to 22:30 27-Dec Sending Asset Event to FFA REDACTED MCKOC03 Sending Asset Event to FFA MCKLS1 Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 22:30 27-Dec to 23:30 27-Dec Sending Asset Event to FFA Time On modified from 23:30 27-Dec to 23:00 27-Dec Sending Asset Event to FFA FFA Order Acknowledged F-AE23MK10251-1-0 mckls1 REDACTED 0438648510 FFA Order En Route F-AE23MK10251-1-0 mckls1 FFA Order On Site F-AE23MK10251-1-0 mckls1 FFA Order F-AE23MK10251-1-0 Completed by technician REDACTED in crew mckls1(0438648510) with code A-T-317 - Severe Weather Action Taken : replaced 11kv x arm after storm Site Label : 4082910 auto-completed Updated Reasons tab. Reason for Event changed from Equipment Failure or Malfunction | 1 | 2876879 | Braeside Stn 525 Braeside Rd Nebo | 1892210 | 4082910 | 2876879 | 2023-09-01 | 116 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1982 | -21.7385 | 148.7302 | 000002876879 | 01/JAN/82
EECL | OT211499 | OP | Operational |  | 2023-12-21 | 202312 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1687185 | 2024 | 23SW22611 | 2023-12-21 18:38 | 2023-12-21 21:00 | CAN | Cancelled |  |  | South West | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 118 BANKS RD;FELTON EAST QLD 4358 | Fault occurred at:21/12/2023 16:06; REDACTED, 0447881716;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details:Cross arm on pole 3092242 broken after storm has come through, tension is being taken by next pole, customer still has power. transformer Pole is at end of line;COVID-19:NO;Warnings[uphSafety]: ADVISED;Dog restraint:ARRIVAL;Sensitive Load:N | CANCELLED - Captured under Forced Outage 23SW22572. FC 2389001 linked there. | 1 | 2943683 | PE7582,acc 118 BANKS RD,FELTON | 1687185 | 3092242 | 2943683 | 2023-04-13 | 252 | N |  |  | 14 | 3 | 1 | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 12 kiloNewton | 1985 | -27.8073 | 151.8324 | 000002943683 | 01/JAN/85
EECL | OT214918 | OP | Operational |  | 2023-12-31 | 202312 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1485348 | 2024 | 23SW23999 | 2023-12-31 05:06 | 2023-12-31 07:31 | COMP | Completed |  | Fine | South West | Unplanned Outage | SUBT-Unassisted failure(Apparent defect) | Lightning / Storm | due to damage caused by storm activity. | GT |  | BELL: BUNYA HWY, CASSIDY ST, CHALLACOMBE ST, CRAWSHAY ST, DENNIS ST, ENSOR ST, MAXWELL ST, MCPHEE ST, WALLACE ST | F-1992-r 11kV Pole Dist Sub PC00268, Ensor St - Fault calls suggest possible fault/protection operated | 11kV Pole Dist Sub PC00268, Ensor St - Fault calls suggest possible fault/protection operated dlbloc01 Sending Asset Event to FFA FFA Order Created F-AE23SW23999-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW23999-1-0 dlbloc01 REDACTED 0409186844 FFA Order En Route F-AE23SW23999-1-0 dlbloc01 FFA Order On Site F-AE23SW23999-1-0 dlbloc01 Time On modified from 23:59 31-Dec to 14:54 31-Dec Sending Asset Event to FFA FFA Order F-AE23SW23999-1-0 Completed by technician REDACTED in crew dlbloc01(0409186844) with code A-T-320 - SUBT-Unassisted failure(Apparent defect) Action Taken : replace broken Lv term arm due to white rot in arm Site Label : 3144400 Actual Power Restoration for F-AE23SW23999-1-0: 31-DEC-2023 15:29:00 auto-completed | 1 | 3214210 | pc268next to shop ensor st bell | 1485348 | 3144400 | 3214210 | 2022-08-24 | 494 | N |  |  | 12.5 | 3 | 1 | Serviceable | Y | Urb inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -26.9319 | 151.4505 | 000003214210 | 01/JAN/74
EECL | OT211641 | OP | Operational |  | 2023-12-22 | 202312 | Crossarm | Xarm, Wood Dressing | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1654143 | 2024 | 23SW22694 | 2023-12-22 09:39 | 2023-12-23 10:54 | COMP | Completed |  | Storm Electrical | South West | Unplanned Outage | Vibration | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | GT |  | IRONGATE: EVANSLEA RD | 11kV Pole Dist Sub PE02726 | 11kV Pole Dist Sub PE02726 twmoc02 Sending Asset Event to FFA FFA Order Created F-AE23SW22694-1-0 DfltHost Time On modified from 23:59 23-Dec to 12:03 23-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW22694-1-0 twmoc02 REDACTED 0423949358 FFA Order En Route F-AE23SW22694-1-0 twmoc02 FFA Order On Site F-AE23SW22694-1-0 twmoc02 FFA Order F-AE23SW22694-1-0 Completed by technician REDACTED in crew twmoc02(0423949358) with code A-T-30 - Vibration Action Taken : replaced broken EDO arm Site Label : 3147242 Actual Power Restoration for F-AE23SW22694-1-0: 23-DEC-2023 12:21:00 | 1 | 3226216 | PE2726, acc 665 Wallingford Rd, Irongate | 1654143 | 3147242 | 3226216 | 2019-09-19 | 1555 | N |  |  | 12.5 | 4 | 1 | Serviceable | Y | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Garden Bed | Backyard | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -27.6525 | 151.5094 | 000003226216 | 01/JAN/66
EECL | OT213932 | OP | Operational |  | 2023-12-28 | 202312 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1144891 | 2024 | 23MK10346 | 2023-12-28 13:45 | 2023-12-28 13:47 | COMP | Completed |  | Fine | Mackay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Protective Device Operated | due to the operating of protective equipment. | FC |  | CARMILA, ILBILBIE, ORKABIE, WEST HILL | F-2803-s - ILBILBIE 11kV Orkabie ACR CB tripped. SCADA Interface automated outage. EF trip to lockout. Crew to investigate. | entered from the SCADA Interface EF trip to lockout. Crew to investigate. Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Created F-AE23MK10346-1-0 DfltHost Crew attending REDACTED 0438 791 641 Sending Asset Event to FFA No EF pickup at RC798466. Opened up and will attempt an MRC from RC798380. Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23MK10346-1-0 saroc01 REDACTED 0438791641 FFA Order En Route F-AE23MK10346-1-0 saroc01 Power beyond RC798466 restored at 1416 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA restored up to isolations Sending Asset Event to FFA FFA Order On Site F-AE23MK10346-1-0 saroc01 Time On modified from 23:59 28-Dec to 19:40 28-Dec HV Wires Down Sending Asset Event to FFA FFA Order F-AE23MK10346-1-0 Completed by technician REDACTED in crew saroc01(0438791641) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Replaced broken 11kv Pin arm Site Label : 4000924 auto-completed | 1 | 5917667 | 4 SE of acc 86986 Bruce Hwy Ilbilbie | 1144891 | 4000924 | 5917667 | 2020-01-14 | 1444 | N |  |  | 14 | 2 |  | Unserviceable - P2 | N | Rrl inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | Unknown |  | -21.7454 | 149.3729 | 000005917667 | 01/JAN/64
EECL | OT217512 | OP | Operational |  | 2024-01-10 | 202401 | Crossarm | Xarm, Wood Dressing | Deteriorated | Termites |  | LV |  |  |  | 722043 | 2024 | 24CA0649 | 2024-01-10 13:30 | 2024-01-10 12:21 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | CLERMONT: RUBYVALE RD | F-2842-q - 22kV Dropout Fuse X783746 - crew require HV isolation and access to repair broken LV fuse arm at TX Pole 338118 | 22kV Dropout Fuse X783746 - crew require HV isolation and access to repair broken LV fuse arm at TX Pole 338118 . clmcm03- REDACTED 0408438176 Sending Asset Event to FFA FFA Order Created F-AE24CA0649-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA0649-1-0 clmcm03 REDACTED 0408438176 FFA Order En Route F-AE24CA0649-1-0 clmcm03 FFA Order On Site F-AE24CA0649-1-0 clmcm03 Time On modified from 23:59 10-Jan to 17:20 10-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24CA0649-1-0 Completed by technician REDACTED in crew CLMCM03(0408438176) with code A-F-C - Completed Action Taken : Replaced broken LV arm with new wood arm Site Label : 2008387 Actual Power Restoration for F-AE24CA0649-1-0: 10-JAN-2024 17:22:00 | 1 | 2018821 | SP338118 clermont sports grounds | 722043 | 2008387 | 2018821 | 2021-06-14 | 940 | N |  |  | 12.5 | 3 | 1 | Serviceable | Y | Urb inter sub pole | WOOD UNTREATED ROUND | Lawn |  | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -22.833 | 147.6266 | 000009386881
EECL | OT218243 | OP | Operational |  | 2024-01-15 | 202401 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 729460 | 2024 | 24NQ0725 | 2024-01-15 03:25 | 2024-01-15 03:28 | COMP | Completed |  | Wet / Rain | North Queensland | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to a SCADA Automated Event | FC |  | INGHAM: HAWKINS CREEK RD BEMERSIDE: GANGEMIS RD HAWKINS CREEK: PALMAS RD, GORTONS RD, HAWKINS CREEK RD | F-2978-s LANNERCOST 11kV Tie ACR CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface Trip to lockout O/C 2nd time tonight poor visibility due to heavy rain Sending Asset Event to FFA FFA Order Created F-AE24NQ0725-1-0 DfltHost Crew dispatched REDACTED- 0407 657 024 Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ0725-1-0 ingcsfr01 REDACTED 040657024 FFA Order En Route F-AE24NQ0725-1-0 ingcsfr01 Crews advised broken Xarm Pole 2020951 two poles from INS1147 Towards hawkins creek no.3 Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ0725-1-0 ingcsfr02 REDACTED 0407657024 FFA Order En Route F-AE24NQ0725-1-0 ingcsfr02 FFA Order On Site F-AE24NQ0725-1-0 ingcsfr02 Restoration Comments for F-AE24NQ0725-1-0 by INGCSFR02: RESTORATION APPROX 1300 FFA Order F-AE24NQ0725-1-0 Completed by technician REDACTED in crew INGCSFR02(0407657024) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replace broken xarm Site Label : 2020951 Actual Power Restoration for F-AE24NQ0725-1-0: 15-JAN-2024 09:21:00 FFA Order F-AE24NQ0725-1-0 Completed by technician REDACTED in crew INGCSFR02(0407657024) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replace broken xarm Site Label : 2020951 Actual Power Restoration for F-AE24NQ0725-1-0: 15-JAN-2024 09:21:00 FFA Order F-AE24NQ0725-1-0 Completed by technician REDACTED in crew INGCSFR02(0407657024) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replace broken xarm Site Label : 2020951 Actual Power Restoration for F-AE24NQ0725-1-0: 15-JAN-2024 09:21:00 Time On modified from 23:59 15-Jan to 09:21 15-Jan auto-completed | 1 | 2060355 | .5km W of 1240 Hawkins ck rd Ingham | 729460 | 2020951 | 2060355 | 2022-03-22 | 664 | N |  |  | 11 | 1 |  | Serviceable | N | Rrl unsty ang 5-20o | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | RM RED MAHOGANY | 8 kiloNewton | 1965 | -18.5832 | 146.0692 | 000002060355 | 01/JAN/65
EECL | OT220818 | OP | Operational |  | 2024-01-26 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1760623 | 2024 | 24NQ2963 | 2024-01-25 19:55 | 2024-01-25 19:57 | COMP | Completed | M | Cyclonic | North Queensland | Unplanned Outage | Severe Weather | Cyclone | due to damage caused by cyclone activity. | FE |  | KELSO | F-3095-s 11kV Rasmussen No.4 Feeder CB D252 OPENED FORM OCC DUE TO MULTIPLE LINES DOWN REPORTS | 11kV Rasmussen No.4 Feeder CB D252 OPENED FORM OCC DUE TO MULTIPLE LINES DOWN REPORTS Time On modified from 23:59 25-Jan to 23:59 26-Jan Time On modified from 23:59 26-Jan to 23:59 27-Jan Crew have isolated and earthed lines down adjacent TVS714, 11kV Switch Samantha St No.1 is opend and dnob and earthed On Fault Sheet F-3095-s RASM-04 11kV Feeder CB D252 closed @ 11:14am. Customers beyod MILES AVE NO.1 are still without supply as these customers are transferred to RASM-08 via CAROO ST NO.2 due to sycon 23NQ13827 Asset selection modified as per restoration plan Time On modified from 23:59 27-Jan to 22:00 28-Jan All customers restored via RASM 8 up to SAMANTHA ST NO.1 @ 1721. Refer to 24NQ2954 Asset selection modified All restored at 1244 Time On modified from 22:00 28-Jan to 12:44 28-Jan | 1 | 2091029 | cnr Inglong st + Samantha st Kelso | 1760623 | 2017097 | 2091029 | 2020-02-25 | 1431 | N |  |  | 12.5 | 2 | 2 | Serviceable | N | Urb unsty angle | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | SG SPOTTED GUM | 12 kiloNewton | 1974 | -19.378 | 146.7315 | 000002091029 | 01/JAN/74
EECL | OT218455 | OP | Operational |  | 2024-01-16 | 202401 | Crossarm | Xarm, Wood Strain | Broken | Corrosion |  | LV |  |  |  | 745973 | 2024 | 24MK0379 | 2024-01-16 07:11 | 2024-01-16 07:14 | COMP | Completed |  |  | Mackay | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FC |  | BLOOMSBURY, CALEN, CATHU, ELAROO, MENTMORE, PINDI PINDI, WAGOORA, YALBOROO | F-2984-s - 11kV PINDI FDR CB FB02Q00 opened for public safety due to reports of fallen powerlines, refer to F/C 2398359. Crews advise of lv lines down at Sub2429 which have been made safe on FC 2398359 (24MK0382). | 11kV PINDI FDR CB FB02Q00 opened for public safety due to reports of fallen powerlines, refer to F/C 2398359. F-2984-s Time Off modified from 08:00 16-Jan to 07:11 16-Jan Crew heading to site, approx ETA 0820 hrs. Crews advise of lv lines down at Sub2429 which have been made safe on FC 2398359 Assets extracted from 2429 (HEMMENS) into event 24MK0382 Time On modified from 23:59 16-Jan to 08:51 16-Jan Added notes to Reasons tab. | 1 | 2121729 | 7261 Bruce Hwy Yalboroo | 745973 | 2049509 | 2121729 | 2021-05-14 | 977 | N |  |  | 8 |  | 1 | Serviceable | N | Light serv pole | WOOD UNTREATED ROUND | Lawn | Front Yard | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -20.8072 | 148.6172 | 000002121729 | 01/JAN/61
EECL | OT218871 | OP | Operational |  | 2024-01-18 | 202401 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 751143 | 2024 | 24NQ0897 | 2024-01-18 12:21 | 2024-01-18 12:23 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | HV-Conductor Connection Failure | Protective Device Operated | due to the operating of protective equipment. | FE |  | BROUGHTON, CHARTERS TOWERS, CHARTERS TOWERS CITY | F-2996-s - CHART TWRS 11kV CT04 Fdr CB D252 tripped. SCADA Interface automated outage. | entered from the SCADA Interface CHTO - D252 SEF trip. Crews to patrol Reason for Event changed from Unknown . Sending Asset Event to FFA FFA Order Created F-AE24NQ0897-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Crew advise HV wires down at SL 2068628. Crews currently under access making repairs HV Wires Down Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ0897-1-0 chtcs01 REDACTED 0467521941 FFA Order En Route F-AE24NQ0897-1-0 chtcs01 FFA Order On Site F-AE24NQ0897-1-0 chtcs01 FFA Order F-AE24NQ0897-1-0 Completed by technician REDACTED in crew CHTCS01(0467521941) with code A-T-304 - HV-Conductor Connection Failure Action Taken : broken crossarm at cts613 Site Label : 2068628 Time On modified from 23:59 18-Jan to 15:45 18-Jan auto-completed | 1 | 2199940 | 12049 flinders hwy ch towers | 751143 | 2068628 | 2199940 | 2021-02-26 | 1056 | N |  |  | 12.5 | 2 |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1986 | -20.0526 | 146.3257 | 000002199940 | 01/JAN/86
EECL | OT219895 | OP | Operational |  | 2024-01-23 | 202401 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 751206 | 2024 | 24NQ1032 | 2024-01-23 09:18 | 2024-01-23 07:23 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | BROUGHTON: FENTON GROVE RD SEVENTY MILE: CHERRY CREEK RD, THOMASSON RD, WOKOLENA LANE | Forced outage to replace broken crossarm on 2068713 | Forced outage to replace broken crossarm on 2068713 Time Off modified from 08:00 23-Jan to 09:18 23-Jan Time On modified from 23:59 23-Jan to 13:00 23-Jan Sending Asset Event to FFA FFA Order Created F-AE24NQ1032-1-0 DfltHost FFA Order Acknowledged F-AE24NQ1032-1-0 chtfco01 REDACTED 0418735767 FFA Order En Route F-AE24NQ1032-1-0 chtfco01 Time On modified from 13:00 23-Jan to 11:52 23-Jan Sending Asset Event to FFA FFA Order On Site F-AE24NQ1032-1-0 chtfco01 Sending Asset Event to FFA FFA Order F-AE24NQ1032-1-0 Completed by technician REDACTED in crew chtfco01(0418735767) with code A-F-C - Completed Action Taken : replaced broken 11kv term arm Site Label : 2068713 | 1 | 2200804 | 548 Cherry Creek Rd Charters Towers | 751206 | 2068713 | 2200804 | 2021-11-21 | 793 | N |  |  | 12.5 | 3 |  | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1987 | -20.1799 | 146.2681 | 000002200804 | 01/JAN/87
EECL | OT218818 | OP | Operational |  | 2024-01-18 | 202401 | Crossarm | Xarm, Wood Termination | Split | Rot/Decay |  | LV |  |  |  | 1024159 | 2024 | 24SW1200 | 2024-01-18 09:25 | 2024-01-18 09:22 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | BALLANDEAN: RICCA RD, SUNDOWN RD |  | Crews need access to the LV mains to make repairs to a broken LV Term arm. LV Switching Only. sttcs01 Sending Asset Event to FFA FFA Order Created F-AE24SW1200-1-0 DfltHost Time Off modified from 10:00 18-Jan to 09:25 18-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW1200-1-0 sttcs01 REDACTED 0447653814 FFA Order En Route F-AE24SW1200-1-0 sttcs01 FFA Order On Site F-AE24SW1200-1-0 sttcs01 FFA Order F-AE24SW1200-1-0 Completed by technician REDACTED in crew STTCS01(0447653814) with code A-F-C - Completed Action Taken : repair damaged Lv term arm Site Label : 3191439 Time On modified from 14:00 18-JAN to 11:12 18-JAN | 1 | 2265713 | 289 Sundown Rd,Ballandean | 1024159 | 3191439 | 2265713 | 2020-01-09 | 1470 | N |  |  | 12.5 | 2 | 1 | Serviceable | N | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Crop | SG SPOTTED GUM | 5 kiloNewton | 1964 | -28.8125 | 151.8202 | 000002265713 | 01/JAN/64
EECL | OT215305 | OP | Operational |  | 2024-01-01 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1780777 | 2024 | 24NQ0013 | 2024-01-01 04:01 | 2024-01-01 04:03 | COMP | Completed |  | Storm | North Queensland | Unplanned Outage | Overload | Unknown | due to a SCADA Automated Event | FE |  | MAJORS CREEK, TOONPAN, WOODSTOCK | F-2831-s - WOODSTCK STH 11kV WO-02 Fdr CB FB05Q00 tripped. SCADA Interface automated outage. | entered from the SCADA Interface F-2831-s O/C Supervisor REDACTED 0418 985 424 is aware of outage, crews will not be dispatched until weather system passes. Depot Co-ord Advised Issue to REDACTED twvoc05 Sending Asset Event to FFA FFA Order Created F-AE24NQ0013-1-0 DfltHost Sending Asset Event to FFA REDACTED enroute shortly, supported by REDACTED to begin patrol. ETR 1600hrs at this stage Time On modified from 23:59 01-Jan to 16:00 01-Jan Sending Asset Event to FFA FFA Order Pending F-AE24NQ0013-1-0 FFA Order Acknowledged F-AE24NQ0013-1-0 twvcs02 REDACTED 0407639496 FFA Order En Route F-AE24NQ0013-1-0 twvcs02 FFA Order On Site F-AE24NQ0013-1-0 twvcs02 Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 16:00 01-Jan to 15:25 01-Jan Sending Asset Event to FFA Crew patrolled and found broken crossarm. Repaired under access. Relivened feeder at 1524. Sending Asset Event to FFA FFA Order F-AE24NQ0013-1-0 Completed by technician REDACTED in crew twvcs02(0407639496) with code A-T-28 - Overload Action Taken : replaced Brocken x arm Site Label : 2102313 auto-completed | 1 | 2286621 | 3291 WOODSTOCK GIRU RD | 1780777 | 2102313 | 2286621 | 2021-10-30 | 793 | N |  |  | 14 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1980 | -19.5997 | 146.8598 | 000002286621 | 01/JAN/80
EECL | OT220219 | OP | Operational |  | 2024-01-24 | 202401 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1773724 | 2024 | 24NQ1132 | 2024-01-24 12:07 | 2024-01-24 12:08 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FC |  | MAJORS CREEK: COOK RD, HABERECHT RD, MAJORS CREEK RD, MOUNTVIEW DR, OLD COACH RD, QUIGLEY RD, TOLSON RD, WEBB RD, WOODSTOCK GIRU RD WOODSTOCK: WOODSTOCK GIRU RD | ACR RC765964 opened for safety due to lines down call. Crew replaced HV term cross-arm REDACTED | ACR RC765964 opened for safety due to lines down call. Time Off modified from 12:56 24-Jan to 12:06 24-Jan Call log ID 2401320 Sending Asset Event to FFA FFA Order Created F-AE24NQ1132-1-0 DfltHost FFA Order Acknowledged F-AE24NQ1132-1-0 twvfr07 REDACTED 0419269209 FFA Order En Route F-AE24NQ1132-1-0 twvfr07 FFA Order On Site F-AE24NQ1132-1-0 twvfr07 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 24-Jan to 18:41 24-Jan Sending Asset Event to FFA FFA Order F-AE24NQ1132-1-0 Completed by technician REDACTED in crew twvfr07(0419269209) with code A-F-C - Completed Action Taken : Opened HV links at Quigley Rd No. 1. Replaced HV term crossarm. Site Label : Olinks Added notes to Reasons tab. | 1 | 2336342 | Acs.2773 Woodstock Giru Rd.Major Ck.Area | 1773724 | 2126004 | 2336342 | 2021-11-23 | 792 | N |  |  | 14 | 2 | 1 | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Crop | SG SPOTTED GUM | 12 kiloNewton | 1989 | -19.6152 | 146.9113 | 000002336342 | 01/JAN/89
EECL | OT222462 | OP | Operational |  | 2024-01-29 | 202401 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1007806 | 2024 | 24CA2186 | 2024-01-29 16:26 | 2024-01-29 16:29 | COMP | Completed |  | Hot | Capricornia | Unplanned Outage | HV-Conductor Connection Failure | Unknown | due to a SCADA Automated Event | FC |  | CALLIOPE, RIVER RANCH | F-2358-r - CALLIOPE 11kV Stowe Rd ACR CB X6599 tripped. SCADA Interface automated outage. | entered from the SCADA Interface Depot Co-ord Advised MRC Unsuccessful Manual Reclose Checklist pcoc01 Sending Asset Event to FFA FFA Order Created F-AE24CA2186-1-0 DfltHost FFA Order Acknowledged F-AE24CA2186-1-0 pcoc01 REDACTED 0437709739 FFA Order En Route F-AE24CA2186-1-0 pcoc01 FFA Order On Site F-AE24CA2186-1-0 pcoc01 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 29-Jan to 20:00 29-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE24CA2186-1-0 pcoc01 FFA Order On Site F-AE24CA2186-1-0 pcoc01 Time On modified from 20:00 29-Jan to 19:51 29-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24CA2186-1-0 Completed by technician REDACTED in crew pcoc01(0437709739) with code A-T-315 - Service Asset Fault Action Taken : Replaced broken cross arm at pole 2149320 Site Label : 2149320 | 1 | 2336773 | 1p sth 30 RIVERIVEW DR CALLIOPE | 1007806 | 2149320 | 2336773 | 2022-05-16 | 623 | N |  |  | 11 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1986 | -23.9804 | 151.1537 | 000002336773 | 01/JAN/86
EECL | OT222768 | OP | Operational |  | 2024-01-30 | 202401 | Crossarm | Xarm Kingbolt | Deteriorated | Corrosion |  | LV |  |  |  | 1285039 | 2024 | 24WB2512 | 2024-01-30 13:15 | 2024-01-30 13:09 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | BARGARA: WOONGARRA SCENIC DR | Crew advises LV isolation required to change LV crossarm .11kV Pole Dist Sub 7903. bndcsfr10.. | Crew advises LV isolation required to change LV crossarm .11kV Pole Dist Sub 7903. bndcsfr10.. Sending Asset Event to FFA FFA Order Created F-AE24WB2512-1-0 DfltHost FFA Order Acknowledged F-AE24WB2512-1-0 bndcsfr10 REDACTED 0401944718 FFA Order En Route F-AE24WB2512-1-0 bndcsfr10 FFA Order On Site F-AE24WB2512-1-0 bndcsfr10 Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24WB2512-1-0 Completed by technician REDACTED in crew bndcsfr10(0401944718) with code A-F-C - Completed Action Taken : replaced U/S LV pin arm Site Label : 2109981 Time On modified from 23:59 30-JAN to 15:00 30-JAN | 1 | 2339644 | 24 grevillia avenue innes park | 1285039 | 2109981 | 2339644 | 2020-05-29 | 1341 | N |  |  | 11 |  | 1 | Serviceable | Y | Urb LV inter | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1986 | -24.853 | 152.474 | 000002339644 | 01/JAN/86
EECL | OT223038 | OP | Operational |  | 2024-01-31 | 202401 | Crossarm | Xarm, Wood Strain | Deteriorated | Rot/Decay |  | LV |  |  |  | 862060 | 2024 | 24SW4122 | 2024-01-31 03:35 | 2024-01-31 06:37 | COMP | Completed |  |  | South West | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 100 STUART ST;TOOWOOMBA QLD 4350 | 3rd Party->Fault occurred at:31/01/2024 01:55; REDACTED, 0460721214;>WDPP --> AffectingTraffic:YES -- StillHavePower:UNSURE<;Incident Details:Passerby Saw sparking & noticed fallen power line across Roundabout & unsure if ran over it or it dropped after he went past;Access Details:Round-A-Bout Stuart St & Jellicoe Streets.;COVID-19:N/A;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N |  | 1 | 2349706 | cnr jellicoe st and stuart st toowoomba | 862060 | 3202588 | 2349706 | 2021-11-02 | 820 | N |  |  | 12.5 | 2 | 2 | Serviceable | N | Urb unsty trm>=2cct | WOOD UNTREATED DRESSED | Lawn | Footpath | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -27.5474 | 151.9644 | 000002349706 | 01/JAN/50
EECL | OT221367 | OP | Operational |  | 2024-01-27 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1256303 | 2024 | 24SW3706 | 2024-01-27 09:29 | 2024-01-27 08:33 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | CHARLEVILLE | 11kV Load Break AB AB6618, Crew to Replace Broken Xarm | 11kV Load Break AB AB6618, Crew to Replace Broken Xarm chrcmfr06 Sending Asset Event to FFA FFA Order Created F-AE24SW3706-1-0 DfltHost FFA Order Acknowledged F-AE24SW3706-1-0 chrcmfr06 REDACTED 0427542289 FFA Order En Route F-AE24SW3706-1-0 chrcmfr06 FFA Order On Site F-AE24SW3706-1-0 chrcmfr06 Sending Asset Event to FFA Time Off modified from 10:10 27-Jan to 09:19 27-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW3706-1-0 Completed by technician REDACTED in crew chrcmfr06(0427542289) with code A-F-C - Completed Action Taken : replaced broken cross arm Site Label : 3203097 Time Off modified from 09:19 27-Jan to 09:29 27-Jan 0954: Backfeed up to AB616. Close AB6614 on Parry St Fdr Asset selection modified 1055: AB6614 Open Asset selection modified 1104: AB6618 Closed Asset selection modified Time On modified from 23:59 27-Jan to 11:09 27-Jan | 1 | 2352874 | CNR KING AND STURT ST CHARLEVILLE | 1256303 | 3203097 | 2352874 | 2021-08-06 | 904 | N |  |  | 12.5 | 2 |  | Serviceable | N | Urb LV inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | SG SPOTTED GUM | 8 kiloNewton | 1997 | -26.4071 | 146.2418 | 000002352874 | 01/JAN/97
EECL | OT221696 | OP | Operational |  | 2024-01-28 | 202401 | Crossarm | Xarm, Wood Strain | Deteriorated | Rot/Decay |  | 22kV |  |  |  | 765766 | 2024 | 24FN2077 | 2024-01-28 07:09 | 2024-01-28 07:12 | COMP | Completed |  | Wet / Rain | Far North | Unplanned Outage | Distribution substation | Unknown | due to a SCADA Automated Event | FC |  | ATHERTON, EAST BARRON, JAGGAN, MALANDA, MINBUN, TARZALI, UPPER BARRON | F-3158-s ATHERTON 22kV KennedyHwyT64A ACR CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface REDACTED 0487 669 575 Sending Asset Event to FFA FFA Order Created F-AE24FN2077-1-0 DfltHost FFA Order Acknowledged F-AE24FN2077-1-0 athoc01 REDACTED 0459284980 FFA Order En Route F-AE24FN2077-1-0 athoc01 FFA Order On Site F-AE24FN2077-1-0 athoc01 HV Wires Down Manual Reclose Checklist Sending Asset Event to FFA Isolated faulted t-off and restored Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 28-Jan to 10:58 28-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24FN2077-1-0 Completed by technician REDACTED in crew athoc01(0459284980) with code A-T-303 - Distribution substation Action Taken : HV Switching beyond T127 to replace broke HV Strain Darmstadt on SS497 Site Label : 2144265 | 1 | 2374393 | 605 East Barron Rd Upper Barron | 765766 | WA4 | 2374393 | 2021-08-04 | 907 | N |  |  | 15.5 | 5 | 2 | Serviceable | Y | Rrl sty sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | DS DARWIN STRINGYBAR | 12 kiloNewton | 1994 | -17.3406 | 145.5151 | 000002374393 | 01/JAN/94
EECL | OT220311 | OP | Operational |  | 2024-01-24 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1484808 | 2024 | 24SW3616 | 2024-01-24 19:42 | 2024-01-24 19:44 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | ZS |  | BRINGALILY, KOOROONGARRA, MILLMERRAN, MILLWOOD, MOUNT EMLYN | F-2272-r 11kV Recloser CB4408 Tripped due to low lines | 11kV Recloser CB4408 Tripped due to low lines Time Off modified from 19:50 24-Jan to 19:42 24-Jan Asset selection modified Crews to return in the morning to replace pole Time On modified from 23:59 24-Jan to 12:00 25-Jan HV Wires Down . crew to return in the morning to repair pole Sending Asset Event to FFA FFA Order Created F-AE24SW3616-1-0 DfltHost MILOC01 Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW3616-1-0 miloc01 REDACTED 0437712850 FFA Order En Route F-AE24SW3616-1-0 miloc01 Time On modified from 12:00 25-Jan to 08:49 25-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order On Site F-AE24SW3616-1-0 miloc01 FFA Order F-AE24SW3616-1-0 Completed by technician REDACTED in crew miloc01(0437712850) with code A-F-C - Completed Action Taken : replace cross arm Site Label : 3211389 | 1 | 2404651 | 3697 Inglewood/Millmerran Rd,Canning Ck | 1484808 | 3211389 | 2404651 | 2019-11-05 | 1541 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Crop | SG SPOTTED GUM | 3 kiloNewton | 1975 | -28.1601 | 151.2065 | 000002404651 | 01/JAN/75
EECL | OT217664 | OP | Operational |  | 2024-01-11 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1594412 | 2024 | 24SW0836 | 2024-01-11 12:20 | 2024-01-11 14:24 | COMP | Completed |  |  | South West | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | WILLOW VIEW;130 PETERS RD;TALGAI QLD 4362 | Fault occurred at:11/01/2024 09:15; REDACTED, 0403470312;>WDPB --> HasComeAway:UNSURE,AffectingTraffic:NO -- StillHavePower:YES<;Incident Details:Customer adv line is hanging low enough for a tractor to get caught in. coming from pole 2140911. NO DOGS. NO COVID.;COVID-19:NO;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N |  | 1 | 2441830 | AccOppCnrDickensenRd/ElphinstoneRdAllora | 1594412 | 2140911 | 2441830 | 2020-12-16 | 1121 | N |  |  | 14 | 2 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1966 | -28.0131 | 151.9248 | 000002441830 | 01/JAN/66
EECL | OT216044 | OP | Operational |  | 2024-01-02 | 202401 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 822490 | 2024 | 24NQ0136 | 2024-01-02 21:48 | 2024-01-03 01:06 | COMP | Completed |  | Hot | North Queensland | Unplanned Outage | HV-Conductor Connection Failure | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ |  | REID RIVER: FLINDERS HWY | F-2870-s - Crews advised there is a broken cross-arm near Sub TVS547. access will be required beyond HV Fuses Cardington NO.2 to make repairs. | Crews advised there is a broken cross-arm near Sub TVS547. access will be required beyond HV Fuses Cardington NO.2 to make repairs. Fault Job F-2870-s created Asset selection modified issued to REDACTED 408 064 502 Crew ID - TWVOC02 Sending Asset Event to FFA FFA Order Created F-AE24NQ0136-1-0 DfltHost FFA Order Acknowledged F-AE24NQ0136-1-0 twvoc02 REDACTED 0408064502 Crew have isolated and made safe but run out of hrs. another crew is heading to site to make repairs. Time On modified from 23:59 03-Jan to 09:00 03-Jan Sending Asset Event to FFA FFA Order En Route F-AE24NQ0136-1-0 twvoc02 FFA Order On Site F-AE24NQ0136-1-0 twvoc02 Sending Asset Event to FFA FFA Order F-AE24NQ0136-1-0 Completed by technician REDACTED in crew TWVOC02(0408064502) with code A-T-304 - HV-Conductor Connection Failure Action Taken : Replaced broken HV term arm. Site Label : 5001333 Time On modified from 09:00 03-Jan to 06:34 03-Jan | 1 | 2443084 | cardington stn off cardington rd calcium | 822490 | 5001333 | 2443084 | 2021-12-15 | 748 | N |  |  | 12.5 | 3 |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | RI RED IRONBARK | 8 kiloNewton | 1970 | -19.8225 | 146.8179 | 000002443084 | 01/JAN/70
EECL | OT222866 | OP | Operational |  | 2024-01-30 | 202401 | Crossarm | Xarm, Wood Dressing | Broken | Rot/Decay |  | 11kV |  |  |  | 1268473 | 2024 | 24WB2526 | 2024-01-30 15:54 | 2024-01-30 16:27 | COMP | Completed |  | Wet / Rain | Wide Bay | Unplanned Outage | Distribution substation | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | GT |  | NIKENBAH: MADSEN RD URRAWEEN: HANOVER DR, MADSEN RD, TUDOR AVE, WINDSOR WAY | 11kV Pole Dist Sub 8026 crews need access to replace a HV Bridging arm. Access from the EDO's | 11kV Pole Dist Sub 8026 crews need access to replace a HV Bridging arm. hboc01 Sending Asset Event to FFA FFA Order Created F-AE24WB2526-1-0 DfltHost Time On modified from 23:59 30-Jan to 18:30 30-Jan FFA Order Acknowledged F-AE24WB2526-1-0 hboc01 REDACTED 0409487057 Sending Asset Event to FFA FFA Order En Route F-AE24WB2526-1-0 hboc01 FFA Order On Site F-AE24WB2526-1-0 hboc01 Time On modified from 18:30 30-Jan to 18:02 30-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE24WB2526-1-0 hboc01 FFA Order En Route F-AE24WB2526-1-0 hboc01 FFA Order On Site F-AE24WB2526-1-0 hboc01 FFA Order F-AE24WB2526-1-0 Completed by technician REDACTED in crew hboc01() with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced rotten HV bridging arm Site Label : 3001446 Time On modified from 18:02 30-JAN to 18:00 30-JAN | 1 | 2480123 | 22 WINDSOR WAY URRAWEEN | 1268473 | 3001445 | 2480123 | 2020-07-03 | 1306 | N |  |  | 12.5 | 2 | 2 | Serviceable | Y | Urb inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 8 kiloNewton | 1981 | -25.3066 | 152.8151 | 000002480123 | 01/JAN/81
EECL | OT215572 | OP | Operational |  | 2024-01-01 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | LV |  |  |  | 8854142 | 2024 | 24FN0011 | 2024-01-01 13:56 | 2024-01-01 16:59 | COMP | Completed |  |  | Far North | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 3130 MAREEBA RD;YALKULA QLD 4871 | Fault occurred at:01/01/2024 13:19; REDACTED, 0413603205;>OPD --> DimFlickeringlights:NO -- NeighboursAffected:UNSURE -- MultiplePhaseCheck:YES -- CheckSwitchboard:YES<;Incident Details:Customer advises since TX was installed at property, frequent issues occur with part loss of power.;COVID-19:NO;Warnings[opdSafety]: ADVISED;Dog restraint:HOUSE;Sensitive Load:N |  | 1 | 2485677 | 3130 Mulligan Hwy Mt Molloy | 8854142 | 5008286 | 2485677 | 2020-08-18 | 1231 | N |  |  | 11 |  | 1 | Serviceable | Y | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1976 | -16.7325 | 145.3517 | 000002485677 | 01/JAN/76
EECL | OT218481 | OP | Operational |  | 2024-01-16 | 202401 | Crossarm | Xarm, Wood Termination | Deteriorated | Termites |  | 11kV |  |  |  | 1462897 | 2024 | 24MK0385 | 2024-01-16 08:53 | 2024-01-16 08:56 | COMP | Completed |  | Fine | Mackay | Unplanned Outage | Animal nesting/burrowing | Fallen Power Lines | due to fallen power lines. | FE |  | NEBO | F-2985-s - NEBO 11kV N1/1 Fdr CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface Powerlink Investigating to determine if TX Fault. Left a message with REDACTED to call back for patrol requirements Depot Co-ord Advised Reason for Event changed from Unknown Lines Down F/C 2398387 Crew on Route F-2985-s Issued to mnboc01. Sending Asset Event to FFA FFA Order Created F-AE24MK0385-1-0 DfltHost FFA Order Acknowledged F-AE24MK0385-1-0 mnboc01 REDACTED 0456111038 Manual Reclose Checklist Sending Asset Event to FFA HV Wires Down Sending Asset Event to FFA Conductor beyond LKS2918 isolated and earthed due to lines down Fault Call Sending Asset Event to FFA FFA Order En Route F-AE24MK0385-1-0 mnboc01 FFA Order On Site F-AE24MK0385-1-0 mnboc01 Feeder restored upto LKS2918 and work commencing on Repairs Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 16-Jan to 15:00 16-Jan Sending Asset Event to FFA FFA Order En Route F-AE24MK0385-1-0 mnboc01 FFA Order On Site F-AE24MK0385-1-0 mnboc01 Restoration Comments for F-AE24MK0385-1-0 by mnboc01: replace arm. Conductor heights checked and above stat height Reversal underway Time On modified from 15:00 16-Jan to 15:30 16-Jan Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 15:30 16-Jan to 15:16 16-Jan Sending Asset Event to FFA FFA Order F-AE24MK0385-1-0 Completed by technician REDACTED in crew mnboc01(0438515383) with code A-T-301 - Animal nesting/burrowing Action Taken : x-arm eaten out by termites x-arm replaced and wires measured above stat heights Site Label : 4019997 auto-completed | 1 | 2507542 | 537 Airport Rd Nebo | 1462897 | 4019997 | 2507542 | 2023-12-11 | 36 | N |  |  | 12.5 | 3 |  | Unserviceable - P2 | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1998 | -21.7029 | 148.692 | 000002507542 | 01/JAN/98
EECL | OT217682 | OP | Operational |  | 2024-01-11 | 202401 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | LV |  |  |  | 1587948 | 2024 | 24NQ0612 | 2024-01-11 11:05 | 2024-01-11 10:25 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | GT |  | HOME HILL: EIGHTH AVE, NINTH AVE, NINTH ST | REDACTED advises that there is a broken LV cross arm at pole# 5013804 - Crews will requires access to LV only at 11kV Pole Dist Sub BDS1629 | REDACTED advises that there is a broken LV cross arm at pole# 5013804 - Crews will requires access to LV only at 11kV Pole Dist Sub BDS1629 Issued to hhlfr01 REDACTED Time Off modified from 11:20 11-Jan to 10:24 11-Jan Sending Asset Event to FFA FFA Order Created F-AE24NQ0612-1-0 DfltHost FFA Order Acknowledged F-AE24NQ0612-1-0 hhlfr01 REDACTED 0419299921 Sending Asset Event to FFA Time Off modified from 10:24 11-Jan to 11:05 11-Jan Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ0612-1-0 hhlcm13 REDACTED 0428839149 FFA Order En Route F-AE24NQ0612-1-0 hhlcm13 FFA Order On Site F-AE24NQ0612-1-0 hhlcm13 Time On modified from 23:59 11-Jan to 11:52 11-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24NQ0612-1-0 Completed by technician REDACTED in crew hhlcm13(0428839149) with code A-F-C - Completed Action Taken : Replaced broken LV strain crossarm. Site Label : 5013804 Actual Power Restoration for F-AE24NQ0612-1-0: 11-JAN-2024 12:00:00 | 1 | 2514325 | cnr.9TH ST/9TH AVE HOME | 1587948 | 5013804 | 2514325 | 2022-05-04 | 617 | N |  |  | 12.5 |  | 2 | Serviceable | N | Rrl Toff | WOOD (GREEN) SALT IMPREG CCA | Concrete Pre Cut | Footpath | SG SPOTTED GUM | 8 kiloNewton | 1972 | -19.6622 | 147.4149 | 000002514325 | 01/JAN/72
EECL | OT219159 | OP | Operational |  | 2024-01-19 | 202401 | Crossarm | Xarm, Wood Intermediate | Split | Rot/Decay |  | 11kV |  |  |  | 858684 | 2024 | 24SW1383 | 2024-01-19 14:31 | 2024-01-19 14:38 | COMP | Completed |  | Fine | South West | Unplanned Outage | Lightning | Transient Fault of Unknown Origin | our repair crews are attending. Fault finding is in progress. | SZ |  | BRANCHVIEW: LONE PINE RD BROOKSTEAD: BOSTOCK RD, BROOKSTEAD NORWIN RD, DOOLEY RD, LONE PINE RD | F- 2223-r 11kV Sectionaliser SC794369 SEF Trip | 11kV Sectionaliser SC794369 SEF Trip left message with co-ord Depot Co-ord Advised Storm in Area miloc02 Sending Asset Event to FFA FFA Order Created F-AE24SW1383-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW1383-1-0 miloc02 REDACTED 0428052254 FFA Order En Route F-AE24SW1383-1-0 miloc02 FFA Order On Site F-AE24SW1383-1-0 miloc02 HV Wires Down Manual Reclose Checklist Sending Asset Event to FFA Lines down at PE06595 isolated and earthhed. 16:00 hrs - Supply restored up to DL594414.. Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 19-Jan to 19:03 19-Jan Sending Asset Event to FFA Time On modified from 19:03 19-Jan to 20:03 19-Jan Sending Asset Event to FFA Time On modified from 20:03 19-Jan to 23:03 19-Jan Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Time On modified from 23:03 19-Jan to 23:40 19-Jan Sending Asset Event to FFA Time On modified from 23:40 19-Jan to 23:10 19-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE24SW1383-1-0 miloc02 FFA Order On Site F-AE24SW1383-1-0 miloc02 FFA Order F-AE24SW1383-1-0 Completed by technician REDACTED in crew miloc02(0428052254) with code A-T-317 - Severe Weather Action Taken : isolated for call crew Site Label : 2326519 | 1 | 2560463 | TX,opp 1390 Brookstead-Norwin Rd,B'view | 858684 | 3236519 | 2560463 | 2023-03-10 | 315 | N |  |  | 17 | 4 |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Soil | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1969 | -27.6675 | 151.3725 | 000002560463 | 01/JAN/69
EECL | OT218358 | OP | Operational |  | 2024-01-15 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1520844 | 2024 | 24SW1046 | 2024-01-15 13:43 | 2024-01-15 13:45 | COMP | Completed |  | Fine | South West | Unplanned Outage | Lightning | Lightning / Storm | due to damage caused by storm activity. | FC |  | NORWIN: BARLOWS RD CECIL PLAINS: WATSON RD, NANGWEE RD, QUIRE RD W, MCPHERSON RD, BRANCH VIEW RD, TOOWOOMBA CECIL PLAINS RD | F-2881-q - CECIL PLAINS 11kV Nangwee Rd CB603287 CB tripped. SCADA Interface automated outage. FFA Order F-AE24SW1046-1-0 Completed by technician REDACTED in crew twmoc04(0409997610) with code A-T-62 - Lightning Action Taken : replace broken x arm Site Label : 3248089 | entered from the SCADA Interface REDACTED to Advise Depot Co-ord Advised Storm in Area miloc01 Sending Asset Event to FFA FFA Order Created F-AE24SW1046-1-0 DfltHost FFA Order Acknowledged F-AE24SW1046-1-0 miloc01 REDACTED 0437712850 FFA Order En Route F-AE24SW1046-1-0 miloc01 Crew advise wire down on crossarm at SL 3248089. Isolation at GS893270 to restore supply up to here. Sending Asset Event to FFA reassigned to twmoc04 Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW1046-1-0 twmoc04 REDACTED 0409997610 FFA Order En Route F-AE24SW1046-1-0 twmoc04 FFA Order On Site F-AE24SW1046-1-0 twmoc04 . Sending Asset Event to FFA Time On modified from 23:59 15-Jan to 18:59 15-Jan Sending Asset Event to FFA FFA Order F-AE24SW1046-1-0 Completed by technician REDACTED in crew twmoc04(0409997610) with code A-T-62 - Lightning Action Taken : replace broken x arm Site Label : 3248089 Reason for Event changed from Unknown | 1 | 2629164 | by 6697 Tba/Cecil Plains Rd,C.Plains | 1520844 | 3248089 | 2629164 | 2023-08-10 | 158 | N |  |  | 12.5 | 2 |  | Serviceable | N | Rrl Toff | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -27.5494 | 151.3161 | 000002629164 | 01/JAN/89
EECL | OT217340 | OP | Operational |  | 2024-01-09 | 202401 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Termites |  | 11kV |  |  |  | 1880467 | 2024 | 24NQ0539 | 2024-01-09 14:38 | 2024-01-09 14:43 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FC |  | GIRU: BAHR RD, PILCHOWSKI RD, POLETTO RD, SHIRBOURNE RD, TODESCHINO RD, UPPER HAUGHTON RD | F-2937-s - GIRU NO.02-PILCHOWSKIRD NO.02 ACR opened for public safety due to reports of broken cross-arm, refer to F/C 2396642. | F-2937-s - GIRU NO.02-PILCHOWSKIRD NO.02 ACR opened for public safety due to reports of broken cross-arm, refer to F/C 2396642. REDACTED 0408 689 718 heading to site. Crew ETA 1530 hrs. Time Off modified from 15:30 09-Jan to 14:38 09-Jan Isolated & Earthed at DO803493 reclosed At 1604 Asset selection modified Sending Asset Event to FFA FFA Order Created F-AE24NQ0539-1-0 DfltHost FFA Order Acknowledged F-AE24NQ0539-1-0 hhlfr01 REDACTED 0408689718 FFA Order En Route F-AE24NQ0539-1-0 hhlfr01 FFA Order On Site F-AE24NQ0539-1-0 hhlfr01 Time On modified from 23:59 09-Jan to 16:50 09-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24NQ0539-1-0 Completed by technician REDACTED in crew hhlfr01(0408689718) with code A-F-C - Completed Action Taken : REPLACED BROKEN XARM POLE ALREADY NAILED AND HAS TERMITES. NEEDS TO BE CHANGED IN NEAR FUTURE H1 Site Label : 5052692 | 1 | 2746664 | AccesRiverbank.576UpperHaughtonRd.Giru | 1880467 | 5052692 | 2746664 | 2021-06-06 | 947 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass |  | RM RED MAHOGANY | 8 kiloNewton | 1966 | -19.6071 | 147.1111 | 000009384979
EECL | OT216458 | OP | Operational |  | 2024-01-04 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1488368 | 2024 | 24SW0331 | 2024-01-04 15:59 | 2024-01-04 16:02 | COMP | Completed |  | Fine | South West | Unplanned Outage | HV-Conductor Connection Failure | Fallen Power Lines | due to fallen power lines. | FC |  | BRINGALILY, KOOROONGARRA, MILLMERRAN, MILLWOOD, MOUNT EMLYN | F-2092-r MILLMERRAN 11kV Millwood CB4408 ACR CB tripped. SCADA Interface automated outage. Made Safe sent from FFA for F-FC2395558-1-0 by miloc01 REDACTED 0436468579 Event Related To : HV Site - Isolated and earthed Restoration Comments for F-FC2395558-1-0 by miloc01 REDACTED 0436468579: Attended site, found broken cross arm and conductor and pin fallen to ground. Grass fire was started with local farmers on site to put it out. Isolated and earthed the conductors. Returned to depot to gather cross arms and equipment to replace cross arm, reinstate the conductor and restore supply. | entered from the SCADA Interface Depot Co-ord Advised EF/SEF fault downstream of 11kV Sectionaliser SEC609021. Successfully reclosed up to SEC. . Asset selection modified 11kV Sectionaliser SEC609021 currently has syscon for low gas alarm active hence reason for it not operating sec fdr. miloc01 REDACTED Sending Asset Event to FFA FFA Order Created F-AE24SW0331-1-0 DfltHost Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Time On modified from 23:59 04-Jan to 20:37 04-Jan Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW0331-1-0 miloc01 REDACTED 0436468579 Sending Asset Event to FFA FFA Order En Route F-AE24SW0331-1-0 miloc01 FFA Order On Site F-AE24SW0331-1-0 miloc01 FFA Order En Route F-AE24SW0331-1-0 miloc01 FFA Order On Site F-AE24SW0331-1-0 miloc01 FFA Order F-AE24SW0331-1-0 Completed by technician REDACTED in crew miloc01(0428052254) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Attended site and found broken cross arm resulting to conductor falling to ground and starting grass fire. Fire put out and repairs to cross arm and another in poor condition. Supply restored. Site Label : 3048197 | 1 | 2749132 | by 230 Paton Rd,Bringalily | 1488368 | 3048197 | 2749132 | 2019-10-22 | 1535 | N |  |  | 14 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 3 kiloNewton | 1975 | -28.0839 | 151.2058 | 000002749132 | 01/JAN/75
EECL | OT217869 | OP | Operational |  | 2024-01-12 | 202401 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1770596 | 2024 | 24NQ0647 | 2024-01-12 10:32 | 2024-01-12 10:38 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FC |  | GIRU: GEARY RD, SANDY CAMP RD, WOODSTOCK RD MAJORS CREEK: WOODSTOCK GIRU RD | F-988-t 11kV Recloser Spring Creek No.1 opened due to lines down at Sub BDS1974 | 11kV Recloser Spring Creek No.1 opened due to lines down at Sub BDS1974 Fault sheet F-988-t Time Off modified from 11:00 12-Jan to 10:32 12-Jan Crew advise of a repair time of 3hrs HV Wires Down Crew have completed repairs and customers restored @ 1227 Asset selection modified Time On modified from 15:00 12-Jan to 12:34 12-Jan Fault Call was 1402 woodstock giru rd Majors Creek (Call id 2397482.) HV Termination arm broke on pole 5062457 (Adjacent BDS1974). 11kV Lines were 6 feet off the ground so spring 11kV Spring Creek No.1 Recloser never operated . Crew attending was REDACTED . auto-completed | 1 | 2803847 | Rrl.1402 Woodstock Giru Rd Majors Crk | 1770596 | 5062457 | 2803847 | 2021-07-07 | 919 | N |  |  | 12.5 | 2 |  | Serviceable | Y | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | GI GREY IRONBARK | 8 kiloNewton | 1988 | -19.6032 | 147.0246 | 000002803847 | 01/JAN/88
EECL | OT218646 | OP | Operational |  | 2024-01-17 | 202401 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | LV |  |  |  | 1196011 | 2024 | 24WB0746 | 2024-01-17 08:51 | 2024-01-17 21:13 | COMP | Completed |  | Fine | Wide Bay | Unplanned Outage | LV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | 172 HUXLEY RD;CHILDERS QLD 4660 | Fault occurred at:17/01/2024 08:46; REDACTED, 0428796055;>WDPB --> HasComeAway:UNSURE,AffectingTraffic:NO -- StillHavePower:NO<;Incident Details:Service Lines hanging low, low enough can reach up and touch - Crossarm broken on Pole. Cust has Partial LOS and dim power.;Access Details:PEACE NOTES ADV D2 UNREST, EC advised no dogs pls take precautions.;COVID-19:UNKNOWN;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N |  | 1 | 2820523 | lane 174HuxleyRdChilders | 1196011 | 3064027 | 2820523 | 2020-04-21 | 1366 | N |  |  | 14 |  | 1 | Serviceable | N | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Soil | Road Reserve | SG SPOTTED GUM | 12 kiloNewton | 1990 | -25.2194 | 152.2627 | 000002820523 | 01/JAN/90
EECL | OT220200 | OP | Operational |  | 2024-01-24 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1465480 | 2024 | 24SW3612 | 2024-01-24 14:05 | 2024-01-24 18:07 | COMP | Completed |  |  | South West | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 4313 OAKEY COOYAR RD HIGHGROVE QLD 4352 | EE employee REDACTED called in a broken cross arm @ S/L3082279. P1 Call Flag |  | 1 | 2903145 | access 4313 Oakey Cooyar rd, Highgrove | 1465480 | 3082279 | 2903145 | 2023-05-25 | 244 | N |  |  | 12.5 | 1 |  | Unserviceable - P2 | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton |  | -27.1075 | 151.7773 | 000002903145 | 01/JAN/66
EECL | OT217139 | OP | Operational |  | 2024-01-08 | 202401 | Crossarm | Xarm, Wood Termination | Split | Rot/Decay |  | 11kV |  |  |  | 934524 | 2024 | 24CA0542 | 2024-01-08 16:57 | 2024-01-08 16:48 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | THE CAVES: FOURTEEN MILE RD, PAPERBARK DR | F-2830-q 11kV Dropout Fuse S5239 openned to repair broken X/arm | 11kV Dropout Fuse S5239 openned to repair broken X/arm Time Off modified from 17:00 08-Jan to 16:57 08-Jan Time On modified from 19:00 08-Jan to 18:48 08-Jan | 1 | 2912867 | tx hse 16 Paperbark Drive, the caves | 934524 | 4090925 | 2912867 | 2021-05-27 | 956 | N |  |  | 12.5 | 1 |  | Serviceable | Y | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Backyard | SG SPOTTED GUM | 8 kiloNewton | 1980 | -23.1951 | 150.4993 | 000002912867 | 01/JAN/80
EECL | OT216764 | OP | Operational |  | 2024-01-05 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 22kV |  |  |  | 949789 | 2024 | 24CA0450 | 2024-01-05 08:00 | 2024-01-06 06:41 | COMP | Completed |  | Fine | Capricornia | Unplanned Outage | Severe Weather | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ |  | BOOLBURRA, DINGO, DUARINGA, EDUNGALBA | Forced to Replace Broken Xarm Between Switch X8258 & 3278 | Forced to Replace Broken Xarm Between Switch X8258 & 3278 blwoc01 Sending Asset Event to FFA FFA Order Created F-AE24CA0450-1-0 DfltHost FFA Order Acknowledged F-AE24CA0450-1-0 blwoc01 REDACTED 0467388353 FFA Order En Route F-AE24CA0450-1-0 blwoc01 FFA Order On Site F-AE24CA0450-1-0 blwoc01 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 06-Jan to 10:29 06-Jan Sending Asset Event to FFA FFA Order En Route F-AE24CA0450-1-0 blwoc01 FFA Order On Site F-AE24CA0450-1-0 blwoc01 Sending Asset Event to FFA FFA Order F-AE24CA0450-1-0 Completed by technician REDACTED in crew BLWOC01(0467388353) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : switching and access changed x arm and fuse Site Label : 4094408 | 1 | 2926108 | 4nthSP317617TELSTRA TWR cap hwy dingo | 949789 | 4094408 | 2926108 | 2021-10-12 | 815 | N |  |  | 12.5 | 2 |  | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1989 | -23.6665 | 149.4849 | 000002926108 | 01/JAN/89
EECL | OT223055 | OP | Operational |  | 2024-01-31 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | LV |  |  |  | 1791136 | 2024 | 24CA2478 | 2024-01-31 06:10 | 2024-01-31 15:07 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 23 RUFUS ST;BLACKWATER QLD 4717 | Fault occurred at:31/01/2024 06:07; REDACTED, 0428285367;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details:Broken Cross arm has broken and resting on powerlines.;COVID-19:N/A;Warnings[uphSafety]: ADVISED;Sensitive Load:N |  | 1 | 2927722 | 25 Rufus St Blackwater | 1791136 | 4094814 | 2927722 | 2019-05-11 | 1726 | N |  |  | 11 | 1 | 2 | Serviceable | N | HV lower cct Toff | WOOD (GREEN) SALT IMPREG CCA | Lawn | Front Yard | SG SPOTTED GUM | 8 kiloNewton | 1966 | -23.5833 | 148.8832 | 000002927722 | 01/JAN/66
EECL | OT220534 | OP | Operational |  | 2024-01-25 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 22kV |  |  |  | 1205746 | 2024 | 24SW3669 | 2024-01-25 16:32 | 2024-01-25 16:35 | COMP | Completed | M | Fine | South West | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to a SCADA Automated Event | FC |  | MORVEN, MUNGALLALA | F-30779-g CHARLEVILLE 22kV Est Somarva W Hwy RC807285 ACR CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface on call coordiator ringing back with pad number Depot Co-ord Advised chrcmfr06 Sending Asset Event to FFA FFA Order Created F-AE24SW3669-1-0 DfltHost FFA Order Acknowledged F-AE24SW3669-1-0 chrcmfr06 REDACTED 0427542289 Tripped on OC and SEF Sending Asset Event to FFA FFA Order En Route F-AE24SW3669-1-0 chrcmfr06 Crews found broken cross arm at SL6029471 Sending Asset Event to FFA FFA Order On Site F-AE24SW3669-1-0 chrcmfr06 Time On modified from 23:59 25-Jan to 21:16 25-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW3669-1-0 Completed by technician REDACTED in crew chrcmfr06(0427542289) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced broken cross arm Site Label : 6029471 auto-completed | 1 | 2994962 | 29 E AB6621, 67906 Joylands Rd C'hville | 1205746 | 6029471 | 2994962 | 2023-11-12 | 74 | N |  |  | 11 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1969 | -26.4079 | 146.6423 | 000002994962 | 01/JAN/69
EECL | OT221193 | OP | Operational |  | 2024-01-26 | 202401 | Crossarm | Xarm Bracket Nuts | Deteriorated | Unknown |  | 11kV |  |  |  | 1614077 | 2024 | 24NQ3451 | 2024-01-26 16:17 | 2024-01-28 15:25 | CAN | Cancelled |  | Hot | North Queensland | Unplanned Outage | Severe Weather | Unknown | Single Fault Call | GT |  | 147 RUDDYS RD;AYR QLD 4807 | Fault occurred at:26/01/2024 16:14; Con, 0417637390;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details:Timber cross arm slumped not holding the hvs properly/ on an angle, halfway down Ruddys Rd;COVID-19:N/A;Warnings[uphSafety]: ADVISED;Sensitive Load:N | outage cancelled via Clash Wizard | 1 | 2995995 | rural mkr.198 ruddy rd.Jarvisfield Ayr | 1614077 | 5102464 | 2995995 | 2023-08-03 | 176 | N |  |  | 12.5 | 3 |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | BI BROAD LEAF IRONBARK | 8 kiloNewton | 1998 | -19.5856 | 147.4722 | 000002995995 | 01/JAN/98
EECL | OT221797 | OP | Operational |  | 2024-01-28 | 202401 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 22kV |  |  |  | 1173077 | 2024 | 24SW3782 | 2024-01-28 10:03 | 2024-01-28 09:46 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE |  | CHARLEVILLE, COOLADDI, MORVEN, MUNGALLALA | F-2323-r: 22kV Disc Links DL590756 - Broken cross arm requires repair. | 22kV Disc Links DL590756 - Broken cross arm requires repair. chrcmfr05 Sending Asset Event to FFA FFA Order Created F-AE24SW3782-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Time Off modified from 10:00 28-Jan to 10:03 28-Jan Sending Asset Event to FFA 1013: CB7943 Close; Open at AB6630. Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 14:00 28-Jan to 13:47 28-Jan Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW3782-1-0 chrcmfr05 REDACTED 0436487373 FFA Order En Route F-AE24SW3782-1-0 chrcmfr05 FFA Order On Site F-AE24SW3782-1-0 chrcmfr05 Sending Asset Event to FFA FFA Order F-AE24SW3782-1-0 Completed by technician REDACTED in crew CHRCMFR05(0436487373) with code A-F-C - Completed Action Taken : replaced broken 22kV single phase link arm Site Label : 6014167 | 1 | 2996792 | T2 PW2309 acc 222 Wintara Rd C'hville | 1173077 | 6014167 | 2996792 | 2023-11-29 | 60 | N |  |  | 14 | 2 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | BB BLACKBUTT | 5 kiloNewton | 1988 | -26.4523 | 146.2592 | 000002996792 | 01/JAN/88
EECL | OT217116 | OP | Operational |  | 2024-01-08 | 202401 | Crossarm | Xarm Strap(S) | Loose Fitting | Vibration |  | 11kV |  |  |  | 1392720 | 2024 | 24WB0308 | 2024-01-08 12:23 | 2024-01-08 13:00 | COMP | Completed |  | Fine | Wide Bay | Unplanned Outage | HV-Conductor Connection Failure | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ |  | BOOIE, COOLABUNIA, KINGAROY, NANANGO, WATTLE CAMP | F-2124-r - 11kV Air Break AB855612 - Crews require acces to repair/replace broken cross arm brace | F-2124-r - 11kV Air Break AB855612 - Crews require acces to repair/replace broken cross arm brace Sending Asset Event to FFA FFA Order Created F-AE24WB0308-1-0 DfltHost kngcm07 Sending Asset Event to FFA Outage put in wrong, all people beyond S202 will loose power to rectify this HV cross arm Sending Asset Event to FFA Primary Asset de-escalated from Barkers Ck Rd Fdr Comp (FC) Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 08-Jan to 14:05 08-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB0308-1-0 kngcm07 REDACTED 0417850599 FFA Order En Route F-AE24WB0308-1-0 kngcm07 FFA Order On Site F-AE24WB0308-1-0 kngcm07 FFA Order F-AE24WB0308-1-0 Completed by technician REDACTED in crew KNGCM07(0417850599) with code A-T-30 - Vibration Action Taken : install cross arm brace coach screw Site Label : 3114792 | 1 | 3058080 | 108 Schellbachs rd,Booie | 1392720 | 3114792 | 3058080 | 2023-11-16 | 53 | N |  |  | 15.5 | 2 |  | Serviceable | N | Rrl inter spn <200m | WOOD UNTREATED ROUND | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton |  | -26.526 | 151.8937 | 000003058080 | 01/JAN/50
EECL | OT216913 | OP | Operational |  | 2024-01-07 | 202401 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay |  | LV |  |  |  | 1008764 | 2024 | 24FN0218 | 2024-01-07 09:11 | 2024-01-07 10:27 | COMP | Completed |  |  | Far North | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | GT |  | HOPE VALE: KERNICH ST, KOTZUR ST, ROSE ST | event extracted from 24FN0217 Made Safe sent from FFA for F-FC2396152-1-0 by cktcsfr01 REDACTED 0436418642 Event Related To : LV Site - Isolated (eg. removal of fuse, cutting/breaking bridges etc) Restoration Comments for F-FC2396152-1-0 by cktcsfr01 REDACTED 0436418642: Lv tx fuses open and dnobed on ss7680 and all Lv tie points confirmed open . | Event extracted from 24FN0217 Made Safe sent from FFA for F-FC2396152-1-0 by cktcsfr01 REDACTED 0436418642 Event Related To : LV Site - Isolated (eg. removal of fuse, cutting/breaking bridges etc) Restoration Comments for F-FC2396152-1-0 by cktcsfr01 REDACTED 0436418642: Lv tx fuses open and dnobed on ss7680 and all Lv tie points confirmed open . , LV opened and db=nobed to make repairs Sending Asset Event to FFA FFA Order Created F-AE24FN0218-1-0 DfltHost FFA Order Acknowledged F-AE24FN0218-1-0 cktcsfr01 REDACTED 0436418642 FFA Order En Route F-AE24FN0218-1-0 cktcsfr01 FFA Order On Site F-AE24FN0218-1-0 cktcsfr01 FFA Order F-AE24FN0218-1-0 Completed by technician REDACTED in crew cktcsfr01(0436418642) with code A-F-C - Completed Action Taken : replaced two Lv pin arms, power restored Site Label : 5114221, 5114223 Time On modified from 23:59 07-JAN to 13:45 07-JAN | 1 | 3074464 | kotzur st drainway hopevale | 1008764 | KO3 | 3074464 | 2021-08-03 | 887 | N |  |  | 11 |  | 1 | Serviceable | Y | Rrl inter spn <100m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -15.2979 | 145.1119 | 000003074464 | 01/JAN/72
EECL | OT217423 | OP | Operational |  | 2024-01-10 | 202401 | Crossarm | Xarm, Wood Dressing | Loose Fitting | Vibration |  | 11kV |  |  |  | 1505228 | 2024 | 24SW0690 | 2024-01-09 22:25 | 2024-01-09 21:55 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | FORMARTIN, NORWIN, ST RUTH, TIPTON, WEST PRAIRIE | 11kV Disc Links DL8578 - Broken Cross arm Beyond | 11kV Disc Links DL8578 - Broken Cross arm Beyond Time On modified from 23:59 09-Jan to 03:00 10-Jan Asset selection reset Asset selection modified Isolation from CB6044446 Time Off modified from 22:30 09-Jan to 22:24 09-Jan Sending Asset Event to FFA FFA Order Created F-AE24SW0690-1-0 DfltHost FFA Order Acknowledged F-AE24SW0690-1-0 twmug06 FFA Order En Route F-AE24SW0690-1-0 twmug06 FFA Order On Site F-AE24SW0690-1-0 twmug06 Restoration Comments for F-AE24SW0690-1-0 by twmug06: CURRENTLY CHANGING STRAIN ARM Time On modified from 03:00 10-Jan to 06:00 10-Jan Sending Asset Event to FFA Time On modified from 06:00 10-Jan to 08:00 10-Jan Sending Asset Event to FFA twmfrcm01 Sending Asset Event to FFA Crew advise heading back to site to perform reverse switching, 1 hour away traavel time Time On modified from 08:00 10-Jan to 11:00 10-Jan Sending Asset Event to FFA Time On modified from 11:00 10-Jan to 10:38 10-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW0690-1-0 twmfrcm01 REDACTED 0418712115 FFA Order En Route F-AE24SW0690-1-0 twmfrcm01 FFA Order On Site F-AE24SW0690-1-0 twmfrcm01 FFA Order F-AE24SW0690-1-0 Completed by technician REDACTED in crew twmfrcm01(0418712115) with code A-F-C - Completed Action Taken : repaired loose arm brace and coach screw Site Label : 3132975 | 1 | 3150472 | 1plE PE11282,acc Smith Rd,Norwin | 1505228 | 3132975 | 3150472 | 2022-11-30 | 406 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 5 kiloNewton |  | -27.5034 | 151.3329 | 000003150472 | 01/JAN/69
EECL | OT217397 | OP | Operational |  | 2024-01-09 | 202401 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1508369 | 2024 | 24SW0730 | 2024-01-09 19:13 | 2024-01-10 12:13 | COMP | Completed |  | Storm Electrical | South West | Unplanned Outage | HV-Conductor Connection Failure | Unknown | Single Fault Call | GT |  | LOT 2 OLSENS RD;BOWENVILLE QLD 4404 | 3rd Party->Fault occurred at:09/01/2024 19:08; REDACTED, 0418795680;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details: REDACTED (passerby) advised broken x-arm. Wires not low but very close together. Logged under closest NMI. Closest pole is 3132981. The damaged pole is in a paddock;COVID-19:UNKNOWN;Warnings[uphSafety]: ADVISED;Sensitive Load:N |  | 1 | 3155998 | 6plS PE3435,905 Jefferies Rd,Tipton | 1508369 | 3133909 | 3155998 | 2022-12-14 | 391 | N |  |  | 14 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -27.478 | 151.306 | 000003155998 | 01/JAN/69
EECL | OT220491 |  | Operational |  | 2024-01-25 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Termites |  | 11kV |  |  |  | 836827 | 2024 | 24NQ3572 | 2024-01-25 15:41 | 2024-01-29 13:05 |  | Cancelled |  | Wet / Rain | North Queensland | Unplanned Outage | Animal nesting/burrowing | Unknown | Single Fault Call | GT |  | 8124 DALBEG RD;DALBEG QLD 4807 | Fault occurred at:25/01/2024 15:38; REDACTED, 0427885245;>WDPP --> AffectingTraffic:NO -- StillHavePower:NO<;Incident Details:Main lines down on side of the road. Full LOS. Crossarm appears to have failed, no vegetation around lines etc.;COVID-19:NO;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N | outage cancelled via Clash Wizard | 1 | 3171099 | 8476Ayr-DalbegRdToForeman-WalshRdDalbeg | 836827 | 5128582 | 3171099 | 2019-11-27 | 1520 | N |  |  | 17 | 2 |  | Serviceable | N | 66kV rrl inter | WOOD UNTREATED ROUND | Grass | Road Reserve | ZR UNKNOWN RED SPECI | Unknown |  | -20.2548 | 147.3055 | 000003171099 | 01/JAN/56
EECL | OT217393 | OP | Operational |  | 2024-01-09 | 202401 | Crossarm | Xarm, Wood Strain | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1496130 | 2024 | 24MK0253 | 2024-01-09 18:25 | 2024-01-09 18:27 | COMP | Completed |  | Wet / Rain | Mackay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | FOXDALE, GREGORY, GREGORY RIVER, MYRTLEVALE | F-982-t Crew have found a broken crossarm adjacent to sub 2270. | entered from the SCADA Interface SEF trip Crew attending REDACTED ETA 1920 Sending Asset Event to FFA FFA Order Created F-AE24MK0253-1-0 DfltHost FFA Order Acknowledged F-AE24MK0253-1-0 prpoc01 REDACTED 0428271177 Crew have found a broken crossarm adjacent to sub 2270. Crew currently isolating and earthing at LKS326. Sending Asset Event to FFA FFA Order En Route F-AE24MK0253-1-0 prpoc01 Recloser Closed and power restored upto LKS326 Asset selection modified Sending Asset Event to FFA FFA Order Pending F-AE24MK0253-1-0 FFA Order Acknowledged F-AE24MK0253-1-0 prpoh03 REDACTED 0437615982 FFA Order En Route F-AE24MK0253-1-0 prpoh03 FFA Order On Site F-AE24MK0253-1-0 prpoh03 Time On modified from 23:59 09-Jan to 23:43 09-Jan Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Sending Asset Event to FFA FFA Order On Site F-AE24MK0253-1-0 prpoh03 FFA Order F-AE24MK0253-1-0 Completed by technician REDACTED in crew prpoh03(0437615982) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : HV cross arm failed due to rot. Conductors fail to bellow stat height unsure if the conductors hit the ground or not, cross arm has been replaced Site Label : 4223194 | 1 | 3289823 | 254 patullo rd proserpine | 1496130 | 4223194 | 3289823 | 2020-03-13 | 1397 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl sty ang20-30o | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1993 | -20.279 | 148.5768 | 000003289823 | 01/JAN/93
EECL | OT221376 | OP | Operational |  | 2024-01-27 | 202401 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1439396 | 2024 | 24MK1392 | 2024-01-27 10:35 | 2024-01-27 10:36 | COMP | Completed |  |  | Mackay | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | GT |  | SLADE POINT: AMHURST ST, BRECKELL CT, CUMBERLAND AVE, KESWICK AVE, LINDEMAN AVE, PACIFIC ESP, PATON TCE, PELICAN ST, SOUTH PACIFIC AVE | Crew require LV isolation on 11kV Pole Dist Sub 2527 to make repairs. Crew replaced cross-arm. SL 4223751. REDACTED | Crew require LV isolation on 11kV Pole Dist Sub 2527 to make repairs. Time Off modified from 11:16 27-Jan to 10:35 27-Jan Time On modified from 23:59 27-Jan to 15:00 27-Jan Sending Asset Event to FFA FFA Order Created F-AE24MK1392-1-0 DfltHost FFA Order Acknowledged F-AE24MK1392-1-0 mckoc01 REDACTED 0439906736 FFA Order En Route F-AE24MK1392-1-0 mckoc01 FFA Order On Site F-AE24MK1392-1-0 mckoc01 FFA Order F-AE24MK1392-1-0 Completed by technician REDACTED in crew mckoc01(0439906736) with code A-F-C - Completed Action Taken : replace cross arm Site Label : 4223751 Time On modified from 15:00 27-JAN to 12:27 27-JAN Added notes to Reasons tab. | 1 | 3291021 | 16 pacific esplanade lamberts bch | 1439396 | 4223751 | 3291021 | 2020-10-04 | 1210 | N |  |  | 12.5 | 1 | 1 | Serviceable | Y | Urb HV inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1974 | -21.0712 | 149.2272 | 000003291021 | 01/JAN/74
EECL | OT218050 | OP | Operational |  | 2024-01-13 | 202401 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay |  | 66kV |  |  |  | 1226671 | 2024 | 24NQ0692 | 2024-01-13 18:26 | 2024-01-13 16:13 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | ZS |  | BOWEN: ABBOT POINT RD | F-992-t Forced outage required to replace broken 66kV Crossarm on the Abbott Point 66kV Feeder | Forced outage required to replace broken 66kV Crossarm on the Abbott Point 66kV Feeder Time Off modified from 17:00 13-Jan to 18:25 13-Jan Sending Asset Event to FFA FFA Order Created F-AE24NQ0692-1-0 DfltHost Time On modified from 23:59 13-Jan to 22:28 13-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ0692-1-0 bwnoc01 REDACTED 0439250740 FFA Order En Route F-AE24NQ0692-1-0 bwnoc01 FFA Order On Site F-AE24NQ0692-1-0 bwnoc01 FFA Order F-AE24NQ0692-1-0 Completed by technician REDACTED in crew Bwnoc01(0439250740) with code A-F-C - Completed Action Taken : replaced broken 66kv cross arm Site Label : 5169172 | 1 | 3296236 | rd 2 abbot pt 15th pole merinda | 1226671 | 5169172 | 3296236 | 2020-04-30 | 1353 | N |  |  | 17 |  |  | Serviceable | N | 66kV rrl inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | RI RED IRONBARK | 8 kiloNewton | 1981 | -19.972 | 148.0938 | 000003296236 | 01/JAN/81
EECL | OT218041 | OP | Operational |  | 2024-01-13 | 202401 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1948917 | 2024 | 24NQ0690 | 2024-01-13 12:53 | 2024-01-13 14:05 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | HV-Conductor Connection Failure | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | GT |  | KIRWAN: BAMFORD LANE, EKLUND ST, JOYCE ST, MCBRIDE ST, MILL DR | LV isolated part of 24NQ0687 Broken xarm on Mill Dr 11kV Pole Dist Sub TVS560 | LV isolated part of 24NQ0687 Broken xarm on Mill Dr 11kV Pole Dist Sub TVS560 Sending Asset Event to FFA FFA Order Created F-AE24NQ0690-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ0690-1-0 twvoc01 REDACTED 0429797521 FFA Order En Route F-AE24NQ0690-1-0 twvoc01 FFA Order On Site F-AE24NQ0690-1-0 twvoc01 Restoration Comments for F-AE24NQ0690-1-0 by twvoc01: Hv section of line is isolated at mill dr no 2 and mill dr no.3. LV isolated at TVS 560. feeder safe to re energise. Time On modified from 23:59 13-Jan to 19:00 13-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE24NQ0690-1-0 twvoc01 FFA Order On Site F-AE24NQ0690-1-0 twvoc01 FFA Order En Route F-AE24NQ0690-1-0 twvoc01 FFA Order On Site F-AE24NQ0690-1-0 twvoc01 FFA Order F-AE24NQ0690-1-0 Completed by technician REDACTED in crew twvoc01(0429797521) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Old HV cross arm snapped. HV clashed with one phase on LV on TVS560. Isolated and replaced cross arm. Replaced damaged SL head. Inspected switch boards off tvs560. Disconnected and form B customers that had suspected damage. powered up and checked voltage of transformer. all with in stat limits. Site Label : 5201813 Time On modified from 19:00 13-JAN to 21:02 13-JAN | 1 | 3301830 | 159 Mill dr Kirwan Townsville | 1948917 | 5201813 | 3301830 | 2024-01-08 | 5 | N |  |  | 12.5 | 1 | 1 | Unserviceable - P2 | N | Urb inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | SG SPOTTED GUM | 5 kiloNewton | 1975 | -19.2936 | 146.7418 | 000003301830 | 01/JAN/75
EECL | OT220939 | OP | Operational |  | 2024-01-26 | 202401 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1806632 | 2024 | 24NQ3041 | 2024-01-26 10:56 | 2024-01-26 10:17 | COMP | Completed | M |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | BEMERSIDE: GANGEMIS RD HAWKINS CREEK: BIASIS RD, CRUICKSHANKS RD, FABRIS RD, GORTONS RD, HAWKINS CREEK RD, PALMAS RD, QUABBA'S RD, RUSSOS RD INGHAM: HAWKINS CREEK RD | Crew require access to repair broken crossarm on pole near INS603 | Crew require access to repair broken crossarm on pole near INS603 Time On modified from 23:59 26-Jan to 14:00 26-Jan Switching Sheet ID updated from to J-294787-g. dispatched to REDACTED Sending Asset Event to FFA FFA Order Created F-AE24NQ3041-1-0 DfltHost FFA Order Acknowledged F-AE24NQ3041-1-0 ingcm01 REDACTED 0437534712 FFA Order En Route F-AE24NQ3041-1-0 ingcm01 Time Off modified from 10:30 26-Jan to 10:56 26-Jan Sending Asset Event to FFA FFA Order On Site F-AE24NQ3041-1-0 ingcm01 FFA Order F-AE24NQ3041-1-0 Completed by technician REDACTED in crew ingcm01(0437534712) with code A-F-C - Completed Action Taken : broken xarm replaced Site Label : 2030201 Time On modified from 14:00 26-Jan to 11:56 26-Jan | 1 | 8752667 | 3spn NE 348 hawkins crk rd ingham | 1806632 | 2030201 | 8752667 | 2022-03-04 | 693 | N |  |  | 14 |  |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | SG SPOTTED GUM | 8 kiloNewton | 2018 | -18.6279 | 146.1382 | 000008752667 | 01/JAN/18
EECL | OT227336 | OP | Operational |  | 2024-02-28 | 202402 | Crossarm | Xarm, Wood Strain | Split | Laminated |  | 11kV |  |  |  | 1354030 | 2024 | 24WB3548 | 2024-02-28 14:40 | 2024-02-28 16:52 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 359 BUCCA RD;BUCCA QLD 4670 | Fault occurred at:28/02/2024 11:26; REDACTED, 0403051125;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details:Broken cross bar on neighbours side and causing to pull cust powerline. Lines are stringing tight.;Access Details:Best to come down Kleidons Rd for entry or enter at Gate that says "Ulysses Nursery".;COVID-19:N/A;Warnings[uphSafety]: ADVISED;Sensitive Load:N |  | 1 | 2034690 | 144kleindons rd meadowvale | 1354030 | 2003477 | 2034690 | 2019-05-27 | 1738 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | FR FOREST RED GUM | 5 kiloNewton | 2000 | -24.8398 | 152.1916 | 000002034690 | 01/JAN/00
EECL | OT224631 | OP | Operational |  | 2024-02-07 | 202402 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1808994 | 2024 | 24NQ4395 | 2024-02-07 19:05 | 2024-02-07 18:27 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | ABERGOWRIE: MOORES RD | Crew Req Access to Replace Broken Crossarm following Fault Call | Crew Req Access to Replace Broken Crossarm following Fault Call Time Off modified from 19:00 07-Feb to 19:05 07-Feb Time On modified from 23:59 07-Feb to 21:41 07-Feb Sending Asset Event to FFA FFA Order Created F-AE24NQ4395-1-0 DfltHost FFA Order Acknowledged F-AE24NQ4395-1-0 ingcs02 REDACTED 0400892791 FFA Order En Route F-AE24NQ4395-1-0 ingcs02 FFA Order On Site F-AE24NQ4395-1-0 ingcs02 FFA Order F-AE24NQ4395-1-0 Completed by technician REDACTED in crew ingcs02(0400892791) with code A-F-C - Completed Action Taken : Replaced 11KV strain arm Site Label : 2122036 Actual Power Restoration for F-AE24NQ4395-1-0: 07-FEB-2024 22:57:00 auto-completed | 1 | 2327113 | 223 Moore's Rd Abergowrie | 1808994 | 2122036 | 2327113 | 2022-02-06 | 731 | N |  |  | 14 | 2 |  | Unserviceable - P2 | N | Rrl Toff | WOOD (GREEN) SALT IMPREG CCA | Soil | Sugar Cane | RI RED IRONBARK | 12 kiloNewton | 1977 | -18.499 | 145.981 | 000002327113 | 01/JAN/77
EECL | OT227506 | OP | Operational |  | 2024-02-29 | 202402 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1803553 | 2024 | 24NQ5565 | 2024-02-29 13:08 | 2024-02-29 13:41 | ANAL | Data verification |  | Wet / Rain | North Queensland | Unplanned Outage | HV-Conductor Connection Failure | HV or LV Fuse blown | due to damage requiring emergency repairs. | FC |  | ABERGOWRIE: ABERGOWRIE RD, BULLOCK CREEK RD | F-3450-s - Multiple customers with dim flickering lights beyond 11kV Dropout Fuse ABERGOWRIE NO.3 | Multiple customers with dim flickering lights beyond 11kV Dropout Fuse ABERGOWRIE NO.3 F-3450-s created FFA is down - crews are aware of call and heading there now, they will call through with details Manual Reclose Checklist Asset selection modified Abergowie No.3 HV Fuses have failed and Req Replacing Sending Asset Event to FFA FFA Order Created F-AE24NQ5565-1-0 DfltHost Sending Asset Event to FFA Time On modified from 23:59 29-Feb to 19:12 29-Feb Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ5565-1-0 ingcsfr01 REDACTED 0473145674 FFA Order En Route F-AE24NQ5565-1-0 ingcsfr01 FFA Order On Site F-AE24NQ5565-1-0 ingcsfr01 Restoration Comments for F-AE24NQ5565-1-0 by ingcsfr01: Timber crossarm broken on abergowrie No3. this has already been repaired. ABB was not working at the time FFA Order F-AE24NQ5565-1-0 Completed by technician REDACTED in crew ingcsfr01(0473145674) with code A-T-304 - HV-Conductor Connection Failure Action Taken : Double term arm broken with EDOs. EDO fuse had dislodged from holder. replaced all new Site Label : 21424654 | 1 | 2361828 | opp 4712 Abergowrie Rd Abergowrie | 1803553 | 2142465 | 2361828 | 2022-03-21 | 710 | N |  |  | 14 | 3 |  | Unserviceable - P2 | N | Rrl Toff | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | SG SPOTTED GUM | 12 kiloNewton | 1985 | -18.4456 | 145.8324 | 000002361828 | 01/JAN/85
EECL | OT226339 | OP | Operational |  | 2024-02-20 | 202402 | Crossarm | Xarm, Wood Termination | Split | Rot/Decay |  | LV |  |  |  | 766419 | 2024 | 24NQ5028 | 2024-02-20 15:38 | 2024-02-20 15:26 | CAN | Cancelled |  | Fine | North Queensland | Unplanned Outage | Service Asset Fault | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | GT |  | CHARTERS TOWERS: DEANES RD | F-3394-s - CTS847 - Replace LV Xarm | CTS847 - Replace LV Xarm Time Off modified from 15:00 20-Feb to 15:38 20-Feb Sending Asset Event to FFA FFA Order Created F-AE24NQ5028-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ5028-1-0 chtcs01 REDACTED 0467521941 FFA Order En Route F-AE24NQ5028-1-0 chtcs01 FFA Order On Site F-AE24NQ5028-1-0 chtcs01 Power restored 1732 Time On modified from 18:00 20-Feb to 17:32 20-Feb Sending Asset Event to FFA FFA Order En Route F-AE24NQ5028-1-0 chtcs01 FFA Order On Site F-AE24NQ5028-1-0 chtcs01 Time On modified from 17:32 20-FEB to 18:00 20-FEB by REDACTED 0467521941 Restoration Comments for F-AE24NQ5028-1-0 by CHTCS01: X-Arm replaced FFA Order F-AE24NQ5028-1-0 Completed by technician REDACTED in crew CHTCS01(0467521941) with code A-T-315 - Service Asset Fault Action Taken : replaced x-arm Site Label : 2153770 Actual Power Restoration for F-AE24NQ5028-1-0: 20-FEB-2024 17:38:00 auto-completed CANCELLED - See Forced Outage 24NQ5040. | 1 | 2403936 | opp 72 deans rd ch towers | 766419 | 2153770 | 2403936 | 2021-02-04 | 1111 | N |  |  | 12.5 | 2 | 1 | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | GI GREY IRONBARK | 12 kiloNewton | 1994 | -20.0864 | 146.2799 | 000002403936 | 01/JAN/94
EECL | OT227532 | OP | Operational |  | 2024-02-29 | 202402 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | LV |  |  |  | 1742510 | 2024 | 24NQ5585 | 2024-02-29 15:30 | 2024-02-29 20:01 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 79 WELLINGTON ST;MUNDINGBURRA QLD 4812 | Fault occurred at:29/02/2024 14:54; REDACTED, 0406752560;>WDPP --> AffectingTraffic:YES -- StillHavePower:UNSURE<;Incident Details:Reporting Line Hanging from service crossing a Road , Service Line hanging can be touched by Vehicles, Customer reporting Cross arm Snapped in half .;Access Details:On the corner of Wellington St and West St;COVID-19:N/A;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N |  | 1 | 2473668 | Cnr West St & Wellington St Townsville | 1742510 | 5006325 | 2473668 | 2021-03-30 | 1066 | N |  |  | 11 | 2 | 2 | Serviceable | N | Urb Toff | WOOD UNTREATED ROUND | Grass | Footpath | ZZ NO DISC - UNKNOWN | Unknown |  | -19.2922 | 146.7778 | 000002473668 | 01/JAN/58
EECL | OT224897 | OP | Operational |  | 2024-02-09 | 202402 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1533803 | 2024 | 24CA3094 | 2024-02-10 09:11 | 2024-02-10 11:57 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 709 CALLIOPE RIVER RD;WEST STOWE QLD 4680 | Fault occurred at:09/02/2024 10:01; REDACTED, 0429202569;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details:Customer reports cross arm is rotting and appears to be more than 50% fallen off. No lines hanging down or loose yet. Customer provided coordinates of pole via google maps, -23.89690, 151.14630;COVID-19:N/A;Warnings[uphSafety]: ADVISED;Sensitive Load:N |  | 1 | 2590133 | 709 CALLIOPE RIVER RD YARWUN | 1533803 | 4033456 | 2590133 | 2020-12-02 | 1164 | N |  |  | 12.5 | 2 |  | Serviceable | N | Rrl sty term 2 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1986 | -23.8969 | 151.1463 | 000002590133 | 01/JAN/86
EECL | OT225346 | OP | Operational |  | 2024-02-13 | 202402 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | Technical Assessment | LV |  |  |  | 1888475 | 2024 | 24NQ4620 | 2024-02-13 08:54 | 2024-02-13 11:37 | COMP | Completed |  | Hot | North Queensland | Unplanned Outage | Fuse Operated - No Trigger Found | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | GT |  | AYR: DICKS BANK RD, FIVEWAYS RD | Broken crossarm on P# 5025758 - Crews will require access to LV side of 11kV Pole Dist Sub BDS474 to rectify fault | Broken crossarm on P# 5025758 - Crews will require access to LV side of 11kV Pole Dist Sub BDS474 to rectify fault Sending Asset Event to FFA FFA Order Created F-AE24NQ4620-1-0 DfltHost FFA Order Acknowledged F-AE24NQ4620-1-0 hhlfr01 REDACTED 0409894397 FFA Order En Route F-AE24NQ4620-1-0 hhlfr01 FFA Order On Site F-AE24NQ4620-1-0 hhlfr01 FFA Order F-AE24NQ4620-1-0 Completed by technician REDACTED in crew hhlfr01(0409894397) with code A-T-330 - Fuse Operated - No Trigger Found Action Taken : Replaed LV Xarm Replaced 3 x 100 amp LV fuse assembly Replaced 3 x 80 amp LV fuse Replaced 3 x 6/20 HV fuses Site Label : 5025758 Time On modified from 23:59 13-FEB to 14:22 13-FEB | 1 | 2590945 | dicks bank. access 131 bowie rd ayr | 1888475 | 5025758 | 2590945 | 2021-08-23 | 904 | N |  |  | 14 | 1 | 1 | Serviceable | N | Rrl inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Backyard | SG SPOTTED GUM | 5 kiloNewton | 1990 | -19.5823 | 147.3454 | 000002590945 | 01/JAN/90
EECL | OT227034 | OP | Operational |  | 2024-02-26 | 202402 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 66kV |  |  |  | 1810156 | 2024 | 24NQ5332 | 2024-02-26 12:15 | 2024-02-26 12:17 | COMP | Completed |  | Wet / Rain | North Queensland | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FE |  | DALBEG, HOME HILL, MILLAROO, | J-650-s CLARE STH 66kV Millaroo Fdr CB EA08Q00 tripped. SCADA Interface automated outage. | entered from the SCADA Interface Fault dist 24klm, Zone 2 protection crew despatched Crew dispatched REDACTED 0447 653 727, crew to call OCCN when in area. Sending Asset Event to FFA FFA Order Created F-AE24NQ5332-1-0 DfltHost crew have found a broken 66kV cross arm S/L5031723 Sending Asset Event to FFA Sending Asset Event to FFA Crews have isolated and earthed Between ABS CS-ML No.2 and B124 at Millaroo Sub Asset selection modified Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ5332-1-0 hhlfr01 REDACTED 0447653727 FFA Order En Route F-AE24NQ5332-1-0 hhlfr01 FFA Order On Site F-AE24NQ5332-1-0 hhlfr01 Restoration Comments for F-AE24NQ5332-1-0 by HHLFR01: replace wishbone arm 66 kv Time On modified from 23:59 26-Feb to 17:22 26-Feb Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24NQ5332-1-0 Completed by technician REDACTED in crew HHLFR01(0447653727) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : REPLACE WISHBONE 66 KV ARM Site Label : 5031723 FFA Order F-AE24NQ5332-1-0 Completed by technician REDACTED in crew HHLFR01(0447653727) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : REPLACE WISHBONE 66 KV ARM Site Label : 5031723 FFA Order F-AE24NQ5332-1-0 Completed by technician REDACTEDin crew HHLFR01(0447653727) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : REPLACE WISHBONE 66 KV ARM Site Label : 5031723 | 1 | 2629028 | 7pNW CORUNNA HVL 5 ADIREL DOWNS | 1810156 | 5031823 | 2629028 | 2023-05-25 | 277 | N |  |  | 15 |  |  | Serviceable | N | SWER inter | SPUN CONCRETE | Grass | Paddock Grazing | CC SPUN CONCRETE | 5 kiloNewton | 1999 | -22.0616 | 143.868 | 000002629028 | 01/JAN/99
EECL | OT223853 | OP | Operational |  | 2024-02-03 | 202402 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 974658 | 2024 | 24MK1802 | 2024-02-03 14:32 | 2024-02-04 17:44 | CAN | Cancelled |  | Fine | Mackay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | STATION RD;CRYSTAL BROOK QLD 4800 | Fault occurred at:03/02/2024 14:28; REDACTED, 49452103;>DFL --> StartedWithinPastWeek:YES -- LightsDimUnderLoad:NO -- NeighboursAffected:UNSURE -- OccursSameTimeEachDay:NO<;Incident Details:dim and flickering power, cust has turned off main switch; cust onsite; dog will be restrained when crew arrives; this is the last property on the road, property known as 2475 Station Rd;COVID-19:UNKNOWN;Warnings[dimFlickeringLights]: ADVISED;Dog restraint:ARRIVAL;Sensitive Load:N | outage cancelled via Clash Wizard | 1 | 2640234 | 2 past sub r3170 Station rd andromache | 974658 | 4041574 | 2640234 | 2019-08-01 | 1647 | N |  |  | 12.5 | 2 |  | Serviceable | N | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1982 | -20.5403 | 148.3882 | 000002640234 | 01/JAN/82
EECL | OT223529 | OP | Operational |  | 2024-02-01 | 202402 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 975043 | 2024 | 24MK1628 | 2024-01-31 17:23 | 2024-01-31 17:25 | COMP | Completed |  | Wet / Rain | Mackay | Unplanned Outage | HV-Conductor Connection Failure | Unknown | due to a SCADA Automated Event | FC |  | ANDROMACHE, BLOOMSBURY, LETHEBROOK, PROSERPINE, THOOPARA | LAGUNA QUAYS 11kV O Connell R ACR CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface dispatched to REDACTED prpoc01 Sending Asset Event to FFA FFA Order Created F-AE24MK1628-1-0 DfltHost Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Fault is beyond LKS970. Crew to continue tomorrow Time On modified from 23:59 31-Jan to 23:59 01-Feb Sending Asset Event to FFA Sending Asset Event to FFA Crews removed arm brace off insulator, tried to close back in but failed on EF again. Crews to fly line. Sending Asset Event to FFA FFA Order Acknowledged F-AE24MK1628-1-0 prpoc01 REDACTED 0437614982 FFA Order En Route F-AE24MK1628-1-0 prpoc01 FFA Order On Site F-AE24MK1628-1-0 prpoc01 Time On modified from 23:59 01-Feb to 14:07 01-Feb Sending Asset Event to FFA Sending Asset Event to FFA Removing Asset Event from FFA Removing Asset Event from FFA FFA Order cancelled.F-AE24MK1628-1-0 FFA Order Created F-AE24MK1628-1-1 DfltHost FFA Order cancelled.F-AE24MK1628-1-1 Sending Asset Event to FFA FFA Order Created F-AE24MK1628-1-2 DfltHost FFA Order Acknowledged F-AE24MK1628-1-2 prpoc01 REDACTED 0437614982 FFA Order En Route F-AE24MK1628-1-2 prpoc01 FFA Order On Site F-AE24MK1628-1-2 prpoc01 FFA Order F-AE24MK1628-1-2 Completed by technician REDACTED in crew prpoc01(0427114514) with code A-T-304 - HV-Conductor Connection Failure Action Taken : replaced broken cross arm Site Label : 4048314 | 1 | 2681627 | 1 E tx6287 398 Caping Rd Bloomsbury | 975043 | 4048314 | 2681627 | 2019-05-21 | 1717 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | SG SPOTTED GUM | 5 kiloNewton | 1991 | -20.6014 | 148.5882 | 000002681627 | 01/JAN/91
EECL | OT226694 | OP | Operational |  | 2024-02-23 | 202402 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 873892 | 2024 | 24SW5346 | 2024-02-23 09:57 | 2024-02-23 09:52 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | NEWTOWN: BRIGALOW ST, HAMPTON ST, HURSLEY RD, JAPONICA ST, REDWOOD ST, WYALLA ST | 11kV Pole Dist Sub PE07480, crew require to Open LV that feeds into access area | 11kV Pole Dist Sub PE07480, crew require to Open LV that feeds into access area Time Off modified from 10:00 23-Feb to 09:57 23-Feb TWMFR03 Sending Asset Event to FFA FFA Order Created F-AE24SW5346-1-0 DfltHost FFA Order Acknowledged F-AE24SW5346-1-0 twmfr03 REDACTED 0418712115 FFA Order En Route F-AE24SW5346-1-0 twmfr03 FFA Order On Site F-AE24SW5346-1-0 twmfr03 FFA Order F-AE24SW5346-1-0 Completed by technician REDACTED in crew twmfr03(0418712115) with code A-F-C - Completed Action Taken : Replace broken HV and LV Pin arms under F-3079-q sheet Closed out LV Sheet outage complete at 1240pm Site Label : 3258438 Time On modified from 14:00 23-FEB to 12:54 23-FEB | 1 | 2688560 | 104 Hursley Rd,Toowoomba | 873892 | 3258438 | 2688560 | 2022-05-25 | 639 | N |  |  | 15.5 | 3 | 1 | Serviceable | N | Rrl inter 3 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 8 kiloNewton | 1968 | -27.5599 | 151.9178 | 000002688560 | 01/JAN/68
EECL | OT226204 | OP | Operational |  | 2024-02-19 | 202402 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1495038 | 2024 | 24SW5146 | 2024-02-19 15:14 | 2024-02-19 14:41 | COMP | Completed |  |  | South West | Forced Outage |  | P1 Lines works | to allow emergency maintenance of the electricity network. | FC |  | KOOROONGARRA: KOOROONGARRA CEMETERY RD, MABBET RD | Forced Outage required to repair broken X-arm | Forced Outage required to repair broken X-arm Switching Sheet ID updated from to J-298201-g. Broken x-arm at SL 3043059 milcs01 Time On modified from 23:59 19-Feb to 20:30 19-Feb Time Off modified from 15:30 19-Feb to 15:09 19-Feb Time Off modified from 15:09 19-Feb to 15:14 19-Feb twmoc01 Sending Asset Event to FFA FFA Order Created F-AE24SW5146-1-0 DfltHost FFA Order Acknowledged F-AE24SW5146-1-0 twmoc01 REDACTED 0428221390 FFA Order En Route F-AE24SW5146-1-0 twmoc01 FFA Order On Site F-AE24SW5146-1-0 twmoc01 Time On modified from 20:30 19-Feb to 18:47 19-Feb Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW5146-1-0 Completed by technician REDACTED in crew twmoc01(0428221390) with code A-F-C - Completed Action Taken : Replaced broken xarm. Site Label : 3043059 | 1 | 2721194 | 136 Kooroongarra CemeteryRd,Kooroongarra | 1495038 | 3043059 | 2721194 | 2019-10-09 | 1594 | N |  |  | 12.5 | 2 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | GB GREY BOX | 5 kiloNewton | 1995 | -28.0929 | 151.2708 | 000002721194 | 01/JAN/95
EECL | OT225763 | OP | Operational |  | 2024-02-15 | 202402 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1490087 | 2024 | 24SW5001 | 2024-02-15 22:56 | 2024-02-15 22:03 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | DALBY: UNMETERED SUPPLY KOOROONGARRA: HAIN RD, KOOROONGARRA CEMETERY RD, KOOROONGARRA RD, MABBET RD, MOSQUITO CREEK RD, STONEHENGE RD LEYBURN: STONEHENGE RD MILLMERRAN: KOOROONGARRA RD, STONEHENGE RD | Crew advised broken X arm past 11kV Disc Links DL12167 F-2493-r | Crew advised broken X arm past 11kV Disc Links DL12167 Crew advised straight through construction Sending Asset Event to FFA FFA Order Created F-AE24SW5001-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 02:00 16-Feb to 05:00 16-Feb Sending Asset Event to FFA Time Off modified from 23:00 15-Feb to 22:56 15-Feb Time On modified from 05:00 16-Feb to 03:51 16-Feb Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW5001-1-0 twmoc04 REDACTED 0459819951 FFA Order En Route F-AE24SW5001-1-0 twmoc04 FFA Order On Site F-AE24SW5001-1-0 twmoc04 FFA Order F-AE24SW5001-1-0 Completed by technician REDACTED in crew twmoc04(0459819951) with code A-F-C - Completed Action Taken : replace broken 11 kv link/strain arm, replace links and install new bridging Site Label : 3043075 | 1 | 2721290 | DL12168,2325 Kooroongarra Rd,K'garra | 1490087 | 3043075 | 2721290 | 2019-10-09 | 1590 | N |  |  | 12.5 | 2 |  | Serviceable | N | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1977 | -28.0981 | 151.2539 | 000002721290 | 01/JAN/77
EECL | OT224709 | OP | Operational |  | 2024-02-08 | 202402 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1351749 | 2024 | 24WB2900 | 2024-02-08 09:30 | 2024-02-08 13:31 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 24015 MONTO RD EIDSVOLD QLD 4627 | Broken Strain arm reported in by REDACTED 0428196190 Hv Arm SL 3062477 |  | 1 | 2814794 | TX10708 24015 burnett hwy eidsvold | 1351749 | 3062477 | 2814794 | 2021-12-14 | 786 | N |  |  | 12.5 | 2 |  | Serviceable | Y | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Soil | Road Reserve | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -25.3565 | 151.1185 | 000002814794 | 01/JAN/89
EECL | OT226369 | OP | Operational |  | 2024-02-20 | 202402 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 22kV |  |  |  | 1288811 | 2024 | 24FN3114 | 2024-02-20 20:55 | 2024-02-20 19:33 | COMP | Completed |  |  | Far North | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | FE |  | CRAIGLIE: CAPTAIN COOK HWY, CREES RD, FERRERO RD PORT DOUGLAS: HOPE ST | F-3396-s CRAI - Inlet Fdr: Crew adv req emeregency access between Links I1 & ABS I14 & Switch I9 to repair broken HV Xarm at Pole 5066472 near SS6683. | Crew adv req emeregency access between Links I1 & ABS I14 & Switch I9 to repair broken HV Xarm at Pole 5066472 near SS6683. Refer to FC 2411328. Time Off modified from 20:00 20-Feb to 20:55 20-Feb Time On modified from 23:00 20-Feb to 23:30 20-Feb Time On modified from 23:30 20-Feb to 22:21 20-Feb | 1 | 2826306 | 4spns W 143 ferrero rd craiglie | 1288811 | RY13 | 2826306 | 2021-08-17 | 917 | N |  |  | 14 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | DS DARWIN STRINGYBAR | 5 kiloNewton | 1994 | -16.5391 | 145.4558 | 000002826306 | 01/JAN/94
EECL | OT224260 | OP | Operational |  | 2024-02-06 | 202402 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1746107 | 2024 | 24NQ4179 | 2024-02-06 09:00 | 2024-02-06 07:58 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE |  | BALFES CREEK, BASALT, PENTLAND | F-3298-s - Repair Broken 11kV xarm near CTS136 | F-3298-s - Repair Broken 11kV xarm near CTS136 Sending Asset Event to FFA FFA Order Created F-AE24NQ4179-1-0 DfltHost FFA Order Acknowledged F-AE24NQ4179-1-0 chtfco01 REDACTED 0418735767 FFA Order En Route F-AE24NQ4179-1-0 chtfco01 FFA Order On Site F-AE24NQ4179-1-0 chtfco01 Sending Asset Event to FFA Time On modified from 12:00 06-Feb to 14:00 06-Feb Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24NQ4179-1-0 Completed by technician REDACTEDin crew chtfco01(0418735767) with code A-F-C - Completed Action Taken : replaced broken 11kv pin arm Site Label : 5085886 Time On modified from 14:00 06-Feb to 13:25 06-Feb | 1 | 2915602 | 3 spn e Springfern st hstd toff pentland | 1746107 | 5085886 | 2915602 | 2019-05-18 | 1725 | N |  |  | 11 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | WS WHITE STRINGYBARK | 5 kiloNewton | 1966 | -20.4652 | 145.4384 | 000002915602 | 01/JAN/66
EECL | OT226998 | OP | Operational |  | 2024-02-26 | 202402 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 22kV |  |  |  | 996018 | 2024 | 24CA3753 | 2024-02-26 11:21 | 2024-02-26 10:22 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | GINDIE: GLENORINA RD, OFF GEM RD, OLIVE VALE RD SPRINGSURE: GLENORINA RD, MILROY DOWNS RD, OFF GLENORINA RD, OFF MILROY DOWNS RD YAMALA: BONNIE DOON RD, OLIVEVALE RD | 22kV Air Break S3049 - outage to repair broken x-arm | 22kV Air Break S3049 - outage to repair broken x-arm HV Wires Down Switching Sheet Written Time Off modified from 11:00 26-Feb to 11:21 26-Feb Asset selection modified Time On modified from 15:30 26-Feb to 14:06 26-Feb auto-completed | 1 | 2940520 | x8505 wyntoon rd springsure | 996018 | 4098091 | 2940520 | 2021-06-08 | 993 | N |  |  | 14 | 2 |  | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 12 kiloNewton |  | -23.8721 | 148.298 | 000002940520 | 01/JAN/70
EECL | OT226963 | OP | Operational |  | 2024-02-25 | 202402 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1500226 | 2024 | 24SW5418 | 2024-02-25 18:52 | 2024-02-25 22:11 | COMP | Completed |  | Fine | South West | Unplanned Outage | LV-Conductor Connection Failure | Unknown | Single Fault Call | GT |  | 89 EDWARD ST CHARLEVILLE QLD 4470 | Firecom advise Sparking lines. Exploded and is now hanging very low. Request EE attend |  | 1 | 2975380 | CNR EDWARD & EYRE STS CHARLEVILLE | 1500226 | 6047734 | 2975380 | 2019-09-04 | 1635 | N |  |  | 11 |  | 1 | Serviceable | N | Urb LV ABC inter | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 12 kiloNewton | 1992 | -26.4018 | 146.2432 | 000002975380 | 01/JAN/92
EECL | OT225811 | OP | Operational |  | 2024-02-16 | 202402 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 22kV |  |  |  | 924131 | 2024 | 24CA3286 | 2024-02-15 22:09 | 2024-02-15 22:12 | COMP | Completed |  | Wet / Rain | Capricornia | Unplanned Outage | HV-Conductor Connection Failure | Unknown | due to a SCADA Automated Event | FE |  | BARCALDINE: ARAMAC RD, BLOODWOOD DR, SANDALWOOD DR, LANDSBOROUGH HWY, SALTERN CREEK RD, BARCALDINE DOWNS RD, OFF LANDSBOROUGH HWY, BARCALDINE-ISISFOR RD, BARCALDINE-L'REACH RD, BARCALDINE-ISISFORD RD | F-2494-r BARCALDINE 22kV West Hway Fdr CB S203 tripped. SCADA Interface automated outage. | entered from the SCADA Interface F-2494-r Coordinator adv crew will patrol it in the morning. Depot Co-ord Advised Read Above Time On modified from 23:59 15-Feb to 23:59 16-Feb Asset selection modified Manual Reclose Checklist Crew sectionalised at X12152 and performed MRC - closed bb-s203 successful BRCCS01 Sending Asset Event to FFA FFA Order Created F-AE24CA3286-1-0 DfltHost FFA Order Acknowledged F-AE24CA3286-1-0 brccs01 REDACTED 0428110442 FFA Order En Route F-AE24CA3286-1-0 brccs01 FFA Order On Site F-AE24CA3286-1-0 brccs01 Restoration Comments for F-AE24CA3286-1-0 by brccs01: broken cross arm at 4110511 have earthed conductors Back fed from Ilfracombe fdr up to X11955 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 16-Feb to 16:06 16-Feb Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24CA3286-1-0 Completed by technician REDACTED in crew brccs01(0428110442) with code A-T-28 - Overload Action Taken : replace broken cross arm Site Label : 4110511 | 1 | 3013611 | 11pNtaraStnHouse43766L'boroughHwyBarcy | 924131 | 4110511 | 3013611 | 2023-02-18 | 363 | N |  |  | 11 |  |  | Unserviceable - P2 | N | SWER inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | Unknown |  | -23.5565 | 145.0352 | 000003013611 | 01/JAN/08
EECL | OT224983 | OP | Operational |  | 2024-02-09 | 202402 | Crossarm | Xarm, Wood Termination | Split | Rot/Decay |  | LV |  |  |  | 1001698 | 2024 | 24CA3089 | 2024-02-09 17:11 | 2024-02-09 19:41 | COMP | Completed |  | Fine | Capricornia | Unplanned Outage | LV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | 44 CLEMATIS ST;BLACKALL QLD 4472 | 3rd Party->Fault occurred at:09/02/2024 17:09; REDACTED, 0459960715;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details:Customer advised that pole 4117812 has a broken cross arm;COVID-19:N/A;Warnings[uphSafety]: ADVISED;Sensitive Load:N |  | 1 | 3056763 | Cnr Clematis St/Ivy St, Blackall | 1001698 | 4117812 | 3056763 | 2020-03-11 | 1430 | N |  |  | 12.5 | 1 | 2 | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Bitumen | Road | SG SPOTTED GUM | 8 kiloNewton | 1967 | -24.4186 | 145.4679 | 000003056763 | 01/JAN/67
EECL | OT223914 | OP | Operational |  | 2024-02-04 | 202402 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1615867 | 2024 | 24NQ4110 | 2024-02-04 05:02 | 2024-02-04 05:04 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | Service Asset Fault | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FE |  | DALBEG | MILLAROO 11kV Dalbeg Fdr CB A252 tripped. SCADA Interface automated outage. | entered from the SCADA Interface Tripped on OC Manual reclose attemp failed, patrol required Erri Vener to attend Asset selection modified Manual Reclose Checklist Crew have found Broken Crossarm at Site Lab 5116857 Isolating and Earthing for Repairs. Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Created F-AE24NQ4110-1-0 DfltHost Time On modified from 23:59 04-Feb to 12:51 04-Feb Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ4110-1-0 hhlfr01 REDACTED 0439680072 FFA Order En Route F-AE24NQ4110-1-0 hhlfr01 FFA Order On Site F-AE24NQ4110-1-0 hhlfr01 Restoration Comments for F-AE24NQ4110-1-0 by hhlfr01: broken cross arm on pole 5116857. Restoration Comments for F-AE24NQ4110-1-0 by hhlfr01: broken cross arm on pole 5116857. FFA Order F-AE24NQ4110-1-0 Completed by technician REDACTED in crew hhlfr01(0439680072) with code A-T-315 - Service Asset Fault Action Taken : replaced cross -arm on pole 5116857. Site Label : 5116857 FFA Order F-AE24NQ4110-1-0 Completed by technician REDACTED in crew hhlfr01(0439680072) with code A-T-315 - Service Asset Fault Action Taken : replaced cross -arm on pole 5116857. Site Label : 5116857 Restoration Comments for F-AE24NQ4110-1-0 by hhlfr01: broken cross arm on pole 5116857. FFA Order F-AE24NQ4110-1-0 Completed by technician REDACTED in crew hhlfr01(0439680072) with code A-T-315 - Service Asset Fault Action Taken : replaced cross -arm on pole 5116857. Site Label : 5116857 | 1 | 3091733 | 7674Ayr-DalbegRdToExpeditionPassCk | 1615867 | 5116857 | 3091733 | 2019-11-13 | 1544 | N |  |  | 17 | 2 |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1978 | -20.1704 | 147.2802 | 000003091733 | 01/JAN/78
EECL | OT224227 | OP | Operational |  | 2024-02-06 | 202402 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | Replace | 22kV |  |  |  | 1219658 | 2024 | 24FN2424 | 2024-02-05 10:02 | 2024-02-05 09:01 | COMP | Completed |  |  | Far North | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | NORMANTON: GREEN ST, LANDSBOROUGH ST, NOEL ST, NOEL ST W, NOEL ST WEST, PHILP ST, SUTHERLAND ST, THOMPSON ST, TRAVERS ST | F-31007-g NORM - Normanton Town Feeder - Crews to repair broken HV Xarm pole 5137559 | F-31007-g NORM - Normanton Town Feeder - Crews to repair broken HV Xarm pole 5137559 Time Off modified from 10:00 05-Feb to 10:02 05-Feb Time On modified from 16:00 05-Feb to 10:52 05-Feb | 1 | 3221396 | 12 noel st normanton | 1219658 | NOE3 | 3221396 | 2020-08-04 | 1281 | N |  |  | 12.5 | 1 | 1 | Serviceable | Y | Urb inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Soil | Footpath | RB RED BLOODWOOD | 5 kiloNewton | 1986 | -17.676 | 141.0703 | 000003221396 | 01/JAN/86
EECL | OT226050 | OP | Operational |  | 2024-02-18 | 202402 | Crossarm | Xarm, Wood Intermediate | Split | Rot/Decay |  | 19kV |  |  |  | 1768231 | 2024 | 24NQ4850 | 2024-02-19 07:27 | 2024-02-18 14:26 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | ZS |  | WINTON: ALDINGHAM RD, APSLEY STATION, DAHLIA STATION, FAIRYMEAD STATION, KYWONG STATION, LESWALT STATION, WANDO STATION | 19.1kV SWER RC857602 - DL857604 + DO857603 Forced outage required to replace P0 angle x-arm at pole # 5223974 Found by assest inspector - site visit done by crew - access required downstream of RC857602 | Switching Sheet ID updated from to J-298096-g. Time Off modified from 08:30 19-Feb to 07:27 19-Feb Time On modified from 14:30 19-Feb to 09:29 19-Feb | 1 | 3381001 | Homestead Leswalt stn Winton | 1768231 | 5223974 | 3381001 | 2019-06-19 | 1705 | N |  |  | 12.5 | 1 |  | Serviceable | N | SWER sty angle | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 5 kiloNewton |  | -22.4329 | 143.402 | 000003381001 | 01/JAN/78
EECL | OT226658 | OP | Operational |  | 2024-02-23 | 202402 | Crossarm | Xarm Bracket Nuts | Broken | Corrosion | Repair | 66kV |  |  |  | 6975533 | 2024 | 24NQ5146 | 2024-02-23 01:47 | 2024-02-23 01:50 | COMP | Completed |  | Wet / Rain | North Queensland | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FE |  | BAMBAROO, COOLBIE, GREENVALE, MOUNT FOX, MOUNT GARNET, MUTARNEE, PALUMA | INGHAM 66kV Black Rv Fdr CB A152 tripped. SCADA Interface automated outage. | entered from the SCADA Interface Dist 55klm. Timed EF. IGM P5064930 Aph MRC failed. Crew dispatched. Manual Reclose Checklist Crews Attending: 1st On Call Crew REDACTED 0473 145 674 ingcsfr01 2nd On Call Crew REDACTED 0437 796 129. Sending Asset Event to FFA FFA Order Created F-AE24NQ5146-1-0 DfltHost Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ5146-1-0 ingcsfr01 REDACTED 0473145674 FFA Order En Route F-AE24NQ5146-1-0 ingcsfr01 Second DTF is 46.7 KLM Sending Asset Event to FFA FFA Order On Site F-AE24NQ5146-1-0 ingcsfr01 Asset selection modified Sending Asset Event to FFA Crtew arranging parol and repairs ASAP in daylight. Sending Asset Event to FFA Helicopter trying to patrol . Ground crew heading up to ground patrol. Sending Asset Event to FFA Helicopter unable to patrol still waiting better weather. Sending Asset Event to FFA REDACTED advised will attend in morning to connect PEG1 (0900) Sending Asset Event to FFA Crew adv Helicopter could not patrol but Ground Patrol Completed between Mount Fox and IN-GR-2 will attempt MRC Sending Asset Event to FFA MRC Failed Dist to Faul 46.5km Line Isolated and Earthed for Repairs but Very Wet Conditions and Limited Visibility Sending Asset Event to FFA Replay sequence/s deleted after 23-FEB-24 01:47:20 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Initial trip DTF was 55km approx near pole 5255289. Subsequent trips DTF at 46km and approx pole 5082114. Due to weather further patrolling to be done tomorrow morning. Crew to be on site at Greenvale to connect Pegasus to supply remaining customers at approx 0830. Time On modified from 23:59 23-Feb to 23:59 24-Feb Sending Asset Event to FFA REDACTED advised on way home has not patrolled from 5082135 towards Ingham. Sending Asset Event to FFA Crews advise that they will continue to patrol on the ground this morning. unable to fly line due to weather (Cloudy conditions) Sending Asset Event to FFA Sending Asset Event to FFA Pegasus has been connected to the 11kV Network at greenvale Asset selection modified Sending Asset Event to FFA Crews advise that a conductor has pulled through some discs at Pole 5045501 Sending Asset Event to FFA Crews have signed onto access to make repairs Sending Asset Event to FFA HV Wires Down Reason for Event changed from Protective Device Operated Sending Asset Event to FFA Crew hoping to have Feeder restored by 1630 Sending Asset Event to FFA Time On modified from 23:59 24-Feb to 17:13 24-Feb Sending Asset Event to FFA FFA Order cancelled.F-AE24NQ5146-1-0 | 1 | 5679104 | between ewan rd 1371 mt fox rd mt fox | 6975533 | 5045501 | 5679104 | 2019-08-06 | 1662 | N |  |  | 17 |  |  | Serviceable | N | 66kV rrl inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1973 | -18.834 | 145.8982 | 000005679104 | 01/JAN/73
EECL | OT226025 | OP | Operational |  | 2024-02-18 | 202402 | Crossarm | Xarm, Wood Strain | Split | Rot/Decay |  | 11kV |  |  |  | 3224675 | 2024 | 24MK2136 | 2024-02-18 | 2024-02-18 | COMP | Completed |  |  | Mackay | [9 empty] | 1 | 20214 |  | 20214 |  |  |  | 45340 | [11 empty] | Inaccessible to heavy vehicles |  |  |  | -21.1208 | 148.4928 | 000001494124 | 01/JAN/86
EECL | OT227708 | OP | Operational |  | 2024-03-01 | 202403 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1517321 | 2024 | 24MK2529 | 2024-03-01 20:32 | 2024-03-01 21:40 | COMP | Completed |  | Wet / Rain | Mackay | Unplanned Outage | HV-Conductor Connection Failure | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ |  | PALMYRA: BELLS RD, GRANTS RD | Disc Links LKS260 - Crews require acess beyond to repair broken cross arm | 11kV Disc Links LKS260 - Crews require acess beyond to repair broken cross arm Sending Asset Event to FFA FFA Order Created F-AE24MK2529-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24MK2529-1-0 mckoc01 REDACTED 0409913086 FFA Order En Route F-AE24MK2529-1-0 mckoc01 FFA Order On Site F-AE24MK2529-1-0 mckoc01 Asset selection reset Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Replay sequence/s deleted after 01-MAR-24 20:31:52 Asset selection modified Sending Asset Event to FFA FFA Order F-AE24MK2529-1-0 Completed by technician REDACTED in crew mckoc01(0409913086) with code A-T-304 - HV-Conductor Connection Failure Action Taken : replaced broken 11kv strain arm Site Label : 4012429 Time On modified from 23:59 01-Mar to 01:26 02-Mar Assets extracted from 6387 (WEDGNER) into event 24MK2533 | 1 | 2461889 | 160 Bells rd Palmyra | 1517321 | 4012429 | 2461889 | 2023-02-22 | 373 | N |  |  | 14 | 2 |  | Serviceable | Y | Rrl unsty sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 12 kiloNewton | 1990 | -21.2128 | 149.0729 | 000002461889 | 01/JAN/90
EECL | OT227863 | OP | Operational |  | 2024-03-03 | 202403 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 22kV |  |  |  | 1288312 | 2024 | 24FN3596 | 2024-03-03 15:57 | 2024-03-03 14:51 | COMP | Completed |  |  | Far North | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE |  | CRAIGLIE: CREES RD | F-3463-s - CRAI - Inlet Fdr - broken HV xarm at SL 5066493 near SS6811 | CRAI - Inlet Fdr - broken HV xarm at SL 5066493 near SS6811 Time Off modified from 15:30 03-Mar to 15:57 03-Mar Time On modified from 18:00 03-Mar to 17:10 03-Mar | 1 | 2826428 | Opp 59 crees rd craiglie | 1288312 | EU4 | 2826428 | 2021-08-16 | 930 | N |  |  | 14 | 4 |  | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | DS DARWIN STRINGYBAR | 8 kiloNewton | 1995 | -16.5316 | 145.454 | 000002826428 | 01/JAN/95
EECL | OT227933 | OP | Operational |  | 2024-03-03 | 202403 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 8628718 | 2024 | 24WB3653 | 2024-03-03 20:16 | 2024-03-03 20:19 | COMP | Completed |  | Storm Electrical | Wide Bay | Unplanned Outage | HV-Conductor Connection Failure | Fallen Power Lines | due to fallen power lines. | FC |  | TIARO: WILSONS RD, BALINDINAS DR BIDWILL: BIDWILL RD MAGNOLIA: BIDWILL RD, PALLANT RD, FORESTERS RD, EXMOUTH ACCESS LANE OWANYILLA: BALANDINAS DR, OWANYILLA BOUNDARY RD TEDDINGTON: STUTZ RD | F-2585-r - OWANYILLA 11kV Stuz Rd ACR S1248 CB tripped. SCADA Interface automated outage. Wires grounded and in trees - Crew reconductored over creek due to broken steel conductor. SL 11131920. REDACTED | entered from the SCADA Interface 11kV Recloser S1248 - Tripped to Lockout OC Depot Co-ord Advised Crew to patrol the main line MRBOC01. Sending Asset Event to FFA FFA Order Created F-AE24WB3653-1-0 DfltHost FFA Order Acknowledged F-AE24WB3653-1-0 mrboc01 REDACTED 0428429821 FFA Order En Route F-AE24WB3653-1-0 mrboc01 FFA Order On Site F-AE24WB3653-1-0 mrboc01 Crew found wires down Isolated and earthed at DL791644 Reason for Event changed from Unknown Sending Asset Event to FFA Crew request reclose of remainder off fdr Manual Reclose Checklist Sending Asset Event to FFA Reclose Successful at 2249 Crew to return around midday to make repairs to lines.. Asset selection modified Sending Asset Event to FFA . Sending Asset Event to FFA FFA Order En Route F-AE24WB3653-1-0 mrboc01 FFA Order On Site F-AE24WB3653-1-0 mrboc01 Std Reason Changed from Fallen Power Lines by REDACTED 0428429821 Restoration Comments for F-AE24WB3653-1-0 by mrboc01: crews onsite Time On modified from 23:59 03-Mar to 23:59 04-Mar Sending Asset Event to FFA Time On modified from 23:59 04-Mar to 21:09 04-Mar Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24WB3653-1-0 Completed by technician REDACTED in crew mrboc01(0428429821) with code A-T-304 - HV-Conductor Connection Failure Action Taken : reconductored over creek due to broken 3/12 steel. tripped on overcurrent and wires on ground and in trees Site Label : 11131920 Updated Reasons tab. Updated Event Trigger from Distribution substation to HV-CCF. Reason for Event changed from Unknown | 1 | 8666254 | 213 stutz rd teddington | 8628718 | 11131920 | 8666254 | 2021-08-25 | 921 | N |  |  | 14 |  |  | Serviceable | N | Urb Toff | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | BI BROAD LEAF IRONBARK | 8 kiloNewton | 2017 | -25.6887 | 152.6662 | 000008666254 | 01/JAN/17
EECL | OT228079 | OP | Operational |  | 2024-03-04 | 202403 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 66kV |  |  |  | 1851765 | 2024 | 24WB3721 | 2024-03-04 16:26 | 2024-03-04 17:28 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 147 BOORAL RD;NIKENBAH QLD 4655 | Fault occurred at:04/03/2024 14:22; REDACTED, 0427860089;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details:Broken Cross-arm and Higher wires are resting on the lower wires.;COVID-19:N/A;Warnings[uphSafety]: ADVISED;Dog restraint:YARD;Sensitive Load:N |  | 1 | 2053232 | 16 MOORABINDA DR SUNSHINE ACRES | 1851765 | 3153154 | 2053232 | 2020-03-19 | 1446 | N |  |  | 18.5 |  |  | Serviceable | N | 66kV rrl inter | WOOD (GREEN) SALT IMPREG CCA | Lawn | Front Yard | SG SPOTTED GUM | 8 kiloNewton | 2002 | -25.3491 | 152.7899 | 000002053232 | 01/JAN/02
EECL | OT228295 | OP | Operational |  | 2024-03-05 | 202403 | Crossarm | Xarm, Wood Termination | Split | Rot/Decay |  | LV |  |  |  | 1518627 | 2024 | 24SW5883 | 2024-03-05 09:23 | 2024-03-05 09:40 | COMP | Completed |  | Fine | South West | Unplanned Outage | LV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | GT |  | STANTHORPE: CONNOR ST, HARRIS ST, HIGH ST, JOHNSON ST, MCLUCAS LANE, RICH ST, SHORT ST | Crew adv, broken cross arm, require LV access 11kV Pole Dist Sub PE00112. LV only. Crew replaced LV term arm due to rot, wire still above stat. height. SL 3147440. REDACTED | Crew adv, broken cross arm, require LV access 11kV Pole Dist Sub PE00112. LV only. Crew adv sttoc01. Sending Asset Event to FFA FFA Order Created F-AE24SW5883-1-0 DfltHost FFA Order Acknowledged F-AE24SW5883-1-0 sttoc01 \REDACTED 0439186719 FFA Order En Route F-AE24SW5883-1-0 sttoc01 FFA Order On Site F-AE24SW5883-1-0 sttoc01 FFA Order F-AE24SW5883-1-0 Completed by technician REDACTED in crew sttoc01(0439186719) with code A-T-311 - LV-Unassisted failure(Apparent defect) Action Taken : replaced Lv term arm due to rot, wire still above stat height Site Label : 3147440 Time On modified from 23:59 05-MAR to 11:55 05-MAR Updated Reasons tab. | 1 | 3226841 | cnr Johnson/Connor St,Stanthorpe | 1518627 | 3147440 | 3226841 | 2021-01-19 | 1141 | N |  |  | 12.5 | 1 | 3 | Serviceable | N | Urb Toff | WOOD UNTREATED ROUND | Lawn | Footpath | ZZ NO DISC - UNKNOWN | 12 kiloNewton |  | -28.6514 | 151.9396 | 000003226841 | 01/JAN/51
EECL | OT229149 | OP | Operational |  | 2024-03-11 | 202403 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1116647 | 2024 | 24SW6131 | 2024-03-11 10:13 | 2024-03-11 10:16 | COMP | Completed |  | Wet / Rain | South West | Unplanned Outage | HV-Leakage / Pole top fire | Fallen Power Lines | due to fallen power lines. | FC |  | BALLANDEAN, EUKEY, MOUNT TULLY, SEVERNLEA, STANTHORPE | STANTHORP TN 11kV Back Ck ACR4151 CB tripped. SCADA Interface automated outage. Lines down - Crew replaced 2 x HV arms. SL 3306292. REDACTED | entered from the SCADA Interface oc trip Depot Co-ord Advised REDACTED will organise crews to carry out a line patrol. Reclose attempt failed. Crews will start sectionalising. Crew advised Lineds Down past DL16268 Asset selection modified Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Created F-AE24SW6131-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 11-Mar to 15:39 11-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW6131-1-0 sttoc01 REDACTED 0423309921 FFA Order En Route F-AE24SW6131-1-0 sttoc01 FFA Order On Site F-AE24SW6131-1-0 sttoc01 FFA Order F-AE24SW6131-1-0 Completed by technician \REDACTED in crew STTOC01(0423309921) with code A-T-305 - HV-Leakage / Pole top fire Action Taken : REPLACED 2 HV ARMS Site Label : 3306292 Added notes to Reasons tab. | 1 | 2739896 | acc 680 Mt Tully Rd,Eukey | 1116647 | 3306292 | 2739896 | 2019-08-21 | 1664 | N |  |  | 14 | 2 |  | Serviceable | N | Rrl unsty trm 1 cct | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1967 | -28.739 | 151.951 | 000002739896 | 01/JAN/67
EECL | OT229474 | EX | External |  | 2024-03-14 | 202403 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 9261588 | 2024 | 24WB4041 | 2024-03-14 07:14 | 2024-03-14 07:16 | COMP | Completed |  | Fine | Wide Bay | Unplanned Outage | HV-Conductor Connection Failure | Unknown | due to a SCADA Automated Event | FC |  | KINKUNA: GOODWOOD RD CHILDERS: FOLEYS RD FARNSFIELD: PRANGES RD, STRANOS RD, JOHNSONS RD, FARNSFIELD RD, HETHERINGTONS RD NORTH GREGORY: FOLEYS RD | FARNSFIELD 11kV Gregory River 593248 ACR CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface chlcs01 Sending Asset Event to FFA FFA Order Created F-AE24WB4041-1-0 DfltHost Crew advised that there is a broken cross arm and require access to repair it Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 14-Mar to 10:45 14-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB4041-1-0 chlcs01 REDACTED 0418889698 FFA Order En Route F-AE24WB4041-1-0 chlcs01 FFA Order On Site F-AE24WB4041-1-0 chlcs01 FFA Order En Route F-AE24WB4041-1-0 chlcs01 FFA Order On Site F-AE24WB4041-1-0 chlcs01 FFA Order F-AE24WB4041-1-0 Completed by technician REDACTED in crew chlcs01(0418889698) with code A-T-43 - Vehicle/Machinery impact Action Taken : machine has hit pole and broken the cross arm Site Label : 3095400 | 1 | 9296293 | 3095400 | 9261588 | 3095400 | 9296293 | 2024-04-15 | -32 |  |  |  | 11 |  |  | Serviceable | N | Urb service pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | GM GYMPIE MESSMATE | 8 kiloNewton |  |  |  | 000009296293
EECL | OT229970 | OP | Operational |  | 2024-03-18 | 202403 | Crossarm | Xarm, Wood Intermediate | Loose Fitting | Vibration |  | 11kV |  |  |  | 1553518 | 2024 | 24SW6416 | 2024-03-18 16:55 | 2024-03-18 13:19 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | UMBIRAM: WYREEMA ATHOL RD WYREEMA: WESTBROOK WYREEMA RD, WYREEMA ATHOL RD | Outage required to repair windmill arm at 3181788 Located between PE03093 and PE11088 | Switching Sheet ID updated from to J-302466-g. Time Off modified from 16:00 18-Mar to 16:55 18-Mar Time On modified from 20:00 18-Mar to 17:52 18-Mar | 1 | 2178581 | 1plE 483 Wyreema/Athol Rd,Athol | 1553518 | 3181788 | 2178581 | 2020-11-23 | 1211 | N |  |  | 14 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 4 kiloNewton | 1968 | -27.6423 | 151.8049 | 000002178581 | 01/JAN/68
EECL | OT230114 | OP | Operational |  | 2024-03-19 | 202403 | Crossarm | Xarm, Wood Strain | Deteriorated | Rot/Decay |  | LV |  |  |  | 1009303 | 2024 | 24CA4644 | 2024-03-19 13:32 | 2024-03-19 12:43 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | CAPELLA: BURN ST, CONRAN ST | 22kV Pole Dist Sub 338799 - LV outage to replace LV arm | 22kV Pole Dist Sub 338799 - LV outage to replace LV arm Time On modified from 14:00 19-Mar to 15:30 19-Mar clmcm03 Sending Asset Event to FFA Time Off modified from 13:00 19-Mar to 13:32 19-Mar Time On modified from 15:30 19-Mar to 14:25 19-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Created F-AE24CA4644-1-0 DfltHost FFA Order cancelled.F-AE24CA4644-1-0 Crews need AE to complete forms clmcm03 Sending Asset Event to FFA FFA Order Created F-AE24CA4644-1-1 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA4644-1-1 clmcm03 REDACTED 0408438176 FFA Order En Route F-AE24CA4644-1-1 clmcm03 FFA Order On Site F-AE24CA4644-1-1 clmcm03 FFA Order F-AE24CA4644-1-1 Completed by technician REDACTED in crew CLMCM03(0408438176) with code A-F-C - Completed Action Taken : P0 LV arm changed under lv forced outage. Site Label : 4046019 Time On modified from 14:25 19-MAR to 07:10 20-MAR | 1 | 2667167 | opp 52 Conran St Capella | 1009303 | 4046019 | 2667167 | 2024-03-20 | -1 | N |  |  | 11 |  |  | Serviceable | Y | Urb sty term 1 cct | WOOD UNTREATED ROUND | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -23.0842 | 148.0288 | 000002667167 | 01/JAN/54
EECL | OT230161 | OP | Operational |  | 2024-03-19 | 202403 | Crossarm | Xarm, Steel Termination | Broken | Corrosion |  | LV |  |  |  | 983770 | 2024 | 24NQ6397 | 2024-03-19 21:43 | 2024-03-19 21:47 | COMP | Completed |  | Wet / Rain | North Queensland | Unplanned Outage | Animal Insects (termites/borers/white ants) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FE |  | CAMOOWEAL: BARKLY ST | F-3570-s - CAMOOWEAL 415V Feeder 3 CB CW-03 tripped. SCADA Interface automated outage. Broken LV cross-arm at IGS865 due to termite damage - Replaced under 24NQ6418. Pole needs to be replaced in the next 12 months. SL 5127747. REDACTED | entered from the SCADA Interface REDACTED supi advised leave till Depto hrs/early morning he will contact REDACTED to organise crew and have them call with pad ID. As per above notes Time On modified from 23:59 19-Mar to 23:59 20-Mar PSA has reported broken cross arms near the Post Office Hotel Motel, details have been emailled to O/C Supervisor REDACTED and O/C Crew REDACTED. Depot Co-ord Advised F-3570-s REDACTED is arranging crews - ETA 0900 IGS865, LV isolated due to broken LV x-arm. No supplies to servo, hotel, etc. Sending Asset Event to FFA FFA Order Created F-AE24NQ6397-1-0 DfltHost FFA Order Acknowledged F-AE24NQ6397-1-0 mtioc01 REDACTED 0483220419 FFA Order En Route F-AE24NQ6397-1-0 mtioc01 FFA Order On Site F-AE24NQ6397-1-0 mtioc01 Assets extracted from IGS865 (FRANCES WEST) into event 24NQ6418 Time On modified from 23:59 20-Mar to 12:35 20-Mar Manual Reclose Checklist Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24NQ6397-1-0 Completed by technician REDACTEDin crew MTIOC01(0483220419) with code A-T-299 - Animal Insects (termites/borers/white ants) Action Taken : Top x arm snapped due to termites. replaced x arm. bottom arm and pole need to be replaced in the next 12 months Site Label : 5127747 Updated Reasons tab. Reason for Event changed from Unknown | 1 | 3165785 | Cnr Kennedy & barkly hwy camooweal | 983770 | 20 | 3165785 | 2020-02-27 | 1482 | N |  |  | 11 |  | 2 | Serviceable | N | LV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | FR FOREST RED GUM | 8 kiloNewton | 1995 | -19.9212 | 138.1176 | 000003165785 | 01/JAN/95
EECL | OT230488 | OP | Operational |  | 2024-03-22 | 202403 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 66kV |  |  |  | 5306013 | 2024 | 24NQ6545 | 2024-03-22 11:19 | 2024-03-22 10:12 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE |  | N/A | Replace Cross Arm at Pole 5242972 | Replace Cross Arm at Pole 5242972 Switching Sheet ID updated from to J-303197-g. Time Off modified from 11:00 22-Mar to 11:19 22-Mar Time On modified from 13:30 22-Mar to 13:37 22-Mar Sending Asset Event to FFA FFA Order Created F-AE24NQ6545-1-0 DfltHost FFA Order Acknowledged F-AE24NQ6545-1-0 hhlfr01 REDACTED 0438092091 FFA Order En Route F-AE24NQ6545-1-0 hhlfr01 FFA Order On Site F-AE24NQ6545-1-0 hhlfr01 FFA Order F-AE24NQ6545-1-0 Completed by technician REDACTED in crew hhlfr01(0438092091) with code A-F-C - Completed Action Taken : Replaced broken 66kV wishbone arm Site Label : 5242972 | 1 | 5306014 | Rrl.71 Giddy Rd Ayr | 5306013 | 5242972 | 5306014 | 2022-10-27 | 512 | N |  |  | 17 | 2 | 1 | Unserviceable - P2 | Y | 66kV with HV sub | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1970 | -19.6186 | 147.3853 | 000005306014 | 01/JAN/70
EECL | OT230593 | OP | Operational |  | 2024-03-23 | 202403 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | LV |  |  |  | 1814526 | 2024 | 24NQ6578 | 2024-03-23 15:10 | 2024-03-23 18:28 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | LV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | GT |  | HOME HILL: KIRKNIE RD | Report of LV conductors down beyond 11kV Pole Dist Sub BDS860 | Report of LV conductors down beyond 11kV Pole Dist Sub BDS860 Sending Asset Event to FFA FFA Order Created F-AE24NQ6578-1-0 DfltHost REDACTED on HHLFR01 Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ6578-1-0 hhlfr01 REDACTED 0438092091 FFA Order En Route F-AE24NQ6578-1-0 hhlfr01 FFA Order On Site F-AE24NQ6578-1-0 hhlfr01 FFA Order F-AE24NQ6578-1-0 Completed by technician REDACTED in crew hhlfr01(0438092091) with code A-T-311 - LV-Unassisted failure(Apparent defect) Action Taken : Broken LV intermediate cross arm. Broken LV conductor. Replaced broken LV cross arm and repaired damaged conductor. Site Label : 5159441 Time On modified from 23:59 23-MAR to 19:07 23-MAR | 1 | 3275351 | ToffSWBtwn.Rrl.485to533KirknieRdHomehill | 1814526 | 5159441 | 3275351 | 2024-03-11 | 12 | N |  |  | 11 |  | 1 | Serviceable | Y | Rrl inter spn <100m | WOOD (GREEN) SALT IMPREG CCA | Soil | Sugar Cane | GM GYMPIE MESSMATE | 5 kiloNewton | 1979 | -19.6874 | 147.3756 | 000003275351 | 01/JAN/79
EECL | OT230703 | OP | Operational |  | 2024-03-24 | 202403 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 996002 | 2024 | 24WB4393 | 2024-03-24 14:53 | 2024-03-24 15:59 | COMP | Completed |  | Wet / Rain | Wide Bay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | DUNMORA: SUTHERS RD | 11kV Pole Dist Sub 15057 - Due to lines down FFA Order F-AE24WB4393-1-0 Completed by technician REDACTED in crew mrboc01(0418394900 ) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Cross arm broke causing HV conductor to fall to the round. Protection operated at 11kv fuse 10782. Repairs made replaced HV strain arm and single phase 10 KVA transformer. Site Label : 3057494 | 11kV Pole Dist Sub 15057 - Due to lines down HV Wires Down Sending Asset Event to FFA FFA Order Created F-AE24WB4393-1-0 DfltHost MRBOC01 Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Replay sequence/s deleted after 24-MAR-24 14:52:34 Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB4393-1-0 mrboc01 REDACTED 0418394900 FFA Order En Route F-AE24WB4393-1-0 mrboc01 FFA Order On Site F-AE24WB4393-1-0 mrboc01 Crew updated restore time. Time On modified from 23:59 24-Mar to 02:00 25-Mar Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 02:00 25-Mar to 01:03 25-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24WB4393-1-0 Completed by technician REDACTED in crew mrboc01(0418394900 ) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Cross arm broke causing HV conductor to fall to the round. Protection operated at 11kv fuse 10782. Repairs made replaced HV strain arm and single phase 10 KVA transformer. Site Label : 3057494 | 1 | 5349960 | Sub15057 275 Suthers RD DUNMORA | 996002 | 3057494 | 5349960 | 2020-05-14 | 1410 | N |  |  | 12.5 | 3 |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 12 kiloNewton | 1999 | -25.5016 | 152.5383 | 000005349960 | 01/JAN/99
EECL | OT230746 | OP | Operational |  | 2024-03-25 | 202403 | Crossarm | Xarm, Wood Termination | Loose Fitting | Vibration |  | 11kV |  |  |  | 1535543 | 2024 | 24SW6773 | 2024-03-25 07:15 | 2024-03-25 07:17 | DLY | Delayed |  | Wet / Rain | South West | Unplanned Outage | HV-Conductor Connection Failure | Protective Device Operated | due to the operating of protective equipment. | FE |  | BROOKSTEAD, KINCORA, YARRANLEA | F-3593-s YARRNLEA STH 11kV Brkstd Fdr CB 3994 tripped. SCADA Interface automated outage. | entered from the SCADA Interface OC trip to lockout MILOC01 - REDACTED . Sending Asset Event to FFA FFA Order Created F-AE24SW6773-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW6773-1-0 miloc01 REDACTED 0417600214 Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order En Route F-AE24SW6773-1-0 miloc01 FFA Order On Site F-AE24SW6773-1-0 miloc01 FFA Order En Route F-AE24SW6773-1-0 miloc01 FFA Order On Site F-AE24SW6773-1-0 miloc01 Asset selection modified Sending Asset Event to FFA No customers affected, this TX maybe left off until further notice. Sending Asset Event to FFA Sending Asset Event to FFA REDACTED advised the Customer is considering removing line. Live Line Taps left open. Sending Asset Event to FFA as above Time On modified from 23:59 25-Mar to 23:59 30-Jun Sending Asset Event to FFA FFA Order F-AE24SW6773-1-0 Completed by technician REDACTED in crew miloc01(0417600214) with code A-T-304 - HV-Conductor Connection Failure Action Taken : hv eye bolt rusted out and let go replaced arm and spliced in conductors retenssioned spans Site Label : 3038220 | 1 | 2697045 | 5001 Gore Hwy,Brookstead | 1535543 | 3038220 | 2697045 | 2020-11-11 | 1230 | N |  |  | 12.5 | 2 |  | Serviceable | N | Rrl Toff | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1989 | -27.7548 | 151.5104 | 000002697045 | 01/JAN/89
EECL | OT231179 | OP | Operational |  | 2024-03-27 | 202403 | Crossarm | Xarm, Wood Termination | Deteriorated | Termites |  | LV |  |  |  | 721952 | 2024 | 24CA4993 | 2024-03-27 14:11 | 2024-03-27 14:10 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | CLERMONT: CAPELLA ST, CAPRICORN ST, LIME ST, MIMOSA ST | REDACTED advised lv cross arm snapped at SL 2008177 need LV outage for repairs at TRX 338105. | REDACTED advised lv cross arm snapped at SL 2008177 need LV outage for repairs at TRX 338105. Sending Asset Event to FFA FFA Order Created F-AE24CA4993-1-0 DfltHost CLMCM03 Time Off modified from 14:30 27-Mar to 14:11 27-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA4993-1-0 clmcm03 REDACTED 0408438176 FFA Order En Route F-AE24CA4993-1-0 clmcm03 FFA Order On Site F-AE24CA4993-1-0 clmcm03 Time On modified from 23:59 27-Mar to 15:40 27-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24CA4993-1-0 Completed by technician REDACTED in crew clmcm03(0408438176) with code A-F-C - Completed Action Taken : lv cross arm snapped lv outage at tx338105 to replace lv cross arm. Pole is deemed as PO and will be replaced under forced outage Friday 29.03.24 Site Label : 2008177 Time On modified from 15:40 27-MAR to 15:45 27-MAR | 1 | 2018509 | Cnr Lime St /Capella St Clermont | 721952 | 2008177 | 2018509 | 2021-06-14 | 1017 | N |  |  | 12.5 |  | 2 | Serviceable | N | LV fully suppd | WOOD CREOSOTE IMPREGNATED | Lawn |  | ZZ NO DISC - UNKNOWN | 5 kiloNewton |  | -22.8187 | 147.6412 | 000009384674
EECL | OT231364 | OP | Operational |  | 2024-03-28 | 202403 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | LV |  |  |  | 1827080 | 2024 | 24NQ6845 | 2024-03-28 17:45 | 2024-03-28 17:48 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | due to public safety concerns. | GT |  | KALKADOON: KILLARA CRES, KOLONGO CRES | MIS620, crew advised broken lv x-arm. Crews isolated Lv on sub. | MIS620, crew advised broken lv x-arm. Crews isolated Lv on sub. Time Off modified from 19:00 28-Mar to 17:45 28-Mar Sending Asset Event to FFA FFA Order Created F-AE24NQ6845-1-0 DfltHost A/R restored Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ6845-1-0 mtioc01 FFA Order En Route F-AE24NQ6845-1-0 mtioc01 FFA Order On Site F-AE24NQ6845-1-0 mtioc01 Restoration Comments for F-AE24NQ6845-1-0 by mtioc01: change of crossarm and resag conductors, safe to energise FFA Order En Route F-AE24NQ6845-1-0 mtioc01 FFA Order On Site F-AE24NQ6845-1-0 mtioc01 FFA Order F-AE24NQ6845-1-0 Completed by technician REDACTED n crew mtioc01() with code A-F-C - Completed Action Taken : isolate via lv fuses on MIS620, replace crossarm on 5214900 Site Label : 5214900 Time On modified from 23:59 28-MAR to 19:53 28-MAR | 1 | 3348562 | 2 kolongo cres mt isa | 1827080 | 5214900 | 3348562 | 2019-10-14 | 1627 | N |  |  | 11 |  | 2 | Serviceable | Y | Urb unsty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | RI RED IRONBARK | 5 kiloNewton | 1974 | -20.6622 | 139.4941 | 000003348562 | 01/JAN/74
EECL | OT231426 | OP | Operational |  | 2024-03-29 | 202403 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1474591 | 2024 | 24SW7035 | 2024-03-29 11:08 | 2024-03-29 11:10 | COMP | Completed |  | Fine | South West | Unplanned Outage | HV-Conductor Connection Failure | Unknown | due to damage requiring emergency repairs. Fault finding is in progress. | SZ |  | KOOROONGARRA, MILLMERRAN, MILLWOOD, MOUNT EMLYN | F-2686-r - MILM - Bringalily FDR - 11kV Sectionaliser SEC609025 has operated | 11kV Sectionaliser SEC609025 has operated Sending Asset Event to FFA FFA Order Created F-AE24SW7035-1-0 DfltHost twmoc03 Sending Asset Event to FFA Sending Asset Event to FFA re-assigned twmoc04 Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW7035-1-0 twmoc04 REDACTED 0427965369 Asset selection modified Sending Asset Event to FFA HV Wires Down Sending Asset Event to FFA Time On modified from 23:59 29-Mar to 18:40 29-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE24SW7035-1-0 twmoc04 FFA Order On Site F-AE24SW7035-1-0 twmoc04 FFA Order F-AE24SW7035-1-0 Completed by technician REDACTED n crew twmoc04(0427965369) with code A-T-304 - HV-Conductor Connection Failure Action Taken : crew attended site and found customers who found the broken cross arm were guarding the fallen wire which had come down across a rural road. Cross arm at pole 3037294 was broken due to age and one 11kv conductor was on the ground and the other two were in the air. crew barricaded road with signs and cones either way and isolated and earthed the supply at DL12168. Site Label : 3037294 | 1 | 2693466 | 2936/3406 Stonehenge Rd,Stonehenge | 1474591 | 3037294 | 2693466 | 2019-10-15 | 1627 | N |  |  | 14 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -28.1279 | 151.3281 | 000002693466 | 01/JAN/76
EECL | OT231451 | OP | Operational |  | 2024-03-29 | 202403 | Crossarm | Xarm, Wood Strain | Deteriorated | Rot/Decay |  | LV |  |  |  | 1326799 | 2024 | 24WB4540 | 2024-03-29 16:39 | 2024-03-29 19:46 | COMP | Completed |  | Wet / Rain | Wide Bay | Unplanned Outage | LV-Conductor Connection Failure | Unknown | Single Fault Call | GT |  | 694 RIVER RD;BUNGADOO QLD 4671 | Fault occurred at:29/03/2024 16:36; REDACTED, 0409547115;>WDPP --> AffectingTraffic:NO -- StillHavePower:YES<;Incident Details:1 line is hanging low to the TX that feeds this metering point. Tree growing through one of the poles;Access Details:Past first house towards second house pole 6568 3311975;COVID-19:NO;Warnings[wiresDownSafety]: ADVISED;Dog restraint:ARRIVAL;Sensitive Load:N |  | 1 | 2774312 | at house 694 river rd bungadoo | 1326799 | 3311973 | 2774312 | 2020-05-08 | 1421 | N |  |  | 12.5 | 3 | 1 | Serviceable | N | Rrl sty term 2 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1981 | -25.053 | 152.0914 | 000002774312 | 01/JAN/81
EECL | OT231787 | OP | Operational |  | 2024-04-02 | 202404 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1660724 | 2024 | 24SW7101 | 2024-04-02 19:04 | 2024-04-02 16:44 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | AUBIGNY: CIESIOLKA RD YARGULLEN: ARMITAGE RD, O'BRIEN RD, OAKEY-PITTSWORTH RD, RYAN RD | 11kV Disc Links DL3784 - Crew require access down stream of Disc Links DL3784 to replace a X-Arm at the Tee off to Dist Sub PE09528 | 11kV Disc Links DL3784 - Crew require access down stream of Disc Links DL3784 to replace a X-Arm at the Tee off to Dist Sub PE09528 F-2697 TWMOC01 Sending Asset Event to FFA FFA Order Created F-AE24SW7101-1-0 DfltHost Time Off modified from 17:03 02-Apr to 19:04 02-Apr Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW7101-1-0 twmoc01 REDACTED 0428221390 FFA Order En Route F-AE24SW7101-1-0 twmoc01 FFA Order On Site F-AE24SW7101-1-0 twmoc01 Time On modified from 23:59 02-Apr to 21:25 02-Apr Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW7101-1-0 Completed by technician REDACTED in crew twmoc01(0428221390) with code A-F-C - Completed Action Taken : Replaced broken HV term arm Site Label : 3073260 | 1 | 2864545 | 4w 114 Armitage Rd Aubigny | 1660724 | 3073260 | 2864545 | 2024-04-27 | -25 | N |  |  | 14 | 2 |  | Serviceable | N | Rrl sty ang20-30o | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -27.4959 | 151.6733 | 000001660724 | 01/JAN/68
EECL | OT231904 | OP | Operational |  | 2024-04-03 | 202404 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1448947 | 2024 | 24MK3325 | 2024-04-03 15:32 | 2024-04-03 15:37 | COMP | Completed |  | Fine | Mackay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | MIA MIA: HOGANS RD MIRANI: BADGER WALES RD, MACKAY EUNGELLA RD, MIA MIA CONNECTION RD, MIRANI ETON RD PINEVALE: PINEVALE RD, WELSHS RD, WHITEFORDS RD SEPTIMUS: KADDATZ RD | Weir Fdr, broken crossarnm at sub 5991, wirea at 1m above ground, tripped fdr Crew replaced 2 x broken cross-arms. SL 4143731. REDACTED | Weir Fdr, broken crossarnm at sub 5991, wirea at 1m above ground, tripped fdr Sending Asset Event to FFA FFA Order Created F-AE24MK3325-1-0 DfltHost Crew; REDACTED Time Off modified from 15:34 03-Apr to 15:32 03-Apr Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 03-Apr to 20:30 03-Apr Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 20:30 03-Apr to 21:30 03-Apr Sending Asset Event to FFA Time On modified from 21:30 03-Apr to 22:30 03-Apr Sending Asset Event to FFA FFA Order Acknowledged F-AE24MK3325-1-0 pncoc01 REDACTED 0401409049 FFA Order En Route F-AE24MK3325-1-0 pncoc01 FFA Order On Site F-AE24MK3325-1-0 pncoc01 FFA Order F-AE24MK3325-1-0 Completed by technician REDACTED in crew pncoc01(0401409049) with code A-T-330 - Fuse Operated - No Trigger Found Action Taken : replaced 2 x broken x arm Site Label : 4143731 Time On modified from 22:30 03-Apr to 23:30 03-Apr Time On modified from 23:30 03-Apr to 23:09 03-Apr Updated Reasons tab. Updated Event Trigger from FO - NTF to HV-Unassisted failure. | 1 | 3213379 | sub5991 off nicholson rd mirani-eton rd | 1448947 | 4143731 | 3213379 | 2020-03-28 | 1467 | N |  |  | 14 | 4 | 1 | Serviceable | Y | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | GI GREY IRONBARK | 8 kiloNewton | 1990 | -21.1919 | 148.8346 | 000001448947 | 01/JAN/90
EECL | OT232062 | OP | Operational |  | 2024-04-04 | 202404 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1342399 | 2024 | 24WB4631 | 2024-04-04 18:20 | 2024-04-04 18:23 | COMP | Completed |  | Fine | Wide Bay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to a SCADA Automated Event | FE |  | BURRUM HEADS, BURRUM RIVER, PACIFIC HAVEN | F-2709-r - HOWARD 11kV Burrum Heads Fdr CB FB08Q00 tripped. SCADA Interface automated outage. Crew replaced broken 11kV term arm. SL 3024477. REDACTED | entered from the SCADA Interface FB08Q00 11KV BURRUM HEADS FDR CB FB08Q00 - Tripped to Lockout on OC HBOC01 Depot Co-ord Advised Sending Asset Event to FFA FFA Order Created F-AE24WB4631-1-0 DfltHost Fault call indicates possible cable theft. crews to advise Sending Asset Event to FFA Crew Continuing patrolling Fault call for digging up cables didnt seem to be an issue. Sending Asset Event to FFA crew found broken term arm between TX7788 & DL895616. Crew comnpleting isolations and earthing. Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB4631-1-0 hboc01 REDACTED 0447761083 FFA Order En Route F-AE24WB4631-1-0 hboc01 FFA Order On Site F-AE24WB4631-1-0 hboc01 Gradually restoring Supply with S455 with Reclosers RC805148 & 583458 Open. Sending Asset Event to FFA Closing S455 at 2137 Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA Closed RC805148 at 2148 Asset selection modified Sending Asset Event to FFA Opened RC805146 due to load issue Asset selection modified Sending Asset Event to FFA Close 583458 at 2158 Asset selection modified Sending Asset Event to FFA Crew advised by the time they sectionalise downstream of RC805146 they will be ready to reverse switch. Sending Asset Event to FFA Std Reason Changed from Unknown by REDACTED 0447761083 Asset selection modified Sending Asset Event to FFA FFA Order F-AE24WB4631-1-0 Completed by technician REDACTED in crew hboc01(0447761083) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Replaced broken 11kV Term arm Site Label : 3024477 Time On modified from 23:59 04-Apr to 23:38 04-Apr Added notes to Reasons tab. | 1 | 2621626 | 43 CONDAMINE RD HOWARD | 1342399 | 3024477 | 2621626 | 2019-07-03 | 1737 | N |  |  | 14 | 2 | 1 | Serviceable | N | HV partly suppd | WOOD UNTREATED ROUND | Grass | Road Reserve | NI NARROW LEAF RED I | 3 kiloNewton |  | -25.3057 | 152.5796 | 000001342399 | 01/JAN/99
EECL | OT232311 | OP | Operational |  | 2024-04-07 | 202404 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1404291 | 2024 | 24WB4678 | 2024-04-07 06:38 | 2024-04-07 06:48 | COMP | Completed |  | Wet / Rain | Wide Bay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | GAYNDAH: BERONNE RD IDERAWAY: BONNY ST, IDERAWAY RD, MINGO ST, OLD STOCK ROUTE RD, TANJOUR ST, YENDA ST | F-3251-q - Fault calls from Sub 1818 and 526081 indicate possible issue with 11kV Dropout Fuse 509121 - 1 Phase Down Crew advise - Broken Crossarm | Fault calls from Sub 1818 and 526081 indicate possible issue with 11kV Dropout Fuse 509121 - 1 Phase Down gynoh01 Sending Asset Event to FFA FFA Order Created F-AE24WB4678-1-0 DfltHost FFA Order Acknowledged F-AE24WB4678-1-0 gynoh01 REDACTED 0427847195 FFA Order En Route F-AE24WB4678-1-0 gynoh01 FFA Order On Site F-AE24WB4678-1-0 gynoh01 Time On modified from 23:59 07-Apr to 10:00 07-Apr Reason for Event changed from Unknown Sending Asset Event to FFA Time On modified from 10:00 07-Apr to 12:00 07-Apr Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24WB4678-1-0 Completed by technician REDACTED in crew GYNOH01(0427847195) with code A-T-304 - HV-Conductor Connection Failure Action Taken : 3phase Termination x arm snapped @ king bolt on pole causing line fuse to blow. replaced x arm. Site Label : 3046886 Time On modified from 12:00 07-Apr to 11:37 07-Apr | 1 | 2742194 | lks 5328 2E Cadell st/Bonny st Ideraway | 1404291 | 3046886 | 2742194 | 2023-12-18 | 111 | N |  |  | 15.5 | 2 |  | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 12 kiloNewton | 1983 | -25.5813 | 151.6229 | 000001404291 | 01/JAN/83
EECL | OT232477 | OP | Operational |  | 2024-04-08 | 202404 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1384947 | 2024 | 24WB4717 | 2024-04-08 16:53 | 2024-04-08 15:42 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | ALDERSHOT: BRUCE HWY, FLUERTY RD, STEIN RD MARYBOROUGH: BRUCE HWY | 11kV Disc Links S3463. Outage to repair broken crossarm just past 7715 | 11kV Disc Links S3463. Outage to repair broken crossarm just past 7715 Time Off modified from 15:55 08-Apr to 16:00 08-Apr Time On modified from 23:59 08-Apr to 18:30 08-Apr Time Off modified from 16:00 08-Apr to 16:53 08-Apr Time On modified from 18:30 08-Apr to 19:30 08-Apr Time On modified from 19:30 08-Apr to 18:13 08-Apr | 1 | 2801061 | 23817 bruce h/way aldershot | 1384947 | 3059281 | 2801061 | 2019-09-23 | 1659 | N |  |  | 12.5 | 2 |  | Serviceable | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1986 | -25.4636 | 152.6469 | 000001384947 | 01/JAN/86
EECL | OT232488 | OP | Operational |  | 2024-04-08 | 202404 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1370591 | 2024 | 24WB4720 | 2024-04-08 16:24 | 2024-04-08 16:50 | COMP | Completed |  | Fine | Wide Bay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | SZ |  | GOOMERI: KINBOMBI RD KINBOMBI: KINBOMBI FALLS RD, KINBOMBI RD, WALKER RD, WIDE BAY HWY | F-3257-q - 11kV Dropout Fuse S1970 - Fault calls suggest possible fuse blown | 11kV Dropout Fuse S1970 - Fault calls suggest possible fuse blown mrgoc05 Sending Asset Event to FFA FFA Order Created F-AE24WB4720-1-0 DfltHost FFA Order Acknowledged F-AE24WB4720-1-0 mrgoc05 REDACTED 0407690142 FFA Order En Route F-AE24WB4720-1-0 mrgoc05 FFA Order ETA submitted 08-APR-2024 17:45:00 FFA Order On Site F-AE24WB4720-1-0 mrgoc05 Sending Asset Event to FFA Crew to patrol before MR, found wires down Sending Asset Event to FFA HV Wires Down Reason for Event changed from Unknown Sending Asset Event to FFA ETA restore time 2300 Time On modified from 23:59 08-Apr to 23:00 08-Apr Sending Asset Event to FFA Restoration Comments for F-AE24WB4720-1-0 by MRGOC05: Grounded HV conductor restrung to pole and bridged in. Time On modified from 23:00 08-Apr to 23:45 08-Apr Sending Asset Event to FFA FFA Order F-AE24WB4720-1-0 Completed by technician REDACTED in crew MRGOC05(0407690142) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : White rot in one side of one arm in bulla strain construction. Bulla pulled out of arm bring 2 span of conductor to ground. Drilled hole further in on arm and reattached Bulla and restrung conductor. Site Label : 3044143 Time On modified from 23:45 08-Apr to 23:27 08-Apr | 1 | 2727193 | 922 Kinbombi rd, Kinbombi. acc g W of | 1370591 | 3044143 | 2727193 | 2020-04-27 | 1442 | N |  |  | 11 | 2 |  | Serviceable | N | Rrl sty angle 5-20o | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1974 | -26.2447 | 152.1763 | 000001370591 | 01/JAN/74
EECL | OT232585 | OP | Operational |  | 2024-04-09 | 202404 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 995218 | 2024 | 24SW7438 | 2024-04-09 12:09 | 2024-04-09 17:12 | CAN | Cancelled |  |  | South West | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | WANDELLA 555 BRIGALOW-CANAGA RD BRIGALOW QLD 4412 | REDACTED (3267) 0429 538597 has report HV support Xarm has broken at pole 3102482 no line downs. REDACTED will wait onsite. Sub PC00116 P1 Call Flag | outage cancelled via Clash Wizard | 1 | 2999009 | pc116 555 BRIGALOW CANAGA RD Brigalow | 995218 | 3102482 | 2999009 | 2024-04-10 | -1 | N |  |  | 14 | 4 | 1 | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Backyard | SG SPOTTED GUM | 5 kiloNewton | 1981 | -26.8016 | 150.8197 | 000000995218 | 01/JAN/81
EECL | OT232718 | OP | Operational |  | 2024-04-10 | 202404 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | LV |  |  |  | 815875 | 2024 | 24WB4793 | 2024-04-10 13:22 | 2024-04-10 13:28 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | BULLCAMP: MYLETTS LANE, RETSCHLAG RD NANANGO: BULLCAMP RD, HORNE LANE, MOUNT STANLEY RD, SELECTION LANE | 11kV Recloser S5822 - Report of Lines down and low conductor. Depot Co-Ordinator requested SWER to be tripped for safety.. | 11kV Recloser S5822 - Report of Lines down and low conductor. Depot Co-Ordinator requested SWER to be tripped for safety.. send to kngcm01 REDACTED Sending Asset Event to FFA FFA Order Created F-AE24WB4793-1-0 DfltHost Crew found broken LV crossarm on TX 10610, isolating TX to re-energise & repair Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 10-Apr to 17:22 10-Apr Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB4793-1-0 kngcm01 REDACTED 0437306402 FFA Order En Route F-AE24WB4793-1-0 kngcm01 FFA Order En Route F-AE24WB4793-1-0 kngcm01 FFA Order On Site F-AE24WB4793-1-0 kngcm01 FFA Order F-AE24WB4793-1-0 Completed by technician REDACTEDin crew kngcm01(0437306402) with code A-F-C - Completed Action Taken : replaced broken lv term on SWER tranny pole Site Label : 4243978 | 1 | 3162558 | TX10610 end Niagara Rd Nanango | 815875 | 4243978 | 3162558 | 2020-08-23 | 1326 | N |  |  | 12.5 |  | 1 | Serviceable | Y | SWER sty angle | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | ZZ NO DISC - UNKNOWN | 12 kiloNewton | 1992 | -26.6539 | 152.1147 | 000000815875 | 01/JAN/92
EECL | OT232727 | OP | Operational |  | 2024-04-10 | 202404 | Crossarm | Xarm, Wood Termination | Split | Termites |  | 11kV |  |  |  | 6237204 | 2024 | 24NQ7278 | 2024-04-10 15:30 | 2024-04-10 14:39 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | BROUGHTON: ALEXANDRA RD, ASHGLEN RD, BROUGHTON RD, HARBUTT RD, ROBERTSON RD CHARTERS TOWERS: ALEXANDRA RD, QUEENSLANDER CK RD | F-3684-s - CHTO - 04 - Crews required to repair broken Xarm tee off pole towards CTS688 | F-3684-s - CHTO - 04 - Crews required to repair broken Xarm tee off pole towards CTS688 Sending Asset Event to FFA FFA Order Created F-AE24NQ7278-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 18:00 10-Apr to 15:33 10-Apr Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ7278-1-0 chtcs05 REDACTED 0438521601 FFA Order En Route F-AE24NQ7278-1-0 chtcs05 FFA Order On Site F-AE24NQ7278-1-0 chtcs05 FFA Order F-AE24NQ7278-1-0 Completed by technician REDACTED in crew CHTCS05(0438521601) with code A-F-C - Completed Action Taken : termites caused broken arm. hv switching isolated earthed and access to complete cross arm change Site Label : 2153801 | 1 | 2404094 | 53 alexandra rd ch towers | 6237204 | 2153801 | 2404094 | 2021-02-12 | 1153 | N |  |  | 12.5 | 2 |  | Serviceable | N | Rrl Toff | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | GI GREY IRONBARK | 5 kiloNewton | 1988 | -20.1006 | 146.2961 | 000006237204 | 01/JAN/88
EECL | OT232766 | OP | Operational |  | 2024-04-10 | 202404 | Crossarm | Xarm, Wood Dressing | Broken | Rot/Decay |  | LV |  |  |  | 1436209 | 2024 | 24SW7493 | 2024-04-10 20:48 | 2024-04-10 20:30 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | HARRISTOWN: BLACKDOWN ST, DUNNE ST, FIRST AVE, FOURTH AVE, SECOND AVE, STEPHEN ST, THIRD AVE, UNDERWOOD CRES, WEST ST TOOWOOMBA: WEST ST | Crew adv need access to the LV network and will isolate at the LV TX Fuses on 11kV Pole Dist Sub PE00379, LV SWITCHING ONLY. Crew replaced LV pin arm. SL 3208230. REDACTED | Crew adv need access to the LV network and will isolate at the LV TX Fuses on 11kV Pole Dist Sub PE00379, LV SWITCHING ONLY. twmfrsl01 Time On modified from 23:59 10-Apr to 22:30 10-Apr Sending Asset Event to FFA FFA Order Created F-AE24SW7493-1-0 DfltHost Sending Asset Event to FFA Time Off modified from 21:00 10-Apr to 20:48 10-Apr Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW7493-1-0 twmfrsl01 REDACTED 0401294792 FFA Order En Route F-AE24SW7493-1-0 twmfrsl01 FFA Order On Site F-AE24SW7493-1-0 twmfrsl01 Time On modified from 22:30 10-Apr to 22:08 10-Apr Sending Asset Event to FFA FFA Order F-AE24SW7493-1-0 Completed by technician REDACTED in crew twmfrsl01(0401294792) with code A-F-C - Completed Action Taken : replace lv pin arm Site Label : 3208230 Actual Power Restoration for F-AE24SW7493-1-0: 10-APR-2024 22:12:00 Added notes to Reasons tab. | 1 | 2384447 | 5 Dunne St,Harristown Tba | 1436209 | 3208230 | 2384447 | 2020-11-12 | 1245 | N |  |  | 9.5 |  | 2 | Serviceable | N | Urb LV inter | WOOD UNTREATED ROUND | Lawn | Road Reserve | ZZ NO DISC - UNKNOWN |  |  | -27.5707 | 151.9384 | 000001436209 | 01/JAN/50
EECL | OT232905 | OP | Operational |  | 2024-04-11 | 202404 | Crossarm | Xarm Strap(S) | Loose Fitting | Vibration |  | 11kV |  |  |  | 727378 | 2024 | 24SW7547 | 2024-04-11 23:42 | 2024-04-11 23:45 | COMP | Completed |  | Fine | South West | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | OAKEY: AJUGA CT, WARREGO HWY, BROOKVALE PARK RD JONDARYAN: AJUGA CT, NORGAARD RD, WARREGO HWY, JONDARYAN MOUNT TYSON RD | F-2729-r - OAKEY 11kV Brokvle Pk CB18406 CB tripped. SCADA Interface automated outage. Crew replaced cross-arm coach screw that came out and twisted cross-arm, causing conductors to clash. SL 6024725. REDACTED | entered from the SCADA Interface Depot Co-ord Advised Co-ordinator (REDACTED) will get back to OCCs with plan. REDACTED on TWMOC01 Sending Asset Event to FFA FFA Order Created F-AE24SW7547-1-0 DfltHost Sending Asset Event to FFA Time On modified from 23:59 11-Apr to 23:59 12-Apr Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW7547-1-0 twmoc01 REDACTED 0451002449 FFA Order En Route F-AE24SW7547-1-0 twmoc01 Crew 5min from start of patrol Sending Asset Event to FFA 01:19 - MR unsuccessful Sending Asset Event to FFA Arm on pole 6024725 has broken causing phase to phase fault. switching to isolate & gain access under way. Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 12-Apr to 04:09 12-Apr Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW7547-1-0 twmoc03 REDACTED 0427365393 FFA Order En Route F-AE24SW7547-1-0 twmoc03 FFA Order On Site F-AE24SW7547-1-0 twmoc03 FFA Order F-AE24SW7547-1-0 Completed by technician REDACTED in crew twmoc03(0427365393) with code A-T-304 - HV-Conductor Connection Failure Action Taken : replaced x arm coach screw that came out and twisted x arm and made conductors clash at pole sl6024725 Site Label : 6024725 Added notes to Reasons tab. Updated Event Trigger from HV-CCF to HV-Unassisted failure. | 1 | 5663660 | 1S pe8704 13275 warrego hwy jondaryan | 727378 | 6024725 | 5663660 | 2023-11-17 | 146 | N |  |  | 17 | 6 |  | Serviceable | N | HV fully suppd | WOOD UNTREATED ROUND | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN |  |  | -27.4133 | 151.6204 | 000000727378 | 01/JAN/52
EECL | OT232968 | EX | External |  | 2024-04-12 | 202404 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1453164 | 2024 | 24SW7579 | 2024-04-12 19:54 | 2024-04-12 16:12 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | CAMBOOYA | F-2730-r Forced outage due to broken HV crossarm. Possible HV/ LV contact. | Forced outage due to broken HV crossarm. Possible HV/ LV contact. Alternative feeds in place. Time Off modified from 18:00 12-Apr to 19:54 12-Apr Asset selection modified Asset selection modified Time On modified from 23:00 12-Apr to 22:00 12-Apr | 1 | 2121401 | 454 Cambooya Connection Rd,Cambooya | 1453164 | 2036918 | 2121401 | 2022-04-05 | 738 | N |  |  | 14 |  | 1 | Serviceable | N | Urb unsty angle | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | BB BLACKBUTT | 5 kiloNewton | 1984 | -27.7111 | 151.869 | 000001453164 | 01/JAN/84
EECL | OT233001 | OP | Operational |  | 2024-04-12 | 202404 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | LV |  |  |  | 1905439 | 2024 | 24NQ7393 | 2024-04-12 16:28 | 2024-04-12 16:55 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | HV-Conductor Connection Failure | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | ST |  | CLARE | 11KV CLSO-02 FDR CB FB02Q00 opened for safety due to FC2422736 potential broken cross arm and lines running down pole still connected | 11KV CLSO-02 FDR CB FB02Q00 opened for safety due to FC2422736 potential broken cross arm and lines running down pole still connected crews Attending: REDACTED - 0437 728 197 . Sending Asset Event to FFA FFA Order Created F-AE24NQ7393-1-0 DfltHost Field Crews have confirmed LV Xarm only. Crews will make safe and power will be restored. Sending Asset Event to FFA Assets extracted from BDS47 into event 24NQ7394 Removing Asset Event from FFA FFA Order cancelled.F-AE24NQ7393-1-0 Time On modified from 23:59 12-Apr to 17:07 12-Apr Sending Asset Event to FFA FFA Order Created F-AE24NQ7393-1-1 DfltHost Sending Asset Event to FFA FFA Order cancelled.F-AE24NQ7393-1-1 | 1 | 2746433 | Rrl.235 George St Clare Township | 1905439 | 5052650 | 2746433 | 2024-01-11 | 92 | N |  |  | 11 |  | 1 | Serviceable | N | Urb LV inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1988 | -19.7845 | 147.2294 | 000001905439 | 01/JAN/88
EECL | OT233094 | OP | Operational |  | 2024-04-13 | 202404 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1716663 | 2024 | 24NQ7408 | 2024-04-13 17:06 | 2024-04-13 17:08 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | Vehicle/Machinery impact | Fallen Power Lines | due to fallen power lines. | FE |  | AYR, RITA ISLAND | F-3701-s - JARVISFIELD 11kV Jarv No.5 Fdr CB FB07Q00 tripped. SCADA Interface automated outage. Crew replaced termination cross-arm and retensioned conductors. SL 5113286. REDACTED | entered from the SCADA Interface Sending Asset Event to FFA FFA Order Created F-AE24NQ7408-1-0 DfltHost F-3701-s - 11KV CB FB07Q00 - EF Trip to Lockout Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Crews found HV conductors down adjacent to pole 5113286 HV Wires Down Sending Asset Event to FFA Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ7408-1-0 hhlfr01 REDACTED 0437728197 FFA Order En Route F-AE24NQ7408-1-0 hhlfr01 FFA Order On Site F-AE24NQ7408-1-0 hhlfr01 Time On modified from 23:59 13-Apr to 22:00 13-Apr Sending Asset Event to FFA Time On modified from 22:00 13-Apr to 21:08 13-Apr Sending Asset Event to FFA FFA Order F-AE24NQ7408-1-0 Completed by technician REDACTED in crew hhlfr01(0437728197) with code A-T-43 - Vehicle/Machinery impact Action Taken : Replaced termination Xarm and re tensioned conductors Site Label : 5113286 Updated Reasons tab. Updated Asset Event Type from Transmission to Distribution. Reason for Event changed from Unknown | 1 | 3068284 | cnr.Kilrie/Rita Island Rds.Jarvisfield | 1716663 | 5113286 | 3068284 | 2021-03-22 | 1118 | N |  |  | 12.5 | 2 | 1 | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | SG SPOTTED GUM | 8 kiloNewton | 1979 | -19.6112 | 147.4648 | 000001716663 | 01/JAN/79
EECL | OT233154 | OP | Operational |  | 2024-04-14 | 202404 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 22kV |  |  |  | 906866 | 2024 | 24CA5675 | 2024-04-14 16:22 | 2024-04-14 16:24 | COMP | Completed |  | Fine | Capricornia | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | DULULU: BURNETT HWY, WILLETTS RD, ALMA VALE RD, JAMESONS LANE, OFF BURNETT HWY, OFF GELOBERA RD, BUNERBA SCHOOL RD, DULULU BUNERBA RD | F-2735-r - WOWAN 22kV Willetts Rd RC852142 ACR CB tripped. SCADA Interface automated outage. ACR RC852142 ( Willetts Rd ) tripped on EF along with up stream ACR X5520 ( Deeford ). Deeford ACR reclosed successfully however Willetts Rd remain de energised Crew replaced broken cross-arm at SL 2009020 REDACTED | entered from the SCADA Interface F-2735-r - Tripped multiple times on EF - On call crew to investigate REDACTED bilcm06 Sending Asset Event to FFA FFA Order Created F-AE24CA5675-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA5675-1-0 bilcm06 REDACTED 0437516802 Sending Asset Event to FFA Onsite Crew confirmed that the is a broken x arm at pole 2009007 with a wire on the ground and a small grass fire, crews to isolate and earth HV Wires Down Sending Asset Event to FFA Sending Asset Event to FFA Contacted crew to confirm they have there switching steps and they are trying find there way out of a paddock Sending Asset Event to FFA Time On modified from 23:59 14-Apr to 14:00 15-Apr Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Time On modified from 14:00 15-Apr to 09:46 15-Apr Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA5675-1-0 bilcm02 REDACTED 0419410119 FFA Order En Route F-AE24CA5675-1-0 bilcm02 FFA Order On Site F-AE24CA5675-1-0 bilcm02 FFA Order F-AE24CA5675-1-0 Completed by technician REDACTED in crew BILCM02(0419410119) with code A-T-320 - SUBT-Unassisted failure(Apparent defect) Action Taken : replaced broken crossarm Site Label : 2009020 Updated Reasons tab. Updated Event Trigger from HV-CCF to HV-Unassisted failure. Reason for Event changed from Equipment Failure or Malfunction | 1 | 2019754 | 559 Dululu-Bunerba Rd Dululu 6 NE X2634 | 906866 | 2009020 | 2019754 | 2019-12-12 | 1585 | N |  |  | 12.5 | 1 | 1 | Serviceable | Y | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1976 | -23.8516 | 150.3435 | 000000906866 | 01/JAN/76
EECL | OT233201 | OP | Operational |  | 2024-04-15 | 202404 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1582150 | 2024 | 24SW7635 | 2024-04-15 09:18 | 2024-04-15 09:20 | COMP | Completed |  | Fine | South West | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | MARYVALE: BOURKES RD, MAILMANS RD, RATHMELLS RD, NORTH BRANCH RD | ALLORA 11kV North Branch Rd RC887474 ACR CB tripped. SCADA Interface automated outage. Crew replaced failed wishbone. SL 2140609. REDACTED | entered from the SCADA Interface sent to waroc02 Sending Asset Event to FFA FFA Order Created F-AE24SW7635-1-0 DfltHost 3 X OC trip to L/O Sending Asset Event to FFA Time On modified from 23:59 15-Apr to 23:59 16-Apr Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW7635-1-0 waroc02 REDACTED 0428723616 FFA Order En Route F-AE24SW7635-1-0 waroc02 FFA Order On Site F-AE24SW7635-1-0 waroc02 Time On modified from 23:59 16-Apr to 16:53 15-Apr Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW7635-1-0 Completed by technician REDACTED in crew waroc02(0428723616) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Replaced failed wishbone. Site Label : 2140609 Updated Event Trigger from Animal impact to HV-Unassisted failure. Updated Reasons tab. Reason for Event changed from Unknown | 1 | 2439794 | 415 North Branch rd Maryvale | 1582150 | 2140609 | 2439794 | 2022-07-26 | 629 | N |  |  | 14 | 2 | 1 | Serviceable | Y | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1964 | -28.0335 | 152.2542 | 000001582150 | 01/JAN/64
EECL | OT233202 |  | Operational |  | 2024-04-15 | 202404 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1372581 | 2024 | 24WB4909 | 2024-04-15 10:25 | 2024-04-15 10:27 |  | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | ARAMARA, BIGGENDEN, BOOMPA, BROOWEENA, DOONGUL, NORTH ARAMARA, TEEBAR, | F-2737-r - 11kV Recloser S2848 - tripped due to low hanging wires | 11kV Recloser S2848 - tripped due to low hanging wires Time Off modified from 11:00 15-Apr to 10:25 15-Apr Crew require access from Gas switch S1013 to repair lines Isolated and earthed fault call made safe. reclosing S2848 up to S1013 Asset selection modified Time On modified from 14:00 15-Apr to 15:00 15-Apr Time On modified from 15:00 15-Apr to 17:00 15-Apr Time On modified from 17:00 15-Apr to 16:54 15-Apr bgncdwgl1 Sending Asset Event to FFA FFA Order Created F-AE24WB4909-1-0 DfltHost FFA Order Acknowledged F-AE24WB4909-1-0 bgncdwgl1 REDACTED 0437047448 FFA Order En Route F-AE24WB4909-1-0 bgncdwgl1 FFA Order On Site F-AE24WB4909-1-0 bgncdwgl1 FFA Order F-AE24WB4909-1-0 Completed by technician REDACTED in crew bgncdwgl1(0437047448) with code A-F-C - Completed Action Taken : Replaced pole at SL 3040663 Site Label : 3040663 | 1 | 9390224 | 7 E Abs1013 Mboro-Biggenden Rd Biggenden | 1372581 | 3040663 | 9390224 |  | 45397 |  |  |  | 12.5 | [7 empty] | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 2023 | -25.538 | 152.0852 | 000001372581
EECL | OT233233 | OP | Operational |  | 2024-04-15 | 202404 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 66kV |  |  |  | 1187881 | 2024 | 24NQ7445 | 2024-04-15 14:33 | 2024-04-15 13:16 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | ZS |  | GREENVALE, MOUNT FOX, MOUNT GARNET | INGH - Blackriver 66kV FDR - Crew require access to repair broken xarm | INGH - Blackriver 66kV FDR - Crew require access to repair broken xarm Time On modified from 23:59 15-Apr to 17:00 15-Apr F-3710-s. Time Off modified from 14:00 15-Apr to 14:33 15-Apr Time On modified from 17:00 15-Apr to 16:14 15-Apr | 1 | 2846315 | Allendale Rd 14spnsWst Miltons Rd Ingham | 1187881 | 5070199 | 2846315 | 2024-03-21 | 25 | N |  |  | 17 |  |  | Serviceable | N | 66kV rrl inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | RI RED IRONBARK | 8 kiloNewton | 1973 | -18.7996 | 146.0576 | 000001187881 | 01/JAN/73
EECL | OT233476 | OP | Operational |  | 2024-04-17 | 202404 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1701326 | 2024 | 24NQ7537 | 2024-04-17 15:29 | 2024-04-17 15:39 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | BOWEN: BRUCE HWY N, HERMANS RD, PETER DELAMOTHE RD, WYLIE PARK RD | Crew require access to repair broken crossarm | Crew require access to repair broken crossarm Time Off modified from 15:55 17-Apr to 15:29 17-Apr Time On modified from 23:59 17-Apr to 18:00 17-Apr Time On modified from 18:00 17-Apr to 17:33 17-Apr | 1 | 3301591 | 1 spn Wylie Park Rd HermanRd end Bowen | 1701326 | 5201702 | 3301591 | 2024-01-18 | 90 | N |  |  | 12.5 | 2 |  | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | GI GREY IRONBARK | 5 kiloNewton | 1982 | -20.044 | 148.1808 | 000001701326 | 01/JAN/82
EECL | OT233782 | OP | Operational |  | 2024-04-20 | 202404 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 22kV |  |  |  | 1286787 | 2024 | 24FN5497 | 2024-04-20 16:15 | 2024-04-20 19:26 | COMP | Completed |  | Wet / Rain | Far North | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | 446 NERADA RD;NERADA QLD 4860 | Fault occurred at:20/04/2024 09:00; REDACTED, 0429653461;>LOS --> DimFlickeringLights:NO -- NeighboursAffected:UNSURE -- LostLights&Power:YES -- Switchboard:YES<;Incident Details:TLOS - believed was part of planned outage today as also has property at 50 Gattera rd. 446 Nerada has been without supply all day and still off;COVID-19:NO;Warnings[losSafety]: ADVISED;Sensitive Load:N |  | 1 | 3303437 | 141 maruff rd nerada | 1286787 | 39873 | 3303437 | 2024-03-27 | 24 | N |  |  | 14 | 4 |  | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Crop | WS WHITE STRINGYBARK | 12 kiloNewton | 1984 | -17.5296 | 145.8782 | 000001286787 | 01/JAN/84
EECL | OT233851 | OP | Operational |  | 2024-04-22 | 202404 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 22kV |  |  |  | 803689 | 2024 | 24CA5913 | 2024-04-22 06:28 | 2024-04-22 06:30 | COMP | Completed |  | Fine | Capricornia | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to a SCADA Automated Event | FC |  | THEODORE: BANANA RD, POPE'S RD, WATSONS RD, HEINICKES RD, LETCHFORD RD, LEICHHARDT HWY, CASTLE CREEK RD | THEODORE 22kV Watsons Rd RC871331 ACR CB tripped. SCADA Interface automated outage. Crew replaced broken term cross-arm. Delay in repairs due to wet paddock. SL 4228984. REDACTED | entered from the SCADA Interface Depot Co-ord Advised Sending Asset Event to FFA FFA Order Created F-AE24CA5913-1-0 DfltHost MORFR04 F-2742-r. Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA5913-1-0 morfr04 REDACTED 0428794459 FFA Order En Route F-AE24CA5913-1-0 morfr04 FFA Order On Site F-AE24CA5913-1-0 morfr04 Std Reason Changed from Unknown by REDACTED 0428794459 Restoration Comments for F-AE24CA5913-1-0 by morfr04: hv wires on the ground along castle Ck Rd. need paddock to dry out to get access with truck, may take a couple days. Asset selection modified Sending Asset Event to FFA Read Above Time On modified from 23:59 22-Apr to 23:59 23-Apr Sending Asset Event to FFA Crew advised repairs will be complete 24/4 Time On modified from 23:59 23-Apr to 16:00 24-Apr Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 16:00 24-Apr to 15:00 24-Apr Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE24CA5913-1-0 morfr04 FFA Order En Route F-AE24CA5913-1-0 morfr04 FFA Order On Site F-AE24CA5913-1-0 morfr04 FFA Order F-AE24CA5913-1-0 Completed by technician REDACTED in crew morfr04(0428794459) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced broken Term xarm Site Label : 4228984 Actual Power Restoration for F-AE24CA5913-1-0: 24-APR-2024 14:30:00 Added notes to Reasons tab. Updated Event Trigger from HV-CCF to HV-Unassisted failure. | 1 | 3064164 | 939 Castle Crk Rd Theodore-at SP261334 | 803689 | 4228984 | 3064164 | 2022-01-29 | 814 | N |  |  | 12.5 | 1 | 1 | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Crop Harvester | SG SPOTTED GUM | 5 kiloNewton | 1991 | -24.8766 | 150.1603 | 000000803689 | 01/JAN/91
EECL | OT234077 | OP | Operational |  | 2024-04-23 | 202404 | Crossarm | Xarm, Wood Intermediate | Split | Rot/Decay |  | 11kV |  |  |  | 1491892 | 2024 | 24SW8055 | 2024-04-23 12:36 | 2024-04-23 12:44 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | KOOROONGARRA, MILLMERRAN, MILLWOOD, MOUNT EMLYN | F-3305-q 11kV Sectionaliser SEC609025, Forced outage due to broken cross-arm at PE05513 Crew replaced cross-arm split at SL 3083284 REDACTED | 11kV Sectionaliser SEC609025, Forced outage due to broken cross-arm at PE05513 Time Off modified from 13:00 23-Apr to 12:36 23-Apr F-3305-q Time On modified from 23:59 23-Apr to 20:32 23-Apr Sending Asset Event to FFA FFA Order Created F-AE24SW8055-1-0 DfltHost FFA Order Acknowledged F-AE24SW8055-1-0 miloc02 \REDACTED 0437851614 FFA Order En Route F-AE24SW8055-1-0 miloc02 FFA Order On Site F-AE24SW8055-1-0 miloc02 FFA Order F-AE24SW8055-1-0 Completed by technician REDACTED in crew miloc02(0437851614) with code A-F-C - Completed Action Taken : replaced cross arm split Site Label : 3083284 Added notes to Reasons tab. | 1 | 2907746 | acc 3869 Stonehenge Rd,Kooroongarra | 1491892 | 3083284 | 2907746 | 2019-10-14 | 1653 | N |  |  | 15.5 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1977 | -28.1157 | 151.2705 | 000001491892 | 01/JAN/77
EECL | OT234118 | OP | Operational |  | 2024-04-23 | 202404 | Crossarm | Xarm, Wood Intermediate | Split | Rot/Decay |  | 12.7kV |  |  |  | 1502919 | 2024 | 24SW8071 | 2024-04-23 19:56 | 2024-04-23 18:24 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | BLAXLAND: GERAGHTYS RD BOWENVILLE: BLAXLAND RD, IRVINGDALE SOUTH RD | 12.7kV SWER Disc Links DL64 - access to remediate lines down | 12.7kV SWER Disc Links DL64 - access to remediate lines down Sending Asset Event to FFA Time Off modified from 19:00 23-Apr to 20:00 23-Apr Time On modified from 20:30 23-Apr to 21:30 23-Apr Sending Asset Event to FFA FFA Order Created F-AE24SW8071-1-0 DfltHost Sending Asset Event to FFA Time Off modified from 20:00 23-Apr to 19:56 23-Apr Sending Asset Event to FFA Time On modified from 21:30 23-Apr to 20:45 23-Apr Sending Asset Event to FFA HV Wires Down Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW8071-1-0 dlbcs04 REDACTED 0499505176 FFA Order En Route F-AE24SW8071-1-0 dlbcs04 FFA Order On Site F-AE24SW8071-1-0 dlbcs04 FFA Order F-AE24SW8071-1-0 Completed by technician REDACTED in crew dlbcs04(0499505176) with code A-F-C - Completed Action Taken : eye bolt pulled through crossarm on underslung sewer pole, repaired arm and reinstated insulators Site Label : 3084246 | 1 | 2911579 | PdkOpp1511BowenvilleBlaxlandRdBowenvlle | 1502919 | 3084246 | 2911579 | 2024-03-12 | 42 | N |  |  | 11 | 1 |  | Serviceable | N | SWER inter | WOOD UNTREATED ROUND | Soil | Paddock Crop | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -27.2524 | 151.4036 | 000001502919 | 01/JAN/57
EECL | OT234358 | OP | Operational |  | 2024-04-26 | 202404 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | LV |  |  |  | 1251364 | 2024 | 24SW8171 | 2024-04-26 16:33 | 2024-04-26 16:36 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | GEHAM: GEHAM STATION RD | 11kV Pole Dist Sub PE01219 - AHC REDACTED advised LV Forced outage reqd to repair broken LV X-arm | 11kV Pole Dist Sub PE01219 - AHC REDACTED advised LV Forced outage reqd to repair broken LV X-arm twmfrsl01 Time Off modified from 17:34 26-Apr to 16:33 26-Apr Time On modified from 23:59 26-Apr to 20:30 26-Apr Sending Asset Event to FFA FFA Order Created F-AE24SW8171-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA LV Wires Down Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW8171-1-0 twmfrsl01 REDACTED 0418712115 FFA Order En Route F-AE24SW8171-1-0 twmfrsl01 FFA Order On Site F-AE24SW8171-1-0 twmfrsl01 Time On modified from 20:30 26-Apr to 18:30 26-Apr Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW8171-1-0 Completed by technician REDACTED in crew twmfrsl01(0418712115) with code A-F-C - Completed Action Taken : replaced lv term arm Site Label : 3101622 Time On modified from 18:30 26-APR to 18:34 26-APR | 1 | 2993894 | 248 Geham Station Rd,Geham | 1251364 | 3101622 | 2993894 | 2019-11-10 | 1629 | N |  |  | 11 |  | 2 | Serviceable | N | Rrl sty term 1 cct | WOOD UNTREATED ROUND | Soil | Road Reserve | ZZ NO DISC - UNKNOWN | 12 kiloNewton |  | -27.4057 | 152.0208 | 000001251364 | 01/JAN/61
EECL | OT234393 | OP | Operational |  | 2024-04-26 | 202404 | Crossarm | Xarm, Wood Termination | Split | Rot/Decay |  | LV |  |  |  | 1516653 | 2024 | 24SW8175 | 2024-04-26 23:06 | 2024-04-26 23:10 | COMP | Completed |  | Fine | South West | Unplanned Outage | Service Asset Fault | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | GT |  | DRAYTON: ANZAC AVE, CANNING ST, COLVIN ST, PARKER ST | 11kV Pole Dist Sub SP791381Crossarm replace | 11kV Pole Dist Sub SP791381 Broken Crossarm TWMOC02 Time On modified from 23:59 26-Apr to 02:30 27-Apr Sending Asset Event to FFA FFA Order Created F-AE24SW8175-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW8175-1-0 twmoc02 FFA Order En Route F-AE24SW8175-1-0 twmoc02 FFA Order En Route F-AE24SW8175-1-0 twmoc02 FFA Order On Site F-AE24SW8175-1-0 twmoc02 FFA Order F-AE24SW8175-1-0 Completed by technician REDACTED in crew twmoc02() with code A-T-315 - Service Asset Fault Action Taken : Replaced crossarm Site Label : 3096196 Time On modified from 02:30 27-APR to 01:33 27-APR . | 1 | 2960528 | 45 Canning St,Drayton | 1516653 | 3096196 | 2960528 | 2019-10-18 | 1652 | N |  |  | 11 |  | 1 | Serviceable | N | Urb unsty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Soil | Footpath | BB BLACKBUTT | 8 kiloNewton | 1982 | -27.5935 | 151.913 | 000001516653 | 01/JAN/82
EECL | OT234593 | OP | Operational |  | 2024-04-29 | 202404 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 1353094 | 2024 | 24WB5316 | 2024-05-01 09:17 | 2024-04-30 14:49 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE |  | BUCCA: BUCCA RD, KLEIDONS RD, SMITHS CROSSING RD | HV cross arm change due to arm is rotten and needs changing S/L 2003441 found by asset inspectors | Switching Sheet ID updated from to J-308229-g. Time On modified from 13:30 01-May to 14:00 01-May Time Off modified from 08:30 01-May to 09:17 01-May Time On modified from 14:00 01-May to 14:26 01-May | 1 | 2034537 | 360 BUCCA RD smiths crossing | 1353094 | 2003441 | 2034537 | 2019-05-15 | 1811 | N |  |  | 14 | 5 | 1 | Serviceable | N | Rrl unsty trm 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 5 kiloNewton | 1982 | -24.8315 | 152.1858 | 000001353094 | 01/JAN/82
EECL | OT234775 | OP | Operational |  | 2024-05-01 | 202405 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1914744 | 2024 | 24NQ8050 | 2024-05-01 06:15 | 2024-05-01 06:17 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | Other Zone Sub Outage | Unknown | due to a SCADA Automated Event | FE |  | HOME HILL, INKERMAN | F-3773-s HOHI - 11kV HH06 Fdr CB F252 tripped. SCADA Interface automated outage. OC Trip. | entered from the SCADA Interface Crew attending REDACTED 0437 720 625 Sending Asset Event to FFA FFA Order Created F-AE24NQ8050-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ8050-1-0 hhlfr01 Ian 0437720625 FFA Order En Route F-AE24NQ8050-1-0 hhlfr01 Broken xarm at pole 2003001 Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA FFA Order On Site F-AE24NQ8050-1-0 hhlfr01 Restoration Comments for F-AE24NQ8050-1-0 by hhlfr01: F-3773-s.broken 11kv timber cross arm.isolation and test and earth.replace.restore power Time On modified from 23:59 01-May to 11:02 01-May Sending Asset Event to FFA FFA Order F-AE24NQ8050-1-0 Completed by technician REDACTED in crew hhlfr01(0437720625) with code A-T-234 - Other Zone Sub Outage Action Taken : F-3773-s.broken 11kv timber cross arm.isolation and test and earth.replace.restore power.conducter remained unbroken above stat. height.F-252 Trip out of home hill sub Site Label : 2003001 auto-completed | 1 | 2027560 | HURNEY RD]1st.Ave.To 6th.Ave.HOME HILL | 1914744 | 2003001 | 2027560 | 2021-09-23 | 951 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn <100m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1982 | -19.6725 | 147.4146 | 000001914744 | 01/JAN/82
EECL | OT234886 | OP | Operational |  | 2024-05-01 | 202405 | Crossarm | Xarm, Wood Termination | Split | Rot/Decay |  | 22kV |  |  |  | 996126 | 2024 | 24CA6366 | 2024-05-01 18:11 | 2024-05-01 19:48 | COMP | Completed |  | Fine | Capricornia | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | FC |  | BLACKALL | F-2765-r Broken Crossarm - Tripped for safety | Broken Crossarm - Tripped for safety bklcdwgl1 Sending Asset Event to FFA FFA Order Created F-AE24CA6366-1-0 DfltHost Asset selection reset Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA6366-1-0 bklcdwgl1 REDACTED 0455518385 FFA Order En Route F-AE24CA6366-1-0 bklcdwgl1 FFA Order On Site F-AE24CA6366-1-0 bklcdwgl1 Time On modified from 23:59 01-May to 22:39 01-May Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24CA6366-1-0 Completed by technician REDACTED in crew bklcdwgl1(0455518385) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replace cross arm Site Label : 4113759 | 1 | 3034946 | Lot 4 Aerodrone Rd Blackall | 996126 | 4113759 | 3034946 | 2020-03-31 | 1492 | N |  |  | 11 | 3 |  | Serviceable | N | Rrl unsty trm 1 cct | WOOD UNTREATED ROUND | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -24.4254 | 145.4346 | 000000996126 | 01/JAN/53
EECL | OT234907 | OP | Operational |  | 2024-05-02 | 202405 | Crossarm | Xarm, Wood Termination | Split | Rot/Decay |  | 11kV |  |  |  | 1856888 | 2024 | 24NQ8098 | 2024-05-02 09:32 | 2024-05-02 07:56 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | BLACK RIVER: HOLSTEIN PL | F-3778-s - REDACTED reported cross arm at S/L2076232 is splitting and requires replacement | REDACTED reported cross arm at S/L2076232 is splitting and requires replacement Please Send to REDACTED twvfr01 Sending Asset Event to FFA FFA Order Created F-AE24NQ8098-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ8098-1-0 twvfr01 REDACTED 0437176349 FFA Order En Route F-AE24NQ8098-1-0 twvfr01 FFA Order On Site F-AE24NQ8098-1-0 twvfr01 Time Off modified from 08:15 02-May to 09:32 02-May Sending Asset Event to FFA Time On modified from 23:59 02-May to 11:43 02-May Sending Asset Event to FFA FFA Order F-AE24NQ8098-1-0 Completed by technician REDACTED in crew twvfr01(0437176349) with code A-F-C - Completed Action Taken : Term arm replaced Site Label : 2076232 | 1 | 2225508 | 9 Holstein Pl Black River- | 1856888 | 2076232 | 2225508 | 2022-06-02 | 700 | N |  |  | 14 | 3 |  | Unserviceable - P2 | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | SG SPOTTED GUM | 12 kiloNewton | 1985 | -19.2115 | 146.6267 | 000001856888 | 01/JAN/85
EECL | OT235007 | OP | Operational |  | 2024-05-03 | 202405 | Crossarm | Xarm, Wood Dressing | Burnt Off | Rot/Decay |  | 11kV |  |  |  | 1752926 | 2024 | 24NQ8145 | 2024-05-03 06:13 | 2024-05-03 06:16 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | HV-Leakage / Pole top fire | Fallen Power Lines | due to fallen power lines. | FE |  | BAMBAROO | F-3783-s BAMBAROO - 11kV BA02 Fdr B252 ACR CB tripped. SCADA Interface automated outage. Cross-arm snapped, pole burnt severely - Crew replaced pole. SL 2110133. REDACTED | entered from the SCADA Interface Bambaroo B252 Fdr CB - EF Trip. Crew to patrol. Manual Reclose Checklist Sending Asset Event to FFA FFA Order Created F-AE24NQ8145-1-0 DfltHost 1st On Call Crew dispatched REDACTED 0407 657 024 Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ8145-1-0 ingcsfr02 REDACTED 0407657024 FFA Order En Route F-AE24NQ8145-1-0 ingcsfr02 Depot Co-ord Advised Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ8145-1-0 ingcsfr01 REDACTED 0428496319 FFA Order En Route F-AE24NQ8145-1-0 ingcsfr01 FFA Order On Site F-AE24NQ8145-1-0 ingcsfr01 Restoration Comments for F-AE24NQ8145-1-0 by INGCSFR01: hechts road number 1 open and DNOB and earthed Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 03-May to 17:00 03-May Sending Asset Event to FFA FFA Order En Route F-AE24NQ8145-1-0 ingcsfr01 FFA Order On Site F-AE24NQ8145-1-0 ingcsfr01 Time On modified from 17:00 03-May to 16:16 03-May Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24NQ8145-1-0 Completed by technician REDACTED in crew INGCSFR01(0428496319) with code A-T-305 - HV-Leakage / Pole top fire Action Taken : cross arm snapped pole burnt severaly replaced pole like for like Site Label : 2110133 Updated Event Trigger from HV-CCF to HV-Leakage / Pole top fire. Added notes to Reasons tab. | 1 | 9396006 | 1st Pole East of Catatis Rd Bambaroo | 1752926 | 2110133 | 9396006 |  | 45415 |  |  |  | 15.5 | [7 empty] | Road Reserve | BI BROAD LEAF IRONBARK | 20 kiloNewton | 2024 | -18.8791 | 146.1751 | 000001752926
EECL | OT235110 | OP | Operational |  | 2024-05-04 | 202405 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | 19kV |  |  |  | 948769 | 2024 | 24NQ8198 | 2024-05-04 08:10 | 2024-05-04 08:25 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | SZ |  | ALPURRURULAM: ATNYER ST DAJARRA: BOULIA RD, CARMODY ST, DILLON ST, LETHAM ST, MATHESON ST DUCHESS: DUKE ST, MAYFIELD STATION MORNINGTON: DUCHESS RD MOUNT ISA: STANBROKE STATION | F-3786-s - Indication of Blown Fuse or Dajarra SWER NO.1 tripping due to Alarms beyond Bridging cross-arm failed causing line to contact stay - Crew replaced cross-arm and associated hardware. SL 5234788. REDACTED | Indication of Blown Fuse or Dajarra SWER NO.1 tripping due to Alarms beyond Sending Asset Event to FFA FFA Order Created F-AE24NQ8198-1-0 DfltHost REDACTED attending. Sending Asset Event to FFA Time Off modified from 08:20 04-May to 08:10 04-May Sending Asset Event to FFA Dajarra Generator started Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ8198-1-0 mtioc01 REDACTED 0419299921 FFA Order En Route F-AE24NQ8198-1-0 mtioc01 FFA Order On Site F-AE24NQ8198-1-0 mtioc01 Crews advise Fuse MIS594312 was still closed but DAJARRA SWER NO.1 had tripped to LO x 4 and have commenced patrol Sending Asset Event to FFA Crews advise a helicopter is required to patrol and is unavailable until 05/05/24 and will contact OCCN when they leave in the morning. Sending Asset Event to FFA Time On modified from 23:59 04-May to 16:00 05-May Sending Asset Event to FFA Crews to patrol in a helicopter 05/05 Sending Asset Event to FFA REDACTED Patrolling line in Helicopter Sending Asset Event to FFA REDACTED advised Broken Cross arm at S/L 5234788 allowing conductors to contact a Stay onsite Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 16:00 05-May to 18:00 05-May Sending Asset Event to FFA Fault repaired and all customers restored at 1644 Time On modified from 18:00 05-May to 16:44 05-May Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ8198-1-0 clccmcs01 REDACTED 0427701876 FFA Order En Route F-AE24NQ8198-1-0 clccmcs01 FFA Order On Site F-AE24NQ8198-1-0 clccmcs01 FFA Order F-AE24NQ8198-1-0 Completed by technician REDACTEDin crew clccmcs01(0427701876) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : bridging cross arm failed causing line to come into contact with stay replaced cross arm and associated hardware Site Label : 5234788 Added notes to Reasons tab. Updated Event Trigger from HV-CCF to HV-Unassisted failure. | 1 | 3415670 | Ashover stn Mt Isa rd Duchess | 948769 | 5234788 | 3415670 | 2023-11-04 | 182 | N |  |  | 12.5 | 1 |  | Serviceable | Y | SWER sty angle | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | GM GYMPIE MESSMATE | 5 kiloNewton | 1984 | -21.3735 | 139.7965 | 000000948769 | 01/JAN/84
EECL | OT235448 | OP | Operational |  | 2024-05-08 | 202405 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1804998 | 2024 | 24NQ8340 | 2024-05-08 13:15 | 2024-05-08 16:58 | CAN | Cancelled |  |  | North Queensland | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 2578 ABERGOWRIE RD ABERGOWRIE QLD 4850 | EQL Wes Bahr advises broken 11kV cross arm on pole 2142251 | CANCELLED - Captured under Forced Outage 24NQ8318. FC 2427257 linked there. . | 1 | 2290721 | 3pELongreach/TocalrdL/reach | 1804998 | 2112251 | 2290721 | 2022-04-05 | 764 | N |  |  | 11 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 2005 | -23.7438 | 143.8327 | 000001804998 | 01/JAN/05
EECL | OT235504 | OP | Operational |  | 2024-05-08 | 202405 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1009913 | 2024 | 24SW8616 | 2024-05-08 21:10 | 2024-05-08 21:12 | COMP | Completed |  | Fine | South West | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | HODGSON VALE, PRESTON, RAMSAY | F-3346-q: KEARNYS SPRG 11kV Preston CB18751 CB tripped. SCADA Interface automated outage. Crew replaced cross-arm that broke due to white rot. SL 3177074. REDACTED | entered from the SCADA Interface twmoc01 Depot Co-ord Advised Sending Asset Event to FFA FFA Order Created F-AE24SW8616-1-0 DfltHost Sending Asset Event to FFA EF Trips; crew to perform initial patrol. Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW8616-1-0 twmoc01 REDACTED 0415309502 FFA Order En Route F-AE24SW8616-1-0 twmoc01 Reason for Event changed from Unknown Sending Asset Event to FFA Crew found line fault indicator past AB18756 has operated, opening AB18756 preforming a MRC and atempting a close on rest of feeder Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA Reclose successful, crew continuing patrol Sending Asset Event to FFA Time On modified from 23:59 08-May to 23:59 09-May Sending Asset Event to FFA Crew found broken cross arm at SL 3177074 HV Wires Down Sending Asset Event to FFA FFA Order On Site F-AE24SW8616-1-0 twmoc01 Time On modified from 23:59 09-May to 02:58 09-May Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW8616-1-0 Completed by technician REDACTED in crew twmoc01(0415309502) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced broken xarm, white Rott Site Label : 3177074 Updated Reasons tab. Reason for Event changed from Transient Fault of Unknown Origin | 1 | 2136711 | 355 savage rd hodgesonvale | 1009913 | 3177074 | 2136711 | 2020-06-09 | 1429 | N |  |  | 14 | 2 | 2 | Serviceable | N | Urb unsty trm>=2cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | GB GREY BOX | 5 kiloNewton | 1989 | -27.6919 | 151.9358 | 000001009913 | 01/JAN/89
EECL | OT235512 | OP | Operational |  | 2024-05-09 | 202405 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | LV |  |  |  | 1724272 | 2024 | 24NQ8345 | 2024-05-09 06:13 | 2024-05-09 06:14 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | LV-Unassisted failure(Apparent defect) | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | GT |  | HOME HILL: GROPER CREEK RD | 11kV Pole Dist Sub BDS289 LV broken crossarm | 11kV Pole Dist Sub BDS289 LV broken crossarm Sending Asset Event to FFA FFA Order Created F-AE24NQ8345-1-0 DfltHost FFA Order Acknowledged F-AE24NQ8345-1-0 hhlfr01 REDACTED 0417198351 FFA Order En Route F-AE24NQ8345-1-0 hhlfr01 FFA Order On Site F-AE24NQ8345-1-0 hhlfr01 Restoration Comments for F-AE24NQ8345-1-0 by hhlfr01: Replacing a broken LV x-arm on BDS289. Isolated and earthed tx to replace arm. Time On modified from 23:59 09-May to 07:48 09-May Sending Asset Event to FFA FFA Order F-AE24NQ8345-1-0 Completed by technician REDACTED in crew hhlfr01(0417198351) with code A-T-311 - LV-Unassisted failure(Apparent defect) Action Taken : Replacing a broken LV x-arm on BDS289. Isolated and earthed tx to replace arm. Site Label : 2012781 Actual Power Restoration for F-AE24NQ8345-1-0: 09-MAY-2024 08:08:00 auto-completed | 1 | 2043226 | opp. rrl.484 GROPER CK RD HOME HILL | 1724272 | 2012781 | 2043226 | 2021-10-25 | 927 | N |  |  | 12.5 | 4 | 1 | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Grass | Sugar Cane | SG SPOTTED GUM | 8 kiloNewton | 1985 | -19.679 | 147.4719 | 000001724272 | 01/JAN/85
EECL | OT235954 | OP | Operational |  | 2024-05-14 | 202405 | Crossarm | Xarm, Wood Strain | Deteriorated | Rot/Decay |  | 11kV |  |  |  | 994256 | 2024 | 24MK4278 | 2024-05-14 11:37 | 2024-05-14 08:45 | COMP | Completed |  |  | Mackay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | ANDROMACHE: GUNYARRA RD | F-3821-s 11kV Disc Links LKS466 - Asset inspector reporting HV conductors are hanging about 100mm above stay cable. Held on by bridging wire. New strain arm required. Asset Insp remaining on site. | 11kV Disc Links LKS466 - Asset inspector reporting HV conductors are hanging about 100mm above stay cable. Held on by bridging wire. New strain arm required. Asset Insp remaining on site. Time Off modified from 12:00 14-May to 09:30 14-May Time Off modified from 09:30 14-May to 11:28 14-May Sending Asset Event to FFA FFA Order Created F-AE24MK4278-1-0 DfltHost . Sending Asset Event to FFA Time Off modified from 11:28 14-May to 11:37 14-May Time On modified from 23:59 14-May to 13:39 14-May Sending Asset Event to FFA FFA Order Acknowledged F-AE24MK4278-1-0 prpcsfr02 REDACTED 0456455770 FFA Order En Route F-AE24MK4278-1-0 prpcsfr02 FFA Order On Site F-AE24MK4278-1-0 prpcsfr02 FFA Order F-AE24MK4278-1-0 Completed by technician REDACTED in crew prpcsfr02(0456455770) with code A-F-C - Completed Action Taken : replaced broken cross arm Site Label : 4042003 auto-completed | 1 | 2642565 | Rrl1620 Gunyarra Rd Andromache | 994256 | 4042003 | 2642565 | 2024-05-16 | -2 | N |  |  | 12.5 | 2 |  | Serviceable | N | HV partly suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1992 | -20.5561 | 148.4859 | 000000994256 | 01/JAN/92
EECL | OT236022 | OP | Operational |  | 2024-05-14 | 202405 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay | Replace | 22kV |  |  |  | 1107800 | 2024 | 24FN6262 | 2024-05-15 08:50 | 2024-05-14 13:58 | COMP | Completed |  |  | Far North | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | COOKTOWN: GAMPE DR, MULLIGAN HWY TREVETHAN CREEK: MT AMOS RD | 22kV Annan River Spur - Pole R.120 (5161327) Mulligan Hwy Cooktown Replace Broken HV Twin Strain Xarms | Switching Sheet ID updated from to J-310369-g. S-11257-s Switching Sheet Written Switch Sheet Distributed Time Off modified from 09:00 15-May to 08:49 15-May Time On modified from 13:00 15-May to 14:00 15-May Time On modified from 14:00 15-May to 13:53 15-May auto-completed | 1 | 3279914 | 7spns S of Gampe Dr on Mulligan Hwy Cook | 1107800 | R119 | 3279914 | 2024-05-22 | -8 | N |  |  | 12.5 | 2 |  | Serviceable | N | Rrl sty angle 5-20o | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | RW RED BLOODWOOD | 5 kiloNewton | 1968 | -15.6393 | 145.2223 | 000001107800 | 01/JAN/68
EECL | OT236076 | OP | Operational |  | 2024-05-15 | 202405 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1015847 | 2024 | 24FN6292 | 2024-05-15 09:21 | 2024-05-15 09:21 | COMP | Completed |  |  | Far North | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | JAPOONVALE: INNISFAIL JAPOON RD, SILKWOOD JAPOON RD | 22kV Pole Dist Sub SS2076Crew REDACTED 0437337 760 reported broken LV crossarm s/l 5138491- Lines still up & in the air. not L/T, crew onsite | 22kV Pole Dist Sub SS2076Crew REDACTED 0437337 760 reported broken LV crossarm s/l 5138491- Lines still up & in the air. not L/T, crew onsite Time Off modified from 15:17 15-May to 09:20 15-May Time On modified from 23:59 15-May to 12:00 15-May Sending Asset Event to FFA FFA Order Created F-AE24FN6292-1-0 DfltHost FFA Order Acknowledged F-AE24FN6292-1-0 inslcm3 REDACTED 0437308303 FFA Order En Route F-AE24FN6292-1-0 inslcm3 FFA Order On Site F-AE24FN6292-1-0 inslcm3 FFA Order F-AE24FN6292-1-0 Completed by technician REDACTEDin crew inslcm3(0437308303) with code A-F-C - Completed Action Taken : Replaced broken LV crossarm. Site Label : 5138485 Time On modified from 12:00 15-MAY to 11:16 15-MAY | 1 | 3225930 | 1399 Innisfail-Japoon Rd Japoonvale | 1015847 | RO1 | 3225930 | 2023-12-05 | 162 | N |  |  | 14 | 1 | 2 | Serviceable | Y | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Lawn | Road Reserve | RI RED IRONBARK | 5 kiloNewton | 1981 | -17.7238 | 145.9309 | 000001015847 | 01/JAN/81
EECL | OT236119 | OP | Operational |  | 2024-05-15 | 202405 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1325613 | 2024 | 24WB5727 | 2024-05-15 16:40 | 2024-05-15 16:26 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | BUNDABERG: KOKODA ST, WOONGARRA ST MILLBANK: BOURBONG ST, BYRNE ST, ISAMBERT LANE, OCONNELL ST, PARKER ST, PENNY ST | Ouate past 11kV Disc Links S2547 required to replace broken X-arm | Ouate past 11kV Disc Links S2547 required to replace broken X-arm Time Off modified from 16:35 15-May to 16:40 15-May Sending Asset Event to FFA FFA Order Created F-AE24WB5727-1-0 DfltHost Time On modified from 18:00 15-May to 17:48 15-May Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB5727-1-0 bndcsfr04 REDACTED 0408180990 FFA Order En Route F-AE24WB5727-1-0 bndcsfr04 FFA Order On Site F-AE24WB5727-1-0 bndcsfr04 FFA Order F-AE24WB5727-1-0 Completed by technician REDACTED in crew bndcsfr04(0408180990) with code A-F-C - Completed Action Taken : replaced broken cross arm Site Label : 3243113 | 1 | 2597970 | TX6917 17 O'Connell St Millbank | 1325613 | 3243113 | 2597970 | 2022-02-19 | 816 | N |  |  | 12.5 | 3 | 2 | Serviceable | Y | Urb inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -24.8741 | 152.3266 | 000001325613 | 01/JAN/92
EECL | OT236254 | OP | Operational |  | 2024-05-17 | 202405 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay | Replace | 11kV |  |  |  | 1017603 | 2024 | 24CA6997 | 2024-05-16 15:20 | 2024-05-16 14:26 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | ROCKHAMPTON CITY, WANDAL | Damaged 11kV x-arms at site 2120610 - cnr of North St & George St. | Damaged x-arms at site 2120610 - cnr of North St & George St. Switching Sheet ID updated from to J-310799-g. Time Off modified from 16:00 16-May to 15:20 16-May Time On modified from 20:00 16-May to 17:36 16-May | 1 | 2293068 | CrnGeorge/ North St R/tonSth | 1017603 | 2120610 | 2293068 | 2020-09-24 | 1331 | N |  |  | 12.5 | 2 | 1 | Unserviceable - P2 | Y | Urb Toff | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | SG SPOTTED GUM | 8 kiloNewton | 1981 | -23.3739 | 150.5004 | 000001017603 | 01/JAN/81
EECL | OT236831 | OP | Operational |  | 2024-05-23 | 202405 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 22kV |  |  |  | 1129930 | 2024 | 24FN6605 | 2024-05-23 11:48 | 2024-05-23 09:06 | COMP | Completed |  |  | Far North | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | BOOGAN: EXPERIMENTAL STATION RD, SOUTH JOHNSTONE RD, WILKIE GRAY RD SOUTH JOHNSTONE: BOOGAN RD, GREEN ST, SOUTH JOHNSTONE RD | Forced outage to repair broken Xarm at SL 5202676. Silwood No.1 FDR. | Forced outage to repair broken Xarm at SL 5202676. Silwood No.1 FDR. Switching Sheet ID updated from to J-311892-g. Asset selection reset Asset selection modified Time Off modified from 10:00 23-May to 11:40 23-May Sending Asset Event to FFA FFA Order Created F-AE24FN6605-1-0 DfltHost Time Off modified from 11:40 23-May to 11:48 23-May Time On modified from 13:00 23-May to 15:00 23-May Sending Asset Event to FFA FFA Order Acknowledged F-AE24FN6605-1-0 inscs02 REDACTED 0437697142 FFA Order En Route F-AE24FN6605-1-0 inscs02 FFA Order On Site F-AE24FN6605-1-0 inscs02 FFA Order F-AE24FN6605-1-0 Completed by technician REDACTED in crew inscs02(0437697142) with code A-F-C - Completed Action Taken : replaced broken HV pin arm under access Site Label : 5202676 Time On modified from 15:00 23-May to 14:08 23-May | 1 | 3303715 | 407 south johnstone rd, boogan | 1129930 | T1.133 | 3303715 | 2022-08-06 | 656 | N |  |  | 15 | 3 | 1 | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | IB IRONBARK | 8 kiloNewton | 1991 | -17.6071 | 146.0041 | 000001129930 | 01/JAN/91
EECL | OT236895 | OP | Operational |  | 2024-05-24 | 202405 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 66kV |  |  |  | 1215128 | 2024 | 24NQ8941 | 2024-05-24 07:38 | 2024-05-24 07:50 | COMP | Completed |  | Fine | North Queensland | Unplanned Outage | HV-Conductor Connection Failure | Protective Device Operated | due to the operating of protective equipment. | ZS |  | BOWEN, CAPE UPSTART, GUMLU, GUTHALUNGRA, WUNJUNGA | HOHI - MERI 66kV Feeder CB C152 tripped @ HOHI end on Timed EF. Distance to fault 92.2km. | HOHI - MERI 66kV Feeder CB C152 tripped @ HOHI end on Timed EF. Distance to fault 92.2km. Time Off modified from 07:47 24-May to 07:38 24-May F-3877-s Depot Co-ord Advised Sending Asset Event to FFA FFA Order Created F-AE24NQ8941-1-0 DfltHost Manual Reclose Checklist Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ8941-1-0 bwnoh01 FFA Order En Route F-AE24NQ8941-1-0 bwnoh01 FFA Order On Site F-AE24NQ8941-1-0 bwnoh01 Crew patrolling fault location Sending Asset Event to FFA Crew advised tree brushing the line at pole 5169145. Will remove and attempt a close.. Sending Asset Event to FFA Attempted close at 0948 SOTF trip, Opened at HH-M. Crew to close HH-ME11 and open at AB810643. Sending Asset Event to FFA Amended - Attempted close at 0948 SOTF trip, Opened at HH-ME11 Sending Asset Event to FFA Attempted close at 1015 SOTF trip. Closed HH-ME11 open at AB810643 Sending Asset Event to FFA Closed in Ca152 at HOHI upto AB810643. Crew to patrol beyond. Asset selection modified Sending Asset Event to FFA Crew advise broken xarm at pole 5169132 Sending Asset Event to FFA Time On modified from 23:59 24-May to 18:18 24-May Sending Asset Event to FFA FFA Order Pending F-AE24NQ8941-1-0 FFA Order Acknowledged F-AE24NQ8941-1-0 bwnoc01 REDACTED 0437768581 FFA Order En Route F-AE24NQ8941-1-0 bwnoc01 FFA Order On Site F-AE24NQ8941-1-0 bwnoc01 FFA Order F-AE24NQ8941-1-0 Completed by technician REDACTED in crew bwnoc01(0437768581) with code A-T-304 - HV-Conductor Connection Failure Action Taken : 66kv x-arm snapped, replaced Site Label : 5169132 | 1 | 3296156 | maria ck to battery ck b hway merinda | 1215128 | 5169132 | 3296156 | 2020-05-02 | 1483 | N |  |  | 14 |  |  | Serviceable | N | 66kV rrl inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | FR FOREST RED GUM | 12 kiloNewton | 1974 | -19.9707 | 148.0525 | 000001215128 | 01/JAN/74
EECL | OT237042 | OP | Operational |  | 2024-05-25 | 202405 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 954196 | 2024 | 24WB6003 | 2024-05-25 18:09 | 2024-05-25 18:12 | COMP | Completed |  | Fine | Wide Bay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Fallen Power Lines | due to fallen power lines. | FC |  | COONAMBULA, MUNDUBBERA, O'BIL BIL, RIVERLEIGH | F-3394-q MUNDUBBERA T 11kV Rverlegh R 580445 ACR CB tripped. SCADA Interface automated outage. End of cross-arm broke off allowing conductor to be grounded - Crew replaced cross-arm. SL 3156081. REDACTED | entered from the SCADA Interface MUNCS01 Depot Co-ord Advised Sending Asset Event to FFA FFA Order Created F-AE24WB6003-1-0 DfltHost FFA Order Acknowledged F-AE24WB6003-1-0 muncs01 REDACTED 0400103169 FFA Order En Route F-AE24WB6003-1-0 muncs01 FFA Order On Site F-AE24WB6003-1-0 muncs01 crew have been fault finding energised upto S1067. Asset selection modified Sending Asset Event to FFA Sending Asset Event to FFA lines down at 3156081 Time On modified from 23:59 25-May to 23:30 25-May HV Wires Down Reason for Event changed from Unknown Sending Asset Event to FFA crew have issue lifting conductors - return tomorrow with bucket truck Time On modified from 23:30 25-May to 10:00 26-May Sending Asset Event to FFA Gayndah Crew to continue with fault this morning REDACTED Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 10:00 26-May to 07:46 26-May Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24WB6003-1-0 Completed by technician REDACTEDin crew muncs01(0400103169) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : The end of the cross arm has broken off. This has allowed the conductor to come to the ground. Crossarm replaced. Site Label : 3156081 Added notes to Reasons tab. Updated Event Trigger from HV-CCF to HV-Unassisted failure. | 1 | 2076103 | 590 RIVERLEIGH STATION RD RIVERLEIGH | 954196 | 3156081 | 2076103 | 2020-01-14 | 1593 | N |  |  | 15.5 | 1 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1991 | -25.565 | 151.1876 | 000000954196 | 01/JAN/91
EECL | OT237165 | OP | Operational |  | 2024-05-27 | 202405 | Crossarm | Xarm Strap(S) | Deteriorated | Corrosion | no worrie | 11kV |  |  |  | 1426424 | 2024 | 24WB6027 | 2024-05-27 13:46 | 2024-05-27 11:32 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FE |  | BOONDOOMA, DARR CREEK, DURONG, DURONG SOUTH | F-2825-r Reports of Xarm brace failure and the x arm is now vertical Crew advise conductor off crossarm at SL3300710 - low wires approx 3m off ground, Require access from 11kV Air Break S3549. Second fault call beyond RC797643 to be recitified in this outage also. HV pin replaced and wire returned to stat. height at SL 3300710. Secondary fault of failure of hardware on cross-arm caused low wires, hardware replaced and wires returned to stat. height. SL 2097651. REDACTED | Reports of Xarm brace failure and the x arm is now vertical Asset selection reset Crew advise conductor off crossarm at SL3300710 - low wires approx 3m off ground, Require access from 11kV Air Break S3549. Second fault call beyond RC797643 to be recitified in this outage also. Asset selection modified Time Off modified from 12:00 27-May to 14:00 27-May HV Wires Down Time Off modified from 14:00 27-May to 13:45 27-May Sending Asset Event to FFA FFA Order Created F-AE24WB6027-1-0 DfltHost mrgcm01 Sending Asset Event to FFA Time On modified from 23:59 27-May to 17:28 27-May Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB6027-1-0 mrgcm01 REDACTED 0428071189 FFA Order En Route F-AE24WB6027-1-0 mrgcm01 FFA Order On Site F-AE24WB6027-1-0 mrgcm01 FFA Order F-AE24WB6027-1-0 Completed by technician REDACTED in crew mrgcm01(0428071189) with code A-F-C - Completed Action Taken : failure of hardware on cross arm caused low wires hardware was replaced and wires returned to stat height Site Label : 2097651 Added notes to Reasons tab. | 1 | 5747353 | Acc 9258 Durong/Mundubbera rd Boondooma | 1426424 | 2097651 | 5747353 | 2022-11-28 | 546 | N |  |  | 12.5 | 1 |  | Serviceable | N | Rrl inter spn <200m | WOOD UNTREATED ROUND | Grass | Paddock Grazing | ZZ NO DISC - UNKNOWN |  |  | -26.2844 | 151.2598 | 000001426424 | 01/JAN/58
EECL | OT237241 | OP | Operational |  | 2024-05-28 | 202405 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1540423 | 2024 | 24SW9432 | 2024-05-28 14:16 | 2024-05-28 10:59 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | BROXBURN: BROXBURN RD, DRONEY RD, LEIFELS RD, WIEMERS RD PITTSWORTH: DRONEY RD, WEIMERS RD SOUTHBROOK: DRONEY RD, WEIMERS RD | Access Required Between 11kV Air Break AB8584, AB608646 and AB16891 To Repair/ replace crossarm | Access Required Between 11kV Air Break AB8584, AB608646 and AB16891 To Repair/ replace crossarm Switching Sheet ID updated from to J-312495-g. Asset selection reset Asset selection modified Time Off modified from 12:00 28-May to 14:16 28-May Time On modified from 18:00 28-May to 19:30 28-May Time On modified from 19:30 28-May to 17:38 28-May | 1 | 2200087 | CB4146 Wiemers/Broxburn Rd,Broxburn | 1540423 | 2060774 | 2200087 | 2023-03-20 | 435 | Y |  |  | 14 | 6 |  | Serviceable | Y | Urb HV inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | BB BLACKBUTT | 12 kiloNewton | 1984 | -27.7186 | 151.6744 | 000001540423 | 01/JAN/84
EECL | OT237388 | OP | Operational |  | 2024-05-29 | 202405 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1749734 | 2024 | 24NQ9179 | 2024-05-29 15:05 | 2024-05-29 12:39 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | CLONCURRY: MILE GDN, PHILLIPS ST, ROXMERE STN RD, SCARR ST, WALTONS FARM HOLDING, WALTONS WELL RVR, WELL RVR | S-11625-s CLON - CC01 Fdr: REDACTED advises of broken 11kV strain arm 1 span away from 11kV Pole Dist Sub CLS25. | REDACTED advises of broken 11kV strain arm 1 span away from 11kV Pole Dist Sub CLS25 Conductors still in the air but broken arm on Pole5097926 Access Roxmere Rd Switching Sheet ID updated from to J-312744-g. Time Off modified from 14:34 29-May to 15:00 29-May Issued to REDACTED clccmcs01 Sending Asset Event to FFA FFA Order Created F-AE24NQ9179-1-0 DfltHost Time Off modified from 15:00 29-May to 15:05 29-May Sending Asset Event to FFA Reverse switching commenced. Time On modified from 23:59 29-May to 18:30 29-May Sending Asset Event to FFA Time On modified from 18:30 29-May to 18:16 29-May Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ9179-1-0 clccmcs01 REDACTED 0427701876 FFA Order En Route F-AE24NQ9179-1-0 clccmcs01 FFA Order On Site F-AE24NQ9179-1-0 clccmcs01 FFA Order F-AE24NQ9179-1-0 Completed by technician REDACTED in crew clccmcs01(0427701876) with code A-F-C - Completed Action Taken : replaced broken cross arms Site Label : 5097926 | 1 | 2969677 | 11 sth rail off Roxmere rd cloncurry | 1749734 | 5097926 | 2969677 | 2021-10-16 | 956 | N |  |  | 12 | 2 | 1 | Serviceable | Y | HV fully suppd |  | Grass | Paddock Grazing | HS HOLLOW/TUBULAR ST |  |  | -20.7313 | 140.4919 | 000001749734 | 01/JAN/92
EECL | OT237723 | OP | Operational |  | 2024-06-03 | 202406 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1361452 | 2024 | 24WB6156 | 2024-06-03 07:13 | 2024-06-03 11:28 | COMP | Completed |  | Cold | Wide Bay | Unplanned Outage | LV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | 14 MCCARTHYS RD;NORTH GREGORY QLD 4660 | Fault occurred at:03/06/2024 07:07; REDACTED, 0421527211;>WDPP --> AffectingTraffic:YES -- StillHavePower:UNSURE<;Incident Details:Cross arm broken/ rotted out at pole 3313316. insulated wire crossing road to pump shed, wire has begun untwisted and insulator from cross beam gone. wires humming. 1/2 down dead-end rd. wires running along roadside as well, from the next pole wires are sagging.;COVID-19:N/A;Warnings[wiresDownSafety]: ADVISED;Sensitive Load:N |  | 1 | 2782605 | past sub994 14mccarthysRdNorthGregory | 1361452 | 3313316 | 2782605 | 2024-06-17 | -14 | N |  |  | 14 | 1 | 1 | Serviceable | Y | Rrl inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | IB IRONBARK | 12 kiloNewton | 1987 | -25.035 | 152.2818 | 000001361452 | 01/JAN/87
EECL | OT237881 | OP | Operational |  | 2024-06-04 | 202406 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 66kV |  |  |  | 1899300 | 2024 | 24CA7684 | 2024-06-04 11:40 | 2024-06-04 11:42 | COMP | Completed |  | Fine | Capricornia | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to a SCADA Automated Event | FE |  | BILOELA: COAL RD | F-3428-q BILOELA 66kV 6010 Call Mn Fdr CB S615 tripped. SCADA Interface automated outage. | entered from the SCADA Interface PROT TRIP BILFR01 Sending Asset Event to FFA FFA Order Created F-AE24CA7684-1-0 DfltHost Sending Asset Event to FFA Crews have found wire down near SL 4139938 cannot get close due to fire Time On modified from 23:59 04-Jun to 18:00 04-Jun Sending Asset Event to FFA Sending Asset Event to FFA HV Wires Down Sending Asset Event to FFA Depot Co-ord Advised Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Onsite crew advised that they replaced broken cross arms and repaired replaced conductors Time On modified from 18:00 04-Jun to 17:11 04-Jun Manual Reclose Checklist Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA7684-1-0 bilfr01 REDACTED 0419410119 FFA Order En Route F-AE24CA7684-1-0 bilfr01 FFA Order On Site F-AE24CA7684-1-0 bilfr01 Restoration Comments for F-AE24CA7684-1-0 by bilfr01: replaced 66 kv xarm FFA Order F-AE24CA7684-1-0 Completed by technician REDACTED in crew bilfr01(0419410119) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : 66 kv long arm broke at arm brace bolt and fell to the ground setting fire to the grass Site Label : 4139930 | 1 | 3192170 | acc 154 Callide Dam Rd Biloela | 1899300 | 4139930 | 3192170 | 2019-11-11 | 1667 | N |  |  | 17 |  |  | Serviceable | Y | 66kV rrl inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 12 kiloNewton | 1974 | -24.3642 | 150.5468 | 000001899300 | 01/JAN/74
EECL | OT238065 | OP | Operational |  | 2024-06-06 | 202406 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay | Replace | 22kV |  |  |  | 986871 | 2024 | 24CA7737 | 2024-06-06 08:11 | 2024-06-06 06:16 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | BARALABA: ALBERTA RD, DENBY RD MOURA: BEARS LAGOON RD, DAWSON HWY, OFF DAWSON HWY | Customer report broken x arm down stream of 22kV Dropout Fuse S7792 | Customer report broken x arm down stream of 22kV Dropout Fuse S7792 Time Off modified from 07:14 06-Jun to 06:40 06-Jun Time On modified from 23:59 06-Jun to 12:00 06-Jun Time Off modified from 06:40 06-Jun to 08:11 06-Jun Asset selection reset Asset selection modified Time On modified from 12:00 06-Jun to 09:47 06-Jun | 1 | 3328000 | X7792 OPP 20492 DAWSON HWY ROUNDSTONE | 986871 | 4256481 | 3328000 | 2021-08-12 | 1029 | N |  |  | 12.5 | 3 |  | Serviceable | N | Rrl inter spn >200m | WOOD (GREEN) SALT IMPREG CCA | Soil | Paddock Grazing | RI RED IRONBARK | 8 kiloNewton | 1990 | -24.6278 | 149.7905 | 000000986871 | 01/JAN/90
EECL | OT238128 | OP | Operational |  | 2024-06-06 | 202406 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 22kV |  |  |  | 898633 | 2024 | 24CA7755 | 2024-06-06 15:17 | 2024-06-06 15:56 | COMP | Completed |  | Fine | Capricornia | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to damage requiring emergency repairs. Fault finding is in progress. | SZ |  | MIRIAM VALE: THORNES RD | Crews report crossarm broken at S/L 4137968 beyond 22kV Dropout Fuse S1410 | Crews report crossarm broken at S/L 4137968 beyond 22kV Dropout Fuse S1410 pcoc07 Sending Asset Event to FFA FFA Order Created F-AE24CA7755-1-0 DfltHost Time On modified from 23:59 06-Jun to 17:46 06-Jun Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA7755-1-0 pcoc07 REDACTED 0437689369 FFA Order En Route F-AE24CA7755-1-0 pcoc07 FFA Order On Site F-AE24CA7755-1-0 pcoc07 FFA Order F-AE24CA7755-1-0 Completed by technician REDACTED in crew pcoc07(0437689369) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced broken hv strain arm Site Label : 4137968 | 1 | 3180680 | 255 thornes rd miriam vale | 898633 | 4137968 | 3180680 | 2023-04-28 | 405 | N |  |  | 12.5 | 5 |  | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 8 kiloNewton | 1979 | -24.3161 | 151.5726 | 000000898633 | 01/JAN/79
EECL | OT238436 | OP | Operational |  | 2024-06-10 | 202406 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1636493 | 2024 | 24SW9927 | 2024-06-10 01:36 | 2024-06-10 01:38 | COMP | Completed |  | Fine | South West | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | due to a SCADA Automated Event | FC |  | KYOOMBA, MOUNT TULLY, STANTHORPE, STORM KING, SUGARLOAF | F-3460-q - STANTHORP TN 11kV Sgarlf Fdr ACR4172 CB tripped. SCADA Interface automated outage. | entered from the SCADA Interface sttoc01 Sending Asset Event to FFA FFA Order Created F-AE24SW9927-1-0 DfltHost crews on route to patrol Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW9927-1-0 sttoc01 REDACTED 0438738255 FFA Order En Route F-AE24SW9927-1-0 sttoc01 FFA Order On Site F-AE24SW9927-1-0 sttoc01 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 10-Jun to 06:50 10-Jun Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW9927-1-0 Completed by technician REDACTED in crew sttoc01(0438738255) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : found broken pin arm. completed switching to change arm Site Label : 3224717 Actual Power Restoration for F-AE24SW9927-1-0: 10-JUN-2024 07:11:00 | 1 | 2485426 | 32 gillbard rd stanthorpe | 1636493 | 3224717 | 2485426 | 2021-10-02 | 982 | N |  |  | 12.5 | 1 | 2 | Serviceable | N | Rrl inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 3 kiloNewton | 1971 | -28.6867 | 152 | 000001636493 | 01/JAN/71
EECL | OT238691 | OP | Operational |  | 2024-06-12 | 202406 | Crossarm | Xarm, Wood Intermediate | Deteriorated | Rot/Decay |  | 66kV |  |  |  | 841728 | 2024 | 24NQ9660 | 2024-06-12 12:00 | 2024-06-12 08:04 | COMP | Completed |  |  | North Queensland | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | N/A | F-3973-s - BLRI-INGH 66kV - Broken Crossarm @ SL 5227571 | Broken Crossarm BLRI-INGH 66kV @ SL 5227571 Time Off modified from 11:00 12-Jun to 12:00 12-Jun Time On modified from 15:00 12-Jun to 16:00 12-Jun Sending Asset Event to FFA FFA Order Created F-AE24NQ9660-1-0 DfltHost FFA Order Acknowledged F-AE24NQ9660-1-0 twvcdwgl3 REDACTED 0418985424 FFA Order En Route F-AE24NQ9660-1-0 twvcdwgl3 FFA Order On Site F-AE24NQ9660-1-0 twvcdwgl3 Time On modified from 16:00 12-Jun to 17:30 12-Jun Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24NQ9660-1-0 Completed by technician REDACTED in crew twvcdwgl3(0418985424) with code A-F-C - Completed Action Taken : replaced broken 66kv wishbone cross arm Site Label : 5227571 | 1 | 3390789 | 1spn nth Surveyor Ck Bruce Hwy | 841728 | 5227571 | 3390789 | 2021-05-16 | 1123 | N |  |  | 17 |  |  | Serviceable | N | 66kV rrl inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1978 | -19.0695 | 146.416 | 000000841728 | 01/JAN/78
EECL | OT238719 | OP | Operational |  | 2024-06-12 | 202406 | Crossarm | Xarm, Wood Termination | Deteriorated | Rot/Decay |  | LV |  |  |  | 8643026 | 2024 | 24CA8001 | 2024-06-12 12:14 | 2024-06-12 10:51 | COMP | Completed |  | Fine | Capricornia | Unplanned Outage | Animal Other | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | GT |  | BILOELA: DAKENBA RD | 11kV Pole Dist Sub 218297 LV Only | 11kV Pole Dist Sub 218297 LV Only Sending Asset Event to FFA FFA Order Created F-AE24CA8001-1-0 DfltHost Time Off modified from 10:47 12-Jun to 12:13 12-Jun Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 12-Jun to 13:39 12-Jun Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA8001-1-0 bilcm02 REDACTED 0417370313 FFA Order En Route F-AE24CA8001-1-0 bilcm02 FFA Order On Site F-AE24CA8001-1-0 bilcm02 FFA Order F-AE24CA8001-1-0 Completed by technician REDACTED in crew bilcm02() with code A-T-302 - Animal Other Action Taken : replaced arm Site Label : 4098971 Actual Power Restoration for F-AE24CA8001-1-0: 12-JUN-2024 13:36:00 auto-completed | 1 | 8643027 | W opp 246 Tognolini Baldwin Rd Biloela | 8643026 | 4098971 | 8643027 | 2020-01-31 | 1594 | N |  |  | 11 |  |  | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | ZZ NO DISC - UNKNOWN | 8 kiloNewton |  | -24.38 | 150.5035 | 000008643026 | 01/JAN/74
EECL | OT238750 | OP | Operational |  | 2024-06-12 | 202406 | Crossarm | Xarm, Wood Strain | Broken | Rot/Decay |  | 11kV |  |  |  | 1449245 | 2024 | 24MK5044 | 2024-06-12 14:33 | 2024-06-12 18:53 | CAN | Cancelled |  | Fine | Mackay | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | 64 BURGESS LANE;ETON QLD 4741 | 3rd Party->Fault occurred at:12/06/2024 14:00; REDACTED, 0405903122;>UPH --> Details:Broken Cross-arm-WiresExposed:NO,TripHazard:NO -- Broken Cross-arm-Touchable:NO<;Incident Details:Broken crossarm on pole 4106515. Area clear.;COVID-19:NO;Warnings[uphSafety]: ADVISED;Dog restraint:YARD;Sensitive Load:N | outage cancelled via Clash Wizard | 1 | 5474696 | behind shed, 64 burgess lane eton | 1449245 | 4106515 | 5474696 | 2024-03-19 | 85 | N |  |  | 12.5 | 2 |  | Serviceable | N | HV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Lawn | Sugar Cane | SG SPOTTED GUM | 5 kiloNewton | 1982 | -21.2699 | 148.95 | 000001449245 | 01/JAN/82
EECL | OT238761 | OP | Operational |  | 2024-06-12 | 202406 | Crossarm | Xarm, Wood Termination | Split | Rot/Decay |  | LV |  |  |  | 1019068 | 2024 | 24WB6463 | 2024-06-12 15:45 | 2024-06-12 19:09 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Public Safety Isolation - NOT Directed by Emerg Serv Authorised Agent | Single Fault Call | GT |  | 153 WIDE BAY HWY BELLS BRIDGE QLD 4570 | Asset Inspector REDACTED 0429 272 958, Reports LV Term X-arm has shackle has let go and is holdind by bridge, conductor about chest height mid span, SL 4203857. Remaining onsite P1 Call Flag |  | 1 | 5454592 | 153 Wide Bay Hway Bells Bridge | 1019068 | 4203857 | 5454592 | 2024-06-07 | 5 | N |  |  | 12.5 | 3 | 1 | Serviceable | Y | Rrl sty sub pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Backyard | RI RED IRONBARK | 8 kiloNewton | 1984 | -26.1232 | 152.5591 | 000001019068 | 01/JAN/84
EECL | OT238979 | OP | Operational |  | 2024-06-14 | 202406 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1510644 | 2024 | 24SW10186 | 2024-06-14 14:40 | 2024-06-14 13:50 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | FC |  | JONDARYAN: WEST PRAIRIE RD | F-3485-q 11kV Pole Dist Sub PE04428 - Report of Broken Cross-arm on TX pole. | 11kV Pole Dist Sub PE04428 - Report of Broken Cross-arm on TX pole. Sending Asset Event to FFA FFA Order Created F-AE24SW10186-1-0 DfltHost Asset selection reset Asset selection reset Asset selection modified Sending Asset Event to FFA Sending Asset Event to FFA Time Off modified from 14:30 14-Jun to 14:40 14-Jun Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW10186-1-0 twmfrcm01 REDACTED 0456859181 FFA Order Acknowledged F-AE24SW10186-1-0 twmoc02 REDACTED 0428301490 FFA Order En Route F-AE24SW10186-1-0 twmoc02 Time On modified from 23:59 14-Jun to 19:00 14-Jun Sending Asset Event to FFA FFA Order On Site F-AE24SW10186-1-0 twmoc02 Sending Asset Event to FFA FFA Order F-AE24SW10186-1-0 Completed by technician REDACTED in crew twmoc02(0428301490) with code A-F-C - Completed Action Taken : replaced broken arms Site Label : 3134216 Time On modified from 19:00 14-Jun to 20:30 14-Jun Asset selection modified Time On modified from 20:30 14-Jun to 21:30 14-Jun Time On modified from 21:30 14-Jun to 20:57 14-Jun | 1 | 3157848 | pe4428/1413 WEST PRAIRIE RD Jondaryan | 1510644 | 3134216 | 3157848 | 2020-03-11 | 1556 | N |  |  | 14 | 4 | 2 | Serviceable | Y | Rrl inter sub pole | WOOD (GREEN) SALT IMPREG CCA | Soil | Road Reserve | SG SPOTTED GUM | 5 kiloNewton | 1971 | -27.4424 | 151.4655 | 000001510644 | 01/JAN/71
EECL | OT239196 | OP | Operational |  | 2024-06-17 | 202406 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | 11kV |  |  |  | 1320095 | 2024 | 24WB6586 | 2024-06-17 12:17 | 2024-06-17 14:24 | COMP | Completed |  | Fine | Wide Bay | Unplanned Outage | HV-Conductor Connection Failure | Unknown | Single Fault Call | GT |  | 8 TRURO ST TORQUAY QLD 4655 | REDACTED reported Broken King Pin on HV pole 3154165 P1 Call Flag |  | 1 | 2061031 | 18 WILLIAM ST URANGAN | 1320095 | 3154165 | 2061031 | 2024-06-25 | -8 | N |  |  | 12.5 | 1 | 1 | Serviceable | N | Urb inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 3 kiloNewton | 1972 | -25.2851 | 152.8931 | 000001320095 | 01/JAN/72
EECL | OT239211 | OP | Operational |  | 2024-06-17 | 202406 | Crossarm | Xarm Kingbolt | Broken | Corrosion | Replace | 11kV |  |  |  | 1320095 | 2024 | 24WB6585 | 2024-06-17 12:52 | 2024-06-17 12:54 | COMP | Completed |  |  | Wide Bay | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | URANGAN: CHURCHILL ST, CUNNINGHAM ST, GIBBS ST, HOOP WAY, RICHARD ST, SHELL ST, SOUTH ST, TRURO ST, WILLIAM ST | 11kV Disc Links S3342 cross arm broken past | 11kV Disc Links S3342 cross arm broken past Time On modified from 23:59 17-Jun to 14:07 17-Jun Time Off modified from 12:52 17-Jun to 12:52 17-Jun | 1 | 2061031 | 18 WILLIAM ST URANGAN | 1320095 | 3154165 | 2061031 | 2024-06-25 | -8 | N |  |  | 12.5 | 1 | 1 | Serviceable | N | Urb inter 2 cct | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | SG SPOTTED GUM | 3 kiloNewton | 1972 | -25.2851 | 152.8931 | 000001320095 | 01/JAN/72
EECL | OT239897 | OP | Operational |  | 2024-06-24 | 202406 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | LV |  |  |  | 1659030 | 2024 | 24CA8451 | 2024-06-24 08:26 | 2024-06-24 11:41 | COMP | Completed |  | Fine | Capricornia | Unplanned Outage | HV-Unassisted failure(Apparent defect) | Unknown | Single Fault Call | GT |  | 2 RAILWAY ST BLACKWATER QLD 4717 | Crew advised broken LV xarm at SL# 4094714 P1 Call Flag |  | 1 | 2927340 | Behind 41 Wey St Blackwater | 1659030 | 4094714 | 2927340 | 2024-02-13 | 132 | N |  |  | 11 |  | 1 | Serviceable | N | Urb LV inter | WOOD (GREEN) SALT IMPREG CCA | Grass | Road Reserve | SG SPOTTED GUM | 8 kiloNewton | 1965 | -23.5851 | 148.8782 | 000001659030 | 01/JAN/65
EECL | OT240118 | OP | Operational |  | 2024-06-26 | 202406 | Crossarm | Xarm, Wood Intermediate | Broken | Rot/Decay |  | LV |  |  |  | 1008190 | 2024 | 24FN7800 | 2024-06-26 08:11 | 2024-06-26 08:12 | COMP | Completed |  |  | Far North | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | BUNGALOW: HARTLEY ST PORTSMITH: BUCHAN ST, HARTLEY ST | Pole Dist Sub SP812186 - REDACTED 0427 803 739 reported broken LV crossarm. Outage required to carry out emergency repairs. No access to sub needed, LV isolation only. | Pole Dist Sub SP812186 - REDACTED 0427 803 739 reported broken LV crossarm. Outage required to carry out emergency repairs. No access to sub needed, LV isolation only. Time Off modified from 10:06 26-Jun to 08:10 26-Jun Time On modified from 23:59 26-Jun to 10:30 26-Jun Sending Asset Event to FFA FFA Order Created F-AE24FN7800-1-0 DfltHost FFA Order Acknowledged F-AE24FN7800-1-0 cnscm05 REDACTED 0458585658 FFA Order En Route F-AE24FN7800-1-0 cnscm05 FFA Order On Site F-AE24FN7800-1-0 cnscm05 FFA Order F-AE24FN7800-1-0 Completed by technician REDACTED in crew cnscm05(0458585658) with code A-F-C - Completed Action Taken : emergency shut. broken LV pin arm. replaced cross arm. no more work required. isolated overhead at 08:20am, power restored at 09:05am Site Label : 5017537 Time On modified from 10:30 26-JUN to 09:04 26-JUN | 1 | 2535701 | cnr buchan/hartley sts bungalow cairns | 1008190 | HA27A | 2535701 | 2024-02-16 | 131 | N |  |  | 12.5 |  | 1 | Serviceable | N | Urb LV inter | WOOD (GREEN) SALT IMPREG CCA | Lawn | Footpath | BI BROAD LEAF IRONBARK | 5 kiloNewton | 1999 | -16.936 | 145.7662 | 000001008190 | 01/JAN/99
EECL | OT240243 | OP | Operational |  | 2024-06-27 | 202406 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 947093 | 2024 | 24CA8603 | 2024-06-27 12:24 | 2024-06-27 10:49 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | CLAIRVIEW: COLONIAL DR, FLINDERS LANE | REDACTED requested Forced Outage of 22kV Pole Dist Sub 100057 to repair broken LV X-Arm Termination. Sent to ROKFR05 | REDACTED requested Forced Outage of 22kV Pole Dist Sub 100057 to repair broken LV X-Arm Termination. Sent to ROKFR05 Time Off modified from 11:00 27-Jun to 11:00 27-Jun Sending Asset Event to FFA FFA Order Created F-AE24CA8603-1-0 DfltHost Sending Asset Event to FFA Time Off modified from 11:00 27-Jun to 12:24 27-Jun Sending Asset Event to FFA Time On modified from 23:59 27-Jun to 14:15 27-Jun Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA8603-1-0 rokfr05 REDACTED 0438306174 FFA Order En Route F-AE24CA8603-1-0 rokfr05 FFA Order On Site F-AE24CA8603-1-0 rokfr05 FFA Order F-AE24CA8603-1-0 Completed by technician REDACTED in crew rokfr05(0438306174) with code A-F-C - Completed Action Taken : completed crossarm change Site Label : 4158801 Time On modified from 14:15 27-JUN to 14:37 27-JUN | 1 | 3254733 | caravan prk colonial drive clairview | 947093 | 4158801 | 3254733 | 2021-12-22 | 918 | N |  |  | 12.5 | 2 | 1 | Serviceable | N | Rrl inter spn <200m | WOOD (GREEN) SALT IMPREG CCA | Grass | Footpath | SG SPOTTED GUM | 8 kiloNewton | 1976 | -22.1215 | 149.5354 | 000000947093 | 01/JAN/76
EECL | OT240270 | OP | Operational |  | 2024-06-27 | 202406 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | LV |  |  |  | 1380310 | 2024 | 24CA8595 | 2024-06-27 09:34 | 2024-06-27 09:34 | COMP | Completed |  |  | Capricornia | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | GT |  | YEPPOON: ADELAIDE ST, BARTLEM ST, CLIFF ST, FREEMAN ST, HILL ST, NORMANBY ST, RAYMOND TCE | REDACTED requested LV Outage due to Low Conductors 11kV Pole Dist Sub 111341 Crew replaced LV termination cross-arm that broke due to rot. SL 2107466. REDACTED | REDACTED requested LV Outage due to Low Conductors 11kV Pole Dist Sub 111341 yepcm09 Time Off modified from 10:00 27-Jun to 09:34 27-Jun Sending Asset Event to FFA FFA Order Created F-AE24CA8595-1-0 DfltHost FFA Order Acknowledged F-AE24CA8595-1-0 yepcm09 REDACTED 0428835839 FFA Order En Route F-AE24CA8595-1-0 yepcm09 FFA Order On Site F-AE24CA8595-1-0 yepcm09 Time On modified from 23:59 27-JUN to 11:30 27-AUG by REDACTED 0428835839 Restoration Comments for F-AE24CA8595-1-0 by yepcm09: Lv crossarm broken - LV wires low over roadway - isolated Sub 111341 FFA Order F-AE24CA8595-1-0 Completed by technician REDACTED in crew yepcm09(0428835839) with code A-F-C - Completed Action Taken : replaced broken LV termination crossarm - fungal/rot. Site Label : 2107466 Time On modified from 11:30 27-AUG to 11:48 27-JUN Added notes to Reasons tab. | 1 | 2274626 | cnr BARTLEM & CLIFF ST YEPPOON | 1380310 | No Description Provided | 2274626 | 2021-08-19 | 1043 | N |  |  | 11 |  | 2 | Serviceable | N | LV fully suppd | WOOD (GREEN) SALT IMPREG CCA | Garden Bed | Front Yard | FR FOREST RED GUM | 8 kiloNewton | 1969 | -23.1266 | 150.7483 | 000001380310 | 01/JAN/69
EECL | OT240487 | OP | Operational |  | 2024-06-29 | 202406 | Crossarm | Xarm, Wood Strain | Split | Termites |  | 33kV |  |  |  | 1913929 | 2024 | 24SW10800 | 2024-06-29 20:37 | 2024-06-29 20:01 | COMP | Completed |  |  | South West | Forced Outage |  | Lines Emergency Maintenance | to allow emergency maintenance of the electricity network. | SZ |  | N/A | Forced Outage required to make repairs downstream of 33kV Disc Links DL1498. HV Conductor hanging by bridge. | Forced Outage required to make repairs downstream of 33kV Disc Links DL1498. HV Conductor hanging by bridge. Switching Sheet ID updated from to J-317536-g. STGCMFR04 Time Off modified from 20:30 29-Jun to 20:37 29-Jun Onsite crew advised that isolations and earth will happen now but works will be conducted tomorrow Crew identified that there isn't a HV identifier for the links DL1798 crew to install a HV Identifier tomorrow when they return to site Sending Asset Event to FFA FFA Order Created F-AE24SW10800-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW10800-1-0 stgcmfr04 REDACTED 0438503552 Crew to return tomorow to carry out the maintenance Sending Asset Event to FFA FFA Order En Route F-AE24SW10800-1-0 stgcmfr04 FFA Order On Site F-AE24SW10800-1-0 stgcmfr04 Time On modified from 16:00 30-Jun to 17:00 30-Jun Sending Asset Event to FFA Time On modified from 17:00 30-Jun to 17:00 01-Jul Sending Asset Event to FFA Time On modified from 17:00 01-Jul to 17:00 02-Jul Sending Asset Event to FFA Time On modified from 17:00 02-Jul to 15:42 02-Jul Sending Asset Event to FFA Sending Asset Event to FFA | 1 | 3219014 | DL958 Carnarvon Hwy Thallon | 1913929 | 4251420 | 3219014 | 2022-12-13 | 564 | N |  |  | 12.5 | 3 |  | Serviceable | Y | Rrl sty term 1 cct | WOOD (GREEN) SALT IMPREG CCA | Grass | Paddock Grazing | SG SPOTTED GUM | 3 kiloNewton | 1972 | -28.4465 | 148.8317 | 000001913929 | 01/JAN/72
EECL | OT240502 | OP | Operational |  | 2024-06-30 | 202406 | Crossarm | Xarm, Wood Termination | Broken | Rot/Decay |  | 11kV |  |  |  | 1722020 | 2024 | 24NQ10368 | 2024-06-30 07:47 | 2024-06-30 07:52 | CAN | Cancelled |  |  | North Queensland | Unplanned Outage |  | Equipment Failure or Malfunction | due to damage requiring emergency repairs. | GT |  | AYR: CLARE RD | Report of broken x-arm with low hanging wires beyond 11kV Pole Dist Sub BDS510 | Report of broken x-arm with low hanging wires beyond 11kV Pole Dist Sub BDS510 Sending Asset Event to FFA FFA Order Created F-AE24NQ10368-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ10368-1-0 hhlfr01 REDACTED 0427650719 Removing Asset Event from FFA FFA Order cancelled.F-AE24NQ10368-1-0 Cancelling outage as forced outage created for larger area. 24NQ10372 | 1 | 2207440 | Toff At 1153 AyrDalbegRd MonaPark Ayr | 1722020 | 2069511 | 2207440 | 2022-11-10 | 598 | N |  |  | 14 | 3 | 1 | Serviceable | Y | Rrl sty sub pole | WOOD (GREEN) SALT IMPREG CCA | Lawn | Sugar Cane | SG SPOTTED GUM | 12 kiloNewton | 1987 | -19.7018 | 147.3121 | 000001722020 | 01/JAN/87