## Numbers
Row Labels | Count of CB2 | Count of ACR2 | Count of RMU2 | Count of Switches
11 | 28 | 4 | 5 | 5
22 | 8 | 4 | 2
33 | 8 | 2
66 | 13 |  |  | 2
132 | 2
220 | 0
Grand Total | 59 | 10 | 7 | 7 |  | 83
0
RIN Data
< = 11 kV ; FUSE
[5 empty] | < = 11 kV ; Switch | 10
[5 empty] | < = 11 kV ; Circuit Breaker | 32
[5 empty] | > 11 kV & < = 22 kV ; Switch | 2
[5 empty] | > 11 kV & < = 22 kV ; Circuit Breaker | 12
[5 empty] | > 22 kV & < = 33 kV ; Switch | 0
[5 empty] | > 22 kV & < = 33 kV ; Circuit Breaker | 10
[5 empty] | > 33 kV & < = 66 kV ; Switch | 2
[5 empty] | > 33 kV & < = 66 kV ; Circuit Breaker | 13
[5 empty] | > 66 kV & < = 132 kV ; Switch | 0
[5 empty] | > 66 kV & < = 132 kV ; Circuit Breaker | 2
[5 empty] | > 132 kV ; Switch | 0
[5 empty] | > 132 kV ; Circuit Breaker | 0

## CB Failures
Column1 | REQUEST_ID | RAISED_DATE | FY | WORK_ORDER | WO_DESC | WO_JOB_CODEX1_1 | ORIG_PRIORITY | ORIG_PRIORITY_DESCRIPTION | WO_STATUS_M | WO_STATUS_M_DESCRIPTION | WO_STATUS_U | WO_STATUS_U_DESCRIPTION | CLOSED_DT | CLOSED_COMMIT_DT | CLOSED_TIME | COMPLETED_CODE | COMPLETED_CODE_DESCRIPTION | CLOSED_STATUS | CLOSED_STATUS_DESCRIPTION | SHUTDOWN_EQUIP | SHUTDOWN_TYPE | SHUTDOWN_TYPE_DESCRIPTION | PARENT_WO | PARENT_WO_DESC | MAINT_TYPE | MAINT_TYPE_DESCRIPTION | MSSS_OBJECT_FAILURE_DESCRIPTION | MSSS_DAMAGE_APPARENT_CAUSE_DESCRIPTION | MSSS_CAUSE_DESCRIPTION | CONSEQUENCE_DESCRIPTION | VOLTAGE_DESCRIPTION | PLAN_PRIORITY | PLAN_PRIORITY_DESCRIPTION | CUST_NO | FAILURE_PART | EQUIP_NO | COMP_CODE | COMP_CODE_DESCRIPTION | COMP_MOD_CODE | COMP_MOD_CODE_DESCRIPTION | REQUEST_ID_2 | SHORT_DESC_1 | SHORT_DESC_2 | LOCATION | ITEM_NAME_1 | ITEM_NAME_2 | EQUIP_STATUS | EQUIP_LOCATION | PLANT_NO | EQUIP_CLASS | EQUIP_CLASS_DESCRIPTION | WORK_ORDER_EXTENDED_DESCRIPTION | REQUEST_ID_3 | WORK_REQUEST_EXTENDED_DESCRIPTION | NAMP_LINE | NAMP_LINE_DESCRIPTION | Voltage | OT | CB | CB FAULT | ACR | Rec Fault | RMU | RMUFault | Switch | Switch Fault | Isol | Isol Fault | CB2 | ACR2 | RMU2 | Switches | Switches Comment2 | RMU Comm2
6310 | 000001934346 | 2024-06-23 | 2024 | OT239846 | MERI CB FB04Q00 Did Not Operate | 1 | 0 | P0 - Forced | A | Authorised | VG | (1) Investigate |  |  | 0.99931 | [9 empty] | MF | Maintenance Forced | [5 empty] | 0 | P0 - Forced |  |  | 200154 |  |  |  |  | 000001934346 | NURGT System Condition - 24NQ10108 |  |  | FB04Q00 11KV MERI-04 FDR CB | MERISS MERI-04 FEEDER CB SLOT | IS | XLHBB | MERISS-FB04-Q00 | ST | Slot - GIS |  | 000001934346 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
39633 | 000001910347 | 2024-02-23 | 2024 | OT226703 | CALL TX CP-T2 11kV CB CP-S102 | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-24 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Incorrect operation/activity | Technical Assessment | 11kV | 0 | P0 - Forced |  |  | 282801 |  |  |  |  | 000001910347 | URGNT System Condition - 24CA3681 |  |  | CP-T2 66/11KV TRANSF 2 | CALLSS TRANSF 2 SLOT | IS | XLFPG | CALLSS-TX02-T01 | ST | Slot - GIS |  | 000001910347 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
49985 | 000001926968 | 2024-05-17 | 2024 | OT236264 | WEMA FB09Q00 CB Fail on OC trip | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-21 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> | <null> | 11kV | 0 | P0 - Forced |  |  | 224816 |  |  |  |  | 000001926968 | URGNT System Condition - 24MK4393 |  |  | FB09Q00 11KV ROCKLEIGH FDR CB | WEMASS ROCKLEIGH FEEDER CB SLOT | IS | XLFPK | WEMASS-FB09-Q00 | ST | Slot - GIS |  | 000001926968 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
46387 | 000001921084 | 2024-04-15 | 2024 | OT233185 | PIRR CB3710 pitch leaking in spouts | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-10 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Leaking | Leakage |  | 11kV | 0 | P0 - Forced |  |  | 187161 |  |  |  |  | 000001921084 | NURGT System Condition - 24SW7634 |  |  | CB3710 11KV PIRRINUAN FDR CB | PIRRSS PIRRINUAN FEEDER CB SLOT | IS | XLGDD | PIRRSS-FB04-Q00 | ST | Slot - GIS |  | 000001921084 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
39458 | 000001910233 | 2024-02-22 | 2024 | OT226651 | CALL T1 11kV CB CP-S106 Arc sounds cubi | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-09 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Inadequate coating | Repair | 11kV | 0 | P0 - Forced |  |  | 282781 |  |  |  |  | 000001910233 | URGNT System Condition - 24CA3656 |  |  | CP-T1 66/11KV TRANSF 1 | CALLSS TRANSF 1 SLOT | IS | XLFPG | CALLSS-TX01-T01 | ST | Slot - GIS |  | 000001910233 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
12429 | 000001912313 | 2024-03-03 | 2024 | OT227865 | STUA_Unable to Close via Scada or locall | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-03-06 |  | 11:59:00 pm | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> | <null> | 11kV | 0 | P0 - Forced |  |  | 000000164465 |  |  |  |  | 000001912313 | URGNT System Condition - 24NQ5650 |  |  | J252 11KV CLUDEN ST FDR CB | STUASS CLUDEN ST FEEDER CB SLOT | IS | XLHBT | STUASS-FB15-Q00 | ST | Slot - GIS |  | 000001912313 |  |  |  | 11 | 1 | 4 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 4
9084 | 000001906977 | 2024-02-08 | 2024 | OT224726 | EAAY_Cap2 CB V252 won't close. left OOS | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2024-02-16 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Circuit Breaker | Deteriorated | Intermittent Fault |  | 11kV | 0 | P0 - Forced |  |  | 164 |  |  |  |  | 1906977 | NURGT System Condition - 24NQ4424 |  |  | EAST AYR SPILLER ST 66/11KV SUB (EAAY) | EAAYSS 66/11KV ZONE SUB | IS | XLHBH | EAAYSS | SS | Substation Site |  | 000001906977 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
6284 | 000001902420 | 2024-01-27 | 2024 | OT221297 | Switchgear RTS Friendlys CB | 1 |  |  | C | Closed |  |  | 2024-02-12 |  | 0.97917 | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Damaged | Unknown |  | 11kV | 0 | P0 - Forced |  |  | 6553235 | SW | Switch | OC | Outage Codes | 1902420 | BUNDABERG FRIENDLY SOCIETY MED | P - Phase Down (LV) |  | 86052 | 23 BINGERA ST, BUNDABERG WEST QLD 4670 | IS | XLFBB | NS86052 | NS | Network Site |  | 000001902420 |  |  |  | 11 | 1 | 4 | 4 | 0 |  | 4 | 4 | 0 |  | 0 |  | 4 |  | 4 |  |  | 0
6372 | 000001902803 | 2024-01-28 | 2024 | OT221651 | FD-1206_CB J252 possibly miss latching | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-01-31 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 36766 |  |  |  |  | 1902803 | URGNT System Condition - 24NQ3322 |  |  | CLUDEN | STOA ST10 | IS | XLHBT | FD-1206 | FD | Feeder |  | 000001902803 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
5508 | 000001902396 | 2024-01-26 | 2024 | OT221268 | EAAY_No.10 Fdr CB J252 Spring Charge Alm | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-01-31 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 7089303 |  |  |  |  | 1902396 | URGNT System Condition - 24NQ3153 |  |  | EASTAYR NO.10 | EAAY 14019 | IS | XLHBH | FD-4019 | FD | Feeder |  | 000001902396 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
3107 | 000001899145 | 2024-01-17 | 2024 | OT218707 | GLFS GF-S105 spring charg mot bear fail | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-01-30 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Fatigue | Repair | 11kV | 0 | P0 - Forced |  |  | 290420 |  |  |  |  | 1899145 | URGNT System Condition - 24CA0967 |  |  | GF-S105 11KV WEST GLADSTONE FDR CB | GLFSSS WEST GLADSTONE FDR CB SLOT | IS | XLFPG | GLFSSS-FB59-Q00 | ST | Slot - GIS |  | 000001899145 |  |  |  | 11 | 1 | 4 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
1725 | 000001896911 | 2024-01-08 | 2024 | OT217151 | TORQ CB D452 failed to to close from OCC | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2024-01-08 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Circuit Breaker | Loose Connection | Loose Connection | Repair | 11kV | 0 | P0 - Forced |  |  | 164709 |  |  |  |  | 1896911 | URGNT System Condition - 24WB0317 |  |  | D452 11KV SCARNESS HEIGHTS FDR CB | TORQSS SCARNESS HEIGHTS FEEDER CB SLOT | IS | XLFBH | TORQSS-FB04-Q00 | ST | Slot - GIS |  | 000001896911 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
11519 | 000001892430 | 2023-12-26 | 2024 | OT213166 | PURR CB 4489 - unable to close | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-12-27 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Wiring and Electrical Componen | Out of Specification | Corrosion |  | 11kV | 0 | P0 - Forced |  |  | 190467 |  |  |  |  | 000001892430 | URGNT System Condition - 23SW23452 |  |  | CB4489 11KV ROSSVALE FDR CB | PURRSS ROSSVALE FEEDER CB SLOT | IS | XLGDT | PURRSS-FB55-Q00 | ST | Slot - GIS |  | 000001892430 |  |  |  | 11 | 1 | 5 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 4
11163 | 000001891774 | 2023-12-25 | 2024 | OT212507 | SCR0 SOKO CB C452 exploded-fault finding | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-12-27 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 163173 |  |  |  |  | 000001891774 | SCR0 RTS R0 - High Priority 23WB16325 |  |  | C452 11KV SHARON FDR CB | SOKOSS SHARON FEEDER CB SLOT | IS | XLFBB | SOKOSS-FB52-Q00 | ST | Slot - GIS |  | 000001891774 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
4932 | 000001883497 | 2023-11-29 | 2024 | OT205944 | ALST Cap1 CB Continously tying to close | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-12-12 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Circuit Breaker | Repairable Degradation | Fatigue |  | 11kV | 0 | P0 - Forced |  |  | 5290144 |  |  |  |  | 000001883497 | SCR0 RTS R0 - 23MK9446 |  |  | FB0352 CAPACITOR 1 11KV CB | ALSTSS CAP 1 CB SLOT | IS | XLFPK | ALSTSS-MX01-Q00 | ST | Slot - GIS |  | 000001883497 |  |  |  | 11 | 1 | 1 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 4
3665 | 000001881661 | 2023-11-22 | 2024 | OT204744 | NESM CB A552 burnt out trip coil | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-11-29 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 185207 |  |  |  |  | 000001881661 | URGNT System Condition - 23NQ13761 |  |  | 11kV TRANSF 1 CB | NESM A552 SLOT | IS | XLHBT | NESMSS-TX01-Q00 | ST | Slot - GIS |  | 000001881661 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
2640 | 000001880470 | 2023-11-16 | 2024 | OT203917 | TUAN D452 CB not closing | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-11-23 |  | 0.91667 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Circuit Breaker | No Damage | Unknown | Repair | 11kV | 0 | P0 - Forced |  |  | 23788 |  |  |  |  | 000001880470 | TFUO Transient Fault of Unknown 23WB1464 |  |  | MBOROUGH - MBOROUGH CITY T/TUAN | MBOROUGH - MBOROUGH CITY 66KV T/TUAN | IS | XLFBA | FD-6219 | FD | Feeder |  | 000001880470 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
2087 | 000001879627 | 2023-11-13 | 2024 | OT203414 | PROT_11kV CB A452 Intermitant & Alm Acti | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-11-20 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 145397 |  |  |  |  | 000001879627 | URGNT System Condition - 23WB14486 |  |  | A452 11KV PROSTON FDR CB | PROTSS PROSTON FEEDER CB SLOT | IS | XCFBR | PROTSS-FB52-Q00 | ST | Slot - GIS |  | 000001879627 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
4193 | 1875927 | 2023-10-29 | 2024 | OT201090 | ROSO_11KV Bus CB RS-S107 will not close | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-11-15 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Not Working | Inadequate coating |  | 11kV | 0 | P0 - Forced |  |  | 4316 |  |  |  |  | 1875927 | URGNT System Condition - 23CA15044 |  |  | RSSS ROCKHAMPTON SOUTH 66/11KV SUB | ROSOSS 66/11KV ZONE SUB | IS | XLFPR | ROSOSS | SS | Substation Site |  | 000001875927 |  |  |  | 11 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
412 | 1870285 | 2023-10-03 | 2024 | OT197724 | AITK B252 Replace Bushing Dampener | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2023-10-30 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 6771704 |  |  |  |  | 1870285 | URGNT System Condition - 23NQ11939 |  |  | B252 11KV AV02 FDR CB | AITKSS AV02 FEEDER CB SLOT | IS | XLHBT | AITKSS-FB61-Q00 | ST | Slot - GIS |  | 000001870285 |  |  |  | 11 | 1 | 12 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
3440 | 1874881 | 2023-10-25 | 2024 | OT200358 | MACI CB C452 damaged | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-10-25 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 157001 |  |  |  |  | 1874881 | URGNT System Condition - 23WB13873 |  |  | C452 11KV TINANA CREEK FDR CB | MACISS TINANA CREEK FEEDER CB SLOT | IS | XLFBA | MACISS-FB55-Q00 | ST | Slot - GIS |  | 000001874881 |  |  |  | 11 | 1 | 9 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
580 | 1870604 | 2023-10-04 | 2024 | OT197878 | DAGL 11kV CB H252 requires maintenance | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-10-19 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 161714 |  |  |  |  | 1870604 | URGNT System Condition -23NQ11966 |  |  | H252 11KV DG08 FDR CB | DAGLSS DG08 FEEDER CB SLOT | IS | XLHBT | DAGLSS-FB56-Q00 | ST | Slot - GIS |  | 000001870604 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
865 | 1871115 | 2023-10-06 | 2024 | OT198156 | OAKE FB0852 Bus Sect 1-2 CB Spring disch | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-10-11 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 248825 |  |  |  |  | 1871115 | URGNT System Condition - 23SW18050 |  |  | FB0852 11KV BUS TIE CB | OAKESS 11KV BUS CB SLOT | IS | XLGDT | OAKESS-FB08-Q00 | ST | Slot - GIS |  | 000001871115 |  |  |  | 11 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
68840 | 000001861279 | 2023-08-17 | 2024 | OT192578 | CANN FB0352 bent location lock slide pin | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-12 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Corrosion |  | 11kV | 0 | P0 - Forced |  |  | 241885 |  |  |  |  | 000001861279 | NURGT System Condition - 23MK6763 |  |  | FB0352 11KV TFR1 CB | CANNSS TRANSF 1 CB SLOT | IS | XLHBP | CANNSS-TX01-Q10 | ST | Slot - GIS |  | 000001861279 |  |  |  | 11 | 1 | 4 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
69495 | 000001861962 | 2023-08-21 | 2024 | OT192998 | PURR CB 4488 wont close locally/remotely | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-01 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 213802 |  |  |  |  | 000001861962 | URGNT System Condition - 23SW16297 |  |  | CB4488 11KV TRANSF 1 CB | PURRSS TRANSF 1 CB SLOT | IS | XLGDT | PURRSS-TX01-Q00 | ST | Slot - GIS |  | 000001861962 |  |  |  | 11 | 1 | 1 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 4
66696 | 000001856875 | 2023-07-25 | 2024 | OT190213 | ROSO Tx1 CB RS-S104 Bus Shuts wont close | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-29 |  | 0.375 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Incorrect operation/activity |  | 11kV | 0 | P0 - Forced |  |  | 307407 |  |  |  |  | 000001856875 | URGNT System Condition -23CA11433 |  |  | RS-S104 11KV TRANSF 1 CB | ROSOSS TRANSF 1 CB SLOT | IS | XLFPR | ROSOSS-TX51-Q10 | ST | Slot - GIS |  | 000001856875 |  |  |  | 11 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
105520 | 000001856429 | 2023-07-21 | 2024 | OT189943 | FREN FV-T3 11kV CB FV-S110 fail to close | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-07 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 289576 |  |  |  |  | 000001856429 | URGNT System Condition - 23CA11353 |  |  | FV-S110 11KV NORMAN RD FDR CB | FRENSS NORMAN RD FEEDER CB SLOT | IS | XLFPR | FRENSS-FB10-Q00 | ST | Slot - GIS |  | 000001856429 |  |  |  | 11 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
70359 | 000001856353 | 2023-07-21 | 2024 | OT189891 | WETO TX 3 11kV CB3982. CB will not close | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-07-28 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 204203 |  |  |  |  | 000001856353 | URGNT System Condition - 23SW9744 |  |  | CB3982 11KV TRANSF 3 CB | WETOSS TRANSF 3 CB SLOT | IS | XLGDT | WETOSS-TX55-Q10 | ST | Slot - GIS |  | 000001856353 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
1904 | 000001927300 | 2024-05-19 | 2024 | OT236441 | ATHE 2/RMU 2 FDR CB Spring Not Charging | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2024-06-21 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Incorrect operation/activity |  | 22kV | 0 | P0 - Forced |  |  | 133547 |  |  |  |  | 000001927300 | URGNT System Condition - 24FN6466 |  |  | FA12Q00 22KV ATHERTON 2/RMU 2 FDR CB | ATHESS ATHERTON 2 FEEDER CB SLOT | IS | XLTNA | ATHESS-FA12-Q00 | ST | Slot - GIS |  | 000001927300 |  |  |  | 22 | 1 | 5 | 4 | 0 |  | 1 | 4 | 0 |  | 0 |  | 4 |  | 4 |  |  | 0
2710 | 000001928561 | 2024-05-26 | 2024 | OT237084 | BARC Tx BB-T6 22kV CB BB-S207 Serv Mech | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-06-05 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Contamination | Pollution |  | 22kV | 0 | P0 - Forced |  |  | 267787 |  |  |  |  | 000001928561 | URGNT System Condition - 24CA7410 |  |  | BB-S207 22KV TRANSF 6 CB | BARCSS TRANSF 6 CB SLOT | IS | XCPNB | BARCSS-TX06-Q00 | ST | Slot - GIS |  | 000001928561 |  |  |  | 22 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
47200 | 000001922419 | 2024-04-22 | 2024 | OT233909 | MOSS TX1 22kV Fail To Close | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-07 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Pollution |  | 22kV | 0 | P0 - Forced |  |  | 71 |  |  |  |  | 000001922419 | URGNT System Condition - 24FN5533 |  |  | MOSSMAN 66/22KV SUB (MOSSMAN) | MOSSSS 66/22KV ZONE SUB | AR | XCTNS | MOSSSS | SS | Substation Site |  | 000001922419 |  |  |  | 22 | 1 | 4 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
17920 | 000001920870 | 2024-04-12 | 2024 | OT233010 | SCR0 RTS CB RL-S203 Work Clear to Off | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-04-30 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Comms | 0 | P0 - Forced |  |  | 306513 |  |  |  |  | 1920870 | SCR0 RTS R0 - High Priority 24CA5623 |  |  | RL-S203 22KV BAJOOL FDR CB | RAGLSS BAJOOL FEEDER CB SLOT | IS | XLFPR | RAGLSS-FA51-Q00 | ST | Slot - GIS |  | 000001920870 |  |  |  | 22 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
10477 | 000001909112 | 2024-02-17 | 2024 | OT226007 | GEOR_T3 22kV CB wont close_mislatching | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-02-28 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Pollution |  | 22kV | 0 | P0 - Forced |  |  | 78 |  |  |  |  | 1909112 | URGNT System Condition - 24FN2969 |  |  | GEORGETOWN 132/66/22/6.6KV SUB (GEOR) | GEORSS 132/66/22/6.6KV ZONE SUB | AR | XCTNG | GEORSS | SS | Substation Site |  | 000001909112 |  |  |  | 22 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
5580 | 000001901950 | 2024-01-26 | 2024 | OT220816 | PAND EFM CB PD-S207 not latch after clos | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2024-02-01 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Suspect Operation | Incorrect operation/activity |  | 22kV | 0 | P0 - Forced |  |  | 302413 |  |  |  |  | 1901950 | EFM Equip Failure or Malfunct 24CA1968 |  |  | PD-S207 22KV GLENDALE ROAD CB | PANDSS GLENDALE ROAD FEEDER CB SLOT | IS | XLFPR | PANDSS-FA07-Q00 | ST | Slot - GIS |  | 000001901950 |  |  |  | 22 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
10250 | 000001890755 | 2023-12-21 | 2024 | OT211547 | TIER FA03Q00 CB slow to op during storm | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-01-09 |  | 0.41667 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Inadequate coating |  | 22kV | 0 | P0 - Forced |  |  | 309386 |  |  |  |  | 000001890755 | NURGT System Condition -23CA18072 |  |  | FA03Q00 22KV CARAVAN PARK FDR CB | TIERSS CARAVAN PARK FEEDER CB SLOT | IS | XCFZD | TIERSS-FA03-Q00 | ST | Slot - GIS |  | 000001890755 |  |  |  | 22 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
64273 | 000001859925 | 2023-08-09 | 2024 | OT191846 | CANO FA07Q00 Will not close | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-08-11 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Incorrect operation/activity |  | 22kV | 0 | P0 - Forced |  |  | 5790122 |  |  |  |  | 000001859925 | URGNT System Condition - 23FN11375 |  |  | FA07Q00 22KV TRANSF 1 CB | CANOSS TRANSF 1 CB SLOT | IS | XLTNC | CANOSS-TX01-Q00 | ST | Slot - GIS |  | 000001859925 |  |  |  | 22 | 1 | 4 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
5450 | 000001933401 | 2024-06-18 | 2024 | OT239365 | MILE_Wandoan Feeder 33kV CB3715 slow | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-06-20 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Defective component |  | 33kV | 0 | P0 - Forced |  |  | 186754 |  |  |  |  | 000001933401 | URGNT System Condition - 24SW10325 |  |  | CB3715 33KV WANDOAN FDR CB | MILESS WANDOAN FEEDER CB SLOT | IS | XCGDH | MILESS-EB03-Q00 | ST | Slot - GIS |  | 000001933401 |  |  |  | 33 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
5066 | 000001932644 | 2024-06-14 | 2024 | OT238946 | MILE_Bus 1-3 33kV CB CB3714 Trips | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-06-14 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> | <null> | Not Applicable | 0 | P0 - Forced |  |  | 197212 |  |  |  |  | 000001932644 | URGNT System Condition - 24SW10152 |  |  | CB3714 33KV BUS 1-3 CB | MILESS 33KV BUS CB SLOT | IS | XCGDH | MILESS-EB07-Q | ST | Slot - GIS |  | 000001932644 |  |  |  | 33 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
1977 | 000001927334 | 2024-05-20 | 2024 | OT236473 | MILE_CB3715 Delay when Close Command Iss | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-06-03 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Wiring and Electrical Componen | Out of Specification | Incorrect operation/activity |  | 33kV | 0 | P0 - Forced |  |  | 7685 |  |  |  |  | 000001927334 | NURGT System Condition - 24SW9035 |  |  | MILES 33/11KV SUB (MC008) | MILESS 33/11KV ZONE SUB | IS | XCGDH | MILESS | SS | Substation Site |  | 000001927334 |  |  |  | 33 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
29148 | 000001895508 | 2024-01-02 | 2024 | OT216046 | NOCL Cloncurry SWER ACR trip Fdr CB B252 | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-29 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | OHEW | 0 | P0 - Forced |  |  | 6402688 |  |  |  |  | 000001895508 | URGNT System Condition - 24NQ0126 |  |  | CLS262 CLONCURRY SWER ACR | CLS262-FLINDERS HWY, CLONCURRY QLD 4824 | IS | XCHBL | RC-492164 | NT | Network Slot |  | 000001895508 |  |  |  | 33 | 1 | 1 | 4 | 1 | 4 | 0 |  | 0 |  | 0 |  | 4 | 0
75383 | 000001852575 | 2023-07-02 | 2024 | OT187844 | JUCR J652 failed to close via SCADA | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-01 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | ACR, Body | Suspect Operation | Defective component |  | 33kV | 0 | P0 - Forced |  |  | 160577 |  |  |  |  | 000001852575 | URGNT System Condition - 23NQ7014 |  |  | J652 19.1KV JC10 CB | JUCRSS JC10 FEEDER CB SLOT | IS | XCHBJ | JUCRSS-EB56-Q00 | ST | Slot - GIS |  | 000001852575 |  |  |  | 33 | 1 | 12 | 4 | 12 |  | 0 |  | 0 |  | 0 |  | 4
63121 | 000001856475 | 2023-07-22 | 2024 | OT189983 | SARI 33kV TX 2 CB EB08 failed to operate | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-07-27 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Corroded | Fatigue |  | 33kV | 0 | P0 - Forced |  |  | 237647 |  |  |  |  | 000001856475 | URGNT System Condition - 23MK6128 |  |  | 2T CB 11KV TRANSF 2 CB | SARISS TRANSF 2 CB SLOT | IS | XLFPS | SARISS-TX02-Q10 | ST | Slot - GIS |  | 000001856475 |  |  |  | 33 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
19775 | 000001852876 | 2023-07-03 | 2024 | OT188025 | YARA-33kV ABB RMAG CB EB07Q00-NAR Applie | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-07-17 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Incorrect operation/activity |  | 33kV | 0 | P0 - Forced |  |  | 8750071 |  |  |  |  | 000001852876 | SYNAR System Condition - 23SW9074 | Restriction Applies |  | EB07Q00 33KV MARYRRGH FDR CB | YARASS MARYROROUGH SOLAR FDR CB SLOT | AR | XCGDI | YARASS-EB07-Q00 | ST | Slot - GIS |  | 000001852876 |  |  |  | 33 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
75423 | 000001853442 | 2023-07-06 | 2024 | OT188371 | OAKE Tx3 Fdr CB Spring EB1152 toggl | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-07-07 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Defective component |  | 33kV | 0 | P0 - Forced |  |  | 248006 |  |  |  |  | 000001853442 | NURGT System Condition - 23SW9171 |  |  | EB1152 33KV TFR3 CB | OAKESS TFR3 CB SLOT | IS | XLGDT | OAKESS-EB11-Q00 | ST | Slot - GIS |  | 000001853442 |  |  |  | 33 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
4718 | 000001932075 | 2024-06-12 | 2024 | OT238698 | GEOR T1 CB Bearing Fail_Spring Chrg Mech | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2024-06-21 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Incorrect operation/activity |  | 66kV | 0 | P0 - Forced |  |  | 143015 |  |  |  |  | 000001932075 | URGNT System Condition - URGENT 24FN7331 |  |  | T1 66KV TRANSF 1 CB | GEORSS TRANSF 1 CB SLOT | IS | XCTNG | GEORSS-TX51-Q10 | ST | Slot - GIS |  | 000001932075 |  |  |  | 66 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
51142 | 000001929008 | 2024-05-28 | 2024 | OT237300 | HOHI T1 CB A452 NOT OPENING FULLY | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-31 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Broken | Fatigue |  | 66kV | 0 | P0 - Forced |  |  | 177843 |  |  |  |  | 000001929008 | URGNT System Condition - 24NQ9146 |  |  | A452 66KV TRANSF 1 CB | HOHISS TRANSF 1 CB SLOT | IS | XLHBH | HOHISS-TX01-Q00 | ST | Slot - GIS |  | 000001929008 |  |  |  | 66 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
9292 | 000001907351 | 2024-02-09 | 2024 | OT224941 | POCU EA0352 EA0652 Dif trip CB fail | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2024-02-21 |  | 0.45972 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 5192779 |  |  |  |  | 1907351 | HESS Human Error - Second Sys 24CA2757 |  |  | EA0652 66KV 6111 GLADSTONE NTH CB | POCUSS 6111 GLADSTONE NORTH CB SLOT | IS | XLFPG | POCUSS-EA06-Q00 | ST | Slot - GIS |  | 000001907351 |  |  |  | 66 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
1316 | 000001896499 | 2024-01-06 | 2024 | OT216858 | WEBU CB A1224, Gas Locked Oper A1124 | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2024-01-15 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Leaking | Defective component |  | 66kV | 0 | P0 - Forced |  |  | 8744992 |  |  |  |  | 1896499 | URGNT System Condition - 24WB0264 |  |  | A1124 66KV BUS SECTION CB | WEBUSS 66KV BUS SECTION CB SLOT | IS | XLFBB | WEBUSS-EA55-Q00 | ST | Slot - GIS |  | 000001896499 |  |  |  | 66 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
4632 | 000001883117 | 2023-11-28 | 2024 | OT205686 | MURG Sus burntout close coil on CB B352 | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-12-04 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Attachment Tie | Loose Nut | Wind |  | 66kV | 0 | P0 - Forced |  |  | 158152 |  |  |  |  | 000001883117 | URGNT System Condition -23WB14979 |  |  | 66KV KINGAROY FDR CB | MURG B352 SLOT | IS | XCFBR | MURGSS-EA53-Q00 | ST | Slot - GIS |  | 000001883117 |  |  |  | 66 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
1894 | 000001879227 | 2023-11-11 | 2024 | OT203151 | EMER EM-T2 CB EM-S608 C ph Oil Loss | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-11-13 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Leakage |  | 66kV | 0 | P0 - Forced |  |  | 367068 |  |  |  |  | 000001879227 | URGNT System Condition - 23CA15754 |  |  | DELLE 66KV OCB | EMERSS 66KV TRANSF 2 CB EM-S608 | IS | XLFPE | CB91641941 | CB | Circuit Breaker |  | 000001879227 |  |  |  | 66 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
551 | 000001865183 | 2023-09-06 | 2024 | OT194719 | LITT CB LM-S613 Wont Close after Outage | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-20 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Loose/missing component | Repair | 66kV | 0 | P0 - Forced |  |  | 294788 |  |  |  |  | 000001865183 | URGNT System Condition - 23CA13121 |  |  | LM-S613 66KV 6030 MONTO FDR CB | LITTSS 6030 MONTO FEEDER CB SLOT | IS | XCFZV | LITTSS-EA52-Q00 | ST | Slot - GIS |  | 000001865183 |  |  |  | 66 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
68835 | 000001857850 | 2023-07-30 | 2024 | OT190752 | ROSO CB RS-S101 Service switch maint | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-12 |  | 0.5 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | High Coolant Temperature | Incorrect operation/activity |  | DC | 0 | P0 - Forced |  |  | 307335 |  |  |  |  | 000001857850 | NURGT System Condition - 23CA11617 |  |  | RS-S101 11KV GRACEMERE CB | ROSOSS GRACEMERE FEEDER CB SLOT | IS | XLFPR | ROSOSS-FB56-Q00 | ST | Slot - GIS |  | 000001857850 |  |  |  | 66 | 1 | 0 |  | 0 |  | 0 |  | 13 | 4 | 0 |  | 4 |  |  |  | CB
62752 | 000001863401 | 2023-08-29 | 2024 | OT193736 | ROSO CB RS-S603 Motor Limit Switc faulty | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-08 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Wiring and Electrical Componen | Out of Specification | Vibration |  | DC | 0 | P0 - Forced |  |  | 307739 |  |  |  |  | 000001863401 | URGNT System Condition - 23CA12714 |  |  | RS-S603 66KV TRANSF 1 CB | ROSOSS TRANSF 1 CB SLOT | IS | XLFPR | ROSOSS-TX51-Q00 | ST | Slot - GIS |  | 000001863401 |  |  |  | 66 | 1 | 1 | 4 | 0 |  | 0 |  | 12 |  | 0 |  | 4
70370 | 000001855180 | 2023-07-14 | 2024 | OT189268 | LACR CB LC-S610 not staying closed | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-30 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 371282 |  |  |  |  | 000001855180 | URGNT System Condition - 23CA8613 |  |  | ASEA 66KV OCB | LACRSS LC-S610 66KV 6096 EGANS HILL FDR | IS | XLFPR | CB92283579 | CB | Circuit Breaker |  | 000001855180 |  |  |  | 66 | 1 | 13 | 4 | 1 | 0 | 0 |  | 0 |  | 0 |  | 4
20342 | 000001859786 | 2023-08-09 | 2024 | OT191775 | WEBU CB G452 bearing spring char slippin | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-15 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Armour Rod | Leaning | Cement Growth |  | 66kV | 0 | P0 - Forced |  |  | 165667 |  |  |  |  | 000001859786 | URGNT System Condition - 23WB11552 |  |  | G452 11KV OAKWOOD CB | WEBUSS OAKWOOD FEEDER CB SLOT | IS | XLFBB | WEBUSS-FB57-Q00 | ST | Slot - GIS |  | 000001859786 |  |  |  | 66 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
18481 | 000001859549 | 2023-08-08 | 2024 | OT191672 | MORA EA10T03 Low oil C phase sight glass | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-15 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Tank, Head & Secondary Term Bo | Leaking | Seal | Repair | 66kV | 0 | P0 - Forced |  |  | 256111 |  |  |  |  | 000001859549 | URGNT System Condition - 23MK6498 |  |  | EA10T03 66KV UTAH 1 FDR CT | MORASS UTAH 1 FEEDER CT SLOT | IS | XCPNO | MORASS-EA10-T03 | ST | Slot - GIS |  | 000001859549 |  |  |  | 66 | 1 | 12 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
75415 | 000001858924 | 2023-08-04 | 2024 | OT191286 | WEBU CB J452 bearing slippin charg motor | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-09 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 66kV | 0 | P0 - Forced |  |  | 165457 |  |  |  |  | 000001858924 | NURGT System Condition - 23WB11424 |  |  | J452 11KV AVOCA STREET CB | WEBUSS AVOCA ST FEEDER CB SLOT | IS | XLFBB | WEBUSS-FB52-Q00 | ST | Slot - GIS |  | 000001858924 |  |  |  | 66 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
3517 | 000001929981 | 2024-06-03 | 2024 | OT237778 | MICB 132kV CB 7B190 contact alignment | 1 | 0 | P0 - Forced | A | Authorised | SC | (4)With Scheduler |  |  | 0.99931 | [9 empty] | MF | Maintenance Forced | Switch, Control Box | No Damage | Fatigue |  | 220kV | 0 | P0 - Forced |  |  | 7445686 |  |  |  |  | 000001929981 | NURGT System Condition - 24NQ9351 |  |  | 7B190 132KV GEN B1 GCB | MICBSS GEN B1 FEEDER GCB SLOT | IS | XCHBI | MICBSS-DA03-Q00 | ST | Slot - GIS |  | 000001929981 |  |  |  | 132 | 1 | 5 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 4
4717 | 000001932054 | 2024-06-12 | 2024 | OT238696 | GEOR T1 CB4412 Bearing Fail_Spring Mech | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2024-06-21 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Incorrect operation/activity |  | 132kV | 0 | P0 - Forced |  |  | 143032 |  |  |  |  | 000001932054 | URGNT System Condition - URGENT 24FN7330 |  |  | 4412 TRANSF 1 132KV CB 4412 | GEORSS TRANSF 1 CB SLOT | IS | XCTNG | GEORSS-TX51-Q00 | ST | Slot - GIS |  | 000001932054 |  |  |  | 132 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4

## ACR failures
Column1 | REQUEST_ID | RAISED_DATE | FY | WORK_ORDER | WO_DESC | WO_JOB_CODEX1_1 | ORIG_PRIORITY | ORIG_PRIORITY_DESCRIPTION | WO_STATUS_M | WO_STATUS_M_DESCRIPTION | WO_STATUS_U | WO_STATUS_U_DESCRIPTION | CLOSED_DT | CLOSED_COMMIT_DT | CLOSED_TIME | COMPLETED_CODE | COMPLETED_CODE_DESCRIPTION | CLOSED_STATUS | CLOSED_STATUS_DESCRIPTION | SHUTDOWN_EQUIP | SHUTDOWN_TYPE | SHUTDOWN_TYPE_DESCRIPTION | PARENT_WO | PARENT_WO_DESC | MAINT_TYPE | MAINT_TYPE_DESCRIPTION | MSSS_OBJECT_FAILURE_DESCRIPTION | MSSS_DAMAGE_APPARENT_CAUSE_DESCRIPTION | MSSS_CAUSE_DESCRIPTION | CONSEQUENCE_DESCRIPTION | VOLTAGE_DESCRIPTION | PLAN_PRIORITY | PLAN_PRIORITY_DESCRIPTION | CUST_NO | FAILURE_PART | EQUIP_NO | COMP_CODE | COMP_CODE_DESCRIPTION | COMP_MOD_CODE | COMP_MOD_CODE_DESCRIPTION | REQUEST_ID_2 | SHORT_DESC_1 | SHORT_DESC_2 | LOCATION | ITEM_NAME_1 | ITEM_NAME_2 | EQUIP_STATUS | EQUIP_LOCATION | PLANT_NO | EQUIP_CLASS | EQUIP_CLASS_DESCRIPTION | WORK_ORDER_EXTENDED_DESCRIPTION | REQUEST_ID_3 | WORK_REQUEST_EXTENDED_DESCRIPTION | NAMP_LINE | NAMP_LINE_DESCRIPTION | Voltage | OT | CB | CB FAULT | ACR | Rec Fault | RMU | RMUFault | Switch | Switch Fault | Isol | Isol Fault | CB2 | ACR2 | RMU2 | Switches | Switches Comment2 | RMU Comm2
50047 | 000001927188 | 2024-05-18 | 2024 | OT236357 | SCR0 RTS R0 - High Prior BYPASS RECLOSER | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-05-20 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> | <null> | Not Applicable | 0 | P0 - Forced |  |  | 2270298 |  |  |  |  | 000001927188 | DD RTS R1 CB16374 PECHEY TO NOJA |  |  | Pechey Recloser | Pechey Recloser | IS | XLGDT | RC-66409 | NT | Network Slot |  | 000001927188 |  |  |  | 11 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
47239 | 000001922339 | 2024-04-22 | 2024 | OT233859 | SCR0 RTS R0 - Hawes Lane Recloser | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-05-14 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Pole Possum Guard | Missing | Unknown | Replace | 11kV | 0 | P0 - Forced |  |  | 8223826 |  |  |  |  | 000001922339 | SCR0 RTS R0 - High Priority |  |  | Hawes Lane Recloser |  | IS | XLFBA | RC-1355360 | NT | Network Slot |  | 000001922339 |  |  |  | 11 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
7534 | 000001887142 | 2023-12-12 | 2024 | OT208673 | SCR0 RTS R0 - High Priority-SugarloafACR | 1 | 0 | P0 - Forced | C | Closed |  |  | 2023-12-19 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 2366492 |  |  |  |  | 000001887142 | SCR0 RTS R0 - High Priority |  |  | SUGARLOAF RECLOSER | SUGARLOAF-1405 SHUTE HARBOUR RD, CANNON | IS | XLHBP | RC-57147 | NT | Network Slot |  | 000001887142 |  |  |  | 11 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
5361 | 000001884213 | 2023-12-01 | 2024 | OT206458 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2023-12-01 |  | 0.66667 | CL | Closed | C | Completed | [5 empty] | CN | Construction | ACR, Body | Damaged | Corrosion |  | 11kV | 0 | P0 - Forced |  |  | 1442176 | RECL | Recloser | OC | Outage Codes | 000001884213 | U Unknown |  |  | 4090494 | 388 | IS | XLFPK | NS4090494 | NS | Network Site |  | 000001884213 |  |  |  | 11 | 1 | 0 |  | 4 | 4 | 0 |  | 0 |  | 0 |  |  | 4
14521 | 000001915607 | 2024-03-17 | 2024 | OT229855 | SCR2 RTS R2 - PH-58 ACR Bypassed | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2024-03-20 |  | 11:59:00 pm | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 000005929895 |  |  |  |  | 000001915607 | SCR2 RTS R2 - Low Priority 24FN4147 |  |  | Brooks Rd SWER Recloser | 84 CAMPBELL RD, MUNGALLI QLD 4886 | IS | XCTNR | RC-362322 | NT | Network Slot |  | 000001915607 |  |  |  | 22 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
14515 | 000001915579 | 2024-03-17 | 2024 | OT229831 | U Unknown | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-03-18 |  | 11:59:00 pm | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Surge Diverter Body, Unknown | Short Circuit | Unknown |  | 12.7kV | 0 | P0 - Forced |  |  | 000001137716 | SURG | Surge Diverters | OC | Outage Codes | 000001915579 | U Unknown |  |  | WA4 | Watson Rd | IS | XCTNR | NS5208932 | NS | Network Site |  | 000001915579 |  |  |  | 22 | 1 | 0 |  | 4 | 4 | 0 |  | 0 |  | 0 |  |  | 4
3451 | 000001881436 | 2023-11-21 | 2024 | OT204597 | SCR2 RTS R2 - 22kV Recloser RC885338 | 1 | 0 | P0 - Forced | C | Closed |  |  | 2023-11-28 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 22kV | 0 | P0 - Forced |  |  | 9232802 |  |  |  |  | 000001881436 | SCR2 RTS R2 - Low Priority |  |  | Harvey Rd | 211 HARVEY RD, REDLYNCH QLD 4870 | IS | XLTNC | RC-885338 | NT | Network Slot |  | 000001881436 |  |  |  | 22 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
546 | 000001864311 | 2023-09-01 | 2024 | OT194207 | 607088 Hollands rd swer ACR VT volts | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-29 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | SWER HV Elec Recloser 12.7kV | Out of Specification | Unknown | Repair | 12.7kV | 0 | P0 - Forced |  |  | 7762155 |  |  |  |  | 000001864311 | SCR2 RTS R2 - Low Priority 23WB12303 |  |  | Hollands Rd SWER Recloser | MERCERS RD, MEADOWVALE QLD 4670 | IS | XLFBB | RC-1103285 | NT | Network Slot |  | 000001864311 |  |  |  | 22 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
10247 | 000001890453 | 2023-12-21 | 2024 | OT211296 | MOSS System Condition -URGENT RC-868498 | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-01-05 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 9080982 |  |  |  |  | 000001890453 | URGNT System Condition - URGENT |  |  | RC868498 | 59 STEWART CREEK RD, DAINTREE QLD 4873 | IS | XCTNS | RC-868498 | NT | Network Slot |  | 000001890453 |  |  |  | 33 | 1 | 0 |  | 4 | 4 | 0 |  | 4 |  | 0 |  |  | 4
8563 | 000001888782 | 2023-12-16 | 2024 | OT209883 | NEBO - 19kV Landsborough West ACR failed | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-12-29 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 9147713 |  |  |  |  | 000001888782 | NURGT System Condition - Non Urgent |  |  | RC875520 | STRATHFIELD RD, STRATHFIELD QLD 4742 | IS | XCPNO | RC-875520 | NT | Network Slot |  | 000001888782 |  |  |  | 33 | 1 |  |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4

## RMU Failures
Column1 | REQUEST_ID | RAISED_DATE | FY | WORK_ORDER | WO_DESC | WO_JOB_CODEX1_1 | ORIG_PRIORITY | ORIG_PRIORITY_DESCRIPTION | WO_STATUS_M | WO_STATUS_M_DESCRIPTION | WO_STATUS_U | WO_STATUS_U_DESCRIPTION | CLOSED_DT | CLOSED_COMMIT_DT | CLOSED_TIME | COMPLETED_CODE | COMPLETED_CODE_DESCRIPTION | CLOSED_STATUS | CLOSED_STATUS_DESCRIPTION | SHUTDOWN_EQUIP | SHUTDOWN_TYPE | SHUTDOWN_TYPE_DESCRIPTION | PARENT_WO | PARENT_WO_DESC | MAINT_TYPE | MAINT_TYPE_DESCRIPTION | MSSS_OBJECT_FAILURE_DESCRIPTION | MSSS_DAMAGE_APPARENT_CAUSE_DESCRIPTION | MSSS_CAUSE_DESCRIPTION | CONSEQUENCE_DESCRIPTION | VOLTAGE_DESCRIPTION | PLAN_PRIORITY | PLAN_PRIORITY_DESCRIPTION | CUST_NO | FAILURE_PART | EQUIP_NO | COMP_CODE | COMP_CODE_DESCRIPTION | COMP_MOD_CODE | COMP_MOD_CODE_DESCRIPTION | REQUEST_ID_2 | SHORT_DESC_1 | SHORT_DESC_2 | LOCATION | ITEM_NAME_1 | ITEM_NAME_2 | EQUIP_STATUS | EQUIP_LOCATION | PLANT_NO | EQUIP_CLASS | EQUIP_CLASS_DESCRIPTION | WORK_ORDER_EXTENDED_DESCRIPTION | REQUEST_ID_3 | WORK_REQUEST_EXTENDED_DESCRIPTION | NAMP_LINE | NAMP_LINE_DESCRIPTION | Voltage | OT | CB | CB FAULT | ACR | Rec Fault | RMU | RMUFault | Switch | Switch Fault | Isol | Isol Fault | CB2 | ACR2 | RMU2 | Switches | Switches Comment2 | RMU Comm2 | Make | Model | YoM | Column2
6654 | 000001935034 | 2024-06-26 | 2024 | OT240182 | RTS R2 - COMMUNITY CENTRE RMU NO GAS | 1 | 0 | P0 - Forced | A | Authorised |  |  |  |  | 0.64583 | [9 empty] | MF | Maintenance Forced |  |  |  |  | 22kV | 0 | P0 - Forced |  |  | 2401965 |  |  |  |  | 000001935034 | PN RTS R1 BARNFIELD DR COMMUNITY CTR_RMU | LO RBD 26/07 |  | 1684S | 86 CELEBER DVE, ANDERGROVE QLD 4740 | IS | XLFPK | LB-77633 | NT | Network Slot |  | 000001935034 |  |  |  | 11 | 1 | 0 |  | 0 |  | 1 | 4 | 0 |  | 0 |  |  |  | 4 |  |  | 0 | ABB | Safelink | 1993
18023 | 000001921040 | 2024-04-14 | 2024 | OT233156 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2024-04-14 |  |  | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Alignment Incorrect | Internal Fault |  | 11kV | 0 | P0 - Forced |  |  | 2403741 |  |  |  |  | 1921040 | THURINGOWA STATE HIGH SCHOOL | O - Other |  | TVS3886 | THURINGOWA STATE HIGH SCHOOL, SOUTH VIC | IS | XLHBT | GT-184170 | NT | Network Slot |  | 000001921040 |  |  |  | 11 | 1 | 0 |  | 0 |  | 4 | 4 | 4 | 4 | 0 |  |  |  | 4 | 4 | 0 | 0 | ABB | Safelink | 2006
9552 | 000001907670 | 2024-02-12 | 2024 | OT225200 | SCR0 RTS R0 - High Priority | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-02-13 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 8254690 |  |  |  |  | 1907670 | BB_RTS R2_RMU 615693 BAKERFINCH DR BARG |  |  | Baker-Finch Dve | BAKER-FINCH DVE, BARGARA QLD 4670 | IS | XLFBB | GT-1184961 | NT | Network Slot |  | 000001907670 |  |  |  | 11 | 1 | 0 |  | 0 |  | 4 | 4 | 0 |  | 0 |  |  |  | 4 |  |  | 0 | Schneider | FBX | 2015
6284 | 000001902420 | 2024-01-27 | 2024 | OT221297 | Switchgear RTS Friendlys CB | 1 |  |  | C | Closed |  |  | 2024-02-12 |  | 0.97917 | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Damaged | Unknown |  | 11kV | 0 | P0 - Forced |  |  | 6553235 | SW | Switch | OC | Outage Codes | 1902420 | BUNDABERG FRIENDLY SOCIETY MED | P - Phase Down (LV) |  | 86052 | 23 BINGERA ST, BUNDABERG WEST QLD 4670 | IS | XLFBB | NS86052 | NS | Network Site |  | 000001902420 |  |  |  | 11 | 1 | 4 | 4 | 0 |  | 4 | 4 | 0 |  | 0 |  | 4 |  | 4 |  |  | 0 | ABB | SAFERING | 2008
10470 | 000001891160 | 2023-12-23 | 2024 | OT211905 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2024-01-04 |  | 0.64601 | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Damaged | Internal Fault |  | 11kV | 0 | P0 - Forced |  |  | 8169052 |  |  |  |  | 000001891160 | U Unknown |  |  | GLENVALE EAST | 11KV GLENVALE EAST FDR (14088) | IS | XLGDT | FD-4088 | FD | Feeder |  | 000001891160 |  |  |  | 11 | 1 | 0 |  | 0 |  | 4 | 4 | 0 |  | 0 |  |  |  | 4 |  |  | 0 | ABB | SDAF 3 SERIES 3 | 1994
1904 | 000001927300 | 2024-05-19 | 2024 | OT236441 | ATHE 2/RMU 2 FDR CB Spring Not Charging | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2024-06-21 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Incorrect operation/activity |  | 22kV | 0 | P0 - Forced |  |  | 133547 |  |  |  |  | 000001927300 | URGNT System Condition - 24FN6466 |  |  | FA12Q00 22KV ATHERTON 2/RMU 2 FDR CB | ATHESS ATHERTON 2 FEEDER CB SLOT | IS | XLTNA | ATHESS-FA12-Q00 | ST | Slot - GIS |  | 000001927300 |  |  |  | 22 | 1 | 5 | 4 | 0 |  | 1 | 4 | 0 |  | 0 |  | 4 |  | 4 |  |  | 0 | GEC | AV24 | 1985
43970 | 000001917722 | 2024-03-26 | 2024 | OT231068 | Cable Return to Service | 1 |  |  | C | Closed |  |  | 2024-05-01 |  | 0.66667 | CL | Closed | C | Completed | [5 empty] | CN | Construction | Padmount Substation | Broken | Unknown |  | 22kV | 0 | P0 - Forced |  |  | 24240 |  |  |  |  | 000001917722 | Unknown |  |  | WHITE ROCK |  | IS | XLTNC | FD-2122 | FD | Feeder |  | 000001917722 |  |  |  | 22 | 1 | 0 |  | 0 |  | 4 | 4 | 0 |  | 0 |  |  |  | 4 |  |  | 0 | ORMAZABAL | GA3K1TS-C | 2011

## Switch Failures
Column1 | REQUEST_ID | RAISED_DATE | FY | WORK_ORDER | WO_DESC | WO_JOB_CODEX1_1 | ORIG_PRIORITY | ORIG_PRIORITY_DESCRIPTION | WO_STATUS_M | WO_STATUS_M_DESCRIPTION | WO_STATUS_U | WO_STATUS_U_DESCRIPTION | CLOSED_DT | CLOSED_COMMIT_DT | CLOSED_TIME | COMPLETED_CODE | COMPLETED_CODE_DESCRIPTION | CLOSED_STATUS | CLOSED_STATUS_DESCRIPTION | SHUTDOWN_EQUIP | SHUTDOWN_TYPE | SHUTDOWN_TYPE_DESCRIPTION | PARENT_WO | PARENT_WO_DESC | MAINT_TYPE | MAINT_TYPE_DESCRIPTION | MSSS_OBJECT_FAILURE_DESCRIPTION | MSSS_DAMAGE_APPARENT_CAUSE_DESCRIPTION | MSSS_CAUSE_DESCRIPTION | CONSEQUENCE_DESCRIPTION | VOLTAGE_DESCRIPTION | PLAN_PRIORITY | PLAN_PRIORITY_DESCRIPTION | CUST_NO | FAILURE_PART | EQUIP_NO | COMP_CODE | COMP_CODE_DESCRIPTION | COMP_MOD_CODE | COMP_MOD_CODE_DESCRIPTION | REQUEST_ID_2 | SHORT_DESC_1 | SHORT_DESC_2 | LOCATION | ITEM_NAME_1 | ITEM_NAME_2 | EQUIP_STATUS | EQUIP_LOCATION | PLANT_NO | EQUIP_CLASS | EQUIP_CLASS_DESCRIPTION | WORK_ORDER_EXTENDED_DESCRIPTION | REQUEST_ID_3 | WORK_REQUEST_EXTENDED_DESCRIPTION | NAMP_LINE | NAMP_LINE_DESCRIPTION | Voltage | OT | CB | CB FAULT | ACR | Rec Fault | RMU | RMUFault | Switch | Switch Fault | Isol | Isol Fault | CB2 | ACR2 | RMU2 | Switches | Switches Comment2 | RMU Comm2 | Make | Model | YoM
18023 | 000001921040 | 2024-04-14 | 2024 | OT233156 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2024-04-14 |  |  | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Alignment Incorrect | Internal Fault |  | 11kV | 0 | P0 - Forced |  |  | 2403741 |  |  |  |  | 1921040 | THURINGOWA STATE HIGH SCHOOL | O - Other |  | TVS3886 | THURINGOWA STATE HIGH SCHOOL, SOUTH VIC | IS | XLHBT | GT-184170 | NT | Network Slot |  | 000001921040 |  |  |  | 11 | 1 | 0 |  | 0 |  | 4 | 4 | 4 | 4 | 0 |  |  |  | 4 | 4 | 0 | 0 | ABB | Safelink | 2006
13078 | 000001913462 | 2024-03-06 | 2024 | OT228590 | CAFE_11kV Bus Tie Gas Switch A829_FIS | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-03-15 |  | 11:59:00 pm | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Switch Oil/Gas Insulation | Gas Leakage | Fatigue | Replace | 11kV | 0 | P0 - Forced |  |  | 000000170205 |  |  |  |  | 000001913462 | URGNT System Condition - 24NQ5832 |  |  | A829 11KV BUS ISOL | CAFESS BUS ISOL SLOT | IS | XLHBT | CAFESS-FB51-Q01 | ST | Slot - GIS |  | 000001913462 |  |  |  | 11 | 1 | 0 |  | 0 |  | 0 |  | 5 | 4 | 0 |  |  |  |  | 4 | 0 |  | Scneider | RL27 | N/A
8522 | 000001888652 | 2023-12-16 | 2024 | OT209763 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2023-12-16 |  |  | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Damaged | Unknown |  | 11kV | 0 | P0 - Forced |  |  | 1864849 | SW | Switch | OC | Outage Codes | 000001888652 | MRS D M JANSEN | S - Sparking Lines/Pole |  | 3312297 | 28693 BRUCE HWY, CHILDERS QLD 4660 | IS | XCFBC | NS3312297 | NS | Network Site |  | 000001888652 |  |  |  | 11 | 1 | 0 |  | 0 |  | 0 |  | 4 | 4 | 0 |  |  |  |  | 4 | 0 |  | HV link | N/A | N/A
2814 | 1873838 | 2023-10-20 | 2024 | OT199703 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2023-11-15 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Damaged | Unknown | Replace | 11kV | 0 | P0 - Forced |  |  | 1522735 | SW | Switch | OC | Outage Codes | 1873838 | DD RTS R1 TMBA CEC PLNS RD DL7157 RPLC |  |  | 3248105 | F3145 | IS | XCGDI | NS3248105 | NS | Network Site |  | 000001873838 | .HEADING RTS R1 - Medium Priority 11kV Disc Links DL7157 B Phase has nearly pulled through crossarm and require replacing. Unable to be Operated. 11kV Disc Links DL7157 B Phase has nearly pulled through\rcrossarm and require replacing. Unable to be Operated. ============================================================ COMMENTS: \r02/11/23 201384 KJ: Issued to XCGDL via Opex. |  |  | 11 | 1 | 0 |  | 0 |  | 0 |  | 12 | 4 | 0 |  |  |  |  | 4 | 0 |  | HV Link | N/A | N/A
75391 | 000001858784 | 2023-08-04 | 2024 | OT191216 | BOWE D257 Earth Switch faulty - 23NQ9768 | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-05 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 168725 |  |  |  |  | 000001858784 | URGNT System Condition - 23NQ9768 |  |  | D257 11KV BN04 FDR ES | BOWESS BN04 FEEDER ES SLOT | IS | XLHBB | BOWESS-FB52-Q05 | ST | Slot - GIS |  | 000001858784 | .HEADING System Condition - URGENT D257 Earth Switch faulty. Earth Switch contacts not moving when handle operated. Also contacts appear to be not fully opened\rD257 Earth Switch faulty. Earth Switch contacts not moving when handle operated. Also contacts appear to be not fully opened. |  |  | 11 | 1 | 0 |  | 0 |  | 0 |  | 13 | 4 | 0 |  |  |  |  | 4 | 0 |  | Mitsubishi | 10-PVR | 1981
2139 | 1872996 | 2023-10-16 | 2024 | OT199253 | ATHE 66kV Earth Switch EA05Q05 | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-10-30 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | HV Isolators Fuses & Earth Swi | Loose Connection | Wear and Tear |  | DC | 0 | P0 - Forced |  |  | 101 |  |  |  |  | 1872996 | URGNT System Condition - 23FN13778 |  |  | ATHERTON 66/22KV SUB (ATHE) | ATHESS 66/22KV ZONE SUB | IS | XLTNA | ATHESS | SS | Substation Site |  | 000001872996 | System Condition - URGENT Atherton No.1 Fdr - 66kV Earth Switch EA05Q05 - indicating closed. Limit switch needs to be adjusted. Atherton No.1 Fdr - 66kV Earth Switch EA05Q05 - indicating closed. Limit switch needs to be adjusted. |  |  | 66 | 1 | 0 |  | 0 |  | 0 |  | 13 | 4 | 0 |  |  |  |  | 4 | 0 |  | ACELEC TAPLIN | 66RD-1 | 2004
69497 | 000001859551 | 2023-08-08 | 2024 | OT191675 | CANN EA0229 contacts sticking on switch | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-01 |  | 0.625 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | HV Isolators Fuses & Earth Swi | Deteriorated | Incorrect operation/activity |  | 66kV | 0 | P0 - Forced |  |  | 243767 |  |  |  |  | 000001859551 | URGNT System Condition - 23MK6500 |  |  | EA0229 66KV TFR1-TFR2 TIE ISOL | CANNSS 66KV BUS ISOL SLOT | IS | XLHBP | CANNSS-EA02-Q02 | ST | Slot - GIS |  | 000001859551 | System Condition - URGENT [CANN] 66kV TFR1-TFR2 TIE ISOL EA0229 - contacts sticking on switch [CANN] 66kV TFR1-TFR2 TIE ISOL EA0229 - Sticky contacts on switch |  |  | 66 | 1 | 0 |  | 0 |  | 0 |  | 13 | 4 | 12 | 4 |  |  |  | 4 | 0 |  | HAYCOLEC | 930 | 1999

## Version Info
This workbook is created as a cut down version of the full data set only showing the failures. The information is copy and past of filtered data from Ergon WO 23_24_RIN_Revised V2.xlsx