## DNA
Existing Designated Network Assets - as at 8 April 2025
Parent | Name of DNA | Existing DNA Description | Location and Route of Existing DNA | Capacity | Owner/Controller/Operator of DNA
Lumea | Riverina DNA | The DNA comprises the Riverina BESS 132/33kV substation and approximately 200m of 132kV underground cable. 132 kV Underground Single Circuit cable from Darlington Point substation to Riverina BESS substation (approx. 200 m); 132 kV feeder switch bay without breaker including 132kV cable termination structure; One of 132/33 kV 180 MVA Transformer; One switchgear building including; 5 x 33 kV indoor switchboards (Transformer incomer excludes the CB); One Aux Services Building (ASB) with secondary systems equipment installed; One earthing/auxiliary Transformer; Site amenities and storage shed. The Designated Assets includes the Primary and Secondary works associated with the above. | Adjacent to TG's Darlington Point Substation in the Murrumbidgee Shire, New South Wales | The capacity of the DNA is 150MW and there is currently no spare capacity. There are space limitations to increasing capacity. | Lumea Pty Limited (ACN 626 136 865) as trustee for Lumea Trust (ABN 94 121 353 950)
ElectraNet | Redhill to Clements Gap North DNA | Redhill-Clements Gap North 132 kV transmissions line (Redhill F1887); and Clements Gap North Substation. | The Designated Network Asset owned by ElectraNet connects the Clements Gap Wind Farm and a development to construct a battery energy storage system (BESS). The battery will connect to the Transmission Network by nearly 13 kilometres of 132kV cable. | The maximum capacity of the DNA is 105 MVA being the summer thermal rating of the DNA. The maximum capacity of ElectraNet’s transmission network at the Transmission Network Connection Point under summer system normal operating conditions is 141 MVA and is associated with network thermal limitations. | ElectraNet Pty Limited ACN 094 482 416.
Powerlink | MacIntyre DNA | The DNA owned by Powerlink is comprised of: • the 330kV Tummaville Switching Station • the 330kV MacIntyre Intermediate Switching Station • the 330kV transmission line between Tummaville Switching Station and MacIntyre Intermediate Switching Station • cut-in-works and related assets. | The MacIntyre DNA connects the MacIntyre Wind Precinct, located south-west of Warwick, Queensland, to the Transmission Network via the MacIntyre Intermediate Switching Station and the Tummaville Switching Station. | In a Satisfactory Operating State, 1,826 MVA. A Runback Scheme will trip up to 750 MVA initially following a contingency. Current details of the MacIntyre DNA Capacity are available at Powerlink’s MacIntyre DNA webpage https://www.powerlink.com.au/dna-macintyre. The webpage also lists the capacity of generating plants and load facilities for Existing Connected Parties and Conditional Proponents, in relation to the MacIntyre DNA. | Queensland Electricity Transmission Corporation Limited ABN 82 078 849 233, trading as Powerlink, in its capacity as owner of the MacIntyre DNA.
Powerlink | Western Downs DNA | The DNA owned by Powerlink is comprised of: • DNA Component 1, made up of 48.5km of 275kV double circuit transmission line between Halys Substation to the Diamondy Switching and associated easements; and • DNA Component 2, made up of the 275kV Diamondy Switching Station and associated access easement. | The Western Downs DNA connects the Wambo Wind Farm, located near Jandowae, Queensland, to the Transmission Network via the Halys Substation. | As at 8 April 2025, under normal operating conditions, the Western Downs DNA has a limiting transfer capacity of 750 MVA. Current details of the Western Downs DNA capacity are available at Powerlink's Western Downs DNA webpage. The webpage also lists the capacity of generating plants and load facilities for Existing Connected Parties and Conditional Proponents, in relation to the Western Downs DNA. | Queensland Electricity Transmission Corporation Limited ABN 82 078 849 233, trading as Powerlink, in its capacity as owner of the Western Downs DNA.
GreenPoint Energy | Calala BESS DNA | The Calala BESS DNA owned by GreenPoint Energy is comprised of a 1.612 km 330 kV underground cable and associated 330 kV substation infrastructure. | The Calala BESS DNA owned by GreenPoint Energy connects the Calala BESS Substation to Transgrid’s Tamworth 330/132/11 kV Substation. | The Calala DNA has a rated capacity of 300 MW / 371 MVA. The Initial Users, Calala BESS A1 and Calala BESS A2, account for 250 MW, leaving nominal spare capacity of approximately 60 MVA, subject to upstream limitations at and beyond Tamworth Substation that are outside GreenPoint Energy’s control. | GP Energy (Cal) Common AssetCo Pty Ltd, (GreenPoint Energy, ABN 54 679 229 602)
ElectraNet | Whyalla Industrial Link DNA | The Whyalla Industrial Link DNA owned by ElectraNet is comprised of: • The Cultana East to Roopena 275 kV double circuit transmission line, and • The Roopena substation (capacity 275 kV). | The DNA connects the Cultana East and Roopena substations in Whyalla, South Australia. The Roopena Substation has an intended capacity of 275 kV. | The Roopena Substation has an intended capacity of 275 kV. The maximum capacity of the DNA will be constrained by upstream regulated network limitations. Any upgrade works may require new development, planning and environmental approvals, which will be the responsibility of the Service Applicant. The Roopena Substation can be expanded for a maximum of eight exits for customer connections. Three exits are currently constructed and available for new user connections at the published date of this policy. | ElectraNet (ABN 41 094 482 416). The DNA has been funded by the Pioneer User, which is the Minister for Energy and Mining for and on behalf of the Crown in Right of the State of South Australia, acting through the Department of Energy and Mining.