## TRR Summary
UST Removal, Validation, Environmental sampling and report | C-I-C
Bund Cleaning | C-I-C | Opex
Bund Integrity Check | C-I-C
Holding tank clean out and liquid disposal (150kL liquid, 10kL sludge) | C-I-C
GAC system fit out and annual carbon filter change (1 year) | C-I-C
Septic Tank Service | C-I-C
Puraceptor Service | C-I-C
Install Puraceptor | C-I-C
Install Hardstand (not transformer bund) | C-I-C | 5122679.4726
Instal Holding Tank Alarm | C-I-C
Cranbourne CBTS Drainage Reconfiguration | C-I-C
Hazelwood Drainage Reconfiguration | C-I-C
Install shut off valve | C-I-C
Decommission and remove holding tank | C-I-C
Install new/ temporary holding tank | C-I-C | 10269082.5175
15391761.9901
| RY28 | RY29 | RY30 | RY31 | RY32
Environmental | 1024535.8945 | 1024535.8945 | 1024535.8945 | 1024535.8945 | 1024535.8945
PRA-BlueSphere Estimate (Rework) | 2053816.5035 | 2053816.5035 | 2053816.5035 | 2053816.5035 | 2053816.5035

## Environmental Scope Items
|  |  | Total Cost for Environmental Scope Items | C-I-C
UST Removal, Validation, Environmental sampling and report
UST Removal, Validation, Environmental sampling and report | 1 | C-I-C | Cost provided by Consultant
Number of Sites |  | C-I-C | Assumptions: | C-I-C
C-I-C
Design | 5% | C-I-C
SPA Internal Costs | 5% | C-I-C
Sub-Contractor Indirect Costs | 5% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Bund Cleaning
Bund Cleaning | 1 | C-I-C | Cost provided by Consultant
Number of Sites | 1 | C-I-C | Assumptions: | C-I-C
|  | C-I-C |  | C-I-C
Design | 5% | C-I-C
SPA Internal Costs | 5% | C-I-C
Sub-Contractor Indirect Costs | 5% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Bund Integrity Check
Bund Integrity Check |  | C-I-C | Cost provided by Consultant
Number of Sites |  | C-I-C | Assumptions: | C-I-C
|  | C-I-C |  | C-I-C
Design | 5% | C-I-C
SPA Internal Costs | 5% | C-I-C
Sub-Contractor Indirect Costs | 5% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Holding tank clean out and liquid disposal (150kL liquid, 10kL sludge)
Holding tank clean out and liquid disposal (150kL liquid, 10kL sludge) |  | C-I-C | Cost provided by Consultant
Number of Sites |  | C-I-C | Assumptions: | C-I-C
|  | C-I-C |  | C-I-C
Design | 5% | C-I-C
SPA Internal Costs | 5% | C-I-C
Sub-Contractor Indirect Costs | 5% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
GAC system fit out and annual carbon filter change (1 year)
GAC system fit out and annual carbon filter change (1 year) |  | C-I-C | Cost provided by Consultant
Number of Sites |  | C-I-C | Assumptions: | C-I-C
C-I-C
Design | 5% | C-I-C
SPA Internal Costs | 5% | C-I-C
Sub-Contractor Indirect Costs | 5% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Septic Tank Service
Septic Tank Service |  | C-I-C | Cost provided by Consultant
Number of Sites |  | C-I-C | Assumptions: | C-I-C
|  | C-I-C |  | C-I-C
Design | 5% | C-I-C
SPA Internal Costs | 5% | C-I-C
Sub-Contractor Indirect Costs | 5% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Puraceptor Service
Septic Tank Service |  | C-I-C | Assumptions: | C-I-C
Number of Sites |  | C-I-C
C-I-C
Design | 5% | C-I-C
SPA Internal Costs | 5% | C-I-C
Sub-Contractor Indirect Costs | 5% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Install Puraceptor |  |  | Assumptions: | C-I-C
Install Puraceptor | 1 | C-I-C |  | C-I-C
Number of Sites |  | C-I-C | Price from Quote | C-I-C
|  | C-I-C | Price | C-I-C
Design | 15% | C-I-C | Price | C-I-C
SPA Internal Costs | 15% | C-I-C
Sub-Contractor Indirect Costs | 15% | C-I-C | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Install Hardstand (not transformer bund)
Install Hardstand |  | C-I-C | Assumptions: | C-I-C
Number of Sites |  | C-I-C
|  | C-I-C | C-I-C
Design | 15% | C-I-C
SPA Internal Costs | 15% | C-I-C
Sub-Contractor Indirect Costs | 15% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C

## Sheet1 (hidden)
66kV Feeder X & Y Protection Scheme "X" Prot Type Siemens 7SL87 & Y Prot GE Multilin L90 - Line Current Differential Relay
Materials
Materials for 66kV Feeder X & Y Protection Scheme, | 1 | Each | 82645.38 | 82645.38
Cabling
Secondary Cables for 66kV Feeder X & Y Protection Scheme | 1 | Each | 49152.0306 | 49152.0306
Earthing
Cubicle Earthing | 1 | Each | 1961.6918 | 1961.6918
Installation
Protection Cabinet Installation | 1 | Each | 29639.9252 | 29639.9252
Testing
System Pre-test | 64 | Hour | 271.91 | 17402.24
System Commission | 96 | Hour | 271.91 | 26103.36
206904.6275
Cost Structure for 66kV Bus Tie X & Y Protection Scheme, "X" Prot / "Y" Prot, Protection & control Panel Layout
Materials
Materials for 66kV Bus Tie X & Y Protection Scheme, "X" Prot P145 / "Y" Prot SEL 351-6, Protection & control Panel Layout (Drawing No.T14/119/51/2 rev A dated 04/06/08) | 1 | Each | 49760.1875 | 49760.1875
0
Cabling |  |  |  | 0
Secondary Cables for 66kV Bus Tie X & Y Protection Scheme, "X" Prot P145 / "Y" Prot SEL 351-6, Protection & control Panel Layout (Drawing No.T14/119/51/16 rev A dated 04/06/08) | 1 | Each | 29639.9252 | 29639.9252
0
Earthing |  |  |  | 0
Install | 4 | Each | 1453.105 | 5812.42
0
Installation |  |  |  | 0
Labour | 1 | Each | 8518.4 | 8518.4
0
Testing |  |  |  | 0
Tester Field Services - Secondary Tester NSG PD | 48 | Hour | 271.91 | 13051.68
Commissioning | 64 | Hour | 271.91 | 17402.24
124184.8527
Anti-Islanding Scheme Based on SMTS T2/752/786/2 | 0 |  | 0 | 0
| 0 |  | 0 | 0
Materials | 0 |  | 0 | 0
Material Anti-Islanding Scheme Based on SMTS T2/752/786/2 | 1 | Each | 42209.3125 | 42209.3125
| 0 |  | 0 | 0
Installation | 0 |  | 0 | 0
Prot Cabinet Installation | 1 | Each | 29639.9252 | 29639.9252
| 0 |  | 0 | 0
Cabling | 0 |  | 0 | 0
| 0 |  | 0 | 0
Secondary Cabling Anti-Islanding Scheme Based on SMTS T2/752/786/14 | 1 | Each | 20833.223 | 20833.223
| 0 |  | 0 | 0
Earthing | 0 |  | 0 | 0
Cubicle Earthing | 1 | Each | 1453.105 | 1453.105
| 0 |  | 0 | 0
Testing | 0 |  | 0 | 0
Anti-Islanding Protection Testing | 1 | Each | 19577.52 | 19577.52
| 0 |  | 0 | 0
577916.1026 | 0 |  | 0 | 113713.0857
Protection Panel - 66kV Cap Bank X&Y Protection & Control Cubicle - T2/319/359/2 | 0 |  | 0 | 0
| 0 |  | 0 | 0
| 0 |  | 0 | 0
Materials | 0 |  | 0 | 0
Materials Only - 66kV Cap Bank Protection & Control Scheme | 1 | Each | 81978.3125 | 81978.3125
| 0 |  | 0 | 0
Cabling | 0 |  | 0 | 0
| 0 |  | 0 | 0
Secondary Cables - 66kV Cap Bank Prot & Ctrl - T2/319/359/37 | 1 | Each | 23450.8608 | 23450.8608
| 0 |  | 0 | 0
Earthing | 0 |  | 0 | 0
Cadweld to Steelwork | 1 | Each | 109.9691 | 109.9691
Conductor - 40 x 4mm Copper Flat Bar, Alloy C11000, half hard, full radius complying with AS/NZS 1567 | 1 | Metre | 44 | 44
| 0 |  | 0 | 0
Installation | 0 |  | 0 | 0
Installation of Cubicles into Modular ZSS Buildings | 1 | Each | 5135 | 5135
| 0 |  | 0 | 0
Testing | 0 |  | 0 | 0
Site Testing | 64 | Hour | 271.91 | 17402.24
Commissioning | 24 | Hour | 271.91 | 6525.84
134646.2224
Materials - 220kV CB Management (7VK87 + Multilin C60) Scheme | 1 | Each | 52874.95 | 52874.95
| 0 |  | 0 | 0
Cabling | 0 |  | 0 | 0
Secondary Cables - 220kV 1 x CB Management Transformer Protection Panel | 1 | Each | 24985.8615 | 24985.8615
| 0 |  | 0 | 0
Earthing | 0 |  | 0 | 0
Cadweld - Joint / Shot | 1 | Set | 109.9691 | 109.9691
Conductor - 40 x 4mm Copper Flat Bar, Alloy C11000, half hard, full radius complying with AS/NZS 1567 | 1 | Metre | 44 | 44
| 0 |  | 0 | 0
Installation | 1 |  | 8135 | 8135
Field Services - Secondary NSG PD |  |  |  | 0
Tray Truck - 3.5 tonne, 4m tray, incl travel 75kms |  |  |  | 0
| 0 |  | 0 | 0
Testing | 0 |  | 0 | 0
Technical Services - Prot & Measurement NSG PD | 96 | Hour | 271.91 | 26103.36
| 0 |  | 0 | 0
577916.1026 | 0 |  | 0 | 112253.1406

## PRA-BlueSphere Estimate
Instal Holding Tank Alarm |  |  | Total Cost | 10269082.5175
Install Hardstand |  | C-I-C
Number of Sites |  | C-I-C | Assumptions: This is a high level scope
|  | C-I-C | Install a holding tank alarm
Design | 15% | C-I-C | Connect to secondary system
SPA Internal Costs | 15% | C-I-C
Sub-Contractor Indirect Costs | 15% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Cranbourne CBTS Drainage Reconfiguration
Cranbourne CBTS Drainage Reconfiguration | 1 | C-I-C | Assumptions: This is a high level scope
|  | C-I-C | Service and repair leaking transformers
Design | 25% | C-I-C | Clean bund surfaces and check bund integrity;
SPA Internal Costs | 15% | C-I-C | Clean out oil and sediment from the puraceptor, and clean internal filters
Sub-Contractor Indirect Costs | 15% | C-I-C | Review, reconfigure and update drainage at the site to rectify apparent design limitations resulting in overflow events.
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Hazelwood Drainage Reconfiguration
Hazelwood CBTS Drainage Reconfiguration | 1 | C-I-C | Assumptions: This is a high level scope
|  | C-I-C | Service and repair leaking transformers
Design | 25% | C-I-C | Clean bund surfaces and check bund integrity;
SPA Internal Costs | 15% | C-I-C | Clean out oil and sediment from the puraceptor, and clean internal filters
Sub-Contractor Indirect Costs | 15% | C-I-C | Reconfigure and resolve drainage from transformer bunds and holding tank areas;
|  | C-I-C | Installation of granulated activated carbon (GAC) scrubbers to treat filtered water exiting a puraceptor.
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Install shut off valve
Install shut off valve |  | C-I-C | Assumptions:
Number of Sites |  | C-I-C | Install a shut off valve
|  | C-I-C | Testing & Commissoning
Design | 15% | C-I-C
SPA Internal Costs | 15% | C-I-C
Sub-Contractor Indirect Costs | 15% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Decommission and remove holding tank
Decommission and remove holding tank |  | C-I-C | Assumptions:
Number of Sites |  | C-I-C | Decommission and removal of existing holding tank
|  | C-I-C | Dispose of existing holding tank
Design | 15% | C-I-C
SPA Internal Costs | 15% | C-I-C
Sub-Contractor Indirect Costs | 15% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C
Install new/ temporary holding tank
Install new/ temporary holding tank |  | C-I-C | Assumptions:
Number of Sites |  | C-I-C | Install new/ temporary holding tank
|  | C-I-C | Drain and clean holding tank
Design | 15% | C-I-C | Periodically inspect the existing holding tank to confirm that it remains functional
SPA Internal Costs | 15% | C-I-C
Sub-Contractor Indirect Costs | 15% | C-I-C
C-I-C
Nominal Risk Allowance | 7.5% | C-I-C
DIRECT COSTS SUB-TOTAL |  | C-I-C

## Master All_TRR_TS
Site Details | [11 empty] | Status Tracking |  |  |  | Knowledge Base Relevant documentation | [9 empty] | Likelihood of Contamination (drivers of likelihood rating highlighted in bold) | [7 empty] | Oil Filled Equipment | [10 empty] | Site Hazards | [18 empty] | Consequence of Contamination | [10 empty] | Duty to Manage |  |  | Duty to Notify |  | Future Actions | [7 empty] | Knowledge Base - Relevant Documentation |  |  |  | Oil Filled Equipment | [5 empty] | Historical Parameters - Retained for Information Purposes Only
[34 empty] | Note: Numbers in red reflect sites where controls are not applicable or not known |  |  |  |  | Note: Where there is a leak score above 2.9, the maximum of the leak, and bunding rating is adopted (i.e. what is the measure of control if there is a leak). If below 2.9 the leak score is adopted (i.e. there must be a leak for there to be a risk). | [24 empty] | Impact Factor |  | Drivers | [28 empty] | Note: Where there is a leak score above 2.9, the maximum of the leak, and bunding rating is adopted (i.e. what is the measure of control if there is a leak). If below 2.9 the leak score is adopted (i.e. there must be a leak for there to be a risk). | [37 empty] | Denotes cost not assigned to item | Denotes cost pending
[25 empty] | 1 Low - 5 High | Legacy / Known Issues | [5 empty] | Current Activities |  |  | 1 Low - 5 High | 1 Low - 5 High | 1 Low - 5 High | [26 empty] | 80% |  | 20% | [24 empty] | Note: Numbers in red reflect sites where controls are not applicable or not known
Site Type | Site Name | Site Number | Region | Site Address | Special Parcel Identifier | Latitude | Longitude | Site Owner | Site Occupier | Property Type | Property Status | Last AusNet Site Environmental Assessment Date | Added to Enablon / Sharepoint | AusNet: Date Last Assessed | AusNet: Audit Lead | Environmental Site Inspection | PSI: Preliminary Site Investigation (or initial consulting reports) | DSI: Detailed Site Investigation | Site Environmental Management Plan | Site Specific Risk Assessment or Audit | EPA Report/Investigation | Relevant Documents: Soft Copy | Relevant Documents: Hard Copy | Last Enviromental Assessment Date | Confidence Factor | Asset Age - oldest asset (years) | Past Incidents | Former Land Uses (i.e. on-site landfill & historic filling activities) and existing impacts | Status of Existing Controls relating to former land uses and existing issues | Status of existing controls relating to former land uses - Comments | Infrastructure Risk Classicatiion (GeoEng 2002) - Prior to Upgrade program | Potential Contaminating Activities (i.e. ASTs, USTs, transformers, generators etc.) Needs correcting for other land uses also | Potential Contaminating Activities - Comments | 1) No. Of Transformers or other oil filled equipment | 2) Oil Leak Condition | 3) Bunding Rating | 3b) Oil/water separator and shut off valve | Control Score (Max of bunding and oil/water score) | DB: Oil Filled Equipment Score | Status of Existing Controls relating to current activities | EDPR:Oil Filled Equipment Score | Comment | Likelihood of Contamination (Adopt highest) | PCB Oil (> LOR) | Mineral and/or hydraulic oil | Batteries | Fuel Storage / Generators | Chemicals (i.e. herbicides, pesticides, solvents etc.) | SF6 Gas Cylinders | LPG Gas Assets / Cylinders | Stockpiles | On-site Septic Systems | UST | Landfilling | Asbestos (in soil) | On-Site Containment | Default | Mercury | NAPL | HIL/HSL Exceedances | Lead Paint | Deluge Systems | Firefighting Foams | Environmental Impacts | Human Health and Wellbeing | Surrounding Land Users | Off-site Drainage Discharge (Y/N) | Surrounding Groundwater Users | Existing GW Users within 500m | Surrounding Ecosystems (currently from site factor but can be refined based on each location) | Inherent Consequence of Contamination | Updated Risk (based on findings from DtM and WQIP programs completed to date) | Previous Risk Assessment (All factors) MANUAL INPUT Reference Purposes Only | Column1 | Management Driver | Comments | Potential Notification Trigger | Notification Driver | Potential Stockpile Sampling | Potential Drainage Assessment | Recommended Actions | Upgrades | Upgrade - Comments | Rebuild | Rebuild - Comments | Further Work Required | Site Environmental Management Plan2 | Soft Copy Documents | Hard copy documents | EPA | 1) No. Of Transformers or other oil filled equipment | 2) Oil Leak Condition | 3) Bunding Rating | 3b) Oil/water separator and shut off valve | Site Condition Score | Site Condition Score (Rounded) LIKELIHOOD | 4) Current Use of Surrounding Land | 5) Site Factor and Waterways | Relative Criticality Score (Average) | Relative Criticality Score (Rounded) CONSEQUENCE | LAND CONTAMINATION RISK RATING | ZSS RATING 2018 | Other notes | Transformer details (Red < 1990) Station Service | Incidents | Enablon/IMS Incidents | Site Activity | SF6 sources | Gas cylinders | Dust | Spoil Stockpiles | Noise | Visual | Odours | Diesel Generators | Waste | Weeds | Batteries | Chemicals | CO2 emissions | Site information (from 2002) | Buildings 2002 | PROJECTS (From Electricity Networks Works Program FY18-FY22) | Asset Type | Region | Assessed by | Site Environmental Risk Rating | Condition Assessment (AusNet, Nov 2024) | Condition Assessment (AusNet, Nov 2024) | Remote site? (how to define) - outside of Greater Melbourne or regional centre | Step 1: Validate Risk Ratings (is risk being driven by lack of information) | Step 2: Identify the risk drivers that are resulting in the risk ratings (for example, condition of oil filled equipment, presence/ absence/ type of oil filled equipment bunding, type of technology being used) | Step 3: Possible upgrades/ improvements to remove risk drivers/ reduce risk rating, description | UST removal, validation, environmental sampling and report. | Bund cleaning (per site) | Bund integrity check (per site) | Transformer/ circuit breaker service, leak repair. Not Calculating. | Holding tank clean out and liquid disposal (150kL liquid, 10kL sludge) | GAC system fit out and annual carbon filter change (1 year). | Septic tank service | Replace bunds from brick to concrete | Decommission and remove holding tank | Install new/ temporary holding tank | Install shut off valve. | Hardstand install (not transformer bund) | Drainage reconfiguration | Puraceptor service | Containnated Soil | Holding tank alarm | Install puraceptor | Cost (approx, ex GST)
Depot, Office and Warehouse Storage | Alexandra Depot | TBC Alex Depot |  | 2 Bayley St, Alexandra, Victoria 3714 | 1\LP26252 | -37.191 | 145.7078 | AusNet Services | Downer | Leased | Active | DOWNER REMOVE | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 0 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 Rare: E | N/A | Site located on farmland. Shared site AST/APA. Cattle onsite around compound. | N/A | No |  | City Gate | No | Yes | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC
City Gate | Allansford City Gate | ALLA |  | Government Rd, Allansford, Victoria 3277 | None | -38.3855 | 142.5908 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-16 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | Yes - Small Volume | None | None | [5 empty] | No | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC
Terminal Station | Altona TS (ATS) | TS-ATSX | Central | 130 Cherry Lane, Laverton North, Victoria, 3026 | 1\TP758680 | -37.8396 | 144.7896 | TBC | TBC | Freehold | Active | 2020-06-19 | Yes / Yes | 2020-06-19 | A Ryan | Yes | Yes |  | AusNet, Transmission Sites, Portfolio EMP |  |  |  | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 5 | 13 |  | 3 |  | Richmond material transported to site. Also stockpiles on northern boundary of site - contamination status unknown. | Medium Risk | 5 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume | Yes - LPG | Spoil / Waste | Yes - Septic |  |  |  |  | No | [6 empty] | 4 | 4 | 4 | Yes | 4 | No | 2 | 4 | C | D | No | Potential contaminating activities. |  | #REF! | Operational areas are sealed and stockpiles comprise clean fill imported from Richmond. Therefore no Duty to Notify. | Y | Y | PSI with limited soil sampling program. GME from existing wells. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP |  | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | C2 | Enviro - one above ground stormwater isolation valve in place | N | Confidence 5/5. Soil classification works completed in 2022 and 2023. | Risk driven by current chemicals and storage of materials on site (results in a higher consequence of contamination). Bund is fully compliant and sealed. Consequence of contamination is high - mainly driven by proximity to environmental receptors. | 1. Site inspection to confirm bund and leak status, storage of chemicals and other potential environmental hazards. | [17 empty] | C-I-C
City Gate | Ararat City Gate | ARAR |  | 5818 Pyrenees Hwy, Ararat VIC 3377 | None | -37.2601 | 142.9661 | TBC | TBC | TBC | TBC | Uploaded 14/03 | Yes / Yes | 2021-02-25 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | 2.5 | 3 | 3 Rare: D | N/A | Spoon drain crossing front of compound on roadway. Shared compound AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Ex Gas Works Site | Ararat Former Gas Works Site | TBC - Ararat |  | 26-28 Grano Street, Ararat, Victoria, 3377 | 2~55\PP5017 & 3~55\PP5017 | -37.2801 | 142.9469 | AusNet Services |  |  |  | Documentation to Dan/Will. Not in Sharepoint list | assessment complete - to do |  |  | Yes |  |  | AusNet - Ararat Site Management Plan (SMP) | Yes | Pollution Abatement Notice / Clean Up Notice and associated correspondence (2006) | Coffey - Environmental Audit Report: Former Ararat Gasworks (2012) |  |  | 5 |  |  | 5 | 2 | CUTEP Complete |  | 1 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | Oil Default | [11 empty] | No | [6 empty] | 3 | 2 | [5 empty] | 3 | C | D | Yes |  |  | #REF! | [9 empty] | AusNet - Ararat Site Management Plan (SMP) | Coffey - Environmental Audit Report: Former Ararat Gasworks (2012) |  | Pollution Abatement Notice / Clean Up Notice and associated correspondence (2006) | 1 | 1 | 2 | 3 | 1 | 1 | 2 | 4 | 3 | 3 | 3 Rare: D | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Comms Site | Arthurs Seat Comms Site (ASET) | TC-ASETXXXX |  | 27 Steane Ave, Dromana, Victoria 3926 | 27\LP13438 | -38.3543 | 144.9509 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-10 | A Ryan | Yes | [8 empty] | 2 | [6 empty] | 2 |  |  | 3 | 4 | 5 | 5 | 4 | 5 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 5 |  |  |  | 4 | 3 | C | D | Yes |  |  | #REF! | [13 empty] | 2 | 5 | 1 | 3 | 5 | 5 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Auburn Laboratory and Office | TBC Auburn Depot |  | 28 Raglan Road, Auburn NSW 2144 | None | -33.8739 | 151.0216 | TBC | TBC | Leased | Active | Interstate | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  |  | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 5 | 1 | 1 | 1 | 2 | 4 | 3 | 3 | 3 Rare: D | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | Yes | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Avalon City Gate | AVAL |  | Beach Rd, Avalon VIC 3212 | None | -38.0173 | 144.4759 | TBC | TBC | Licensed | Active | Done | Yes / Yes | 2020-11-16 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | Check | 4 | 4 | 5 | 5 | 5 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | A | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 3 | 1 | 1 | 4 | 1 | 2.5 | 3 | 3 Rare: D | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Avoca City Gate | AVOC |  | Greenhill Ct Bulleen VIC 3105 | None | -37.7685 | 145.0879 | TBC | TBC | TBC | TBC | Complete | Yes / Yes | 2021-04-28 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | Check | 3 | 4 | 5 | 5 | 4 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | [5 empty] | 2 | D | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 1 | 2.5 | 3 | 3 Rare: D | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Bacchus Marsh City Gate | BACC |  | Rowsley Station Road, Bacchus Marsh, Victoria, 3340 | None | -37.7119 | 144.4263 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-18 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 3 | 5 | 4 | 5 | 5 | 5 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Odour: possible natural gas. CO2 emissions from Water Bath Heater Shared site AusNet Services and APA. Water tank onsite to capture rain water for heater top up Site located in Parkland beside freeway ramp. | N/A | No |  | City Gate | No | No | No | No | No | No | Yes | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Bairnsdale Depot | WH-0010 |  | 28 McMillan Street (8 Meringo Place), Bairnsdale VIC 3875 | 1\PS442908 | -37.8227 | 147.6518 | Downer | Downer | Leased | Active | Sharepoint updated. Downer received lease - don't do | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | B | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 4 | 2 | 1 | 1 | 4 | 1 | 2.5 | 3 | 3 Rare: D | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Switchyard | Bairnsdale Switching Station (BDSS) | TBC SS-BDSS |  | Princes Highway/Mittons Lane (25 Power Station Road), Bairnsdale, Victoria 3875 | 1\PS445149 | -37.8446 | 147.5645 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-08-27 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 3 | Oil containing equipment and batteries | 1 | 1 | 1 | 3 | 3 | 1 | 1 |  | Fully compliant sealed bund and basic oil/water separator - no shut off valve | 3 | None | None | Yes | None | None | Yes - Small Volume | Yes - LPG | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Sub Station | Bairnsdale ZSS (BDL) | DS-BDL | East | 125 Great Alpine Road, Lucknow, Victoria, 3875 | 1\TP245562 & 1\TP246430 | -37.8084 | 147.6482 | TBC | TBC | Freehold | Active | Uploaded 17/03 | Yes / Yes | 2020-12-31 | M Snell | Yes | WSP(2023) |  | AusNet, Distribution Sites, Portfolio EMP |  |  | PSI-WSP (2023), Surface water sampling report-WSP (2024) |  | 2024-01-01 | 5 | 5 |  | 4 | 3 | Concreted over former leaks (2020), oil coming back up |  | 5 | Oil containing equipment and batteries, AusNet has indicated that historical leakage is known to have occurred in 2020 within the transformer area prior to the construction of concrete bunding beneath transformers (previously gravel). It is understood that the contaminated material may have been left in situ beneath the current hardstand area. | 6 | 4 | 4 | 5 | 5 | 5 | 1 |  | Brick bund with gravel floor | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | None | None | None | None |  | None |  |  | No |  | None |  |  |  |  | 3 | 2 | 3 | Yes |  | No | 3 | 3 | C | E | Yes | Historical leakage | Investigate leakage and condition of hardstand, likely needs targeted sampling in accordance with Duty to Manage. No Duty to Notify | #REF! | Historical leakages, concreted over former leaks, oil coming back up, however, as sealed exposure not likely, no Duty to Notify |  | Y | PSI with limited soil sampling program. | Yes | Stage 2 - due 2018 |  |  |  | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Ballan City Gate | BALN |  | Denholmes Rd, Ballan VIC 3342 | None | -37.6056 | 144.2239 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2021-03-02 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 3 | 4 | 4 | 5 | 5 | 5 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 4 |  |  |  |  | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1.5 | 2 | 2 Rare: E | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Ballarat City Gate | BALR |  | Clarks Road, Ballarat, Victoria 3353 | None | -37.5677 | 143.9328 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-18 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | Check | 5 | 1 | 1 | 1 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 2 | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1.5 | 2 | 2 Rare: E | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Ballarat TS (BATS) | TS-BATS | West | yackandandah Road, Dederang, Victoria 3691 (0.5kms from Kiewa Valley) | None | -37.5667 | 143.9217 | TBC | TBC | Freehold | Active | 2020-07-14 | Yes / Yes | 2020-07-14 | A Ryan | Yes | Yes | [5 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 6 |  |  |  |  | Medium Risk | 5 | Oil filled equipment plus battery farm | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve, batteries in containment system | 1 | >10 kg or >50 mg/kg | Large | Yes | None | Default Chemicals |  |  | Spoil / Waste | [5 empty] | No | [6 empty] | 4 | 4 | 4 |  |  |  | 2 | 4 | C | C | No |  |  | #REF! | Stockpiles | Y | [9 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 1 | 2.5 | 3 | 3 Rare: D | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | C3 | Enviro - one above ground system, was an issue of ground water seeping into holding tank, stormwater isolation valves fitted | N | Confidence 3/5. Cell DZ20L: Is groundwater shallow or is it perched around the holding tank? | Risk driven by presence of oil filled equipment and battery farm. Site has fully compliant sealed bund with puraceptor oil/water separator + shut off valve, batteries in containment system. Site inspection photos show staining under transformers. Stockpiles present on site. It is unknown if erosion controls need to be applied to the stockpiles. | 1. Replace the above ground holding tank that is subject to leaks (per cell DZ20). Includes decommission, removal and installation of new holding tank. 2. Confirm the contamination status of stockpiles of soil on site as indicated in the PRA. Apply erosion controls if required, confirm origin of materials. 3. Service transformers and repair leaks. 4. Decommission and remove damaged holding tank. |  |  |  | x |  |  |  |  | C-I-C | C-I-C |  |  |  |  | C-I-C |  |  | C-I-C
Comms Site | Bamawn Comms Site (BAMA) | TC-BAMAXXXX |  | PART 623 PRAIRIE-ROCHESTER ROAD, BAMAWM, VICTORIA 3561 | None | -36.2991 | 144.6198 | TBC | TBC | Leased | In Progress | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 4 | 3 | 4 | 5 | 5 | 4 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 4 |  |  |  | 1 | 2 | A | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | 2.5 | 3 | 3 Rare: D | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Comms Site | Banimboola Comms Site (BANM) | TC-BANMXXXX |  | Dartmouth Road, Dartmouth, VIC, 3701 (licenced site – ground lease from GMW) | TBC | -36.5353 | 147.5039 | TBC | TBC | TBC | Active | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | None | None | None | None | None | None | [5 empty] | No | [6 empty] | 1 | 1 | 2 |  |  |  | 1 | 1 | B | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 1 | 2.5 | 3 | 3 Rare: D | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | Yes | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Bannockburn City Gate | BANN |  | Fyansford-Gheringhap Rd Victoria | None | -38.0887 | 144.2452 | TBC | TBC | TBC | TBC | 2021-06-10 | Yes / Yes | 2021-06-10 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 3 | 4 | 4 | 5 | 5 | 5 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | [5 empty] | 2 | A | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 1 | 3 | 3 | 3 Rare: D | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Sub Station | Barnawartha ZSS (BWA) | DS-BWA | North | Baxter/Whelans Rd, Barnawartha VIC 3688 | 1\PS538251 | -36.0738 | 146.7169 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-08-13 | CJ Wilson | Yes | [8 empty] | 2 | 4 | [5 empty] | 4 |  | 1 | 1 | 1 | 2 | 2 | 1 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume |  | Spoil / Waste | [5 empty] | No | [6 empty] | 3 | 2 | 2 |  |  |  | 2 | 3 | C | D | No |  |  | #REF! |  | Y | [11 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Shared site AST/APA Odour: Possible natural gas via leakage Land adjacent to compound for sale for future residence | N/A | No |  | City Gate | No | No | No | No | No | No | Yes | No | No | Yes | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Sub Station | Bayswater ZSS (BWR) | DS-BWR | Central | 365-371 Bayswater Road/Glenpark Road, Bayswater, Victoria 3153 | 1\TP532480 | -37.8345 | 145.2719 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-25 | A Ryan | Yes | WSP(2023) | [7 empty] | 3 | 52 |  | 3 | 3 |  |  | 4 |  | 7 | 4 | 1 | 1 | 1 | 3 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None |  | None | Yes - Septic | Yes |  |  |  | No | [6 empty] | 3 | 4 | 5 |  | 3 | Yes | 2 | 4 | C | C | Yes |  |  | #REF! |  |  |  |  | Yes | Stage 1 - due 2017 | [7 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 2 | 3 | 3 | 3 Rare: D | N/A | Shared site AST/APA Odour: Possible natural gas via leakage | N/A | No |  | City Gate | No | No | No | No | No | No | Yes | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Beaconsfield Depot | WH-0011 |  | cnr Beaconsfield Avenue and Station Road, Beaconsfield, Victoria 3807 | 1\TP441813 | -38.0514 | 145.3711 | AusNet Services Electricity Services Pty Ltd | Downer | Freehold | Active | UPLOAD 20/03 | Yes / Yes | 2021-02-16 | Jenkins and Emily Utting | Yes | [8 empty] | 2 | [6 empty] | 3 | Oil containing equipment and UST | 1 | 1 | 1 | 3 | 3 | 1 | 1 |  | Fully compliant sealed bund with weekly fuel readings and annual integrity testing | 3 | None | Oil Default | None | Fuel Default | None | Yes - Small Volume | Yes - LPG | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 5 |  |  |  |  | 4 | C | C | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 1 | 1 | 1 | 4 | 1 | 2.5 | 3 | 3 Rare: D | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Comms Site | Beech Forest Comms Site (BEEF) | TC-BEEFXXXX |  | 37 Beech Forrest (Lavers Hill) Road, Beech Forrest, Victoria 3237 | 1\TP561506 | -38.6067 | 143.5643 | TBC | TBC | Freehold | Active | Done (Name in Enablon not Environ Site Audit on end) | Yes / Yes | 2020-11-10 | A Ryan | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 0 | 2 | 4 | 5 | 5 | 3 | 2 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 1 | 1.5 | 2 | 2 Rare: E | N/A | Shared site AST/APA Land opposite to compound for sale for future residence | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | Yes | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Sub Station | Belgrave ZSS (BGE) | DS-BGE | Central | 132 Belgrave Hallam Road/Temple Road, Belgrave, Victoria 3160 | 1\TP758228 | -37.9301 | 145.361 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-25 | A Ryan | Yes | [8 empty] | 2 | 37 | [5 empty] | 3 |  | 3 | 4 | 4 | 3 | 4 | 4 | 1 |  | Brick bund with gravel floor and basic oil/water separator - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 2 | 4 | C | C | Yes |  |  | #REF! |  |  |  |  | Yes | Stage 3 - due 2020-2023 | [7 empty] | 2 | 1 | 2 | 3 | 1 | 1 | 2 | 1 | 1.5 | 2 | 2 Rare: E | N/A | Single occupant AST only | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Benalla Depot | WH-0008 |  | 84-88 Samaria Road, Benalla, Victoria 3672 | PC170259 | -36.5589 | 145.9949 | AusNet Services Electricity Services Pty Ltd | Downer | Freehold | Active | UPLOAD 20/03. Zinfra, AST and Downer on site. | Yes / Yes | 2021-02-17 | J Smith | Yes | [8 empty] | 2 |  | Small area of scorched ground due to angle grinder sparks and oily substance identified on roadway in 2020 |  |  |  |  | 3 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Hardstand, drainage and some bunding | 5 | None | Oil Default | None | None | <100 L | Yes - Small Volume | Yes - LPG | None | None |  |  |  |  | No | [6 empty] | 3 | 3 | 4 |  |  |  |  | 3 | C | D | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Shared site AST/APA | N/A | No |  | City Gate | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Sub Station | Benalla ZSS (BN) | DS-BNX | North | Cnr Midland Highway and Baddaginnie-Benalla Road, Benalla, Victoria 3673 | 1\TP318441 | -36.5553 | 145.9617 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-07-17 | CJ Wilson | Yes | [5 empty] | Jacobs 2021 |  |  | 2 | 45 | [5 empty] | 2 |  | 3 | 4 | 4 | 5 | 5 | 5 | 1 |  | Brick bund with gravel floor | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 5 |  |  |  | 1 | 3 | D | D | Yes | Hydrocarbons above management limits, no HIL D exceedences |  | No | No exceedences of HIL D |  |  | PSI and soil classification prior to commencement. Remediation and validation to be undertaken as part of site upgrades. | Yes | Stage 3 - due 2020-2023 |  |  |  |  | Jacobs 2021 |  |  | 1 | 1 | 0 | 5 | 1 | 1 | 5 | 1 | 3 | 3 | 3 Rare: D | N/A | Shared site AST/APA Odour: Possible natural gas via leakage. Noise: Heater burners Site located very close to housing New larger water bath heater installed Dec 2019 which may need to have noise testing conducted for noise of burner in the early hours of night/morning. | N/A | No |  | City Gate | No | No | No | No | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Bendigo City Gate | BEND |  | Government Road, Bendigo, Victoria 3550 | None | -36.7519 | 144.2647 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-17 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 2 |  |  |  | 4 | 2 | C | E | No |  |  | #REF! | [13 empty] | 2 | 1 | 2 | 3 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Odour: possible natural gas. | N/A | No |  | City Gate | No | No | No | No | No | No | Yes | No | No | No | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Bendigo TS (BETS) | TS-BETS | West | 111-113 Allingham Street, Bendigo (Golden Square), Victoria 3550 | 238~C\PP3473A | -36.7839 | 144.2528 | AusNet Services | Zinfra | Freehold | Active | Done | Yes / Yes | 2020-09-08 | CJ Wilson | Yes | Yes | [5 empty] | Geo-Eng - Environmental Risk Assessment (1996). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 8 |  |  |  | Historic report from 1996 indicates presence of low-level contaminated soil | Medium Risk | 5 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1 | <10 kg or <50 mg/kg | Large | Yes | Fuel Default | None | Yes - Small Volume |  | Spoil / Waste | [5 empty] | No | [6 empty] | 4 | 4 | 2 |  |  |  | 2 | 4 | B | C | No |  |  | #REF! | Stockpiles | Y | [9 empty] | Geo-Eng - Environmental Risk Assessment (1996). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 2 | 3 | 1 | 1 | 5 | 1 | 3 | 3 | 3 Rare: D | N/A | Odour: possible natural gas. Shared site AusNet Services and APA. Site located next to car dealership and residences. | N/A | No |  | City Gate | No | No | No | No | No | No | Yes | No | No | Yes | Yes | No | Yes |  |  |  | N/A | West | TBC | TBC | C1 | Enviro - one above ground system, stormwater isolation valves fitted | N | Confidence 3/5. No recent environmental information | Risk primarily driven by oil storage and presence of stockpiles on site. Sealed brick bund (noted in 2020 site inspection notes) with puraceptor oil/water separator + shut off valve. Contamination status of stockpiles unknown. It is unknown if erosion controls need to be applied to the stockpiles. | 1. Site inspection to confirm status of items driving risk. 3. Confirm the contamination status of stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. | [7 empty] | C-I-C | [6 empty] | C-I-C |  |  | C-I-C
Sub Station | Berwick Nth ZSS (BWN) | DS-BWN | Central | Old Coach Rd, Berwick VIC 3806 | 1\TP142375 | -38.0137 | 145.3479 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-05-26 | A Ryan | Yes | [8 empty] | 2 | 20 | [5 empty] | 3 |  | 1 | 1 | 4 | 2 | 4 | 2 | 1 |  | Brick bund with gravel floor and basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 4 | None | Large | Yes | None | Default Chemicals | Yes - Small Volume |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 2 |  |  |  | 2 | 4 | D | C | Yes |  |  | #REF! | [13 empty] | 2 | 1 | 2 | 3 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Comms Site | Big Hill/Mt Herbert Comms Site (MTHB) | TC-BIGHXXXX |  | Big Hill Rd/Mt Herbert Calder Hwy, Kangaroo Flat VIC 3555 | 1\TP441116 | -36.8077 | 144.2548 | TBC | TBC | Freehold | ACTIVE | Done - Gas site B Scott divestment options? | Yes / Yes | 2020-11-12 | A Ryan | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 4 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Comms Site | Blackwarry Comms Site (BLAK) | TC-BLAKXXXX |  | Grand Ridge Road, Blackwarry (Balook), Victoria 3844 | 1\TP235285 | -38.4059 | 146.6386 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-08-24 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 4 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 2 |  |  |  | 4 | 2 | C | E | No |  |  | #REF! | [13 empty] | Check | 4 | 1 | 1 | 4 | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Sub Station | Boronia ZSS (BRA) | DS-BRA | Central | 7 Wadhurst Drive, Boronia, Victoria, 3155 | 1\TP144704 & 1\TP562609 | -37.8655 | 145.2537 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-25 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 22 | [5 empty] | 4 |  | 3 | 2 | 4 | 2 | 4 | 3 | 1 |  | Brick bund with gravel floor and basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None | None | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 5 | No | 5 | No | 3 | 4 | C | C | Yes | Potential contaminating activities. |  | #REF! | NA |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Sub Station | Bright ZSS (BRT) | DS-BRT | North | 40 Hawthorne Lane/Mountbatten Avenue, Bright, Victoria 3741 | 8B~C\PP2227 | -36.7262 | 146.9701 | TBC | TBC | Freehold | Active | 2020-07-15 | Yes / Yes | 2020-07-17 | CJ Wilson | Yes | [8 empty] | 2 | 11 | [5 empty] | 2 |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1 | <10 kg or <50 mg/kg | None | Yes | None | None |  |  | None | [5 empty] | No | [6 empty] | 2 | 2 | 5 |  |  |  | 1 | 3 | B | D | No |  |  | #REF! |  |  |  |  | Yes | Stage 1 - due 2017 | [7 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Brock Industrial Drive | WH-0014 |  | 30 Melba Ave, Lilydale, Victoria | 14\PS604433 | -37.7611 | 145.347 | External Land Owner- Leased Facility | TBC | Leased | Active | Uploaded 14/03 | Yes / Yes | 2021-02-10 | Mark Dyer | Yes | [8 empty] | 2 | [6 empty] | 1 |  | 1 | 1 | 4 | 5 | 5 | 3 | 4 |  |  | 5 | None | None | None | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 1 | 1 | 3 |  |  |  | 1 | 1 | B | E | No |  |  | #REF! | [13 empty] | 7 | 4 | 1 | 2 | 4 | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Brooklyn TS (BLTS) | TS-BLTS | Central | 70-84 Kyle Road, Altona North, Victoria, 3025 | 1\TP966322, 3\TP966323, 1\TP966324, 2\TP966324, 1\TP966325 & part 2\TP966323 | -37.8256 | 144.8601 | TBC | TBC | Freehold | Active | 2020-05-18 | Yes / Yes | 2020-05-18 | A Ryan | Yes | WSP (2023) |  | AusNet, Transmission Sites, Portfolio EMP |  |  | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021), PSI-WSP (2023) | Groundwater environmental appraisal (2005), Drainage outfall rehab report (2006). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) | 2024-01-01 | 5 | 8 | Potential asbestos pipe encountered during excavation in 2019. Historic spills | 5 | 4 | Pockets of asbestos in ground from former factory. Stockpiles - mostly removed. | Medium Risk | 5 | Heavy surface staining beneath the transformers (within concrete bunds), heavy oil staining was observed on gravel beneath the circuit breakers located within the western area of the site and on gravel outside and adjacent to the bunded storage area within the central area of the site. | 5 | 4 | 1 | 1 | 1 | 3 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 4 | <10 kg or <50 mg/kg | Large | None | None | None | Yes - Small Volume | Yes - LPG | Contaminated soil - safe for current use | None |  |  | Default Asbestos |  | No | [6 empty] | 4 | 5 | 5 | Yes | 3 | Yes | 2 | 5 | C | C | Yes | Contaminated stockpiles |  | No |  | Stage 1 complete | Y | PSI with limited soil sampling program. Communicate with the site contractor to determine when the spoil and rubble stockpiles will be removed and ensure the waste records are provided to AusNet | [5 empty] | AusNet, Transmission Sites, Portfolio EMP | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021) | Groundwater environmental appraisal (2005), Drainage outfall rehab report (2006). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | C2 | Enviro - one above ground stormwater isolation valve in place | N | Confidence 5/5. Environmental report from 2023. | Risk driven by heavy surface staining beneath the transformers (within concrete bunds) Heavy oil staining was observed on gravel beneath the circuit breakers located within the western area of the site and on gravel outside and adjacent to the bunded storage area within the central area of the site. Oil leak rating 4/5. Surface water sample results collected post puraceptor treatment in 2023 reported elevated hydrocarbons. | 1. Service transformers and repair leaks. There are 5 on site. 2. Repair leaking circuit breakers. 3. Install hardstand under circuit breakers. 4. Clean bunds 5. Check bund integrity. 6. Install GAC post puraceptor treatment to further decrease hydrocarbon load. |  | C-I-C | C-I-C | x |  | C-I-C | [5 empty] | C-I-C | [5 empty] | C-I-C
Comms Site | Browns Bunker and Test Hut Communications | TBC TC-BB |  | HAZELWOOD DRIVE, MORWELL, VICTORIA 3840 | 5D~A\PP2749 | -38.247 | 146.4119 | TBC | TBC | Leased | Active | Uploaded 16/03 | Yes / Yes | 2021-02-24 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 1 |  | 1 | 1 | 4 | 5 | 5 | 3 | 2 |  | 6 or 12 monthly inspection program | 5 | None | None | None | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 1 | 1 | 2 |  |  |  | 4 | 2 | B | E | No |  |  | #REF! | [13 empty] | 3 | 2 | 2 | 1 | 2 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Brunswick TS (BTS) | TS-BTSX | Central | 46 King Street, Brunswick East, Victoria, 3056 | 1\PS725945 | -37.7739 | 144.9837 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-08-04 | A Ryan | Yes | Coffey (2011), WSP (2023) |  | AusNet, Transmission Sites, Portfolio EMP |  |  | PSI-Coffey (2011), PSI-WSP (2023), Water Quality Investigation Program (2022) | Geo-Eng - Environmental Risk Assessment (1996). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003). Coffey - Preliminary Geotechnical Assessment (2011) | 2023-01-01 | 5 | 5 | Historic report indicates drainage discharge exceeding discharge criteria (GHD, 2003) | 5 |  | Filling with contaminated soils (i.e. in retaining walls etc.), other material disposed off-site | High | 5 | Hydrocarbon sheen visible on water contained within the transformer concrete bund at the rear of the middle transformer radiator located within the southern portion of the site. | 6 | 3 | 1 | 1 | 1 | 2 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | >1,000 L | Default Chemicals | Yes - Large Volume | Yes - LPG | None | None | Yes |  |  |  | No |  |  | None |  |  |  | 3 | 4 | 5 | Yes | 5 | Yes | 5 | 4 | C | C | Yes | Potential contaminating activities. |  | #REF! |  |  | Y | PSI with limited soil sampling program. GME from existing wells. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP |  | Geo-Eng - Environmental Risk Assessment (1996). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003). Coffey - Preliminary Geotechnical Assessment (2011) |  | 2 | 1 | 4 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | C1 | Enviro - one above ground stormwater isolation valve in place | N | Confidence 5/5. Environmental report from 2023. | Risk driven by an oil leak rating 3/5, storage of >1,000 L fuel, presence of an underground storage tank (UST). Oil leak rating 3/5 Fully compliant, sealed bund. | 1. Remove UST and validate. 2. Repair leaking transformers. There are 6 on site. 3. Clean bunds 4. Check bund integrity. | C-I-C | C-I-C | C-I-C | x | [13 empty] | C-I-C
Terminal Station | Bulgana TS (BGTS) | TS-BGTS | West | Vance Crossing Road, Joel South VIC 3384 | None | -37.0418 | 142.9856 | TBC | TBC | Pending Acquisition | Pending Acquisition | Done | Yes / Yes | 2020-08-25 | CJ Wilson | Yes | [8 empty] | 2 | 2 | [5 empty] | 4 |  | 1 | 1 | 1 | 2 | 2 | 1 | 2 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | None | Large | Yes | None | None | Yes - Small Volume |  | None | [5 empty] | No | [6 empty] | 3 | 2 | 3 |  |  |  | 1 | 3 | C | D | No |  |  | #REF! | [13 empty] | 3 | 2 | 4 | 1 | 2 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | N/A | Not in this list. | Y | Confidence 2/5. Risk partially driven by lack of information. Last site inspection in 2020, no other info available. | Risk driven by lack of information. PRA notes indicate fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 1. Install shut off valve. 2. Conduct site inspection to confirm current status. | [10 empty] | C-I-C | [6 empty] | C-I-C
Comms Site | Campbells Hill Comms Site (CAMH) | TC-CAMHXXXX |  | Mirboo (Yarragon Rd), Allambee, Victoria 3823 | 1\TP192252 | -38.2461 | 146.0886 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-10-15 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | D | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | #N/A | #N/A | #N/A |  | City Gate | No | No | No | No | No | No | Yes | No | No | No | Yes | No | Yes | N/A | N/A | N/A | N/A | West | TBC | TBC | [23 empty] | C-I-C
Sub Station | Cann River ZSS (CNR) | DS-CNR | East | Old Coast Road (Tip), Cann River, Victoria 3890 | 9\PP3605 | -37.5798 | 149.1289 | TBC | TBC | Licensed | Active | Done | Yes / Yes | 2020-08-02 | M Snell | Yes | [8 empty] | 2 | 58 | [5 empty] | 3 |  | 3 | 4 | 4 | 5 | 5 | 5 | 1 |  | Brick bund with gravel floor | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | None | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 3 |  |  |  | 4 | 3 | B | D | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Possible natural gas via leakage | #N/A | #N/A |  | #N/A | No | No | No | No | No | No | Yes | No | No | No | Yes | No | Yes | N/A | N/A | N/A | N/A | West | TBC | TBC | [23 empty] | C-I-C
Comms Site | Carrajung Comms Site (CARJ) | TBC TC-Curr |  | GRAND RIDGE ROAD, CARRAJUNG, VICTORIA 3844 | 1\TP559706 | -38.4226 | 146.5812 | TBC | TBC | Freehold | ACTIVE | gas radio site earmarked for removal in 2020 (A Ryan) B Scott email | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 31 | 3 | 4 | 5 | 5 | 4 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Possible natural gas via leakage | #N/A | No |  | City Gate | No | No | No | No | No | No | Yes | No | No | No | Yes | No | Yes | N/A | N/A | N/A | N/A | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Castlemaine City Gate | CAST |  | Castlemaine-Maldon Road, Castlemaine, Victoria 3450 | None | -37.0627 | 144.1705 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-17 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 8 | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 2.5 | 3 | N/A adondoned site | N/A |  | N/A | Station has been vandalised after being abandoned by Ausnet |  | Abondoned site | No | No | No | No | No | No | No | Yes | No | No | Yes | No | 0 |  |  |  | N/A | Central | TBC | TBC | [23 empty] | C-I-C
Sub Station | Chirnside Park ZSS (CPK) | DS-CPK | Central | 11 Fletcher Road, Mooroolbark VIC 3138 | 2\PS516019 | -37.7614 | 145.3124 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-25 | A Ryan | Yes | [8 empty] | 2 | 7 | [5 empty] | 3 | Relatively new site | 2 | 1 | 1 | 1 | 1 | 1 | 4 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1 | None | Large | Yes | None | Default Chemicals |  |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 2 | 4 | C | C | No |  |  | #REF! | [13 empty] | 9 | 4 | 4 | 5 | 4 | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Sub Station | Clover Flat Power Station ZSS (CLPS) / Clover Flat ZSS (CF) | DS-CFX | North | Bogong High Plains Road, Bogong, Victoria 3708 | 11A\PP2361 | -36.8064 | 147.2249 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-07-02 | CJ Wilson | Yes | [8 empty] | 2 | 85 | [5 empty] | 3 |  | 3 | 4 | 1 | 1 | 1 | 3 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | None | None |  | None | [5 empty] | No | [6 empty] | 3 | 2 | 1 |  |  |  | 5 | 3 | C | D | Yes |  |  | #REF! |  |  |  |  | Yes | Stage 2 - due 2018 | Yes | Rebuild due 2014-2020 | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 4 | 4.5 | 5 | 5 Rare: C | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | Yes | Yes | Yes | No | 0 |  |  |  | N/A | Central | Andrew Ryan | C | [23 empty] | C-I-C
Sub Station | Clyde North ZSS (CLN) | DS-CLN | Central | Berwick-Cranbourne Rd, Clyde North, Victoria, 3978 | RES1\PS818695 | -38.0948 | 145.3329 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-05-26 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 15 | [5 empty] | 5 |  | 10 | 4 | 4 | 3 | 4 | 4 | 1 |  | Brick bund with gravel floor and basic oil/water separator - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 4 | 4 | 4 | No | 4 | No | 2 | 4 | C | D | Yes | Potential contaminating activities. |  | #REF! | NA |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 1 | 2.5 | 3 | 3 Rare: D | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | Cameron Wilson | D | [23 empty] | C-I-C
City Gate | Cobden City Gate | COBD |  | Cobden-Terang Road, Cobden VIC 3266 | None | -38.3307 | 143.046 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2021-04-09 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | No | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | [5 empty] | 2 | A | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1.5 | 2 | 2 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | No | No | 0 |  |  |  | N/A | North | Cameron Wilson | E | [23 empty] | C-I-C
Comms Site | Cockatoo Comms Site (COCK) | TC-COCKXXXX |  | Patemoster Road, Cockatoo (Emerald), Victoria 3782 | 1\TP172109 | -37.953 | 145.4878 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-11 | A Ryan | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 2 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 4 | 3 | 3 | 3 Rare: D | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | Yes | Yes | No | 0 |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
City Gate | Colac City Gate | COLA |  | Christies Road, Colac VIC 3250 | 1\PS620886 | -38.3733 | 143.5709 | TBC | TBC | Leased | Expired | Done | Yes / Yes | 2021-01-21 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 2 | 4 | 4 | 5 | 5 | 5 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A | Weeds within yard and access track | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | Yes | Yes | No | 0 |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Collingwood Office and Warehouse | TBC Colling |  | 32 Cromwell St, Collingwood VIC 3066 | None | -37.8078 | 144.9898 | TBC | AusNet Services | Leased | Active | UPLOAD 20/03 | Yes / Yes | 2021-02-12 | S Kibell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 4 | 3 | 4 | 5 | 5 | 4 | 1 |  | Gas bottle in standing heater, BBQ gas bottle stores on shelf | 5 | None | None | None | None | None | None | Yes - LPG | None | None |  | None |  |  | No | [6 empty] | 1 | 2 | [5 empty] | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1.5 | 2 | 2 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | Yes | Yes | Yes | No | 0 |  |  |  | N/A | Central | Andrew Ryan | E | [23 empty] | C-I-C
City Gate | Corio City Gate | CORI |  | 19-73 Railway Avenue, Corio, Victoria, 3214 | 1\TP851951 | -38.0669 | 144.3821 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-16 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 5 | 1 | 4 | 5 | 5 | 3 | 2 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | Yes - Small Volume | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 2 |  |  |  | 4 | 2 | C | E | No |  |  | #REF! | [13 empty] | 3 | 2 | 4 | 0 | 2 | 2 | 3 | 4 | 3.5 | 4 | 4 Rare: C | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | Yes | Yes | Yes | No | 0 |  |  |  | N/A | Central | Andrew Ryan | C | [23 empty] | C-I-C
City Gate | Craigieburn City Gate | CRAI |  | Boundary Road, Craigieburn VIC 3064 | None | -37.719 | 144.9608 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-11-20 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 20 | 3 | 4 | 5 | 5 | 4 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 4 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 4 | 5 | 1 | 1 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A | Weeds with in yard and access track | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Cranbourne TS (CBTS) | TS-CBTS | Central | 1120 Thompsons Rd, Cranbourne VIC 3977 | 1\TP420735 | -38.0849 | 145.2652 | TBC | TBC | Freehold | Active | 2020-07-16 | Yes / Yes | 2020-07-16 | A Ryan | Yes | Yes |  |  |  |  | Water Quality Investigation Program-BSE(2022) | SKM - Groundwater Assessment (2001) |  | 3 | 12 | [5 empty] | 5 | Water within the HT had a visible sheen, Oil staining was observed on the internal and external wall of the bund, Illegal rubbish dumping in driveway of the site (BSE-2022) | 6 | 3 | 1 | 2 | 2 | 2 | 4 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals |  |  | None | None |  |  |  |  | No | [6 empty] | 3 | 4 | 4 | Yes |  |  | 2 | 4 | C | C | Yes |  |  | #REF! |  |  | Y | [8 empty] | SKM - Groundwater Assessment (2001) |  | 2 | 3 | 4 | 5 | 4 | 4 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | East | TBC | TBC | C5 | Enviro - had underground unit-turned into holding tank, then added one above ground unit with a triple interceptor tank, have found the design is flawed and heavy rain/filter issue events overflow the holding tank and it spills the top of its contents onto the grass, needs repair asap | N | Confidence 3/5. Captured in WQIP (BlueSphere 2022) and emergency sampling event in 2023. No groundwater information. | Observations associated with oil filled equipment driving risk. Water within the holding had a visible sheen. Oil staining was observed on the internal and external wall of the bund Illegal rubbish dumping in driveway of the site (BSE, 2022) 6 Transformers on site, oil leak rating 3/5. Known holding tank overflow events in 2023 and 2024. With known sheen in water in holding tanks (likely from leaking transformers), risk is likely higher than C in column BU. | 1. Install shut off valve. 2. Review, reconfigure and update drainage at the site to rectify apparent design limitations resulting in overflow events. 3. Service and repair leaking transformers. 6 on site. 4. Clean bund surfaces 5. Drain and clean holding tank. 6. Clean out oil and sediment from the puraceptor, and clean internal filters, directing water into the TIT (per comment in DZ56). 7. Check bund integrity 8. Install holding tank alarm |  | C-I-C | C-I-C | x | C-I-C | [5 empty] | C-I-C |  | C-I-C | C-I-C |  | C-I-C |  | C-I-C
Sub Station | Cranbourne ZSS (CRE) | DS-CRE | Central | 1120 Thompsons Rd, Cranbourne VIC 3977 | 1\TP420735 | -38.0849 | 145.2652 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-07-23 | A Ryan | Yes | [8 empty] | 2 | 9 | [5 empty] | 2 |  | 2 | 1 | 1 | 2 | 2 | 1 | 0 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | None | Large | Yes | None | Default Chemicals | None | None | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 4 |  |  |  | 2 | 4 | B | C | No |  |  | #REF! | [13 empty] | 0 | 0 | 2 | 1 | 0 | 0 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A |  | N/A | Hydraulic pump containing oil leaking observed action taken to have oil leak addressed No other oil field equipment on site. |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Crowlands TS (CWTS) | TS-CWTS | West | Off Spring Flat Road, Crowlands VIC 3377 | 1\PS811585 | -37.1204 | 143.1539 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-08-25 | CJ Wilson | Yes | [8 empty] | 2 | 3 | [5 empty] | 2 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | New asset, bunding and oil/water separator | 1 | None | Small | Yes | None | None | Yes - Small Volume |  | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 4 | 4 | 4 | 4 Rare: C | N/A |  | N/A | Original building destroyed by fire, asbestos materials cleaned up as part of rebuild works, new building free of any contaminates |  | Comms Site | No | No | No | No | No | No | No | No | Yes | Yes | Yes | No | 0 |  |  |  | N/A | Central | TBC | TBC | N/A | Not in this list. | Y | Low confidence, 2/5. New asset. | Risk driven by lack of information. PRA notes indicate site is a new asset, with bunding and oil/water separator. 1 transformer on site. The status of shut off valve etc unclear. | 1. Confirm status of shut off valve. Install if not present. 2. Consider installing an alarm on the holding tanks as site is remote. | [10 empty] | C-I-C |  |  |  |  | C-I-C |  | C-I-C
Sub Station | Croydon ZSS (CYN) | DS-CYN | Central | 336 Dorset Road, Croydon, Victoria, 3136 (220m south of Mt Dandenong Rd) | 1\LP220900 | -37.8019 | 145.2876 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-25 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 43 | [5 empty] | 4 |  | 3 | 2 | 4 | 2 | 4 | 3 | 1 |  | Brick bund with gravel floor and basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume | None | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 5 | No | 4 | No | 2 | 4 | C | D | Yes | Potential contaminating activities. |  | #REF! | NA |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Daylesford City Gate | DAYL |  | Knox Street, Daylesford VIC 3460 | 1\TP83494 | -37.3412 | 144.159 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-11-17 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 5 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 4 |  |  |  | 1 | 2 | D | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | Cameron Wilson | E | [23 empty] | C-I-C
Terminal Station | Dederang TS (DDTS) | TS-DDTS | North | Yackandandah Road, Dederang, Victoria 3691 (0.5kms from Kiewa Valley) | 1\TP241980 | -36.4532 | 146.993 | TBC | TBC | Freehold | Active | 2020-07-02 | Yes / Yes | 2020-07-02 | CJ Wilson | Yes | Yes | [5 empty] | Groundwater Monitoring (2005). Geoworks - Terminal Station Discharge Water Sampling (2004). SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 60 | Uncontrolled stormwater discharges containing oil to farm dam | 5 | 2 | Some level of remediation completed before bunding upgrades |  | 5 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1 | >10 kg or >50 mg/kg | Large | Yes | Fuel Default | None | Yes - Small Volume |  | Spoil / Waste | [5 empty] | No | [6 empty] | 4 | 4 | 3 | Yes |  |  | 4 | 4 | C | C | No |  |  | #REF! |  | Y | Y | [8 empty] | Groundwater Monitoring (2005). Geoworks - Terminal Station Discharge Water Sampling (2004). SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 3 | 4 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Dam approx 200m on opposite side of road | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | Cameron Wilson | E | C2 | Enviro - one above ground system, one below ground system stormwater isolation valves fitted, | Y | Confidence 3/5. Past incident of water release containing oil to neighbouring farm dam. | Risk appears largely driven by consequences of contamination, primarily due to the proximity to neighbouring and environmental receptors. Also PRA records stockpiles on site which add to risk rating. Off-site drainage. Fully compliant sealed bund with puraceptor oil/water separator + shut off valve. | 1. Confirm the contamination status of stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. 2. Confirm drainage plans for site, to ensure no accidental releases to neighbouring farms possible in future. | [16 empty] | C-I-C | C-I-C
Comms Site | Dederang TS Comms Site (DDTS-COMS) | TC-DDTSXXXX |  | Yackandandah Road, Dederang, Victoria 3691 (0.5kms from Kiewa Valley) | None | -36.4532 | 146.993 | TBC | TBC | Leased | Active | C​ameron Wilson confirmed that this site audit has already been covered as it is included in the Dederang Terminal Audit and is not a stand-alone Comms site. The Comms room is part of the main Control Buildong. | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 3 | 2 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | North | Cameron Wilson | E | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Delegate Depot | TBC Delegate |  | 21 Victoria Pde, Delegate NSW 2633 | None | -37.0455 | 148.9403 | TBC | Downer | Licensed | Active | Interstate | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | North | Cameron Wilson | E | [23 empty] | C-I-C
City Gate | Derrimut City Gate | DERR |  | Middle Road, Derrimut VIC 3030 | None | -37.7976 | 144.7512 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-01-12 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 3 | 1 | 1 | 5 | 4 | 4.5 | 5 | 5 Rare: C | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Diggers Rest City Gate | DIGG |  | Watsons Road, Diggers Rest VIC 3427 | None | -37.6153 | 144.7214 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2021-04-13 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | Check | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 4 |  |  |  |  | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 Rare: E | N/A | Very remote site. | N/A | No |  | Comms Site | No | No | No | No | No | No | No | Yes | No | No | Yes | No | 0 |  |  |  | N/A | North | Cameron Wilson | E | [23 empty] | C-I-C
Sub Station | Doreen ZSS (DRN) | DS-DRN | Central | 900 Bridge Inn Road, Doreen VIC 3754 | 1\TP139446 | -37.7227 | 141.9943 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-29 | A Ryan | Yes | [8 empty] | 2 | 12 | [5 empty] | 3 |  | 2 | 1 | 4 | 3 | 4 | 2 | 1 |  | Brick bund with gravel floor and basic oil/water separator - no shut off valve | 4 | None | Large | Yes | None | Default Chemicals | Yes - Small Volume |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 1 | 4 | C | C | Yes |  |  | #REF! |  |  |  |  | Yes | Stage 1 - due 2017 | [7 empty] | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 1.5 | 2 | 2 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | Yes | Yes | Yes | No | 0 |  |  |  | N/A | Central | Andrew Ryan | E | [23 empty] | C-I-C
Terminal Station | Dundonnell Wind Farm (DDWF) | TS-DDWF | West | TBC | None | -37.8432 | 142.8795 | TBC | TBC | Pending Acquisition | Pending Acquisition | MONDO TO DO - ask Ben | New |  |  | N/A | [8 empty] | 1 | [6 empty] | 3 | New | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | New | 1 | None | Oil Default | [11 empty] | Yes | [6 empty] | 3 | 2 | [5 empty] | 3 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A | Weeds with in yard and access track | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | TBC | TBC | N/A | Not in this list. | Y | Confidence 1/5. Default oil filled equipment selected. | The risk is driven by a lack of information. There are no site inspections or reports on Env Register. | 1. Conduct baseline site inspection to confirm current status. | [17 empty] | C-I-C
Comms Site | Dunns Hill Comms Site (DUNN) | TC-DUNNXXXX |  | off One Tree Hill Road, Ferny Creek, Victoria 3786 | None | -37.8796 | 145.3315 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-06-11 | A Ryan | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 4 | 2 | B | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A | Access track overgrown | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | Yes | Yes | No | 0 |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Comms Site | East Greenwald Comms Site (EGRN) | TC-EGRNXXXX |  | East Greenwald Rd off Princess Highway, Greenwald VIC 3304 | 2\PS747679 | -37.9703 | 141.3972 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-09-28 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 4 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | A | E | No |  |  | #REF! | [13 empty] | 10 | 4 | 1 | 1 | 4 | 4 | 1 | 1 | 1 | 1 | 1 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | East Rowville TS (ERTS) | TS-ERTS | Central | Lot 1 Police Road, East Rowville, Victoria 3178 | 1\LP111072 | -37.9412 | 145.2312 | TBC | TBC | Freehold | Active | 2020-05-22 | Yes / Yes | 2020-05-22 | A Ryan | Yes | Yes | [5 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 2 |  |  |  | Stockpile on site, NW corner of site | Low | 5 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1 | >10 kg or >50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume |  | Spoil / Waste | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 2 | 4 | B | C | No |  |  | #REF! |  | Y |  |  |  | Transformer upgrades over next 2 years | [5 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | North | Cameron Wilson | E | C2 | Enviro -one above ground and stormwater isolation valve in place | N | Confidence 3/5. Fully compliant sealed bund with puraceptor oil/ water separator and shut off valve. | Risk driven by possible impacts to human health and environment surrounding site. No environment reports since 2003. Site inspection in 2020 shows shut off valve, concrete bunds, puraceptor, no oil leaks, very good transformer condition. | 1. Site inspection to confirm current status. There is potential for some legacy impacts from previously installed old transformers that were leaky. Reported that some level of soil removal / remediation was performed (not on enviro register) and transformers / bunds upgraded. Stockpiles of spoil reported in 2020 but photo just looks like excess crushed rock has been spread on ground. | [17 empty] | C-I-C
Comms Site | Echuca Ambulance - Use of radio site | TBC TC-Echuca |  | HIGH STREET, ECHUCA, VICTORIA 3564 | None | -36.1491 | 144.7532 | TBC | TBC | Licensed | No Agreement | Daniel Dobrosak not aware of this site | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 3 | 1 | 4 | 5 | 5 | 3 | 2 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 3 | 2 | 4 | 3 | 2 | 2 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A | Weeds with in yard and access track | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Eildon Power Station (EPS) | TS-EPSY | North | 15 Eildon Road, Eildon, Victoria 3713 (below dam wall) | None | -37.2231 | 145.9215 | TBC | TBC | Leased | Active | 2020-07-15 | Yes / Yes | 2020-07-15 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 3 | Diesel generator and batteries | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  | None | 1 | <10 kg or <50 mg/kg | Oil Default | Yes | None | None | Yes - Small Volume | Yes - LPG | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 3 |  |  |  | 2 | 3 | D | D | No |  |  | #REF! | [13 empty] | 3 | 2 | 4 | 3 | 2 | 2 | 1 | 1 | 1 | 1 | 1 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | North | Cameron Wilson | E | N/A | Enviro - NA | Y | Confidence 2/5. Site used for battery storage. | Risk driven by lack of information, apart from an AusNet 2020 inspection. No site inspections or reports on Env Register. No oil containing equipment according to env inspection in 2020. Diesel generator - Pallet bunding for spare fuel drum. Generator is self bunded. Excellent bunding condition reported. | 1. Site inspection to confirm current status. Suggest no upgrades required at this stage. | [17 empty] | C-I-C
Sub Station | Eltham ZSS (ELM) | DS-ELM | Central | 9-11 Brisbane Street, Eltham, Victoria 3095 (200m west of Silver St) | 1\TP552577 | -37.7166 | 145.1379 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-05 | A Ryan | Yes | [8 empty] | 2 | 17 | Transformer leaking oil outside bunded area in 2020 |  |  |  |  | 4 |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 2 | >10 kg or >50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 2 | 4 | C | C | No |  |  | #REF! |  |  |  |  | Yes | Stage 2 - due 2018 | [7 empty] | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A | Weeds with in yard and access track | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Sub Station | Epping ZSS (EPG) | DS-EPG | Central | 51 Cooper Street, Epping, Victoria, 3076 (opposite Howard Street) | 1\TP177865 | -37.6525 | 145.0262 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-03 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 20 | [5 empty] | 5 |  | 3 | 2 | 4 | 3 | 4 | 3 | 1 |  | Brick bund with gravel floor and basic oil/water separator - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None | None | Spoil / Waste | Yes - Septic |  |  |  |  | No | [6 empty] | 4 | 4 | 5 | No | 4 | No | 3 | 4 | D | D | Yes | Potential contaminating activities. |  | #REF! | Stockpiles evident, however, were derived from road upgrade in non-operational area. Therefore, low potential for contamination. |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 1 | 1 | 3 | 4 | 1 | 1 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Sub Station | Erica Cap Bank ZSS (CERA) | DS-CER | East | Moe/Rawson Rd, Erica VIC 3825 (Erica Rd) | None | -37.897 | 146.3687 | TBC | TBC | TBC | TBC | Uploaded 16/03 | Yes / Yes | 2021-01-15 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 | Batteries | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Dedicated battery room | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 4 |  |  |  | 4 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Switchyard | Exeter Rd Switchboard Sub (EXSB) | DS-EXS |  | Karingal St, Croydon North VIC 3136 (50m north of 31-35 Exeter Rd) | 1\TP840998 | -37.77 | 145.294 | TBC | TBC | Leased | Active | LOOK UP NOTES | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | HOW DOES A ZSS HAVE NO TR? KIOSK ONLY? | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | B | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Public lookout tower approx. 200m away, with toilet facilities | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | Cameron Wilson | E | [23 empty] | C-I-C
Sub Station | Ferntree Gully ZSS (FGY) | DS-FGY | Central | 61 Glenfern Road/Brenock Park Drive, Ferntree Gully, Victoria 3156 | 1\TP334256 | -37.8932 | 145.2924 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-25 | A Ryan | Yes | [8 empty] | 2 | 15 | [5 empty] | 5 |  | 2 | 1 | 4 | 3 | 4 | 2 | 1 |  | Brick bund with gravel floor and basic oil/water separator - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 2 | 4 | B | C | Yes |  |  | #REF! |  |  |  |  | Yes | Stage 1 - due 2017 | [7 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | Cameron Wilson | E | [23 empty] | C-I-C
Terminal Station | Fishermans Bend TS (FBTS) | TS-FBTS | Central | 132-140 Turner Street, Port Melbourne, Victoria, 3207 | 1\PS401838 | -37.8248 | 144.9294 | TBC | TBC | Leased | Active | 2020-05-22 | Yes / Yes | 2020-05-22 | A Ryan | Yes | WSP (2023) |  | AusNet, Transmission Sites, Portfolio EMP |  |  | PSI- WSP (2023) | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) | 2023-01-01 | 5 | 5 | Asbestos in soil identified in 2020 | 5 | 5 | Old abandoned asbestos pipes in ground, number of stockpiles removed, source of stockpile near freeway? | Medium Risk | 5 | Staining on the surface of and beneath one of the main the transformers labelled B3 (within the concrete bund) | 3 | 3 | 1 | 1 | 1 | 2 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | <1,000 L | Default Chemicals | Yes - Small Volume | Yes - LPG | Spoil / Waste | Yes - Septic | Yes |  | Default Asbestos |  | No | [6 empty] | 3 | 5 | 2 | Yes | 1 | Yes | 4 | 5 | C | C | Yes | Infrastructure with high potential for contamination and stockpiles | Investigate stockpiles and confirm nature of asbestos | Possible | Stockpile sampling necessary to confirm if triggers have been met | Y | Y | PSI with limited soil sampling program. GME from existing wells. Sample stockpiles. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP |  | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A | Weeds with in yard and access track | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | West | TBC | TBC | C1 | Enviro -one above ground and stormwater isolation valve in place | N | Confidence 5/5. Environmental report from 2024. Fully compliant sealed bund with puraceptor oil/ water separator and shut off valve. | Risk drivers include presence of UST (listed in PRA), proximity to nearby environmental receptors. Asbestos in soil identified in 2020. Present in Site infrastructure and underground services. Found during excavation activities. Oil leak rating 3/5. Presence of 3 transformers with staining on the surface of and beneath one of the main the transformers labelled B3 (within the concrete bund) in 2023. Note: Checked WSP 2024 report - Asbestos within stockpile on-site was scheduled for disposal in 2018. No record of disposal. ACM present in underground services, buildings and transformers, switchyard/switchboard on Site. ACM sheeting and pipes found during excavation on site. Several related Enablon incidents. Some of the ACM in above ground infrastructure is friable. WSP noted that they did not see fragments of ACM when soil sampling or on soil surface, so did not test for it. WSP note: "No above or below ground storage tanks were observed at the site, with the exception of holding tank (interceptor) associated with the Puraceptor treatment system" | 1. Remove and validate UST. 2. Implement management of buried ACM and ACM in buildings/ on site (if not already). 3. Service and repair leaking transformers 4. Clean bund surfaces. 5. Check bund integrity. | C-I-C | C-I-C | C-I-C | x | [13 empty] | C-I-C
Depot, Office and Warehouse Storage | Flinders St Office | TS-FLIN |  | Level 14 & 15, 452 Flinders Street, Melbourne VIC 300 | 1\TP81877 | -37.8195 | 144.9586 | External Land Owner- Leased Facility | AusNet Services | Leased | Active | UPLOAD 20/03 | Yes / Yes | 2021-02-19 | J Weghorn | Yes | [8 empty] | 2 | [6 empty] | 3 | Diesel generator and large battery bank on-site | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Generator owned and maintained by building management with regular maintenance. | 5 | None | None | Yes | Fuel Default | None | None | None | None | None |  | None |  |  | No | [6 empty] | 4 | 4 | 4 |  |  |  |  | 4 | C | C | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 1 | 3 | 3 | 3 Rare: D | N/A | Residential farmhouse approx. 1km away | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | North | Cameron Wilson | D | [23 empty] | C-I-C
Sub Station | Foster ZSS (FTR) | DS-FTR | East | 5 Elphicks Road, Foster, Victoria, 3960 (off South Gippsland Highway) | 1\TP104794 | -38.6601 | 146.2214 | TBC | TBC | Freehold | Active | Uploaded 16/03 | Yes / Yes | 2020-11-04 | M Snell | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 35 | [5 empty] | 3 | Oil containing equipment and batteries | 2 | 3 | 4 | 5 | 5 | 4 | 1 |  | Brick bund with gravel floor | 5 | None | Large | Yes | None | None | None | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 3 |  |  |  | 4 | 3 | A | D | Yes | Potential contaminating activities. |  | #REF! |  |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 Rare: E | N/A |  | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | North | Cameron Wilson | E | [23 empty] | C-I-C
Terminal Station | Frankston TS (FTS) | TS-FTSX | Central | 585 Mc Cleland Drive, Frankston, Victoria 3199 | 1\TP078997 | -38.1629 | 145.1684 | TBC | TBC | Freehold | Active | 2020-06-10 | Yes / Yes | 2020-06-10 | A Ryan | Yes | Yes | [5 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | [5 empty] | Low | 3 | Oil containing equiment, chemicals and batteries | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Bunding and shut off valve | 5 | <10 kg or <50 mg/kg | Oil Default | Yes | None | Default Chemicals | None |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 2 | 4 | B | C | Yes |  |  | #REF! | [11 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 Rare: E | N/A | Residential farmhouse approx. 800m away Earthen drainage ditch running alongside roadway adjacent to front entry | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | Cameron Wilson | E | C1 | Enviro -one above ground and stormwater isolation valve in place | N | Confidence 3/5. No recent environmental information | Risk drivers are based on consequence of contamination and lack of recent information. There is a septic tank at the site. Known leaking stormwater pipe (not in PRA). Lack of bunding controls. More information needed - confirm presence of oil filled equipment. | 1. Complete site inspection to determine presence of oil filled transformer. 2. If oil filled equipment still present, upgrade the brick bund to a concrete bund. 3. Resolve status of septic tank. Remove if not in use, or service/ repair if in use. | [6 empty] | C-I-C | C-I-C | [9 empty] | C-I-C
Depot, Office and Warehouse Storage | Freshwater Place Office | TS-FWPX |  | Level 28-32, 2 Southbank Boulevard, Southbank VIC 3006 | CM1\PS504017 | -37.8215 | 144.9625 | External Land Owner- Leased Facility | AusNet Services | Leased | Active | UPLOAD 20/03 | Yes / Yes | 2021-02-12 | V Cripps | Yes | [8 empty] | 2 | [6 empty] | 3 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Annual tank integrity testing and fuel sampling | 5 | None | None | None | Fuel Default | None | None | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 4 | 4 | [5 empty] | 4 | C | C | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 2.5 | 3 | 3 Rare: D | N/A | Weeds with in yard and access track | N/A | No |  | Comms Site | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Geelong TS (GTS) | TS-GTSX | West | 169-199 Cox Road, Norlane, Victoria, 3220 | 1\TP376051 & 1\TP562117 | -38.0829 | 144.3383 | TBC | TBC | Freehold | Active | UPLOAD 20/03 Done - CJ and A Ryan | Yes / Yes | 11-25/11/2020 | A Ryan / CJ Wilson | Yes | Yes |  | AusNet, Transmission Sites, Portfolio EMP |  |  | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021) | Geo-Eng - Environmental Risk Assessment (1996). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 5 | 13 |  | 5 | 3 | Previous remediation undertaken, stockpiles of former excavated materials | Low | 5 | Oil containing equipment, SF6/gas cylinders and batteries | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Fully compliant sealed bund, puraceptor oil/water separator and shut off valve | 1 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume | Yes - LPG | Contaminated soil - safe for current use | Yes - Septic |  |  | Default Asbestos |  | No | [6 empty] | 4 | 5 | 5 |  | 4 | No | 3 | 5 | A | E | No | Contaminated stockpiles |  | No |  | Stage 1 complete |  | PSI with limited soil sampling program. GME from existing wells. EMP, plus stockpile ESC | [5 empty] | AusNet, Transmission Sites, Portfolio EMP | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021) | Geo-Eng - Environmental Risk Assessment (1996). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 4 | 4 | 4 | 4 Rare: C | N/A | This site is owned by Ausnet and has been leased out it has not been maintained for quite awhile. Batteries leaking. Diesel generator not maintained. | N/A | No |  | Comms Site | No | No | No | No | No | Yes | No | Yes | No | No | Yes | No | No |  |  |  | N/A | East | TBC | TBC | C4 | Enviro - one above ground system, stormwater isolation valves fitted, erosion from spoil mounds needs adressing, noted in switchyards | N | Confidence 5/5. But no recent environmental reports. Fully compliant sealed bund, puraceptor oil/water separator and shut off valve. | High risk rating driven by consequence of contamination. Photos from site inspections show eroding of spoil mounds, unsure of their contamination status. Stockpiles are all fill material apart from one Cat C stockpile (BlueSphere, 2021) | 1. Complete Site inspection to determine current status of stockpiles. They require erosion controls if unvegetated. Hydroseed or implement sedimentation controls. | [14 empty] | C-I-C |  |  | C-I-C
Terminal Station | Glenrowan TS (GNTS) | TS-GNTS | North | Hume Highway (Winton Glenrowan Road), Glenrowan, Victoria 3675 | 1\TP345760 | -36.4931 | 146.1328 | TBC | TBC | Freehold | Active | 2020-07-27 | Yes / Yes | 2020-07-27 | CJ Wilson | Yes | Yes | [5 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 7 |  |  |  |  | Medium Risk | 5 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1 | <10 kg or <50 mg/kg | Large | Yes | None | None |  |  | Spoil / Waste | [5 empty] | No | [6 empty] | 3 | 2 | 2 | Yes |  |  | 1 | 3 | C | D | No |  |  | #REF! |  | Y | Y | [8 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | Weeds poisoned to manage infestation | N/A | No | No | Comms Site | No | No | No | No | No | No | No | No | Yes | Yes | CHECK | No | No |  |  |  | N/A | West | TBC | TBC | C1 | Enviro - one above ground system, stormwater isolation valves fitted, minor erosion issues around the site | Y | Confidence 3/5. Fully compliant sealed bund with puraceptor oil/water separator + shut off valve. No environmental reports since 2003. | Risk driven by consequence of contamination. A 2020 site inspection did not outline any leakage issues. Drawings of environmental upgrade works conducted in 2004 on Env Register. Stockpiles recorded as being on Site (no details) | 1. Complete site inspection to determine presence of stockpiles and status of other potentially contaminating activities. 2. Confirm the contamination status of stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. | [14 empty] | C-I-C |  |  | C-I-C
Comms Site | Gnarwarre/Bayview Comms Site (GNAR) | TC-GNARXXXX |  | Haines Road, Barrabool, Victoria 3221 | None | -38.16 | 144.2036 | TBC | TBC | Leased | Active | Done. CJ also completed. Used A Ryan. | Yes / Yes | 2020-11-10 | A Ryan | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 0 | 1 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 5 |  |  |  | 2 | 3 | C | D | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A |  | N/A | No | No | Comms Site | No | No | No | No | No | No | No | No | Yes | Yes | Yes | No | No |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Hamilton City Gate | HAMI |  | Henty Hwy, Hamilton VIC 3300 | None | -37.7227 | 141.9943 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2021-03-30 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 4 |  |  |  |  | 2 | A | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 2 | 3.5 | 4 | 4 Rare: C | N/A | Weeds poisoned to manage infestation | N/A | No | No | Comms Site | No | No | No | No | No | No | No | No | Yes | Yes | Yes | No | No |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Ex Gas Works Site | Hamilton Ex Gas Works Site | TBC Hamil Gas |  | 2-16 Craig Street, Hamilton, Victoria 3300 | 11A~11\PP5364 | -37.75 | 142.0261 | TBC | TBC | Freehold | ACTIVE | 2020-04-06 | No assessment needed |  |  | Yes | Yes |  |  |  |  | EES - Draft Remediation Action Plan: Hamilton (2004), Jacobs - Preliminary Conceptual Site Model (pCSM) (2021), Jacobs - Contamination Management Plan (CMP) (2021), Jacobs - Gfactuakl Report: Groundwater Monitoring Event March 2021 (2021) |  |  | 3 |  |  | 5 | [5 empty] | 1 | 1 | 4 | 5 | 5 | 3 | 4 |  |  | 5 | None | Oil Default | [8 empty] | Inert |  |  | No |  | NAPL Present | None |  |  |  | 4 | 4 | 5 |  |  |  |  | 4 | B | A | Yes | Confirmed contaminated soil and groundwater | Refer to Gasworks Team | #REF! | Known contamination (former Gasworks) |  |  | DSI | [6 empty] | EES - Draft Remediation Action Plan: Hamilton (2004), Jacobs - Preliminary Conceptual Site Model (pCSM) (2021), Jacobs - Contamination Management Plan (CMP) (2021), Jacobs - Gfactuakl Report: Groundwater Monitoring Event March 2021 (2021) |  |  | 2 | 3 | 4 | 5 | 4 | 4 | 2 | 4 | 3 | 3 | 3 Rare: D | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No | No | No | No | No | No | No | No | No | No | No | No | No | N/A | N/A | N/A | N/A | East | TBC | TBC | [23 empty] | C-I-C
Sub Station | Hampton Park ZSS (HPK) | DS-HPK | Central | 83-87 Hallam Road, Hampton Park, Victoria, 3976 | 1\TP197231 | -38.036 | 145.2671 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-16 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 32 | [5 empty] | 5 |  | 3 | 2 | 4 | 2 | 4 | 3 | 1 |  | Brick bund with gravel floor and basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None | None | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 5 | No | 5 | Yes | 3 | 4 | C | D | Yes | Potential contaminating activities. |  | #REF! | NA |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 1 | 1 | 2 | 3 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Haunted Gully Terminal Station (HGTS) | TS-HGTS | West | 2210 LOWER DARLINGTON ROAD, LISMORE, VICTORIA 3324 | 1\PS817798 | -38.0078 | 143.3084 | TBC | TBC | Freehold | Active | New station (A Ryan) | New |  |  | N/A | [8 empty] | 1 | 2 | Scissor lift leaking hydraulic oil in 2019 |  |  |  |  | 3 | New | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | New | 1 | None | Large | [11 empty] | Yes | [6 empty] | 3 | 2 | [5 empty] | 3 | E | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 3 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | East | TBC | TBC | N/A | Not in this list. | Y | Confidence 1/5. New site (post 2018). ESA report from 2018 | Very low risk rating of E from the PRA. Suggest complete site inspection is completed to update all fields. | 1. Complete Site inspection to confirm environmental status. | [17 empty] | C-I-C
Depot, Office and Warehouse Storage | Hazelwood Depot | WH-1001 |  | Tramway Road, Morwell, Victoria, 3841 | 2G~A\PP2749 | -38.2799 | 146.4309 | AusNet Services Transmission Group Pty Ltd | Zinfra | Freehold | Active | UPLOAD 20/03 | Yes / Yes | 2021-03-17 | M Snell | Yes | [6 empty] | GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 2 | [6 empty] | 3 | Gas cylinders and storage of equipment | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Gas cylinders in cages and routine inspections | 5 | None | None | None | None | None | None | Yes - LPG | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 3 |  |  |  |  | 3 | C | D | Yes |  |  | #REF! | [11 empty] | GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Switchyard | Hazelwood Power Station (HWPS) | TBC PS-HWPS | East | Brodribb Road, Hazelwood, Victoria 3840 | Part of 2\PS827363 | -38.2737 | 146.3918 | TBC | TBC | Pending Acquisition | Pending Acquisition | UPLOAD 20/03 See emails from Adam - asbestos in concrete John H or Mark | Yes / Yes | 2021-12-31 | M Snell | Yes | Yes | Yes | AusNet, Transmission Sites, Portfolio EMP |  |  | ERM - Hazelwood Switchyard - Final Baseline Assessment (2018), Water Quality Investigation Program-BSE(2022) | GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002); ERM 2018, Hazelwood Switchyard, Final Baseline Assessment, June 2018 | 2022-09-01 | 5 |  | Oil spill from trailer and battery acid leaks reported in 2018 and small oil spill from bushings reported in 2019, off-site disposal of potentially contaminated soils and suspected asbestos identified in concrete rubble in 2020 | 4 |  | Potential contaminated material on site, asbestos packing between some of the slabs. Ponds and contamination issues | Medium Risk | 5 | Oil containing equipment, fuel storage, generators and batteries, There is a flooded basement in the old power station, AusNet have noted that soil in the vicinity of the basement is impacted with hydrocarbons; and that the water is impacted with faecal matter from the septic tank at the old HWPS. | 1 | 1 | 3 | 2 | 3 | 1 | 1 |  | Oil/water separator, shut off valve and bunding around generator | 3 | <10 kg or <50 mg/kg | Small | Yes | <1,000 L | Default Chemicals | Yes - Small Volume | Yes - LPG | Spoil / Waste | Yes - Septic |  |  | Default Asbestos |  | No | [6 empty] | 4 | 5 | 1 | Yes | 2 | No |  | 4 | C | C | Yes | Potentially contaminating activities and contamination reported in previous investigation. Not significant for ongoing commercial land use but would be significant if land use changed. | Stockpiles are still present but have not been sampled | No | Stockpile sampling necessary to confirm if triggers have been met | Y | Y | Sample stockpiles if present. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP | ERM - Hazelwood Switchyard - Final Baseline Assessment (2018) | GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002); ERM 2018, Hazelwood Switchyard, Final Baseline Assessment, June 2018 |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No | No | Yes | No | No | No | No | No | No | No | Yes | No | No |  |  |  | N/A | Central | TBC | TBC | C2 | Enviro - NA | Y | Confidence 5/5. ERM report from 2018 and BlueSphere WQIP report from 2022 available. | Risk driven by presence of oil containing equipment, fuel storage, generators and batteries. There is a flooded basement in the old power station, AusNet have noted that soil in the vicinity of the basement is impacted with hydrocarbons; and that the water is impacted with faecal matter from the septic tank at the old HWPS. PRA notes presence of stockpiles. Bunding rating 3/5. Oil/water separator, shut off valve and bunding around generator. | 1. Check status of basement and stormwater drainage at site (is the drainage at site contributing to the flooded basement). 2. Service and repair leaking oil filled equipment. 1 transformer on site. 3. Replace brick bund (1) with concrete hardstand. 4. Confirm the status of the stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. |  |  |  | x |  |  |  | C-I-C |  |  |  |  | C-I-C |  |  |  |  | C-I-C
Comms Site | Hazelwood Test Hut | TBC TC-Hazel |  | HAZELWOOD DRIVE, HAZELWOOD, VICTORIA 3840 | None | -38.2869 | 146.5057 | TBC | TBC | Leased | Active | In HWTS Comms 11/11/20 Mark S | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 3 | 5 | 4 | 5 | 5 | 5 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | A | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | North | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Hazelwood TS (HWTS) | TS-HWTS | East | 530 Tramway Road, Hazelwood North, Victoria, 3840 | 2G~A\PP2749 | -38.2799 | 146.4309 | AusNet Services Transmission Group Pty Ltd | Zinfra | Freehold | Active | Done | Yes / Yes | 2021-02-24 | M Snell | Yes | Yes | WSP (2023) | AusNet, Transmission Sites, Portfolio EMP |  |  | WSP - DSI (2023), Aecom - HWTS 500 kV EMF Assessment Report (2023), Water Quality Investigation Program-BSE(2022), Water Quality Investigation Program, Phase 2 of Works for High-Risk Sites-BSE (2023), | Geo-Eng - Environmental Risk Assessment (1996). EES - Groundwater Monitoring at HWTS, HWPS and MWTS (2005). GHD - Confirmation Groundwater Monitoring (2005). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) | 2023-09-01 | 5 | 41 | Oil separation pit overflow in 2019, 100-200 L oil spill in 2020 that was subsequently cleaned up by vacuum truck. Discharge from oil/water separation discharge point in 2020. Historic report indicates drainage discharge exceeding discharge criteria (GHD, 2003) | 4 |  | Potential contaminated fill material, historic report also reports low-level contaminated soil |  | 5 | Oil containing equipment, fuel, batteries & SF6/gas cylinders | Varying | 3 | 4 | 5 | 5 | 4 | 1 |  |  | 5 | <10 kg or <50 mg/kg | Large | Yes | <1,000 L | Default Chemicals | Yes - Small Volume | Yes - LPG | Spoil / Waste | Yes - Septic |  |  |  |  | No |  |  | None |  |  |  | 3 | 4 | 4 | Yes | 3 | Yes | 4 | 4 | C | D | Yes | Infrastructure with high potential for contamination | No soil or groundwater contamination reported in previous reports. No evidence of notifiable contamination. | Possible | Stockpiles | Y | Y | PSI with limited soil sampling program. GME from existing wells. Sample stockpiles. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP |  | Geo-Eng - Environmental Risk Assessment (1996). EES - Groundwater Monitoring at HWTS, HWPS and MWTS (2005). GHD - Confirmation Groundwater Monitoring (2005). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 2 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | North | TBC | TBC | C3 | Enviro - one above ground system stormwater isolation valves fitted | Y | Confidence 5/5. Multiple environmental reports. | Status of oil leaks and proximity to environmental receptors driving risk rating. In 2020 there was an overflow of an oil separation pit where 100-200 L had to be cleaned up. Bunding rating of 4 however BSE WQIP (2022) photos suggest concrete bunds for operational transformers which potentially have some one way valves that may not be configured properly. WQIP suggested to check integrity. Brick bunding noted on old transformers that are not in use. Elevated concentrations of hydrocarbons detected in pond that collects water draining off site by BlueSphere in 2022. | 1. Service and repair leaking transformers. 2. Clean and Inspect bunds, and confirm integrity. 3. Conduct site inspection to confirm whether any brick bunds are being used for operational oil filled equipment. 4. Replace brick bunds with concrete hardstand bunds. 5. Resolve drainage/ overflow issues, potentially reconfigure drainage. 6. Install GAC scrubbing unit post puraceptor to further decrease hydrocarbon load. |  | C-I-C | C-I-C | x |  | C-I-C | [11 empty] | C-I-C
Comms Site | Hazelwood TS Comms Site (HWTS-COMS) | TC-HWTSXXXX |  | Tramway Road, Hazelwood VIC 3841 (in HWTS) | 2G~A\PP2749 | -38.2799 | 146.4309 | AusNet Services Transmission Group Pty Ltd | Zinfra | Freehold | Active | Done | Yes / Yes | 2020-11-11 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | A | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | North | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Heatherton TS (HTS) | TS-HTSX | Central | 495-503 Warrigal Road, Heatherton, Victoria, 3202 | 1\TP318304 | -37.9411 | 145.0773 | TBC | TBC | Freehold | Active | 2020-06-16 | Yes / Yes | 2020-06-16 | A Ryan | Yes | WSP(2023) |  | AusNet, Transmission Sites, Portfolio EMP |  |  | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021), PSI-WSP (2023), GME-GeoWorks (2005) | Geo-Eng - Environmental Risk Assessment (1996). Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003). A.S. James - Environmental Sampling and Analysis for Offsite Disposal (2013). | 2023 | 5 | 55 |  | 4 |  | Historic oil contaminated soil taken to open land at back - testing available? | Low | 5 | Minor surface staining beneath the transformers (within concrete bund) that was consistent with leaking/spilled transformer oil, stockpiles consisted of various material such as asphalt, concrete, rocks or gravel and piles of tree branches/material | 4 | 3 | 1 | 1 | 1 | 2 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume | Yes - LPG | Verified clean fill | None | Yes |  |  |  | No |  | NAPL Present |  |  |  |  | 3 | 4 | 3 | No | 5 | Yes | 3 | 4 | C | C | Yes | Infrastructure with high potential for contamination | Limited testing has not identified contamination. | No |  | Stage 1 complete |  | PSI with limited soil sampling program. GME from existing wells. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021) | Geo-Eng - Environmental Risk Assessment (1996). Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003). A.S. James - Environmental Sampling and Analysis for Offsite Disposal (2013). |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | North | TBC | TBC | C1 | Enviro -one above ground system in place ansd stormwater isolation valves fitted | N | Confidence 5/5. Recent environmental information available (WSP 2024) | Risk being driven by NAPL and UST presence in PRA, however not in WSP 2024 report. 3/5 oil leak rating and consequence of environmental impacts. | 1. Confirm if UST and LNAPL present. 2. Remove UST and validate (if present) 3. Service and repair leaking transformers. 4. Clean bund surfaces. 5. Check bund integrity. 6. LNAPL delineation, remediation etc (if required after recommendation 1) | C-I-C | C-I-C | C-I-C | x | [13 empty] | C-I-C
Terminal Station | Heywood TS (HYTS) | TS-HYTS | West | 79 Rifle Range Road, Heywood, Victoria 3304 | 27~A\PP3278 | -38.1815 | 141.6393 | TBC | TBC | Freehold | Active | UPLOAD 20/03 | Yes / Yes | 2020-11-09 | A Ryan | Yes | Yes | [5 empty] | Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 32 |  |  |  |  | Medium Risk | 5 | Oil containing equipment, diesel generator, SF6/gas cylinders, batteries | 0 | 3 | 1 | 1 | 1 | 2 | 1 |  | Fully compliant sealed bund, puraceptor oil/water separator and shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | <1,000 L | Default Chemicals | Yes - Small Volume | Yes - LPG | Spoil / Waste | Yes - Septic |  |  |  |  | No | [6 empty] | 4 | 4 | 3 | Yes |  |  |  | 4 | C | C | Yes |  |  | #REF! |  | Y | Y | [8 empty] | Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | North | TBC | TBC | C3 | Enviro - one above ground system, stormwater isolation valves fitted, run off issues from remote bays to 22kv switchroom has been mitigated with rock drains to try to curb the erosion being created, will need to look at this as area is all sand | Y | Confidence 3/5. No environmental information post 2003. | Risk is being driven by presence of oil containing equipment, diesel generator, SF6/gas cylinders, batteries. No transformers on site. Oil leak rating 3/5. Consequence of contamination driven by potential environmental and human health impacts. | 1. Investigate and amend soil erosion issue. Initially, conduct a site inspection to ascertain erosion status and obtain updated environmental information. 2. Repair leaking oil filled equipment (if not transformer, likely a generator) 3. Clean bund surfaces. 4. Check bund integrity |  | C-I-C | C-I-C | x | [13 empty] | C-I-C
City Gate | Hoppers Crossing (Forsyth Rd) City Gate | FORS |  | Forsyth Rd, Hoppers Crossing VIC 3029 | None | -37.8599 | 144.7311 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2021-01-12 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | Check | 4 | 4 | 5 | 5 | 5 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 5 |  |  |  | 1 | 3 | B | D | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | Central | TBC | TBC | [23 empty] | C-I-C
City Gate | Hoppers Crossing (Heaths Rd) City Gate | HEAT |  | Heaths Road, Hoppers Crossing, Victoria 3029 | None | -37.8777 | 144.6847 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-19 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 4 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Horsham City Gate | HORS |  | Burnt Creek Dr, Bungalally VIC 3401 | None | -36.7609 | 142.2411 | TBC | TBC | TBC | TBC | Uploaded 14/03 | Yes / Yes | 2021-02-26 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | Check | 3 | 4 | 5 | 5 | 4 | 2 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | B | D | No |  |  | #REF! | [13 empty] | 3 | 2 | 4 | 3 | 2 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Horsham TS (HOTS) | TS-HOTS | West | Williams/Riverside East Roads, Horsham, Victoria 3400 | 1\TP342215 | -36.7224 | 142.2474 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-08-26 | CJ Wilson | Yes | Yes | [5 empty] | Groundwater Monitoring (2005). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 14 |  |  |  |  | Medium Risk | 5 |  | 0 | 1 | 1 | 2 | 2 | 1 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | >10 kg or >50 mg/kg | Large | Yes | None | None | Yes - Small Volume |  | Spoil / Waste | [5 empty] | No | [6 empty] | 3 | 4 | 4 | Yes |  |  | 2 | 4 | A | C | No |  |  | #REF! | Stockpiles | Y | Y | [8 empty] | Groundwater Monitoring (2005). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 3 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | C3 | Enviro - one above ground system, stormwater isolation valves fitted, material of yards contaminate the enviro system and gets into the stormwater drains | N | Confidence 3/5. No environmental information post 2005. | Risk drivers include proximity to environmental receptors and storage of fuels, presence of spoil/ stockpile. Site has a fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank. 2020 site inspection shows no leaks of transformers and minimal staining. Sheen was observed on the surface of the TIP in 2005. Groundwater results in 2005 were <LOR. | 1. Confirm the status of the stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. 2. Service and repair leaking transformers. 3. Conduct site inspection to inform extent of contaminants leaking from the yards. 4. Review drainage configuration at site to ascertain flow pathways from yards. 5. Install GAC scrubbing unit on the puraceptor, as sheen noted on the surface of water in the TIP historically, and leaking from yards into stormwater drains in 2024. 6. Clean bund surfaces. 7. Check bund integrity. |  | C-I-C | C-I-C | x |  | C-I-C | [11 empty] | C-I-C
Switchyard | Hull Rd Switchboard Sub (HUSB) | DS-HUS |  | Part 456 Hull Rd, Mooroolbark VIC 3138 (150m east of Mooroolbark Rd) | 1\LP76307 | -37.7752 | 145.3317 | TBC | TBC | Leased | Active | LOOK UP NOTES | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 0 | 3 | 4 | 5 | 5 | 4 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | B | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Comms Site | Jeeralang Hill Comms Site (JERH) | TC-JERHXXXX |  | Off Jeeralang North Road (655 Thomson Road), Jeeralang, Victoria 3840 | 1\TP170215 | -38.3456 | 146.4747 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-08-01 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 5 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Switchyard | Jeeralang Switchyard | TBC SS-Jeer |  | Bonds Lane, Jeeralang VIC 3840 | None | -38.2723 | 146.4262 | TBC | TBC | Leased | Active | In Jeeralang Terminal Station GS 66kV SUB Station | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 0 | 3 | 4 | 5 | 5 | 4 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | B | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Jeeralang TS (JLTS) | TS-JLTS | East | Bonds Lane, Jeeralang VIC 3840 | None | -38.2723 | 146.4262 | TBC | TBC | Pending Acquisition | Pending Acquisition | UPLOAD 20/03 | Yes / Yes | 2021-01-19 | M Snell | Yes | Yes | [5 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | [5 empty] | Low | 3 | Oil containing equipment, batteries | 3 | 1 | 4 | 5 | 5 | 3 | 1 |  | Hardstand with regular inspections of equipment | 5 | None | Small | Yes | None | None | Yes - Small Volume | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | [5 empty] | 3 | B | D | Yes |  |  | #REF! | [11 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | Central | TBC | TBC | C2 | Enviro - NA | Y | Confidence 3/5. No environmental information post 2003 | Risk is driven by consequence of contamination and likelihood of contamination. There is no oil water separator or shut off valve. Bunding 4/5. 5/5 likelihood of contamination. Site has hardstand with regular equip inspections. Oil containing equipment and batteries. Brick bund with trench through bunded area. All stormwater runs directly off site. Oil filled equipment includes circuit breakers (2021 site inspection), minimal leaks. | 1. Install oil water separator (puraceptor) 2. Install shut off valve 3. Replace brick bund with concrete bund and hardstand. 4. Conduct site inspection to confirm contamination status. | [7 empty] | C-I-C |  |  | C-I-C | [5 empty] | C-I-C | C-I-C
Sub Station | Kalimna West Zone Substation (LKE) | TBC DS-Kalimna |  | 10 COMERS ROAD, KALIMNA WEST, VICTORIA 3909 | 1\PS421104 | -37.8777 | 147.9616 | TBC | TBC | Freehold | Active | Uploaded 17/03 | Yes / Yes | 2021-02-10 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 1 | No contaminating activities | 0 Transformers. Circuit Breakers | 1 | 1 | 1 | 1 | 1 | 1 |  | Not required | 1 | None | None | None | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 1 | 1 | 3 |  |  |  | 4 | 2 | B | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Sub Station | Kalkallo ZSS (KLO) | DS-KLO | Central | 30 Donnybrook Rd, Mickleham VIC 3064 | B\PS623515 | -37.5387 | 144.9414 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-29 | A Ryan | Yes | [8 empty] | 2 | 11 | [5 empty] | 5 |  | 2 | 1 | 1 | 2 | 2 | 1 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | None | Large | Yes | None | Default Chemicals | Yes - Small Volume |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 2 |  |  |  | 2 | 4 | B | C | No |  |  | #REF! |  |  |  |  | Yes | Stage 1 - due 2017 | [7 empty] | Varying | 1 | 2 | 1 | 1 | 1 | 4 | 2 | 3 | 3 | 3 Rare: D | N/A |  | N/A | No | Check | Depot/office | No | Yes | No | No | No | No | No | No | Yes | Yes | No | Yes | 0 |  |  |  | Electricity Transmission | Central | TBC | TBC | [23 empty] | C-I-C
Comms Site | Kangaroo Ground Radio Site Agreement | TBC TC-Kanga |  | ELTHAM PARK, KANGAROO GROUND, VICTORIA 3097 | None | -37.6883 | 145.2244 | TBC | TBC | Freehold | Active | Daniel Dobrosak not aware of this site | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 4 | 4 | 5 | 5 | 5 | 5 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 5 | 2 | 1 | 5 | 5 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Keilor TS (KTS) | TS-KTSX | Central | 86 Dodds Road, Keilor East, Victoria, 3036 | 1\TP224240, 4\PS346574, 3\PS346574 & 2\PS346574 | -37.738 | 144.8461 | AusNet Services Electricity Services Pty Ltd | Zinfra | Freehold | Active | Done | Yes / Yes | 2020-06-02 | A Ryan | Yes | Yes |  | AusNet, Transmission Sites, Portfolio EMP |  |  | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021), Water Quality Investigation Program-BSE(2022), Water Quality Investigation Program, Phase 2 of Works for High-Risk Sites-BSE (2023) | Geo-Eng - Environmental Risk Assessment (1996). Preliminary Groundwater Investigation 2003. Geoworks - Phase 1 Site Investigation (2003). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) | 2023-09-01 | 5 | 9 | Less than 1L hydraulic oil leaked from hose under pressure and dark contaminated soil encountered during excavation in 2021 | 5 | 4 | Significant soil removed and some level of remediation completed for some sections, old leaky transformers not remediated or controlled | Medium Risk | 5 | Oil containing equipment, stockpiles, batteries, chemical & SF6/gas cylinders, The pump from the HT to the puraceptor was observed to be leaking oil A hydrocarbon / paint smell was noted to be coming from the puraceptor unit, Staining was observed on the concrete and ground surface in the vicinity of the radiators, Weak hydrocarbon smell coming from isolation valve pit. This is the last point prior to off – Site discharge (2022) | 2 | 3 | 3 | 1 | 3 | 3 | 5 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | >10 kg or >50 mg/kg | Large | Yes | Fuel Default | Default Chemicals | Yes - Small Volume | Yes - LPG | Contaminated soil - safe for current use | Yes - Septic |  |  | Default Asbestos |  | No | [6 empty] | 2 | 5 | 2 | Yes | 3 | No | 4 | 5 | C | B | Yes | Contaminated stockpiles | TRHs around transformer T2, but below notification triggers | No |  | Stage 1 complete | Y | PSI with limited soil sampling program. GME from existing wells. EMP, ESC for stockpiles. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021) | Geo-Eng - Environmental Risk Assessment (1996). Preliminary Groundwater Investigation 2003. Geoworks - Phase 1 Site Investigation (2003). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 8 | 5 | 1 | 1 | 5 | 5 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | East | TBC | TBC | C5 | Enviro -one above ground system in place and stormwater isolation valves fitted, issue is capacity and the holding tanks ability to manage so many transformers catchment areas and until the A trans deluge is removed its an issue, A trans due to be replaced soon, this will remove the deluge and add a second processing system, but until then? | N | Confidence 5/5. Multiple environmental reports and site visits. | Risk driven by oil leaks and known offsite discharge of water to environmental receptor. KTS has oil containing equipment, stockpiles, batteries, chemical & SF6/gas cylinders, The pump from the HT to the puraceptor was observed to be leaking oil. A hydrocarbon / paint smell was noted to be coming from the puraceptor unit, Staining was observed on the concrete and ground surface in the vicinity of the radiators, Weak hydrocarbon smell coming from isolation valve pit. This is the last point prior to off – Site discharge (2022). Oil leak score 3/5 | 1. Improve puraceptor, add GAC scrubbers. 2. Install temporary holding tank per DZ108 note. 3. Service and repair all transformers. 4. Periodically inspect existing holding tank to confirm that is remains functional 5. Clean bund surfaces. 6. Check bund integrity |  | C-I-C | C-I-C | x |  | C-I-C |  |  |  | C-I-C | [7 empty] | C-I-C
Terminal Station | Kerang TS (KGTS) | TS-KGTS | West | Loddon Valley Highway, Kerang, Victoria 3579 (5km SE Kerang) | 1\TP337631 | -35.7714 | 143.9341 | AusNet Services Electricity Services Pty Ltd | Zinfra | Freehold | Active | Done | Yes / Yes | 2020-07-30 | CJ Wilson | Yes | Yes | WSP (2023) |  |  |  | Water Quality Investigation Program-BSE(2022), Phase 2 of Works for High-Risk Sites-BSE (2023) | Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003), BSE - wastewater quality investigation program (WQIP) (2022), WSP - DSI (2023) | 2023-01-01 | 4 | 59 |  | 1 | 1 | Formerly vacant/grazing land use. | Medium Risk | 5 | Oil containing equipment, batteries & SF6/gas cylinders, 17 transformers, two capacitor banks, oil filled equipment noted leaking into concrete lined service trench outside of the diesel generator building, TRH contamination in drainage newtwork (BSE, 2022 report) | 17 | 5 | 3 | 1 | 3 | 5 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 5 | <10 kg or <50 mg/kg | Large | Yes | Fuel Default | Default Chemicals | Yes - Small Volume | Yes - LPG | Spoil / Waste | Yes - Septic | Yes |  | Default Asbestos |  | No |  |  | None |  |  |  | 4 | 5 | 1 | Yes |  |  | 1 | 4 | C | D | Yes |  |  | #REF! |  | Y | Y | [8 empty] | Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 2 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | Central | TBC | TBC | C1 | Enviro - one above ground system, stormwater isolation valves fitted, | Y | Confidence 4/5. Environmental report from 2022. | Risk driven by presence of potentially contaminating activities and proximity to environmental receptors. Septic tank on site. This includes presence of a UST and oil leak rating of 3/5. Leaking transformers noted. There is a spoon drain that needs repairing. Water goes out to the Loddon Valley highway without pretreatment. Bund repairs were required. Hydrocarbons detected in surface water post last triple interceptor in 2022. | 1. Remove and validate a UST. 2. Service and repair leaking transformers. 3. Repair spoon drain. Currently socks are in the drain but this is a temporary fix until leaks are repaired. 4. Repair bunds. 5. Resolve status of septic tank. If in use, service. If not, decommission and remove. 6. Clean bund surfaces. 7. Check bund integrity. 8. Install GAC post puraceptor to further reduce hydrocarbon load. | C-I-C | C-I-C | C-I-C | x |  | C-I-C | C-I-C | C-I-C | [9 empty] | C-I-C
Sub Station | Kilmore South ZSS (KMS) | DS-KMS | North | 175 Quinns Road, Kilmore, Victoria 3764 | RES1\PS312688 | -37.3166 | 144.9717 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-23 | A Ryan | Yes | [8 empty] | 2 | 10 | [5 empty] | 2 |  | 2 | 2 | 4 | 3 | 4 | 3 | 1 |  | Brick bund with gravel floor and basic oil/water separator - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 3 |  |  |  | 1 | 3 | B | D | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 4 | 1 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No | No | No | No | No | No | No | No | Yes | No | No | No | No | N/A | N/A | N/A | N/A | Central | TBC | TBC | [23 empty] | C-I-C
Comms Site | Kinglake Comms Site (KING) | TC-KINGXXXX |  | 223 Whittlesea Kinglake Rd, Kinglake VIC 3763 | 1\TP246653 | -37.5272 | 145.3363 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-18 | A Ryan | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 5 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 4 |  |  |  | 4 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | North | TBC | TBC | [23 empty] | C-I-C
Sub Station | Kinglake ZSS (KLK) | DS-KLK | Central | 339 Kinglake-Whittlesea Road, Kinglake, Victoria 3763 (cnr Bowden Spur Road) | 1\TP246653, 13\LP41480, 2\LP47163 | -37.5144 | 145.3164 | TBC | TBC | Freehold, Leased, Freehold | Active | Done | Yes / Yes | 2020-06-18 | A Ryan | Yes | [8 empty] | 2 | 2 | Oil spill from CT mech box during prep for transport in 2019 |  |  |  |  | 5 |  | 2 | 2 | 1 | 2 | 2 | 2 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 4 | 4 | C | C | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | Interstate | TBC | TBC | [23 empty] | C-I-C
City Gate | Koroit City Gate | KORO |  | Koroit-Woolsthorpe Rd, Koroit VIC 3220 | None | -38.258 | 142.3822 | TBC | TBC | Freehold | Active | Complete | Yes / Yes | 2021-04-14 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | [5 empty] | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Comms Site | Koroit Radio Transmitters | TBC TC-Koroit |  | COMMERCIAL ROAD, KOROIT, VICTORIA 3282 | None | -38.2921 | 142.3668 | TBC | TBC | Licensed | ACTIVE | Gas radio? (A Ryan) Daniel Dobrosak not aware of this site | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 5 | 3 | 4 | 5 | 5 | 4 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | B | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | North | TBC | TBC | [23 empty] | C-I-C
City Gate | Kyneton City Gate | KYNE |  | Lauriston-Reservoir Rd, Kyneton, Victoria 3444 | None | -37.2551 | 144.4373 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-17 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | Check | 2 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 3 | 1 | 4 | 4 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | North | TBC | TBC | [23 empty] | C-I-C
City Gate | Lancefield City Gate | LANC |  | Melbourne-Lancefield Rd, Lancefield VIC 3435 | None | -37.3037 | 144.737 | TBC | TBC | Freehold | Active | 2021-05-26 | Yes / Yes | 2021-05-26 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | No | 1 | 4 | 5 | 5 | 3 | 4 |  |  | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | [5 empty] | 2 | C | E | No |  |  | #REF! | [13 empty] | 3 | 4 | 2 | 3 | 4 | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Sub Station | Lang Lang ZSS (LLG) | DS-LLG | Central | Western Port Rd (between McDonalds Track and Bass Hwy), Lang Lang VIC 3984 | 1\PS542732 | -38.2674 | 145.5565 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-07-23 | A Ryan | Yes | [8 empty] | 2 | 16 | [5 empty] | 2 |  | 1 | 1 | 1 | 2 | 2 | 1 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | None | Large | Yes | None | None | Yes - Small Volume | None | Spoil / Waste | None |  |  |  |  | No | [6 empty] | 3 | 2 | 2 |  |  |  | 1 | 3 | C | D | No |  |  | #REF! |  | Y | [11 empty] | 1 | 1 | 1 | 3 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
City Gate | Lara City Gate | LARA |  | Cozens Lane, Lara, Victoria 3212 | 6A~6B\PP5452 | -38.0397 | 144.4158 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-11-16 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 0 | 3 | 4 | 5 | 5 | 4 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 2 | 1 | 5 | 3 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | North | TBC | TBC | [23 empty] | C-I-C
City Gate | Laverton North City Gate | LAVE |  | Fitzgerald Road, Laverton North, Victoria, 3026 | None | -37.8274 | 144.7861 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-19 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 6 | 3 | 4 | 5 | 5 | 4 | 4 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 2 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 3 | 4 | 2 | 3 | 4 | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | Interstate | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Leongatha Depot | WH-0013 |  | 60 Horn Street, Leongatha, Victoria 3953 | 1\TP539545,1\TP742417 | -38.4731 | 145.9585 | AusNet Services Electricity Services Pty Ltd | Downer | Freehold | Active | UPLOAD 20/03 | Yes / Yes | 2020-05-20 | D Green | Yes | [8 empty] | 2 | [6 empty] | 2 | Minor chemical/fuel storage | 1 | 1 | 1 | 2 | 2 | 1 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank 0 no shut off valve | 2 | None | Oil Default | None | Fuel Default |  | Yes - Small Volume | Yes - LPG | None | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 2 | 4 | C | C | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 2 | 3.5 | 4 | 4 Rare: C | N/A | On Yarra River | #N/A | #N/A | #N/A | Depot/office | No | No | No | No | No | No | No | No | Yes | No | No | No | No |  |  |  | N/A | Central | TBC | TBC | [23 empty] | C-I-C
Sub Station | Leongatha ZSS (LGA) | DS-LGA | East | 62 Horn Street, Leongatha, Victoria 3953 (cnr Turner St) | 1\TP247958 & 1\TP539545 | -38.4725 | 145.9584 | TBC | TBC | Freehold | Active | Uploaded 16/03 | Yes / Yes | 2021-01-29 | M Snell | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 7 |  | 4 |  | Concreted over former leaks, oil coming back up |  | 4 | Oil containing equipment, batteries & SF6/gas cylinders | 8 | 5 | 4 | 5 | 5 | 5 | 3 |  | Brick bund with gravel floor | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 4 |  |  |  | 4 | 3 | A | D | Yes | Potential contaminating activities. | Investigate leakage and condition of hardstand, likely needs targeted sampling in accordance with Duty to Manage. No Duty to Notify | #REF! | Historical leakages, concreted over former leaks, oil coming back up, however, as sealed exposure not likely, no Duty to Notify |  |  | PSI with limited soil sampling program. | Yes | Stage 1 - due 2017 |  |  |  | AusNet, Distribution Sites, Portfolio EMP |  |  |  | Various | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 Possible: B | N/A | Overgrown weeds and broken fences noted. | #N/A | No | No | Depot/office | Yes | Yes | No | No | No | Yes | No | Yes | Yes | Yes | No | No | No | N/A | N/A | N/A | N/A | Central | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Lilydale Depot | WH-0014b |  | 30 Melba Ave, Lilydale, Victoria, 3140 | 1-9\PS443459 & B\SP22391 | -37.7611 | 145.347 | External Land Owner- Leased Facility | Downer | Leased | Active | Uploaded 14/03 | Yes / Yes | 2021-02-24 | Jessica Mendes | Yes | Yes |  | Leased land - Downer in management control |  | Historic PAN re contaminated bunding |  | Bunding upgrade report 2016, EPA Site Inspection report |  | 5 |  | Large quantity of oil spilled from kiosk or in transit in 2018, 10-15 litres of oil spilled due to mechanical failure in 2019, leaking transformers impacting bunded area iin 2020 |  |  |  |  | 4 | Oil containing equipment, generators and UST | 1 | 1 | 4 | 3 | 4 | 2 | 3 |  | Brick bund with gravel floor and basic oil/water separator - no shut off valve | 4 | None | Oil Default | None | Fuel Default | None | Yes - Small Volume | Yes - LPG | None | None | Yes |  |  |  | No | [6 empty] | 4 | 4 | 4 |  |  |  | 4 | 4 | B | D | Yes | Potentially contaminating infrastructure, including UST | No investigation undertaken | #REF! | NA |  |  | PSI with limited soil and groundwater investigation focussed on UST. |  |  |  |  | Check location of spills etc relative to sealed areas | Leased land - Downer in management control |  | Bunding upgrade report 2016, EPA Site Inspection report | Historic PAN re contaminated bunding | Various | 3 | 1 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 Unlikely: C | N/A | Treated poles on site. | #N/A | Interceptor blocked. Now fixed. | No | Depot/office | Yes | Yes | No | No | No | No | No | No | Yes | No | No | Yes | No |  |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Sub Station | Lilydale ZSS (LDL) | DS-LDL | Central | 455 Swansea Road, Lilydale, Victoria, 3140 | 2\PS546466 & 3\PS546466 | -37.7635 | 145.358 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-22 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 13 | [5 empty] | 5 |  | 3 | 1 | 4 | 4 | 4 | 2 | 2 |  | Brick bund with gravel floor with shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | Spoil / Waste | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 5 |  |  |  | 2 | 3 | C | D | Yes | Potential contaminating activities. |  | #REF! | Stockpiles | Y |  | PSI with limited soil sampling program. Sample stockpiles if present. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | Various | 2 | 1 | 3 | 2 | 2 | 3 | 4 | 3.5 | 4 | 4 Unlikely: C | N/A | Oil tanker in process of removal | #N/A | #N/A | #N/A | Depot/office | No | No | No | No | No | Yes | No | No | Yes | No | No | No | No | N/A | N/A | N/A | N/A | Central | TBC | TBC | [23 empty] | C-I-C
Comms Site | Lookout Hill Comms Site (LOOK) | TC-LOOKXXXX |  | Mount Cole State Forest, Mount Cole VIC 3377 | None | -37.2824 | 143.2467 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-08-26 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 5 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Yes | Yes | No | Yes | No | Yes | No | No | Yes | Yes | No | No | #N/A |  |  |  | Electricity Transmission | Central | TBC | TBC | [23 empty] | C-I-C
Comms Site | Loy Yang Communications Test Huts | TBC TC-LL |  | BARTONS LANE, LOY YANG, VICTORIA 3844 | None | -38.2503 | 146.5724 | TBC | TBC | Leased | NO AGREEMENT | Part of Loy Yang 66kV SUB Station Mark S | No assessment needed |  |  | N/A | Yes |  |  |  | Clean Up Notice for Groundwater Attenuation Zone |  | Clean Up Notice. SKM - Groundwater Assessment (2001) |  | 3 |  | Groundwater attenuation zone established as a result of Loy Yang Ash Pond |  |  |  |  | 1 |  | 1 | 1 | 4 | 5 | 5 | 3 | 3 |  |  | 5 | None | [12 empty] | No | [6 empty] | 1 | 1 | [5 empty] | 1 | C | D |  |  |  | #REF! | [11 empty] | Clean Up Notice. SKM - Groundwater Assessment (2001) | Clean Up Notice for Groundwater Attenuation Zone | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  | N/A |  | N/A | No | 0 | 0 | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | Central | TBC | TBC | [23 empty] | C-I-C
Switchyard | Loy Yang Power Station (LYPS) | TBC PS-LYPS |  | Bartons Lane, Loy Yang VIC 3844 | None | -38.2502 | 146.5772 | TBC | TBC | Leased | Active | Uploaded 17/03 | Yes / Yes | 2021-02-12 | M Snell | Yes | [6 empty] | GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 2 | [5 empty] | Medium Risk | 3 | Oil containing equipment and batteries | 1 | 1 | 4 | 2 | 4 | 2 | 1 |  | Brick bund with gravel floor and puraceptor oil/water separator + shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 2 |  |  |  | 2 | 3 | C | D | Yes |  |  | #REF! | [11 empty] | GHD - Environmental Inspections, Maintenance and Tests (2003) |  | TBC | 1 | 1 | 2 | 1 | 1 | 5 | 2 | 3.5 | 4 | 4 Rare: C | N/A | Fuel and oil for chainsaws stored in specific fuel locker in store. | N/A | No |  | Depot/office | Yes - Switchgear store items | Yes | No | No | Yes - vehicles | No | No | No | Yes | No | No | No |  |  |  |  | N/A | East | David Green | C | C2 | Enviro - NA | Y | Confidence 2/5. No environmental report since 2003. | Rating driven by bunding rating and presence of potentially contaminating activities. There is a brick bund with gravel floor and puraceptor oil/water separator + shut off valve. Oil containing equipment and batteries. 2021 site inspection noted that grey water discharges to yard surface. | 1. Replace brick bunds and gravel floors with concrete hardstand bunds. 2. Confirm that only grey water discharging to surface and not also septic. Could be done during a septic unit service. 3. Service and repair transformers and any leaking oil filled equipment. 4. Complete site inspection to confirm environmental status of site. |  |  |  | x |  |  | C-I-C | C-I-C | [9 empty] | C-I-C
Comms Site | Loy Yang Power Station Transformer | TBC TC-LL2 |  | LOY YANG P.S., LOY YANG, VICTORIA 3844 | None | -38.2534 | 146.575 | TBC | TBC | Leased | NO AGREEMENT | Part of PS-LYPS assessment. Mark S confirmed | No assessment needed |  |  | N/A | [6 empty] | GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002) |  | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 5 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [11 empty] | GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002) |  | 3 | 5 | 2 | 1 | 5 | 5 | 0 | 0 | 0 | 0 |  | N/A |  | N/A | No | 0 | 0 | Yes | Yes | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | N/A | Central | TBC | TBC | [23 empty] | C-I-C
Sub Station | Loy Yang South ZSS (LYS) | DS-LYS | East | Bartons Lane, Loy Yang, Victoria 3844 | Part of 1\PS340417 | -38.2502 | 146.5772 | TBC | TBC | Leased | Active | Uploaded 17/03 | Yes / Yes | 2021-03-16 | M Snell | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP |  |  |  | GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 5 | 41 | [5 empty] | 3 | Oil containing equipment and batteries | 3 | 4 | 4 | 4 | 4 | 4 | 1 |  | Brick bund with gravel floor | 4 | None | Large | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 2 |  |  |  | 2 | 3 | C | D | Yes | Potential contaminating activities. |  | #REF! |  |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  | GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 2 | 1 | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  | N/A |  | N/A | No | 0 | 0 | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No | 0 |  |  |  | N/A | North | TBC | TBC | [23 empty] | C-I-C
Sub Station | Loy Yang ZSS (LY) | TBC DS-LY | East | Open Cut, Bartons Lane, Loy Yang, Victoria 3844 | None | -38.2502 | 146.5772 | TBC | TBC | Leased | Active | UPLOAD 20/03 | Yes / Yes | 2021-02-12 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 | Transformers | 1 | 1 | 5 | 5 | 5 | 3 | 1 |  | Hardstand/gravel and drainage | 5 | <10 kg or <50 mg/kg | Oil Default | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | [5 empty] | 3 | B | D | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No | Yes | No | No | No | No | No | No | Yes | No | No | Yes | #N/A |  |  |  | N/A | North | TBC | TBC | C2 | Enviro - NA | Y | Confidence 2/5. No environmental reports. | Risk rating driven by gravel surfaces and lack of bunds. Oil filled equipment known to be on site. Hardstand/gravel and drainage. Photos from site inspection show gravel surfaces. | 1. Install concrete bunds and hardstand surfaces. 2. Service and repair oil filled equipment. 3. Complete site inspection to confirm environmental status of the site. 4. Ensure that oil filled equipment is stored on hardstand. |  |  |  | x |  |  |  | C-I-C | [9 empty] | C-I-C
Sub Station | Lysterfield ZSS (LYD) | DS-LYD | Central | Jacques Road, Narre Warren North VIC 3804 | None | -37.9844 | 145.2959 | TBC | TBC | TBC | TBC | Done | Yes / Yes | 2020-05-26 | A Ryan | Yes | [8 empty] | 2 | 11 | [5 empty] | 4 |  | 1 | 1 | 1 | 1 | 1 | 1 | 4 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1 | None | Large | Yes | None | Default Chemicals | Yes - Small Volume |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 1 | 4 | B | C | No |  |  | #REF! | [13 empty] | 2 | 4 | 2 | 1 | 4 | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Yes | Yes | No | No | No | Yes | No | No | Yes | Yes | No | Yes | #N/A |  |  |  | N/A | North | TBC | TBC | [23 empty] | C-I-C
Sub Station | Maffra North Regulator (RMFN) | DS-RMF | East | Fulton Rd (near Golf Course), Maffra, Victoria 3860 | 2\PS607833 | -37.9505 | 146.9979 | TBC | TBC | Leased | Active | Uploaded 16/03 | Yes / Yes | 2020-10-20 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 3 | Oil containing equipment and batteries | 1 | 1 | 2 | 3 | 3 | 1 | 4 |  | Compliant bund with partial treatment | 3 | None | Oil Default | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 4 |  |  |  | 4 | 3 | C | D | Yes |  |  | #REF! | [13 empty] | 3 | 4 | 2 | 1 | 4 | 4 | 0 | 0 | 0 | 0 |  | N/A |  | N/A | No | 0 | 0 | No | No | No | No | Yes | No | No | Yes | Yes | No | Yes | No | 0 |  |  |  | N/A | Central | TBC | TBC | [23 empty] | C-I-C
Sub Station | Maffra ZSS (MFA) | DS-MFA | East | 32 Station Street, Maffra, Victoria, 3860 | 1A~9\PP5490 & 1B~9\PP5490 | -37.9707 | 146.9824 | TBC | TBC | Freehold | Active | Uploaded 17/03 | Yes / Yes | 2020-10-20 | M Snell | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 23 | Oil spill from transformer failure in 2020 | 5 | 1 |  |  | 3 | Oil containing equipment and batteries | 3 | 5 | 4 | 5 | 5 | 5 | 4 |  | Brick bund with gravel floor | 5 | <10 kg or <50 mg/kg | Large | None | None | None | None | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 5 |  |  |  | 1 | 3 | C | D | Yes | Potential contaminating activities. | NA |  | oil spill from transformer - since cleaned up |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 3 | 4 | 2 | 1 | 4 | 4 | 0 | 0 | 0 | 0 |  | N/A |  | N/A | No | 0 | 0 | No | No | No | No | No | No | No | Yes | Yes | No | Yes | No | 0 |  |  |  | N/A | Central | TBC | TBC | [23 empty] | C-I-C
Comms Site | Mallacoota/Cann River Comms Site (CNR) | TC-CNRXXXXX |  | NEAR CANN RIVER(& MARAMINGO HI, MALLACOOTA, VICTORIA 3892 | None | -37.5664 | 149.1512 | TBC | TBC | Leased | Expired | New | New |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 1 | 1 | 1 | 1 | 4 |  | New | 1 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | E | No |  |  | #REF! | [13 empty] | 2 | 3 | 4 | 3 | 4 | 4 | 0 | 0 | 0 | 0 |  | N/A |  | N/A | No | 0 | 0 | No | Yes | No | No | No | No | No | No | Yes | No | No | No | 0 |  |  |  | N/A | Central | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Malvern Depot | WH-1003 |  | 632-684 Waverley Road, Malvern, Victoria 3144 | 2\LP11096 | -37.877 | 145.0844 | TBC | TBC | Freehold | Active | Uploaded 14/03 | Yes / Yes | 2021-02-19 | James Weghorn | Yes | [6 empty] | GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 2 | [6 empty] | 3 |  | Various | 3 | 1 | 3 | 3 | 3 | 1 |  | Fully compliant sealed bund basic oil/water separator - no shut off valve | 3 | None | Oil Default | None | None | None | None | Yes - LPG | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 3 |  |  |  | 4 | 3 | B | D | Yes |  |  | #REF! | [11 empty] | GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 2 | 3 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | Central | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Malvern TS (MTS) | TS-MTSX | Central | 632-684 Waverley Road, Malvern VIC 3144 | 2\LP11096 | -37.878 | 145.0843 | TBC | TBC | Freehold | Active | 2020-05-28 | Yes / Yes | 2020-05-28 | A Ryan | Yes | Yes |  |  |  |  | AG:Water Quality Investigation Program-BSE(2022) | Geo-Eng - Environmental Risk Assessment (1996). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 14 |  |  |  |  | High | 5 | Oil staining was observed within the bunds of the transformer | 2 | 3 | 1 | 1 | 1 | 2 | 4 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals |  |  | None | [5 empty] | No | [6 empty] | 3 | 4 | 5 | Yes |  |  | 2 | 4 | B | C | Yes |  |  | #REF! |  |  | Y | [8 empty] | Geo-Eng - Environmental Risk Assessment (1996). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 2 | 3 | 4 | 5 | 4 | 4 | [31 empty] | C1 | Enviro -one above ground system in place ansd stormwater isolation valves fitted | N | Confidence 3/5. | Risk rating driven by oil staining in transformer bunds. Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1. Service and repair leaking transformers. 2. Inspect bunds and confirm integrity. 3. Clean bund surfaces. |  | C-I-C | C-I-C | [14 empty] | C-I-C
Depot, Office and Warehouse Storage | Mansfield Depot | WH-0015 |  | 16 Crosby Lane, Mansfield, Victoria 3722 | 2\LP210934 | -37.0648 | 146.1016 | Downer | Downer | Leased | Active | Sharepoint updated. Downer received lease - don't do | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 2 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 2 | 4 | 4 | 2 | 2 | [54 empty] | C-I-C
Sub Station | Mansfield ZSS (MSD) | DS-MSD | North | 3540 Maroondah Highway/Kidstone Road, Mansfield, Victoria 3724 | 1\TP633700 | -37.05 | 146.0714 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-07-20 | CJ Wilson | Yes | [8 empty] | 2 | 74 | Stormwater discharge to aged care retirement facility in 2020 |  |  |  |  | 2 |  | 2 | 3 | 4 | 5 | 5 | 4 | 4 |  | Brick bund with gravel floor | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 4 |  |  |  | 4 | 3 | B | D | Yes |  |  | #REF! |  |  |  | Remediation and validation to be undertaken as part of site upgrades | [9 empty] | 3 | 4 | 2 | 4 | 4 | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | Jacobs | A | [23 empty] | C-I-C
City Gate | Maryborough City Gate | MARY |  | Pyrenees Hwy, Maryborough, Victoria 3465 | None | -37.0235 | 143.7517 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-17 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 4 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 4 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 4 | 4 | 2 | 1 | 4 | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | Jacobs | A | [23 empty] | C-I-C
City Gate | Melton City Gate | MELT |  | Eynesbury Rd, Exford (Melton), Victoria 3338 | None | -37.727 | 144.5752 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-18 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 2 | 2 | C | E | No |  |  | #REF! | [13 empty] | 2 | 1 | 4 | 3 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | N/A | West | Jacobs | A | [23 empty] | C-I-C
Sub Station | Merrijig ZSS (MJG) | DS-MJG | North | Mt Buller Rd cnr School Lane, Merrijig VIC 3723 | None | -37.1024 | 146.2624 | TBC | TBC | TBC | Active | Done | Yes / Yes | 2020-07-15 | CJ Wilson | Yes | [8 empty] | 2 | 16 | [5 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 2 |  | Brick bund with gravel floor | 5 | None | Large | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 5 |  |  |  | 4 | 3 | C | D | Yes |  |  | #REF! |  |  |  | Remediation and validation to be undertaken as part of site upgrades | [9 empty] | 2 | 2 | 4 | 5 | 2 | 2 | 5 | 2 | 3.5 | 4 | 4 Possible: B | D |  | 2 PT 1984. | Yes - Old transformers pre-bunding upgrades. Bund walls added however rock floors in place | 0 | ZSS + REFCL project works | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | B | [23 empty] | C-I-C
Comms Site | Mincha West Comms Site (MINW) | TC-MINWXXXX |  | PART 532 MINCHA WEST-COHUNA ROAD, MINCHA WEST, VICTORIA 3568 | None | -35.8976 | 144.1309 |  |  | Leased | In Progress | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 5 | 5 | 5 | 3 | 3 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 0 | 3 | 2 | 1 | 3 | 3 | 5 | 1 | 3 | 3 | 3 Likely: B | C | Planning, 2021-25 | N/A | No | 0 | ZSS | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | B | [23 empty] | C-I-C
Comms Site | Mitiamo Comms Site (MITO) | TC-MITOXXXX |  | PART 183 MITIAMO FOREST ROAD, MITIAMO, VICTORIA 3573 | None | -36.1948 | 144.2317 |  |  | Leased | In Progress | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 5 | 5 | 5 | 3 | 3 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 3 | 3 | 3 | 2 | 3 | 3 | 4 | 2 | 3 | 3 | 3 Possible: C | D |  | 2 PT 1981 and 1 1999 | Yes - Old transformers pre-bunding upgrades. Bunding installed but rock floors remain | 0 | ZSS | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | C | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Moe Depot | TBC Moe |  | 55 Della Torre/Cnr Saviges Rd, Moe VIC 3825 | Part of 2\LP70191 & 9\LP112956 | -37.676 | 144.4388 | TBC | TBC | Freehold | Active | UPLOAD 20/03 Leased to transport company. Underfuel tank. | Yes / Yes | 2021-03-15 | M Snell | Yes | Yes |  | AusNet, Distribution Sites, Portfolio EMP |  |  |  | Geo-Eng - Preliminary Site Assessment (1996) |  | 5 |  |  | 3 |  | UST impacts unknown |  | 3 | Oil containing equipment and potential old petrol bowser on-site with potential UST, The No.1 & 2 Transformers are leaking and saturating the ground surface within bunding, filled drums present collecting spilled oil | 1 | 4 | 4 | 5 | 5 | 5 | 1 |  | Regular inspections and storage of gas cylinders | 5 | None | Oil Default | None | Fuel Default | None | Yes - Small Volume | Yes - LPG | None | Yes - Septic | Yes |  | Default Asbestos |  | No | [6 empty] | 4 | 5 | [5 empty] | 5 | B | D | Yes | UST potentially decomissioned, bowser in place. | No investigation of UPSS undertaken | Possible | Further data needed before trigger can be confirmed |  |  | PSI with limited soil and groundwater investigation focussed on UST. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  | Geo-Eng - Preliminary Site Assessment (1996) |  | 0 | 1 | 2 | 1 | 1 | 1 | 5 | 1 | 3 | 3 | 3 Rare: D | D |  | N/A | No | 0 | ZSS | Yes | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | D | [23 empty] | C-I-C
Sub Station | Moe ZSS (MOE) | DS-MOE | East | 55-57 Della Torre Road, Moe, Victoria, 3825 | Part of 2\LP70191 | -38.1705 | 146.256 | TBC | TBC | Freehold | Active | Uploaded 16/03 | Yes / Yes | 2020-12-31 | M Snell | Yes |  | WSP (2023) | AusNet, Distribution Sites, Portfolio EMP |  |  | WSP- DSI (2023), BSE- GME (2024) |  |  | 5 | 43 | [5 empty] | 4 | Oil containing equipment, batteries & SF6/gas cylinders | 2 | 4 | 4 | 5 | 5 | 5 | 1 |  | Brick bund with gravel floor | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | None | Yes - Septic |  |  |  |  | No |  |  | None |  |  |  | 3 | 3 | 4 | Yes | 5 | Yes | 3 | 3 | C | D | Yes | Potential contaminating activities. | Check surface covering in environmental assessment | #REF! |  |  | Y | PSI and soil classification prior to commencement. Remediation and validation to be undertaken as part of site upgrades. | Yes | Stage 3 - due 2020-2023 |  |  |  | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 3 | 1 | 1 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2 Rare: E | D |  | 2005, 2017, 2020 | No | Check | ZSS | Yes | No | No | Yes | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Moorabool TS (MLTS) | TS-MLTS | West | 680 Ballan Road (Lower Anakie Road), Moorabool, Victoria, 3221 | 1\TP237645 | -38.0374 | 144.2966 | AusNet Serves | Zinfra | Freehold | Active | Uploaded 17/03 | Yes / Yes | 2020-11-26 | CJ Wilson | Yes | Yes | [5 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 14 |  |  |  |  | Medium Risk | 5 | Oil containing equipment, diesel generator, SF6/gas cylinders, batteries | 2 | 2 | 1 | 1 | 1 | 1 | 3 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 2 | <10 kg or <50 mg/kg | Large | Yes | <1,000 L | Default Chemicals | Yes - Small Volume |  | Spoil / Waste | [5 empty] | No | [6 empty] | 4 | 4 | 3 |  |  |  | 2 | 4 | B | C | No |  |  | #REF! |  | Y | [9 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 2 | 3 | 2 | 1 | 3 | 3 | 2 | 2 | 2 | 2 | 2 Possible: D | D | Concrete edge bunding with crushed rock floor, there is a drain point in the corner which runs to in ground tanks, which are understood to be a basic triple interceptor system | 2 2001 | New site there should not be any contamination of the ground. | 0 | ZSS | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | D | C3 | enviro - one above ground system - question on capacity of holding tank due to deluge system and number/size of trans, and one below ground (new reactors) stormwater isolation valves fitted, | Y | Confidence 3/5. No environmental report since 2003. | Risk driven by presence of potentially contaminating activities and proximity to environmental receptors. Stockpiles noted in PRA. Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1. Confirm the status of the stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. 2. Service and repair leaking transformers. 3. Clean bund surfaces. 4. Confirm bund integrity. |  | C-I-C | C-I-C | x | [13 empty] | C-I-C
Comms Site | Moorabool TS Comms Site (MLTS-Comms) | TC-MLTSXXXX |  | 955 Anakie Road, Moorabool, Victoria, 3221 | 1\TP237645 | -38.0379 | 144.2967 | TBC | TBC | Freehold | Active | PART OF MOORABOOL TS ASSESSMENT (need confirmation) | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 8 | 3 | 4 | 5 | 5 | 4 | 5 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 3 | 5 | 2 | 4 | 5 | 5 | 5 | 2 | 3.5 | 4 | 4 Unlikely: C | D |  | 2 PT 1968 and 1 PT 1969 | Yes - Old transformers pre-bunding upgrades. Soil removed and some level of remediation completed before bunding upgrade. | 0 | ZSS | Yes - CB | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | C | N/A | Not in this list. | Y | Confidence 1/5. No environmental reports | Risk driven by presence of oil filled equipment and low confidence. Low oil leak and bunding scores. No environmental reports on environmental register. Bunding rated as 4 - typical brick bund with trench through bunded area. | 1. Complete Site inspection to confirm oil filled equipment and bund status. 2. Upgrade brick bunds to concrete hardstand bunds. 3. Service and repair leaking transformers and any other oil filled equipment. |  |  |  | x |  |  |  | C-I-C | [9 empty] | C-I-C
Terminal Station | Mortlake Power Station (MOPS) | TBC PS-MOPS | West | Connewarren Lane, Mortlake VIC 3272 | 2\PS620663 | -38.063 | 142.668 | TBC | TBC | Freehold | Active | UPLOAD 20/03 New station (A Ryan) | Yes / Yes | 2020-12-17 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 3 | SF6/gas cylinders and batteries | 2 | 2 | 4 | 5 | 5 | 3 | 2 |  | Batteries in designated room with administrative controls/inspections in place | 5 | None | None | Yes | None | None | Yes - Small Volume | Yes - LPG | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 4 |  |  |  |  | 3 | C | D | Yes |  |  | #REF! | [13 empty] | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 5 | 3 | 3 | 3 Rare: D | C | DD-7219 will be delivered 2021 | 2 1936 | No | 0 | ZSS | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | D | N/A | Not in this list. | Y | Confidence 2/5. No environmental reports. | Risk driven by low confidence and low level of environmental controls. SF6/gas cylinders and batteries. No shut off valve, gravel bund. | 1. Complete site inspection to confirm environmental status. 2. Service and repair leaking transformers 3. Install shut off valve. 4. Replace brick/ gravel bunds to hardstand bunds. |  |  |  | x |  |  |  | C-I-C |  |  | C-I-C | [6 empty] | C-I-C
Sub Station | Morwell East ZSS (MWE) | DS-MWE | East | Eastern Perimeter Road, Morwell, Victoria, 3840 | 1\PS827363 | -38.2533 | 146.4046 | TBC | TBC | Leased | On Overhold | Uploaded 17/03 | Yes / Yes | 2021-02-10 | M Snell | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 2 | [5 empty] | 3 | Oil containing equipment and batteries | 2 | 3 | 4 | 2 | 4 | 4 | 4 |  | Brick bund with gravel floor and basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | None | None | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 3 |  |  |  | 2 | 3 | E | D | Yes | Potential contaminating activities. |  | #REF! |  |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 4 | 4 | 2 | 3 | 4 | 4 | 5 | 2 | 3.5 | 4 | 4 Possible: B | D | No damage to the concrete walled bunds, has gravel floor, transformer enclosures drain to environmental system | 2 2001, 2004, 2006 | New site there should not be any contamination of the ground. | 0 | ZSS | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | B | [23 empty] | C-I-C
Sub Station | Morwell North ZSS (MWN) | DS-MWN | East | Eastern Perimeter Road, Morwell, Victoria, 3840 | 1\PS827363 | -38.2502 | 146.4063 | TBC | TBC | Leased, Licensed | Active | Uploaded 17/03 | Yes / Yes | 2021-02-10 | M Snell | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 44 | [5 empty] | 3 | Oil containing equipment and batteries | 2 | 3 | 4 | 5 | 5 | 4 | 2 |  | Brick bund with gravel floor | 5 | None | Large | Yes | None | None | None | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 3 |  |  |  | 2 | 3 | B | D | Yes | Potential contaminating activities. | Check location, no sub evident at coordinates | #REF! |  |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 2 | 2 | 2 | 1 | 2 | 2 | 3 | 4 | 3.5 | 4 | 4 Possible: B | B | ASAP, 2021-25 | 1986; 1963 | No | No | ZSS | No | No | No | No | No | No | No | No | Yes | No | Yes | No | 0 |  |  | Refurbishment work due 16/17. ZSS Oil Spill Control Stage 2 BC - was this done? | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Sub Station | Morwell Power Station (MPS) | TBC PS-MPS | East | Commercial Road, Morwell, Victoria, 3840 | Part of 2\PS449983 | -38.243 | 146.4142 | TBC | TBC | TBC | TBC | 2021-06-24 | Yes / Yes | 2021-06-24 | J. Hartley | Yes | Yes | [5 empty] | Historic report related to spill from Energy Brix Power Station |  | 3 |  | Previous spill to creek here or on terminal station | 5 | 3 | Former energy brix power station - currently being demolished |  | 5 |  | 8 | 4 | 4 | 5 | 5 | 5 | 2 |  |  | 5 | None | None | None | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 1 | 1 | [5 empty] | 1 | B | E | No | Potential contaminating activities. | Remediation and validation to be undertaken as part of site upgrades. Note site is not in management control of Site, therefore, it is not incumbent on Ausnet to notify. |  | TPH/TRH contamination, presence of LNAPL - Currently under audit but not Ausnet management control |  |  | PSI and soil classification prior to commencement. Remediation and validation to be undertaken as part of site upgrades. | Currently 90% decomissioned | [6 empty] | Historic report related to spill from Energy Brix Power Station |  | 2 | 2 | 2 | 1 | 2 | 2 | 5 | 2 | 3.5 | 4 | 4 Rare: C | N/A | New site | 2 PT 2014 | No - New site there should not be any contamination of the ground. | 0 | ZSS | Yes - CB | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | C | C2 | No assesment yet. Need to confirm if still in service | Y | Confidence 3/5. | Former energy brix power station, currently being demolished. 8 transformers with oil leak ratings 4/5. High risk driven by poor scoring in environmental controls and low confidence. | Site scheduled for demolition - no upgrades or improvements recommended at this stage. | [17 empty] | C-I-C
Sub Station | Morwell South ZSS (MWS) | TBC DS-MWS | East | Brodribb Road in Open Cut, Morwell, Victoria 3840 | 2A~A\PP2749 | -38.2757 | 146.3883 | TBC | TBC | Leased | On Overhold | Uploaded 17/03 | Yes / Yes | 2021-02-10 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 1 | No contaminating activities | 1 | 3 | 1 | 1 | 1 | 2 | 1 |  | Not required | 3 | None | None | None | None | None | None | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 3 |  |  |  | 2 | 3 | C | D | Yes |  |  | #REF! | [13 empty] | 0 | 1 | 2 | 1 | 1 | 1 | 4 | 2 | 3 | 3 | 3 Rare: D | E | Visual - Yes, earth mound along residential sides of the site and trees planted to screen station New site there should not be any contamination of the ground. | 0 | No | 0 | ZSS | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | D | [23 empty] | C-I-C
Terminal Station | Morwell TS (MWTS) | TS-MWTS | East | 240 Monash Way, Morwell VIC 3840 | 6N~A\PP2749 | -38.2581 | 146.4206 | TBC | TBC | Freehold | Active | UPLOAD 20/03 | Yes / Yes | 2020-10-21 | M Snell | Yes | Yes |  |  |  |  | Water Quality Investigation Program-BSE(2022) | Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 6 | Previous spill to creek here or on power station. Historic report indicates drainage discharge exceeding discharge criteria (GHD, 2003) |  |  |  | Medium Risk | 3 | Oil containing equipment, SF6/gas cylinders and batteries | 4 | 3 | 1 | 3 | 3 | 3 | 5 |  | Fully compliant sealed bund with oil/water separator | 3 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | Yes - LPG | Spoil / Waste | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 |  | Yes |  |  |  | 3 | C | C | Yes |  |  | #REF! |  | Y | Y | [8 empty] | Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | Check | 5 | 2 | 2 | 5 | 5 | 5 | 2 | 3.5 | 4 | 4 Possible: B | D | Bund walls in good condition, one transformer new and fully compliant, the other two are old and have gravel floors | 3 1978, 2 1963? | No knowledge of any soil samples taken, two transformers are old | 0 | ZSS | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | B | C2 | Enviro - one above ground system, stormwater isolation valves fitted | Y | Confidence 3/5. Surface water sampling during WQIP (BlueSphere, 2022) | Main risk drivers include presence of oil containing equipment, oil observed in bunds by BlueSphere in 2022. Off site drainage of surface water. Fully compliant sealed bund with oil/water separator | 1. Service and repair leaking transformers. 2. Clean and check integrity of existing hardstand surfaces and bunds. |  | C-I-C | C-I-C | x | [13 empty] | C-I-C
Sub Station | Morwell West ZSS (MWW) | DS-MWW | East | Brodribb Road in Open Cut, Morwell, Victoria 3840 | None | -38.2749 | 146.3925 | TBC | TBC | TBC | Active | Uploaded 17/03 | Yes / Yes | 2021-02-10 | M Snell | Yes | [8 empty] | 2 | 55 | [5 empty] | 3 | Oil containing equipment and batteries | 2 | 3 | 1 | 3 | 3 | 3 | 1 |  | Fully compliant sealed bund and basic oil/water separator - no shut off valve | 3 | None | Large | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 3 |  |  |  | 2 | 3 | C | D | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 3 | 1 | 1 | 5 | 1 | 3 | 3 | 3 Unlikely: D | D |  | 1 2006, 1 2009 | No knowledge of any soil samples taken, two transformers are old (not right comment??) | 0 | ZSS | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | D | [23 empty] | C-I-C
Switchyard | Mount Baw Baw PS (MBB) | TBC PS-MBB |  | Mt Baw Baw Alpine Village, Mt Baw Baw VIC | None | -37.8409 | 146.2662 | TBC | TBC | Leased | Active | NO LONGER OURS | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 5 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | B | D | No |  |  | #REF! | [13 empty] | 1 | 5 | 2 | 2 | 5 | 5 | 5 | 2 | 3.5 | 4 | 4 Unlikely: C | C | Station is being rebuilt currently as part of Refcl project, all oil filled 22kv switchgear will be replaced, transformers will be retained | 1 2004, 2 1969 | Old transformers pre-bunding upgrades. Soil removed and some level of remediation completed before bunding upgrade | 0 | ZSS + REFCL project works | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | C | [23 empty] | C-I-C
Terminal Station | Mount Beauty TS (MBTS) | TS-MBTS | North | Kiewa Valley Highway (Bogong High Plains Road), Mt Beauty, Victoria 3699 | AST: 1\PS339019 Crown: 5A~4\PP2620 | -36.7424 | 147.1665 | TBC | TBC | AST: Freehold Crown: Leased | Active | 2020-07-02 | Yes / Yes | 2020-07-02 | CJ Wilson | Yes | Yes | [5 empty] | Groundwater Monitoring (2005). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002) |  | 3 | 16 |  |  |  |  | Medium Risk | 5 |  | Check | 5 | 1 | 1 | 1 | 3 | 3 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 5 | <10 kg or <50 mg/kg | Large | Yes | Fuel Default | None | Yes - Small Volume |  | Spoil / Waste | [5 empty] | No | [6 empty] | 4 | 4 | 3 |  |  |  | 2 | 4 | C | C | Yes |  |  | #REF! |  | Y | [9 empty] | Groundwater Monitoring (2005). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002) |  | 5 | 3 | 2 | 1 | 3 | 3 | 2 | 2 | 2 | 2 | 2 Possible: D | C |  | 2 1980, 1 2001, 2 1979 | Unknown | 0 | ZSS | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | D | C2 | Enviro - need more time for this one, I believe there is one above ground system on site, however there is some weird pipework coming from the trans bunds, I assume there is stormwater isolation valves fitted. | Y | Confidence 3/5. Last environmental report in 2003. | Risks driven by low confidence, oil leak rating 5/5. Unsure of transformer numbers. Stockpiles on site. Also influenced by proximity to environmental receptors. Site has puraceptor, shut off valve and generator. | 1. Complete site inspection to confirm environmental status (including presence of shut off valves) 2. Service and repair leaking transformers. 3. Review and resolve drainage configuration at site. 4. Confirm the status of the stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. 5. Clean bund surfaces 6. Check bund integrity 7. Install GAC post puraceptor to further reduce hydrocarbon load. |  | C-I-C | C-I-C | x |  | C-I-C | [11 empty] | C-I-C
Sub Station | Mount Beauty ZSS (MBY) | DS-MBY | North | Chalet Road, Mount Beauty, Victoria 3699 | 2\PS340418 | -36.7466 | 147.1694 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-07-02 | CJ Wilson | Yes | [8 empty] | 2 | 4 | [5 empty] | 4 |  | 2 | 5 | 1 | 2 | 2 | 4 | 4 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume |  | None | [5 empty] | No | [6 empty] | 3 | 2 | 4 |  |  |  | 1 | 3 | B | D | Yes |  |  | #REF! | [13 empty] | 2 | 4 | 3 | 3 | 4 | 4 | 5 | 2 | 3.5 | 4 | 4 Possible: B | C |  | 1 TR 2006, 1 TR 2003, 1 TR 1962, 1 TR 1960 | Yes - Bund walls added however rock floors in place. Project to replace old transformers, newer transformers have rock floors inside bunded areas | 0 | ZSS + REFCL project works | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | B | [23 empty] | C-I-C
City Gate | Mount Cottrell City Gate | MTCO |  | 620 Mt Atkinson Rd Truganina VIC 3029 | None | -37.7897 | 144.6814 | TBC | TBC | TBC | TBC | Done | Yes / Yes | 2021-01-12 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 3 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 4 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | 4 | 3 | 3 | 2 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Possible: B | D |  | 2 1979 2 1989 | Unknown | 0 | ZSS | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | B | [23 empty] | C-I-C
Sub Station | Mount Dandenong ZSS (MDG) | DS-MDG | Central | Glasgow Track/Ridge Rd, Mount Dandenong Victoria 3767 | 1\TP337788 | -37.8338 | 145.3499 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-05 | A Ryan | Yes | [8 empty] | 2 | 8 | [5 empty] | 2 |  | 1 | 1 | 1 | 2 | 2 | 1 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 4 |  |  |  | 4 | 4 | B | C | No |  |  | #REF! | [6 empty] | Yes | Rebuild due 2014-2020 | [5 empty] | 4 | 1 | 1 | 2 | 1 | 1 | 5 | 4 | 4.5 | 5 | 5 Rare: C | C |  | 2 2018, 2 2019 | Old transformers pre-transformer replacement works. Soil removed and some level of remediation completed before bunding upgrade | 0 | ZSS | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | C | [23 empty] | C-I-C
Comms Site | Mounty Beauty Comms Site (MBY) | TC-MBYXXXXX |  | BIG HILL, MOUNT BEAUTY, VICTORIA 3699 | None | -36.7728 | 147.1839 | TBC | TBC | Leased | Active | Cameron Wilson confirmed the equipment is a Comms rack on an AGL site in a room of an AGL owned building up on Big Hill. No site assessment required. | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 3 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [6 empty] | Yes | Rebuild due 2014-2020 | [5 empty] | 4 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 Rare: E | D |  | 4 2010 | New site no contamination should be present | 0 | ZSS | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | E | [23 empty] | C-I-C
Comms Site | Mt Baranduda Comms Site (MTBD) | TC-MTBDXXXX |  | Ewarts Road, Yackandandah (Leneva), Victoria 3749 | None | -36.2573 | 146.8208 | TBC | TBC | Licensed | Active | Done | Yes / Yes | 2020-07-03 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 5 | 5 | 5 | 3 | 3 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 1 | 2 | D | E | No |  |  | #REF! | [13 empty] | 0 | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 2 | 2 | 2 Possible: D | D | DD-7231 to be completed in 2019 | 0 | Yes - Potential for some historical contamination under the original transformer | 0 | ZSS | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | No | 0 |  |  |  | Electricity Distribution | North | Andrew Ryan | D | [23 empty] | C-I-C
Switchyard | MT BAW BAW POWER STATION | DS-BAW |  | Mt Baw Baw Alpine Village, Mt Baw Baw VIC | None | -37.8457 | 146.2473 | TBC | TBC | TBC | TBC | NO LONGER OURS | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 0 | 3 | 4 | 5 | 5 | 4 | 3 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 6 | 3 | 3 | 4 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Possible: B | B |  | 1950; 2002; 2005; 2x2007;2008 | Potential for some historical contamination under the original transformers that were on site however no reports of any issues found | Check | ZSS + construction (Downer) REFCL works | Yes | No | No | Yes | No | No | No | No | Yes | Yes | Yes | No | 0 |  |  | Refcl | Electricity Distribution | Central | Andrew Ryan | TBC | [23 empty] | C-I-C
Comms Site | Mt Benambra Comms Site (MTBN) | TC-MTBNXXXX |  | Mt Benambra Road, Dartmouth, Victoria 3701 | 2\PP2114 | -36.5056 | 147.5735 | TBC | TBC | Licensed | Active | Done | Yes / Yes | 2020-07-03 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 5 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 1.5 | 2 | 2 Rare: E | D |  | 0 | No - New and Compliant | 0 | ZSS | Yes | No | No | Yes | No | No | No | No | Yes | Yes | Yes | No | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | E | [23 empty] | C-I-C
Comms Site | Mt Blackwood Comms Site (MTBL) | TC-MTBLXXXX |  | off Mount Blackwood Road (Tower Track), Myrniong, Victoria 3341 | None | -37.5573 | 144.3599 | TBC | TBC | Licensed | Active | Done | Yes / Yes | 2020-09-08 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 5 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 5 |  |  |  | 4 | 3 | C | D | Yes |  |  | #REF! | [13 empty] | 3 | 1 | 1 | 1 | 1 | 1 | 5 | 1 | 3 | 3 | 3 Rare: D | D | New site | 3 2010 | New site there should not be any contamination of the ground | 0 | ZSS | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | D | [23 empty] | C-I-C
Comms Site | Mt Burramboot Comms Site (MTBB) | TC-MTBBXXXX |  | Off Trewin Road (Mt Burramboot Trein Rd), Colbinabbin VIC 3559 | 5~A\PP2298 | -36.5014 | 144.695 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 5 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | 3 | 1 | 1 | 2 | 1 | 1 | 4 | 1 | 2.5 | 3 | 3 Rare: D | C |  | 3 2017 | No | 0 | ZSS | Yes | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | D | [23 empty] | C-I-C
Comms Site | Mt Clay Comms Site (MTCL) | TC-MTCLXXXX |  | Tower Rd, off Mt Clay Rd, Tyrendarra VIC 3285 | None | -38.2057 | 141.7335 | TBC | TBC | Leased | Expired | Done | Yes / Yes | 2020-09-29 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | A | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 2 | 1 | 1 | 4 | 4 | 4 | 4 | 4 Rare: C | C | DD-7231 will be delivered 2019 | 1 2013 | Old transformer pre-transformer replacement works. Soil removed and some level of remediation completed | 0 | ZSS | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | C | [23 empty] | C-I-C
Comms Site | Mt Fatigue Comms Site (MTFT) | TC-MTFTXXXX |  | off Toora-Gunyah Rd, Gunyah, Victoria 3960 | 6C~B\PP3885 | -38.5659 | 146.3041 | TBC | TBC | Licensed | Active | Done | Yes / Yes | 2020-11-04 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 4 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | B | E | No |  |  | #REF! | [13 empty] | 0 | 4 | 3 | 4 | 4 | 4 | 3 | 1 | 2 | 2 | 2 Likely: C | B | MDI will be removed in the future |  | No |  | ZSS | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | North | Andrew Ryan | C | [23 empty] | C-I-C
Comms Site | Mt Holden Comms Site (HOLD) | TBC TC-HOLD |  | Mt Holden off Wileman Rd, Sunbury VIC 3429 | 1\TP597302 | -37.5725 | 144.6834 | TBC | TBC | Freehold | ACTIVE | Done - NOTE: B Scott - disposal of site options? | Yes / Yes | 2020-06-23 | A Ryan | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 2 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 1 |  |  |  | 4 | 3 | A | D | Yes |  |  | #REF! | [13 empty] | 0 | 2 | 3 | 5 | 2 | 2 | 5 | 4 | 4.5 | 5 | 5 Possible: A | D |  | 0 | No | 0 | ZSS | No | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | A | [23 empty] | C-I-C
Comms Site | Mt Macedon Comms Site (MTMD) | TC-MTMDXXXX |  | 253 Cameron Drive, Mt Macedon, Victoria 3441 | 2019\PP3304 | -37.3836 | 144.5776 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-09-08 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 3 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 1 | 2 | A | E | No |  |  | #REF! | [13 empty] | 0 | 3 | 3 | 5 | 3 | 3 | 4 | 4 | 4 | 4 | 4 Likely: B | C | Under REFCL rebuild | 0 | No | 0 | ZSS | Yes | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | B | [23 empty] | C-I-C
Comms Site | Mt Major Comms Site (MTMJ) | TC-MTMJXXXX |  | 310 TV Access Road, Mt Major (Dookie), Victoria 3646 | 161F\PP2535 | -36.3626 | 145.6957 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 3 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 4 | 3 | 3 | 5 | 3 | 3 | 4 | 1 | 2.5 | 3 | 3 Likely: B | B | DD-2694 MYT rebuild by 2019 | 2 1950, 2 2018 | No | 0 | ZSS | Yes | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | B | [23 empty] | C-I-C
Comms Site | Mt Shadwell Comms Site (MTSD) | TC-MTSD |  | Off Mortlake Ararat Rd, Mortlake, VIC, 3272 | TBC | -38.0542 | 142.8186 | TBC | TBC | TBC | TBC | Done | Yes / Yes | 2020-09-29 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 4 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | D | E | No |  |  | #REF! | [13 empty] | 3 | 4 | 3 | 3 | 4 | 4 | 3 | 4 | 3.5 | 4 | 4 Possible: B | B | Planning 2021-25 | 2x1949; 1970 | No | Dec-2013: Project Manager reported oil/water mixture leaking from bund at NLA Z/S/S. | ZSS | Yes | No | No | Yes | No | No | No | No | Yes | No | No | No | 0 |  |  | Planning for 21-25 (from ZSS 2018 work) | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Comms Site | Mt Stanley Comms Site (MTST) | TC-MTSTXXXX |  | Mt Stanley Rd, Stanley VIC 3747 | 17A~11A\PP3498 | -36.4155 | 146.7711 | TBC | TBC | Licensed | Annual License | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 4 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | Check | 4 | 3 | 5 | 4 | 4 | 3 | 2 | 2.5 | 3 | 3 Possible: C | C |  | 1 TR 2001, 1 TR 2002 | New site there should not be any contamination of the ground. | 0 | ZSS | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | C | [23 empty] | C-I-C
Comms Site | Mt Taurus Comms Site (MTTA) | TC-MTTAXXXX |  | Mount Taurus Rd, Winslow VIC 3281 | 1\TP827840 | -38.2457 | 142.4125 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-09-29 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | B | E | No |  |  | #REF! | [13 empty] | 4 | 1 | 2 | 3 | 1 | 1 | 5 | 1 | 3 | 3 | 3 Rare: D | D |  | 4 2009 | New site there should not be any contamination of the ground. | 0 | ZSS | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | D | [23 empty] | C-I-C
Comms Site | Mt Taylor Comms Site (MTTL) | TC-MTTLXXXX |  | off Tower Rd, Mt Taylor (Calulu), Victoria 3875 | None | -37.7018 | 147.5594 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-08-14 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 4 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | C | E | No |  |  | #REF! | [13 empty] | Check | 4 | 3 | 5 | 4 | 4 | 5 | 2 | 3.5 | 4 | 4 Possible: B | D | Yes, during rebuild vegetation was required to be removed, visual screening added to fences to block out visual impact of the site to neighbours | 4x2017 (2XSS) | Spare transformer still in place and contamination will be present. Old transformers pre-bunding upgrades saw soil removed and some level of remediation completed before new transformers installed with bunding upgrade | Check | ZSS | Yes | No | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | TBC | [23 empty] | C-I-C
Comms Site | Mt Toole-Be-Wong Comms Site (MTBW) | TC-MTBWXXXX |  | Off Moora Road, Healesville, Victoria 3777 | 1\TP170314 | -37.7094 | 145.5717 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-18 | A Ryan | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 3 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 2 | 2 | B | E | No |  |  | #REF! | [13 empty] | 4 | 3 | 2 | 3 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Possible: B | D | There was stockpiles of soil but this was being loaded directly into skips, the seepage from the skips was being managed by silt bunding along the nearest stormwater drain Noise complaints -has been in the past, not recent, and the sound enclosure was built around the transformers, and fans placed in auto so they turn off at night even during summer | 1977; 2x2006;2014 | Old transformers pre-bunding upgrades. Bunding installed but rock floors remain | Transformer explosion Feb 2014 | ZSS + REFCL project works | No | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | TBC | [23 empty] | C-I-C
Comms Site | Mt Warrenheip Comms Site (MTWH) | TC-MTWHXXXX |  | Mt Warrenheip-Summit Rd (off Forbes Rd), Dunnstown VIC 3352 | None | -37.5764 | 143.9584 | TBC | TBC | Licensed | Active | Done | Yes / Yes | 2020-09-08 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 3 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | 3 | 3 | 2 | 1 | 3 | 3 | 4 | 2 | 3 | 3 | 3 Rare: D | D |  | 3 PT 2016, 1 TR 2013 | Old transformers pre-transformer replacement works. Soil removed and some level of remediation completed | 0 | ZSS | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | D | [23 empty] | C-I-C
Comms Site | Mt William Comms Site | TBC TC-Mt William |  | MT WILLIAM, HALLS GAP, VICTORIA 3381 | None | -37.2833 | 142.6 | TBC | TBC | Leased | Active | CJ/ Daniel D confirmed site gone. A Ryan said: building owned by ausnet but only tenant assets in it. Confirm with property | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 7 | 3 | 4 | 5 | 5 | 4 | 3 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | B | D | No |  |  | #REF! | [13 empty] | 2 | 3 | 2 | 3 | 3 | 3 | 4 | 2 | 3 | 3 | 3 Rare: D | E | Not that there were complaints but planning permit required a visual screen to be built to minimise visual impact of the site | 1905-07-05 | New site there should not be any contamination of the ground. | Check | ZSS | No | No | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | TBC | [23 empty] | C-I-C
Terminal Station | Murra Warra TS (MRTS) | TS-MRTS | West | Ailsa Wheat Rd off Dimboola-Minyup Rd, Murra Warra VIC 3401 | RES1\PS817783 | -36.4372 | 142.3275 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-08-26 | CJ Wilson | Yes | [8 empty] | 2 | 2 | [5 empty] | 4 |  | 5 | 3 | 1 | 1 | 1 | 2 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | None | Large | Yes | None | None | Yes - Small Volume |  | None | [5 empty] | No | [6 empty] | 3 | 2 | 4 |  |  |  | 1 | 3 | A | D | Yes |  |  | #REF! | [13 empty] | 0 | 1 | 2 | 3 | 1 | 1 | 5 | 1 | 3 | 3 | 3 Rare: D | C | DD-2680 SMR Rebuild by 2018 | N/A | No | 0 | ZSS | Yes | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | D | N/A | Not in this list. | Y | Confidence 2/5. No environmental reports. | Oil leak rating 3/5 and 5 transformers on site. Risk driven by consequence of contamination and presence of potentially contaminating activities on site. Unbunded diesel generator. Transformers bunded. | 1. Complete site inspection to confirm environmental status. 2. Move diesel generator to a hardstand bunded area. 3. Service and repair leaking transformers. |  |  |  | x | [13 empty] | C-I-C
Sub Station | Murrindindi ZSS (MDI) | DS-MDI | North | 258 Wilhelmena Falls Road, Murrindindi, Victoria, 3717 (behind closed mill) | 1\PS728105 & 2\PS728105 | -37.3854 | 145.54 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-06-23 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP |  |  | EnviroProtect Phase 1 ESA (2014), covers surrounding land |  |  | 5 | 54 | [5 empty] | 2 |  | 1 | 2 | 4 | 4 | 4 | 3 | 3 |  | Brick bund with gravel floor with shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None | None | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 3 | No | 5 | No | 4 | 4 | C | D | Yes | Infrastructure with high potential for contamination | No actual testing but likely to be impacts based on design | Possible | High likelihood of contamination due to large oil storage and unsealed bund, however, no testing currently available to confirm. |  |  | PSI and soil classification prior to commencement. Remediation and validation to be undertaken as part of site upgrades. | Yes | Some upgrades due to occur |  |  |  | AusNet, Distribution Sites, Portfolio EMP | EnviroProtect Phase 1 ESA (2014), covers surrounding land |  |  | 3 | 3 | 2 | 4 | 3 | 3 | 2 | 2 | 2 | 2 | 2 Unlikely: D | E | TT Stage 2 rebuild will be completed 2020 | 0 | No | 0 | ZSS | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | D | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Myrtleford Depot | WH-0016 |  | 10 Matthews St, Myrtleford VIC 3737 | 52\PS406397 | -36.5528 | 146.7198 | Downer | Downer | Leased | Active | Sharepoint updated. Downer received lease - don't do | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 3 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | B | D | No |  |  | #REF! | [13 empty] | 1 | 3 | 3 | 5 | 3 | 3 | 4 | 2 | 3 | 3 | 3 Likely: B | C |  | 1 TR 1935 | New site there should not be any contamination of the ground. | 0 | ZSS | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | B | [23 empty] | C-I-C
Sub Station | Myrtleford ZSS (MYT) | DS-MYT | North | Merriang Road/Tonazzio Road, Myrtleford, Victoria, 3737 | 1\TP321387 | -36.5661 | 146.703 | AusNet Electrical Services | TBC | Freehold | Active | Done | Yes / Yes | 2020-07-03 | CJ Wilson | Yes | BSE (2022) |  | AusNet, Distribution Sites, Portfolio EMP |  |  | Jacobs 2021, PSI-BSE(2022) |  | 2022-09-01 | 5 | 71 |  | 3 |  | Recently completed upgrade, many assets since removed from the site |  | 5 |  | 3 | 4 | 4 | 5 | 5 | 5 | 3 |  | Brick bund with gravel floor | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 5 | Yes | 5 | Yes | 3 | 3 | B | E | Yes | Hydrocarbons above management limits, no HIL D exceedences |  | No | No exceedences of HIL D |  | Y | PSI and soil classification prior to commencement. Remediation and validation to be undertaken as part of site upgrades. | Yes | Stage 3 - due 2020-2023 |  |  |  | AusNet, Distribution Sites, Portfolio EMP | Jacobs 2021 |  |  | 0 | 3 | 3 | 5 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Likely: B | C |  | 0 | No | 0 | ZSS | Yes | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | B | [23 empty] | C-I-C
Sub Station | Narre Warren ZSS (NRN) | DS-NRN | Central | 188E Quarry Rd, Narre Warren VIC 3805 (in old tip area) | 1\PS70500 | -38.0037 | 145.3304 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-05-26 | A Ryan | Yes | [8 empty] | 2 | 19 | [5 empty] | 3 |  | 1 | 1 | 4 | 4 | 4 | 2 | 1 |  | Brick bund with gravel floor with shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 3 |  |  |  | 2 | 4 | B | C | Yes |  |  | #REF! | [13 empty] | HOW DOES A ZSS HAVE NO TR? KIOSK ONLY? | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1.5 | 2 | 2 Rare: E | E | Under REFCL rebuild | N/A | No | 0 | ZSS | No | No | No | Yes | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | E | [23 empty] | C-I-C
Sub Station | Newmerella ZSS (NLA) | DS-NLA | East | 5246 Princes Highway, Newmerella, Victoria, 3886 | 17C~C\PP3306 | -37.7391 | 148.4252 | AusNet Electrical Services | TBC | Freehold | Active | Done | Yes / Yes | 2020-08-02 | M Snell | Yes | BSE (2022) |  | AusNet, Distribution Sites, Portfolio EMP |  |  | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021), PSI-BSE(2022) |  | 2022-09-01 | 5 | 72 | [5 empty] | 4 | No obvious signs of contamination were observed at the Site other than the stained gravels located within the bunded areas with transformers | 4 | 4 | 4 | 3 | 4 | 4 | 3 |  | Brick bund with gravel floor and basic oil/water separator - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | None | None | None | Yes - Small Volume | None | Verified clean fill | Yes - Septic | Yes |  | None |  | No |  |  | None |  |  |  | 2 | 2 | 4 | Yes | 5 | No | 2 | 3 | C | D | Yes | Infrastructure with high potential for contamination | No actual testing but likely to be impacts based on design | Possible | High likelihood of contamination due to large oil storage and unsealed bund - no testing to confirm. | Stage 1 complete | Y | PSI and soil classification prior to commencement. Remediation and validation to be undertaken as part of site upgrades. | Yes | Stage 1 - due 2017 | Yes | Rebuild due 2017-2024 |  | AusNet, Distribution Sites, Portfolio EMP | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021) |  |  | 0 | 3 | 3 | 5 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Likely: B | C |  | 0 | No | 0 | ZSS | Yes | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | B | [23 empty] | C-I-C
Switchyard | Newport Power Station (NPSD) | TBC PS-NPSD |  | 350 Douglas Parade, Newport, Victoria 3015 | None | -37.8414 | 144.8929 | TBC | TBC | Leased | Active | Done - added to Sharepoint. In Enablon | Yes / Yes | 2020-07-28 | A Ryan | Yes | [6 empty] | KTA-TATOR - Implications of lead-based paint (2015). |  | 2 | [6 empty] | 3 | Oil containing equipment, batteries & SF6/gas cylinders | 0 | 3 | 4 | 5 | 5 | 4 | 3 |  | Engineered & administrative controls | 5 | None | None | Yes | None | None | Yes - Large Volume | Yes - LPG | None | None |  |  |  |  | No |  |  |  | Yes - Lead |  |  | 2 | 3 | 4 |  |  |  | 1 | 3 | B | D | Yes |  |  | #REF! | [11 empty] | KTA-TATOR - Implications of lead-based paint (2015). |  | 0 | 3 | 3 | 3 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Possible: B | C | I am aware of transformer noise complaints from many years ago that resulted in a sound wall being erected along one boundary of the site | 0 | Yes - Old transformers are likely to have soil contamination around them, unknown levels, no contamination detected when newest transformer installed | 0 | ZSS | Yes | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | B | na | Enviro -power station responsibility | N | Confidence 2/5. No environmental reports. | Risk being driven by lack of info and lack of controls for oil filled equipment - but oil filled equipment not on site. Oil containing equipment, batteries & SF6/gas cylinders. No fuel or chemical storage. AusNet is a tenant onto the site. Suggest not included in this exercise. | 1. Confirm site ownership and whether AusNet needs to complete actions. 2. If AusNet owns site, complete site inspection to confirm environmental status and presence/ absence of oil filled equipment. | [17 empty] | C-I-C
Sub Station | Northern Reactor Compensator Station (NRCS) | TS-NRCS | Central | McCormacks Road, Cardinia | None | -38.1255 | 145.388 | Government | AusNet Services | TBC | TBC | Done | Yes / Yes | 2020-07-23 | A Ryan | Yes | [8 empty] | 2 | 10 | [5 empty] | 5 | Oil containing equipment, diesel generator, batteries & SF6/gas cylinders | 1 | 1 | 1 | 3 | 3 | 1 | 3 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 3 | None | Large | Yes | None | None | Yes - Small Volume | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 2 |  |  |  | 1 | 3 | D | D | Yes |  |  | #REF! | [13 empty] | 0 | 3 | 3 | 2 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Possible: B | D |  | 0 | Not sure: Original transformers in place and bunded since installation | 0 | ZSS | No | No | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | B | C1 | Enviro - one below ground system, outlet free flows to stormwater drains | N | Confidence 2/5. No environmental reports. | Risk driven by the low confidence rating. Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve. Low environmental risk rating. Surface water flows offsite. | 1. Move diesel generator to bunded area 2. Install shut-off valve 3. Complete site inspection to resolve environmental status. | [10 empty] | C-I-C | [6 empty] | C-I-C
Sub Station | Northern Reactor Compensator Station Tie (NRCS Tie) | TBC NRCS Tie | Central | next to Cranbourne TS, 1120 Thompsons Rd, Cranbourne VIC 3977 | None | -38.0849 | 145.2652 | Government | AusNet Services | TBC | TBC | Done - check is it TS-NRCS???? | Yes / Yes | 2020-07-16 | A Ryan | Yes | [8 empty] | 2 | [6 empty] | 3 | Batteries, chemicals & SF6 gas | 1 | 1 | 4 | 5 | 5 | 3 | 2 |  | Dedicted battery room with chemicals in cabinets with bunds | 5 | None | None | Yes | None | Default Chemicals | Yes - Small Volume | None | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 1 |  |  |  | 2 | 4 | C | D | Yes |  |  | #REF! | [13 empty] | 1 | 2 | 3 | 5 | 2 | 2 | 5 | 2 | 3.5 | 4 | 4 Rare: C | E |  | 0 | No | 0 | ZSS | Yes | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Distribution | North | Cameron Wilson | C | N/A | Not in this list. | N | Confidence 2/5. No environmental reports. | Risk driven by proximity to environmental receptors; control scores for oil filled equipment, but none on site according to site inspection form. Chemicals are stored on site. | 1. Complete site inspection to resolve environmental status. 2. Confirm presence of oil filled equipment on site and bunds if applicable. | [17 empty] | C-I-C
Sub Station | Officer ZSS (OFR) | DS-OFR | Central | 55 Peck Road, Officer VIC 3809 | 2\PS534843 | -38.0513 | 145.445 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-26 | A Ryan | Yes | [8 empty] | 2 | 12 | [5 empty] | 5 |  | 2 | 1 | 1 | 3 | 3 | 1 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 3 | None | Large | Yes | None | Default Chemicals | Yes - Small Volume |  | None | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 1 | 4 | C | C | Yes |  |  | #REF! |  |  |  |  | Yes | Stage 1 - due 2017 | [7 empty] | 0 Transformers. Circuit Breakers | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1.5 | 2 | 2 Rare: E |  |  | N/A | No | 0 | 0 | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | TBC | [23 empty] | C-I-C
Comms Site | One Tree Hill Comms Site (OTHB) | TC-OTHBXXXX |  | One Tree Hill Road, Bendigo, Victoria 3550 | None | -36.8031 | 144.3001 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | 2 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 Rare: E |  | Visual - earth mound that has been vegetated is installed on the east and north sides and blast walls have been camouflage painted | 0 | No | 0 | 0 | Yes | No | No | No | No | Yes | No | Yes | Yes | Yes | Yes | No | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | E | [23 empty] | C-I-C
Sub Station | Pakenham ZSS (PHM) | DS-PHM | Central | Racecourse/Princes Highway, Pakenham, Victoria 3810 | 1\TP594254 | -38.0708 | 145.4942 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-26 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 4 | [5 empty] | 5 | Oil containing equipment, batteries, chemicals & SF6 | 2 | 1 | 4 | 2 | 4 | 2 | 2 |  | Brick bund with gravel floor and basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 4 | 4 | 5 | No | 4 | Yes | 4 | 4 | C | E | Yes | Potential contaminating activities. |  | #REF! |  |  |  | PSI with limited soil sampling program. |  |  | Yes | Rebuild due 2014-2020 |  | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 2 | 2 | 4 | 5 | 2 | 2 | 2 | 1 | 1.5 | 2 | 2 Rare: E |  |  | 2 2011 | No | 0 | 0 | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | No | 0 |  |  |  | Electricity Distribution | Central | Andrew Ryan | E | [23 empty] | C-I-C
Sub Station | Phillip Island ZSS (PHI) | DS-PHI | East | Phillip Island Road, Wimbledon Heights, Victoria, 3922 | 1\TP412019 | -38.4814 | 145.2395 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2021-02-10 | M Snell | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 59 | Hydraulic oil leak onto gravel driveway in 2019 | 4 |  |  |  | 4 | Oil containing equipment, batteries & SF6/gas cylinders | 2 | 2 | 4 | 5 | 5 | 3 | 4 |  | Brick bund with gravel floor | 5 | None | Large | Yes | None | None | Yes - Small Volume | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 4 |  |  |  | 2 | 3 | B | B | Yes | Potential contaminating activities. | Follow up on rectification of spillage and surface condition | #REF! | Historical spillage, very small volume reported to have been cleaned up. Therefore, no Duty to Notify |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | Check | 4 | 3 | 5 | 4 | 4 | 4 | 2 | 3 | 3 | 3 Likely: B | D |  | CHECK | No | No | Zone sub station | Yes | No | No | No | No | No | No | No | Yes | No | Yes | No | No |  |  |  | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
City Gate | Plumpton City Gate | PLUM |  | 1048 TAYLORS ROAD, Plumpton, 3335 | None | -37.7187 | 144.7121 | TBC | TBC | TBC | Active | Done | Yes / Yes | 2021-01-12 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 3 | 1 | 4 | 5 | 5 | 3 | 3 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | Check | 3 | 1 | 5 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Possible: B | D | New Bunds part of the Station Upgrade | 0 | No | 0 | Zone sub station | Yes | No | No | No | No | No | No | No | Yes | No | Yes | No | No |  |  |  | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Comms Site | Point Henry Smelter Alcoa Site (PTH) | TC-PTH |  | 430 Point Henry Rd, Moolap VIC 3221 (Owned by Portland Aluminium) | TBC | -38.1372 | 144.4209 | TBC | TBC | TBC | TBC | Demolished (A Ryan) | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2.5 | 3 | 3 Rare: D |  |  | #N/A | #N/A | #N/A | #N/A | No | No | No | No | No | No | No | No | Yes | Yes | Yes | No | No | N/A | N/A | N/A | N/A | East | TBC | TBC | [23 empty] | C-I-C
City Gate | Portland City Gate | PORT |  | Gorae West Rd, Portland VIC 3305 | None | -38.2514 | 141.5604 | TBC | TBC | Freehold | Active | Complete | Yes / Yes | 2021-04-27 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 0 | 1 | 4 | 5 | 5 | 3 | 2 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | [5 empty] | 2 | B | E | No |  |  | #REF! | [13 empty] | Check | 2 | 2 | 5 | 2 | 2 | 4 | 4 | 4 | 4 | 4 Possible: B | D | DD-7218 will be delivered 2021 | #N/A | #N/A | #N/A | #N/A | No | No | No | No | No | No | No | No | Yes | No | Yes | No | No | N/A | N/A | N/A | Electricity Transmission | East | TBC | TBC | [23 empty] | C-I-C
Ex Gas Works Site | Portland Gas Site | TBC Portland Gas |  | 25 Glenelg Street, Portland, Victoria | TBC | -38.3529 | 141.6032 | TBC | TBC | TBC | Active | 2020-04-06 | No assessment needed |  |  | Yes | Yes |  |  |  |  | EES - Draft Remediation Action Plan: Portland (2004), Jacobs - Preliminary Conceptual Site Model (pCSM) (2021), Jacobs - Contamination Management Plan (CMP) (2021), Jacobs - Gfactuakl Report: Groundwater Monitoring Event March 2021 (2021) | GroundScience - Results of Contamination Sampling (2014). GroundScience - Waste Soil Hazard Classification (2013) |  | 3 |  |  | 5 |  | On-site waste disposal |  |  |  | 3 | 3 | 4 | 5 | 5 | 4 | 4 |  |  | 5 | None | Oil Default | [8 empty] | Inert |  |  | No |  | NAPL Present | HIL/HSL Exceedances |  |  |  | 4 | 4 | 5 |  |  |  |  | 4 | C | A | Yes | Confirmed contaminated soil and groundwater | Refer to Gasworks Team | #REF! | Known contamination (former Gasworks) |  |  | DSI | [6 empty] | EES - Draft Remediation Action Plan: Portland (2004), Jacobs - Preliminary Conceptual Site Model (pCSM) (2021), Jacobs - Contamination Management Plan (CMP) (2021), Jacobs - Gfactuakl Report: Groundwater Monitoring Event March 2021 (2021) | GroundScience - Results of Contamination Sampling (2014). GroundScience - Waste Soil Hazard Classification (2013) |  | Check | 4 | 3 | 5 | 4 | 4 | 3 | 4 | 3.5 | 4 | 4 Likely: B | C |  | #N/A | #N/A | #N/A | Zone sub station | No | No | No | No | No | No | No | No | Yes | No | Yes | No | No | N/A | N/A | N/A | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Comms Site | Pyramid Hill Comms Site (PDHL) | TC-PDHLXXXX |  | PART 1487 GLADFIELD ROAD, PYRAMID HILL, VICTORIA 3575 | None | -36.055 | 144.1026 | TBC | TBC | Leased | In Progress | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 5 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 3 | 5 | 3 | 3 | 5 | 5 | 4 | 4 | 4 | 4 | 4 Likely: B | C |  | #N/A | #N/A | #N/A | Zone sub station | Yes | No | No | No | No | No | No | No | Yes | No | Yes | No | No | N/A | N/A | N/A | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Comms Site | Quoin Hill Comms Site (QHIL) | TC-QNHLXXXX |  | 240 Troys Rd, Waubra VIC 3352 |  | -37.3569 | 143.5973 | TBC | TBC | Peppercorn Lease | Active | On Waubra TS (A Ryan) | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 1 |  | 1 | 1 | 4 | 5 | 5 | 3 | 5 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | Check | 5 | 3 | 5 | 5 | 5 | 4 | 2 | 3 | 3 | 3 Likely: B | B | DD-7164, REFCL will be done before 2020 | #N/A | #N/A | #N/A | Zone sub station | Yes | No | No | No | No | No | No | No | Yes | No | Yes | No | No | N/A | N/A | N/A | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Red Cliffs TS (RCTS) | TS-RCTS | West | Pumps Rd (718 Woomera Avenue), Red Cliffs, Victoria 3496 | 1\TP12019 | -34.2921 | 142.2384 | TBC | TBC | Freehold | Active | 2020-07-30 | Yes / Yes | 2020-07-30 | CJ Wilson | Yes | Yes |  |  |  |  | Water Quality Investigation Program-BSE(2022), Water Quality Investigation Program-Phase 2 of Works for High-Risk Sites-BSE (2023) | Geo-Eng - Environmental Risk Assessment (1996). Preliminary Groundwater Investigation 2003 & Soil sampling results from 2006 - related to bunds. No action required. SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) | 2023-09-01 | 3 | 60 |  |  |  | Historic report from 1996 indicates presence of low-level contaminated soil | High | 5 |  | 2 | 4 | 3 | 1 | 3 | 4 | 4 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 4 | >10 kg or >50 mg/kg | Large | Yes | Fuel Default | Default Chemicals |  |  | Spoil / Waste | [5 empty] | No | [6 empty] | 4 | 4 | 5 | Yes |  |  | 2 | 4 | B | C | Yes |  |  | #REF! |  | Y | Y | [8 empty] | Geo-Eng - Environmental Risk Assessment (1996). Preliminary Groundwater Investigation 2003 & Soil sampling results from 2006 - related to bunds. No action required. SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | Check | 4 | 3 | 5 | 4 | 4 | 2 | 2 | 2 | 2 | 2 Possible: D | D | Planning, 2021-25 | #N/A | Visible oil leaks observed | #N/A | Zone sub station | Yes | No | No | No | No | No | No | No | Yes | No | Yes | No | No | N/A | N/A | N/A | Electricity Distribution | East | TBC | TBC | C2 | Enviro - one above ground system stormwater isolation valves fitted, | Y | Confidence 3/5. BlueSphere conducted surface water sampling in 2022 and 2023 as part WQIP. | Risk rating driven by oil filled equipment rating such as bunds. Oil staining observed within concrete bunds. The site is next to the Murray River so the proximity to environmental receptors elevates risk ratings. | 1. Upgrade brick bunds to concrete hardstand bunds. 2. Retrofit puraceptor with GAC scrubber to further facilitate removal of hydrocarbons from water. | [5 empty] | C-I-C |  | C-I-C | [9 empty] | C-I-C
Terminal Station | Richmond TS (RTS) and Data Centre | TS-RTSX | Central | 347 Mary Street, Richmond, Victoria, 3121 | 8A\PP2796H, 8B\PP2796H, 8C\PP2796H | -37.8308 | 145.0003 | TBC | TBC | Freehold | Active | Done - check it is Enablon | Yes / Yes | 2020-06-19 | A Ryan | Yes | WSP (2023) |  | AECOM - Site Environmental Management Plan, Former Burnley Depot (2009), AusNet, Transmission Sites, Portfolio EMP |  |  |  | Geo-Eng - Environmental Risk Assessment (1996). Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003). LanePiper - Auditor review of Site Contamination Investigations (2009). Marshall Day Acoustics - Noise Impact Assesment (2011). Noel Arnold & Associates - Waste Classification Information for soil located at RTS (2014). | 2023-01-01 | 5 | 8 | Possible contamination of storm water with lead paint | 5 | 4 | Former landfill site, terminal on former site. UST identified in historic report, removed as part of upgrade works. | High | 5 | Oil containing equipment, batteries, chemicals & SF6/gas cylinders | 5 | 5 | 1 | 1 | 1 | 3 | 3 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 5 | <10 kg or <50 mg/kg | Large | Yes | >1,000 L | Default Chemicals | Yes - Large Volume | Yes - LPG | None | None |  | Yes - Septic | None | On-Site Containment | No |  |  | HIL/HSL Exceedances | Yes - Lead |  |  | 4 | 4 | 5 | No | 5 | Yes | 5 | 4 | C | C | Yes | Contaminated fill, appropriately managed for existing use but risk if change to more senstive land use | Low level soil contamination reported. No evidence of notifiable contamination. | #REF! | Landfill & USTs are at Burnley St, not RTS. Soil and gw has identified contamination, however, nothing signficant for commercial/industrial land use |  |  | PSI with limited soil sampling program. GME from existing wells. | [5 empty] | AECOM - Site Environmental Management Plan, Former Burnley Depot (2009), AusNet, Transmission Sites, Portfolio EMP |  | Geo-Eng - Environmental Risk Assessment (1996). Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003). LanePiper - Auditor review of Site Contamination Investigations (2009). Marshall Day Acoustics - Noise Impact Assesment (2011). Noel Arnold & Associates - Waste Classification Information for soil located at RTS (2014). |  | Check | 3 | 2 | 1 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Likely: B | D |  | #N/A | #N/A | #N/A | Zone sub station | Yes | No | No | No | No | No | No | No | Yes | No | Yes | No | No | N/A | N/A | N/A | Electricity Distribution | East | TBC | TBC | C1 | Enviro -one above ground system in place and stormwater isolation valves fitted | N | Confidence 5/5. WSP 2024 PSI report. | Risk driven by presence of oil filled equipment and proximity to sensitive receptors (Yarra River). The Site has oil containing equipment, batteries, chemicals & SF6/gas cylinders. Fully compliant sealed bund with puraceptor oil/water separator + shut off valve. Staining observed on bund surfaces in 2024. Surface water sample results collected post puraceptor treatment in 2023 reported elevated hydrocrbons. | 1. Service and repair leaking transformers. 2. Check bund integrity. 3. Complete groundwater monitoring event to confirm risk to groundwater (recommendation in WSP, 2024 report) 4. Replace brick wall bunds with concrete hardstand bunds. 5. Install GAC scrubber post puraceptor treatment to further decrease hydrocarbon load. |  | C-I-C | C-I-C | x |  | C-I-C |  | C-I-C | [9 empty] | C-I-C
Sub Station | Ringwood North ZSS (RWN) | DS-RWN | Central | 195A Warrandyte Road, Ringwood North, Victoria, 3134 | 1\LP60019 & 1\TP424928 | -37.793 | 145.2346 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-28 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP |  | Clean up notice (CUN 90004695) issued in relation to excavation, validation and soil disposal works |  | Toxfree - PCB Decontamination Jon at SPI Powernet Substation Ringwood (2014). PB - Excavation Validation Assessment Report (2014). PB - Transformer oil release incident at SP AusNet Zone Substation, Ringwood North (2014). PB - In-situ Waste Classification of Soils, SP AusNet Ringwood North (2014). AusNet - Significant Incident Report - Ringwood North Zone Sunstation (2014). PB - Addendum to Excavation Validation Assessment Report, SP AusNet Ringwood North (2014). PB - Summary of Emergency Response Works (2014). |  | 5 | 7 | Previous excavation, validation and assessment of impacts related to previous spill | 3 |  | Historic leakage incidents |  | 5 | Various oil containing equipment, stockpiles, batteries and chemicals | 4 | 4 | 4 | 2 | 4 | 4 | 4 |  | Brick bund with gravel floor and basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None | None | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 5 | No | 4 | No | 2 | 4 | B | D | Yes | Off-site migration of stormwater from hardstand areas | Investigate contamination status of hardstand due to off-site migration risk in accordance with Duty to Manage. No evidence of Duty to Notify. | #REF! | Historical stockpiles, however, all capped and contained. |  | Yes | PSI with limited soil sampling. Drainage/runoff testing or management. Surface grab samples from hardstand area | Yes | Stage 3 - due 2020-2023 |  |  |  | AusNet, Distribution Sites, Portfolio EMP |  | Toxfree - PCB Decontamination Jon at SPI Powernet Substation Ringwood (2014). PB - Excavation Validation Assessment Report (2014). PB - Transformer oil release incident at SP AusNet Zone Substation, Ringwood North (2014). PB - In-situ Waste Classification of Soils, SP AusNet Ringwood North (2014). AusNet - Significant Incident Report - Ringwood North Zone Sunstation (2014). PB - Addendum to Excavation Validation Assessment Report, SP AusNet Ringwood North (2014). PB - Summary of Emergency Response Works (2014). | Clean up notice (CUN 90004695) issued in relation to excavation, validation and soil disposal works | Check | 4 | 3 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 Likely: B | D | DD-7245 to be delivered in 2019; Planning, 2021-25 | #N/A | #N/A | #N/A | Zone sub station | No | No | No | No | No | No | No | No | Yes | No | Yes | No | No | N/A | N/A | N/A | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Ringwood TS (RWTS) | TS-RWTS | Central | 59-63 Heatherdale Road, Ringwood, Victoria 3134 (opposite Good Governs Street) | 1\PS613879 | -37.8284 | 144.9969 | TBC | AusNet/Mondo | Freehold | Active | 2020-06-17 | Yes / Yes | 2020-06-17 | A Ryan | Yes | WSP (2023) | WSP (2023) | AusNet, Transmission Sites, Portfolio EMP |  | Clean Up Notice for industrial waste identified during excavation near RWTS - appears to be two notices, Waste record: F6Q-1294245-P1X | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021), Waste record: F6Q-1294245-P1X | Preliminary Groundwater Investigation 2003. Numereous documents relating to the costing and cleanup of PIW in response to Clean Up Notice. SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) | 2023-01-01 | 5 | 3 | AusNet Site Assessment form (2021): Noted recent spill of oil, cleaned with absorbent materials and retained with spill socks, further clean up noted to be required | 5 | 3 | On-site containment of Category A soil (treated with lime), Category C filling also. Soil still contained on the Site. 2023: during site inspection SPA was disposed of off-site as category A 750m3 | High | 5 | Site perdominatly used for storage of macinery (old transformers) and small/moderate (requires clarification) amounts of chemicals | 7 | 3 | 1 | 1 | 1 | 2 | 4 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve, transformers no longer in use | 3 | <10 kg or <50 mg/kg | Large | Yes | <1,000 L | Default Chemicals | Yes - Large Volume | Yes - LPG | Contaminated soil - potential risk | Yes - Septic |  | Yes - Septic | Default Asbestos | On-Site Containment | No | None | None | HIL/HSL Exceedances |  |  |  | 3 | 5 | 5 | No | 3 | Yes | 2 | 5 | C | C | Yes | Known residual contamination retained beneath capping | Management plan | N | Operational areas are sealed and legacy contamination is maintained beneath capping. Therefore, no need to notify, however, potential risks to groundwater due to legacy contamination need to be resolved as per Duty to Manage. | Stage 1 complete |  | PSI, desktop only. Obtain as-builts of Cat A containment cell, include contaminated soil re-use in EMP. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021) | Preliminary Groundwater Investigation 2003. Numereous documents relating to the costing and cleanup of PIW in response to Clean Up Notice. SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) | Clean Up Notice for industrial waste identified during excavation near RWTS - appears to be two notices | No | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 3.5 | 4 | 4 Rare: C | N/A | Lakes Entrance - future site | N/A | No | No | Future ZSS | No | No | No | No | No | No | No | No | No | Yes | No | No | No |  |  |  | N/A | East | TBC | TBC | C1 | Enviro -one above ground system in place and stormwater isolation valves fitted | N | Confidence 5/5. WSP 2024 PSI report. | Risk rating driven by use of site for fuel and chemical storage, known contamination from PSI/ DSIs reports, consequence of contamination rating. Transformers have oil leak rating of 3/5. Some transformers no longer in use (per WSP 2024 report). Puraceptor with shut off valve. Stockpiles on site. | 1. Service and repair leaking transformers. 2. Clean oil staining from bunds. 3. Confirm the status of the stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. 4. Check bund integrity. |  | C-I-C | C-I-C | x | [13 empty] | C-I-C
Depot, Office and Warehouse Storage | Ringwood Warehouse | TBC WH-RWD |  | 59-61 Heatherdale Rd, Ringwood, Victoria, 3134 | 1\PS613879 | -37.8228 | 145.2136 | AusNet Services | AusNet Services | Freehold | Active | 2021-06-30 | Yes / Yes | 2021-06-30 | A Duffield | Yes |  |  | AusNet, Transmission Sites, Portfolio EMP |  |  | EES DSI (2015), Depot component only. |  |  | 5 |  | Concrete slurry into drainage pit in 2019 | 4 |  |  |  | 4 |  | 4 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | <10 kg or <50 mg/kg | Oil Default | None | Fuel Default | <100 L | Yes - Small Volume | Yes - LPG | Spoil / Waste | None |  |  |  |  | No | [6 empty] | 4 | 4 | 5 | No | 3 | No | 2 | 4 | C | B | Yes | Potentially contaminating activities, including contaminated stockpiles | One PCB result above trigger in DSI. Need further data to confirm if trigger met. | Possible | Further data needed before trigger can be confirmed | Y |  | GME from existing wells and stockpile sampling to calculate UCLs. No need for PSI as existing DSI complete. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP | EES DSI (2015), Depot component only. |  |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | E |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Comms Site | Riverside Plaza Comms Site | TC-FLINXXXX |  | Level 20, 452 Flinders Street, Melbourne, Victoria 3000 | 2/PS304276 | -37.819 | 144.9588 | TBC | TBC | Leased | Active | Danny - sent followup email 12/03 | Yes / Yes | 2021-04-18 | S. Whitehouse | Yes | [8 empty] | 2 | [6 empty] | 1 |  | 0 | 3 | 4 | 5 | 5 | 4 | 1 |  |  | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | [5 empty] | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | No | No | No | No | No | No | No | No | Yes | No | Yes | No | #N/A |  |  |  | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Riverside Quay Office | TBC River Quay |  | Level 6, 4 Riverside Quay, Southbank VIC 3006 | 2/PS304276 | -37.8208 | 144.9633 | External Land Owner- Leased Facility | AusNet Services | Leased | Active | Uploaded 14/03 | Yes / Yes | 2021-02-19 | Vanessa Cripps | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Kept in plant room with regular maintenance | 5 | None | None | None | Fuel Default | None | None | None | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 5 |  |  |  | 2 | 4 | A | C | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | Electricity Distribution | Central | TBC | TBC | [23 empty] | C-I-C
City Gate | Rockbank City Gate | ROCK |  | 1004 CHRISTIES ROAD, Truganina, 3029 | None | -37.7947 | 144.7343 | TBC | TBC | TBC | Active | Done | Yes / Yes | 2021-01-12 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 7 | 1 | 4 | 5 | 5 | 3 | 3 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 4 |  |  |  | 2 | 2 | C | E | No |  |  | #REF! | [14 empty] | 3 | 1 | 5 | 3 | 3 | 2 | 5 | 3.5 | 4 | 4 Possible: B |  |  |  | No |  | Regulator | No | No | No | No | No | No | No | No | No | No | Yes | No | #N/A |  |  |  | Electricity Distribution | North | Cameron Wilson | B | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Rowville Depot and Data Centre | WH-1004 |  | 890-900 Wellington Road, Rowville VIC 3178 | Part of 2\PS331610 | -37.9269 | 145.2281 | TBC | TBC | Freehold | Active | UPLOAD 20/03 4 assessments complete for Rowville | Yes / Yes | 2020-06-16 | Trevor Harris / David Cairns | Yes |  |  | AusNet, Transmission Sites, Portfolio EMP | [5 empty] | 5 |  | Oil spill onto grassed area in 2019. Reported to be small and cleaned up. |  |  |  |  | 5 | Oil drums, generators, chemical storage | 4 | 3 | 3 | 5 | 5 | 4 | 5 |  | Bunding, engineering and administrative controls | 5 | None | Oil Default | Yes | >1,000 L | >100 L | Yes - Small Volume | Yes - LPG | Spoil / Waste | [5 empty] | No | [6 empty] | 4 | 4 | [5 empty] | 4 | C | C | Yes | Potential contaminating activities and reported spillage | Confirm clean up of spill with Zinfra |  | No stockpiles reported | Y |  | PSI with limited soil sampling program. Confirm spill clean up with Zinfra or sample to confirm. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP |  |  |  | 4 | 5 | 4 | 5 | 5 | 5 | 3 | 4 | 3.5 | 4 | 4 Likely: B | D | Leaking transformers | CHECK | Leaking transformers | #N/A | Zone sub station | No | No | No | No | No | No | No | No | Yes | No | Yes | No | No |  |  |  | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Switchyard | Rowville Terminal Station 500Kv Switch Yard | TBC TS-Rowville TS-RTFX |  | 890-900 Wellington Road, Rowville VIC 3178 | 3\PS331610 | -37.9319 | 145.2282 | TBC | TBC | Leased | Active | Done - TBC TS-Rowville | Yes / Yes | 2020-06-12 | A Ryan | Yes |  |  |  |  | EPA notified of spill |  |  |  | 2 |  | Known spill in 2006 - cleanup conducted with EPA |  |  |  |  | 5 | Oil containing equipment, diesel generators, batteries & SF6/gas cylinders | 3 | 4 | 1 | 1 | 1 | 3 | 5 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 4 | None | Large | Yes | <1,000 L | Default Chemicals | Yes - Small Volume | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 4 | 4 | 4 |  |  |  | 2 | 4 | C | D | Yes |  |  | #REF! | [12 empty] | EPA notified of spill | 3 | 5 | 4 | 5 | 5 | 5 | 3 | 2 | 2.5 | 3 | 3 Possible: C | E | Mostly upgraded - old transformers on site | CHECK | No | 0 | Zone sub station | No | No | Yes | No | No | No | No | No | Yes | No | Yes | No | No | N/A | N/A | N/A | Electricity Distribution | East | TBC | TBC | C2 | Enviro -one above and one below ground systems in place ansd stormwater isolation valves fitted | N | Confidence 2/5. No environmental reports. | Known spill in 2006 done with EPA (PRA note). Risk rating driven by high consequence of contamination score, oil containing equipment with leak rating of 4/5. Presence of other potentially contaminating activities. Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1. Site inspection to confirm current environmental status. 2. Service and repair leaking transformers. 3. Clean oil staining from bunds. 4. Check bund integrity. 5. Install GAC scrubber post puraceptor treatment to further decrease hydrocarbon load. |  | C-I-C | C-I-C | x |  | C-I-C | [11 empty] | C-I-C
Terminal Station | Rowville TS (ROTS) | TS-ROTS | Central | 890-900 Wellington Road, Rowville, Victoria 3178 | 2\PS331610 | -37.9269 | 145.2281 | AusNet Services | Zinfra | Freehold | Active | 2020-06-12 | Yes / Yes | 2020-06-12 | A Ryan | Yes | Yes | [5 empty] | Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 38 | Drainage complaints from residents |  |  |  |  | 5 |  | Check | 4 | 1 | 1 | 1 | 3 | 4 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Large Volume |  | Spoil / Waste | [5 empty] | No | [6 empty] | 4 | 4 | 5 |  |  |  | 2 | 4 | C | C | Yes |  |  | #REF! |  | Y | [9 empty] | Preliminary Groundwater Investigation 2003. SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 2 | 4 | 4 | 3 | 4 | 4 | 3 | 2 | 2.5 | 3 | 3 Likely: B | E |  | CHECK | No | 0 | Zone sub station | No | No | No | No | No | No | No | No | Yes | No | Yes | No | No | N/A | N/A | N/A | Electricity Distribution | East | TBC | TBC | C1 | enviro -one above and one below ground systems in place ansd stormwater isolation valves fitted | N | Confidence 3/5. Environmental report from 2003. | Past drainage complaints from residents (cell 206AB). Date unknown. Risks driven by oil leak condition 4/5, presence of other potentially contaminating activities, consequence of contamination score. Stockpiles on site. Self bunded diesel generators on site, no photo though. Number of Transformers is unknown | 1. Site inspection to confirm current environmental status. 2. Service and repair leaking transformers. 3. Clean oil staining from bunds. 4. Check bund integrity. 5. Confirm the status of the stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. 6. Install GAC scrubber post puraceptor treatment to further decrease hydrocarbon load. |  | C-I-C | C-I-C | x |  | C-I-C | [11 empty] | C-I-C
Sub Station | Rubicon A ZSS (RUB-A) | DS-RUB | North | 220-240 Rubicon Road, Rubicon, Victoria 3712 | 1\PS347126 | -37.2925 | 145.8184 | TBC | TBC | Freehold | Active | Uploaded 16/03 | Yes / Yes | 2020-07-15 | CJ Wilson | Yes | [8 empty] | 2 | 7 | [5 empty] | 3 | Oil containing equipment and batteries | 0 | 1 | 1 | 2 | 2 | 1 | 3 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | <10 kg or <50 mg/kg | Large | Yes |  | None | None |  | None | [5 empty] | No | [6 empty] | 3 | 2 | 5 |  |  |  | 2 | 3 | C | D | No |  |  | #REF! | [6 empty] | Yes | Rebuild due 2014-2020 | [5 empty] | Check | 3 | 1 | 3 | 3 | 3 | 3 | 2 | 2.5 | 3 | 3 Unlikely: D | E |  | CHECK | No | 0 | Zone sub station | No | No | No | No | No | No | No | No | Yes | No | Yes | No | No | N/A | N/A | N/A | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Sale Depot | WH-0017 |  | 7-9 Dawson Street, Sale, Victoria 3850 | 1\LP128327 | -38.0916 | 147.0591 | Downer | Downer | Leased | Active | Sharepoint updated. Downer received lease - don't do | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 4 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 3 | 4 | 4 | 5 | 4 | 4 | 2 | 2 | 2 | 2 | 2 Likely: C | C | Oil leaking | CHECK | Leaking transformers | check | Zone sub station | No | No | Yes | No | No | No | No | No | Yes | No | Yes | No | No |  |  |  | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Sub Station | Sale ZSS (SLE) | DS-SLE | East | 391-403 Raglan Street, Sale, Victoria, 3850 | 1\TP749361 | -38.1015 | 147.0958 | AusNet Electrical Services | TBC | Freehold | Active | Done | Yes / Yes | 2021-01-21 | M Snell | Yes | BSE (2022) |  | AusNet, Distribution Sites, Portfolio EMP |  |  | BSE - PSI (2022), Water Quality Investigation Program-BSE(2022) |  | 2022-09-01 | 5 | 6 |  | 4 |  | Concreted over former leaks, oil coming back up |  | 3 | Oil filled equipment | 3 | 3 | 3 | 5 | 5 | 4 | 4 |  | Fully compliant sealed bund | 5 | <10 kg or <50 mg/kg | Large | Yes | Fuel Default | Default Chemicals | Yes - Small Volume | None | Spoil / Waste | Yes - Septic | Yes |  |  |  | No | [6 empty] | 3 | 4 | 5 | Yes | 5 | Yes | 3 | 4 | C | C | Yes | Potential contaminating activities. | Investigate leakage and condition of hardstand, likely needs targeted sampling in accordance with Duty to Manage. No Duty to Notify | #REF! | Historical leakages, concreted over former leaks, oil coming back up, however, as sealed exposure not likely, no Duty to Notify | Y | Y | PSI with limited soil and groundwater investigation. | Yes | Stage 2 - due 2018 |  |  |  | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 3 | 4 | 4 | 5 | 4 | 4 | 5 | 1 | 3 | 3 | 3 Likely: B | B | Planning 2021-25 | CHECK | Leak/explosion June 2020 | Check details | Zone sub station | No | No | No | No | No | No | No | No | Yes | No | No | No | No |  |  |  | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Sub Station | Sassafras ZSS (SFS) | DS-SFS | Central | Ferndale Road (The Basin), Sassafras, Victoria 3787 (between Hilton and Coach Rd) | 293\LP12973 | -37.8607 | 145.3352 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-06-11 | A Ryan | Yes | [8 empty] | 2 | 8 | [5 empty] | 4 | Oil containing equipment, batteries and chemicals | 1 | 1 | 1 | 2 | 2 | 1 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | None | Large | Yes | None | Default Chemicals | None | None | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 4 |  |  |  | 2 | 4 | C | C | No |  |  | #REF! | [6 empty] | Yes | Rebuild due 2014-2020 | [5 empty] | Check | 1 | 1 | 2 | 1 | 1 | 5 | 2 | 3.5 | 4 | 4 Rare: C |  |  |  | No |  | ZSS | No | No | No | No | No | No | No | No | No | No | Yes | No | #N/A |  |  |  | Electricity Distribution | North | Cameron Wilson | C | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Scoresby Office | TBC Scoresby |  | Level 1, 37 Dalmore Dve, Scoresby VIC 3179 | None | -37.914 | 145.2184 | TBC | TBC | Leased | Active | Closed office. | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | B | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | C | Stage 2 rebuild DD-6205 will be delivered 2020 | #N/A | #N/A | #N/A | #N/A | Yes | No | No | Yes | No | No | No | No | Yes | No | Yes | #N/A | #N/A |  |  |  | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Seymour Depot | WH-0018 |  | 67 Anzac Avenue, Seymour, Victoria 3660 | 1\TP136972 | -37.0278 | 145.142 | AusNet Services Electricity Services Pty Ltd | Downer | Freehold | Active | UPLOAD 20/03 | Yes / Yes | 2021-02-15 | J Smith | Yes | [8 empty] | 2 | [6 empty] | 2 |  | Various | 3 | 3 | 3 | 3 | 3 | 1 |  | Various types of bunding and triple interceptor trap on-site with administrative controls in place | 3 | None | Oil Default | Yes |  | None | None | Yes - LPG | None | [5 empty] | No | [6 empty] | 3 | 2 | 5 |  |  |  |  | 3 | B | D | Yes |  |  | #REF! | [13 empty] | No | 1 | 3 | 1 | 1 | 1 | 3 | 2 | 2.5 | 3 | 3 Rare: D |  | No assets on site | CHECK | Check | #N/A | Zone sub station | No | No | No | No | No | No | No | No | Yes | No | No | No | No |  |  |  | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Sub Station | Seymour East Regulator (RSME) | DS-RSME | North | 2 Darcy Street cnr Pearce Street, Seymour VIC 3660 | None | -37.055 | 145.1719 | TBC | TBC | Peppercorn Lease | Active | Uploaded 16/03 | Yes / Yes | 2020-07-14 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 3 | Oil containing equipment and batteries | 0 | 1 | 4 | 5 | 5 | 3 | 1 |  | Brick bund with no oil/water separator & monthly inspections | 5 | <10 kg or <50 mg/kg | Oil Default | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 2 |  |  |  | 5 | 3 | B | D | Yes |  |  | #REF! | [13 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 4 | 1 | 2.5 | 3 | N/A not owned by AST | 0 | Ausnet is not responsible for any of the oil filled plant or drainage on site. Site not owned by Ausnet. | N/A | No | 0 | 0 | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | No | 0 |  |  |  | Electricity Transmission | Central | TBC | TBC | [23 empty] | C-I-C
Sub Station | Seymour ZSS (SMR) | DS-SMR | North | 200 Anzac Avenue, Seymour, Victoria 3660 (cnr Howell Rd) | 2\LP126874 | -37.0358 | 145.1547 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-07-14 | CJ Wilson | Yes | [8 empty] | 2 | 3 | [5 empty] | 3 | Oil containing equipment, batteries and SF6 | Check | 4 | 1 | 2 | 2 | 3 | 2 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 5 |  |  |  | 1 | 3 | C | D | Yes |  |  | #REF! | [6 empty] | Yes | Rebuild due 2017-2024 | [5 empty] | Check | 2 | 1 | 3 | 2 | 2 | 3 | 1 | 2 | 2 | 2 Unlikely: D | #N/A | #N/A | Check | No | No | Switching Station | Yes | Yes | No | No | No | No | No | No | No | No | Yes | No | No | #N/A | We have recently taken back the SVC which was a shred site with the Gas Power Station, The SVC is currently in the process to be updated in to SAP. |  | Electricity Distribution | East | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Shepparton TS (SHTS) | TS-SHTS | North | 280-300 Verney Road, Shepparton North, Victoria, 3631 | 1\TP329292, 1\TP335779 & part 2\LP57717 | -36.3435 | 145.4157 | TBC | TBC | Freehold | Active | 2020-07-15 | Yes / Yes | 2020-07-15 | CJ Wilson | Yes | Yes | WSP (2023) | AusNet, Transmission Sites, Portfolio EMP |  |  | GME-GHD (2005), DSI-WSP (2023) | Geo-Eng - Environmental Risk Assessment (1996). GHD - Groundwater Monitoring (2005). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) | 2022-01-01 | 5 | 20 |  | 5 |  | Contaminated soil and asbestos on-site | Medium Risk | 5 | 5 transformers on-site | 5 | 3 | 3 | 2 | 3 | 3 | 3 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | Fuel Default | None | Yes - Small Volume | Yes - LPG | Spoil / Waste | Yes - Septic |  |  | Default Asbestos |  | No |  |  | None |  |  |  | 4 | 5 | 5 | Yes | 4 | Yes | 2 | 5 | C | B | Yes | Infrastructure with high potential for contamination | No actual testing but likely to be impacts based on design | Possible | High likelihood of contamination due to large oil storage and unsealed bund - no testing to confirm. | Y | Y | PSI and soil classification prior to commencement. Remediation and validation to be undertaken as part of site upgrades. GME from existing wells. | Yes | New project to replace building currently in prgress |  |  |  | AusNet, Transmission Sites, Portfolio EMP |  | Geo-Eng - Environmental Risk Assessment (1996). GHD - Groundwater Monitoring (2005). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 4 | 3 | 1 | 1 | 3 | 3 | 4 | 2 | 3 | 3 | 3 Unlikely: D | N/A | Station has been compliant since built so no contamination should be present | 1999; 3x2000 | No | Check | Terminal Station | Yes | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes |  | Not included |  |  | Electricity Transmission | Central | TBC | TBC | C1 | Enviro - one above ground system stormwater isolation valves fitted. | Y | Confidence 5/5. 2023 and 2024 PSI and GME reports for site. | Risk driven by oil leak and bunding rating 3/5 each; and consequence of contamination score. Bunds have brick walls - what are the seals like? No shut off valve at site (according to PRA) but noted in cell DZ215. Water goes into an on-site dam south of the switch yard a triple interceptor trap (TIT) and water retention dam were observed. The TIT comprised of a large in-ground concrete pit that was used for processing effluent and stormwater captured within the transformer bunded area. The concrete tank was connected to an above ground tank located, at the southern end of the concrete pit. The above ground tank was within a concrete bunded area. Water from this tank was pumped via an underground service into a swale drain and allowed to soak into the ground. | 1. Replace brick bunds with concrete hardstand. 2. Service and repair leaking transformers. 3. Clean oil staining from existing hardstand 4. Check integrity of existing hardstand surfaces. 5. Resolve status of swale drain soak area (is this lined?) |  | C-I-C | C-I-C | x |  |  |  | C-I-C | [9 empty] | C-I-C
Terminal Station | South Morang TS (SMTS) | TS-SMTS | Central | 385 McDonalds Road, South Morang, Victoria, 3752 | 1\PS405696, 1\TP89646, 1\TP379262, 2\TP379262 & 2\TP740561 | -37.645 | 145.0748 | AusNet Services | AusNet Services | Freehold | Active | 2020-06-03 | Yes / Yes | 2020-06-03 | A Ryan | Yes | BSE (2022) |  | AusNet, Transmission Sites, Portfolio EMP |  |  | BSE - PSI (2022), BSE-Soil report (2023) | SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) | 2023-06-01 | 5 | 3 |  | 3 | 2 | Historic backfilling with unknown material. PSI has not identified widespread issues, but data gaps remain. |  | 5 | AGST present but areas inaccessible for PSI. Therefore risk unchanged. | 10 | 4 | 1 | 2 | 2 | 3 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | >1,000 L | <100 L | Yes - Small Volume | Yes - LPG | Spoil / Waste | Yes - Septic |  |  | None | None | No |  |  | None |  |  |  | 2 | 2 | 5 | Yes | 5 | Yes | 3 | 3 | B | B | Yes | Potential for localised contamination to be present in vicinity of site infrastructure. Areas of fill remaining to be assessed. WQIP to be undertaken. | No widespread contamination identified by PSI. | #REF! |  | Y | Y | PSI with limited soil sampling program. GME from existing wells. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP |  | SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | Electricity Distribution | Central | TBC | TBC | C2 | enviro -four above ground systems in place and stormwater isolation valves fitted | N | Confidence 5/5. BlueSphere 2022 and 2023 reports available. | Risk driven by oil leak rating of 4/5. No shut off valve noted in PRA, which drives the consequence of contamination rating. However, shut off valve noted as present in cell DZ216. Transformers in bunds with hardstand, staining with bunds. Aboveground Storage Tank (AGST) present at Site (BlueSphere, 2022) | 1. Service and repair leaking transformers. 2. Check bund integrity 3. Clean bunds. 4. Consider completing surface water testing post puraceptor treatment to ascertain if a GAC scrubber is recommended. |  | C-I-C | C-I-C | x | [13 empty] | C-I-C
Sub Station | South Morang ZSS (SMG) | DS-SMG | Central | 385 McDonalds Road, South Morang VIC 3752 | 2\TP740561 | -37.645 | 145.0748 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-03 | A Ryan | Yes | [8 empty] | 2 | 8 | [5 empty] | 5 | Large oil containing equipment, batteries and chemicals | 2 | 1 | 1 | 2 | 2 | 1 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | None | Large | Yes | None | Default Chemicals | None | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 4 | 4 | 4 |  |  |  | 2 | 4 | B | C | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | Electricity Distribution | Central | TBC | TBC | [23 empty] | C-I-C
Sub Station | Southern Reactor Compensator Station (SRCS) | TBC SRCS | Central | Bass Hwy/Rayner Hoff Drive, Lang Lang VIC 3984 | None | -38.3376 | 145.5589 | Government | AusNet Services | TBC | TBC | Done | Yes / Yes | 2020-07-23 | A Ryan | Yes | [8 empty] | 2 | [6 empty] | 5 | Oil containing equipment, diesel generator, batteries & SF6/gas cylinders | 1 | 1 | 1 | 2 | 2 | 1 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 2 | None | Oil Default | Yes | <1,000 L | None | Yes - Small Volume | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 2 |  |  |  | 2 | 3 | B | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Yes | Yes | No | No | No | No | No | Yes | #N/A | #N/A | Yes | #N/A | #N/A | #N/A |  |  | Electricity Transmission | East | TBC | TBC | C1 | enviro - one below ground system, outlet free flows to stormwater drains | Y | Confidence 2/5. No environmental reports. 1 site inspection report. | Risk driven by presence of oil containing equipment, diesel generator, consequence of contamination. New site. Generators said to be self bunding, but photos don't show bunds. Review of Caterpillar XQE100 generator shows that it has a containment area for fuel spills. | 1. Complete site inspection to confirm environmental status of the site. 2. Install shut off valve at site. Cell DZ218 says that outlet free flows. | [10 empty] | C-I-C | [6 empty] | C-I-C
Comms Site | Speers Lane Comms Site (SPLN) | TBC TC-SPLN |  | Speers Lane, Dederang VIC 3691 | None | -36.4463 | 147.0037 | TBC | TBC | Leased | Active | Cameron Wilson confirmed the site is a repeater board in a farmers paddock. Site assessment not required.​ | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 3 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | B | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | Electricity Transmission | East | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Springvale TS (SVTS) | TS-SVTS | Central | 905 Princes Highway, Springvale, Victoria 3171 | 1\PS401439 | -37.9278 | 145.146 | TBC | TBC | Freehold | Active | 2020-06-16 | Yes / Yes | 2020-06-16 | A Ryan | Yes | Yes | [5 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 18 | Minor oil spill with marginal PCB contamination and a second oil spill with less than 10L in 2020. Oil spill from exploded cap bank in 2021 |  |  | Category A soil in upper couple of metres identified April 2021 - planned to be taken off site | Medium Risk | 5 |  | Check | 3 | 1 | 1 | 1 | 2 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals |  |  | Spoil / Waste | [5 empty] | No | [6 empty] | 4 | 4 | 2 |  |  |  | 2 | 4 | A | C | Yes |  |  | #REF! |  | Y | [9 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | Electricity Distribution | East | TBC | TBC | C1 | Enviro -one above ground system in place and stormwater isolation valves fitted | N | Confidence 3/5. No environmental report since 2003. | Risk driven by note of minor oil spill with marginal PCB contamination and a second oil spill with less than 10L in 2020. Oil spill from exploded cap bank in 2021. Oil leak condition 3/5. Presence of potentially contaminating activities. Soil remediation was described in 2020 site inspection. Nothing on the environment register to indicate if it was closed out. Presence of stockpiles. | 1. Complete site inspection to confirm environmental status of the site. 2. Validate that environmental incidents from 2020/ 2021 were closed out, and that soil remediation was completed. 3. Service and repair leaking transformers. 4. Clean bunds. 5. Check bund integrity. 6. Confirm the status of the stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. |  | C-I-C | C-I-C | x | [13 empty] | C-I-C
City Gate | Stawell City Cate | STAW |  | DANE ROAD, Stawell, 3384 | None | -37.0248 | 142.8218 | TBC | TBC | TBC | Active | Uploaded 14/03 | Yes / Yes | 2021-02-16 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Ex Gas Works Site | Stawell Former Gas Works Site | TBC - Stawell |  | 47 - 49 Wimmera Street, Stawell, Victoria, 3380 | 13~39\PP3499 & 15~39\PP3499 | -37.0587 | 142.7829 | AusNet Services |  |  |  | Documentation to Dan/Will. Not in Sharepoint list | assessment complete - to do |  |  | Yes |  |  | Coffey - Environmental Management Plan (EMP) (2012) | Yes | Pollution Abatement Notice / Clean Up Notice and associated correspondence (2005) | Coffey - Environmental Audit Report: Former Stawell Gasworks (2012), Coffey - Groundwater Management Plan: Former Stawell Gasworks Site (2012) |  |  | 5 |  |  | 5 | 2 | CUTEP Complete |  | 1 |  | TBC | 1 | 4 | 5 | 5 | 3 | 3 |  |  | 5 | None | Oil Default | [11 empty] | No | [6 empty] | 3 | 2 | [5 empty] | 3 | B | D | Yes |  |  | #REF! | [9 empty] | Coffey - Environmental Management Plan (EMP) (2012) | Coffey - Environmental Audit Report: Former Stawell Gasworks (2012), Coffey - Groundwater Management Plan: Former Stawell Gasworks Site (2012) |  | Pollution Abatement Notice / Clean Up Notice and associated correspondence (2005) | Check | 3 | 3 | 1 | 3 | 3 | 2 | 2 | 2 | 2 | 2 Unlikely: D | N/A | Transformer on site owned/maintained by Snowy Hydro | CHECK | Check |  | Switching Station | Yes | No | Yes | No | No | No | No | No | Yes | No | Yes | No | No | N/A |  |  | N/A | East | TBC | TBC | [23 empty] | C-I-C
Comms Site | Strathdownie Comms Site (STRN) | TC-STRNXXXX |  | Hutchinsons Rd, Strathdownie VIC 3312 | 1\PS747680 | -37.7978 | 141.0328 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 29/09/2020 (put 20/09 in Enablon) | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | Check | 2 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | B | E | No |  |  | #REF! | [13 empty] | 5 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 Rare: E | N/A |  | 2x1992; 1993; 2004;2008 | No - Transformers have been fully bunded since installed | 0 | Terminal Station | Yes | Yes | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | 0 | 0 |  |  | Electricity Transmission | Central | Andrew Ryan | E | [23 empty] | C-I-C
City Gate | Sunbury City Gate | SUNB |  | Shields Rd, Sunbury, Victoria 3429 | None | -37.5879 | 144.7312 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-18 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | HOW DOES A PS HAVE NO TR? | 1 | 4 | 5 | 5 | 3 | 3 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 4 |  |  |  | 1 | 2 | #VALUE! | E | No |  |  | #REF! | [13 empty] | 20 | 3 | 1 | 1 | 3 | 3 | 4 | 2 | 3 | 3 | 3 Unlikely: D | N/A | Screening panels in the front fence | 1969;2015;18x2018 | No | N/A | Terminal Station | Yes | No | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | 0 | The site is located on Coulsons Road, Ballarat within a semi rural setting. The Terminal Station (“the site”) is relatively flat and level, however the site is in an elevated position and natural surface drainage of the surrounding area is to both the south west and east. The property on the opposite (northern) side of Coulsons Road is residential with an adjoining workshop that has an above ground fuel storage tank. | There is also a farm dam north east of the workshop. The nearest water receptor is this dam, however, there is no hydraulic connection except via possible local groundwater (unlikely). Stormwater from the site drains to either a creek (Palmer Gully) approximately 200 metres east of the site or to the south west. | TD-0003466 XC38 - BATS SHTS Station Service Tx Upgr | Electricity Transmission | West | Andrew Ryan | D | [23 empty] | C-I-C
City Gate | Sunshine City Gate | TBC Sunshine CG |  | 134 Phoenix Street, Sunshine, Victoria, 3020 | 19/LP80228 | -37.7752 | 144.8296 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-11-20 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 6 | 2 | 4 | 5 | 5 | 3 | 3 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 2 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 3 | 3 | 3 | 4 | 3 | 3 | 2 | 2 | 2 | 2 | 2 Rare: E | 0 |  | 5x2013, 1981 | No | 0 | Terminal Station | Yes | No | No | No | No | No | No | No | No | No | Yes | No | 0 | The site is located on Allingham Street, Bendigo within an industrial setting. The Terminal Station (“the site”) is terraced into two levels to house the 220 kV yard and the 66kV yard. The site is in an elevated position and natural surface drainage of the surrounding area is generally to the north. The adjacent property to the south is a motor wrecker. Stormwater from the site drains to the municipal Stormwater System. The nearest residences are approx 250m west from the site | The site is approximately rectangular and contains a Control Room and a number of other associated buildings including a workshop/store, a hazardous goods store and a compressor house. The site has a total area of approximately 3.7 Ha. | 0 | Electricity Transmission | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Sydenham City Gate | SYDE |  | 1052 MELTON HIGHWAY, Plympton, 3335 | None | -37.6891 | 144.7179 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2021-01-12 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 7 | 2 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 2 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | 3 | 1 | 1 | 2 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Unlikely: D | 0 |  | 3x2019 | No | 0 | Terminal Station | Yes | No | No | No | No | No | No | Yes | No | No | Yes | No | 0 |  |  |  | Electricity Transmission | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Sydenham TS (SYTS) | TS-SYTS | Central | 67 Victoria Road, Sydenham (Plumpton), Victoria 3038 | 1\TP78358 | -37.6879 | 144.7629 | TBC | TBC | Freehold | Active | 2020-06-02 | Yes / Yes | 2020-06-02 | A Ryan | Yes | Yes | [5 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | [5 empty] | Low | 3 |  | 3 | 5 | 4 | 4 | 4 | 5 | 2 |  | Shut off valve | 5 | <10 kg or <50 mg/kg | Oil Default | Yes | None | Default Chemicals | Yes - Large Volume |  | Spoil / Waste | [5 empty] | No | [6 empty] | 4 | 4 | 4 |  |  |  | 2 | 4 | B | C | Yes |  |  | #REF! |  | Y | [9 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 10 | 2 | 3 | 4 | 2 | 2 | 5 | 2 | 3.5 | 4 | 4 Rare: C | N/A |  | 1967; 2006; 5x2012;3x2013 | Old transformers pre-bunding upgrades. Soil removed and some level of remediation completed before bunding upgrade. | 0 | TS | Yes | Yes | No | No | No | No | No | No | Yes | No | No | No | 0 |  |  |  | Electricity Transmission | Central | Andrew Ryan | D | C1 | enviro -no enviro system but has stormwater isolation valves fitted | N | Confidence 3/5. No environmental report since 2003. | Risk driven by oil leak condition and no bunding, presence of potentially contaminating activities including stockpiles on Site. There is a shut off valve. | Site is to be decommissioned. No upgrades/ management improvements recommended. | [17 empty] | C-I-C
Comms Site | Sydenham TS Comms Site (SYTS-COMS) | TC-SYTSXXXX |  | 67 Victoria Road, Sydenham (Plumpton), Victoria 3038 | 1\TP78358 | -37.6879 | 144.7629 | TBC | TBC | Freehold | Active | In SYTS Done | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 8 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 5 | 5 | 5 Rare: C | N/A | Yes there have been noise complaints since long before the rebuild to the current station, a lot of works have been done regarding noise control, from interlocked fans with lighting, time switches on toilet fans and sound proofing on the ventilation covers of the transformers Yes visual complaints over a long period of the old station and then in design for the new station, however planning permit required a visual screening to be built to minimise visual impact of the site | 2x2006; 2011; 2x2015; 3x2016 | Considerable soil remediation was carried out during rebuild and new transformers with fully compliant bunds installed | Check | Terminal Station | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 0 | The site is located on the corner of King and Alister Street, Brunswick, within a residential setting. The Terminal Station (“the site”) is relatively flat and level, however the site is in an elevated position in relation to the adjacent Merri Creek. South east of the site is the “Sumner Park Recreation reserve. Natural surface drainage of the surrounding area is to the Merri Creek. | The site is approximately rectangular, however the north eastern boundary follows the course of the Merri Creek. The site contains a large workshop building and numerous other associated buildings including a former training complex. The main building and the former training complex appear to be disused. The site has been utilised as a Terminal Station since 1975. There is a disused incinerator at the site. It has a total area of approximately 4.4 Ha. | 0 | Electricity Transmission | Central | TBC | TBC | [23 empty] | C-I-C
Comms Site | Taminick Comms Site (TAMK) | TC-TAMKXXXX |  | Off Gravel Pit Rd, Taminick VIC 3675 | 1/PS642373 | -36.38 | 146.2447 | TBC | TBC | Easement | Active | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 5 | 2 | 4 | 5 | 5 | 3 | 2 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 5 |  |  |  | 1 | 3 | A | D | Yes |  |  | #REF! | [13 empty] | 9 | 2 | 1 | 2 | 2 | 2 | 4 | 2 | 3 | 3 | 3 Unlikely: D | N/A | Yes, a timber fence and vegetation was positioned along the railway easement to reduce visual outlook and vegetation on earth mounds placed around the station | 7x2005; 2009; unknown | Transformers have been fully bunded since installed | 0 | Terminal Station | Yes | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | 0 | Not included | Not included | 0 | Electricity Transmission | Central | Andrew Ryan | D | [23 empty] | C-I-C
Terminal Station | Tarrone TS (TRTS) | TBC TS-TRTS | West | Tarrone North Road, Tarrone VIC 3283 | 2\LP218923 | -38.1792 | 142.181 | TBC | TBC | Leased | Active | New station (A Ryan) | New |  |  | N/A | [8 empty] | 1 | [6 empty] | 3 | New | 10 | 2 | 1 | 1 | 1 | 1 | 1 |  | New | 2 | None | Oil Default | [11 empty] | Yes | [6 empty] | 3 | 2 | [5 empty] | 3 | A | D | No |  |  | #REF! | [13 empty] | 1 - service | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 Rare: E | 0 |  | 1905-07-10 | No | 0 | Terminal Station | Yes | No | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Transmission | West | TBC | TBC | N/A | Not in this list. | Y | Confidence 1/5. No environmental reports. | New Site. Risk driven by lack of information. No site inspection information at all on Env register. | 1. Site inspection to confirm environmental status. | [17 empty] | C-I-C
Comms Site | Tatura Comms Site (TATA) | TC-TATAXXXX |  | 5735 Midland Hwy, Tatura VIC 3616 (East of Mulcahy Rd) | 1\PS648490 | -36.4151 | 145.2133 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 1 | 2 | E | E | No |  |  | #REF! | [13 empty] | 7 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 3.5 | 4 | 4 Rare: C | N/A |  | 1961; 2x1979; 2002; 2003; 2x2015 | No | 0 | Terminal Station | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | No | 0 |  |  |  | Electricity Transmission | North | Cameron Wilson | C | [23 empty] | C-I-C
| TBA | TBA | TBA | Selby | [20 empty] | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | [20 empty] | 0 | 0 | [5 empty] | N/A | [19 empty] | HOW DOES A PS HAVE NO TR? | 1 | 1 | 1 | 1 | 1 | 3 | 2 | 2.5 | 3 | 3 Rare: D | 0 |  | 0 | No | 0 | Power Station Switch | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | No | 0 |  |  |  | Electricity Transmission | North | Cameron Wilson | D | [23 empty] | C-I-C
Terminal Station | Templestowe TS (TSTS) | TS-TSTS | Central | 630-658 Blackburn Road, Templestowe, Victoria 3106 | 1\TP448079 | -37.7488 | 145.1693 | TBC | TBC | Freehold | Active | 2020-05-28 | Yes / Yes | 2020-05-28 | A Ryan | Yes | Yes |  | AusNet, Transmission Sites, Portfolio EMP |  |  |  | SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 5 | 56 | Historic report indicates drainage discharge exceeding discharge criteria (GHD, 2003) | 4 | 3 |  |  | 5 | Known oil in ground beneath transformers. In 2022, observations of oil in vicinity of transformers leaking through concrete into pits. | 6 | 4 | 1 | 2 | 2 | 3 | 2 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve. In 2022/ 2023 oil was observed to be seeping out of concrete in vicnity of transformers and into drains, which flowed into the holding tanks. Oily water flowed out of holding tank into swale drain and into retention dam. As at 2024, remediation of the retention dam was pending. | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume | Yes - LPG | Spoil / Waste | None |  |  |  |  | No | [6 empty] | 4 | 4 | 5 | No | 3 | Yes | 4 | 4 | B | C | Yes | Potential contaminating activities. |  | #REF! |  | Y |  | PSI with limited soil sampling program. GME from existing wells. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP |  | SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 7 | 2 | 1 | 1 | 2 | 2 | 5 | 2 | 3.5 | 4 | 4 Rare: C | N/A |  | 1 PT 2019, 2 PT 2011, 2 PT 1970; 1969; 1996 | Yes - Old transformers pre-bunding upgrades. Soil removed and some level of remediation completed before bunding upgrade. | 0 | TS | Yes - CB | Yes | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Transmission | Central | Andrew Ryan | C | C1 | Enviro -old system abandonded, now has one underground system, stormwater isolation valves fitted | N | Confidence 5/5. No recent environmental reports on register, however multiple visits have taken place. AECOM have conducted recent works. | Risk driven by known environmental issues at site - including NAPL in soil in the transformer area and to the north towards the retention dam. Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve. In 2022/ 2023, oil was observed to be seeping out of concrete in vicinity of transformers and into drains, which flowed into the holding tanks. Oily water flowed out of holding tank into swale drain and into retention dam. In 2024 the remediation of the retention dam was commenced. Also noted that in time, all existing transformers will be replaced. | 1. Install GAC scrubber post puraceptor treatment to further decrease hydrocarbon load. 2. Completion of a detailed Conceptual Site Model (CSM) and DSI including a soil and groundwater assessment around transformer area. 3. Confirm that swale drain rectification conducted in 2022 remains effective. 4. Prioritise replacement of transformers as to help bring forward environmental investigation, decrease oil load and ongoing leaks. | [5 empty] | C-I-C | [11 empty] | C-I-C
Comms Site | Tennyson Comms Site (TENN) | TC-TENNXXXX |  | PART 76 PINEGROVE SOUTH ROAD, TENNYSON, VICTORIA 3572 | None | -36.2949 | 144.4069 | TBC | TBC | Leased | In Progress | Done | Yes / Yes | 2020-07-13 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 2 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 1 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 6 | 2 | 1 | 1 | 2 | 2 | 4 | 2 | 3 | 3 | 3 Rare: D | N/A |  | 4 PT 1971, 1 PT 2016, 1 PT 1989 | Yes - Old transformers pre-bunding upgrades. Soil removed and some level of remediation completed before bunding upgrade. | 0 | TS. Some construction works were underway at the time, Ausnet major projects were the Principal Contractor in charge of the site | Yes - CB | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Transmission | Central | Andrew Ryan | D | [23 empty] | C-I-C
Terminal Station | Terang TS (TGTS) | TS-TGTS | West | Littles Lane/McRae Road, Terang, Victoria 3264 (0.5kms north of Princes Hwy) | 1\TP337263 | -38.233 | 142.932 | TBC | TBC | Freehold | Active | UPLOAD 20/03 CJ in Enablon. Andy also completed | Yes / Yes | 10/11/2020 & 17/12/2020 | A Ryan / CJ WIlson | Yes | Yes | [5 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003). Geoworks - Preliminary Site Assessment (2004). |  | 3 | 14 |  |  |  |  | Medium Risk | 4 | Oil containing equipment, SF6/gas cylinders, batteries & chemicals | 9 | 3 | 1 | 1 | 1 | 2 | 3 |  | Fully compliant sealed bund, puraceptor oil/water separator, shut off valve & administrative controls | 3 | >10 kg or >50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume | Yes - LPG | Spoil / Waste | Yes - Septic |  |  |  |  | No | [6 empty] | 4 | 4 | 5 |  |  |  |  | 4 | A | C | Yes |  |  | #REF! |  | Y | [9 empty] | SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003). Geoworks - Preliminary Site Assessment (2004). |  | 1 | 3 | 0 | 4 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Unlikely: C | N/A | No bunding required sized transformers on site, only 66kv circuit breakers and a station service transformer | 1 1968 | No | 0 | TS | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Transmission | Central | Andrew Ryan | C | C1 | Enviro - one above ground system, stormwater isolation valves fitted. | Y | Confidence 3/5. Environmental report from 2004. | Risk driven by known environmental incident in 2004. It was investigated, but unclear if remediation occurred. Sealed bund now reported, in 2004 it was gravel. Risk also driven by consequence of contamination. Review of site inspection from 2020 shows that transformers are new, not leaking. What was the extent of the 2004 impact. Unclear how much oil leaked, if it was ever cleaned up. Fully compliant sealed bund, puraceptor oil/water separator, shut off valve & administrative controls | 1. Confirm if there are records documenting the clean up of the leak in 2004. 2. Complete site inspection to resolve environmental status. 3. Confirm the status of the stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. | [17 empty] | C-I-C
Depot, Office and Warehouse Storage | Thomastown Depot | WH-1006 |  | 15 High Street (cnr Mahoney's Road), Thomastown, Victoria 3074 | 183\PSLP128541 | -37.7525 | 145.0263 | AusNet Services | Zinfra | Leased | Active | Done | Yes / Yes | 2020-06-04 | A Ryan | Yes |  |  |  | 53V Environmental Audit (2009) in response to a Clean-up notice |  |  |  |  | 5 |  |  | 1 |  |  |  | 3 | Oil containing equipment, chemicals and gas cylinders | 1 | 1 | 1 | 2 | 2 | 1 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank w no shut off valve | 2 | None | Oil Default | None | None | Default Chemicals | None | Yes - LPG | None | None |  |  | Default Asbestos |  | No | [6 empty] | 3 | 5 | 4 |  | 5 | Yes | 2 | 5 | C | C | Yes | Potential contaminating activities. | No actual testing but likely to be impacts based on nature of activities undertaken at the site. | #REF! |  |  |  | PSI with limited soil sampling program | [9 empty] | 2 | 1 | 2 | 3 | 1 | 1 | 2 | 1 | 1.5 | 2 | 2 Rare: E | N/A |  | 1966;1981;2x2014 | No | 0 | Terminal Station | Yes | Yes | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Transmission | North | Cameron Wilson | E | [23 empty] | C-I-C
Terminal Station | Thomastown TS (TTS) | TS-TTSX | Central | 15 High Street (30 Mahoney's Road), Thomastown, Victoria 3074 | 2\PS401440 | -37.6918 | 145.0119 | TBC | TBC | Freehold | Active | 2020-06-04 | Yes / Yes | 2020-06-04 | A Ryan | Yes | Yes |  |  | 53V Environmental Audit (2009) in response to a Clean-up notice, |  | Stormwater Sampling, Thomastown Terminal Station- BSE (July 2023), Stormwater Sampling, Thomastown Terminal Station- BSE (October 2023) | Coffey - 53V Audit report (2009). Coffey - Preliminary Waste Classification (2006). SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) | 2024-10-01 | 5 | 3 | Former dumping of mixed industrial wastes by former tenant | 1 |  | Historic filling activities and dumping activities. Some epa involvement. All closed out. |  | 5 |  | 5 | 3 | 1 | 1 | 1 | 2 | 2 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | >10 kg or >50 mg/kg | Large | Yes | None | None |  |  | Spoil / Waste |  | Yes |  | Default Asbestos |  | No | [6 empty] | 2 | 5 | 5 | Yes | 5 | Yes | 2 | 5 | C | C | Yes | Residual contamination above residential thresholds, but below industrial. Site managment plan in relation to residual asbestos. | 53V audit completed and risk well understood. | #REF! |  | Y | Y | Prepare Site Management Plan as per recommendation of 53V environmental audit. | [7 empty] | Coffey - 53V Audit report (2009). Coffey - Preliminary Waste Classification (2006). SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 5 | 2 | 1 | 2 | 2 | 2 | 4 | 2 | 3 | 3 | 3 Unlikely: D | 0 |  | 1986, 2006, 3x2007 | No | 0 | Terminal Station | Yes | Yes | No | Yes | No | No | No | No | No | No | Yes | No | 0 | The site is located on Williams Road, Horsham, on the corner of Riverside East Road, within a rural setting. The Terminal Station (“the site”) and the surrounding area is flat and the natural surface drainage of the surrounding area is generally to the west. Stormwater from the site drains to the table drain at the front (southern side) of the property. The table drain discharges to Burnt Creek approximately 2 km to the west. The nearest residences are approximately 300 metres to the east. | The site is approximately square and contains a Control Room, a maintenance workshop/store, and a compressor house. The site has a total area of approximately 9.0 Ha | 0 | Electricity Transmission | West | TBC | TBC | C1 | Enviro - one above ground system, stormwater isolation valves fitted | N | Confidence 5/5. Portion of the site has been audited (west of Edgars Creek). | Risk driven by presence of a UST, asbestos in soil (audit site), consequence of contamination. Site has a fully compliant sealed bund with puraceptor oil/water separator + shut off valve. Joey has observed sheen in water post triple interceptor trap treatment in 2024. Site has off site drainage to Edgar's Creek. Staining visible inside transformer bunds. | 1. Remediate/manage asbestos in western portion of Site. 2. Add GAC scrubbing system post puraceptor treatment. 3. Service and repair leaking bunds. 4. Clean bunds. 5. Check bund integrity |  | C-I-C | C-I-C | x |  | C-I-C | [11 empty] | C-I-C
Sub Station | Thomastown ZSS (TT) | DS-TTX | Central | 19 High Street, Thomastown, Victoria, 3074 (next to TTS, 500m north Mahoney's Rd) | 1\PS401440 | -37.8637 | 145.0398 | AusNet Electrical Services | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-04 | A Ryan | Yes | BSE (2022) |  | AusNet, Distribution Sites, Portfolio EMP | Yes | PAN (2003). EPA Correspondence (2005). Clean Up Notice (2006). Revocation of Clean Up Notice (2009). | PSI-BSE (2022) | AECOM - Groundwater Investigation (2008). AECOM - Soil Validation Report (2008). Coffey - Preliminary Waste Classification (2006). GHD - Environmental Inspections, Maintenance and Tests (2003) | 2022-09-01 | 5 | 54 |  | 3 |  |  |  | 4 | Oil containing equipment, chemicals and batteries | 3 | 3 | 1 | 1 | 1 | 2 | 2 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None | None | None | None | Yes |  |  |  | No |  |  | None |  |  |  | 4 | 4 | 4 | No | 5 | Yes | 4 | 4 | C | D | Yes |  |  |  | No duty to notify |  |  |  | Yes | Stage 2 - due 2018 |  |  |  | AusNet, Distribution Sites, Portfolio EMP |  | AECOM - Groundwater Investigation (2008). AECOM - Soil Validation Report (2008). Coffey - Preliminary Waste Classification (2006). GHD - Environmental Inspections, Maintenance and Tests (2003) | PAN (2003). EPA Correspondence (2005). Clean Up Notice (2006). Revocation of Clean Up Notice (2009). | 2 | 2 | 4 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 Rare: E | N/A |  | 3 1966, 2 2016; 2018 | Old transformers pre-transformer replacement works. Soil removed and some level of remediation completed before bunding upgrade | 0 | TS | Yes | Yes | No | Yes | No | Yes - coloured screen panels | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Transmission | Central | Andrew Ryan | E | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Traralgon Depot | WH-0020 |  | Lot 2, 5-13 Stratton Drv, Traralgon VIC 3844 | 2\PS540149 | -38.1887 | 146.5643 | Downer | Downer | Leased | Active | Sharepoint updated. Downer received lease - don't do | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 3 | 1 | 1 | 3 | 2 | 2.5 | 3 | 3 Rare: D | N/A |  | 1950; 3x2005 | No | 0 | Terminal Station | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | No | 0 |  |  |  | Electricity Transmission | North | Cameron Wilson | D | [23 empty] | C-I-C
Sub Station | Traralgon ZSS (TGN) | DS-TGN | East | Traralgon-Maffra Road, Traralgon, Victoria, 3844 | 1\TP518718 | -38.1893 | 146.5602 | TBC | TBC | Freehold | Active | Uploaded 16/03 | Yes / Yes | 2020-12-31 | M Snell | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 8 | [5 empty] | 4 | Oil containing equipment, batteries & SF6/gas cylinders | 3 | 3 | 1 | 5 | 5 | 4 | 1 |  | Fully compliant sealed bund | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 2 |  |  |  | 2 | 3 | B | C | Yes | Potential contaminating activities. |  | #REF! |  |  |  | PSI with limited soil sampling program. | Yes | Stage 1 - due 2017 |  |  |  | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 3 | 1 | 1 | 1 | 1 | 1 | 4 | 1 | 2.5 | 3 | 3 Rare: D | 0 |  | 2019x3 (1SS) | No | 0 | Terminal Station | Yes | No | No | No | No | No | No | Yes | No | No | Yes | No | 0 | Not included in the report |  |  | Electricity Transmission | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Tyabb TS (TBTS) | TS-TBTS | Central | 21 Thornells Lane (cnr Tyabb-Tooradin Road), Tyabb, Victoria 3913 | 1\TP162565 | -38.2681 | 145.202 | TBC | TBC | Freehold | Active | 2020-06-10 | Yes / Yes | 2020-06-10 | A Ryan | Yes | Yes | [5 empty] | Geo-Eng - Environmental Risk Assessment (1996). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 8 |  |  |  |  | Medium Risk | 5 |  | 5 | 3 | 1 | 1 | 1 | 2 | 2 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume | Yes - LPG | None | Yes - Septic |  |  |  |  | No | [6 empty] | 4 | 4 | 4 |  |  |  | 2 | 4 | B | C | Yes |  |  | #REF! | [11 empty] | Geo-Eng - Environmental Risk Assessment (1996). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 6 | 2 | 2 | 1 | 2 | 2 | 5 | 2 | 3.5 | 4 | 4 Rare: C | N/A |  | 6x2007 | Significant soil removed and some level of remediation completed before bunding upgrade as part of station rebuild the transformers have been fully bunded since installed. | Check | Terminal Station | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 | The site is located on Waverley Road, Malvern East, within a Residential setting. The Depot is built on a slope at the front of the property (“the site”) whereas the Terminal Station at the rear of the property is relatively flat. The site shares its south western boundary with the south eastern freeway. Natural surface drainage of the surrounding area is towards the freeway, which is built over a former drainage channel (“Scotchman’s Creek”). There is a Mobil Service Station immediately to the north of the site, on the opposite side of Waverley Road, on the corner of Batesford Road | The depot section of the site includes an office building, maintenance workshops and a hazardous good store. The Terminal Station includes a control building, machine building, additional maintenance workshops and storage sheds, and a cooling tower. The site is approximately triangular and has a total area of approximately 9.9 Ah |  | Electricity Transmission | Central | Andrew Ryan | TBC | C1 | Enviro -one above ground system in place and stormwater isolation valves fitted | Y | Confidence 3/5. Most recent environmental report from 2003. | Risk driven by oil leak rating, potentially contaminating activities. Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1. Complete site inspection to confirm environmental status. 2. Service and repair leaking transformers. 3. Clean bunds. 4. Check bund integrity. |  | C-I-C | C-I-C | x | [13 empty] | C-I-C
Sub Station | Upwey ZSS (UWY) | DS-UWY | Central | 155 Old Belgrave Road, Upwey, Victoria, 3158 | 1\TP533890 | -37.9023 | 145.3288 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-11 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 86 | [5 empty] | 4 | Oil containing equipment, chemicals and batteries | 1 | 2 | 4 | 5 | 5 | 3 | 3 |  | Brick bund with gravel floor, batteries in dedicated room, regular inspections | 5 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None | None | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 5 | No | 4 | No | 3 | 4 | A | D | Yes | Potential contaminating activities. |  | #REF! | NA |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 9 | 3 | 2 | 3 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Unlikely: C | N/A | 2002: Significant previous oil spills – 600 litres from reactor; Potential for presence of fill material (Bunker Ash); Previous clean-ups at site – removal by licensed contractor. Significant surface oil staining was identified, particularly around the transformers. Total volume of contaminated soil at the site is estimated to be 74 cubic metres. | 2x1961;3x1962;1974;1987;2006;2007 | No | 0 | Terminal Station | Yes | Yes | No | No | No | No | No | No | No | No | Yes | No | 0 | The site is located on Woomera Road, adjacent to the Murray River, approximately 5km east from the township of Red Cliffs. The site is located within a rural residential setting. West of the site, on the opposite side of Woomera Road is residential. South and east of the site is the Murray River, and north is agricultural. The site is relatively flat and level and the natural surface drainage of the surrounding area is east towards the River, which is the nearest water receptor. | The site is irregular in shape and includes a control room, a workshop with attached hazardous goods storage, and two separate switchyards (22kV Yard and 220kV/66kV Yard) located on either side of the control room. The site has a total area of approximately 7.0 Ha. | TD-0003380 RCTS KGTS 22kV switchgear replacement TD-0003485 RCTS Flood Protection | Electricity Transmission | West | Cameron Wilson | C | [23 empty] | C-I-C
Comms Site | Vine Banks Broadwater (VINE) | TC-VINE |  | 84 Barrys Rd, Broadwater VIC 3301 (enter Rowbottoms Rd) | TBC | -38.1541 | 142.0785 | TBC | TBC | TBC | TBC | Done | Yes / Yes | 2020-09-29 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 2 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 1 |  |  |  | 4 | 2 | C | E | No |  |  | #REF! | [13 empty] | 2 | 2 | 1 | 3 | 2 | 2 | 5 | 2 | 3.5 | 4 | 4 Unlikely: C | N/A |  | 2x1982; 4x1983; 4x2007; 2x2010; 2x2014 | Significant soil removed and some level of remediation completed before bunding upgrade as part of station rebuild the transformers have been fully bunded since installed. | Check | Terminal Station | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | 0 | Not included | 0 | 0 | Electricity Transmission | Central | Andrew Ryan | TBC | [23 empty] | C-I-C
City Gate | Wallace City Gate | WALL |  | Wescotts Rd, Wallace VIC 3352 | None | -37.5646 | 144.0499 | TBC | TBC | TBC | TBC | Done | Yes / Yes | 2020-11-18 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 3 | 4 | 5 | 5 | 4 | 2 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 3 |  |  |  | 1 | 2 | B | E | No |  |  | #REF! | [13 empty] | 7 | 2 | 2 | 3 | 2 | 2 | 4 | 2 | 3 | 3 | 3 Rare: D | N/A |  | 1984; 2x2007; 2009; 2012; 2013; 2018 | Significant soil removed and some level of remediation completed before bunding upgrade as part of station rebuild the transformers have been fully bunded since installed. | 29/01/2014 - The number 3 transformer at Ringwood North ZS failed and starting leaking oil. The amount of oil was so much that it escaped the bunding area and spilled into the ground and into two drain pits in the back corner of the yard. 26/05/2014 - Oil separator at RWTS in 66KV yard near cap bank has a considerable amount of contaminate in it , needs to be cleaned out. | Terminal Station | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Transmission | Central | Andrew Ryan | D | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Wangaratta Depot | TBC - WANGR DEPOT |  | 2 Gibson St, Wangaratta, Victoria 3676 | 1\PS404357 | -36.3624 | 146.2968 | AusNet Services Electricity Services Pty Ltd | Downer | Freehold | Active | UPLOAD 20/03 | Yes / Yes | 2021-02-18 | J Smith | Yes | [6 empty] | GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002) |  | 2 | [5 empty] | Low | 3 | Several used transformers on-site | Various | 2 | 2 | 5 | 5 | 3 | 3 |  | Bunding present | 5 | None | Oil Default | None | None | <100 L | None | Yes - LPG | None | None |  |  |  |  | No | [6 empty] | 3 | 3 | [5 empty] | 3 | B | D | Yes |  |  | #REF! | [11 empty] | GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002) |  | 5 | 3 | 2 | 1 | 3 | 3 | 5 | 1 | 3 | 3 | 3 Unlikely: D | N/A |  | 1969;1971; 2001; 2x2019 | No | 0 | Terminal Station | Yes | Yes | No | Yes | No | No | No | No | No | Yes | Yes | No | 0 |  |  |  | Electricity Transmission | North | Cameron Wilson | D | [23 empty] | C-I-C
Sub Station | Wangaratta ZSS (WN) | DS-WNX | North | 64 Vincent Road/Greta Road, Wangaratta, Victoria 3677 | 1\TP760453 | -36.3647 | 146.3145 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-07-14 | CJ Wilson | Yes | [5 empty] | Jacobs 2021 |  |  | 2 | 36 | [5 empty] | 3 | Oil containing equipment, batteries & SF6 | 2 | 2 | 4 | 5 | 5 | 3 | 3 |  | Brick bund with gravel floor | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 5 |  |  |  | 2 | 3 | B | D | Yes | Hydrocarbons above management limits, no HIL D exceedences |  | No | No exceedences of HIL D |  |  | PSI and soil classification prior to commencement. Remediation and validation to be undertaken as part of site upgrades. | Yes | Stage 3 - due 2020-2023 |  |  |  |  | Jacobs 2021 |  |  | 34 | 3 | 2 | 1 | 3 | 3 | 4 | 2 | 3 | 3 | 3 Unlikely: D | N/A | Generator has been decommissioned and is awaiting removal | 1960s;1982; 2009;2017;2018 | Significant soil removed and some level of remediation completed before bunding upgrade as part of station rebuild the transformers have been fully bunded since installed. New transformers are complete and in good condition, older transformers are fully bunded however have considerable leaks being address | N/A | Station rebuild - WaterlecNew F2 trans 330kV switchyard duplication Terminal Station | Yes | Yes | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | 0 | Not included | Not included | TD-0003439 SMTS H2 Transformer Replacement Stage 1 | Electricity Transmission | Central | Andrew Ryan | D | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Warragul Depot | WH-0021 |  | 194 Sutton Street (cnr Normanby Street), Warragul, Victoria 3820 | 1\TP127619 | -38.1537 | 145.9425 | AusNet Services Transmission Group Pty Ltd | Downer | Freehold | Active | MT - Downer | Yes / Yes | 2021-02-17 | Daniel Wood | Yes | [8 empty] | 2 | [6 empty] | 3 | Oil containing equipment | 1 | 1 | 1 | 3 | 3 | 1 | 3 |  | Fully compliant sealed bund basic oil/water separator - no shut off valve | 3 | None | Oil Default | None | None | Default Chemicals | Yes - Small Volume | Yes - LPG | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 4 |  |  |  | 4 | 4 | A | C | Yes |  |  | #REF! | [13 empty] | 6 | 3 | 2 | 1 | 3 | 3 | 2 | 2 | 2 | 2 | 2 Unlikely: D | N/A |  | 3x1967; 1969; 2003; 2010 | Old transformers pre-bunding upgrades. Soil removed and some level of remediation completed before bunding upgrade , current project will see further soil remediation and replacement of transformers and their enclosures | N/A | Station rebuild - CCP Terminal Station | Yes | Yes | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | 0 | The site is located on Dandenong Road, Springvale, within a light industrial setting, 1 km from residential areas. The site is relatively flat and level, with the surface drainage of the site likely to be to the east. The nearest water receptor is Mile Creek, which runs along the eastern boundary of the site. The site is a rectangular and has a total area of approximately 8 Ha. The site has operated as a Terminal Station for approximately 40 years. | N/A | TD-0003415 SVTS Redevelopment Project. The project scope included replacement of the exisiting three transformers and refurbishment of one transformer. https://spausnet.sharepoint.com/CommsCentre/NewsCentre/Pages/Value-Engineering-driving-efficiencies-at-Springvale-Terminal-Station.aspx | Electricity Transmission | Central | Andrew Ryan | D | [23 empty] | C-I-C
Sub Station | Warragul ZSS (WGL) | DS-WGL | East | 192 Normanby Street, Warragul, Victoria, 3820 | 1\LP70180 & 1\TP247913 | -38.1537 | 145.9426 | TBC | TBC | Freehold | Active | Uploaded 16/03 | Yes / Yes | 2020-12-31 | M Snell | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 10 | [5 empty] | 3 | Oil containing equipment and batteries | Check | 4 | 4 | 5 | 5 | 5 | 2 |  | Brick bund with gravel floor | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 4 |  |  |  | 4 | 3 | B | C | Yes | Potential contaminating activities. |  | #REF! |  |  |  | PSI with limited soil sampling program. | Yes | Stage 2 - due 2018 |  |  |  | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 2 | 2 | 2 | 3 | 2 | 2 | 4 | 2 | 3 | 3 | 3 Unlikely: D | N/A | Generator remains on site but has been decommissioned and is awaiting removal | 2x1982 | Significant soil removed and some level of remediation completed before bunding upgrade as part of station rebuild the transformers have been fully bunded since installed CHECK AS NO BUNDING? | 0 | Terminal Station | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 | The Sydenham Terminal Station is located on Victoria Road, Sydenham, within a rural setting. The site is surrounded by grazing property. Calder Park racetrack is located approximately 500 metres to the north east on the opposite side of the nearby Bendigo train line. The nearest residential area is Hillside approximately 700 metres to the south, on the opposite side of a ridge. The natural surface slopes to the northeast, and the Terminal Station site has been cut into the slope to form a level platform. Natural surface drainage is to the northeast | The site is approximately rectangular and contains a Control Room, a maintenance building a generator room and a microwave tower and building. The site has a total area of approximately 22.5 Ha. | TD-0008033 500kv GIS Replacement? In progress? | Electricity Transmission | Central | Andrew Ryan | B | [23 empty] | C-I-C
Ex Gas Works Site | Warrnambool Ex Gas Works Site | TBC - WRNL GAS |  | Wellington Street, Warrnambool, Victoria 3280 | 1\TP100515 | -38.3842 | 142.4699 | TBC | TBC | Freehold | ACTIVE | 2020-04-06 | No assessment needed |  |  | Yes | Yes |  |  |  |  | EES - Draft Remediation Action Plan: Warrnambool (2004), Jacobs - Preliminary Conceptual Site Model (pCSM) (2021), Jacobs - Contamination Management Plan (CMP) (2021), Jacobs - Gfactuakl Report: Groundwater Monitoring Event March 2021 (2021) |  |  | 3 |  |  | 5 |  | Former landfill |  |  |  | Check | 3 | 4 | 5 | 5 | 4 | 3 |  |  | 5 | None | Oil Default | [8 empty] | Putrescible |  |  | No |  | None | HIL/HSL Exceedances |  |  |  | 4 | 4 | 5 |  |  |  |  | 4 | C | A | Yes | Confirmed contaminated soil and groundwater | Refer to Gasworks Team | #REF! | Known contamination (former Gasworks), landfill |  |  | DSI | [6 empty] | EES - Draft Remediation Action Plan: Warrnambool (2004), Jacobs - Preliminary Conceptual Site Model (pCSM) (2021), Jacobs - Contamination Management Plan (CMP) (2021), Jacobs - Gfactuakl Report: Groundwater Monitoring Event March 2021 (2021) |  |  | 5 | 3 | 2 | 2 | 3 | 3 | 4 | 2 | 3 | 3 | 3 Unlikely: D | N/A |  | 4x1985; 2013 | No | 0 | Terminal Station | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Transmission | Central | Andrew Ryan | D | [23 empty] | C-I-C
Sub Station | Watsonia ZSS (WT) | DS-WTX | Central | 67 Frensham Road, Watsonia, Victoria, 3087 (100m south of Elder Street) | 94\LP84037 | -37.7131 | 145.0857 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-06-05 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP |  |  | BSE- Water Quality Investigation Program, Phase 3 of Works for High-Risk Sites; Watsonia Zone Substation (2024) |  | 2024-01-01 | 5 | 11 | [5 empty] | 4 | Oil containing equipment, batteries, chemicals & SF6, Staining was noted within all three transformer bunds on Site, with heavy staining observed within transformer bunds 1 and 2. It was noted that transformers 1 and 2 were constructed with brick bunding and gravel bases. Cracks and gaps were noted within the bund walls. (2024) | 4 | 5 | 4 | 3 | 4 | 5 | 5 |  | Brick bund with gravel floor and basic oil/water separator - no shut off valve | 5 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Small Volume | None | None | None |  |  |  |  | No | [6 empty] | 3 | 4 | 5 | Yes | 4 | No | 2 | 4 | A | D | Yes | Potential contaminating activities. |  | #REF! | NA |  | Y | PSI with limited soil sampling program. | Yes | Stage 3 - due 2020-2023 |  |  |  | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 3 | 5 | 4 | 5 | 5 | 5 | 4 | 2 | 3 | 3 | 3 Unlikely: D | N/A |  | 4x1965;1966;1968; 1984 | Significant soil removed and some level of remediation completed before bunding upgrade as part of station rebuild the transformers have been fully bunded since installed. | 0 | Terminal Station | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | 0 |  |  |  | Electricity Transmission | Central | Andrew Ryan | D | [23 empty] | C-I-C
Comms Site | Waubra Passive Repeater Facitity | TBC TC-Waubra |  | 230 TROYS ROAD, WAUBRA, VICTORIA 3352 | 1\TP79226 | -37.3578 | 143.604 | TBC | TBC | Leased | Active | On Waubra TS (A Ryan) | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 |  | 2 | 5 | 4 | 5 | 5 | 5 | 3 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | B | D | No |  |  | #REF! | [13 empty] | 8 | 3 | 1 | 1 | 3 | 3 | 5 | 2 | 3.5 | 4 | 4 Unlikely: C | N/A |  | 1967; 1999; 2007;2009; 2x2010; 2013; 2018 | No | 0 | Terminal Station | Yes | Yes | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Transmission | Central | Andrew Ryan | C | [23 empty] | C-I-C
Terminal Station | Waubra TS (WBTS) | TS-WBTS | West | Troys Road, Waubra VIC 3352 | 1\PS609794 | -37.356 | 143.6058 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-08-26 | CJ Wilson | Yes | [8 empty] | 2 | 12 | [5 empty] | 4 |  | 34 | 3 | 1 | 1 | 1 | 2 | 2 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | None | Large | Yes | None | None | Yes - Small Volume |  | Spoil / Waste | [5 empty] | No | [6 empty] | 3 | 2 | 1 | Yes |  |  | 2 | 3 | B | D | Yes |  |  | #REF! |  | Y | Y | [10 empty] | 3 | 2 | 1 | 1 | 2 | 2 | 1 | 2 | 1.5 | 2 | 2 Rare: E | 0 |  | 2008, 2x2009 | No | 0 | Terminal Station | Yes | Yes | No | Yes | No | No | No | Yes | No | No | Yes | No | 0 | Not included in the report | 0 | 0 | Electricity Transmission | West | TBC | TBC | C4 | Enviro - one above ground system, stormwater isolation valves fitted, found all pits from bunds to holding tank are not sealed so a blockage would see ground leaks need gatic style lids to be fitted | Y | Confidence 2/5. No enviro reports available. | Risk driven by lack of information, presence of potentially contaminating activities, consequence of contamination. One site inspection from 2020 available. 34 items of oil filled equipment on site. Hardstand, bunded. Generators with self containing bunds. Stockpiles recorded in PRA. | 1. Complete site inspection to confirm environmental status. 2. Review drains and structure of pond to confirm if is lined, contains contaminated water etc. 3. Service and repair leaking transformers. 4. Clean bunds 5. Check bund integrity. 6. Repairs required per cell DZ252. |  | C-I-C | C-I-C | x | [13 empty] | C-I-C
Terminal Station | Wemen TS (WETS) | TS-WETS | West | Hattah-Robinvale Rd, Wemen VIC 3549 | None | -34.7869 | 142.525 | TBC | TBC | Leased | Active | 2020-07-30 | Yes / Yes | 2020-07-30 | CJ Wilson | Yes | [8 empty] | 2 | 3 | [5 empty] | 4 |  | 6 | 3 | 1 | 2 | 2 | 2 | 1 |  | Fully compliant sealed bund with basic oil/water separator + shut off valve or triple interceptor tank - no shut off valve | 3 | None | Large | Yes | None | None |  |  | Greenfields build | [5 empty] | No | [6 empty] | 3 | 2 | 3 | Yes |  |  | 1 | 3 | B | D | Yes |  |  | #REF! |  |  | Y | [10 empty] | 3 | 1 | 1 | 2 | 1 | 1 | 3 | 1 | 2 | 2 | 2 Rare: E | N/A |  | 2x2011;2018 | No | 0 | Terminal Station | Yes | Yes | No | No | No | No | No | No | No | No | Yes | No | 0 | 0 | 0 | 0 | Electricity Transmission | West | Cameron Wilson | E | C1 | Enviro - one above ground system, stormwater isolation valves fitted, | Y | Confidence 2/5. No environmental reports available. | Status of oil leaks and proximity to environmental receptors driving risk rating. In 2020 there was an overflow of an oil separation pit where 100-200 L had to be cleaned up. Fully compliant sealed bund with basic oil/water separator + triple interceptor tank. No shut off valve noted in PRA but present in cell DZ253. | 1. Complete site inspection to confirm environmental status. 2. Service and repair leaking transformers. 3. Verify cleanup of 2020 overflow. 4. Clean bunds 5. Check bund integrity |  | C-I-C | C-I-C | x | [13 empty] | C-I-C
City Gate | Werribee (Lock Ave) City Gate | LOCK |  | 85 Lock Avenue, Werribee, Victoria 3030 | PC360468 | -37.9164 | 144.6637 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-19 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 4 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 2 |  |  |  | 1 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4.5 | 5 | 5 Unlikely: B | N/A | No complaints however planning permit required a visual screen to be built to minimise visual impact of the site | 2x1964; 1965; 2001; 2009x2; 2010; 2018;2019 | Considerable soil remediation was carried out during rebuild and new transformers with fully compliant bunds installed | Check | Terminal Station | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | Yes | No | 0 | Not included | 0 | 0 | Electricity Transmission | Central | TBC | TBC | [23 empty] | C-I-C
City Gate | Werribee (Old Sneydes Rd) City Gate | OLDS |  | Old Sneydes Road, Werribee, 3030 | None | -37.886 | 144.7011 | TBC | TBC | FREEHOLD | ACTIVE | Done | Yes / Yes | 2020-11-19 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 9 | 2 | 4 | 5 | 5 | 3 | 3 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 5 |  |  |  | 1 | 3 | B | D | Yes |  |  | #REF! | [13 empty] | 5 | 3 | 1 | 1 | 3 | 3 | 2 | 2 | 2 | 2 | 2 Unlikely: D | N/A |  | 4x1986; 1987 | No | Check | TS + Refcl | Yes | Yes | No | No | No | No | No | Yes | No | No | Yes | No | 0 | The site is located on the corner of Baranduda Drive and Whytes Road, Wodonga, within a rural setting. The Terminal Station (“the site”) and the surrounding area is flat and the natural surface drainage of the surrounding area is generally to the north west. Stormwater from the site drains to the nearby Middle Creek, approximately 120m to the northwest. The nearest residences are at Baranduda, approximately 1.5 km to the southeast. | The site is approximately square and contains a control and maintenance building and a Diesel Generator Room. The switchyard has two sections separated into 330kV and 66kV yards. The entire switchyard section of the site is separately fenced from the remainder of the site. The area outside the perimeter of the switchyard, but still within the site boundary, is utilised for stock grazing purposes. The site has an area of approximately 13.6 Ha. | 0 | Electricity Transmission | North | TBC | TBC | [23 empty] | C-I-C
Terminal Station | West Melbourne TS (WMTS) | TS-WMTS | Central | 297-307 Arden Street, Kensington, Victoria 3031 | 1\TP18018 | -37.8003 | 144.9336 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-08-04 | A Ryan | Yes | Yes |  |  |  |  | Water Quality Investigation Program-BSE(2022) | SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) | 2022-09-01 | 3 | 12 | Minor spill from circuit breaker in 2018. Oil leak from trailored tanked in 2021 |  |  |  |  | 5 |  | 5 | 3 | 3 | 1 | 3 | 3 | 3 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | Yes - Large Volume | Yes - LPG | Spoil / Waste | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 4 | 5 | Yes |  |  | 4 | 4 | B | C | Yes |  |  | #REF! |  | Y | Y | [8 empty] | SKM - Groundwater Assessment (2001). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 7 | 3 | 1 | 1 | 3 | 3 | 1 | 1 | 1 | 1 | 1 Unlikely: E | N/A |  | 1957;3x1962;1984; 2x2004 | No | 0 | Terminal Station | Yes | Yes | No | No | No | No | No | No | No | No | Yes | No | 0 | 0 | 0 | 0 | Electricity Transmission | West | Cameron Wilson | E | C1 | Enviro - one above ground system, stormwater isolation valves fitted | N | Confidence 3/5. BlueSphere 2022 WQIP report. | Risk driven by oil leak rating 3/5, presence of potentially contaminating activities, consequence of contamination. Puraceptor on site. Brick bund with gravel floor, oil observed on bund surfaces in 2020. The status of stockpiled soil in 2020 is unclear. Review of BSE 2022 WQIP report shows that water in the TIT, which has been treated by the puraceptor is still very high. Leakages of oil in approx. 50% of equipment. | 1. Replace brick and gravel bunds with hardstand. 2. Service and repair leaking equipment. 3. Install GAC scrubber to end of puraceptor system 4. Confirm the status of the stockpiles of soil on site as indicated in the PRA. Apply erosion controls, confirm origin of materials. 5. Bund integrity check 6. Clean bunds. |  | C-I-C | C-I-C | x |  | C-I-C |  | C-I-C | [9 empty] | C-I-C
City Gate | Winchelsea City Gate | WINC |  | 50 MCCONACHY LANE, Winchelsea, 3241 |  | -38.2317 | 143.9621 | TBC | TBC | TBC | Active | 2021-05-26 | Yes / Yes | 2021-05-26 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | Check | 2 | 4 | 5 | 5 | 3 | 3 |  |  | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | [5 empty] | 2 | B | E | No |  |  | #REF! | [13 empty] | 31 | 3 | 1 | 1 | 3 | 3 | 2 | 2 | 2 | 2 | 2 Unlikely: D | N/A | Noise complaints: No, however earth mounds were installed to minimise the visual and sound impacts outside the station | 1964; 15x1970 (7ss); 9x1971 (3ss); 2001; 2010; 2x2012 (1ss); 2013;2018 | Significant soil removed and some level of remediation completed before bunding upgrade as part of station rebuild the transformers have been fully bunded since installed. | 0 | Terminal Station | Yes | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 0 | The site is located on Dodds Road, Keilor, near the intersection of Western Ring Road and Keilor Park Drive. The site is located within a recreational setting, being adjacent to Brimbank Park and the Horseshoe Bend Farm (operated by Parks Victoria). South east of the site is the Western Ring Road, separated from the site by a walking and cycling track. South of the site is undeveloped. The site is relatively flat and level, however the natural surface drainage of the surrounding area is to the south-west. The nearest residential area is Keilor East, which is approximately 400 metres east, on the opposite side of the Western Ring Road. The nearest water receptor is the Maribyrnong River approximately 500 metres to the south west. | The site is approximately “coffin” shaped and has a total area of approximately 25.0 Ha. Buildings at the site include a control room, a relay house, and old control room, a compressor house and maintenance sheds. | 0 | Electricity Transmission | Central | Andrew Ryan | D | [23 empty] | C-I-C
Sub Station | Wodonga 22KV ZSS (WOTS 22) | DS-WOTS | North | 4611 Baranduda Drive (Whytes Road), Baranduda, Victoria 3691 | None | -36.1565 | 146.9513 | TBC | TBC | Leased | Expired | Done | Yes / Yes | 2020-07-15 | CJ Wilson | Yes | [8 empty] | 2 | [6 empty] | 3 | HOW DOES A ZSS HAVE NO TR? KIOSK ONLY? Batteries and stockpiles | 1 | 4 | 4 | 5 | 5 | 5 | 5 |  | Batteries in dedicated room | 5 | None | None | Yes | None | None | None | None | Spoil / Waste | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 2 |  |  |  | 1 | 3 | B | D | Yes |  |  | #REF! |  | Y | [11 empty] | 2 | 5 | 4 | 5 | 5 | 5 | 5 | 4 | 4.5 | 5 | 5 Unlikely: B | N/A | No complaints however planning permit required a visual screen to be built to minimise visual impact of the site | 1968; 2005; 4x2013; 2x2017; 2x2018 | Considerable soil remediation was carried out during rebuild and new transformers with fully compliant bunds installed | Check | Terminal Station | Yes | Yes | No | No | No | Yes | No | No | Yes | Yes | Yes | Yes | 0 | The site is located on Mary Street, Richmond, adjacent to the Yarra River, within an industrial/ residential setting. The 66 kV yard also fronts onto Barkly Street. The site consists of two separate areas, linked by a narrow access road. The northern area is occupied by the 66kV yard. The southern area is the 220 kV yard and the transformer banks. The site has a total area of approximately 2.2 Ha. West and north of the site are residential properties. East is a Melbourne Water depot and south is the Yarra River, which is the nearest water receptor. The site is adjacent to the exit of Citilink’s Burnley tunnel. The exhaust tower for the tunnel is immediately north of the site, on the opposite side of Barkly Avenue. | The site is relatively flat and level. Part of the site has been built on an elevated platform, which extends over the Melbourne Water depot, to the east. Natural surface water drainage is east towards the Yarra River. | 0 | Electricity Transmission | Central | Andrew Ryan | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Wodonga Depot | WH-0022 |  | 24 Moloney Drive, Wodonga, Victoria 3690 | 21\LP133155 | -36.104 | 146.8534 | Downer | Downer | Leased | Active | Sharepoint updated. Downer received lease - don't do | No assessment needed |  |  | N/A | [8 empty] | 1 |  | Containment area filled with damaged and leaking transformers after storm event in 2019 |  |  |  |  | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | [12 empty] | Yes | [6 empty] | 2 | 2 | [5 empty] | 2 | C | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Terminal Station | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | Electricity Transmission | Central | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Wodonga TS (WOTS) | TS-WOTS | North | 4611 Baranduda (Whytes Road) Drive, Baranduda, Victoria 3691 | 2\PS406394 | -36.1565 | 146.9513 | AusNet Services | Zinfra | Freehold | Active | Done | Yes / Yes | 2020-08-13 | CJ Wilson | Yes | Yes | [5 empty] | GHD - Groundwater Monitoring (2005). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 3 | 35 |  |  |  |  | High | 5 | Oil containing equipment, fuel storage, generators, batteries & SF6/gas cylinders | 5 | 3 | 1 | 1 | 1 | 2 | 1 |  | Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 3 | <10 kg or <50 mg/kg | Large | Yes | Fuel Default | None | Yes - Small Volume | Yes - LPG | Greenfields build | Yes - Septic |  |  |  |  | No | [6 empty] | 4 | 4 | 2 | Yes |  |  | 2 | 4 | A | C | Yes |  |  | #REF! |  |  | Y | [8 empty] | GHD - Groundwater Monitoring (2005). SKM - Groundwater Assessment (2001). GeoEng - Environmental Risk Audit for Bunding and Stormwater System Compliance (2002). GHD - Environmental Inspections, Maintenance and Tests (2003) |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Terminal Station | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | Electricity Transmission | West | TBC | TBC | C1 | Enviro - one above ground system, stormwater isolation valves fitted. | Y | Confidence 3/5. Environmental report from 2005. | Risk driven by oil leak rating 3/5. No environmental report since 2005. Presence of potentially contaminating activities, proximity to environmental receptors. In 2023, oil staining observed on gravel surface outside of bunds. The site inspection on environmental register says there is no oil filled equipment on site, however AusNet know this to be the case from 2023 observations. Brick wall bund. Fully compliant sealed bund with puraceptor oil/water separator + shut off valve | 1. Replace brick bund walls with concrete/hardstand. 2. Service and repair leaking transformers. 3. Clean bund surfaces. 4. Check integrity of bund floors. 5. Clean up areas of oil staining on hardstand outside of bunds. 6. Complete site inspection to confirm environmental status. |  | C-I-C | C-I-C | x |  |  |  | C-I-C | [9 empty] | C-I-C
Sub Station | Wodonga ZSS (WO) | DS-WOX | North | 74-80 Elgin Boulevard/Watson St, Wodonga, Victoria 3690 | 1\TP237763 | -36.1187 | 146.8808 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-07-14 | CJ Wilson | Yes | [5 empty] | Jacobs 2021 |  |  | 2 | 25 | [5 empty] | 3 | Oil containing equipment, batteries and SF6 | 3 | 3 | 4 | 5 | 5 | 4 | 1 |  | Brick bund with gravel floor and some administrative controls | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 5 |  |  |  | 2 | 3 | C | D | Yes | Hydrocarbons above management limits, no HIL D exceedences |  | No | No exceedences of HIL D |  |  | PSI and soil classification prior to commencement. Remediation and validation to be undertaken as part of site upgrades. | Yes | Stage 3 - due 2020-2023 |  |  |  |  | Jacobs 2021 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Terminal Station | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | Electricity Transmission | West | TBC | TBC | [23 empty] | C-I-C
Sub Station | Wollert ZSS (WLT) | TBC TS-WLT | Central | 87-95 Harvest Home Road, Wollert VIC 3750 | 5\LP77013 | -37.6234 | 145.0326 | TBC | TBC | Freehold | Active | Future vacant site. Add comment | No assessment needed |  |  | N/A | [8 empty] | 1 | [6 empty] | 2 | Future vacant site | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | Oil Default | [11 empty] | Yes | [6 empty] | 3 | 2 | [5 empty] | 3 | D | D | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 2 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Terminal Station | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | Electricity Transmission | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Wonthaggi Desalination Plant TS (WDP) | TBC WDP | East | Lower Powlett Rd, Dalyston VIC 3992 | None | -38.5854 | 145.5253 | Government | AusNet Services | TBC | TBC | UPLOAD 20/03 - in Marks directory | Yes / Yes | 2020-12-14 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 5 | Oil containing equipment, SF6/gas cylinders and batteries | 1 | 1 | 1 | 2 | 2 | 1 | 1 |  | Fully compliant sealed bund, oil/water separator and shut off valve | 2 | None | Large | Yes | None | None | Yes - Small Volume | Yes - LPG | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | [5 empty] | 3 | B | D | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Terminal Station | Yes | Yes | No | No | No | No | No | No | N/A | No | Yes | #N/A | #N/A |  |  |  | Electricity Transmission | West | TBC | TBC | N/A | Not in this list. | Y | Confidence 2/5. No environmental reports available. | Risk driven by lack of information, presence of potentially contaminating activities, consequence of contamination. No environmental reports available. One site inspection from 2020 available. No reports of contamination issues. No photos of the oil filled equipment. | 1. Completion of site inspection to confirm environmental status. | [17 empty] | C-I-C
Sub Station | Wonthaggi ZSS (WGI) | DS-WGI | East | Korumburra Road/Wonthaggi Road, Wonthaggi, Victoria 3995 | 1\TP379102 | -38.5938 | 145.6098 | TBC | TBC | Freehold | Active | Uploaded 16/03 | Yes / Yes | 2021-02-10 | M Snell | Yes | [8 empty] | 2 | 45 | [5 empty] | 3 | Oil containing equipment and batteries | 1 | 5 | 1 | 5 | 5 | 5 | 1 |  | Fully compliant sealed bund | 5 | <10 kg or <50 mg/kg | Large | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 3 | 2 | 5 |  |  |  | 2 | 3 | C | D | Yes |  |  | #REF! |  |  |  |  | Yes | Stage 1 - due 2017 | [7 empty] | 0 | 1 | 3 | 4 | 1 | 1 | 0 | 0 | 0 | 0 |  | 0 |  | N/A | No | 0 | Terminal Station | Yes | Yes | No | No | No | No | No | No | No | No | Yes | No | 0 |  |  |  | Electricity Transmission | East | TBC | TBC | [23 empty] | C-I-C
City Gate | Woodend City Gate | WOOD |  | 560 Cobb & Co Rd, Woodend VIC 3442 | None | -37.3183 | 144.5252 | TBC | TBC | TBC | TBC | Done | Yes / Yes | 2021-04-07 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 3 | 1 | 4 | 5 | 5 | 3 | 4 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | None |  |  |  |  | No | [6 empty] | 2 | 2 | 4 |  |  |  |  | 2 | C | D | No |  |  | #REF! | [13 empty] | 2 | 4 | 4 | 3 | 4 | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Terminal Station | Yes | Yes | No | No | No | No | No | No | N/A | No | Yes | No | #N/A |  |  |  | Electricity Transmission | East | TBC | TBC | [23 empty] | C-I-C
Sub Station | Woori Yallock ZSS (WYK) | DS-WYK | Central | 15 Symes Road/Haggards Lane, Woori Yallock, Victoria 3139 | 1\LP133465 | -37.8615 | 144.5991 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-05-25 | A Ryan | Yes |  |  | AusNet, Distribution Sites, Portfolio EMP | [5 empty] | 5 | 39 | [5 empty] | 4 | Oil containing equipment, stockpiles, batteries and chemicals | 2 | 2 | 4 | 2 | 4 | 3 | 1 |  | Brick bund with gravel floor and basic oil/water separator + shut off valve or triple interceptor tank 0 no shut off valve | 4 | <10 kg or <50 mg/kg | Large | Yes | None | Default Chemicals | None | None | None | None |  |  |  |  | No | [6 empty] | 4 | 4 | 5 | No | 5 | No | 3 | 4 | C | C | Yes | Potential contaminating activities. |  | #REF! |  |  |  | PSI with limited soil sampling program. | [5 empty] | AusNet, Distribution Sites, Portfolio EMP |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Terminal Station | Yes | Yes | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | #N/A |  |  |  | Electricity Transmission | West | TBC | TBC | [23 empty] | C-I-C
City Gate | Wyndham Vale City Gate | WYND |  | 772 Ballan Rd, Wynham Vale VIC 3024 | B\PS722379 | -37.8615 | 144.5991 | TBC | TBC | Leased | Active | Done | Yes / Yes | 2021-01-12 | Tony W. | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 1 - service | 1 | 4 | 5 | 5 | 3 | 1 |  | Routine inspections and reporting | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 5 |  |  |  | 1 | 3 | D | D | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 4 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Terminal Station | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | Electricity Transmission | East | TBC | TBC | [23 empty] | C-I-C
Sub Station | Yallourn Power Station ZSS (YPS) | DS-YPS | East | Yallourn Drive, Yallourn, Victoria, 3825 | 2004\PP3273 & 50W~A\PP3273 | -38.1736 | 146.3488 | TBC | TBC | Freehold | Active | UPLOAD 20/03 | Yes / Yes | 18-19/01/2021 | M Snell | Yes | Yes |  | AusNet, Distribution Sites, Portfolio EMP |  |  |  | SKM - Groundwater Assessment (2001). Monarc - Waste Material Assessment (2015). |  | 5 | 6 |  | 4 |  | Potential contaminated fill material placed in easement and known issues. Likely contamination issues on-site |  | 5 | Varied, oil containing equipment, fuel and batteries | 2 | 4 | 3 | 3 | 3 | 4 | 4 |  | Some portions with full fully compliant sealed bunds with oil/water separators and shut off valves | 4 | <10 kg or <50 mg/kg | Large | Yes | None | None | Yes - Small Volume | None | Spoil / Waste | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | [5 empty] | 3 | C | D | Yes | Potential contaminating activities. |  | #REF! |  | Y |  | PSI with limited soil sampling program. Sample stockpiles if present. |  |  | Yes | Rebuild due 2017-2024 |  | AusNet, Distribution Sites, Portfolio EMP |  | SKM - Groundwater Assessment (2001). Monarc - Waste Material Assessment (2015). |  | 8 | 4 | 4 | 5 | 4 | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Terminal Station | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | #N/A | Yes | #N/A |  |  |  | Electricity Transmission | West | TBC | TBC | C4 | No assesment yet. | Y | Confidence 5/5. Waste Material Assessment 2015. | Potential contaminated fill material placed in easement and known issues. Likely contamination issues on-site. Risk driven by oil leak rating, presence of oil filled equipment, varied status of bunding. The Yallourn lower yard has leaks in over 50% of equipment. | 1. Service and repair leaking transformers. 2. Clean bunds 3. Check bund integrity, including type of bunds. 4. Replace brick bunds/ gravel hardstand with concrete hardstand bunds. 5. Consider completing surface water testing post puraceptor treatment to ascertain if a GAC scrubber is recommended. |  | C-I-C | C-I-C | x | [13 empty] | C-I-C
Comms Site | Yarragon Comms Site (YGON) | TBC TC-YGON |  | Earls Rd, Yarragon VIC 3823 | \TP511869 | -38.2314 | 146.1182 | TBC | TBC | Freehold | ACTIVE | Done B Scott divest? NEEDS MAINTENANCE | Yes / Yes | 2020-10-15 | M Snell | Yes | [8 empty] | 2 | [6 empty] | 2 |  | 0 | 4 | 4 | 5 | 5 | 5 | 1 |  | 6 or 12 monthly inspection program | 5 | None | None | Yes | None | None | None | None | None | [5 empty] | No | [6 empty] | 2 | 2 | 4 |  |  |  | 4 | 2 | C | E | No |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Terminal Station | Yes | No | No | No | No | No | No | No | Yes | No | Yes | No | #N/A |  |  |  | Electricity Transmission | East | TBC | TBC | [23 empty] | C-I-C
Depot, Office and Warehouse Storage | Yarraville Depot | WH-1008 | Central | 306 Hyde Street, Yarraville, Victoria 3013 | 2\PS401441 | -37.8227 | 144.894 | TBC | TBC | Freehold | Active | UPLOAD 20/03 | Yes / Yes | 2021-02-19 | James Weghorn | Yes |  | WSP (2022) | AusNet, Transmission Sites, Portfolio EMP | 2021 |  | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021) | GHD - Environmental Inspections, Maintenance and Tests (2003) | 2022-12-01 | 5 | 13 | Minor paint spill on roadway in 2018, broken glass bottles and minor oil spill in 2019. Oil spill to ground from bushing in 2021. | 4 | 5 | Contaminated soil in rear paddock (former terminal station) |  | 5 | Large oil collection tank - approx 5,000L | 1 | 1 | 3 | 3 | 3 | 1 | 2 |  | Typical brick bund with 2 oil interceptor systems | 3 | None | Small | Yes | None | Default Chemicals | Yes - Small Volume | Yes - LPG | Contaminated soil - potential risk | None |  | Inert | None |  | No |  |  | HIL/HSL Exceedances |  |  |  | 4 | 4 | 5 | Yes | 1 | Yes | 3 | 4 | B | B | Yes | Former landfill site and contaminated stockpiles |  | Possible | Further data needed before trigger can be confirmed | Stage 1 complete | Y | PSI, including soil and groundwater investigation focussed on landfill. Further stockpile sampling. | [5 empty] | AusNet, Transmission Sites, Portfolio EMP | BlueSphere - Initial Stockpile Assessment Works at Priority Sites (2021) | GHD - Environmental Inspections, Maintenance and Tests (2003) |  | Check | 2 | 1 | 1 | 2 | 2 | 3 | 2 | 2.5 | 3 | 3 Rare: D | N/A | Done. A Ryan also completed. Used CJ Wilson in Enablon. Updated results here on A Ryan version. | #N/A | #N/A | #N/A | Terminal Station | Yes | Yes | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Electricity Transmission | West | TBC | TBC | [23 empty] | C-I-C
Terminal Station | Yarraville Terminal Station (Future TS) | TBC TS-YATS | Central | 308 Hyde Street, Yarraville, Victoria 3013 | 2\PS401441 | -37.8227 | 144.894 | TBC | TBC | Freehold | Active | Future | No assessment needed |  |  | N/A | Yes | [5 empty] | Geo-Eng - Environmental Risk Assessment (1996) |  | 3 | [6 empty] | 2 |  | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  |  | 5 | None | Oil Default | [11 empty] | Yes | [6 empty] | 3 | 2 | [5 empty] | 3 | B | D | Yes |  |  | #REF! | [11 empty] | Geo-Eng - Environmental Risk Assessment (1996) |  | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Terminal Station | Yes | Yes | No | Yes | No | No | No | No | Yes | No | Yes | Yes | #N/A |  |  |  | Electricity Transmission | West | TBC | TBC | N/A | Not in this list. | N | Confidence 3/5. Site has not yet been constructed. | Bunding rating and oil/ water separator shut off valve. | None - as site has not been constructed. | [17 empty] | C-I-C
Sub Station | Yea ZSS (YEA) | DS-YEA | North | 5382 Goulburn Valley Hwy (1.5kms east of Melba Hwy), Yea VIC 3717 | RES1\PS516091 | -37.2115 | 145.4454 | TBC | TBC | Freehold | Active | Done | Yes / Yes | 2020-07-15 | CJ Wilson | Yes | [8 empty] | 2 | 12 | [5 empty] | 2 | HOW DOES A ZSS HAVE NO TR? KIOSK ONLY? Batteries and SF6 | 1 | 1 | 4 | 5 | 5 | 3 | 1 |  | Dedicated battery room with some administrative controls | 5 | None | Small | Yes | None | None | Yes - Small Volume | None | None | Yes - Septic |  |  |  |  | No | [6 empty] | 3 | 3 | 5 |  |  |  | 2 | 3 | D | D | Yes |  |  | #REF! | [13 empty] | 1 | 1 | 1 | 1 | 1 | 1
C-I-C
C-I-C
Note on AX4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: How do we capture leakage of this Reply: Various leakage known
Note on AZ24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Where abouts?
Note on AZ74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Along eastern boundary of the site from road works
Note on AJ95: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual addition based on PSI findings
Note on AT126: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Power station land rather than AusNet
Note on AT131: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Drums
Note on AT143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Drums
Note on AV143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Emtpy????
Note on B178: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Upgrades to happen soonish
Note on AO199: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2023 WSP report: batteries stores in leak proof containers
Note on BD199: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Signed affordavid saying buried asbestos is located at the premises
Note on BI199: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2023 (WSP): Lead in carpark soil/fill
Note on AS200: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PCB concentrations reported in a stockpile sample
Note on AV200: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Former UST
Note on AZ200: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1 stockpile with 9.7 mg/kg PCB's
Note on AJ233: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Updated based on site observations 2022/2023
Note on AT236: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Drums of oil
Note on BD236: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2022-bonded asbestos containing materials and asbestos bundled fibres (non-respirable) in soil within several test pits completed.
Note on BW236: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Updated by DAB 18/11/22 on basis of review.
Note on BD237: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2022-bonded asbestos containing materials and asbestos bundled fibres (non-respirable) in soil within several test pits completed.
Note on AZ266: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Previously identified stockpiles since remove
Note on BM270: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Stockpiles