## Draft Decision
Draft Decision - Powerlink - SERVICE COMPONENT
AER's input data and target calculations:
7.9.1 - Historical performance and proposed floor, caps and targets for the service component of the STPIS
Parameter | Performance Actuals by compliance year |  |  |  |  | Floor (95th Percentile) | Target = Average of performance | Cap (5th Percentile) | REU Distribution
| 2020 | 2021 | 2022 | 2023 | 2024
Unplanned outage circuit event rate (percentage):
Lines event rate – fault | 9.06% | 11.45% | 7.641% | 7.541% | 10.75% | 12.04% | 9.288% | 6.84% | Gamma
Transformer event rate – fault | 11.63% | 11.7% | 14.04% | 10.59% | 14.29% | 15.26% | 12.45% | 9.94% | LogLogistic
Reactive plant event rate – fault | 22.56% | 23.31% | 16.54% | 22.56% | 18.66% | 24.27% | 20.72% | 16.45% | Weibull
Lines event rate – forced | 18.12% | 13.47% | 10.96% | 11.8% | 10.42% | 17.61% | 12.96% | 9.34% | Pearson5
Transformer event rate – forced | 18.6% | 14.62% | 11.11% | 12.94% | 8.333% | 19.31% | 13.12% | 7.98% | Gamma
Reactive plant event rate – forced | 20.3% | 25.56% | 21.8% | 27.07% | 19.4% | 27.91% | 22.83% | 18.18% | Gamma
Loss of supply event frequency (number of events)
Loss of supply events > 0.05 system (x) minutes | 0 | 3 | 2 | 2 | 0 | 3 | 1.4 | 0 | IntUniform
Loss of supply events > 0.40 system (y) minutes | 0 | 1 | 1 | 1 | 0 | 1 | 0.6 | 0 | Bimomial
Average outage duration (minutes)
Average Outage Duration (aggreggate LOS minutes / number of LOS events) | 57.4075 | 44.75 | 611 | 34.2 | 58.3333 | 297.35 | 161.1382 | 13.19 | LogLogistic
Proper operation of equipment (number of events):
Failure of protection system | 21 | 29 | 22 | 20 | 21 | 31 | 22.6 | 15 | Poisson
Material failure of SCADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Can't fit distribution - 5 years of zeros
Incorrect operational isolation of primary or secondary equipment | 9 | 11 | 2 | 2 | 5 | 18 | 5.8 | 0 | Geomet

## @Risk simulation
Powerlink - distributions selected based on mechanical selection of lowest K-S distance statistic, 2020-2024 underlying input data. Calendar year data
| Distribution | KS Distance Statistic | Mean of sample | Mean of fitted distribution | SD of fitted distribution | Cap at 1SD | Cap at 2SD | Collar at 1SD | Collar at 2SD | 5th percentile of fitted distribution | 50th percentile of fitted distribution | 95th percentile of fitted distribution
Lines event rate - fault | Weibull (skew of opp sign to input data) | 0.2421 | 0.0929 | 0.093 | 0.0165 | 0.1095 | 0.126 | 0.0765 | 0.06 | 0.0637 | 0.0943 | 0.1177
| Gamma | 0.2532 | 0.0929 | 0.0929 | 0.0159 | 0.1088 | 0.1247 | 0.077 | 0.0611 | 0.0684 | 0.092 | 0.1204
Transformer event rate - fault | LogLogistic | 0.269 | 0.1245 | 0.1242 | 0.0166 | 0.1408 | 0.1574 | 0.1076 | 0.091 | 0.0994 | 0.1231 | 0.1526
Reactive plant event rate – fault | Weibull | 0.3521 | 0.2072 | 0.2083 | 0.024 | 0.2323 | 0.2563 | 0.1843 | 0.1603 | 0.1645 | 0.211 | 0.2427
Lines event rate - forced | Pearson5 | 0.2364 | 0.1296 | 0.1293 | 0.0257 | 0.155 | 0.1807 | 0.1036 | 0.0779 | 0.0934 | 0.1261 | 0.1761
Transformer event rate - forced | Gamma | 0.1337 | 0.1312 | 0.1312 | 0.0347 | 0.1659 | 0.2006 | 0.0965 | 0.0618 | 0.0798 | 0.1282 | 0.1931
Reactive plant event rate - forced | Gamma | 0.2243 | 0.2283 | 0.2283 | 0.0296 | 0.2579 | 0.2875 | 0.1987 | 0.1691 | 0.1818 | 0.227 | 0.2791
Average outage duration | LogLogistic | 0.3335 | 161.14 | 104.52 | N/A |  |  |  |  | 13.19 | 62.63 | 297.35
Distributions fitted setting: lower limit with fixed bound of zero; unsure upper limit; no change to default "suppress questionable fits" setting
While @Risk allows beta general to be a candidate distribution, we have not included it as a candidate distribution as it uses 4 parameters and we only have 5 data points.
Powerlink - distributions selected based on mechanical selection of lowest AIC, 2020-2024 underlying input data.
| Distribution | AIC | Mean of sample | Mean of fitted distribution | SD of fitted distribution | Cap at 1SD | Cap at 2SD | Collar at 1SD | Collar at 2SD | 5th percentile of fitted distribution | 50th percentile of fitted distribution | 95th percentile of fitted distribution
Number of events > (x) system minutes | Poisson (skew of opposite sign to input data) | 18.9788 | 1.4 | 1.4 | 1.1832 | 2.5832 | 3.7664 | 0.2168 | -0.9664 | 0 | 1 | 4
| Geomet (skew of opposite sign to input data) | 19.634 | 1.4 | 1.4 | 1.833 | 3.233 | 5.066 | -0.433 | -2.266 | 0 | 1 | 5
| IntUniform | 23.8629 | 1.4 | 1.5 | 1.118 | 2.618 | 3.736 | 0.382 | -0.736 | 0 | 1 | 3
Number of events > (y) system minutes | Poisson (skew of opposite sign to input data) | 12.3983 | 0.6 | 0.6 | 0.7746 | 1.3746 | 2.1492 | -0.1746 | -0.9492 | 0 | 0 | 2
| Geomet (skew of opposite sign to input data) | 13.9183 | 0.6 | 0.6 | 0.9798 | 1.5798 | 2.5596 | -0.3798 | -1.3596 | 0 | 0 | 3
| Bimomial | 16.7301 | 0.6 | 0.6 | 0.4899 | 1.0899 | 1.5798 | 0.1101 | -0.3798 | 0 | 1 | 1
Failure of protection system | Poisson | 30.3249 | 22.6 | 22.6 | 4.754 | 27.354 | 32.108 | 17.846 | 13.092 | 15 | 22 | 31
Material failure of SCADA | Can't fit distribution - 5 years of zeros
Incorrect operational isolation of primary or secondary equipment | Geomet | 31.7823 | 5.8 | 5.8 | 6.28 | 12.08 | 18.36 | -0.48 | -6.76 | 0 | 4 | 18