## Current info
Info received from SPA as at 23/3/07
| 2003-08 target | Historical 2002-06 - without aug | Proposed targets (inc capex) - without aug | Adjustment for capex | Historical 2002-06 - with aug | Adjustment for aug | Proposed targets (inc capex & fc aug) - with aug | Adjustment for capex & fc aug | Adjustment for fc aug | Adjustment - Total
Circuit availability
Total | 99.2 | 99.276 | 98.859 | -0.417 | 99.111 | -0.165 | 98.682 | -0.429 | -0.012 | -0.594
Peak critical | 99.9 | 99.734 | 99.55 | -0.184 | 99.619 | -0.115 | 99.283 | -0.336 | -0.152 | -0.451
Peak non-critical | 99.85 | 99.633 | 99.445 | -0.188 | 99.43 | -0.203 | 99.355 | -0.075 | 0.113 | -0.278
Intermediate critical | 99.85 | 99.42 | 98.811 | -0.609 | 99.076 | -0.344 | 98.494 | -0.582 | 0.027 | -0.926
Intemediate non-critical | 99.75 | 99.039 | 98.695 | -0.344 | 98.749 | -0.29 | 98.618 | -0.131 | 0.213 | -0.421
Loss of supply
>0.05 system minutes | 2 | 3.75 | 4 | 0.25 | 3.75 | 0 | 4 | 0.25 | 0 | 0.25
>0.3 system minutes | 1 | 1.25 | 2 | 0.75 | 1.25 | 0 | 2 | 0.75 | 0 | 0.75
Average outage duration
Lines | 10 | 6.589 | 7 | 0.411 | 6.589 | 0 | 7 | 0.411 | 0 | 0.411
Transformers | 10 | 6.871 | 7 | 0.129 | 6.871 | 0 | 7 | 0.129 | 0 | 0.129
Note: historical performance for AOD lines was actually 11.953. SPA have adjusted this figure as if they had a one week cap (proposed) in place for the period, and hence get 6.589.

## Current info updated for 2006
Info received from SPA as at 23/3/07
| 2003-08 target | Historical 2002-06 - without aug | Proposed targets (inc capex) - without aug | Adjustment for capex | Historical 2002-06 - with aug | Adjustment for aug | Proposed targets (inc capex & fc aug) - with aug | Adjustment for capex & fc aug | Adjustment for fc aug | Adjustment - Total
Circuit availability
Total | 99.2 | 99.2754 | 98.8508 | -0.42466 | 99.1479 | -0.1275 | 98.6743 | -0.4736 | -0.048946 | -0.6011
Peak critical | 99.9 | 99.7338 | 99.5507 | -0.18308 | 99.6231 | -0.11077 | 99.2833 | -0.33975 | -0.15667 | -0.45052
Peak non-critical | 99.85 | 99.6322 | 99.4439 | -0.18832 | 99.5605 | -0.071712 | 99.3544 | -0.20615 | -0.017828 | -0.27786
Intermediate critical | 99.85 | 99.4168 | 98.8127 | -0.6041 | 99.172 | -0.24481 | 98.4958 | -0.67625 | -0.072146 | -0.92105
Intemediate non-critical | 99.75 | 99.0802 | 98.7214 | -0.35882 | 99.0462 | -0.034067 | 98.6437 | -0.40248 | -0.043653 | -0.43654
Loss of supply
>0.05 system minutes | 2 | 3.75 | 4 | 0.25 | 3.75 | 0 | 4 | 0.25 | 0 | 0.25
>0.3 system minutes | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 1 | 0 | 1
Average outage duration
Lines | 10 | 6.589 | 7 | 0.411 | 6.589 | 0 | 7 | 0.411 | 0 | 0.411
Transformers | 10 | 6.8707 | 7 | 0.12927 | 6.871 | 0.00026919 | 7 | 0.129 | -0.00026919 | 0.12927
Note: historical performance for AOD lines was actually 11.953. SPA have adjusted this figure as if they had a one week cap (proposed) in place for the period, and hence get 6.589.

## Adjustments to historical data
Adjustments to SPA historical data
Total circuit availability
| 2002 | 2003 | 2004 | 2005 | 2006 | Average 02-06
Total outage hours | 28296.7778 | 38118.3897 | 48919.3003 | 88072.955 | 71163.912 | 54914.267
Forced and fault outages (hrs) | 1507.4997 | 935.1167 | 762.0333 | 782.383 | 3798.682 | 1557.1429
SP AusNet planned asset works outages (hrs) | 6335.0833 | 4211.92 | 8654.364 | 8038.831 | 4060 | 6260.0397
Planned routine maintenance outages (hrs) | 6399.9319 | 6766.68 | 3498.216 | 2943.249 | 5666.932 | 5055.0018
Total outage hours | 14242.515 | 11913.7167 | 12914.6133 | 11764.463 | 13525.614 | 12872.1844
Circuit unavailability (%) | 99.1911 | 99.3234 | 99.2665 | 99.3319 | 99.2318 | 99.2689
Circuit availability (%) - historical performance | 99.1911 | 99.3234 | 99.2665 | 99.3319 | 99.2318 | 99.2689
VENCorp requested augmentation outages (hrs) | 3495.5492 | 294.3 | 398.6497 | 1259.3997 | 1618.3831 | 1413.2563
Customer requested planned augmentation outages (hrs) | 18.5167 | 29.3 | 210.8333 | 904.3497 | 13.45 | 235.2899
Other planned third party outages (hrs) | 1888.9342 | 32.4 | 23.5169 | 807.2506 | 319.1669 | 614.2537
Adjusted total outage hours | 19645.515 | 12269.7167 | 13547.6133 | 14735.463 | 15476.614 | 15134.9844
Circuit unavailability (%) | 98.8843 | 99.3032 | 99.2306 | 99.1631 | 99.121 | 99.1404
Circuit availability (%) - Adj historical performance | 98.8843 | 99.3032 | 99.2306 | 99.1631 | 99.121 | 99.1404
Adjustment to historical data | 0.30686 | 0.020219 | 0.03595 | 0.16873 | 0.1108 | 0.12851

## Forecast data by measure
Forecast capex and augmentation outages
Forecast
| Average 02-06 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | Average 08-13
SP AusNet planned capex outages
Total circuit | 6260.0397 | 16165.6884 | 13440.7773 | 19774.103 | 16605.3391 | 13621.3897 | 5153 | 14126.7162
Peak critical | 159.5946 | 550.0675 | 473.7911 | 532.8841 | 360.7315 | 472.3756 | 133.32 | 420.5283
Peak non-critical | 63.1972 | 96.56 | 63.84 | 258.08 | 303.4821 | 72.48 | 72.8 | 144.5403
Intermediate critical | 438.7733 | 1787.7195 | 1539.821 | 1731.8734 | 1172.3773 | 1535.2207 | 433.29 | 1366.717
Intermediate non-critical | 272.6466 | 313.82 | 207.48 | 838.76 | 986.3168 | 235.56 | 236.6 | 469.7561
Customer requested planned augmentation outages
Total circuit | 849.5437 | 3336 | 816 | 2136 | 1296 | 1104 | 864 | 1592
Peak critical | 70.8266 | 367.0014 | 89.7701 | 234.9865 | 142.5761 | 121.4537 | 95.0507 | 175.1398
Peak non-critical | 35.4 | 49.317 | 12.0632 | 31.5771 | 19.1591 | 16.3207 | 12.7728 | 23.535
Intermediate critical | 95.1799 | 483.2813 | 118.2127 | 309.4391 | 187.7496 | 159.9348 | 125.1664 | 230.6307
Intermediate non-critical | 3.92 | 47.5633 | 11.6342 | 30.4542 | 18.4778 | 15.7404 | 12.3186 | 22.6981
VENCorp requested augmentation outages
Total circuit | 1413.2563 | 552 | 1152 | 2088 | 672 | 3504 | 1584 | 1592
Peak critical | 68.1734 | 60.7269 | 126.7343 | 229.7059 | 73.9283 | 385.4835 | 174.2597 | 175.1398
Peak non-critical | 2.2 | 8.1604 | 17.0303 | 30.8675 | 9.9344 | 51.8006 | 23.4167 | 23.535
Intermediate critical | 252.0201 | 79.9674 | 166.8885 | 302.4854 | 97.3516 | 507.6192 | 229.4717 | 230.6307
Intermediate non-critical | 15.88 | 7.8702 | 16.4248 | 29.7699 | 9.5811 | 49.9586 | 22.584 | 22.6981

## Calculation of targets
Calculation of performance targets
Example only
Availability measures | Total circuit | Peak critical | Peak non-critical | Intermediate critical | Intermediate non-critical
Total plant hours
Planned routine maintenance outages (2002-06 avg) | 5055.0018 | 88.6985 | 68.6103 | 273.1408 | 189.0735
Forced and fault outages (2002-06 avg) | 1557.1429 | 79.1903 | 79.1903 | 87.9892 | 87.9892
SP AusNet planned capex outages (forecast) | 14126.7162 | 420.5283 | 144.5403 | 1366.717 | 469.7561
Customer requested planned augmentation outages (forecast) | 1592 | 175.1398 | 23.535 | 230.6307 | 22.6981
VENCorp requested augmentation outages (forecast) | 1592 | 175.1398 | 23.535 | 230.6307 | 22.6981
Forecast total outage hours | 23922.861 | 938.6967 | 339.4109 | 2189.1084 | 792.2151
Circuit unavailability (%) | 98.6743 | 99.2833 | 99.3544 | 98.4958 | 98.6437
Circuit availability (%) - Forecast target | 98.6743 | 99.2833 | 99.3544 | 98.4958 | 98.6437
Adjustment to historical data | -0.4736 | -0.33975 | -0.20615 | -0.67625 | -0.40248