# ActewAGL

# 2014 Peak Demand Forecast for period: 2015 - 2024

Version 0.5 I Effective date: 05 Jan 2015

Table of Contents

1	Introduction	6

2	Comparison of 2014 Actual Demand to Forecast Data	6

2.1	Introduction of Model Control Colour Threshold	6

2.2	Compare previous forecast to actual peak demand	7

2.2.1	Summary table	7

2.2.2	Colour Threshold Analysis and Actions:	8

2.3	Review of Forecasting Performance	10

2.3.1	Overall Performance	10

2.3.2	Performance Measure Benchmark	10

2.4	Review of Forecast Modelling	11

2.5	Review of Forecasting Scope	11

2.6	Review of Weather conditions 10%PoE and 50%PoE forecast method	11

2.6.1	2013 Demand Forecast: 10%PoE and 50%PoE Projection Method	11

2.6.2	New Projection Method for 10%PoE and 50%PoE forecast in 2014	12

2.7	Modelling/Forecasting Recommendations for 2015 Demand Forecast	13

2.7.1	Weather data	13

2.7.2	Number of Zone Customers	13

2.7.3	Electricity Price / Tariffs or Price Elasticity	13

2.7.4	Demand side solution or Project: Royalla Solar Farm	14

3	Method for Development of Forecast	15

3.1	Method – Bottom up (trend) demand forecast	15

3.2	Method – Top down (econometric) demand forecast	15

3.3	Reconciliation of demand and energy forecasts	15

3.3.1	Reconciliation between bottom-up and top-down forecasts	15

3.3.2	Reconciliation between top-down forecast with energy forecasts	15

4	Modelling/Forecasting Principles followed	17

5	Modelling/Forecasting Methodology	18

5.1	Detailed Methodology	18

5.1.1	Statistical modelling method	18

5.1.2	Segmentation of Summer / Winter scenarios	18

5.1.3	Determine potential explanatory variables	18

5.1.4	Steps taken to develop model/forecast	18

5.2	Summarised Modelling/Forecasting Methodology and Notes	22

6	Important Modelling/Forecasting Notes/Recommendations	24

7	Data used in Modelling	25

8	Forecast Outcomes	26

8.1	System Forecast	26

8.1.1	Summer Forecast	26

8.1.2	Winter Forecast	27

8.2	Zone Forecasts	28

8.2.1	Zone Forecasts 2015 - 2024 – Summary	28

8.2.2	Angle Crossing Zone Forecast	32

8.2.3	Belconnen Zone Forecast	33

8.2.4	City East Zone Forecast	35

8.2.5	Civic Zone Forecast	37

8.2.6	East Lake Zone Forecast	39

8.2.7	Fyshwick Zone Forecast	41

8.2.8	Gilmore Zone Forecast	43

8.2.9	Gold Creek Zone Forecast	45

8.2.10	Latham Zone Forecast	47

8.2.11	Telopea Park Forecast	49

8.2.12	Theodore Forecast	51

8.2.13	Wanniassa Forecast	53

8.2.14	Woden Forecast	55

8.2.15	Molonglo Forecast	57

8.2.16	West Belconnen Forecast	58

9	Appendix	59

9.1	Details of Models/Forecasts	59

9.1.1	System Forecast	59

9.1.2	Belconnen Zone	64

9.1.3	City East Zone	74

9.1.4	Civic Zone	83

9.1.5	East Lake Zone	94

9.1.6	Fyshwick Zone	96

9.1.7	Gilmore Zone Substation	107

9.1.8	Gold Creek Zone Substation	117

9.1.9	Latham Zone Substation	127

9.1.10	Telopea Park Zone Substation	137

9.1.11	Theodore Zone Substation	148

9.1.12	Wanniassa Zone Substation	158

9.1.13	Woden Zone Substation	168

9.2	Block Loads Data	180

9.2.1	Discrete Block Load Projects	180

9.2.2	Continuous Large Block Load Projects	184

9.3	Reconciliation between forecasts	186

9.3.1	Loss Factors	186

9.3.2	Diversity Factors	186

9.3.3	Summer Demand Forecast	187

9.3.4	Winter Demand Forecast	188

9.4	Updating the forecast model	189

Version Control

| Version | Date | Author | Reviewed | Description |
| --- | --- | --- | --- | --- |
| 0.1 | 04/12/14 | B Chen |  | Draft for review |
| 0.2 | 05/12/14 | B Chen | G Pallesen M Schulzer | First Draft Review |
| 0.3 | 09/12/14 | B Chen | G Pallesen M Schulzer | Second Draft Review |
| 0.4 | 16/12/14 | B Chen | C Jones | Jacob Review: New Section 2.7.4 - Royalla Solar Farm; New Section 3.3.2 - Reconciliation of Demand and Energy Forecast. |
| 0.41 | 22/12/14 | B Chen |  | Update: Belconnen Rating |
| 0.5 | 05/01/15 | B Chen |  | Update: Energy Forecast |
| 1.0 |  |  |  | First issue |

Approval

| Endorsed by | Glenn Pallesen | Manager Primary Systems Strategy |
| --- | --- | --- |
| Endorsed by | Dennis Stanley | Branch Manager Asset Strategy and Planning |
| Approved | Stephen Devlin | General Manager Asset Manager |

# Introduction

This report provides the ActewAGL Distribution (AAD) peak demand forecast developed for the period 2015-2024. The forecast includes both a system forecast and Zone Substation forecast.

The report covers the following areas:

- A review of the previous 2013 forecasts.

- A description of the new method used to develop the forecast,

- Detail on the modelling/forecasting principles adhered to, methodology and important notes/recommendations on the model.

- The data used in the modelling and their sources.

- Forecast outcomes – the system and Zone Substation forecast numbers and graphs.

# Comparison of 2014 Actual Demand to Forecast Data

The previous demand forecast for AAD was prepared in December 2013. A review of the ‘actual’ 2014 demand versus the ‘forecast’ for the system and Zone Substation forecasts is presented in this section.

## Introduction of Model Control Colour Threshold

| Colour Code | Definition | Action |
| --- | --- | --- |
| Green | Absolute Variance < 5% | No action – Good fitted Model |
| Amber | Absolute Variance between 5% and 8% | Close Monitoring ? Future redevelopment |
| Red | Absolute Variance > 8% | Immediate model diagnostic and remodelling |
| Yellow | Zone Substation Structure Change occurred | Model Reconstruction |

Threshold benchmarks (5% and 8%) need to be reviewed.

Red Model

Amber Model

Green Model

Yellow Model

Absolute Variance Formula: | Difference %=Forecast -ActualActual ×100%|

## Compare previous forecast to actual peak demand

### Summary table

Table 1.1 Actual Peak Load vs. Forecast Peak Load (including block loads)

| System Level/Zone Substations | Summer Demand 2014 |  |  |  |  | Winter Demand 2014 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Actual (MVA) | Forecast (MVA) |  | Difference |  | Actual (MVA) | Forecast (MVA) |  | Difference |  |
|  |  | 50% PoE | 10% PoE | 50% PoE | 10% PoE |  | 50% PoE | 10% PoE | 50% PoE | 10% PoE |
| System Level | 634.9 | 667.1 | 735.4 | 5% | 16% | 623.5 | 643.1 | 653.8 | 3% | 5% |
| Belconnen | 58.1 | 59.5 | 63.7 | 2% | 10% | 54.8 | 56.8 | 57.2 | 4% | 4% |
| City East | 77.5 | 78.7 | 84.1 | 2% | 9% | 70.3 | 70.5 | 70.8 | 0% | 1% |
| Civic* | 59.6 | 60.4 | 62.7 | 1% | 5% | 51.6 | 56.0 | 56.5 | 9% | 9% |
| East Lake | 8.2 | NA | NA | NA | NA | 16.7 | NA | NA | NA | NA |
| Fyshwick | 31.7 | 40.5 | 42.7 | 28% | 35% | 26.1 | 34.2 | 34.6 | 31% | 32% |
| Gilmore | 26.3 | 22.2 | 23.1 | -16% | -12% | 29.5 | 26.8 | 26.8 | -9% | -9% |
| Gold Creek** | 53.7 | 49.2 | 52.2 | -8% | -3% | 56.9 | 55.6 | 55.7 | -2% | -2% |
| Latham | 55.6 | 54.5 | 58.5 | -2% | 5% | 68.1 | 70.8 | 71.2 | 4% | 5% |
| Telopea Park*** | 99.7 | 101.4 | 106.7 | 2% | 7% | 93.9 | 96.0 | 96.7 | 2% | 3% |
| Theodore | 28.0 | 29.8 | 31.0 | 6% | 11% | 28.4 | 30.4 | 30.6 | 7% | 8% |
| Wanniassa | 71.2 | 73.4 | 79.1 | 3% | 11% | 79.1 | 80.2 | 80.6 | 1% | 2% |
| Woden | 77.9 | 81.7 | 85.4 | 5% | 10% | 74.9 | 79.9 | 80.8 | 7% | 8% |

*Civic zone summer model under Green Threshold and winter model under Red Threshold.

**Gold Creek Zone Substation summer model under Red Threshold and winter model under Green Threshold.

*** Adjustment made as permanent load transfer from Telopea Park Zone to East Lake Zone. The load adjustment is calculated by following equation:

Load Adjustment=Feeders Total Noncoincidence Max Demand ×Coincidence Factor

Coincidence Factor = 0.9

### Colour Threshold Analysis and Actions:

#### Yellow Threshold Model

- Impacted Model: East Lake Zone Substation and  Fyshwick Zone Substation

- East Lake Zone Substation established at December 2013. The following loads were transferred between Fyshwick and East Lake Zone Substations in 2014 on a permanent basis. According to AAD’s future planning, East Lake Zone Substation and Fyshwick Zone Substation will remain connected via the 11kV Distribution Network to provide N-1 support and provide capacity for the future load growth of Fyshwick area.

Table 1.2 Permanent Load Transfers to East Lake Zone Substation

| From |  |  | To |  | Est. Max Demand |
| --- | --- | --- | --- | --- | --- |
| Zone Sub | Feeder | Date | Zone Sub | Feeder |  |
| Fyshwick | Domayne | 15/07/2014 | East Lake ZS | Cessnock | 3.0MVA |
| Fyshwick | Barrier | 09/07/2014 | East Lake ZS | Isa | 2.0MVA |
| Fyshwick | Collie | 13/08/2014 | East Lake ZS | Lyell | 3.7MVA |

- Aim: Produce load forecast for East Lake and Fyshwick Zone Substations

- Assumption: As East Lake Zone Substation does not have any historical data and it will share the load growth in Fyshwick area with the Fyshwick Zone Substation, AAD has assumed the historical trend growth from the new Fyshwick demand forecast (see Appendix 9.1.6 for details) will be equally shared between East Lake Zone Substation (50%) and Fyshwick Zone Substation (50%).

- Solutions:

- Construct a new forecast model for Fyshwick Zone Substation with consideration of the permanent load transfers.

- Calculate the trend growth* from Step 1. (*the trend growth variable is the co-efficient equal to 1 year’s growth in a linear model)

- Split 50% of the load demand trend growth to East Lake Zone Substation and other 50% to Fyshwick Zone Substation.

- Adjust the East Lake Zone Substation load forecast based on the allocated trend growth from Step 3 by using the 2014 actual maximum demand as base year.

- Adjust the Fyshwick Zone Substation load forecast from Step 1 with the allocated trend growth from Step 3.

#### Red Threshold Model

- Impacted Model: Civic Zone Substation (winter), Gilmore Zone Substation and Gold Creek Zone Substation (summer)

- Aim: Build new models for above Zone Substations

- Possible Reasons:

      - Missing 2013 winter peak load data for Civic Zone Substation from trendSCADA due to disruption of installation work of third transformer may have had a major impact on the overestimation of the 2014 winter load forecast.

      - The zones served by Gilmore and Gold Creek Zone Substations contain accelerated levels of land development. This development results in block loads which have not yet been fully modelled. The incomplete modelling, together with an underestimation of the historic trend, accounts for the negative variance in the demand estimate for these zone substations..

- Solutions:

      - Revisit and run model selection procedures for the above Zone Substations and then choose best fit models that is the best explanative to its historical experience. Not only make sure the predictor variables are significant at 5% level, but also assess that the differences between the actual demand and back fit forecast for 2014 are within +/- 5% error range, which is the main purpose of redesigning a model.

      - Assist the Customer Connections Branch to enhance their short term 18 month Block Load forecasting model and develop a long term 10 year block load forecast model to be consistent with the peak demand forecasting report.

#### Amber Threshold Model (Watch List)

- Impacted Model: Models for Theodore Zone Substation and Woden Zone Substation are currently under Amber Threshold and have been placed into the “close monitoring watch list”.

- Assumption: N/A

- Solutions: No action needs to be taken in 2014 demand forecast. However, when the above models are due for review next year in 2015, if the Amber Threshold is maintained or worsened, the model redevelopment procedure should be followed.

## Review of Forecasting Performance

### Overall Performance

Overall, the 2013 peak demand forecasting performance is reasonable:

- Twenty-four models were developed at System and Zone Substation level, including summer and winter load demands.

- 75% of the forecasting models are under Green (58%) and Amber (17%) Threshold.

- Four or 17 % of the models fall under the Red Threshold. (see 1.2.2.2 for reasons)

| Threshold | Green | Amber | Red | Yellow | Total |
| --- | --- | --- | --- | --- | --- |
| Count | 14 | 4 | 4 | 2 | 24 |
| Percentage | 58% | 17% | 17% | 8% | 100% |

### Performance Measure Benchmark

On 13 November 2014, Aaron Settineri, from Ausgrid had discussion with AAD about comparing the performance of demand forecasts and both parties agreed that +/-5% is a common and industry standard performance measure benchmark adopted by many other distribution companies. The Colour Threshold system has been established for the first time in this report and has made the demand forecasting performance measure more visual and easier to interpret.

The future demand projection is a complicated and difficult task, because there are unforeseeable future uncertainties that introduce inaccuracies into the forecast results.  Achieving a 40% - 60% accuracy for statistical modelling of this nature is recognised as being an industry standard.

## Review of Forecast Modelling

The demand forecast models chosen for the 2013 System and Zone Substation forecasts are based on linear regression. This year (2014), other methods such as time series modelling like ARMA model, ARMA-GARCH model and time series regression model were also reconsidered and attempted, but were all ultimately rejected. For example, time series analysis performs well in sample modelling with a big full data set, but the forecast results were poor as the time series’ stationary characteristics drives the forecast to an average result rather than extreme result like peak demand values. Thus, the models chosen for the 2014 System and Zone Substation level forecast remain based on linear regression, with the same methodology as previous years being followed.

## Review of Forecasting Scope

The 2013 Demand Forecast Report covered both summer and winter demand for the System Level and twelve Zone Substations. The East Lake, Molonglo and West Belconnen Zone Substations’ load demand were not forecast and were excluded from the 2013 report. Therefore, those three Zone Substations plus Angle Crossing Mobile Substation have been added into the 2014 report to better reflect the reality and the potential of the ACT electricity demand growth.

## Review of Weather conditions 10%PoE and 50%PoE forecast method

This is the first year an updated weather correction model has been used to provide more accurate estimates of the 10% and 50% PoEs. A summary of the previous and revised methods is provided in clauses 2.6.1 and 2.6.2 below.

### 2013 Demand Forecast: 10%PoE and 50%PoE Projection Method

The previous weather correction model depended on maximum and minimum annual temperatures, as far back as the 1990’s. These data were applied uniformly across all zone substations to determine the effect of temperature on expected summer and winter demands, and subsequently calculate the 50% and 10% PoEs. This model suffers from the following inadequacies:

- Maximum and minimum temperatures do not necessarily correlate with maximum demands

- Applying general weather data in the same way over all zone substations is not the most efficient way to predict the behaviour or individual substations.

- Using temperature data so far into the past will have a distorting effect as customer behaviour with respect to temperature extremes will have changed over time.

### New Projection Method for 10%PoE and 50%PoE forecast in 2014

After consultation with Dr Yanlin Shi, AAD has adopted the following:

- The 2013 10%PoE and 50%PoE weather condition forecast method was general, not explanative and not representative to the sample data;

- The “In Sample Bootstrapping*” Forecasting Method is an appropriate model, which has been used frequently in Dr Shi’s own statistical research.

The Sample Bootstrapping Model is applied as follows:

- Select significant explanatory variable

- Calculate the in sample 50th percentile and 90th percentile of this variable

- Bootstrap this value 2,000 times (By using “R” “boost” package)

- Use the mean value of 2,000 bootstrapping results as the projection of 50%PoE and 10%PoE for that variable

For the weather correction model, only 33 observations were selected, (3 peak points each year for the last 11 years), The Bootstrapping results were close to the “In Sample” 50th percentile and 90th percentile results, therefore it was considered satisfactory to use the direct calculation of “In Sample” 50th percentile and 90th percentiles as explanatory variables for the weather correction model.

* Bootstrapping is a method of simulating more repeated observations from sparse data.

## Modelling/Forecasting Recommendations for 2015 Demand Forecast

The following are the key development areas that are identified from the 2014 Demand Forecasting exercise and need to be considered in improving the future 2015 demand forecast.

### Weather data

#### Current Condition: Maximum and minimum daily temperature data are currently used as explanatory variables for the model selection procedure, but peak demand data arecaptured instantaneously at every five minute interval. This may explain why model variables MaxTemp and MinTemp were not significant for most of models.

#### Recommendation: Use instantaneous weather data to predict instantaneous peak demand load. Instantaneous half hourly weather data can be purchased from Bureau of Meteorology (BOM).

### Number of Zone Customers

#### Current Condition: No data source is variable.

#### Recommendation: Seek the data source within AAD. Eventually, use Zone Customer as a variable to replace current Year variable as the trend growth factor. Zone Customer trend growth is more appropriate than simply using Year variable which is not the best indicator to explain the future Zone Substation load demand growth.

### Electricity Price / Tariffs or Price Elasticity

#### Current Condition: No data source is variable.

#### Recommendation:  Seek contacts in the ActewAGL Retail Division to obtain Tariff data for the future 2015 Demand Forecasting.

### Demand side solution or Project: Royalla Solar Farm

#### Background

Royalla solar farm project was completed and commissioned in 2014, and the first registered meter reading was recorded on 15/08/2014. The solar farm is operating on a 24 hour, 7 day a week basis, but is only generating energy into the Theodore Zone Substation 11kV bus during daylight hours. Outside daylight hours, the solar farm is consuming an average of 39.65 kW per 15 minute interval.

#### Demand Load Impact on Theodore Zone Substation

Impact on Winter Load Demand: During winter the solar farm reaches its peak output between 11am and 1 pm Australian Eastern Time, at approximately 20.3 MVA, but did not materially contribute to any reduction on the peak winter loading on Theodore zone substation, as sunset is typically before 6pm, while the peak winter load is between 6pm and 7pm.

Impact on Summer Load Demand: The solar farm’s output in summer will have some impact on Theodore zone substation peak summer demand, due to the longer daylight hours, and the effect of daylight saving, however the magnitude of the impact is yet to be determined due to no historical summer metering data available at its first year of service.

#### Recommendation

- Quantify the Royalla Solar Farm load output while the 2015 peak summer load reaches at Theodore Zone Substation.

- Incorporate this load impact/output into 2015 Theodore Zone Substation Summer Demand Forecast.

# Method for Development of Forecast

This section is a brief summary of the approach taken to forecasting the peak demand. More details are in the following sections.

## Method – Bottom up (trend) demand forecast

Forecasts for each Zone Substation were developed using a bottom-up / trend forecast. Multiple linear regressions were used to determine the underlying trend as well as the effect of various weather factors, particularly temperature. Known upcoming new customer block loads were also added into the Zone Substation forecasts.

## Method – Top down (econometric) demand forecast

The development of the System demand forecast followed a similar method as for the Zone Substation demand forecasts, with the addition of various econometric / demographic variables. It was established that the only statistically significant variables were weather factors and population. Block loads were not considered for the top-down forecast.

## Reconciliation of demand and energy forecasts

### Reconciliation between bottom-up and top-down forecasts

A bottom-up System demand forecast was obtained by applying a diversity factor to the individually forecasted Zone Substation demand peaks. This bottom-up System demand forecast was then compared against the top-down System demand forecast. The results of the reconciliation can be found in Appendix 10.3.

### Reconciliation between top-down forecast with energy forecasts

The energy forecast (24 Dec 2013 version) was compared to the summer peak demand forecast, using the system annual average load factor. There are no step changes between the historic load factor and the forecast load factor. This indicates that there is sufficient consistency between the methodologies used for the energy and the demand forecasts.

System Annual Average Load Factor=Energy delivered during yearSystem Maximum Demand×Number of hours in year

| Year | Energy Actual/Forecast (GWh) | Summer Demand Actual/Forecast 50%PoE (MVA) | System Annual Average Load Factor (Wh/VAh) |
| --- | --- | --- | --- |
| 2003/04 | 2621 | 577 | 0.52 |
| 2004/05 | 2681 | 579 | 0.53 |
| 2005/06 | 2729 | 648 | 0.48 |
| 2006/07 | 2864 | 643 | 0.51 |
| 2007/08 | 2885 | 624 | 0.53 |
| 2008/09 | 2873 | 711 | 0.46 |
| 2009/10 | 2896 | 682 | 0.48 |
| 2010/11 | 2910 | 707 | 0.47 |
| 2011/12 | 2891 | 555 | 0.59 |
| 2012/13 | 2904 | 656 | 0.51 |
| 2013/14 | 2874 | 635 | 0.52 |
| 2014/15 | 2781 | 666 | 0.48 |
| 2015/16 | 2756 | 673 | 0.47 |
| 2016/17 | 2788 | 680 | 0.47 |
| 2017/18 | 2814 | 687 | 0.47 |
| 2018/19 | 2824 | 695 | 0.46 |

# Modelling/Forecasting Principles followed

The best-practice modelling/forecasting principles that AAD adheres to are described in the table below.

| Principle |  | Description |
| --- | --- | --- |
| 1 | Data | Obtain reliable and unbiased data from reputable sources, conduct data checks to remove/repair erroneous data and manage data effectively. |
| 2 | Model calibration | Use appropriate statistical estimation methods. |
| 3 | Parsimony | Use only as many parameters as necessary to fit the model, to minimise unnecessary complexity and allow model to be easily replicable. |
| 4 | Fit to theory | Choose models which are supported by relevant theory. |
| 5 | Fit to evidence | Show that the model adequately accounts for history used in calibration (conduct back-testing). |
| 6 | Logical model | Explanatory variables in the model should have theoretical basis, and have theoretically correct signs. |
| 7 | Model validation | Analyse the statistical significance of variables, goodness of fit, diagnostic checking of residuals etc. |
| 8 | Model documentation | Detailed and thorough documentation of modelling process to ensure transparency and repeatability. |
| 9 | Version source control | Track changes made to models. |

# Modelling/Forecasting Methodology

## Detailed Methodology

### Statistical modelling method

The models chosen for the System and Zone Substation level forecasts are based on linear regression. All statistical modelling and forecasting was performed using the R statistical program.

### Segmentation of Summer / Winter scenarios

Summer and winter forecasts (corresponding to the calendar year seasons) are developed. The other seasons (spring / autumn) are disregarded in the modelling. This methodology is used because peak demands usually occur in summer and winter when severe weather conditions are prevalent. Moreover, summer and winter demands are modelled separately, as they are observed to have different drivers / patterns of demand.

### Determine potential explanatory variables

| Forecast Type | Potential explanatory variables |
| --- | --- |
| System Level | Economic / demographic variables such as Gross Domestic Product (GDP), Gross State Product (GSP) growth, unemployment rate, population etc. |
| Zone Substation Level | Time trend (implicitly factors in the various possible causes of a change in demand over time), temperature variables: maximum daily temperature, cooling degree days etc. |

This follows the industry best practice load forecasting process which advocates the analysis of top-down econometric variables at the System level, while conducting trend analysis at the Zone Substation, feeder and distribution substation levels

### Steps taken to develop model/forecast

#### Steps to develop Zone Substation level forecast

Step 1: Collect historical data

This step involves the collection and verification of historical data – peak demand data from internal databases, as well as historical data for the potential explanatory variables. All external data is obtained from reputable sources such as the Australian Bureau of Statistics (ABS), BIS Shrapnel and BOM. For additional detail on the precise data sources used for each variable, refer to Section 8.

Step 2: Adjusting for load transfers/switching

ADD has limited data on load transfers/switching. Nevertheless, effects of load transfers/switching are approximated and accounted for when deemed material, e.g.  Abnormal historical maximum demands caused by temporary switching are eliminated, and permanent load transfers are factored into the models.

Step 3: Develop demand forecast model (Model selection)

Three daily peak demand points from each year’s summer/winter are extracted for the last 10 years for each of the Zone Substations. Historical data for potential explanatory variables corresponding to the dates of the peak demand are also obtained. For example, if a peak demand of 50 MVA occurred at the Fyshwick Zone Substation on 20/01/2008, then the maximum temperature/Cooling Degree Days (CDD) for that day is also used.

Using the above data, with peak demand as the dependent variable and the other variables as explanatory variables, separate possible regression models (each with different explanatory variables) are fitted. The model that fits the data “best” is then selected to be the final model used in subsequent forecasting. The way the “best” model is determined is described in the table below.

| Model Selection: 2 main approaches |  |
| --- | --- |
| 1. All subsets approach | Fit all possible models and compare them. This is done with consideration given to the principle of parsimony: “Fit the smallest possible model while making the most possible explanation”. Compare the models based on various criteria: R-squared adj., PRESSp, Cp. Make value judgment after considering all of the factors. - R-squared adj. is the proportion of variability in response that is explained by the model, penalized by number of variables. A good model has high R-squared adj. - PRESSp is the Prediction Sum of Squares – based on cross-validation. Good models have small PRESSp. - Mallow’s Cp - checks if the model is “right” – models that are too small (underfitting) are biased compared with the true model, while models that are too big (overfitting) results in models with inflated variances. GOAL: Values of Cp near p with p as small as possible achieve a satisfactory “bias-variance” trade off. *p refers to the number of explanatory variables in model |
| 2. Stepwise (sequential) procedures | Goal: to find “good” models without necessarily having to check all the bad models. Forward stepwise regression – ensures that the model only includes variables which are significant – meeting a certain F-stat cut-off. |

In AAD’s demand forecast model selection criteria, Method 2 is mainly used, checked against Method 1 to ensure that the right variables are in the model.

*Note 1: Model selection is conducted for each Zone Substation across different seasons. The implication of this is that each Zone Substation could have a different model, which only contains the most significant variables specific to it.

*Note 2: It may be noted that no explicit weather correction is conducted prior to model fitting and regression. This is due to the fact that multiple linear regression is conducted with temperature variables in the model, implicitly correcting for weather.

Step 3: Obtain 10% and 50% PoE weather condition data

In order to forecast the future peak demand, 10% and 50% PoE weather condition data are required to be input into the model. This would allow the model to produce the forecast demand given “1 in 10 year”, and “1 in 2 year” weather conditions. This is obtained by analysing In Sample peak demand point temperature data, and picking out the 10th and 50th percentile.

Step 4: Model validation/derivation of initial forecast (excludes any future block loads)

After an appropriate model has been determined, an initial forecast can be derived. At this point, various checks are conducted on the model to ensure that the model is valid and a good fit for historical data. These checks are described below:

- Visual check – A graph with the historical demands as well as the 50% and 10% PoE forecasts (including back-fit) shows what the maximum demand would have been in the past if 50% and 10% PoE weather conditions had occurred instead of the actual temperatures. To some extent, this graph provides a visual confirmation as to whether the model forecast is reasonable.

- Statistical model diagnostics are scrutinized to ensure that the model is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF etc. are used.

- A back-fit (goodness of fit) analysis is conducted to check the model’s fit for predicting historical demand. Basically, this involves “forecasting” historical demand using the model, given the historical data of the explanatory variables. A graph, as well as a table which shows the % deviation of the back-fit from actual is used to verify the viability of the model.

Step 5: Develop final forecast (factoring in possible future block loads)

After the model has been determined to be a good fit in Step 4, a final forecast can then be developed. This step involves adjusting the initial forecast for expected future block loads.

*Note: AAD currently does not have sufficient data to isolate the effect of historical block customer loads. It is not possible to remove the effect of the embedded historical block loads from the historical trend. An overestimated forecast would therefore result if expected future block loads are simply added on top of the trend. However, it would not be prudent if future block loads are not accounted for. To minimize the overestimation effect, only the effects of block loads ABOVE the trend are added to the forecast.

In this step, 10% and 50% PoE forecasts are developed. This corresponds to the “1 in 10 year”, and “1 in 2 year” weather conditions.

Finally, 90% Prediction Intervals (PI) for each of the 10% and 50% PoE forecasts are generated statistically. This provides the user with a band within which they are 90% confident that demand would fall. For example, the 90% PI for the 50% PoE forecasts is the range within which we can be 90% confident that demand will fall given “1 in 2 year” weather conditions.

Step 6: Produce final graph, forecast numbers and document model used

The final step in the modelling/forecasting process is to produce the final graph and generate the forecast numbers. The model is also documented (e.g. model coefficients), so that it can be easily replicable in the future.

#### Steps to develop system level forecast

The development of the System demand forecast followed a similar method as for the Zone Substation demand forecasts, with the addition of various econometric / demographic variables. It was established that the only statistically significant variables were weather factors and population.

## Summarised Modelling/Forecasting Methodology and Notes

Modelling/Forecasting Methodology

AAD’s Zone Substation demand forecasts use linear regression to model the historical trend of demand growth, and to forecast future peak demand.

Two separate forecast scenarios are produced for summer and winter peak demands, while the other seasons (spring and autumn) are disregarded in the modelling. This methodology is used because peak demands usually occur in summer and winter when severe weather conditions are prevalent.. Also, summer and winter demands are modelled separately as they are observed to have different drivers/patterns of demand.

The steps in developing the Zone Substation forecasts are as follows:

- Determine potential explanatory variables to be analysed – it was decided that at the Zone Substation level, only the time trend (which implicitly factors in the various possible causes of a change in demand over time) and temperature variables would be included. This follows the industry best practice load forecasting process which advocates the analysis of top-down econometric variables at the System level, while conducting trend analysis at the Zone Substation level and network elements between Zone Substations and the customer.

- Collect historical data – peak demand data from internal databases, as well as historical data for temperature variables from the Bureau of Meteorology.

- Adjusting for load transfers/switching – AAD has limited data on load transfers/switching. Nevertheless, effects of load transfers/switching are approximated and accounted for when deemed material, e.g.  Abnormal historical maximum demands caused by temporary switching are eliminated, and permanent load transfers are factored into the models.

- Develop model (Model selection) – 3 daily peak demand points from each year’s summer/winter are extracted for the last 10 years for each of the Zone Substations. Historical data for potential explanatory variables corresponding to the peak demand days are also obtained. Subsequently, using the peak demand as the dependent variable, various possible regression models are fitted. The model that fits the data “best” based on stepwise regression and other statistical criteria is then selected to be the final model used in subsequent forecasting.

- Obtain 10% and 50% PoE weather condition data – analyse individual model’s historical In Sample temperature data, and pick out the 10th and 50th percentile to allow the model to produce the forecast demand given “1 in 10 year” and “1 in 2 year” weather conditions.

- Model validation/derivation of initial forecast (excludes any future block loads) – scrutinize statistical model diagnostics and conduct goodness of fit analysis.

- Develop final forecast (factoring in possible future block loads) – adjust the initial forecast for expected future block loads. Note that only the effects of block loads above the historical trend will be added to the forecast, to minimize the overestimation effect brought about by it being impossible to isolate the effect of historical block customer loads from the historical trend. The final forecast includes 10% and 50% PoE forecasts, which correspond to the “1 in 10 year” and “1 in 2 year” weather conditions, and a 90% prediction interval for each of these forecasts.

- Produce final graphs, forecast numbers and document model used.

Modelling/Forecasting Notes

- The 10% and 50% PoE demand forecasts are based on the 90th percentile and median weather variables respectively. In winter, the difference between the 90th percentile and the median weather variables is small, and as such there is an inconsequential difference between the two forecasts. It is prudent to consider the upper bound of the prediction interval for the 50% PoE forecast as the 1 in 10 year demand.

- Data on block loads is only available and accounted for in the forecasts for approximately the next 18 months. Longer term projects/developments are not accounted for in the forecasts. This has the potential to introduce an underestimation of peak demand in the longer term.

- The forecasts are based on the historical/current state of the network, i.e. they do not factor in planned work. For example, the Fyshwick Zone Substation forecast does not account for possible future transfers to East Lake Zone Substation, which could reduce the Fyshwick peak demand.

- The effect of Photovoltaic (PV) is not directly accounted for in the forecasts. This is analysed separately – currently it has been established that PV has an inconsequential effect on peak demand.

# Important Modelling/Forecasting Notes/Recommendations

- The 10% and 50% PoE demand forecasts are based on the 90th percentile and median weather variables respectively. In winter, the difference between the 90th percentile and the median weather variables is small, and as such there is an inconsequential difference between the two forecasts. It is prudent to consider the upper bound of the prediction interval for the 50% PoE forecast as the 1 in 10 year demand.

- In relation to point 1, a recommendation is to ‘name’ the forecast corresponding to 10% and 50% PoE weather conditions the “High” and “Base” forecasts respectively instead of the 10% PoE and 50% PoE forecasts. With this naming system, AAD can then have the Base 10, 50 and 90% PoE forecasts (the base forecast and the prediction interval around it) and the High 10, 50 and 90% PoE forecasts (the high forecast and the prediction interval around it).

- Data on future block loads is only available and accounted for in the forecasts for approximately the next 18 months. Longer term projects/developments are not accounted for in the forecasts. This has the potential to introduce an underestimation of peak demand in the longer term.

- Historical block loads were not able to be removed from the historical trend because there was no system in place to capture block load transfers between Zone Substations. In the future, a record of block loads coming onto the network should be kept, in order to follow the Best Industry Practices of removing block loads from the historical trend before modelling for the future.

- There is currently no system in place which records information on load transfers/switching. In the forecasts, it is only possible to visually spot the material anomalies and then manually adjust for them. This might affect the accuracy of the forecasts – in the future a record of any temporary/permanent load transfers should be kept.

- The effect of PV is not directly accounted for in the forecasts. This is analysed separately – currently it has been established that PV has an inconsequential effect on peak demand.

# Data used in Modelling

The explanatory variables used in the modelling, along with their sources of historical/forecast data, are listed in the table below.

| Key Driver | Explanatory Variable Used | Source of historical information | Source of future forecast |
| --- | --- | --- | --- |
| Weather | MaxTemp | BOM | Use in sample MaxTemp Data’s median/ 90th percentile |
| Weather | MinTemp | BOM | Use in sample MinTemp Data’s median/ 90th percentile |
| Weather | CDD | BOM | Use in sample CDD Data’s median/ 90th percentile |
| Weather | HDD | BOM | Use in sample HDD Data’s median/ 90th percentile |
| Weather | 3DayCDD | BOM | Use in sample 3DayCDD Data’s median/ 90th percentile |
| Weather | 3DayHDD | BOM | Use in sample 3DayHDD Data’s median/ 90th percentile |
| Economic Growth | Gross State Product (GSP) | ABS 5220.0 Table 1 -Released 21/11/2014 |  |
| Economic Growth | State Final Demand (SFD) | ABS 5220.0 Table 9 – Released 28111/2014 |  |
| Financial influences | CPI | ABS 6401.1 – Released 22/10/2014 |  |
| Demographics | Population | ABS 3101.0 Table 4 – Released 25/09/2013 | Projection based on Historical data |
| Demographics | Households | ABS 3236.0 – Released 8/6/2010 | No historical- this is projected |
| Demographics | Employment | ABS 6202.0 – Released 6/11/2014 |  |

# Forecast Outcomes

## System Forecast

### Summer Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer Ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 665.69 | 730.95 |
| 2016 | 672.75 | 738.01 |
| 2017 | 679.91 | 745.18 |
| 2018 | 687.17 | 752.44 |
| 2019 | 694.54 | 759.80 |
| 2020 | 702.01 | 767.28 |
| 2021 | 709.59 | 774.85 |
| 2022 | 717.27 | 782.54 |
| 2023 | 725.07 | 790.33 |
| 2024 | 732.97 | 798.24 |

### Winter Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 640.6 | 650.3 |
| 2016 | 640.6 | 650.3 |
| 2017 | 640.6 | 650.3 |
| 2018 | 640.6 | 650.3 |
| 2019 | 640.6 | 650.3 |
| 2020 | 640.6 | 650.3 |
| 2021 | 640.6 | 650.3 |
| 2022 | 640.6 | 650.3 |
| 2023 | 640.6 | 650.3 |
| 2024 | 640.6 | 650.3 |

## Zone Forecasts

### Zone Forecasts 2015 - 2024 – Summary

| Summer | 50% PoE Forecast (MVA) | Year | Angle Crossing | Belconnen | City East | East Lake | Fyshwick | Gilmore | Gold Creek | Telopea Park | Theodore | Wanniassa |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 2015 | 1.1 | 59.5 | 80.8 | 16.5 | 30.3 | 25.3 | 55.2 | 100.0 | 28.4 | 73.3 |
|  |  | 2016 | 1.1 | 60.6 | 84.9 | 26.7 | 22.1 | 26.2 | 58.6 | 103.3 | 29.1 | 74.0 |
|  |  | 2017 | 1.1 | 64.4 | 85.1 | 27.2 | 22.6 | 27.0 | 62.1 | 104.4 | 29.9 | 74.7 |
|  |  | 2018 | 1.1 | 68.6 | 85.1 | 40.9 | 10.0 | 27.9 | 65.5 | 105.6 | 30.6 | 75.4 |
|  |  | 2019 | 1.1 | 69.6 | 85.1 | 41.4 | 10.6 | 28.7 | 69.0 | 106.8 | 31.3 | 76.1 |
|  |  | 2020 | 1.1 | 69.6 | 85.1 | 41.9 | 11.1 | 29.5 | 72.4 | 107.9 | 32.1 | 76.8 |
|  |  | 2021 | 1.1 | 69.6 | 85.1 | 42.4 | 11.6 | 30.4 | 75.8 | 109.1 | 32.8 | 77.5 |
|  |  | 2022 | 1.1 | 69.6 | 85.1 | 43.0 | 12.2 | 31.2 | 79.3 | 110.3 | 33.5 | 78.2 |
|  |  | 2023 | 1.1 | 69.6 | 85.1 | 43.5 | 12.7 | 32.1 | 82.7 | 111.4 | 34.3 | 78.9 |
|  |  | 2024 | 1.1 | 69.6 | 85.1 | 44.0 | 13.2 | 32.9 | 86.2 | 112.6 | 35.0 | 79.6 |
|  | 10% PoE Forecast (MVA) | 2015 | 1.1 | 63.4 | 88.3 | 16.5 | 32.9 | 25.7 | 56.6 | 103.1 | 29.9 | 77.4 |
|  |  | 2016 | 1.1 | 64.5 | 92.4 | 26.7 | 24.7 | 26.5 | 60.0 | 106.4 | 30.6 | 78.1 |
|  |  | 2017 | 1.1 | 68.3 | 92.6 | 27.2 | 25.2 | 27.4 | 63.5 | 107.5 | 31.4 | 78.8 |
|  |  | 2018 | 1.1 | 72.5 | 92.6 | 40.9 | 12.7 | 28.2 | 66.9 | 108.7 | 32.1 | 79.5 |
|  |  | 2019 | 1.1 | 73.5 | 92.6 | 41.4 | 13.2 | 29.1 | 70.4 | 109.9 | 32.8 | 80.2 |
|  |  | 2020 | 1.1 | 73.5 | 92.6 | 41.9 | 13.7 | 29.9 | 73.8 | 111.0 | 33.6 | 80.9 |
|  |  | 2021 | 1.1 | 73.5 | 92.6 | 42.4 | 14.3 | 30.7 | 77.2 | 112.2 | 34.3 | 81.6 |
|  |  | 2022 | 1.1 | 73.5 | 92.6 | 43.0 | 14.8 | 31.6 | 80.7 | 113.4 | 35.0 | 82.4 |
|  |  | 2023 | 1.1 | 73.5 | 92.6 | 43.5 | 15.3 | 32.4 | 84.1 | 114.5 | 35.8 | 83.1 |
|  |  | 2024 | 1.1 | 73.5 | 92.6 | 44.0 | 15.8 | 33.3 | 87.6 | 115.7 | 36.5 | 83.8 |

| Summer | 50% PoE Forecast (MVA) | Year | Civic | Woden | Molonglo | Latham | West Belconnen |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 2015 | 59.0 | 84.6 | NC | 56.2 | NC |
|  |  | 2016 | 59.0 | 87.0 | NC | 57.2 | NC |
|  |  | 2017 | 59.2 | 88.9 | NC | 58.2 | NC |
|  |  | 2018 | 60.8 | 88.9 | NC | 59.1 | NC |
|  |  | 2019 | 62.3 | 88.9 | NC | 60.1 | NC |
|  |  | 2020 | 59.1 | 83.5 | 10.2 | 61.1 | NC |
|  |  | 2021 | 59.1 | 83.5 | 11.7 | 62.1 | NC |
|  |  | 2022 | 59.1 | 83.5 | 13.3 | 63.1 | NC |
|  |  | 2023 | 59.1 | 83.5 | 15.1 | 59.1 | 6.5 |
|  |  | 2024 | 59.1 | 83.5 | 16.7 | 60.0 | 7.5 |
|  | 10% PoE Forecast (MVA) | 2015 | 61.7 | 88.9 | NC | 57.9 | NC |
|  |  | 2016 | 61.7 | 91.3 | NC | 58.9 | NC |
|  |  | 2017 | 61.9 | 93.2 | NC | 59.9 | NC |
|  |  | 2018 | 63.5 | 93.2 | NC | 60.9 | NC |
|  |  | 2019 | 65.0 | 93.2 | NC | 61.9 | NC |
|  |  | 2020 | 61.8 | 87.8 | 10.2 | 62.8 | NC |
|  |  | 2021 | 61.8 | 87.8 | 11.7 | 63.8 | NC |
|  |  | 2022 | 61.8 | 87.8 | 13.3 | 64.8 | NC |
|  |  | 2023 | 61.8 | 87.8 | 15.1 | 60.8 | 6.5 |
|  |  | 2024 | 61.8 | 87.8 | 16.7 | 61.8 | 7.5 |

| Winter | 50% PoE Forecast (MVA) | Year | Angle Crossing | Belconnen | City East | East Lake | Fyshwick | Gilmore | Gold Creek | Telopea Park | Theodore | Wanniassa |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 2015 | 2.1 | 57.1 | 72.8 | 26.6 | 14.4 | 29.0 | 59.2 | 93.9 | 29.0 | 78.6 |
|  |  | 2016 | 2.1 | 58.8 | 74.6 | 26.8 | 14.7 | 30.0 | 62.4 | 96.4 | 29.1 | 77.9 |
|  |  | 2017 | 2.1 | 63.8 | 74.4 | 40.2 | 1.8 | 31.0 | 65.5 | 97.5 | 29.1 | 76.8 |
|  |  | 2018 | 2.1 | 66.3 | 74.0 | 40.4 | 2.1 | 32.1 | 68.7 | 98.6 | 29.1 | 75.8 |
|  |  | 2019 | 2.1 | 66.9 | 73.6 | 40.6 | 2.3 | 33.1 | 71.9 | 99.7 | 29.1 | 74.7 |
|  |  | 2020 | 2.1 | 66.9 | 73.2 | 40.9 | 2.5 | 34.2 | 75.0 | 100.7 | 29.1 | 73.7 |
|  |  | 2021 | 2.1 | 66.9 | 72.8 | 41.1 | 2.8 | 35.2 | 78.2 | 101.8 | 29.1 | 72.6 |
|  |  | 2022 | 2.1 | 66.9 | 72.4 | 41.4 | 3.0 | 36.2 | 81.4 | 102.9 | 29.1 | 71.6 |
|  |  | 2023 | 2.1 | 66.9 | 72.0 | 41.6 | 3.3 | 37.3 | 84.6 | 104.0 | 29.1 | 70.5 |
|  |  | 2024 | 2.1 | 66.9 | 71.7 | 41.8 | 3.5 | 38.3 | 87.7 | 105.1 | 29.1 | 69.5 |
|  | 10% PoE Forecast (MVA) | 2015 | 2.1 | 58.3 | 73.8 | 26.6 | 14.4 | 29.0 | 59.2 | 95.0 | 30.1 | 79.9 |
|  |  | 2016 | 2.1 | 59.9 | 75.6 | 26.8 | 14.7 | 30.0 | 62.4 | 97.4 | 30.2 | 79.1 |
|  |  | 2017 | 2.1 | 64.9 | 75.3 | 40.2 | 1.8 | 31.0 | 65.5 | 98.5 | 30.2 | 78.1 |
|  |  | 2018 | 2.1 | 67.5 | 75.0 | 40.4 | 2.1 | 32.1 | 68.7 | 99.6 | 30.2 | 77.1 |
|  |  | 2019 | 2.1 | 68.0 | 74.6 | 40.6 | 2.3 | 33.1 | 71.9 | 100.7 | 30.2 | 76.0 |
|  |  | 2020 | 2.1 | 68.0 | 74.2 | 40.9 | 2.5 | 34.2 | 75.0 | 101.8 | 30.2 | 75.0 |
|  |  | 2021 | 2.1 | 68.0 | 73.8 | 41.1 | 2.8 | 35.2 | 78.2 | 102.9 | 30.2 | 73.9 |
|  |  | 2022 | 2.1 | 68.0 | 73.4 | 41.4 | 3.0 | 36.2 | 81.4 | 104.0 | 30.2 | 72.9 |
|  |  | 2023 | 2.1 | 68.0 | 73.0 | 41.6 | 3.3 | 37.3 | 84.6 | 105.1 | 30.2 | 71.8 |
|  |  | 2024 | 2.1 | 68.0 | 72.7 | 41.8 | 3.5 | 38.3 | 87.7 | 106.2 | 30.2 | 70.8 |

| Winter | 50% PoE Forecast (MVA) | Year | Civic | Woden | Molonglo | Latham | West Belconnen |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 2015 | 52.7 | 76.5 | NC | 69.6 | NC |
|  |  | 2016 | 52.5 | 77.7 | NC | 70.6 | NC |
|  |  | 2017 | 53.3 | 77.6 | NC | 71.6 | NC |
|  |  | 2018 | 54.6 | 76.5 | NC | 72.6 | NC |
|  |  | 2019 | 51.9 | 69.9 | 9.5 | 73.6 | NC |
|  |  | 2020 | 51.7 | 68.8 | 11.0 | 74.6 | NC |
|  |  | 2021 | 51.5 | 67.6 | 12.5 | 75.6 | NC |
|  |  | 2022 | 51.2 | 66.5 | 14.2 | 70.6 | 6.0 |
|  |  | 2023 | 51.0 | 65.4 | 15.9 | 70.6 | 7.0 |
|  |  | 2024 | 50.8 | 64.2 | 17.5 | 70.6 | 8.0 |
|  | 10% PoE Forecast (MVA) | 2015 | 54.2 | 81.1 | NC | 71.1 | NC |
|  |  | 2016 | 54.0 | 82.3 | NC | 72.1 | NC |
|  |  | 2017 | 54.7 | 82.2 | NC | 73.1 | NC |
|  |  | 2018 | 56.1 | 81.1 | NC | 74.1 | NC |
|  |  | 2019 | 53.3 | 74.5 | 9.5 | 75.1 | NC |
|  |  | 2020 | 53.1 | 73.4 | 11.0 | 76.1 | NC |
|  |  | 2021 | 52.9 | 72.2 | 12.5 | 77.1 | NC |
|  |  | 2022 | 52.7 | 71.1 | 14.2 | 72.1 | 6.0 |
|  |  | 2023 | 52.5 | 70.0 | 15.9 | 72.1 | 7.0 |
|  |  | 2024 | 52.3 | 68.8 | 17.5 | 72.1 | 8.0 |

### Angle Crossing Zone Forecast

The main function and purpose of the Angle Crossing Mobile Zone Substation is to provide electricity load capability for Actew Water (now Icon Water) to transfer water between dams in summer or to maintain a sustainable water supply for the ACT when drought occurs.

Table 8.1 Angel Crossing Zone Substation 2014 statistics (from 1/09/2013 to 31/08/2014)

| Summer Maximum Demand (MVA) | 1.05 |
| --- | --- |
| Winter Maximum Demand (MVA) | 2.13 |
| Number of hours Operating (hours) | 46.42 |
| Utilisation Factor | 0.53% |

Note the winter period operation is mainly for the maintenance of the Zone Substation.

A very low utilisation factor indicates the low operation usage of the zone substation. The current Combined Dam Levels in ACT is 83.98% at time of 10:43 am, 4th December 4, 2014 and the past weather conditions in ACT have been moderate and steady, which indicates steady weather condition forecast in future years with no particular signs of drought. Thus, there is reasonable ground to believe that the summer and winter peak demand for Angle Crossing Zone Substation in the next ten years will be similar to the summer and winter maximum demand in 2014 with the assumption of no catastrophic weather events.

| Final Forecast |  |  |
| --- | --- | --- |
| Year | Summer ending Feb | Winter ending Aug |
| 2015 | 1.05 | 2.13 |
| 2016 | 1.05 | 2.13 |
| 2017 | 1.05 | 2.13 |
| 2018 | 1.05 | 2.13 |
| 2019 | 1.05 | 2.13 |
| 2020 | 1.05 | 2.13 |
| 2021 | 1.05 | 2.13 |
| 2022 | 1.05 | 2.13 |
| 2023 | 1.05 | 2.13 |
| 2024 | 1.05 | 2.13 |

### Belconnen Zone Forecast

#### Summer Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 59.5 | 63.4 |
| 2016 | 60.6 | 64.5 |
| 2017 | 64.4 | 68.3 |
| 2018 | 68.6 | 72.5 |
| 2019 | 69.6 | 73.5 |
| 2020 | 69.6 | 73.5 |
| 2021 | 69.6 | 73.5 |
| 2022 | 69.6 | 73.5 |
| 2023 | 69.6 | 73.5 |
| 2024 | 69.6 | 73.5 |

#### Winter Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 57.1 | 58.3 |
| 2016 | 58.8 | 59.9 |
| 2017 | 63.8 | 64.9 |
| 2018 | 66.3 | 67.5 |
| 2019 | 66.9 | 68.0 |
| 2020 | 66.9 | 68.0 |
| 2021 | 66.9 | 68.0 |
| 2022 | 66.9 | 68.0 |
| 2023 | 66.9 | 68.0 |
| 2024 | 66.9 | 68.0 |

### City East Zone Forecast

#### Summer Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 80.8 | 88.3 |
| 2016 | 84.9 | 92.4 |
| 2017 | 85.1 | 92.6 |
| 2018 | 85.1 | 92.6 |
| 2019 | 85.1 | 92.6 |
| 2020 | 85.1 | 92.6 |
| 2021 | 85.1 | 92.6 |
| 2022 | 85.1 | 92.6 |
| 2023 | 85.1 | 92.6 |
| 2024 | 85.1 | 92.6 |

#### Winter Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 72.8 | 73.8 |
| 2016 | 74.6 | 75.6 |
| 2017 | 74.4 | 75.3 |
| 2018 | 74.0 | 75.0 |
| 2019 | 73.6 | 74.6 |
| 2020 | 73.2 | 74.2 |
| 2021 | 72.8 | 73.8 |
| 2022 | 72.4 | 73.4 |
| 2023 | 72.0 | 73.0 |
| 2024 | 71.7 | 72.7 |

### Civic Zone Forecast

#### Summer Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 59.0 | 61.7 |
| 2016 | 59.0 | 61.7 |
| 2017 | 59.2 | 61.9 |
| 2018 | 60.8 | 63.5 |
| 2019 | 62.3 | 65.0 |
| 2020 | 59.1 | 61.8 |
| 2021 | 59.1 | 61.8 |
| 2022 | 59.1 | 61.8 |
| 2023 | 59.1 | 61.8 |
| 2024 | 59.1 | 61.8 |

#### Winter Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 52.7 | 54.2 |
| 2016 | 52.5 | 54.0 |
| 2017 | 53.3 | 54.7 |
| 2018 | 54.6 | 56.1 |
| 2019 | 51.9 | 53.3 |
| 2020 | 51.7 | 53.1 |
| 2021 | 51.5 | 52.9 |
| 2022 | 51.2 | 52.7 |
| 2023 | 51.0 | 52.5 |
| 2024 | 50.8 | 52.3 |

### East Lake Zone Forecast

#### Summer Forecast

| Final Forecast (Incorporating Load Transfers) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 16.5 | 16.5 |
| 2016 | 26.7 | 26.7 |
| 2017 | 27.2 | 27.2 |
| 2018 | 40.9 | 40.9 |
| 2019 | 41.4 | 41.4 |
| 2020 | 41.9 | 41.9 |
| 2021 | 42.4 | 42.4 |
| 2022 | 43.0 | 43.0 |
| 2023 | 43.5 | 43.5 |
| 2024 | 44.0 | 44.0 |

#### Winter Forecast

| Final Forecast (Incorporating Load Transfers) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 26.6 | 26.6 |
| 2016 | 26.8 | 26.8 |
| 2017 | 40.2 | 40.2 |
| 2018 | 40.4 | 40.4 |
| 2019 | 40.6 | 40.6 |
| 2020 | 40.9 | 40.9 |
| 2021 | 41.1 | 41.1 |
| 2022 | 41.4 | 41.4 |
| 2023 | 41.6 | 41.6 |
| 2024 | 41.8 | 41.8 |

### Fyshwick Zone Forecast

#### Summer Forecast

| Final Forecast (Incorporating Block Loads and Load Transfers) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 30.3 | 32.9 |
| 2016 | 22.1 | 24.7 |
| 2017 | 22.6 | 25.2 |
| 2018 | 10.0 | 12.7 |
| 2019 | 10.6 | 13.2 |
| 2020 | 11.1 | 13.7 |
| 2021 | 11.6 | 14.3 |
| 2022 | 12.2 | 14.8 |
| 2023 | 12.7 | 15.3 |
| 2024 | 13.2 | 15.8 |

#### Winter Forecast

| Final Forecast (Incorporating Block Loads and Load Transfers) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 14.4 | 14.4 |
| 2016 | 14.7 | 14.7 |
| 2017 | 1.8 | 1.8 |
| 2018 | 2.1 | 2.1 |
| 2019 | 2.3 | 2.3 |
| 2020 | 2.5 | 2.5 |
| 2021 | 2.8 | 2.8 |
| 2022 | 3.0 | 3.0 |
| 2023 | 3.3 | 3.3 |
| 2024 | 3.5 | 3.5 |

### Gilmore Zone Forecast

#### Summer Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 25.3 | 25.7 |
| 2016 | 26.2 | 26.5 |
| 2017 | 27.0 | 27.4 |
| 2018 | 27.9 | 28.2 |
| 2019 | 28.7 | 29.1 |
| 2020 | 29.5 | 29.9 |
| 2021 | 30.4 | 30.7 |
| 2022 | 31.2 | 31.6 |
| 2023 | 32.1 | 32.4 |
| 2024 | 32.9 | 33.3 |

#### Winter Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 29.0 | 29.0 |
| 2016 | 30.0 | 30.0 |
| 2017 | 31.0 | 31.0 |
| 2018 | 32.1 | 32.1 |
| 2019 | 33.1 | 33.1 |
| 2020 | 34.2 | 34.2 |
| 2021 | 35.2 | 35.2 |
| 2022 | 36.2 | 36.2 |
| 2023 | 37.3 | 37.3 |
| 2024 | 38.3 | 38.3 |

### Gold Creek Zone Forecast

#### Summer Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 55.2 | 56.6 |
| 2016 | 58.6 | 60.0 |
| 2017 | 62.1 | 63.5 |
| 2018 | 65.5 | 66.9 |
| 2019 | 69.0 | 70.4 |
| 2020 | 72.4 | 73.8 |
| 2021 | 75.8 | 77.2 |
| 2022 | 79.3 | 80.7 |
| 2023 | 82.7 | 84.1 |
| 2024 | 86.2 | 87.6 |

#### Winter Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 59.2 | 59.2 |
| 2016 | 62.4 | 62.4 |
| 2017 | 65.5 | 65.5 |
| 2018 | 68.7 | 68.7 |
| 2019 | 71.9 | 71.9 |
| 2020 | 75.0 | 75.0 |
| 2021 | 78.2 | 78.2 |
| 2022 | 81.4 | 81.4 |
| 2023 | 84.6 | 84.6 |
| 2024 | 87.7 | 87.7 |

### Latham Zone Forecast

#### Summer Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 56.2 | 57.9 |
| 2016 | 57.2 | 58.9 |
| 2017 | 58.2 | 59.9 |
| 2018 | 59.1 | 60.9 |
| 2019 | 60.1 | 61.9 |
| 2020 | 61.1 | 62.8 |
| 2021 | 62.1 | 63.8 |
| 2022 | 63.1 | 64.8 |
| 2023 | 59.1 | 60.8 |
| 2024 | 60.0 | 61.8 |

#### Winter Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 69.6 | 71.1 |
| 2016 | 70.6 | 72.1 |
| 2017 | 71.6 | 73.1 |
| 2018 | 72.6 | 74.1 |
| 2019 | 73.6 | 75.1 |
| 2020 | 74.6 | 76.1 |
| 2021 | 75.6 | 77.1 |
| 2022 | 70.6 | 72.1 |
| 2023 | 70.6 | 72.1 |
| 2024 | 70.6 | 72.1 |

### Telopea Park Forecast

#### Summer Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 100.0 | 103.1 |
| 2016 | 103.3 | 106.4 |
| 2017 | 104.4 | 107.5 |
| 2018 | 105.6 | 108.7 |
| 2019 | 106.8 | 109.9 |
| 2020 | 107.9 | 111.0 |
| 2021 | 109.1 | 112.2 |
| 2022 | 110.3 | 113.4 |
| 2023 | 111.4 | 114.5 |
| 2024 | 112.6 | 115.7 |

#### Winter Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 93.9 | 95.0 |
| 2016 | 96.4 | 97.4 |
| 2017 | 97.5 | 98.5 |
| 2018 | 98.6 | 99.6 |
| 2019 | 99.7 | 100.7 |
| 2020 | 100.7 | 101.8 |
| 2021 | 101.8 | 102.9 |
| 2022 | 102.9 | 104.0 |
| 2023 | 104.0 | 105.1 |
| 2024 | 105.1 | 106.2 |

### Theodore Forecast

#### Summer Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 28.4 | 29.9 |
| 2016 | 29.1 | 30.6 |
| 2017 | 29.9 | 31.4 |
| 2018 | 30.6 | 32.1 |
| 2019 | 31.3 | 32.8 |
| 2020 | 32.1 | 33.6 |
| 2021 | 32.8 | 34.3 |
| 2022 | 33.5 | 35.0 |
| 2023 | 34.3 | 35.8 |
| 2024 | 35.0 | 36.5 |

#### Winter Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 29.0 | 30.1 |
| 2016 | 29.1 | 30.2 |
| 2017 | 29.1 | 30.2 |
| 2018 | 29.1 | 30.2 |
| 2019 | 29.1 | 30.2 |
| 2020 | 29.1 | 30.2 |
| 2021 | 29.1 | 30.2 |
| 2022 | 29.1 | 30.2 |
| 2023 | 29.1 | 30.2 |
| 2024 | 29.1 | 30.2 |

### Wanniassa Forecast

#### Summer Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 73.3 | 77.4 |
| 2016 | 74.0 | 78.1 |
| 2017 | 74.7 | 78.8 |
| 2018 | 75.4 | 79.5 |
| 2019 | 76.1 | 80.2 |
| 2020 | 76.8 | 80.9 |
| 2021 | 77.5 | 81.6 |
| 2022 | 78.2 | 82.4 |
| 2023 | 78.9 | 83.1 |
| 2024 | 79.6 | 83.8 |

#### Winter Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 78.6 | 79.9 |
| 2016 | 77.9 | 79.1 |
| 2017 | 76.8 | 78.1 |
| 2018 | 75.8 | 77.1 |
| 2019 | 74.7 | 76.0 |
| 2020 | 73.7 | 75.0 |
| 2021 | 72.6 | 73.9 |
| 2022 | 71.6 | 72.9 |
| 2023 | 70.5 | 71.8 |
| 2024 | 69.5 | 70.8 |

### Woden Forecast

#### Summer Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 84.6 | 88.9 |
| 2016 | 87.0 | 91.3 |
| 2017 | 88.9 | 93.2 |
| 2018 | 88.9 | 93.2 |
| 2019 | 88.9 | 93.2 |
| 2020 | 83.5 | 87.8 |
| 2021 | 83.5 | 87.8 |
| 2022 | 83.5 | 87.8 |
| 2023 | 83.5 | 87.8 |
| 2024 | 83.5 | 87.8 |

#### Winter Forecast

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 76.5 | 81.1 |
| 2016 | 77.7 | 82.3 |
| 2017 | 77.6 | 82.2 |
| 2018 | 76.5 | 81.1 |
| 2019 | 69.9 | 74.5 |
| 2020 | 68.8 | 73.4 |
| 2021 | 67.6 | 72.2 |
| 2022 | 66.5 | 71.1 |
| 2023 | 65.4 | 70.0 |
| 2024 | 64.2 | 68.8 |

### Molonglo Forecast

The Molonglo Forecast is based on the dwelling occupations’ data released from ACT Government Land Release Program. ActewAGL has planned the below feeder extension and upgrade projects to use available network capacity in the area mainly from Civic and Woden Zone Substations to meet the initial stage of the Molonglo area’s load demand. According to summer and winter load demand forecasts below, the non-coincidence maximum demand load of three feeders supply will be exceeded at early 2019. Thus, the new Molonglo Zone Substation is estimated to start its commission during Year 2019 base on the forecast.

| Project | Supply Zone Substation | Estimated Maximum Demand (MVA) |
| --- | --- | --- |
| Hilder Feeder Extension | Woden | 2.7 |
| Streeton Feeder Extension | Woden | 2.7 |
| Black Mountain Upgrade | Civic | 3.2 |
| Total |  | 8.6 |

#### Summer Forecast

| Date (Summer ending Feb) | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020** | 2021 | 2022 | 2023 | 2024 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. Dwelling | 35 | 285 | 855 | 1,538 | 2,228 | 2,878 | 3,478 | 4,078 | 4,678 | 5,328 | 6,028 | 6,678 |
| Total (MVA)* | 0.1 | 0.7 | 2.1 | 3.8 | 5.6 | 7.2 | 8.7 | 10.2 | 11.7 | 13.3 | 15.1 | 16.7 |

* Estimated 2.5kVA per dwelling

** First summer after commission (estimated).

#### Winter Forecast

| Date (Winter Ending Aug) | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019** | 2020 | 2021 | 2022 | 2023 | 2024 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. Dwelling | 160 | 570 | 1196.5 | 1883 | 2553 | 3178 | 3,778 | 4,378 | 5,003 | 5,678 | 6,353 | 7,003 |
| Total (MVA)* | 0.4 | 1.4 | 3.0 | 4.7 | 6.4 | 7.9 | 9.4 | 10.9 | 12.5 | 14.2 | 15.9 | 17.5 |

* Estimated 2.5kVA per dwelling

** First winter after commission (estimated).

### West Belconnen Forecast

#### Timing and assumptions for new Zone Substation

Initial stages of the West Belconnen development can be serviced from the existing Latham Zone Substation which serves existing urban areas of western Belconnen. It is estimated that the new Zone Substation will be required once 2,000 to 3,000 new dwellings are released at West Belconnen. Depending on the rate of new dwelling releases, which could be between 300 and 500 per year, the new Zone Substation would be required within 7 to 10 years.

Therefore, the forecast assumptions are:

- Estimated 2.5kVA per dwelling and 400 dwellings increase per year in the area;

- Latham Zone Substation will take extra 1MVA block load per annum till 1 July 2022 due to the above;

- Supply from new West Belconnen Zone Substation required from 1 July 2022;

- New Zone Substation will take existing load of 2,000 x 2.5kVA (5MVA) from Latham Zone Substation;

- New Zone Substation will take additional load of 400 x 2.5kVA (1MVA) per annum;

#### Summer Forecast

| Date (Summer ending Feb) | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Total (MVA) | NC | NC | NC | NC | NC | NC | NC | NC | NC | 6.5 | 7.5 |

#### Winter Forecast

| Date (Winter Ending Aug) | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Total (MVA) | NC | NC | NC | NC | NC | NC | NC | NC | 6.0 | 7.0 | 8.0 |

# Appendix

## Details of Models/Forecasts

### System Forecast

#### System Summer Forecast

Model Details:	Demand = -150.7 + 32.63*MaxCDD + 0.001278 * Population

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -150.7 | 179.3 | -0.841 | 0.42501 |
| MaxCDD | 32.63 | 6.072 | 5.374 | 0.00067 |
| Population | 0.001278 | 0.0004277 | 2.988 | 0.01738 |
| Residual standard error: 26.1 on 8 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.7961, |  |  |  |  |
| F-statistic: 15.62 on 2 and 8 DF, p-value: 0.001729 |  |  |  |  |

| Year | System Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 577.4 | 604.27 | 5% | 5% |
| 2005 | 579.2 | 558.37 | -4% | 4% |
| 2006 | 648.2 | 639.18 | -1% | 1% |
| 2007 | 642.7 | 648.14 | 1% | 1% |
| 2008 | 623.5 | 625.99 | 0% | 0% |
| 2009 | 711.2 | 701.43 | -1% | 1% |
| 2010 | 681.5 | 708.36 | 4% | 4% |
| 2011 | 707.1 | 658.72 | -7% | 7% |
| 2012 | 555.0 | 574.06 | 3% | 3% |
| 2013 | 656.0 | 663.29 | 1% | 1% |
| 2014 | 634.9 | 654.95 | 3% | 3% |
|  |  | Average | 0% | 3% |

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 665.69 | 730.95 |
| 2016 | 672.75 | 738.01 |
| 2017 | 679.91 | 745.18 |
| 2018 | 687.17 | 752.44 |
| 2019 | 694.54 | 759.80 |
| 2020 | 702.01 | 767.28 |
| 2021 | 709.59 | 774.85 |
| 2022 | 717.27 | 782.54 |
| 2023 | 725.07 | 790.33 |
| 2024 | 732.97 | 798.24 |

|  | 50% PoE |  |  | 10% PoE |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Year | Lower Bound | 50% PoE | Upper Bound | Lower Bound | 10% PoE | Upper Bound |
| 2015 | 608.1262 | 665.6888 | 723.2514 | 668.4458 | 730.9535 | 793.4613 |
| 2016 | 613.0261 | 672.7496 | 732.4730 | 673.0783 | 738.0143 | 802.9503 |
| 2017 | 617.7546 | 679.9106 | 742.0666 | 677.5736 | 745.1753 | 812.7770 |
| 2018 | 622.3303 | 687.1734 | 752.0164 | 681.9478 | 752.4381 | 822.9284 |
| 2019 | 626.7718 | 694.5395 | 762.3072 | 686.2163 | 759.8042 | 833.3921 |
| 2020 | 631.0968 | 702.0104 | 772.9241 | 690.3937 | 767.2751 | 844.1566 |
| 2021 | 635.3219 | 709.5876 | 783.8532 | 694.4935 | 774.8523 | 855.2111 |
| 2022 | 639.4626 | 717.2724 | 795.0823 | 698.5282 | 782.5371 | 866.5461 |
| 2023 | 643.5328 | 725.0665 | 806.6002 | 702.5091 | 790.3312 | 878.1534 |
| 2024 | 647.5454 | 732.9714 | 818.3975 | 706.4466 | 798.2361 | 890.0257 |

#### System Winter Forecast

Model Details:	Demand = 491.78 + 11.36*MaxHDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 491.781 | 66.239 | 7.424 | 0.00004 |
| MaxHDD | 11.363 | 4.972 | 2.286 | 0.04810 |
| Residual standard error: 16.41 on 9 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.3673, Adjusted R-squared: 0.2969 |  |  |  |  |
| F-statistic: 5.224 on 1 and 9 DF, p-value: 0.04812 |  |  |  |  |

| Year | System Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 627.6 | 650.29 | 4% | 4% |
| 2005 | 628.5 | 622.45 | -1% | 1% |
| 2006 | 677.0 | 656.54 | -3% | 3% |
| 2007 | 671.0 | 647.45 | -4% | 4% |
| 2008 | 636.6 | 638.93 | 0% | 0% |
| 2009 | 655.6 | 656.54 | 0% | 0% |
| 2010 | 645.0 | 641.77 | -1% | 1% |
| 2011 | 656.3 | 647.45 | -1% | 1% |
| 2012 | 626.3 | 635.52 | 1% | 1% |
| 2013 | 622.9 | 623.02 | 0% | 0% |
| 2014 | 623.5 | 650.29 | 4% | 4% |
|  |  | Average | 0% | 2% |

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 640.6 | 650.3 |
| 2016 | 640.6 | 650.3 |
| 2017 | 640.6 | 650.3 |
| 2018 | 640.6 | 650.3 |
| 2019 | 640.6 | 650.3 |
| 2020 | 640.6 | 650.3 |
| 2021 | 640.6 | 650.3 |
| 2022 | 640.6 | 650.3 |
| 2023 | 640.6 | 650.3 |
| 2024 | 640.6 | 650.3 |

|  | 50% PoE |  |  | 10% PoE |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Year | Lower Bound | 50% PoE | Upper Bound | Lower Bound | 10% PoE | Upper Bound |
| 2015 | 609.1603 | 640.6330 | 672.1057 | 618.2878 | 650.2913 | 682.2948 |
| 2016 | 609.1603 | 640.6330 | 672.1057 | 618.2878 | 650.2913 | 682.2948 |
| 2017 | 609.1603 | 640.6330 | 672.1057 | 618.2878 | 650.2913 | 682.2948 |
| 2018 | 609.1603 | 640.6330 | 672.1057 | 618.2878 | 650.2913 | 682.2948 |
| 2019 | 609.1603 | 640.6330 | 672.1057 | 618.2878 | 650.2913 | 682.2948 |
| 2020 | 609.1603 | 640.6330 | 672.1057 | 618.2878 | 650.2913 | 682.2948 |
| 2021 | 609.1603 | 640.6330 | 672.1057 | 618.2878 | 650.2913 | 682.2948 |
| 2022 | 609.1603 | 640.6330 | 672.1057 | 618.2878 | 650.2913 | 682.2948 |
| 2023 | 609.1603 | 640.6330 | 672.1057 | 618.2878 | 650.2913 | 682.2948 |
| 2024 | 609.1603 | 640.6330 | 672.1057 | 618.2878 | 650.2913 | 682.2948 |

### Belconnen Zone

#### Belconnen Zone Summer Forecast

Model Selection: Model with variable CDD selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = 40.76 + 1.92 * CDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 40.7555 | 4.0825 | 9.983 | 1.00E-10 |
| CDD | 1.9194 | 0.4431 | 4.331 | 0.000172 |
| Residual standard error: 3.762 on 28 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.4012, Adjusted R-squared: 0.3798 |  |  |  |  |
| F-statistic: 18.76 on 1 and 28 DF, p-value: 0.0001718 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Belconnen Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 53.9 | 59.4 | 10% | 10% |
| 2005 | 53.1 | 56.0 | 5% | 5% |
| 2006 | 57.3 | 62.3 | 9% | 9% |
| 2007 | 59.2 | 62.3 | 5% | 5% |
| 2008 | 59.1 | 57.4 | -3% | 3% |
| 2009 | 65.6 | 64.2 | -2% | 2% |
| 2010 | 62.8 | 63.1 | 1% | 1% |
| 2011 | 69.0 | 60.6 | -12% | 12% |
| 2012 | 51.3 | 55.1 | 7% | 7% |
| 2013 | 57.3 | 59.6 | 4% | 4% |
| 2014 | 58.1 | 58.4 | 1% | 1% |
|  |  | Average | 2.3% | 5.4% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 59.5 | 63.4 |
| 2016 | 60.6 | 64.5 |
| 2017 | 64.4 | 68.3 |
| 2018 | 68.6 | 72.5 |
| 2019 | 69.6 | 73.5 |
| 2020 | 69.6 | 73.5 |
| 2021 | 69.6 | 73.5 |
| 2022 | 69.6 | 73.5 |
| 2023 | 69.6 | 73.5 |
| 2024 | 69.6 | 73.5 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Baldwin | Belconnen | 0.02 | 1/10/2014 | 90% |
| Residential | Cameron South | Belconnen | 0.78 | 1/10/2014 | 100% |
| Commercial | Haydon | Belconnen | 0.0025 | 31/05/2014 | 100% |
| Commercial | Swinden | Belconnen | 0.32 | 1/01/2016 | 100% |
| Community | Swinden | Belconnen | 0.22 | 15/09/2014 | 100% |
| Commercial | William Slim | Belconnen | 0.4 | 1/07/2015 | 100% |
| Commercial | Swinden | Belconnen | 0.19 | 1/09/2015 | 50% |
| Commercial | Latham 3 | Belconnen | 0.05 | 1/01/2016 | 100% |
| Lawson South Stage 1 | Chuculba & Baldwin | Belconnen | 2.58 | 31/12/2015 | 10% |
| Lawson South Stage 1 | Maribyrnong | Belconnen | 2.58 | 31/12/2016 | 70% |
| Lawson South Stage 1 | Maribyrnong | Belconnen | 2.58 | 31/12/2017 | 20% |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 31/12/2016 | 10% |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 31/12/2017 | 70% |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 31/12/2018 | 20% |
| UC Hospital Expansion | NA | Belconnen | 3.00 | 31/12/2016 | 50% |

#### Belconnen Zone Winter Forecast

Model Selection: Model with variable HDD, selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = 50.80 + 0.437 * HDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 50.8035 | 1.5059 | 33.735 | < 2e-16 |
| HDD | 0.4368 | 0.1364 | 3.202 | 0.00315 |
| Residual standard error: 1.655 on 31 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.2485, Adjusted R-squared: 0.2243 |  |  |  |  |
| F-statistic: 10.25 on 1 and 31 DF, p-value: 0.003151 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Belconnen Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 54.7 | 56.2 | 3% | 3% |
| 2005 | 54.5 | 55.8 | 2% | 2% |
| 2006 | 56.7 | 57.1 | 1% | 1% |
| 2007 | 58.3 | 56.8 | -3% | 3% |
| 2008 | 56.1 | 55.7 | -1% | 1% |
| 2009 | 58.7 | 57.1 | -3% | 3% |
| 2010 | 58.6 | 56.5 | -4% | 4% |
| 2011 | 58.0 | 56.2 | -3% | 3% |
| 2012 | 53.9 | 56.3 | 5% | 5% |
| 2013 | 53.0 | 55.1 | 4% | 4% |
| 2014 | 54.8 | 56.9 | 4% | 4% |
|  |  | Average | 0.5% | 2.8% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 57.1 | 58.3 |
| 2016 | 58.8 | 59.9 |
| 2017 | 63.8 | 64.9 |
| 2018 | 66.3 | 67.5 |
| 2019 | 66.9 | 68.0 |
| 2020 | 66.9 | 68.0 |
| 2021 | 66.9 | 68.0 |
| 2022 | 66.9 | 68.0 |
| 2023 | 66.9 | 68.0 |
| 2024 | 66.9 | 68.0 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Baldwin | Belconnen | 0.02 | 1/10/2014 | 90% |
| Residential | Cameron South | Belconnen | 0.78 | 1/10/2014 | 100% |
| Commercial | Swinden | Belconnen | 0.32 | 1/01/2016 | 100% |
| Community | Swinden | Belconnen | 0.22 | 15/09/2014 | 100% |
| Commercial | William Slim | Belconnen | 0.40 | 1/07/2015 | 100% |
| Commercial | Swinden | Belconnen | 0.19 | 1/09/2015 | 50% |
| Commercial | Latham 3 | Belconnen | 0.05 | 1/01/2016 | 100% |
| Lawson South Stage 1 | Chuculba & Baldwin | Belconnen | 2.58 | 30/06/2016 | 45% |
| Lawson South Stage 1 | Maribyrnong | Belconnen | 2.58 | 30/06/2017 | 45% |
| Lawson South Stage 1 | Maribyrnong | Belconnen | 2.58 | 31/12/2017 | 10% |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 30/06/2017 | 45% |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 30/06/2018 | 45% |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 31/12/2018 | 10% |
| UC Hospital Expansion | NA | Belconnen | 3.00 | 31/12/2016 | 50% |

### City East Zone

#### City East Zone Summer Forecast

Model Selection: Model with variable CDD selected based on stepwise procedures and checking against other statistical criteria. Originally chosen model with variables Year and CDD was rejected because the coefficients were unreasonable.

.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = 57.26 + 2.56 * CDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 57.2648 | 4.2599 | 13.443 | 1.79E-14 |
| CDD | 2.5552 | 0.4745 | 5.385 | 7.11E-06 |
| Residual standard error: 4.515 on 31 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.4833, Adjusted R-squared: 0.4667 |  |  |  |  |
| F-statistic: 29 on 1 and 31 DF, p-value: 7.113e-06 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | City East Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 80.56 | 82.05 | 2% | 2% |
| 2005 | 78.92 | 77.58 | -2% | 2% |
| 2006 | 84.35 | 85.88 | 2% | 2% |
| 2007 | 87.35 | 82.31 | -6% | 6% |
| 2008 | 83.70 | 79.37 | -5% | 5% |
| 2009 | 88.55 | 88.44 | 0% | 0% |
| 2010 | 85.51 | 87.03 | 2% | 2% |
| 2011 | 83.99 | 83.71 | 0% | 0% |
| 2012 | 66.90 | 76.30 | 14% | 14% |
| 2013 | 75.48 | 82.31 | 9% | 9% |
| 2014 | 77.53 | 81.92 | 6% | 6% |
|  |  | Average | 1.9% | 4.3% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 80.8 | 88.3 |
| 2016 | 84.9 | 92.4 |
| 2017 | 85.1 | 92.6 |
| 2018 | 85.1 | 92.6 |
| 2019 | 85.1 | 92.6 |
| 2020 | 85.1 | 92.6 |
| 2021 | 85.1 | 92.6 |
| 2022 | 85.1 | 92.6 |
| 2023 | 85.1 | 92.6 |
| 2024 | 85.1 | 92.6 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Braddon | CityEast | 0.25 | 1/09/2016 | 70% |
| Commercial | Aero Park | CityEast | 0.90 | 1/01/2016 | 80% |
| Commercial | Cooyong | CityEast | 0.65 | 15/08/2014 | 100% |
| Commercial/Residential | Ferdinand | CityEast | 1.30 | 1/01/2016 | 90% |
| Commercial/Residential | Haig Feeder | CityEast | 0.17 | 1/01/2016 | 90% |
| Commercial/Residential | Lonsdale | CityEast | 0.50 | 1/08/2014 | 100% |
| Commercial | Lonsdale | CityEast | 0.13 | 15/07/2014 | 100% |
| Commercial | Mackenzie | CityEast | 0.55 | 15/02/2015 | 50% |
| Greenfield (Small) | Mackenzie | CityEast | 0.26 | 15/03/2015 | 70% |
| Residential | Mackenzie | CityEast | 0.41 | 1/06/2015 | 70% |
| Commercial/Restaurant | Northbourne | CityEast | 0.10 | 1/01/2016 | 90% |
| Residential | Mackenzie | CityEast | 0.39 | 1/02/2015 | 100% |
| Commercial/Residential | Lonsdale | CityEast | 0.43 | 1/04/2014 | 100% |
| Commercial | Aero Park | CityEast | 1.50 | 1/06/2015 | 100% |

#### City East Zone Winter Forecast

Model Selection: Model with variable HDD, selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = 839.27 – 0.385 * Year + 0.427HDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 839.2662 | 215.1677 | 3.901 | 0.000502 |
| Year | -0.3847 | 0.1072 | -3.587 | 0.00117 |
| HDD | 0.4267 | 0.1897 | 2.249 | 0.031991 |
| Residual standard error: 1.933 on 30 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.35, Adjusted R-squared: 0.3067 |  |  |  |  |
| F-statistic: 8.078 on 2 and 30 DF, p-value: 0.001561 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | City East Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 72.1 | 73.6 | 2% | 2% |
| 2005 | 70.1 | 72.8 | 4% | 4% |
| 2006 | 76.1 | 73.8 | -3% | 3% |
| 2007 | 76.2 | 73.0 | -4% | 4% |
| 2008 | 73.8 | 71.6 | -3% | 3% |
| 2009 | 74.9 | 72.6 | -3% | 3% |
| 2010 | 70.8 | 71.7 | 1% | 1% |
| 2011 | 71.1 | 71.1 | 0% | 0% |
| 2012 | 69.5 | 70.7 | 2% | 2% |
| 2013 | 69.0 | 69.7 | 1% | 1% |
| 2014 | 70.3 | 70.5 | 0% | 0% |
|  |  | Average | -0.3% | 2.1% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 72.8 | 73.8 |
| 2016 | 74.6 | 75.6 |
| 2017 | 74.4 | 75.3 |
| 2018 | 74.0 | 75.0 |
| 2019 | 73.6 | 74.6 |
| 2020 | 73.2 | 74.2 |
| 2021 | 72.8 | 73.8 |
| 2022 | 72.4 | 73.4 |
| 2023 | 72.0 | 73.0 |
| 2024 | 71.7 | 72.7 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Braddon | CityEast | 0.25 | 1/09/2016 | 70% |
| Commercial | Aero Park | CityEast | 0.90 | 1/01/2016 | 80% |
| Commercial | Cooyong | CityEast | 0.65 | 15/08/2014 | 100% |
| Commercial/Residential | Ferdinand | CityEast | 1.30 | 1/01/2016 | 90% |
| Commercial/Residential | Haig Feeder | CityEast | 0.17 | 1/01/2016 | 90% |
| Commercial/Residential | Lonsdale | CityEast | 0.50 | 1/08/2014 | 100% |
| Commercial | Mackenzie | CityEast | 0.55 | 15/02/2015 | 50% |
| Greenfield (Small) | Mackenzie | CityEast | 0.26 | 15/03/2015 | 70% |
| Residential | Mackenzie | CityEast | 0.41 | 1/06/2015 | 70% |
| Commercial/Restaurant | Northbourne | CityEast | 0.10 | 1/01/2016 | 90% |
| Residential | Mackenzie | CityEast | 0.39 | 1/02/2015 | 100% |
| Commercial | Aero Park | CityEast | 1.50 | 1/06/2015 | 100% |

### Civic Zone

#### Civic Zone Summer Forecast

Model Selection: Model with variable CDD selected based on stepwise procedures and checking against other statistical criteria. Note: Civic Zone is missing 2013 data due to some work on the transformers being completed. The forecast is based on 2004-2012 and 2014.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = 49.614 + 1.06 * CDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 49.6144 | 1.5598 | 31.809 | < 2e-16 |
| CDD | 1.06 | 0.1774 | 5.975 | 1.96E-06 |
| Residual standard error: 2.255 on 28 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.5604, Adjusted R-squared: 0.5447 |  |  |  |  |
| F-statistic: 35.7 on 1 and 28 DF, p-value: 1.958e-06 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Civic Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 58.4 | 56.8 | -3% | 3% |
| 2005 | 58.6 | 57.7 | -2% | 2% |
| 2006 | 59.3 | 61.5 | 4% | 4% |
| 2007 | 62.9 | 61.5 | -2% | 2% |
| 2008 | 56.9 | 58.8 | 3% | 3% |
| 2009 | 62.9 | 62.5 | -1% | 1% |
| 2010 | 60.6 | 62.0 | 2% | 2% |
| 2011 | 65.3 | 60.6 | -7% | 7% |
| 2012 | 52.5 | 55.2 | 5% | 5% |
| 2013 | NA | 59.7 | NA | NA |
| 2014 | 59.6 | 59.8 | 0% | 0% |
|  |  | Average | 0.1% | 2.6% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 59.0 | 61.7 |
| 2016 | 59.0 | 61.7 |
| 2017 | 59.2 | 61.9 |
| 2018 | 60.8 | 63.5 |
| 2019 | 62.3 | 65.0 |
| 2020 | 59.1 | 61.8 |
| 2021 | 59.1 | 61.8 |
| 2022 | 59.1 | 61.8 |
| 2023 | 59.1 | 61.8 |
| 2024 | 59.1 | 61.8 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Miller | Civic | 0.07 | 1/05/2014 | 90% |
| Commercial | Black Mountian | Civic | 0.005 | 31/05/2014 | 100% |
| Residential | Miller | Civic | 0.01 | 1/01/2016 | 90% |
| Residential | Miller | Civic | 0.07 | 30/12/2014 | 100% |
| Molonglo Development | Black Mth | Civic | 0.17 | 1/02/2017 | 100% |
| Molonglo Development | Black Mth | Civic | 1.63 | 1/02/2018 | 100% |
| Molonglo Development | Black Mth | Civic | 1.5 | 1/02/2019 | 100% |
| Molonglo Development | Black Mth | Civic | -3.200 | 1/7/2019 | 100% |

#### Civic Zone Winter Forecast

Model Selection: Model with variables Year and HDD, selected based on stepwise procedures and checking against other statistical criteria. Note: Civic Zone is missing 2013 data due to some work on the transformers being completed. The forecast is based on 2004-2012 and 2014.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = 472.13 – 0.212 * Year + 0.64 * HDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 472.1302 | 138.44415 | 3.41 | 0.002056 |
| MinTemp | -0.21181 | 0.06887 | -3.076 | 0.004769 |
| 3DayHDD | 0.6382 | 0.14269 | 4.473 | 0.000126 |
| Residual standard error: 1.144 on 27 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.5378, Adjusted R-squared: 0.5035 |  |  |  |  |
| F-statistic: 15.71 on 2 and 27 DF, p-value: 2.989e-05 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Civic Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 54.08 | 55.51 | 3% | 3% |
| 2005 | 53.08 | 54.69 | 3% | 3% |
| 2006 | 58.51 | 56.49 | -3% | 3% |
| 2007 | 55.42 | 55.77 | 1% | 1% |
| 2008 | 54.57 | 53.93 | -1% | 1% |
| 2009 | 55.65 | 55.85 | 0% | 0% |
| 2010 | 54.27 | 54.81 | 1% | 1% |
| 2011 | 54.84 | 54.28 | -1% | 1% |
| 2012 | 52.78 | 53.56 | 1% | 1% |
| 2013 | NA | NA | NA | NA |
| 2014 | 51.63 | 53.14 | 3% | 3% |
|  |  | Average | 0.6% | 1.6% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 52.7 | 54.2 |
| 2016 | 52.5 | 54.0 |
| 2017 | 53.3 | 54.7 |
| 2018 | 54.6 | 56.1 |
| 2019 | 51.9 | 53.3 |
| 2020 | 51.7 | 53.1 |
| 2021 | 51.5 | 52.9 |
| 2022 | 51.2 | 52.7 |
| 2023 | 51.0 | 52.5 |
| 2024 | 50.8 | 52.3 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Miller | Civic | 0.010 | 1/01/2016 | 90% |
| Residential | Miller | Civic | 0.070 | 30/12/2014 | 100% |
| Molonglo Development | Black Mth | Civic | 0.985 | 1/08/2017 | 100% |
| Molonglo Development | Black Mth | Civic | 1.565 | 1/08/2018 | 100% |
| Molonglo Development | Black Mth | Civic | -2.550 | 1/7/2019 | 100% |

### East Lake Zone

#### East Lake Zone Summer Forecast

- Historical Fyshwick Summer Demand Trend Growth is 1.057 MVA per annum;

- East Lake Zone Substation summer trend growth = 50% × Historical Fyshwick Trend Growth = 0.528 MVA per annum;

- Base Year = 2014 summer peak demand load = 8.15 MVA

- Peak Demand Forecast (MVA) = Base Year + Cumulated Trend Growth + Cumulated Load Transfer

| Final Forecast |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 16.5 | 16.5 |
| 2016 | 26.7 | 26.7 |
| 2017 | 27.2 | 27.2 |
| 2018 | 40.9 | 40.9 |
| 2019 | 41.4 | 41.4 |
| 2020 | 41.9 | 41.9 |
| 2021 | 42.4 | 42.4 |
| 2022 | 43.0 | 43.0 |
| 2023 | 43.5 | 43.5 |
| 2024 | 44.0 | 44.0 |

Supporting Document: Permanent Load Transfers

| From |  |  | To |  | Coincidence Factor | Est. Max Demand |
| --- | --- | --- | --- | --- | --- | --- |
| Zone Sub | Feeder | Date | Zone Sub | Feeder |  |  |
| Fyshwick | Domayne | 15/07/2014 | East Lake | Cessnock | 90% | 3.00 MVA |
| Fyshwick | Barrier | 09/07/2014 | East Lake | Isa | 90% | 2.00 MVA |
| Fyshwick | Collie | 13/08/2014 | East Lake | Lyell | 90% | 3.70 MVA |
| Fyshwick | NA | 01/07/2015 | East Lake | NA | 100% | 9.67 MVA |
| Fyshwick | NA | 01/07/2017 | East Lake | NA | 100% | 13.10 MVA |

#### East Lake Zone Winter Forecast

- Historical Fyshwick Winter Demand Trend Growth is 0.479 MVA per annum;

- East Lake Zone Substation Winter trend growth = 50% × Historical Fyshwick Trend Growth = 0.24 MVA per annum;

- Base Year = 2014 winter peak demand load = 16.7 MVA

- Peak Demand Forecast (MVA) = Base Year + Cumulated Trend Growth + Cumulated Load Transfer

| Final Forecast |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 26.6 | 26.6 |
| 2016 | 26.8 | 26.8 |
| 2017 | 40.2 | 40.2 |
| 2018 | 40.4 | 40.4 |
| 2019 | 40.6 | 40.6 |
| 2020 | 40.9 | 40.9 |
| 2021 | 41.1 | 41.1 |
| 2022 | 41.4 | 41.4 |
| 2023 | 41.6 | 41.6 |
| 2024 | 41.8 | 41.8 |

Supporting Document: Permanent Load Transfers

| From |  |  | To |  | Coincidence Factor | Est. Max Demand |
| --- | --- | --- | --- | --- | --- | --- |
| Zone Sub | Feeder | Date | Zone Sub | Feeder |  |  |
| Fyshwick | NA | 01/07/2015 | East Lake | NA | 100% | 9.67 MVA |
| Fyshwick | NA | 01/07/2017 | East Lake | NA | 100% | 13.10 MVA |

### Fyshwick Zone

#### Fyshwick Zone Summer Forecast

Model Selection: Model with variables Year and CDD selected based on stepwise procedures and checking against other statistical criteria. Note: permanent switching configurations have been accounted for in this Fyshwick forecast.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = -2108.2 + 1.0568 * Year + 1.074CDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -2108.1765 | 390.1303 | -5.404 | 7.45E-06 |
| Year | 1.0568 | 0.1941 | 5.446 | 6.62E-06 |
| CDD | 1.0739 | 0.29 | 3.703 | 0.000857 |
| Residual standard error: 3.51 on 30 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.571, Adjusted R-squared: 0.5425 |  |  |  |  |
| F-statistic: 19.97 on 2 and 30 DF, p-value: 3.063e-06 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Fyshwick Peak (MVA)* | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 16.3 | 20.2 | 24% | 24% |
| 2005 | 18.3 | 19.3 | 5% | 5% |
| 2006 | 21.4 | 23.9 | 12% | 12% |
| 2007 | 21.4 | 23.4 | 10% | 10% |
| 2008 | 24.7 | 23.0 | -7% | 7% |
| 2009 | 29.9 | 28.1 | -6% | 6% |
| 2010 | 32.0 | 28.6 | -11% | 11% |
| 2011 | 32.5 | 28.3 | -13% | 13% |
| 2012 | 24.3 | 23.9 | -2% | 2% |
| 2013 | 27.2 | 29.8 | 10% | 10% |
| 2014 | 23.9 | 30.7 | 29% | 29% |
|  |  | Average | 5% | 11% |

Final Model/Forecast (including block loads, future load transfer and trend growth adjustment):

- Historical summer trend growth is 1.057 MVA per annum, as this growth is assumed to be equally shared with East Lake Zone Substation. Therefore, the adjusted new trend growth is 0.5284 MVA per annum (50% of historical trend growth). Graph and table showing the final forecast (incorporating potential future block loads and load transfer).

| Final Forecast (Incorporating Block Loads & Load Transfer) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 30.3 | 32.9 |
| 2016 | 22.1 | 24.7 |
| 2017 | 22.6 | 25.2 |
| 2018 | 10.0 | 12.7 |
| 2019 | 10.6 | 13.2 |
| 2020 | 11.1 | 13.7 |
| 2021 | 11.6 | 14.3 |
| 2022 | 12.2 | 14.8 |
| 2023 | 12.7 | 15.3 |
| 2024 | 13.2 | 15.8 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Commercial | Gladstone | Fyshwick | 0.05 | 15/12/2014 | 90% |
| Commercial | Abattoir | Fyshwick | 0.15 | 3/03/2014 | 90% |
| Commercial | Abattoir | Fyshwick | 0.06 | 10/07/2014 | 90% |
| Temporary Supply | Abattoir | Fyshwick | 0.16 | 26/05/2014 | 100% |
| Commercial | Newcastle | Fyshwick | 0.0025 | 31/05/2014 | 100% |
| commercial | Pialligo | Fyshwick | 0.75 | 1/06/2014 | 100% |
| Commercial | Lyell 2 | Fyshwick | 1.5 | 1/06/2015 | 100% |

#### Fyshwick Zone Substation Winter Forecast

Model Selection: Model with variables Year and HDD, selected based on stepwise procedures and checking against other statistical criteria. Note: permanent switching configurations have been accounted for in this Fyshwick Zone Substation forecast.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = -942.1 + 0.479 * Year

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -942.097 | 301.326 | -3.127 | -942.097 |
| Year | 0.479 | 0.15 | 3.194 | 0.479 |
| Residual standard error: 2.725 on 31 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.2476, Adjusted R-squared: 0.2233 |  |  |  |  |
| F-statistic: 10.2 on 1 and 31 DF, p-value: 0.003218 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Fyshwick Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 15.4 | 17.8 | 16% | 16% |
| 2005 | 16.7 | 18.3 | 10% | 10% |
| 2006 | 19.9 | 18.8 | -5% | 5% |
| 2007 | 19.5 | 19.3 | -1% | 1% |
| 2008 | 21.6 | 19.7 | -9% | 9% |
| 2009 | 22.7 | 20.2 | -11% | 11% |
| 2010 | 22.8 | 20.7 | -9% | 9% |
| 2011 | 27.2 | 21.2 | -22% | 22% |
| 2012 | 23.3 | 21.7 | -7% | 7% |
| 2013 | 20.5 | 22.1 | 8% | 8% |
| 2014 | 18.3 | 22.6 | 24% | 24% |
|  |  | Average | -1% | 11% |

Final Model/Forecast (including block loads, load transfers and trend growth adjustment):

- Historical winter trend growth is 0.479 MVA per annum, as this growth is assumed to be equally shared with East Lake Zone Substation. Therefore, the adjusted new trend growth is 0.24 MVA per annum (50% of historical trend growth). Graph and table showing the final forecast (incorporating potential future block loads and load transfers).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 14.4 | 14.4 |
| 2016 | 14.7 | 14.7 |
| 2017 | 1.8 | 1.8 |
| 2018 | 2.1 | 2.1 |
| 2019 | 2.3 | 2.3 |
| 2020 | 2.5 | 2.5 |
| 2021 | 2.8 | 2.8 |
| 2022 | 3.0 | 3.0 |
| 2023 | 3.3 | 3.3 |
| 2024 | 3.5 | 3.5 |

- Graph used in reports/for presentation (incorporating potential future block loads and load transfers)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Commercial | Gladstone | Fyshwick | 0.05 | 15/12/2014 | 90% |
| Commercial | Lyell 2 | Fyshwick | 1.5 | 1/06/2015 | 100% |

### Gilmore Zone Substation

#### Gilmore Zone Substation Summer Forecast

Model Selection: Model with variables Year, MaxTemp and 3DayCDD selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = -1690 + 0.845 * Year + 0.244*MaxTemp + 0.0953 * 3DayCDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -1689.65 | 172.70 | -9.7840 | 1.08E-10 |
| Year | 0.84493 | 0.0859 | 9.8340 | 9.63E-11 |
| MaxTemp | 0.24402 | 0.0871 | 2.8020 | 0.00895 |
| 3DayCDD | 0.09530 | 0.0477 | 1.9990 | 0.05511 |
| Residual standard error: 1.56 on 29 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.7991, Adjusted R-squared: 0.7784 |  |  |  |  |
| F-statistic: 38.46 on 3 and 29 DF, p-value: 3.096e-10 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Gilmore Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 15.66 | 14.63 | -7% | 7% |
| 2005 | 15.77 | 15.48 | -2% | 2% |
| 2006 | 17.43 | 16.71 | -4% | 4% |
| 2007 | 16.03 | 17.38 | 8% | 8% |
| 2008 | 16.03 | 17.38 | 8% | 8% |
| 2009 | 18.66 | 20.91 | 12% | 12% |
| 2010 | 19.87 | 20.88 | 5% | 5% |
| 2011 | 22.52 | 20.15 | -11% | 11% |
| 2012 | 18.91 | 19.61 | 4% | 4% |
| 2013 | 22.69 | 22.98 | 1% | 1% |
| 2014 | 26.30 | 24.16 | -8% | 8% |
|  |  | Average | 0.7% | 6.4% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 25.3 | 25.7 |
| 2016 | 26.2 | 26.5 |
| 2017 | 27.0 | 27.4 |
| 2018 | 27.9 | 28.2 |
| 2019 | 28.7 | 29.1 |
| 2020 | 29.5 | 29.9 |
| 2021 | 30.4 | 30.7 |
| 2022 | 31.2 | 31.6 |
| 2023 | 32.1 | 32.4 |
| 2024 | 32.9 | 33.3 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Commercial | Monaro | Gilmore | 0.07 | 15/04/2014 | 100% |
| Commercial | Tralee | Gilmore | 0.62 | 1/01/2016 | 100% |
| Commercial | Tralee | Gilmore | 0.3 | 1/11/2014 | 100% |
| Commercial | Tralee | Gilmore | 0.07 | 1/12/2014 | 90% |
| Commercial | Tralee | Gilmore | 0.06 | 10/10/2014 | 100% |

#### Gilmore Zone Substation Winter Forecast

Model Selection: There is an obvious increasing trend in winter demand at Gilmore Zone Substation over the most recent 6 years. Hence, the previous years are disregarded when modelling. Only the variable Year was found to be significant in the model, leading to the 50% and 10% PoE forecasts being the same (since there are no weather variables).

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = -2065.37 + 1.039 * Year

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -2065.372738 | 1.35E+02 | -15.29 | 3.93E-12 |
| Year | 1.039167 | 6.72E-02 | 15.47 | 3.20E-12 |
| Residual standard error: 0.6157 on 19 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.9264, Adjusted R-squared: 0.9226 |  |  |  |  |
| F-statistic: 239.3 on 1 and 19 DF, p-value: 3.195e-12 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Gilmore Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 |  |  |  |  |
| 2005 |  |  |  |  |
| 2006 |  |  |  |  |
| 2007 |  |  |  |  |
| 2008 | 21.8 | 21.3 | -3% | 3% |
| 2009 | 22.4 | 22.3 | 0% | 0% |
| 2010 | 23.3 | 23.4 | 0% | 0% |
| 2011 | 24.8 | 24.4 | -1% | 1% |
| 2012 | 25.5 | 25.4 | 0% | 0% |
| 2013 | 26.2 | 26.5 | 1% | 1% |
| 2014 | 29.5 | 27.5 | -7% | 7% |
|  |  | Average | -1.4% | 1.7% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 29.0 | 29.0 |
| 2016 | 30.0 | 30.0 |
| 2017 | 31.0 | 31.0 |
| 2018 | 32.1 | 32.1 |
| 2019 | 33.1 | 33.1 |
| 2020 | 34.2 | 34.2 |
| 2021 | 35.2 | 35.2 |
| 2022 | 36.2 | 36.2 |
| 2023 | 37.3 | 37.3 |
| 2024 | 38.3 | 38.3 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Commercial | Tralee | Gilmore | 0.62 | 1/01/2016 | 100% |
| Commercial | Tralee | Gilmore | 0.3 | 1/11/2014 | 100% |
| Commercial | Tralee | Gilmore | 0.07 | 1/12/2014 | 90% |
| Commercial | Tralee | Gilmore | 0.06 | 10/10/2014 | 100% |

### Gold Creek Zone Substation

#### Gold Creek Zone Substation Summer Forecast

Model Selection: Model with variables Year, MaxTemp and 3DayCDD selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = -6902.5 + 3.44 * Year + 0.382 * MaxTemp + 0.179 * 3DayCDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -6902.5 | 238.0 | -29.004 | < 2e-16 |
| Year | 3.4436 | 0.1196 | 28.794 | < 2e-16 |
| CDD | 0.3818 | 0.1632 | 2.339 | 0.02729 |
| 3DayCDD | 0.1791 | 0.0589 | 3.042 | 0.00531 |
| Residual standard error: 1.913 on 26 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.9764, Adjusted R-squared: 0.9737 |  |  |  |  |
| F-statistic: 359.3 on 3 and 26 DF, p-value: < 2.2e-16 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Gold Creek Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 16.4 | 17.7 | 8% | 8% |
| 2005 | 17.8 | 19.7 | 11% | 11% |
| 2006 | 24.8 | 24.0 | -3% | 3% |
| 2007 | 26.4 | 26.9 | 2% | 2% |
| 2008 | 28.2 | 29.1 | 3% | 3% |
| 2009 | 38.8 | 37.3 | -4% | 4% |
| 2010 | 37.3 | 39.1 | 5% | 5% |
| 2011 | 43.9 | 40.3 | -8% | 8% |
| 2012 | 36.3 | 40.8 | 12% | 12% |
| 2013 | 48.5 | 47.5 | -2% | 2% |
| 2014 | 53.7 | 52.7 | -2% | 2% |
|  |  | Average | 2.0% | 5.5% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 55.2 | 56.6 |
| 2016 | 58.6 | 60.0 |
| 2017 | 62.1 | 63.5 |
| 2018 | 65.5 | 66.9 |
| 2019 | 69.0 | 70.4 |
| 2020 | 72.4 | 73.8 |
| 2021 | 75.8 | 77.2 |
| 2022 | 79.3 | 80.7 |
| 2023 | 82.7 | 84.1 |
| 2024 | 86.2 | 87.6 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Commercial | Boulevard North | GoldCreek | 0.19 | 12/05/2014 | 90% |
| Commercial | West 2 | GoldCreek | 0.08 | 28/02/2014 | 90% |
| Residential | Nona | GoldCreek | 0.22 | 1/02/2015 | 90% |
| Residential & Commercial | Gurrang | GoldCreek | 0.20 | 1/02/2015 | 90% |
| Rural Residential | Lander 2 | GoldCreek | 0.16 | 1/01/2016 | 90% |
| Residential | Meacham | GoldCreek | 0.15 | 1/01/2016 | 100% |
| Residential | Anthony Rolf | GoldCreek | 0.50 | 1/01/2015 | 100% |
| Commercial | West | GoldCreek | 0.23 | 1/08/2015 | 90% |
| Temporary Supply | Nona | GoldCreek | 0.11 | 15/06/2014 | 100% |
| Residential | Nona | GoldCreek | 0.16 | 1/01/2015 | 100% |
| Residential | Nona | GoldCreek | 0.10 | 1/06/2015 | 100% |
| Commercial/Residential | Gurrang | GoldCreek | 0.90 | 1/01/2016 | 90% |
| Commercial | Anthony Rolf | GoldCreek | 0.11 | 15/10/2014 | 90% |
| Commercial | Nona | GoldCreek | 1.00 | 1/06/2015 | 90% |
| Commercial | Maribyrnong 4 | GoldCreek | 0.09 | 1/01/2016 | 90% |

#### Gold Creek Zone Substation Winter Forecast

Model Selection: Model with variables Year and 3DayHDD, selected based on stepwise procedures and checking against other statistical criteria. 3DayHDD is marginally significant.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = -6328 + 3.168 * Year + 0.085 * 3DayHDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -6328.159 | 1.48E+02 | -42.708 | <2e-16 |
| Year | 3.16836 | 7.36E-02 | 43.05 | <2e-16 |
| 3DayHDD | 0.085074 | 4.50E-02 | 1.889 | 0.0686 |
| Residual standard error: 1.291 on 30 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.9848, Adjusted R-squared: 0.9838 |  |  |  |  |
| F-statistic: 972.7 on 2 and 30 DF, p-value: < 2.2e-16 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Gold Creek Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 26.0 | 24.0 | -8% | 8% |
| 2005 | 27.6 | 26.3 | -5% | 5% |
| 2006 | 28.6 | 30.5 | 7% | 7% |
| 2007 | 34.9 | 33.8 | -3% | 3% |
| 2008 | 36.4 | 36.9 | 1% | 1% |
| 2009 | 37.7 | 39.0 | 3% | 3% |
| 2010 | 42.6 | 42.7 | 0% | 0% |
| 2011 | 47.1 | 46.1 | -2% | 2% |
| 2012 | 48.2 | 48.9 | 1% | 1% |
| 2013 | 53.1 | 52.5 | -1% | 1% |
| 2014 | 56.9 | 55.3 | -3% | 3% |
|  |  | Average | -0.8% | 3.2% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 59.2 | 59.2 |
| 2016 | 62.4 | 62.4 |
| 2017 | 65.5 | 65.5 |
| 2018 | 68.7 | 68.7 |
| 2019 | 71.9 | 71.9 |
| 2020 | 75.0 | 75.0 |
| 2021 | 78.2 | 78.2 |
| 2022 | 81.4 | 81.4 |
| 2023 | 84.6 | 84.6 |
| 2024 | 87.7 | 87.7 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Nona | GoldCreek | 0.22 | 1/02/2015 | 90% |
| Residential & Commercial | Gurrang | GoldCreek | 0.20 | 1/02/2015 | 90% |
| Rural Residential | Lander 2 | GoldCreek | 0.16 | 1/01/2016 | 90% |
| Residential | Meacham | GoldCreek | 0.15 | 1/01/2016 | 100% |
| Residential | Anthony Rolf | GoldCreek | 0.50 | 1/01/2015 | 100% |
| Commercial | West | GoldCreek | 0.23 | 1/08/2015 | 90% |
| Residential | Nona | GoldCreek | 0.16 | 1/01/2015 | 100% |
| Residential | Nona | GoldCreek | 0.10 | 1/06/2015 | 100% |
| Commercial/Residential | Gurrang | GoldCreek | 0.90 | 1/01/2016 | 90% |
| Commercial | Anthony Rolf | GoldCreek | 0.11 | 15/10/2014 | 90% |
| Commercial | Nona | GoldCreek | 1.00 | 1/06/2015 | 90% |
| Commercial | Maribyrnong 4 | GoldCreek | 0.09 | 1/01/2016 | 90% |

### Latham Zone Substation

#### Latham Zone Substation Summer Forecast

Model Selection: Model with variables Year and CDD, selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = -1932.7 + 0.98 * Year + 1.298 * CDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -1932.7141 | 300.2426 | -6.437 | 6.74E-07 |
| Year | 0.9811 | 0.1499 | 6.546 | 5.09E-07 |
| CDD | 1.298 | 0.347 | 3.74 | 0.000876 |
| Residual standard error: 2.504 on 27 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.7356, Adjusted R-squared: 0.716 |  |  |  |  |
| F-statistic: 37.55 on 2 and 27 DF, p-value: 1.591e-08 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Latham Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 42.81 | 45.89 | 7% | 7% |
| 2005 | 43.47 | 45.90 | 6% | 6% |
| 2006 | 49.12 | 49.86 | 2% | 2% |
| 2007 | 49.9 | 49.03 | -2% | 2% |
| 2008 | 46.57 | 48.26 | 4% | 4% |
| 2009 | 55.56 | 54.23 | -2% | 2% |
| 2010 | 54.69 | 53.98 | -1% | 1% |
| 2011 | 56.69 | 51.46 | -9% | 9% |
| 2012 | 45.51 | 50.88 | 12% | 12% |
| 2013 | 52.58 | 54.91 | 4% | 4% |
| 2014 | 55.64 | 55.44 | 0% | 0% |
|  |  | Average | 1.7% | 4.5% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 56.2 | 57.9 |
| 2016 | 57.2 | 58.9 |
| 2017 | 58.2 | 59.9 |
| 2018 | 59.1 | 60.9 |
| 2019 | 60.1 | 61.9 |
| 2020 | 61.1 | 62.8 |
| 2021 | 62.1 | 63.8 |
| 2022 | 63.1 | 64.8 |
| 2023 | 59.1 | 60.8 |
| 2024 | 60.0 | 61.8 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Commercial | Tilyard Feeder | Latham | 0.23 | 1/02/2014 | 90% |
| Residential | Conley Feeder | Latham | 0.03 | 1/08/2014 | 90% |
| Community | Lhotsky Feeder | Latham | 0.07 | 1/02/2015 | 70% |
| Residential | Macrossan Feeder | Latham | 0.02 | 1/01/2016 | 90% |
| West Belconnen development | NA | Latham | -5.00 | 1/07/2022 | 100% |

#### Latham Zone Substation Winter Forecast

Model Selection: Model with variable 3DayHDD, selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = 62.984+ 0.2075 * 3DayHDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 62.98406 | 1.97175 | 31.943 | < 2e-16 |
| 3DayHDD | 0.20751 | 0.07278 | 2.851 | 0.00768 |
| Residual standard error: 1.967 on 31 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.2078, Adjusted R-squared: 0.1822 |  |  |  |  |
| F-statistic: 8.131 on 1 and 31 DF, p-value: 0.007678 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Latham Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 68.4 | 68.5 | 0% | 0% |
| 2005 | 69.9 | 67.6 | -3% | 3% |
| 2006 | 73.3 | 70.1 | -4% | 4% |
| 2007 | 73.2 | 70.4 | -4% | 4% |
| 2008 | 69.6 | 70.3 | 1% | 1% |
| 2009 | 68.0 | 67.7 | 0% | 0% |
| 2010 | 70.9 | 69.0 | -3% | 3% |
| 2011 | 69.8 | 69.5 | 0% | 0% |
| 2012 | 66.3 | 69.5 | 5% | 5% |
| 2013 | 69.0 | 69.7 | 1% | 1% |
| 2014 | 68.1 | 68.9 | 1% | 1% |
|  |  | Average | -0.6% | 2.1% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter ending Aug | 50% PoE (in MVA) | 50% PoE (in MVA) |
| 2015 | 69.6 | 71.1 |
| 2016 | 70.6 | 72.1 |
| 2017 | 71.6 | 73.1 |
| 2018 | 72.6 | 74.1 |
| 2019 | 73.6 | 75.1 |
| 2020 | 74.6 | 76.1 |
| 2021 | 75.6 | 77.1 |
| 2022 | 70.6 | 72.1 |
| 2023 | 70.6 | 72.1 |
| 2024 | 70.6 | 72.1 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Conley Feeder | Latham | 0.03 | 1/08/2014 | 90% |
| Community | Lhotsky Feeder | Latham | 0.07 | 1/02/2015 | 70% |
| Residential | Macrossan Feeder | Latham | 0.02 | 1/01/2016 | 90% |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2015 | 100% |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2016 | 100% |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2017 | 100% |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2018 | 100% |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2019 | 100% |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2020 | 100% |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2021 | 100% |
| West Belconnen development | NA | Latham | -5.00 | 1/07/2022 | 100% |

### Telopea Park Zone Substation

#### Telopea Park Zone Substation Summer Forecast

Model Selection: Model with variables Year, CDD and 3DayCDD selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = -2263.92 + 1.167 * Year + 1.374 * CDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -2263.91970 | 515.662 | -4.390 | 0.000157 |
| Year | 1.16700 | 0.257 | 4.537 | 0.000106 |
| CDD | 1.37350 | 0.529 | 2.598 | 0.015016 |
| Residual standard error: 4.358 on 27 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.5557, Adjusted R-squared: 0.5227 |  |  |  |  |
| F-statistic: 16.88 on 2 and 27 DF, p-value: 1.755e-05 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Telopea Park Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 88.1 | 88.1 | 0% | 0% |
| 2005 | 87.3 | 86.9 | 0% | 0% |
| 2006 | 95.0 | 92.5 | -3% | 3% |
| 2007 | 91.8 | 93.8 | 2% | 2% |
| 2008 | 88.6 | 91.4 | 3% | 3% |
| 2009 | 99.7 | 97.4 | -2% | 2% |
| 2010 | 94.7 | 97.8 | 3% | 3% |
| 2011 | 107.0 | 97.2 | -9% | 9% |
| 2012 | 83.3 | 91.4 | 10% | 10% |
| 2013 | 97.5 | 98.8 | 1% | 1% |
| 2014 | 99.7 | 99.7 | 0% | 0% |
|  |  | Average | 0.5% | 3.1% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 100.0 | 103.1 |
| 2016 | 103.3 | 106.4 |
| 2017 | 104.4 | 107.5 |
| 2018 | 105.6 | 108.7 |
| 2019 | 106.8 | 109.9 |
| 2020 | 107.9 | 111.0 |
| 2021 | 109.1 | 112.2 |
| 2022 | 110.3 | 113.4 |
| 2023 | 111.4 | 114.5 |
| 2024 | 112.6 | 115.7 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Mundaring | TelopeaPark | 0.26 | 1/03/2015 | 90% |
| Commercial | Mundaring | TelopeaPark | 0.05 | 1/03/2014 | 90% |
| Residential | Belmore 2 | TelopeaPark | 0.19 | 30/06/2014 | 100% |
| Commercial | Dairy South | TelopeaPark | 0.12 | 30/06/2015 | 90% |
| Residential | Jardine | TelopeaPark | 0.12 | 1/01/2016 | 90% |
| Residential | Mundarin | TelopeaPark | 0.45 | 1/01/2016 | 90% |
| Commercial / Residential | STURT | TelopeaPark | 0.18 | 1/01/2016 | 90% |
| Residential | Ovens | TelopeaPark | 0.41 | 1/01/2016 | 70% |
| Residential | Ovens | TelopeaPark | 0.31 | 1/01/2016 | 70% |
| Residential | Ovens | TelopeaPark | 0.13 | 1/01/2016 | 70% |
| Residential | Ovens | TelopeaPark | 0.41 | 1/01/2016 | 70% |
| Residential | Throsby | TelopeaPark | 0.45 | 10/04/2015 | 90% |
| Commercial / Residential | Young | TelopeaPark | 0.79 | 1/01/2016 | 100% |
| Commercial | Telopea Park East | TelopeaPark | 0.11 | 1/01/2016 | 90% |
| Embassy | Empire 2 | TelopeaPark | 0.11 | 25/04/2015 | 70% |

#### Telopea Park Zone Substation Winter Forecast

Model Selection: Model with variables Year and 3DayHDD, selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = -2115.62 + 1.09 * Year + 0.338 * 3DayHDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -2115.6229 | 369.7447 | -5.722 | 3.04E-06 |
| Year | 1.0914 | 0.1832 | 5.959 | 1.57E-06 |
| 3DayHDD | 0.3381 | 0.1321 | 2.56 | 0.0157 |
| Residual standard error: 2.935 on 30 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.5426, Adjusted R-squared: 0.5121 |  |  |  |  |
| F-statistic: 17.79 on 2 and 30 DF, p-value: 8.038e-06 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Telopea Park Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 81.7 | 83.4 | 2% | 2% |
| 2005 | 79.8 | 83.0 | 4% | 4% |
| 2006 | 90.9 | 86.5 | -5% | 5% |
| 2007 | 89.0 | 86.9 | -2% | 2% |
| 2008 | 85.7 | 86.3 | 1% | 1% |
| 2009 | 86.3 | 87.5 | 1% | 1% |
| 2010 | 90.8 | 89.3 | -2% | 2% |
| 2011 | 89.7 | 88.9 | -1% | 1% |
| 2012 | 89.4 | 89.8 | 0% | 0% |
| 2013 | 88.2 | 90.5 | 3% | 3% |
| 2014 | 93.9 | 92.2 | -2% | 2% |
|  |  | Average | 0.0% | 2.1% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 93.9 | 95.0 |
| 2016 | 96.4 | 97.4 |
| 2017 | 97.5 | 98.5 |
| 2018 | 98.6 | 99.6 |
| 2019 | 99.7 | 100.7 |
| 2020 | 100.7 | 101.8 |
| 2021 | 101.8 | 102.9 |
| 2022 | 102.9 | 104.0 |
| 2023 | 104.0 | 105.1 |
| 2024 | 105.1 | 106.2 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Mundaring | TelopeaPark | 0.26 | 1/03/2015 | 90% |
| Commercial | Dairy South | TelopeaPark | 0.12 | 30/06/2015 | 90% |
| Residential | Jardine | TelopeaPark | 0.12 | 1/01/2016 | 90% |
| Residential | Mundarin | TelopeaPark | 0.45 | 1/01/2016 | 90% |
| Commercial / Residential | STURT | TelopeaPark | 0.18 | 1/01/2016 | 90% |
| Residential | Ovens | TelopeaPark | 0.41 | 1/01/2016 | 70% |
| Residential | Ovens | TelopeaPark | 0.31 | 1/01/2016 | 70% |
| Residential | Ovens | TelopeaPark | 0.13 | 1/01/2016 | 70% |
| Residential | Ovens | TelopeaPark | 0.41 | 1/01/2016 | 70% |
| Residential | Throsby | TelopeaPark | 0.45 | 10/04/2015 | 90% |
| Commercial / Residential | Young | TelopeaPark | 0.79 | 1/01/2016 | 100% |
| Commercial | Telopea Park East | TelopeaPark | 0.11 | 1/01/2016 | 90% |
| Embassy | Empire 2 | TelopeaPark | 0.11 | 25/04/2015 | 70% |

### Theodore Zone Substation

#### Theodore Zone Substation Summer Forecast

Model Selection: Model with variables Year and 3DayCDD selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = -1455.15 + 0.7342 * Year + 0.2133 * 3DayCDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -1455.00 | 281.20 | -5.176 | 1.42E-05 |
| Year | 0.7342 | 0.1398 | 5.25 | 1.15E-05 |
| 3DayCDD | 0.2133 | 0.0591 | 3.608 | 0.00111 |
| Residual standard error: 2.478 on 30 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.5304, Adjusted R-squared: 0.4991 |  |  |  |  |
| F-statistic: 16.94 on 2 and 30 DF, p-value: 1.19e-05 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Theodore Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 18.5 | 22.2 | 20% | 20% |
| 2005 | 18.9 | 21.4 | 13% | 13% |
| 2006 | 22.8 | 23.2 | 2% | 2% |
| 2007 | 23.8 | 22.5 | -6% | 6% |
| 2008 | 26.6 | 22.8 | -14% | 14% |
| 2009 | 29.2 | 27.1 | -7% | 7% |
| 2010 | 27.2 | 26.1 | -4% | 4% |
| 2011 | 28.3 | 24.8 | -12% | 12% |
| 2012 | 22.9 | 23.8 | 4% | 4% |
| 2013 | 25.8 | 28.0 | 9% | 9% |
| 2014 | 28.0 | 29.1 | 4% | 4% |
|  |  | Average | 0.7% | 8.6% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 28.4 | 29.9 |
| 2016 | 29.1 | 30.6 |
| 2017 | 29.9 | 31.4 |
| 2018 | 30.6 | 32.1 |
| 2019 | 31.3 | 32.8 |
| 2020 | 32.1 | 33.6 |
| 2021 | 32.8 | 34.3 |
| 2022 | 33.5 | 35.0 |
| 2023 | 34.3 | 35.8 |
| 2024 | 35.0 | 36.5 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Fire Station | Callister | Theodore | 0.1 | 1/01/2016 | 90% |
| Residential | Chippindall | Theodore | 0.5 | 1/02/2015 | 90% |

#### Theodore Zone Substation Winter Forecast

Model Selection: Model with variables 3DayHDD, selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = 26.726 + 0.099 * 3DayHDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 26.72597 | 0.8035 | 33.262 | <2e-16 |
| 3DayHDD | 0.09915 | 0.0304 | 3.262 | 0.0027 |
| Residual standard error: 1.027 on 31 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.2555, Adjusted R-squared: 0.2315 |  |  |  |  |
| F-statistic: 10.64 on 1 and 31 DF, p-value: 0.002695 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Theodore Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 29.4 | 30.4 | 3% | 3% |
| 2005 | 29.6 | 28.9 | -2% | 2% |
| 2006 | 32.3 | 30.1 | -7% | 7% |
| 2007 | 32.0 | 30.3 | -5% | 5% |
| 2008 | 30.2 | 29.8 | -1% | 1% |
| 2009 | 29.3 | 29.0 | -1% | 1% |
| 2010 | 30.4 | 29.6 | -3% | 3% |
| 2011 | 29.4 | 29.2 | -1% | 1% |
| 2012 | 28.8 | 29.5 | 3% | 3% |
| 2013 | 28.8 | 29.9 | 4% | 4% |
| 2014 | 28.4 | 29.6 | 4% | 4% |
|  |  | Average | -0.5% | 3.1% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 29.0 | 30.1 |
| 2016 | 29.1 | 30.2 |
| 2017 | 29.1 | 30.2 |
| 2018 | 29.1 | 30.2 |
| 2019 | 29.1 | 30.2 |
| 2020 | 29.1 | 30.2 |
| 2021 | 29.1 | 30.2 |
| 2022 | 29.1 | 30.2 |
| 2023 | 29.1 | 30.2 |
| 2024 | 29.1 | 30.2 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Fire Station | Callister | Theodore | 0.1 | 1/01/2016 | 90% |
| Residential | Chippindall | Theodore | 0.5 | 1/02/2015 | 90% |

### Wanniassa Zone Substation

#### Wanniassa Zone Substation Summer Forecast

Model Selection: Model with variables Year and CDD selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = -1370.87 + 0.707 * Year + 2.09 * CDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | -1370.8745 | 403.6116 | -3.397 | 0.00213 |
| Year | 0.7071 | 0.2014 | 3.512 | 0.00158 |
| CDD | 2.0903 | 0.4496 | 4.649 | 7.83E-05 |
| Residual standard error: 3.41 on 27 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.6131, Adjusted R-squared: 0.5844 |  |  |  |  |
| F-statistic: 21.39 on 2 and 27 DF, p-value: 2.707e-06 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Wanniassa Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 61.5 | 66.4 | 8% | 8% |
| 2005 | 64.1 | 63.5 | -1% | 1% |
| 2006 | 69.5 | 71.0 | 2% | 2% |
| 2007 | 70.3 | 71.8 | 2% | 2% |
| 2008 | 67.8 | 67.1 | -1% | 1% |
| 2009 | 77.5 | 75.2 | -3% | 3% |
| 2010 | 73.7 | 74.1 | 1% | 1% |
| 2011 | 75.6 | 72.7 | -4% | 4% |
| 2012 | 62.9 | 67.4 | 7% | 7% |
| 2013 | 71.1 | 73.0 | 3% | 3% |
| 2014 | 71.2 | 73.4 | 3% | 3% |
|  |  | Average | 1.6% | 3.1% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 73.3 | 77.4 |
| 2016 | 74.0 | 78.1 |
| 2017 | 74.7 | 78.8 |
| 2018 | 75.4 | 79.5 |
| 2019 | 76.1 | 80.2 |
| 2020 | 76.8 | 80.9 |
| 2021 | 77.5 | 81.6 |
| 2022 | 78.2 | 82.4 |
| 2023 | 78.9 | 83.1 |
| 2024 | 79.6 | 83.8 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Domestic/commercial | Brookman | Wanniassa | 0.125 | 1/01/2016 | 90% |
| Commercial/Residential | Mugga | Wanniassa | 0.315 | 17/08/2016 | 50% |
| Commercial/Residential | Mugga | Wanniassa | 0.500 | 17/08/2014 | 100% |
| Commercial/Residential | Mugga | Wanniassa | 0.250 | 17/08/2014 | 100% |
| Commercial | Pitman Rowland | Wanniassa | 0.004 | 1/01/2016 | 90% |

#### Wanniassa Zone Substation Winter Forecast

Model Selection: Model with variables Year and HDD, selected based on stepwise procedures and checking against other statistical criteria. HDD is marginally significant.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = 2191.1 – 1.046 * Year – 0.5974 * MaxTemp

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 2191.0879 | 267.4076 | 8.194 | 3.80E-09 |
| Year | -1.0461 | 0.1332 | -7.852 | 9.20E-09 |
| MaxTemp | -0.5974 | 0.2195 | -2.721 | 0.0107 |
| Residual standard error: 2.403 on 30 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.7149, Adjusted R-squared: 0.6959 |  |  |  |  |
| F-statistic: 37.62 on 2 and 30 DF, p-value: 6.675e-09 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Wanniassa Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 89.5 | 90.0 | 1% | 1% |
| 2005 | 88.0 | 89.6 | 2% | 2% |
| 2006 | 94.7 | 89.2 | -6% | 6% |
| 2007 | 91.1 | 87.8 | -4% | 4% |
| 2008 | 85.2 | 84.4 | -1% | 1% |
| 2009 | 86.5 | 87.1 | 1% | 1% |
| 2010 | 85.6 | 83.2 | -3% | 3% |
| 2011 | 84.7 | 82.6 | -2% | 2% |
| 2012 | 79.9 | 79.8 | 0% | 0% |
| 2013 | 80.5 | 80.6 | 0% | 0% |
| 2014 | 79.1 | 80.1 | 1% | 1% |
|  |  | Average | -1.0% | 1.8% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 78.6 | 79.9 |
| 2016 | 77.9 | 79.1 |
| 2017 | 76.8 | 78.1 |
| 2018 | 75.8 | 77.1 |
| 2019 | 74.7 | 76.0 |
| 2020 | 73.7 | 75.0 |
| 2021 | 72.6 | 73.9 |
| 2022 | 71.6 | 72.9 |
| 2023 | 70.5 | 71.8 |
| 2024 | 69.5 | 70.8 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Domestic/commercial | Brookman | Wanniassa | 0.125 | 1/01/2016 | 90% |
| Commercial/Residential | Mugga | Wanniassa | 0.315 | 17/08/2016 | 50% |
| Commercial/Residential | Mugga | Wanniassa | 0.500 | 17/08/2014 | 100% |
| Commercial/Residential | Mugga | Wanniassa | 0.250 | 17/08/2014 | 100% |
| Commercial | Pitman Rowland | Wanniassa | 0.004 | 1/01/2016 | 90% |

### Woden Zone Substation

#### Woden Zone Substation Summer Forecast

Model Selection: Model with variable CDD selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = 59.187 + 2.197* CDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 59.1872 | 3.6483 | 16.223 | 9.05E-16 |
| CDD | 2.1970 | 0.3931 | 5.588 | 5.57E-06 |
| Residual standard error: 3.246 on 28 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.5273, Adjusted R-squared: 0.5104 |  |  |  |  |
| F-statistic: 31.23 on 1 and 28 DF, p-value: 5.573e-06 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Woden Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 75.7 | 80.5 | 6% | 6% |
| 2005 | 73.1 | 76.7 | 5% | 5% |
| 2006 | 82.5 | 83.8 | 2% | 2% |
| 2007 | 83.4 | 83.9 | 1% | 1% |
| 2008 | 80.9 | 78.2 | -3% | 3% |
| 2009 | 86.3 | 86.0 | 0% | 0% |
| 2010 | 84.5 | 84.8 | 0% | 0% |
| 2011 | 85.1 | 81.9 | -4% | 4% |
| 2012 | 77.5 | 69.3 | -11% | 11% |
| 2013 | 78.8 | 80.7 | 2% | 2% |
| 2014 | 77.9 | 80.4 | 3% | 3% |
|  |  | Average | 0.1% | 3.4% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Summer ending Feb | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 84.6 | 88.9 |
| 2016 | 87.0 | 91.3 |
| 2017 | 88.9 | 93.2 |
| 2018 | 88.9 | 93.2 |
| 2019 | 88.9 | 93.2 |
| 2020 | 83.5 | 87.8 |
| 2021 | 83.5 | 87.8 |
| 2022 | 83.5 | 87.8 |
| 2023 | 83.5 | 87.8 |
| 2024 | 83.5 | 87.8 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Commercial | Phiilip South | Woden | 0.157 | 28/02/2014 | 90% |
| Residential | Cotter | Woden | 0.675 | 1/02/2014 | 90% |
| Commercial | Garran | Woden | 1.400 | 31/05/2014 | 100% |
| Residential | Brookman | Woden | 0.050 | 1/04/2015 | 100% |
| Commercial & Residential | Bunbury | Woden | 0.100 | 1/07/2014 | 90% |
| Residential | Cotter | Woden | 0.085 | 31/03/2014 | 90% |
| Commercial | Carruthers | Woden | 0.003 | 31/05/2014 | 100% |
| Commercial | Cotter | Woden | 0.120 | 1/11/2014 | 90% |
| Residential | Cotter | Woden | 0.250 | 1/11/2014 | 90% |
| Community | Cotter | Woden | 0.373 | 8/12/2014 | 90% |
| Commercial | Streeton | Woden | 0.727 | 1/09/2015 | 70% |
| Community | Streeton | Woden | 0.475 | 1/09/2016 | 70% |
| Residential | Wilson | Woden | 0.038 | 20/05/2014 | 100% |
| Residential | Wilson | Woden | 0.058 | 1/01/2015 | 80% |
| Commercial | Wilson 2 | Woden | 0.523 | 20/12/2014 | 100% |
| Residential | Cotter | Woden | 0.165 | 1/02/2016 | 70% |
| Molonglo Development | Hilder | Woden | 1.424 | 1/02/2015 | 100% |
| Molonglo Development | Hilder & Streeton | Woden | 1.708 | 1/02/2016 | 100% |
| Molonglo Development | Streeton | Woden | 1.555 | 1/02/2017 | 100% |
| Molonglo Development | Hilder & Streeton | Woden | -5.400 | 1/7/2019 | 100% |

#### Woden Zone Substation Winter Forecast

Model Selection: Model with variables Year, MaxTemp and HDD selected based on stepwise procedures and checking against other statistical criteria.

Model/Forecast (before adding block loads):

- Graph showing historical demand, the 10% and 50% PoE 10-year forecasts, and back-fit showing what historical demand the model would forecast given 10% and 50% PoE weather conditions in the past.

Model Details:	Demand = 2017.19 – 0.97 * Year + 1.22 * HDD

| Model Coefficients |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Estimate | Std. Error | t value | Pr(>¦t¦) |
| (Intercept) | 2364.8091 | 344.3419 | 6.868 | 1.52E-07 |
| Year | -1.1366 | 0.1708 | -6.653 | 2.70E-07 |
| MaxTemp | -0.7107 | 0.2201 | -3.23 | 0.00307 |
| HDD | 0.6567 | 0.3474 | 1.89 | 0.06876 |
| Residual standard error: 3.04 on 29 degrees of freedom |  |  |  |  |
| Multiple R-squared: 0.7077, Adjusted R-squared: 0.6774 |  |  |  |  |
| F-statistic: 23.4 on 3 and 29 DF, p-value: 6.765e-08 |  |  |  |  |

The model is scrutinized to ensure that it is suited for the data. For e.g. diagnostic checking of residuals, normal Q-Q plots, leverage plots, VIF, and a number of other methods are used. Attached below are some diagnostic graphs supporting the model.

- Graph and statistics assessing the back-fit accuracy of the model. The back-fit forecast is compared to the single highest peak demand point from each year.

| Year | Woden Peak (MVA) | Back-fit using actual temp (MVA) | Deviation of Backfit from actual | Deviation Magnitude |
| --- | --- | --- | --- | --- |
| 2004 | 84.1 | 86.1 | 2% | 2% |
| 2005 | 80.6 | 84.9 | 5% | 5% |
| 2006 | 89.6 | 90.2 | 1% | 1% |
| 2007 | 88.2 | 87.5 | -1% | 1% |
| 2008 | 83.6 | 80.5 | -4% | 4% |
| 2009 | 92.9 | 88.0 | -5% | 5% |
| 2010 | 78.5 | 81.7 | 4% | 4% |
| 2011 | 79.9 | 80.9 | 1% | 1% |
| 2012 | 76.6 | 77.9 | 2% | 2% |
| 2013 | 75.8 | 78.2 | 3% | 3% |
| 2014 | 74.9 | 75.7 | 1% | 1% |
|  |  | Average | 0.9% | 2.7% |

Final Model/Forecast (including block loads):

- Graph and table showing the final forecast (incorporating potential future block loads).

| Final Forecast (Incorporating Block Loads) |  |  |
| --- | --- | --- |
| Winter Ending Aug | 50% PoE (in MVA) | 10% PoE (in MVA) |
| 2015 | 76.5 | 81.1 |
| 2016 | 77.7 | 82.3 |
| 2017 | 77.6 | 82.2 |
| 2018 | 76.5 | 81.1 |
| 2019 | 69.9 | 74.5 |
| 2020 | 68.8 | 73.4 |
| 2021 | 67.6 | 72.2 |
| 2022 | 66.5 | 71.1 |
| 2023 | 65.4 | 70.0 |
| 2024 | 64.2 | 68.8 |

- Graph used in reports/for presentation (incorporating potential future block loads)

Supporting Document: Block Load Data

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Brookman | Woden | 0.050 | 1/04/2015 | 100% |
| Commercial | Cotter | Woden | 0.120 | 1/11/2014 | 90% |
| Residential | Cotter | Woden | 0.250 | 1/11/2014 | 90% |
| Community | Cotter | Woden | 0.373 | 8/12/2014 | 90% |
| Commercial | Streeton | Woden | 0.727 | 1/09/2015 | 70% |
| Community | Streeton | Woden | 0.475 | 1/09/2016 | 70% |
| Residential | Wilson | Woden | 0.038 | 20/05/2014 | 100% |
| Residential | Wilson | Woden | 0.058 | 1/01/2015 | 80% |
| Commercial | Wilson 2 | Woden | 0.523 | 20/12/2014 | 100% |
| Residential | Cotter | Woden | 0.165 | 1/02/2016 | 70% |
| Molonglo Development | Hilder | Woden | 1.566 | 1/08/2015 | 100% |
| Molonglo Development | Hilder & Streeton | Woden | 1.7165 | 1/08/2016 | 100% |
| Molonglo Development | Streeton | Woden | 0.6925 | 1/08/2017 | 100% |
| Molonglo Development | Hilder & Streeton | Woden | -5.400 | 1/7/2019 | 100% |

## Block Loads Data

The way that block loads are accounted for are explained in the example below:

Summer – all block loads falling between 15 Jan 2015 and 15 Jan 2016 are included in the 2015 forecast.

Winter – all block loads falling between 15 July 2015 and 15 July 2016 are included in the 2015 forecast.

*Block loads that are “completed” before 15 Jan 2014 are not included in the summer forecasts, block loads that are “completed” before 15 July 2014 are not included in the winter forecasts.

All data on block (spot) loads are provided in the table below.  This data was extracted from the Block Loads Database:

\\JEEVES\ELECPROJMGM\Projects\Load forecast database\

“Proposed Electrical Load Forecast Database (50kVA+).xlsx”

Time of retrieval: 11:10am, 18 Nov 2014.

### Discrete Block Load Projects

| Development type | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply required date | Project probability |
| --- | --- | --- | --- | --- | --- |
| Residential | Baldwin | Belconnen | 0.02 | 1/10/2014 | 90% |
| Residential | Cameron South | Belconnen | 0.78 | 1/10/2014 | 100% |
| Commercial | Haydon | Belconnen | 0.003 | 31/05/2014 | 100% |
| Commercial | Swinden | Belconnen | 0.32 | 1/01/2016 | 100% |
| Community | Swinden | Belconnen | 0.22 | 15/09/2014 | 100% |
| Commercial | William Slim | Belconnen | 0.4 | 1/07/2015 | 100% |
| Commercial | Swinden | Belconnen | 0.19 | 1/09/2015 | 50% |
| Commercial | Latham 3 | Belconnen | 0.05 | 1/01/2016 | 100% |
| Residential | Braddon | CityEast | 0.25 | 1/09/2016 | 70% |
| Commercial | Aero Park | CityEast | 0.90 | 1/01/2016 | 80% |
| Commercial | Cooyong | CityEast | 0.65 | 15/08/2014 | 100% |
| Commercial/Residential | Ferdinand | CityEast | 1.30 | 1/01/2016 | 90% |
| Commercial/Residential | Haig Feeder | CityEast | 0.17 | 1/01/2016 | 90% |
| Commercial/Residential | Lonsdale | CityEast | 0.50 | 1/08/2014 | 100% |
| Commercial | Lonsdale | CityEast | 0.13 | 15/07/2014 | 100% |
| Comemrcial | Mackenzie | CityEast | 0.55 | 15/02/2015 | 50% |
| Greenfield (Small) | Mackenzie | CityEast | 0.26 | 15/03/2015 | 70% |
| Residential | Mackenzie | CityEast | 0.41 | 1/06/2015 | 70% |
| Commercial/Restaurant | Northbourne | CityEast | 0.10 | 1/01/2016 | 90% |
| Residential | Mackenzie | CityEast | 0.39 | 1/02/2015 | 100% |
| Commercial/Residential | Lonsdale | CityEast | 0.43 | 1/04/2014 | 100% |
| Commercial | Aero Park | CityEast | 1.50 | 1/06/2015 | 100% |
| Residential | Miller | Civic | 0.07 | 1/05/2014 | 90% |
| Commercial | Black Mountian | Civic | 0.005 | 31/05/2014 | 100% |
| Residential | Miller | Civic | 0.01 | 1/01/2016 | 90% |
| Residential | Miller | Civic | 0.07 | 30/12/2014 | 100% |
| Commercial | Gladstone | Fyshwick | 0.05 | 15/12/2014 | 90% |
| Commercial | Abattoir | Fyshwick | 0.15 | 3/03/2014 | 90% |
| Commercial | Abattoir | Fyshwick | 0.06 | 10/07/2014 | 90% |
| Temporary Supply | Abattoir | Fyshwick | 0.16 | 26/05/2014 | 100% |
| Commercial | Newcastle | Fyshwick | 0.0025 | 31/05/2014 | 100% |
| Commercial | Pialligo | Fyshwick | 0.75 | 1/06/2014 | 100% |
| Commercial | Newcastle & Abattoir | Fyshwick | 1.5 | 1/06/2015 | 100% |
| Commercial | Monaro | Gilmore | 0.07 | 15/04/2014 | 100% |
| Commercial | Tralee | Gilmore | 0.62 | 1/01/2016 | 100% |
| Commercial | Tralee | Gilmore | 0.3 | 1/11/2014 | 100% |
| Commercial | Tralee | Gilmore | 0.07 | 1/12/2014 | 90% |
| Commercial | Tralee | Gilmore | 0.06 | 10/10/2014 | 100% |
| Commercial | Boulevard North | GoldCreek | 0.19 | 12/05/2014 | 90% |
| Commercial | West 2 | GoldCreek | 0.08 | 28/02/2014 | 90% |
| Residential | Nona | GoldCreek | 0.22 | 1/02/2015 | 90% |
| Residential & Commercial | Gurrang | GoldCreek | 0.20 | 1/02/2015 | 90% |
| Rural Residential | Lander 2 | GoldCreek | 0.16 | 1/01/2016 | 90% |
| Residential | Meacham | GoldCreek | 0.15 | 1/01/2016 | 100% |
| Residential | Anthony Rolf | GoldCreek | 0.50 | 1/01/2015 | 100% |
| Commercial | West | GoldCreek | 0.23 | 1/08/2015 | 90% |
| Temporary Supply | Nona | GoldCreek | 0.11 | 15/06/2014 | 100% |
| Residential | Nona | GoldCreek | 0.16 | 1/01/2015 | 100% |
| Residential | Nona | GoldCreek | 0.10 | 1/06/2015 | 100% |
| Commercial/Residential | Gurrang | GoldCreek | 0.90 | 1/01/2016 | 90% |
| Commercial | Anthony Rolf | GoldCreek | 0.11 | 15/10/2014 | 90% |
| Commercial | Nona | GoldCreek | 1.00 | 1/06/2015 | 90% |
| Commercial | Maribyrnong 4 | GoldCreek | 0.09 | 1/01/2016 | 90% |
| Commercial | Tilyard Feeder | Latham | 0.23 | 1/02/2014 | 90% |
| Residential | Conley Feeder | Latham | 0.03 | 1/08/2014 | 90% |
| Community | Lhotsky Feeder | Latham | 0.07 | 1/02/2015 | 70% |
| Residential | Macrossan Feeder | Latham | 0.02 | 1/01/2016 | 90% |
| Residential | Mundaring | TelopeaPark | 0.26 | 1/03/2015 | 90% |
| Commercial | Mundaring | TelopeaPark | 0.05 | 1/03/2014 | 90% |
| Residential | Belmore 2 | TelopeaPark | 0.19 | 30/06/2014 | 100% |
| Commercial | Dairy South | TelopeaPark | 0.12 | 30/06/2015 | 90% |
| Residential | Jardine | TelopeaPark | 0.12 | 1/01/2016 | 90% |
| Residential | Mundarin | TelopeaPark | 0.45 | 1/01/2016 | 90% |
| Commercial / Residential | STURT | TelopeaPark | 0.18 | 1/01/2016 | 90% |
| Residential | Ovens | TelopeaPark | 0.41 | 1/01/2016 | 70% |
| Residential | Ovens | TelopeaPark | 0.31 | 1/01/2016 | 70% |
| Residential | Ovens | TelopeaPark | 0.13 | 1/01/2016 | 70% |
| Residential | Ovens | TelopeaPark | 0.41 | 1/01/2016 | 70% |
| Residential | Throsby | TelopeaPark | 0.45 | 10/04/2015 | 90% |
| Commercial / Residential | Young | TelopeaPark | 0.79 | 1/01/2016 | 100% |
| Commercial | Telopea Prak East | TelopeaPark | 0.11 | 1/01/2016 | 90% |
| Embassy | Empire 2 | TelopeaPark | 0.11 | 25/04/2015 | 70% |
| Fire Station | Callister | Theodore | 0.1 | 1/01/2016 | 90% |
| Residential | Chippindall | Theodore | 0.5 | 1/02/2015 | 90% |
| Commercial | Phiilip South | Woden | 0.157 | 28/02/2014 | 90% |
| Residential | Cotter | Woden | 0.675 | 1/02/2014 | 90% |
| Commercial | Garran | Woden | 1.400 | 31/05/2014 | 100% |
| Residential | Brookman | Woden | 0.050 | 1/04/2015 | 100% |
| Commercial & Residential | Bunbury | Woden | 0.100 | 1/07/2014 | 90% |
| Residential | Cotter | Woden | 0.085 | 31/03/2014 | 90% |
| Commercial | Carruthers | Woden | 0.003 | 31/05/2014 | 100% |
| Commercial | Cotter | Woden | 0.120 | 1/11/2014 | 90% |
| Residential | Cotter | Woden | 0.250 | 1/11/2014 | 90% |
| Community | Cotter | Woden | 0.373 | 8/12/2014 | 90% |
| Commercial | Streeton | Woden | 0.727 | 1/09/2015 | 70% |
| Community | Streeton | Woden | 0.475 | 1/09/2016 | 70% |
| Reasidential | Wilson | Woden | 0.038 | 20/05/2014 | 100% |
| Residential | Wilson | Woden | 0.058 | 1/01/2015 | 80% |
| Commercial | Wilson 2 | Woden | 0.523 | 20/12/2014 | 100% |
| Residential | Cotter | Woden | 0.165 | 1/02/2016 | 70% |
| Domestic/commercial | Brookman | Wanniassa | 0.125 | 1/01/2016 | 90% |
| Comemrcial/Residential | Mugga | Wanniassa | 0.315 | 17/08/2016 | 50% |
| Comemrcial/Residential | Mugga | Wanniassa | 0.500 | 17/08/2014 | 100% |

### Continuous Large Block Load Projects

#### Summer Block Load

| Project Name | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date |
| --- | --- | --- | --- | --- |
| Lawson South Stage 1 | Chuculba & Baldwin | Belconnen | 2.58 | 31/12/2015 |
| Lawson South Stage 1 | Maribyrnong | Belconnen | 2.58 | 31/12/2016 |
| Lawson South Stage 1 | Maribyrnong | Belconnen | 2.58 | 31/12/2017 |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 31/12/2016 |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 31/12/2017 |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 31/12/2018 |
| UC Hospital Expansion | NA | Belconnen | 3.00 | 31/12/2016 |
| Molonglo Development | Black Mth | Civic | 0.17 | 1/02/2017 |
| Molonglo Development | Black Mth | Civic | 1.63 | 1/02/2018 |
| Molonglo Development | Black Mth | Civic | 1.50 | 1/02/2019 |
| Molonglo Development | Black Mth | Civic | -3.20 | 1/7/2019 |
| West Belconnen development | NA | Latham | -5.00 | 1/07/2022 |
| Molonglo Development | Hilder | Woden | 1.42 | 1/02/2015 |
| Molonglo Development | Hilder & Streeton | Woden | 1.71 | 1/02/2016 |
| Molonglo Development | Streeton | Woden | 1.56 | 1/02/2017 |
| Molonglo Development | Hilder & Streeton | Woden | -5.40 | 1/7/2019 |

#### Winter Block Load

| Project Name | Supply source feeder | Supply source zone sub | Expected ADMD Increase (MVA) | Supply Required Date |
| --- | --- | --- | --- | --- |
| Lawson South Stage 1 | Chuculba & Baldwin | Belconnen | 2.58 | 30/06/2016 |
| Lawson South Stage 1 | Maribyrnong | Belconnen | 2.58 | 30/06/2017 |
| Lawson South Stage 1 | Maribyrnong | Belconnen | 2.58 | 31/12/2017 |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 30/06/2017 |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 30/06/2018 |
| Lawson South Stage 2 | NA | Belconnen | 5.20 | 31/12/2018 |
| UC Hospital Expansion | NA | Belconnen | 3.00 | 31/12/2016 |
| Molonglo Development | Black Mth | Civic | 0.99 | 1/08/2017 |
| Molonglo Development | Black Mth | Civic | 1.57 | 1/08/2018 |
| Molonglo Development | Black Mth | Civic | -2.55 | 1/07/2019 |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2015 |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2016 |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2017 |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2018 |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2019 |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2020 |
| West Belconnen development | NA | Latham | 1.00 | 1/07/2021 |
| West Belconnen development | NA | Latham | -5.00 | 1/07/2022 |
| Molonglo Development | Hilder | Woden | 1.57 | 1/08/2015 |
| Molonglo Development | Hilder & Streeton | Woden | 1.72 | 1/08/2016 |
| Molonglo Development | Streeton | Woden | 0.69 | 1/08/2017 |
| Molonglo Development | Hilder & Streeton | Woden | -5.40 | 1/07/2019 |

## Reconciliation between forecasts

This section shows the comparison of the top-down System demand forecast, with a bottom-up System demand forecast. The bottom-up forecast has been derived by summing the individual Zone Substation forecast, and taking loss factors and diversity factors into account.

The difference between the summer top-down and bottom-up forecasts is 4.8% in the first year and up to 9.4% by the end of the forecast period, while the difference in the winter forecast is 3.5% in the first year and up to 12.1% by the end of the forecast period.

### Loss Factors

The summer and winter system peaks were compared to the sum of the demand at each Zone Substation at the time of the System demand peaks. While complete data was not available for each year, this analysis showed that the losses on the ADD transmission network at the time of the system peak were in the range of 7 to 10 %. This may be different to the average loss factors calculated for other purpose.

### Diversity Factors

|  | Average Diversity Factor (load on the Zone Substation at the time of system peak demand, as a percentage of the Zone Substation peak demand) |  |
| --- | --- | --- |
| Zone | Summer | Winter |
| Angle Crossing | NA | NA |
| Belconnen | 99% | 100% |
| City East | 98% | 98% |
| Civic | 97% | 97% |
| Fyshwick | 94% | 56% |
| East Lake | NA | NA |
| Gilmore | 90% | 95% |
| Gold Creek | 83% | 95% |
| Latham | 82% | 97% |
| Telopea Park | 96% | 94% |
| Molonglo | NA | NA |
| Theodore | 75% | 96% |
| Wanniassa | 94% | 98% |
| West Belconnen | NA | NA |
| Woden | 97% | 99% |

### Summer Demand Forecast

|  | System Summer Peak Demand (MVA) |  |  | Deviation of Top-down forecast from Bottom-up System Forecast |
| --- | --- | --- | --- | --- |
| Year | Historical | Top-down Forecast | Bottom-up Forecast |  |
| 2004 | 577.4 |  |  |  |
| 2005 | 579.2 |  |  |  |
| 2006 | 648.2 |  |  |  |
| 2007 | 642.7 |  |  |  |
| 2008 | 623.5 |  |  |  |
| 2009 | 711.2 |  |  |  |
| 2010 | 681.5 |  |  |  |
| 2011 | 707.1 |  |  |  |
| 2012 | 555.0 |  |  |  |
| 2013 | 656.0 |  |  |  |
| 2014 | 634.9 |  |  |  |
| 2015 |  | 665.7 | 697.6 | 4.8% |
| 2016 |  | 672.8 | 717.5 | 6.6% |
| 2017 |  | 679.9 | 728.7 | 7.2% |
| 2018 |  | 687.2 | 739.1 | 7.6% |
| 2019 |  | 694.5 | 749.4 | 7.9% |
| 2020 |  | 702.0 | 758.3 | 8.0% |
| 2021 |  | 709.6 | 768.4 | 8.3% |
| 2022 |  | 717.3 | 778.6 | 8.5% |
| 2023 |  | 725.1 | 790.6 | 9.0% |
| 2024 |  | 733.0 | 801.9 | 9.4% |

### Winter Demand Forecast

|  | System Winter Peak Demand (MVA) |  |  | Deviation of Top-down forecast from Bottom-up System Forecast |
| --- | --- | --- | --- | --- |
| Year | Historical | Top-down Forecast | Bottom-up Forecast |  |
| 2004 | 627.6 |  |  |  |
| 2005 | 628.5 |  |  |  |
| 2006 | 677.0 |  |  |  |
| 2007 | 671.0 |  |  |  |
| 2008 | 636.6 |  |  |  |
| 2009 | 655.6 |  |  |  |
| 2010 | 645.0 |  |  |  |
| 2011 | 656.3 |  |  |  |
| 2012 | 626.3 |  |  |  |
| 2013 | 622.9 |  |  |  |
| 2014 | 623.5 |  |  |  |
| 2015 |  | 640.6 | 662.8 | 3.5% |
| 2016 |  | 640.6 | 673.5 | 5.1% |
| 2017 |  | 640.6 | 679.5 | 6.1% |
| 2018 |  | 640.6 | 685.0 | 6.9% |
| 2019 |  | 640.6 | 690.6 | 7.8% |
| 2020 |  | 640.6 | 695.9 | 8.6% |
| 2021 |  | 640.6 | 701.2 | 9.5% |
| 2022 |  | 640.6 | 707.0 | 10.4% |
| 2023 |  | 640.6 | 712.7 | 11.3% |
| 2024 |  | 640.6 | 718.3 | 12.1% |

## Updating the forecast model

To assist in future developments and updates of the forecast model, the following example shows how the Belconnen Zone Summer forecast can be replicated.

- Ensure data in \\Jeeves\AssetPerformance\AssetStrategy\Asset Strategy Analyst\Projects\Major Projects\Demand Data Analysis\Zone\Demand Forecast 2013\FORECAST\Data\DATA.xlsx is correct and up to date.

- Open \\Jeeves\AssetPerformance\AssetStrategy\Asset Strategy Analyst\Projects\Major Projects\Demand Data Analysis\Zone\Demand Forecast 2013\FORECAST\Code\Summer FINAL.R for the generic summer forecasting code.

- Change ZONEDEFINITION to “Belconnen”.

- Run all code.

- For model selection diagnostics, type >modelcomparison(). This will generate a .csv file in the \\Jeeves\AssetPerformance\AssetStrategy\Asset Strategy Analyst\Projects\Major Projects\Demand Data Analysis\Zone\Demand Forecast 2013\FORECAST\Diagnostics\ folder, and will allow you to compare models by R^2 adj, Cp, Pressp etc.

- For stepwise regression to determine which variables should stay in the model, type >stepwise.regression.F() and >stepwise.regression(). The first command is the preferred one (only variables above a certain cutoff gets to stay in the model), while the second command uses an AIC criterion.

- Once you determine that the significant variables (e.g. Year and CDD – corresponding to variables 1 and 3), type >FitBestModel(WhichVariables=c(1,3)). The function will run and generate all the graphs and model/forecast output for you.

- *Note that if you are making special changes to the Zone Substation, e.g. Civic Zone Substation where 1 year of data is missing, you will have to go through the program FitBestModel line by line and make the necessary changes manually rather than running the generic code. This said, some of the customized code has been saved for ease of replication. E.g. Fyshwick forecast can be replicated by following the above steps using the Fyshwick 2014 Summer.R file.

Dr Yanlin Shi currently works as lecturer at ANU School of Actuarial Studies, Applied Statistic and Finance and has a PHD in statistic and specialises in time series analysis and regression modelling.