{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Contents","Cover","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":2,"defined_names":97,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Contents","index":0,"n_rows":12,"n_cols":6,"rows_kept":12,"cut":false,"hidden":false,"merged":[[8,2,9,3],[2,1,2,10],[4,1,4,10]]}
[" "]
[]
[null,"Electricity Distribution Network Service Provider\nF-factor Reporting Template"]
[]
[null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]

{"sheet":"Cover","index":1,"n_rows":49,"n_cols":7,"rows_kept":49,"cut":false,"hidden":false,"merged":[[26,3,26,8],[28,3,28,8],[26,1,26,2],[31,3,31,5],[14,1,14,8],[16,1,16,8],[17,1,17,8],[21,1,21,8],[19,1,19,8],[10,1,11,8],[13,1,13,8],[48,2,48,6],[42,2,42,3],[42,4,42,7],[46,2,46,6],[47,2,47,6],[38,2,38,3],[38,4,38,7],[41,2,41,3],[41,4,41,7],[37,2,37,3],[37,4,37,7],[32,3,32,8],[30,3,30,8],[15,1,15,8]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Distribution Network Service Provider"]
[null,"Fire start report"]
[]
[null,"This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
[]
[null,"Colour coding of input sheets:"]
[null,"Dark blue = AER headings"]
[null,"Grey = AER instructions"]
[null,"Yellow = Input cells"]
[null,"Light orange = Automatically-generated cells"]
[]
[null,"Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
[null,"The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings."]
[null,"All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
[null,"DNSP:",null,"AusNet Services"]
[]
[null,"DNSP - trading name:"]
[]
[null,"DNSP - Australian business number: ",null,"91 064 651 118"]
[]
[null,"Reporting year:",null,"2019/20"]
[]
[]
[]
[]
[null,"Business address","Address",null,"Level 31, 2 Southbank Boulevard"]
[null,null,"Suburb",null,"Southbank"]
[null,null,null,"State","Victoria","Postcode",3006]
[]
[null,"Postal address","Address",null,"Locked Bag 14051 MCMC"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode",8001]
[]
[]
[null,"Contact name/s","Hawaii Ho"]
[null,"Contact phone/s","03 9695 6350"]
[null,"Contact email address/s","Hawaii.Ho@ausnetservices.com.au"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":14,"n_cols":15,"rows_kept":14,"cut":false,"hidden":false,"merged":[[12,2,12,3],[13,2,13,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3],[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[11,2,11,3]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"AusNet Services"},"IRU target:",{"$f":"IF(SUM(K6:O6)=0,\"\",SUM(K6:O6))","v":221.1},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!S38:S1993)=0,\"\",SUM('2. Individual fire start info'!S38:S1993))","v":200.89999999999989},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2019/20"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":303000.00000000151},null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 2: Summary of total fire starts by F factor Order definition",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,null,{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J2:$J5,K2:K5))","v":221.1},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J2:$J5,L2:L5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>M1),\"\",LOOKUP($B3,$J2:$J5,M2:M5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>N1),\"\",LOOKUP($B3,$J2:$J5,N2:N5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>O1),\"\",LOOKUP($B3,$J2:$J5,O2:O5))","v":""}]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause"]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1993,'1. F-Factor summary'!$B8)","v":0}]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1993,'1. F-Factor summary'!$B9)","v":23}]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1993,'1. F-Factor summary'!$B10)","v":10}]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1993,'1. F-Factor summary'!$B11)","v":4}]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1993,'1. F-Factor summary'!$B12)","v":6}]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1993,'1. F-Factor summary'!$B13)","v":121}]
[null,"Total",{"$f":"SUM(C8:C13)","v":164}]

{"sheet":"2. Individual fire start info","index":3,"n_rows":201,"n_cols":25,"rows_kept":201,"cut":false,"hidden":false,"merged":[[3,22,3,24],[4,22,4,24],[5,22,5,24],[7,1,7,21],[11,1,11,2],[9,1,9,21],[13,1,13,11],[22,1,22,21],[24,1,24,21],[14,1,14,20],[15,1,15,18],[16,1,16,18],[18,1,18,18],[21,1,21,18],[19,1,19,18],[23,1,23,18],[20,1,20,18],[17,1,17,18],[25,1,25,18],[27,1,27,20],[26,1,26,21],[35,19,35,21],[33,1,33,4],[35,2,35,10],[28,1,28,18],[29,1,29,18],[35,11,35,13],[35,14,35,17]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"AusNet Services"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2019/20"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by AusNet Services. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"AusNet Services must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Address of the property on which the incident occurred or closest to the incident"]
[null,"   (5) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the AusNet Services network"}]
[null,"   (7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (8) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council"]
[null,"   (12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website)"]
[null,{"$f":"\"   (14) \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\"'s record number for the incident\"","v":"   (14) AusNet Services's record number for the incident"}]
[null,"   (15) ESV's OSIRIS reference number for the incident"]
[null,"   (16) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 2: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,null,"Fire Type",null,null,"Risk Factors",null,null,null,"IRU \namount","Additional information"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","Address of incident 4","ID of \nnearest \nasset 5","ID of nearest \npolyphase \nline 6","Voltage of line in which \nfire start \noccurred 7","Network categorisation 8","Type of primary asset \ninvolved in fire start 9","Phase(s) of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","Location \narea 12","Location\nmultiplier","Fire \ndanger \nrating 13","Danger multiplier","Product of multipliers","DNSP record number 14","OSIRIS \n(ESV) reference \nnumber 15","Fault \ndescription 16"]
[{"$f":"COUNTA(C38:O38,Q38,T38:V38)","v":17},1,"2019-07-03T19:44:00",43649.822222222225,-38.038164149869196,145.25482027041301,"1 JEFFREY STREET, HAMPTON PARK VIC 3976",505164,"HPK23","Low voltage AC (<1kV)","URBAN"," - lamps (minor road)","single phase","Otherwise started by a distribution system","LBRA only",{"$f":"IF(O38=\"\",\"\",IF(O38=\"LBRA only\",0.2,IF(O38=\"HBRA only\",1,IF(O38=\"within electric line construction area\",19.8,IF(O38=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"NO FORECAST",{"$f":"IF(Q38=\"\",\"\",IF(Q38=\"No forecast\",0.1,IF(Q38=\"Low-moderate\",0.2,IF(Q38=\"High\",0.5,IF(Q38=\"Very high\",1,IF(Q38=\"Severe\",2,IF(Q38=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P38=\"\",R38=\"\"),\"\",IF(AND(O38=\"within electric line construction area\",Q38=\"No forecast\"),1,P38*R38))","v":2.0000000000000004E-2},"E0022303","20190708SPN_05","Street light on pole LIS505164 caught fire and burnt. Fire likely resulted from failed ignitor or PE Cell.",null,null,"Overhead conductors"]
[17,2,"2019-07-04T22:39:00",43650.943749999999,-37.645339990006498,144.97560099543901,"490 COOPER STREET, EPPING VIC 3076",5712445,"EPG33","Low voltage AC (<1kV)","URBAN"," - connection box","three phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,"E0022366","20190708SPN_04","Fuse box failure believed to be due to poor connections",null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[17,3,"2019-07-06T19:40:00",43652.819444444445,-38.672246011389099,146.692631001824,"15 VICTORIA STREET, PORT ALBERT VIC 3971",2624442,"FTR23","22kV AC","RURAL LONG"," - fuse (EDO fuse)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0022445","20190708SPN_02","Candled EDO HV Fuse",null,null," - overhead conductor (bare; all aluminium conductor)"]
[17,4,"2019-07-07T19:37:00",43653.817361111112,-36.338035824271898,146.30359303307401,"1 WARATAH DRIVE, WANGARATTA VIC 3677",5119925,"WN2","22kV AC","RURAL LONG"," - surge diverter","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0022450","20190708SPN_01","Caused by lightning",null,null," - overhead conductor (bare; copper)"]
[17,5,"2019-07-09T01:30:00",43655.0625,-37.948657989878399,145.48160498957103,"100 PATERNOSTER ROAD, COCKATOO VIC 3781",400246,"BGE12","22kV AC","RURAL SHORT"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,"E0022620","20190809SPN_02","Candled Boric Acid HV fuse",null,null," - overhead conductor (bare; steel)"]
[17,6,"2019-07-09T06:00:00",43655.25,-38.042915014149202,146.00924802221803,"560 MCDOUGAL ROAD, NEERIM SOUTH VIC 3831",2706750,"WGL24","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,"E0022509","20190710SPN_02","Boric Acid HV fuse has candled",null,null," - overhead conductor (ABC)"]
[17,7,"2019-07-10T22:42:00",43656.945833333331,-38.044079668633096,145.330408894599,"107 GOLF LINKS ROAD, BERWICK VIC 3806",2601658157,"CLN14","22kV AC","RURAL SHORT"," - switch (any other type)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0022644","20190809SPN_05","Birds nest found on manual gas switch. Flashover has occurred and damaged the supply side bushings of the switch. Switch replaced and animal proofing to be installed.",null,null," - overhead conductor (covered uninsulated)"]
[17,8,"2019-07-11T03:25:00",43657.142361111109,-37.761241015668098,145.35444898181998,"2 ANDERSON STREET, LILYDALE VIC 3140",1008057,"LDL12","22kV AC","URBAN"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0022634","20190809SPN_03","A Dead tree failed just above ground level where there was significant decay and the tip contacted the outside HV conductor where it smouldered for a while before it broke at the point of contact and ended up resting on the outer 2 phases of the LV. No evidence of ground fire. There was strong wind and heavy rain at the time of the incident. There was no visible evidence of fire on the assets, conductor or ground as a result of this incident.\n\nThe tree was outside the clearance space with the trunk located approx. 4m from the nearest conductor. The tree showed some limb damage but nothing was on site at the time of the investigation. The tree was last inspected on 16/01/17 and was not identified as hazardous at the time. However, the investigation has concluded the dead tree should have been identified by the Assessor as a hazard and he has now been made aware of this error.",null,null," - overhead conductor (insulated)"]
[17,9,"2019-07-12T23:31:00",43658.979861111111,-37.708946984955595,145.050984996588,"70 GRANGE BOULEVARD, BUNDOORA VIC 3083",906948,"WT9","Low voltage AC (<1kV)","URBAN"," - lamps (major road)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0022802","20190717SPN_01","250W HPS street light has failed and caught fire. Investigation concluded the fire originated at the terminal block within the luminaire as a result of an unknown failure.",null,null,"Service lines"]
[17,10,"2019-07-15T09:00:00",43661.375,-37.803663017186501,145.305726024666,"12 TENNYSON AVENUE, KILSYTH VIC 3137",1005921,"CYN13","22kV AC","URBAN"," - switch (disconnector/isolator)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0022832","20190717SPN_03","The centre phase bushing of the manual gas switch has failed resulting in fire. The fire was contained on the pole top and there was no evidence of ground fire.  The investigation was inconclusive and the exact cause of the bushing failure and subsequent fire is unknown at this time.",null,null," - overhead service conductor (residential)"]
[17,11,"2019-07-19T08:38:00",43665.359722222223,-37.846921038553802,145.22192947876601,"743 BORONIA ROAD, WANTIRNA VIC 3152",5625514,"BRA11","Low voltage AC (<1kV)","URBAN"," - lamps (major road)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0023220","20190722SPN_03","Investigation concluded that the igniter appears to have failed resulting in the street light  catching fire. No evidence of ground fire",null,null," - overhead service conductor (commercial / industrial)"]
[17,12,"2019-07-23T10:02:00",43669.418055555558,-37.894341018600095,145.41676002120701,"89 FAIRY DELL ROAD, MONBULK VIC 3793",1304731,"BGE24","22kV AC","RURAL SHORT"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,"E0023367","20190809SPN_04","Candled BA HV fuse. No evidence of ground fire",null,null," - overhead service conductor (subdivision / construction)"]
[17,13,"2019-07-28T19:00:00",43674.791666666664,-37.682927686957797,145.11423448270801,"257 PLENTY RIVER DRIVE, GREENSBOROUGH VIC 3088",5811828,"ELM31","Low voltage AC (<1kV)","URBAN"," - lamps (major road)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0023631","20190809SPN_06","A faulty igniter appears to be the likely cause for the luminaire failure and subsequent fire",null,null," - overhead service conductor (other)"]
[17,14,"2019-08-13T11:30:00",43690.479166666664,-37.931545982113299,145.55709499091802,"2904 GEMBROOK-LAUNCHING PLACE ROAD, GEMBROOK VIC 3783",416465,"OFR23","Low voltage AC (<1kV)","RURAL LONG"," - connection box","three phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,"E0024924","20190821SPN_05","LV fuse box on pole caught fire. A suspected low voltage loose service cable connection within the fused mains box causing it to fail and ignite as a result. The fire was contained within the box only and there was no damage to pole and no evidence of ground fire.",null,null," - underground service cable (residential)"]
[17,15,"2019-08-15T10:00:00",43692.416666666664,-37.816838929126398,145.32587696710701,"56-72 CANTERBURY ROAD, MONTROSE VIC 3765",1005239,"CYN21","22kV AC","URBAN"," - fuse (powder filled)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0025012","20190821SPN_06","Fuse appears to have been damaged, allowing water to enter the fuse element resulting in fuse candling.",null,null," - underground service cable (commercial / industrial)"]
[17,16,"2019-08-19T11:57:00",43696.497916666667,-38.399557610325502,145.53735094703401,"1395 BASS HIGHWAY, GRANTVILLE VIC 3984",2802989,"LLG13","Low voltage AC (<1kV)","RURAL SHORT"," - connection box","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,"E0025162","20190821SPN_07","A faults crew was called to a pole fire and, upon arrival, the crew found an FOLCB that had caught fire. No evidence of ground fire. The FOLCB was completely destroyed and it was not possible to determine the cause of the failure and subsequent fire due to the amount of damage. The FOLCB had melted and molten plastic fell to the ground but did not cause a ground fire as conditions were very wet.",null,null," - underground service cable (subdivision / construction)"]
[17,17,"2019-08-23T15:14:00",43700.634722222225,-38.509238984658793,145.29231701285002,"3 STRADBROKE CRESCENT, SURF BEACH VIC 3922",2809385,"WGI32","Low voltage AC (<1kV)","RURAL SHORT"," - lamps (major road)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,{"$f":"IF(OR(P54=\"\",R54=\"\"),\"\",IF(AND(O54=\"within electric line construction area\",Q54=\"No forecast\"),1,P54*R54))","v":2.0000000000000004E-2},"E0025373","20190917SPN_01","Upon arrival, the fault crew identified the ground at the base of the pole seemed to be smoking and there was a small burn mark on the ground at the base of the pole. The grass around the pole was brown. The ground was smouldering but there was no flame. The concrete pole was live when the fault crew arrived.\nFurther investigation identified that the connections at the street light had burnt and the neutral connection was burnt off in the junction box both as a result of corrosion. It appears the pole had become live as a result of the active conductor supplying the light in the junction box and the light bracket.",null,null," - underground service cable (other)"]
[17,18,"2019-08-30T18:30:00",43707.770833333336,-37.950190014217398,146.95182200672301,"459 MEWBURN PARK ROAD, MAFFRA VIC 3860",2515178,"MFA22","22kV AC","RURAL LONG"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0025785","20190903SPN_01","BA HV Fuse has candled. No evidence of ground fire or damage to pole. Candled BA HV fuse replaced with new and supply restored",null,null,"Underground cables"]
[17,19,"2019-09-04T06:30:00",43712.270833333336,-37.508153007655899,148.136521030371,"415 TIMBARRA ROAD, BUCHAN VIC 3885",1904854,"BDL41","12.7kV AC (SWER)","RURAL LONG"," - fuse (EDO fuse)","single wire earth return (SWER)","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,"E0025909","20190917SPN_04","Candled 5k EDO SWER Fuse",null,null," - underground cable"]
[17,20,"2019-09-04T08:40:00",43712.361111111109,-38.477938009397803,145.92748898146399,"29 BEGG STREET, LEONGATHA VIC 3953",2003532,"LGA23","22kV AC","RURAL LONG"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,"E0025906","20190917SPN_03","Candled 6k BA HV Fuse",null,null," - underground communications cable"]
[17,21,"2019-09-07T20:37:00",43715.859027777777,-38.511392018309998,145.29743300236302,"BRUCE AVENUE, SURF BEACH VIC 3922",2809410,"WGI32","22kV AC","RURAL SHORT"," - dropper / bridge","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0026059","20190917SPN_07","Pole fire reported on transformer pole. \nPole is a termination pole with a pole mounted transformer installed on the supply side of the pole. HV fuses were installed on the back of the pole with the centre phase connection between the fuse and the over head going over the top of the steel termination arm. \n\nUpon investigation, it appears that the centre phase dropper cable failed at the tail, coming to rest on the term arm. The line and substation fuses failed to operate and the dropper/crossarm continued to be back-fed through the transformer resulting in a pole top fire. Fire was contained at the pole top and did not make it to the ground as it was a particularly wet night.",null,null,"Poles"]
[17,22,"2019-09-11T06:35:00",43719.274305555555,-37.563457013218297,145.50393600634001,"1059 MYERS CREEK ROAD, TOOLANGI VIC 3777",1400989,"WYK24","22kV AC","RURAL SHORT"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within electric line construction area",19.8,"NO FORECAST",0.1,1,"E0026200","20190918SPN_01","6k BA HV fuse has candled",null,null," - pole (concrete)"]
[17,23,"2019-10-01T00:48:00",43739.033333333333,-37.934873975159199,145.59934099270299,"620 BEENAK EAST ROAD, GEMBROOK VIC 3783",417099,"OFR23","22kV AC","RURAL LONG"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,"E0027058","20191015SPN_01","Tree has failed at the rootball and fallen onto and bringing down the O/H HV conductors resulting in a ground fire. The tree in question was located 25m from the HV line and uprooted, falling perpendicular to and over the line. There were no externally visible signs of potential hazard so this failure could not have been predicted. There are thousands of similar trees adjacent to this spur, all in reasonably good condition. The span was last inspected on the 12th of June 2019 and last cleared on the 27th of September 2018.",null,null," - pole (steel)"]
[17,24,"2019-10-01T14:15:00",43739.59375,-36.147134001347602,146.943083008282,"WODONGA SALEYARDS, 120 WHYTES ROAD, BANDIANA VIC 3691",5209508,"WOTS25","22kV AC","RURAL SHORT"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,"E0027114","20191015SPN_02","Container lift operator had loaded a container on the Container Lift and was waiting for a truck to arrive to load it on. He had his lunch with him in the cabin of the container lift and decided to drive to where his car was parked in the shade to have lunch while he was waiting. He reversed the container lift along the internal roadway and came into contact with the overhead conductor. He heard a sparking noise initially followed by a loud bang and saw a flash out of the corner of his eye. He stopped the Container lift when he noticed conductors on the ground and spot fires in the direction he was travelling. He drove the Container lift forward about 6-10m away from the fallen power lines, exited the Container Lift with a chemical powder fire extinguisher and walked back to extinguish the fire before waiting for another worker and his supervisor to arrive.\n\nThey inspected the Container Lift and proceeded to drive it away to load the truck. They were not able to continue working though due having no power at the site to operate the weighbridge.\n\nThe Container lift had been moved and continued to be used after the incident and had a container slung under the yellow platform at the time of the incident. \n\nThere were flash marks visible on the mast of the Container Lift at a number of sites. As the Container lift had been moved, the height was simulated and the mast of the Contain Lift raised into the height they believed it to have been at the time of the incident. Highest flash marks were measures at 7.2m and the lowest at 6.5m.\n\nTwo phases of the three conductors had broken and fallen to the ground. The third remaining conductor had some discolouration from the flash but appeared okay. The height of the remaining conductor over the road was measured at 5.9m after the incident.\n\nUpon completion of repairs the conductors were measured at 7.9m above ground. There was no damage to the poles or insulators either side of the incident.",null,null," - pole (wood)"]
[17,25,"2019-10-06T13:08:00",43744.547222222223,-37.874080009051298,147.85838896825402,"705 METUNG ROAD, METUNG VIC 3904",1901172,"BDL6","22kV AC","RURAL SHORT"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0027380","20191010SPN_01","Conductor has broken midspan resulting in ground fire (approx 1m x 3m). Upon further investigation corrosion was identified on the conductor which is believed to have cause the conductor to break during high winds experienced at the time of failure.  Conductor repaired and supply restored. Follow up inspection organised to determine if corrosion present on the remaining O/H conductor.",null,null,"Crossarms"]
[17,26,"2019-10-07T09:18:00",43745.387499999997,-37.253832591830097,145.79701855659701,"10 BACK EILDON ROAD, THORNTON VIC 3712",4711025,"RUBA12","22kV AC","RURAL LONG"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0027390","20191008SPN_01","Fuse Candled: The top and bottom contact of the fuse carrier were still in place in the Unit. Fuses carrier had jammed closed and  failed to dislodge once fuse link had operated. There was no fire on the ground.",null,null," - crossarm (wood)"]
[17,27,"2019-10-07T22:25:00",43745.934027777781,-37.753261001041295,145.21221300414101,"36 HODSON ROAD, WARRANDYTE VIC 3113",1206025,"RWN31","Low voltage AC (<1kV)","RURAL SHORT"," - underground service cable (residential)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0027449","20191010SPN_02","2 x 4 wire services caught fire in conduit on pole and burnt to FOLCB.",null,null," - crossarm (steel)"]
[17,28,"2019-10-09T09:30:00",43747.395833333336,-37.851235993238298,148.039340988465,"PRINCES HWY, LAKE TYERS BEACH VIC 3909",1903088,"NLA34","22kV AC","RURAL SHORT"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0027565","20191010SPN_03","Candled HV Boric Acid Fuse",null,null," - crossarm (other)"]
[17,29,"2019-10-16T09:00:00",43754.375,-38.548599991008594,145.94384398220902,"18 KOONWARRA-INVERLOCH ROAD, KOONWARRA VIC 3954",2001276,"LGA14","22kV AC","RURAL LONG"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0028034","20191017SPN_01","It appears that a small branch (around 1m long) fell onto one phase of the HV and was gradually blown along the span resulting in the branch ending up approximately 160m from the nearest trees. The O/H conductors transpose from horizontal to vertical construction and, as the wires began to cross under one-another, the branch caused a phase to phase fault resulting in fuse candling when the fuse failed to operate correctly.\nNo failed hazard Trees found during onsite visit. Three small gum branches less than 1m long found laying on ground in paddock under line with burn marks located approximately 160m from the nearest tree and 70m from LIS2001314 but no evidence of ground fire.\nThis span was last inspected on 29/05/2019 with no hazardous trees identified and all outside clearance space.",null,null,"Overhead assets"]
[17,30,"2019-10-23T00:59:00",43761.040972222225,-38.533485979814095,146.59001299313499,"104 INGLES ROAD, DEVON NORTH VIC 3971",2624667,"FTR12","Low voltage AC (<1kV)","RURAL LONG"," - connection box","two phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0028467","20191024SPN_01","FOLCB burnt due to wildlife shorting to ground .",null,null," - capacity balancing units"]
[17,31,"2019-10-24T14:18:00",43762.595833333333,-38.527552984263501,145.44657398406002,"3170 BASS HIGHWAY, ANDERSON VIC 3995",2800755,"WGI23","22kV AC","RURAL SHORT"," - surge diverter","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,"E0028993","20191030SPN_01","A surge diverter has failed at Voltage Regulator site during REFCL stress testing resulting in ground fire which stopped at and was contained by the concrete bund. CFA attended site to extinguish the fire.  Damaged Voltage regulator removed from service and replaced with new. Surge diverters replaced and supply restored",null,null," - connector / termination"]
[17,32,"2019-10-24T18:42:00",43762.779166666667,-37.967689986563101,146.867164973466,"TAKUNUMA, 227 MCKINNONS ROAD, TINAMBA VIC 3859",2510389,"MFA22","22kV AC","RURAL LONG"," - fuse (EDO fuse)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,"E0028698","20191025SPN_01","Candled 6k EDO HV Fuse",null,null," - dropper / bridge"]
[17,33,"2019-10-25T17:18:00",43763.720833333333,-38.031899005799794,145.49317501118,"56 REYNOLDS ROAD, PAKENHAM VIC 3810",504298,"OFR23","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0028807","20191028SPN_02","Candled Boric Acid HV fuse",null,null," - guy wire"]
[17,34,"2019-10-27T17:00:00",43765.708333333336,-36.265687006722096,147.100157988321,"ENVYDALE, 96 HIBBERSON ROAD, HUON VIC 3695",5217174,"WOTS13","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0028829","20191029SPN_02","Candled 6k BA HV Fuse",null,null," - insulator tie wires / connections"]
[17,35,"2019-10-29T04:55:00",43767.204861111109,-37.802958014252397,145.344486981426,"CAMBRIDGE ROAD, MOOROOLBARK VIC 3138",1001092,"CYN33","22kV AC","URBAN"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0028907","20191029SPN_01","Candled 25E BA HV Fuse. No evidence of ground fire",null,null," - insulators"]
[17,36,"2019-11-01T15:42:00",43770.654166666667,-36.560030982786401,145.96608899095,"126 WALLER STREET, BENALLA VIC 3672",3903114,"BN4","22kV AC","URBAN"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"VERY HIGH",1,0.2,"E0029286","20191107SPN_01","Fault crew dispatched following feeder CB trip and, upon investigation, found a bird had contacted O/H HV conductors at the centre phase insulator on the pole, causing a flash over and starting a ground fire as it fell to ground. Fire self extinguished but Centre phase insulator damaged.",null,null," - tower"]
[17,37,"2019-11-04T22:42:00",43773.945833333331,-37.592467633678602,145.01534024730799,"145 BOUNDARY ROAD, WOLLERT VIC 3750",599306,"EPG13","22kV AC","RURAL SHORT"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0029369","20191107SPN_02","Most probable cuase is incorrect installation. No photos or failed equipment was available for detailed investigations to confirm the root cause.",null,null," - traction lines"]
[17,38,"2019-11-11T10:41:00",43780.445138888892,-38.497039017554201,145.25765400773301,"161 SMITHS BEACH ROAD, SMITHS BEACH VIC 3922",2808411,"PHI12","22kV AC","RURAL SHORT"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"HIGH",0.5,{"$f":"IF(OR(P75=\"\",R75=\"\"),\"\",IF(AND(O75=\"within electric line construction area\",Q75=\"No forecast\"),1,P75*R75))","v":0.1},"E0029949","20191111SPN_02","Candled HV BA Fuse on spur tee-off. No evidence of ground fire.",null,null,"Underground assets"]
[{"$f":"COUNTA(C76:O76,Q76,T76:V76)","v":17},39,"2019-11-21T14:30:00",43790.604166666664,-38.137974015108298,146.79341800227903,"ROSEDALE-HEYFIELD ROAD, ROSEDALE VIC 3847",2600780,"TGN41","22kV AC","RURAL LONG"," - surge diverter","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",{"$f":"IF(O76=\"\",\"\",IF(O76=\"LBRA only\",0.2,IF(O76=\"HBRA only\",1,IF(O76=\"within electric line construction area\",19.8,IF(O76=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"VERY HIGH",{"$f":"IF(Q76=\"\",\"\",IF(Q76=\"No forecast\",0.1,IF(Q76=\"Low-moderate\",0.2,IF(Q76=\"High\",0.5,IF(Q76=\"Very high\",1,IF(Q76=\"Severe\",2,IF(Q76=\"Extreme\",3.5,5)))))))","v":1},1,"E0030691","20191122SPN_04","Blown surge arrester on pole 2600780 and started a grass fire.",null,null," - LV pillar"]
[17,40,"2019-11-21T15:00:00",43790.625,-37.368617980005098,145.039526012301,"17 BADEN DRIVE, HEATHCOTE JUNCTION VIC 3758",912182,"KLO14","22kV AC","RURAL LONG"," - overhead conductor (bare; all aluminium conductor)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"SEVERE",2,9.1999999999999993,"E0030725","20191125SPN_02","Semi-mature swamp gum trunk failure (stem failure) in extreme winds\nmaking contact with conductors bringing one phase to ground. No obvious defects were\nidentifiable so failure could not have been predicted.",null,null," - services pit"]
[17,41,"2019-11-21T16:00:00",43790.666666666664,-37.802958014252397,145.344486981426,"342 CAMBRIDGE ROAD, MONTROSE VIC 3765",1001092,"CYN33","22kV AC","URBAN"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"VERY HIGH",1,1,"E0030712","20191125SPN_01","Private decayed tree branch outside of vegetation clearance space failed.",null,null,"Transformers"]
[17,42,"2019-11-21T18:21:00",43790.76458333333,-38.173481729357796,146.28710630992302,"63 NORTHERN AVENUE, NEWBOROUGH VIC 3825",2208258,"MOE13","22kV AC","RURAL SHORT"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"VERY HIGH",1,0.2,"E0030656","20191122SPN_01","Currently under investigation. Lightning appears to have struck pole",null,null," - transformer (pole mounted)"]
[17,43,"2019-11-21T18:38:00",43790.776388888888,-37.057056015148596,145.86027800721402,"MAINTONGOON ROAD, BONNIE DOON VIC 3720",3912765,"MSD2","22kV AC","RURAL LONG"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,"E0030651","20191122SPN_05","Tree on private property fell due to high winds. At the time of assessment Vegetation is outside the Minimum Clearance Space from any Bare Wire or HV/ABC conductor/s or Uninsulated Apparatus.",null,null," - transformer (kiosk mounted)"]
[17,44,"2019-11-21T20:23:00",43790.849305555559,-37.884597191111098,145.41999960344302,"Gerber Rd Monbulk VIC 3793",1320862,"BGE11","Low voltage AC (<1kV)","RURAL SHORT"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,"E0030655","20191122SPN_02","Ground fire started by lightning, not caused by network asset.",null,null," - transformer (ground outdoor mounted)"]
[17,45,"2019-11-22T23:33:00",43791.981249999997,-38.128673999464198,146.48589901697201,"125 TROVATELLO PLACE, TYERS VIC 3844",2626341,"TGN31","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0030737","20191205SPN_02","Candled HV Fuse",null,null," - transformer (indoor chamber mounted)"]
[17,46,"2019-11-25T05:16:00",43794.219444444447,-38.216431014232803,146.25760700186601,"2 DAPHNE DRIVE, MOE SOUTH VIC 3825",2202289,"MOE31","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0030753","20191125SPN_05","Candled HV Fuse",null,null," - transformer (any other type)"]
[17,47,"2019-11-26T17:28:00",43795.727777777778,-37.682715944726205,145.02264743132102,"4 MARJORY STREET, THOMASTOWN VIC 3074",909037,"TT5","22kV AC","URBAN"," - crossarm (wood)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0031292","20191127SPN_01","Cause of the fire was tracking on the centre phase insulator and as a result the wooden pole top and xarm had caught fire.",null,null," - measurement transformer (current transformer)"]
[17,48,"2019-11-28T09:42:00",43797.404166666667,-37.280628766274198,144.94407509718701,"45 WILLOWMAVIN ROAD, KILMORE VIC 3764",4716975,"KMS12","22kV AC","RURAL SHORT"," - surge diverter","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0031380","20191128SPN_01","Crow on line and shorted out LA on bypass",null,null," - measurement transformer (voltage transformer)"]
[17,49,"2019-11-29T20:40:00",43798.861111111109,-36.5704749829018,145.93198097630702,"LOT 1 FIRTH ROAD, BENALLA VIC 3672",3910727,"BN1","22kV AC","RURAL LONG"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,"E0031534","20191205SPN_03","Bird is believed to have contacted exposed HV assets on pole top causing flashover resulting in ground fire. CFA extinguished fire. No damage to assets",null,null," - measurement transformer (capacitive voltage transformer)"]
[17,50,"2019-11-30T01:09:00",43799.04791666667,-37.863946014499398,145.25250798956299,"67 LEWIS ROAD, WANTIRNA SOUTH VIC 3152",1218894,"BRA11","22kV AC","URBAN"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0031535","20191205SPN_04","Bird has contacted switch bushings resulting in pole top fire. No evidence of ground fire",null,null,"Fuses and switchgear"]
[17,51,"2019-12-01T22:24:00",43800.933333333334,-37.922174007303497,145.47561400696,"3 UPPER GRIEVE ROAD, AVONSLEIGH VIC 3782",420243,"BGE22","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0031542","20200107SPN_11","Candled fuse (fuse failure)",null,null," - fuse (boric acid)"]
[17,52,"2019-12-11T09:30:00",43810.395833333336,-36.788387997228597,145.96936301359599,"18 PEARCE ROAD, LIMA EAST VIC 3673",3908199,"BN6","Low voltage AC (<1kV)","RURAL LONG"," - connection box","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0032124","20191211SPN_01","Joint box failure",null,null," - fuse (EDO fuse)"]
[17,53,"2019-12-12T17:32:00",43811.730555555558,-37.7103455992699,145.05224349664999,"20 BARLOW RISE, BUNDOORA VIC 3083",5676481,"WT9","Low voltage AC (<1kV)","URBAN"," - LV pillar","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0032323","20200107SPN_09","Impact from vehicle causing LV pillar to catch fire.",null,null," - fuse (Fault Tamer)"]
[17,54,"2019-12-16T07:02:00",43815.293055555558,-37.998116184166193,145.22788849757401,"26 CLAREDALE ROAD, DANDENONG VIC 3175",524123,"ERTS-HPK 66kV","66kV AC","N/A"," - pole (wood)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0032581","20200107SPN_10","Tracking activity at top of pole likely due to pollution/dust on centre phase disks/eyebolt causing top of pole to smoulder/burn.",null,null," - fuse (powder filled)"]
[17,55,"2019-12-16T15:13:00",43815.634027777778,-38.084574980348698,145.49396601376699,"60 BALD HILL ROAD, PAKENHAM VIC 3810",500411,"PHM21","Low voltage AC (<1kV)","URBAN"," - connection box","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0032562","20200107SPN_07","Poor connection (hot joint) resulting in LV fault and overheating of fuse unit.",null,null," - fuse (any other type)"]
[17,56,"2019-12-16T21:46:00",43815.906944444447,-38.122538021198196,147.08117401085403,"1 STEVENS STREET, SALE VIC 3850",2503175,"SLE31","66kV AC","RURAL LONG"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0032580","20200107SPN_05","Bird (pelican) few into line.",null,null," - circuit breaker"]
[17,57,"2019-12-18T13:42:00",43817.570833333331,-36.114293000048498,146.89519898132502,"30 HOVELL STREET, WODONGA VIC 3690",5204893,"WO14","Low voltage AC (<1kV)","URBAN"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"VERY HIGH",1,0.2,"E0032720","20191220SPN_02","truck hit pole, LV conductor to ground, confirmed HVI",null,null," - switch (disconnector/isolator)"]
[17,58,"2019-12-19T14:30:00",43818.604166666664,-37.694779496945898,145.80323803287001,"1 OLD WARBURTON ROAD, WARBURTON VIC 3799",1408905,"WYK13","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0032876","20191220SPN_01","Domino effect resulting in tree contacting conductors. The first tree to fail was a dead stag approx. 25 mts from line. The tree has fallen on a 15-20 degree angle towards the line. The tree has fallen into a mature wattle which has failed in the ground due to the impact. The wattle has then hit a tall juvenile mountain ash 9 approx. 250mm dbh causing it to snap at the ground. This tree was 20 mts from the line and has fallen straight across the conductors.",null,null," - switch (earth)"]
[17,59,"2019-12-19T16:10:00",43818.673611111109,-37.593100212602401,145.24260579713101,"240 HILDEBRAND ROAD, COTTLES BRIDGE VIC 3099",919192,"DRN23","12.7kV AC (SWER)","RURAL LONG"," - fuse (boric acid)","single wire earth return (SWER)","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0032873","20200107SPN_06","HV Candled Fuse at Sub",null,null," - switch (FuseSaver)"]
[17,60,"2019-12-22T13:54:00",43821.57916666667,-37.827385133071999,145.24324661958102,"70 HEATHMONT ROAD, HEATHMONT VIC 3135",1220862,"RWT22","22kV AC","URBAN"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,"E0033011","20200107SPN_02","25meter tall gumtree located on council road side or Metrail land approximately 16 meters east of pole # 12220863 fell on to 66/22kV overhead conductors on pole # 12220863 causing a conductor tie to break and tree branch to ignite, the fire was contained within the touching branch and did not spread or cause a ground fire .",null,null," - switch (any other type)"]
[17,61,"2019-12-23T01:56:00",43822.080555555556,-37.084593004306001,148.26032497623601,"250 SNOWY RIVER ROAD, WULGULMERANG EAST VIC 3885",1904373,"BDL41","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0033016","20200107SPN_04","12K BA fuse candled",null,null,"SCADA, network control and protection systems"]
[17,62,"2019-12-24T18:25:00",43823.767361111109,-36.624453022844193,146.402135993775,"3202 WANGARATTA-WHITFIELD ROAD, EDI VIC 3678",5101611,"WN5","22kV AC","RURAL LONG"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,"E0033079","20200107SPN_03","large public tree came down on HV conductors at 2 greta rd Wangaratta. crew cut tree clear of conductors. there was no damage to conductors and they did not hit the ground. WN5 CB tripped.\nCFA called to extinguish small grass fire. crew restored power",null,null," - audio frequency load controller (AFLC)"]
[17,63,"2019-12-25T23:00:00",43824.958333333336,-38.188977014351003,146.561026982577,"3 NEFERTITI COURT, TRARALGON VIC 3844",2605832,"TGN31","22kV AC","RURAL LONG"," - surge diverter","three phase","Otherwise started by a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,"E0033088","20200106SPN_01","The cause of the incident was a loose connection on the cable head.",null,null," - arc suppresion coil"]
[17,64,"2019-12-26T22:59:22",43825.95789351852,-36.589768986898797,146.69794898028701,"453 BUFFALO RIVER ROAD, BUFFALO RIVER VIC 3737",4505857,"MYT22","22kV AC","RURAL SHORT"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,"E0033084","20200205SPN_05","Eucalyptus Camaldulensis has failed with a combination of bifurcation and drought conditions. Tree was 11 meters from the conductors and wind was around 20-30 km hr gusting",null,null," - automatic circuit recloser (ACR)"]
[17,65,"2019-12-27T14:30:00",43826.604166666664,-38.270771999474199,146.43342002841402,"340 TRAMWAY ROAD, HAZELWOOD NORTH VIC 3840",2616413,"MWL24","22kV AC","RURAL SHORT"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0033097","20200106SPN_02","bird contacted conductor",null,null," - communications linear assets"]
[17,66,"2019-12-27T14:30:00",43826.604166666664,-38.254348014345702,146.42349297633902,"240 MONASH WAY, MORWELL VIC 3840",2626406,"MWL24","22kV AC","RURAL SHORT"," - underground cable","three phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0033567","20200113SPN_01","dead bird found on adjacent pole. Under investigation.",null,null," - communications network assets"]
[17,67,"2019-12-29T13:30:00",43828.5625,-37.800268010682899,145.29556702585199,"363-365 MT DANDENONG ROAD, CROYDON VIC 3136",1003440,"CYN33","22kV AC","URBAN"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"VERY HIGH",1,0.2,"E0033113","20200106SPN_06","A thin branch snapped and fell towards the HV, possible HV/LV Contact, or LV Multiphase Contact which ignited the branch which fell to the ground, but did not start any fires at all besides burning itself slightly, as per photos.",null,null," - communications site infrastructure"]
[17,68,"2019-12-30T17:09:00",43829.714583333334,-37.9684470004849,146.94051098236901,"5667 TRARALGON-MAFFRA ROAD, TINAMBA VIC 3859",2513225,"MFA22","22kV AC","RURAL LONG"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"EXTREME",3.5,0.70000000000000007,"E0033124","20200106SPN_05","Tractor made contact with HV resulting in damage to powerline.",null,null," - field devices"]
[17,69,"2019-12-31T01:02:00",43830.043055555558,-37.637431985029899,145.193929007907,"4 ARTHURS CREEK ROAD, HURSTBRIDGE VIC 3099",925795,"DRN23","22kV AC","RURAL LONG"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0033126","20200106SPN_04","dead possum found on ACR pole",null,null," - local network wiring assets"]
[17,70,"2020-01-01T07:49:00",43831.325694444444,-38.4533449936511,145.99397398842601,"19 CRIGHTONS ROAD, KOOROOMAN VIC 3953",2008257,"LGA13","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,{"$f":"IF(OR(P107=\"\",R107=\"\"),\"\",IF(AND(O107=\"within electric line construction area\",Q107=\"No forecast\"),1,P107*R107))","v":0.5},"E0033147","20200109SPN_03","Candled HV Fuse",null,null," - master station assets"]
[17,71,"2020-01-02T15:54:00",43832.662499999999,-38.4121890217885,145.80823499373901,"305 KORUMBURRA-BENA ROAD, KORUMBURRA VIC 3950",2009391,"LGA24","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0033162","20200110SPN_01","Lightning at pole.",null,null," - neutral earthing resistor"]
[17,72,"2020-01-04T00:33:00",43834.022916666669,-37.735080988207095,145.22113801631602,"246 RESEARCH-WARRANDYTE ROAD, NORTH WARRANDYTE VIC 3113",1206694,"RWN34","22kV AC","RURAL SHORT"," - pole (concrete)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within electric line construction area",19.8,"HIGH",0.5,9.9,"E0033193","20200109SPN_02","Wildlife (possum) came into contact with exposed earth flag bolt on pole top switch and fell onto garden bed covered in wood chips/leaves starting a small grass fire.",null,null," - oil-filled circuit recloser (OCR)"]
[17,73,"2020-01-04T23:31:00",43834.979861111111,-38.589982988440902,146.14476702257301,"37 PEACHES ROAD, FOSTER NORTH VIC 3960",2027084,"LGA13","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"VERY HIGH",1,1,"E0033195","20200109SPN_04","cause lightning",null,null," - rapid earth fault current limiter (REFCL)"]
[17,74,"2020-01-05T13:19:00",43835.554861111108,-37.769271019229599,145.28870197858902,"1 LYONS ROAD, CROYDON NORTH VIC 3136",1217188,"CPK11","22kV AC","URBAN"," - pole (wood)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0033202","20200108SPN_05","Pole burnt 75% through at kingbolt due to dirt and water tracking and leaking electrical current over insulator through damp pole to ground.",null,null," - surge diverter"]
[17,75,"2020-01-05T17:32:00",43835.730555555558,-37.111045005052496,145.983836013998,"WINDY RIDGE, 340 CAMPAGNOLOS ROAD, MANSFIELD VIC 3722",3913642,"MSD2","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0033207","20200108SPN_04","Candled fuse.",null,null," - voltage regulator"]
[17,76,"2020-01-05T19:45:00",43835.822916666664,-37.868921991043699,147.99636701548101,"1 ONEILLS ROAD, LAKES ENTRANCE VIC 3909",1902142,"BDL41","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0033208","20200108SPN_03","Candled fuse.",null,null,"Public lighting"]
[17,77,"2020-01-07T09:38:00",43837.401388888888,-38.216239983116701,146.058257018159,"160 Loch St, Yarragon VIC 3823, Australia",2203214,"MOE22","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0033319","20200107SPN_08","HV fuse candled due to possum.",null,null," - brackets (major road)"]
[17,78,"2020-01-07T20:10:00",43837.840277777781,-37.691213289458396,145.112019126283,"27 CARBORA DALE, GREENSBOROUGH VIC 3088",5806765,"ELM31","Low voltage AC (<1kV)","URBAN"," - LV pillar","three phase","Otherwise started by a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,"E0033386","20200108SPN_02","Cable joint on service cable failed.",null,null," - brackets (minor road)"]
[17,79,"2020-01-14T16:00:00",43844.666666666664,-37.672826888851006,145.001789173936,"248 EDGARS ROAD, THOMASTOWN VIC 3074",908987,"TT9","22kV AC","URBAN"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,"E0033874","20200115SPN_01","Silver tape from a balloon on HV  found onsite as suspect to cause the fire at pole# 908987.",null,null," - lamps (major road)"]
[17,80,"2020-01-15T19:25:00",43845.809027777781,-37.924683016075299,145.51170297500101,"46 MOUNTAIN ROAD, COCKATOO VIC 3781",420544,"BGE22","Low voltage AC (<1kV)","RURAL SHORT"," - dropper / bridge","single phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0033974","20200116SPN_01","Lightning hit substation pole. blue phase lv leads blown off, LV N  down the pole as been on fire.  6 - 8 inches",null,null," - lamps (minor road)"]
[{"$f":"COUNTA(C118:O118,Q118,T118:V118)","v":17},81,"2020-01-16T23:02:00",43846.959722222222,-37.368878498088492,145.353674976549,"959 BREAK ODAY ROAD, GLENBURN VIC 3717",1401202,"KLK11","12.7kV AC (SWER)","RURAL SHORT"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within electric line construction area",19.8,"VERY HIGH",1,19.8,"E0034058","20200117SPN_04","Large tree branch fell on SWER conductor, conductor down and caused grass fire.",null,null," - luminaires (major road)"]
[17,82,"2020-01-17T14:33:00",43847.606249999997,-37.853866078131894,147.99466851809302,"5 ODONNELL DRIVE, LAKES ENTRANCE VIC 3909",5626658,"BDL41","22kV AC","RURAL LONG"," - transformer (kiosk mounted)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0034119","20200117SPN_06","Findings by Crew \nSmall fire inside the Kiosk at the LV Bush end \nIt appears the grass has grown up into the LV bus \nMainly Smoke damage and little scarring of the LV weber strip \nKiosk checked and restored",null,null," - luminaires (minor road)"]
[17,83,"2020-01-19T06:24:00",43849.26666666667,-37.813406001115901,145.36138797116399,"1048 MOUNT DANDENONG TOURIST ROAD, MONTROSE VIC 3765",1001438,"CYN33","Low voltage AC (<1kV)","URBAN"," - pole (concrete)","single phase","Otherwise started by a distribution system","within electric line construction area",19.8,"LOW-MODERATE",0.2,3.9600000000000004,"E0034137","20200121SPN_07","Currently under investigation. Aluminium lug at the Neutral lead on the TX melted falling to the ground was the suspected cause of the small grass fire at the base of pole. This is consistent with the scorch marks found at the pole base. Possible overload on the TX due to number of customers connected.",null,null," - poles / columns (major road)"]
[17,84,"2020-01-19T15:59:00",43849.665972222225,-38.478121987327803,146.54687999074503,"1 WHITELAWS TRACK, DEVON NORTH VIC 3971",2621400,"FTR12","22kV AC","RURAL LONG"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0034139","20200121SPN_06","Candled fuse due to internal degradation.",null,null," - poles / columns (minor road)"]
[17,85,"2020-01-19T19:45:00",43849.822916666664,-37.8085923723999,147.64782254908602,"125 GREAT ALPINE ROAD, LUCKNOW VIC 3875",5830050,"BDL ZSS","22kV AC","RURAL SHORT"," - fuse (powder filled)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0034141","20200121SPN_04","Suspected cause was electrical tracking.",null,null,"Other "]
[17,86,"2020-01-20T08:51:00",43850.368750000001,-38.492238309501502,145.99349394521701,"30 Christoffersens Rd, Nerrena VIC 3953, Australia",2001124,"LGA14","12.7kV AC (SWER)","RURAL LONG"," - fuse (EDO fuse)","single wire earth return (SWER)","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0034155","20200121SPN_03","Suspected lightning/storm impact.",null,null," - connection box"]
[17,87,"2020-01-20T20:35:00",43850.857638888891,-37.836396081715797,145.36028695979701,"32 Hume Ln, Mount Dandenong VIC 3767, Australia",1304263,"MDG1","6.6kV AC","RURAL SHORT"," - overhead conductor (ABC)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within electric line construction area",19.8,"LOW-MODERATE",0.2,3.9600000000000004,"E0034250","20200121SPN_01","Fallen tree due to strong winds and heavy rain.",null,null," - earth / earthing"]
[17,88,"2020-01-21T09:50:00",43851.409722222219,-36.892835387195795,147.70419559961502,"2630 BENAMBRA-CORRYONG ROAD, BENAMBRA VIC 3900",1606823,"BDL8","12.7kV AC (SWER)","RURAL LONG"," - fuse (boric acid)","single wire earth return (SWER)","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0034345","20200123SPN_01","CANDLED FUSE"]
[17,89,"2020-01-21T14:52:00",43851.619444444441,-36.213167983587802,147.869307006414,"27A GREENWATTLE GAP ROAD, CORRYONG VIC 3707",5212236,"WOTS24","22kV AC","RURAL LONG"," - fuse (EDO fuse)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0034333","20200121SPN_08","Fuse hung up. No burn marks on fuse, pole or ground"]
[17,90,"2020-01-22T05:21:00",43852.222916666666,-38.184565023919099,146.13012998702601,"409 NORTH CANAL ROAD, TRAFALGAR VIC 3824",2202815,"MOE22","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0034355","20200123SPN_02","Fuse Candled.",null,null,"Extra low voltage AC (<50V)"]
[17,91,"2020-01-22T15:04:00",43852.62777777778,-37.726043988832195,145.13344799036199,"36 KIRWANA GROVE, MONTMORENCY VIC 3094",900363,"ELM34","Low voltage AC (<1kV)","URBAN"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"SEVERE",2,0.4,"E0034432","20200123SPN_04","Tree branch falling onto LV conductors.",null,null,"Low voltage AC (<1kV)"]
[17,92,"2020-01-23T08:36:00",43853.35833333333,-37.813505998122601,147.70864001273102,"160 LANES ROAD, NICHOLSON VIC 3882",596312,"BDL41","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0034451","20200123SPN_03","Candled fuse.",null,null,"2.2kV AC"]
[17,93,"2020-01-23T11:32:00",43853.480555555558,-37.100666961329694,148.618167120127,"2395 MCKILLOPS ROAD, TUBBUT VIC 3888",5767736,"BM8B31","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0034534","20200124SPN_01","Dead pine tree bringing HV conductor to ground.",null,null,"6.6kV AC"]
[17,94,"2020-01-24T13:00:00",43854.541666666664,-38.174775004600299,146.13371801942401,"141 YULUNGAH ROAD, TRAFALGAR VIC 3824",2202060,"MOE22","22kV AC","RURAL LONG"," - transformer (pole mounted)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0035483","20200204SPN_03","Transformer hit by lightning.",null,null,"11kV AC"]
[17,95,"2020-01-25T13:59:00",43855.582638888889,-37.5834280171903,145.38969099199801,"190 HUNTS LANE, STEELS CREEK VIC 3775",1006993,"CPK12","22kV AC","RURAL SHORT"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0034608","20200128SPN_03","Candled BA fuse due to internal degradation.",null,null,"12.7kV AC (SWER)"]
[17,96,"2020-01-27T13:04:00",43857.544444444444,-38.830217978976897,146.131518976096,"31 ENNISVALE AVENUE, SANDY POINT VIC 3959",2021773,"FTR21","Low voltage AC (<1kV)","RURAL LONG"," - connection box","two phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0034629","20200128SPN_02","Plausible cause is a combination of corroded connection that resulted in an overheated onnection.",null,null,"22kV AC"]
[17,97,"2020-01-27T13:27:00",43857.560416666667,-37.694975014676004,148.39014702273602,"69 BIRKINS ROAD, BETE BOLONG VIC 3888",1906294,"NLA32","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0034630","20200128SPN_01","Candled fuse due to internal degradation.",null,null,"33kV AC"]
[17,98,"2020-01-30T05:22:00",43860.223611111112,-37.8342049802418,145.240600033633,"84 CUTHBERT STREET, HEATHMONT VIC 3135",1220505,"RWT15","Low voltage AC (<1kV)","URBAN"," - connection box","three phase","Otherwise started by a distribution system","LBRA only",0.2,"VERY HIGH",1,0.2,"E0034823","20200130SPN_02","FOLCB failed from possible loose connection causing box to melt and hot plastic falling on the ground.",null,null,"66kV AC"]
[17,99,"2020-01-31T20:22:00",43861.848611111112,-37.570239015804603,145.17827200121999,"1135 ARTHURS CREEK ROAD, ARTHURS CREEK VIC 3099",5637993,"DRN14","22kV AC","RURAL SHORT"," - overhead conductor (ABC)","three phase","Otherwise started by a distribution system","HBRA only",1,"SEVERE",2,2,"E0035165","20200202SPN_02","Extreme storms and weather related event.",null,null,"132kV AC"]
[17,100,"2020-01-31T21:47:00",43861.907638888886,-37.738101989356402,145.22096602174801,"104 BRACKENBURY STREET, WARRANDYTE VIC 3113",1206322,"RWN34","Low voltage AC (<1kV)","RURAL SHORT"," - overhead conductor (ABC)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"SEVERE",2,9.1999999999999993,"E0035161","20200202SPN_01","Failed ABC IPC connector.",null,null,"220kV AC"]
[17,101,"2020-02-01T02:46:00",43862.115277777775,-38.3658159922933,145.67040900609899,"6525 SOUTH GIPPSLAND HIGHWAY, LOCH VIC 3945",2000595,"LLG12","22kV AC","RURAL SHORT"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0035163","20200202SPN_03","Plausible cuases are age and humidity.",null,null,"330kV AC"]
[17,102,"2020-02-01T15:16:00",43862.636111111111,-36.236621989053198,147.65126698129001,"170 LUCYVALE ROAD, BERRINGAMA VIC 3691",5216793,"WOTS24","22kV AC","RURAL LONG"," - overhead conductor (bare; aluminium core steel reinforced)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,{"$f":"IF(OR(P139=\"\",R139=\"\"),\"\",IF(AND(O139=\"within electric line construction area\",Q139=\"No forecast\"),1,P139*R139))","v":4.5999999999999996},"E0035167","20200202SPN_04","The root cause was fallen tree bringing down conductors.",null,null,"500kV AC"]
[{"$f":"COUNTA(C140:O140,Q140,T140:V140)","v":17},103,"2020-02-01T19:47:00",43862.824305555558,-36.574250012439101,145.960468005406,"232 MANSFIELD ROAD, BENALLA VIC 3672",3906619,"BN-MSD 66kV","66kV AC","N/A"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O140=\"\",\"\",IF(O140=\"LBRA only\",0.2,IF(O140=\"HBRA only\",1,IF(O140=\"within electric line construction area\",19.8,IF(O140=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"VERY HIGH",{"$f":"IF(Q140=\"\",\"\",IF(Q140=\"No forecast\",0.1,IF(Q140=\"Low-moderate\",0.2,IF(Q140=\"High\",0.5,IF(Q140=\"Very high\",1,IF(Q140=\"Severe\",2,IF(Q140=\"Extreme\",3.5,5)))))))","v":1},4.5999999999999996,"E0035168","20200303SPN_01","Fallen tree limb as a result of stroms. Refer to attached site photos.",null,null,"Extra low voltage DC (<120V ripple free)"]
[17,104,"2020-02-03T10:32:00",43864.438888888886,-38.548450020983097,146.71454098092502,"366 SOUTH GIPPSLAND HIGHWAY, YARRAM VIC 3971",2612575,"FTR23","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0035242","20200203SPN_02","Plausible cause is combination of age and condition.",null,null,"Low voltage DC (<1.5kV)"]
[17,105,"2020-02-06T13:28:00",43867.561111111114,-37.539601991441998,148.93619302575001,"596 COMBIENBAR ROAD, CLUB TERRACE VIC 3889",1905411,"CNR3","22kV AC","RURAL SHORT"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0035729","20200206SPN_02","Third party tree clearers dropped tree on live HV conductor.",null,null,"600V DC"]
[17,106,"2020-02-07T14:40:00",43868.611111111109,-36.8276809819071,147.070520997768,"1640 GREAT ALPINE ROAD, SMOKO VIC 3741",4502036,"BRT21","22kV AC","RURAL SHORT"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0035906","20200207SPN_01","Car crashed into pole.",null,null,"1500V DC"]
[17,107,"2020-02-10T16:10:00",43871.673611111109,-38.396206007607702,146.360413981432,"805 WHITELAWS TRACK, YINNAR SOUTH VIC 3869",2627005,"MWL25","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0036213","20200211SPN_02","The root cause is fallen tree.",null,null,"Earthing cable"]
[17,108,"2020-02-12T09:38:00",43873.401388888888,-38.376261985493599,145.70559399222699,"90 LOCH-WONTHAGGI ROAD, LOCH VIC 3945",2007693,"LLG12","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0036476","20200212SPN_05","CANDLED FUSE"]
[17,109,"2020-02-15T03:48:00",43876.158333333333,-37.220498126077196,145.11181978859801,"570 STRATH CREEK ROAD, BROADFORD VIC 3658",4703408,"SMR22","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within electric line construction area",19.8,"HIGH",0.5,9.9,"E0037028","20200217SPN_01","fuse found candling due to lightning strike. no ground fire"]
[17,110,"2020-02-15T13:45:00",43876.572916666664,-38.464288502907493,146.08860662472603,"280 COULTERS ROAD, MARDAN VIC 3953",2010360,"LGA13","12.7kV AC (SWER)","RURAL LONG"," - fuse (boric acid)","single wire earth return (SWER)","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0038983","20200225SPN_01","CANDLED FUSE",null,null,"single wire earth return (SWER)"]
[17,111,"2020-02-16T18:46:00",43877.781944444447,-38.135969994360693,146.05359397618801,"782 DARNUM-SHADY CREEK ROAD, SHADY CREEK VIC 3821",2706945,"WGL24","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0037076","20200217SPN_03","Plausible cuase is combination of age and condition.",null,null,"single phase"]
[17,112,"2020-02-16T23:33:00",43877.981249999997,-36.7412290000985,145.58977002668999,"91 BALMATTUM NORTH ROAD, EUROA VIC 3666",3903299,"BN1","22kV AC","RURAL LONG"," - capacitor","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0037085","20200217SPN_04","Failure of CAP Bank blue phase bushing resulted in a grass fire of 100m x 50m. no clear cause but most likely moisture ingress\nCFA extinguished fire\nCAP bank left isolated and tagged do not operate",null,null,"two phase"]
[17,113,"2020-02-19T10:31:00",43880.438194444447,-38.011246997972698,145.91313100816402,"75 PALMER ROAD, JINDIVICK VIC 3818",2718060,"WGL24","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0040109","20200303SPN_02","Candled fuse.",null,null,"three phase"]
[17,114,"2020-02-20T20:17:00",43881.845138888886,-38.069714015078695,146.58282497323302,"555 GLENGARRY NORTH ROAD, GLENGARRY NORTH VIC 3854",2626226,"TGN31","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0045657","20200323SPN_01","Candled fuse."]
[17,115,"2020-02-22T21:51:00",43883.910416666666,-38.1095150928384,147.06615265054802,"JACK RYANS IRISH BAR, 154 RAYMOND STREET, SALE VIC 3850",2501996,"SLE11","Low voltage AC (<1kV)","URBAN"," - lamps (minor road)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0038549","20200224SPN_01","Possible over heated connection due to blown glone and no timing mechanism on ignitors (earlier models of HPS lights). Most likely due to the capacitor or the ballast igniting over and over resulting in overheating."]
[17,116,"2020-02-23T12:24:00",43884.51666666667,-37.1922261394283,145.69552441898702,"4991 MAROONDAH HIGHWAY, ALEXANDRA VIC 3714",4714153,"RUBA12","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0038555","20200224SPN_02","Plausible cuse is age.",null,null,"Negligible: no ground fire"]
[17,117,"2020-02-23T17:33:00",43884.731249999997,-37.815532005109795,147.43664499410099,"730 LINDENOW-GLENALADALE ROAD, LINDENOW SOUTH VIC 3875",1607114,"BDL44","22kV AC","RURAL LONG"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0038558","20200227SPN_02","Plausible cuase is combination of age and condition.",null,null,"Localised: less than 10 sq.m"]
[17,118,"2020-02-25T14:34:00",43886.606944444444,-38.179735982131298,146.152325971062,"52 WHEELBARROW ROAD, TRAFALGAR VIC 3824",2203072,"MOE22","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0039007","20200225SPN_03","CANDLED FUSE",null,null,"Small: 10 - 1000 aq.m"]
[17,119,"2020-02-25T17:54:00",43886.745833333334,-37.6537590043528,148.820938009446,"BELLBIRD HOTEL, 3872 PRINCES HIGHWAY, BELLBIRD CREEK VIC 3889",1910588,"CNR3","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0040396","20200303SPN_03","Candled 6A BA fuse",null,null,"Medium: 1000 sq.m - 10 ha"]
[17,120,"2020-02-26T20:46:00",43887.865277777775,-37.289680995225098,145.28606996662299,"2752 BROADFORD-FLOWERDALE ROAD, FLOWERDALE VIC 3717",4703935,"SMR14","22kV AC","RURAL LONG"," - fuse (any other type)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0039257","20200227SPN_03","CANDLED FUSE",null,null,"Large: more than 10 ha"]
[17,121,"2020-02-26T22:02:00",43887.918055555558,-38.241999993335398,146.79203399322301,"42 FEELYS ROAD, WILLUNG VIC 3847",2611076,"TGN41","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0039261","20200227SPN_04","CANDLED FUSE"]
[17,122,"2020-03-04T11:23:00",43894.474305555559,-37.754418018302601,145.65292497768502,"3045 WARBURTON HIGHWAY, MILLGROVE VIC 3799",1407375,"WYK13","Low voltage AC (<1kV)","RURAL SHORT"," - fuse (any other type)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0040647","20200305SPN_01","LV FUSE FAILED"]
[17,123,"2020-03-06T16:53:00",43896.703472222223,-37.712574984397797,145.08280097800602,"401 GREENSBOROUGH ROAD, WATSONIA VIC 3087",904031,"WT13","22kV AC","URBAN"," - pole (wood)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0041526","20200306SPN_01","Pole was hit by lightning on a stormy day resulting in broken pole.",null,null,"Started in or originated from a distribution system"]
[17,124,"2020-03-10T09:35:00",43900.399305555555,-36.373136997784698,146.27998297362501,"74 SHANLEY STREET, WANGARATTA VIC 3677",5103634,"WN4","Low voltage AC (<1kV)","RURAL SHORT"," - transformer (ground outdoor mounted)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0041737","20200318SPN_01","TX caught fire at LV bushings",null,null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system"]
[17,125,"2020-03-13T12:00:00",43903.5,-38.146672011468397,145.458489020093,"40 HOBSON ROAD, RYTHDALE VIC 3810",516186,"PHM22","22kV AC","RURAL SHORT"," - fuse (boric acid)","single phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"VERY HIGH",1,1,"E0042988","20200313SPN_01","Caused due to wildlife (bird).",null,null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system"]
[17,126,"2020-03-14T00:48:00",43904.033333333333,-37.393819014565899,145.05327997805099,"264 SOUTH MOUNTAIN ROAD, UPPER PLENTY VIC 3756",912330,"KLO14","Low voltage AC (<1kV)","RURAL LONG"," - overhead conductor (ABC)","two phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within electric line construction area",19.8,"HIGH",0.5,9.9,"E0043215","20200316SPN_03","Tree fell and brought down the line.",null,null,"Started by lightning striking a distribution system or a part of a distribution system "]
[17,127,"2020-03-19T20:54:00",43909.870833333334,-36.1060137346023,146.83189601673402,"VISY BOARD, 299 MCKOY STREET, WEST WODONGA VIC 3690",5652435,"WO13","Low voltage AC (<1kV)","RURAL SHORT"," - lamps (major road)","single phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,"E0045390","20200320SPN_01","Deterioration of connection.",null,null,"Started by any other thing forming part of or coming into contact with a distribution system"]
[17,128,"2020-03-24T02:50:00",43914.118055555555,-37.727106016585502,145.149166981382,"28 METERY ROAD, ELTHAM VIC 3095",921885,"ELM34","22kV AC","URBAN"," - fuse (any other type)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0045778","20200326SPN_01","Candled fuse.",null,null,"Otherwise started by a distribution system"]
[17,129,"2020-03-25T08:00:00",43915.333333333336,-36.369527993720396,146.23730301567701,"453 SHANLEY STREET, WANGARATTA SOUTH VIC 3678",5104064,"WN4","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0045946","20200326SPN_02","fallen tree. Root Ball unstable. fault NOT caused by branches inside the clearance space contacting the line. Trunk Distance to nearest conductor 14m."]
[17,130,"2020-03-28T15:46:00",43918.656944444447,-37.846782721330996,145.29034191156401,"16 HILLSIDE AVENUE, BORONIA VIC 3155",1222987,"BWR13","Low voltage AC (<1kV)","URBAN"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,"E0046123","20200130SPN_01","Falling tree branch hit the LV lines as it dropped to the ground."]
[17,131,"2020-03-28T23:56:00",43918.99722222222,-37.661608978557702,145.529213965981,"178 MT RIDDELL ROAD, HEALESVILLE VIC 3777",1409956,"WYK24","22kV AC","RURAL SHORT"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,"E0046125","20200316SPN_01","Plausible cause is degradation due to age.",null,null,1]
[17,132,"2020-03-30T17:30:00",43920.729166666664,-36.147622021854495,146.639686005302,"Hume Highway, CHILTERN, VIC, 3683",5208203,"BWA22","Low voltage AC (<1kV)","RURAL LONG"," - overhead conductor (insulated)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0046230","20200401SPN_02","lv cables on transformer caught fire",null,null,2]
[17,133,"2020-03-30T19:55:00",43920.829861111109,-36.8937519889339,145.62416001253001,"1839 Euroa-Mansfield Rd",3918898,"BN1","22kV AC","RURAL LONG"," - fuse (any other type)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0046229","20200401SPN_01","CANDLED FUSE",null,null,3]
[17,134,"2020-04-01T05:30:00",43922.229166666664,-37.797692193368796,147.64046596182899,"30 SHIELDS ROAD, LUCKNOW VIC 3875",1612084,"BDL44","12.7kV AC (SWER)","RURAL LONG"," - fuse (EDO fuse)","single wire earth return (SWER)","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,{"$f":"IF(OR(P171=\"\",R171=\"\"),\"\",IF(AND(O171=\"within electric line construction area\",Q171=\"No forecast\"),1,P171*R171))","v":0.91999999999999993},"E0046529","20200401SPN_03","CANDLED FUSE",null,null,4]
[17,135,"2020-04-02T07:21:00",43923.306250000001,-38.408794004323504,146.30282299154501,"55 FOX AND FANCKES ROAD, BOOLARRA SOUTH VIC 3870",2623514,"MWL11","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","three phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0046546","20200402SPN_01","A mechanical failure of the conductor.",null,null,5]
[17,136,"2020-04-04T14:47:00",43925.615972222222,-37.7326820125759,145.13715901543199,"UNIT 1 2A PORTER STREET, ELTHAM VIC 3095",900633,"ELM34","22kV AC","URBAN"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0047518","20200602SPN_01","Tree branch fell due to weather conditions",null,null,6]
[17,137,"2020-04-06T07:30:00",43927.3125,-37.9822789909433,146.88312699690903,"4945 TRARALGON-MAFFRA ROAD, TINAMBA VIC 3859",5723936,"MFA22","22kV AC","RURAL LONG"," - fuse (EDO fuse)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0046598","20200508SPN_01","Plausible cause is age of the EDO Fuse.",null,null,7]
[17,138,"2020-04-08T21:05:00",43929.878472222219,-37.827375985172395,145.59864500881901,"650 GEMBROOK-LAUNCHING PLACE ROAD, HODDLES CREEK VIC 3139",1405343,"WYK23","22kV AC","RURAL SHORT"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0046664","20200409SPN_01","CANDLING FUSE",null,null,8]
[17,139,"2020-04-22T05:36:00",43943.23333333333,-37.752824015817396,145.70047098767401,"3494 WARBURTON HIGHWAY, WARBURTON VIC 3799",1407922,"WYK13","22kV AC","RURAL SHORT"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","within electric line construction area",19.8,"LOW-MODERATE",0.2,3.9600000000000004,"E0046988","20200423SPN_01","Possom found burnt and dead at the base of the pole which may of caused the fuse not to eject.\n\n\n\n*Candelling fuse at WT009",null,null,9]
[17,140,"2020-04-24T14:00:00",43945.583333333336,-37.856652215468799,145.23955791759303,"TEDDINGTON WAY, WANTIRNA VIC 3152",5804193,"BRA32","Low voltage AC (<1kV)","URBAN"," - LV pillar","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,"E0047941","20200518SPN_01","Electrical breakdown,fuses operated due to electrical and mechanical breakdown of the pillar due to the fire.",null,null,10]
[17,141,"2020-04-27T11:23:00",43948.474305555559,-38.457586006472802,145.47496499200602,"40 DWYER ROAD, BASS VIC 3991",2803195,"LLG13","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,"E0047159","20200506SPN_01","Possible cause is salt air corrosion and moisture inside fuse holder.",null,null,{"$f":"Y177+1","v":11}]
[17,142,"2020-04-28T09:31:00",43949.396527777775,-38.293705983737198,145.83697099337402,"25 MOUNTAIN VIEW ROAD, MOUNTAIN VIEW VIC 3988",2005050,"LGA24","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,"E0047191","20200429SPN_01","Candling fuse.",null,null,{"$f":"Y178+1","v":12}]
[17,143,"2020-05-04T04:09:00",43955.17291666667,-37.796471992610499,145.25630600142,"434 MAROONDAH HWY, RINGWOOD VIC 3134",1220280,"CYN12","22kV AC","URBAN"," - transformer (pole mounted)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0047402","20200416SPN_01","Transformer has caught fire",null,null,13]
[17,144,"2020-05-13T21:33:00",43964.897916666669,-37.796006023296897,145.257055981956,"436-440 MAROONDAH HIGHWAY, CROYDON VIC 3136",1220282,"CYN32","Low voltage AC (<1kV)","URBAN"," - lamps (major road)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0047827","20200514SPN_01","Dedregation of grey twisted service supplying the pole has made contact with the pole or conductors on the pole.",null,null,14]
[17,145,"2020-05-18T06:30:00",43969.270833333336,-37.8821910187919,145.39521203029003,"1-3 VIEW ROAD, THE PATCH VIC 3792",1321440,"BGE11","22kV AC","RURAL SHORT"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","within electric line construction area",19.8,"NO FORECAST",0.1,1,"E0047942","20200518SPN_02","Found HV fuses were 6k BA Fuses and are wrong fuse rating f or a 200kva.\nUpgraded all 3 existing 6k HV fuses to 15e BA Fuses at Camm s'Patch S \\S. Tested LV off load and on load volts were good",null,null,15]
[17,146,"2020-05-20T19:52:00",43971.827777777777,-37.593563936041193,145.16188734815,"181 CHAPEL LANE, DOREEN VIC 3754",919037,"DRN14","12.7kV AC (SWER)","RURAL SHORT"," - fuse (boric acid)","single wire earth return (SWER)","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,"E0048124","20200601SPN_03","Degradation of the fuse",null,null,16]
[17,147,"2020-05-28T10:38:00",43979.443055555559,-38.069342993149498,147.08358301516702,"Cnr Bengworden Rd and Hagans Rd Cobains",2503447,"SLE32","22kV AC","RURAL SHORT"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0048980","20200529SPN_02","Fuse was candling with significant tracking when crews arrived onsite, fuse then burnt through and 'operated' in that the circuit was Deenergised but the fuse didn't operate traditionally in dropping out. \nCrew inspected the site and found nothing else \nTube had burnt through about 20 mm from top of the fuse , but no other evidence of burning found",null,null,17]
[17,148,"2020-05-29T20:20:00",43980.847222222219,-38.323711017390004,145.67147298483701,"960 YANNATHAN ROAD, NYORA VIC 3987",2006256,"LLG12","22kV AC","RURAL SHORT"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,"E0049149","20200601SPN_01","Crew arrived onsite and found Burnt off BA tube at Lis NO 2006256 \ntop half of tube laying on the ground the other half still in the holder \nNote no evidence of fire on the ground , Tube had burnt marks where it had come in half. It was an older deteriated fuse",null,null,18]
[17,149,"2020-05-31T01:39:00",43982.068749999999,-37.928993991432499,145.96107901079202,"2951 MAIN NEERIM ROAD, NEERIM JUNCTION VIC 3832",2700346,"WGL24","22kV AC","RURAL LONG"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,"E0049156","20200601SPN_02","Fuse was hung up and candleing, burn marks contained to fuse only. No fire.",null,null,19]
[17,150,"2020-06-01T20:34:00",43983.856944444444,-37.7906840103756,145.37741899617899,"4 NORTH AVENUE, MOUNT EVELYN VIC 3796",1000617,"LDL11","22kV AC","URBAN"," - overhead conductor (bare; aluminium core steel reinforced)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within electric line construction area",19.8,"NO FORECAST",0.1,1,"E0049200","20200602SPN_02","An approx. 25 meter tall gumtree located within no.6 North Avenue’s premises, setback approx. 9 meters away from nearest overhead conductors between spanned poles #1000617 & 10000618 is suspected to have been uprooted by rain and windy conditions causing the tree to fall onto to and break an open wire 22kV white phase overhead conductor, 2 x polly 22kV insulators and a shared overhead Telstra cable on pole #1000617 with 22kV fault current causing an approx .5x.5m small grass fire and burning the Telstra cable dressed up pole at base of pole and possibly HV injecting Telstra network?",null,null,20]
[17,151,"2020-06-05T12:07:00",43987.504861111112,-37.811758012032698,145.44272700481901,"25 HEAD ROAD, WANDIN EAST VIC 3139",1011429,"LDL23","22kV AC","RURAL LONG"," - fuse (EDO fuse)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,"E0049437","20200605SPN_02","Fuse operated as required but did not drop."]
[{"$f":"COUNTA(C189:O189,Q189,T189:V189)","v":17},152,"2020-06-05T12:49:00",43987.53402777778,-38.460337022909492,145.81729001275301,"100 SCOTT AND FAHEYS ROAD, KORUMBURRA VIC 3950",2006290,"LGA12","22kV AC","RURAL SHORT"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","HBRA only",{"$f":"IF(O189=\"\",\"\",IF(O189=\"LBRA only\",0.2,IF(O189=\"HBRA only\",1,IF(O189=\"within electric line construction area\",19.8,IF(O189=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"NO FORECAST",{"$f":"IF(Q189=\"\",\"\",IF(Q189=\"No forecast\",0.1,IF(Q189=\"Low-moderate\",0.2,IF(Q189=\"High\",0.5,IF(Q189=\"Very high\",1,IF(Q189=\"Severe\",2,IF(Q189=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P189=\"\",R189=\"\"),\"\",IF(AND(O189=\"within electric line construction area\",Q189=\"No forecast\"),1,P189*R189))","v":0.1},"E0049447","20200605SPN_01","Crew arrived onsite and found blown 6 K BA fuse at Scott ESTATE Pole 1  LIS  no 2006290 - fuse had candle showing burn marks \ncrew advised CEOT of findings \nCrew inspected the sight no fire on the ground and no cause found"]
[{"$f":"COUNTA(C190:O190,Q190,T190:V190)","v":17},153,"2020-06-11T07:30:00",43993.3125,-37.418827992143598,144.97455700571899,"33 RAGLAN STREET, WALLAN VIC 3756",912897,"KLO24","Low voltage AC (<1kV)","RURAL SHORT"," - underground service cable (residential)","three phase","Otherwise started by a distribution system","LBRA only",{"$f":"IF(O190=\"\",\"\",IF(O190=\"LBRA only\",0.2,IF(O190=\"HBRA only\",1,IF(O190=\"within electric line construction area\",19.8,IF(O190=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"NO FORECAST",{"$f":"IF(Q190=\"\",\"\",IF(Q190=\"No forecast\",0.1,IF(Q190=\"Low-moderate\",0.2,IF(Q190=\"High\",0.5,IF(Q190=\"Very high\",1,IF(Q190=\"Severe\",2,IF(Q190=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P190=\"\",R190=\"\"),\"\",IF(AND(O190=\"within electric line construction area\",Q190=\"No forecast\"),1,P190*R190))","v":2.0000000000000004E-2},"E0049650","20200611SPN_04","older type neutral screen service cable had electrical insulation breakdown"]
[17,154,"2020-06-13T22:47:00",43995.949305555558,-38.330475997635503,146.58006203211102,"342 OLD CALLIGNEE ROAD, CALLIGNEE VIC 3844",2605584,"TGN23","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,"E0049811","20200615SPN_03","Crew arrived onsite found candled EDO fuse 6K EDO fuse Lis 2605584 Richie Pole 3 Single phase 10 KVA transformer \nNo Fire on the ground - Fuse tube burnt only - cause Possum (TGN23FDR)"]
[17,155,"2020-06-19T10:26:00",44001.43472222222,-38.0695484319942,145.46786567237902,"14 BEVAN COURT, PAKENHAM VIC 3810",5654539,"OFR24","Low voltage AC (<1kV)","URBAN"," - LV pillar","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0050223","20200622SPN_04","LV pillar had burnt leads due to loose connections. leads replaced tested, and pillar returned to service."]
[17,156,"2020-06-21T00:35:00",44003.024305555555,-37.754988984354796,145.27261897296702,"295-297 YARRA ROAD, WONGA PARK VIC 3115",1203571,"CPK11","22kV AC","RURAL SHORT"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,"E0050241","20200622SPN_05","Fuses had to be cut away due to fuse failing to eject and replaced all faulty components with new ones."]
[17,157,"2020-06-24T17:32:00",44006.730555555558,-38.427433848485101,146.823587494653,"1003 CARRAJUNG-WOODSIDE ROAD, WOODSIDE NORTH VIC 3874",2611451,"FTR23","12.7kV AC (SWER)","RURAL LONG"," - fuse (boric acid)","single wire earth return (SWER)","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,"E0050511","20200626SPN_02","Fuse failed to eject. fuse was replaced and supply restored."]
[17,158,"2020-06-24T23:37:00",44006.984027777777,-37.9707876350273,146.98181381634402,"205-207 Johnston Street/Station Street maffra",5829054,"MFA ZSS","22kV AC","N/A"," - transformer (ground outdoor mounted)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0050515","20200625SPN_01","Tap changer ruptured due to an internal fault which led to the oil release"]
[17,159,"2020-06-26T19:22:00",44008.806944444441,-37.651939021955499,145.51849398797401,"231-235 MAROONDAH HIGHWAY, HEALESVILLE VIC 3777",1403422,"WYK24","Low voltage AC (<1kV)","RURAL SHORT"," - luminaires (minor road)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0050714","20200629SPN_01","PE cell connections overheated due to bad connections."]
[17,160,"2020-06-27T01:38:00",44009.068055555559,-38.454035986145698,145.24677398299102,"24 JENNER AVENUE, COWES VIC 3922",2806004,"PHI13","Low voltage AC (<1kV)","URBAN"," - switch (disconnector/isolator)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,"E0050723","20200629SPN_04","Krone box caught fire due to electrical breakdown."]
[{"$f":"COUNTA(C198:O198,Q198,T198:V198)","v":17},161,"2020-06-28T17:20:00",44010.722222222219,-37.860394003930701,148.03623899342801,"5 CHANDLERS ROAD, LAKE BUNGA VIC 3909",1902798,"NLA34","Low voltage AC (<1kV)","RURAL SHORT"," - connection box","single phase","Otherwise started by a distribution system","HBRA only",{"$f":"IF(O198=\"\",\"\",IF(O198=\"LBRA only\",0.2,IF(O198=\"HBRA only\",1,IF(O198=\"within electric line construction area\",19.8,IF(O198=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"NO FORECAST",{"$f":"IF(Q198=\"\",\"\",IF(Q198=\"No forecast\",0.1,IF(Q198=\"Low-moderate\",0.2,IF(Q198=\"High\",0.5,IF(Q198=\"Very high\",1,IF(Q198=\"Severe\",2,IF(Q198=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P198=\"\",R198=\"\"),\"\",IF(AND(O198=\"within electric line construction area\",Q198=\"No forecast\"),1,P198*R198))","v":0.1},"E0050728","20200629SPN_07","FOLCB caught fire due to Connections in box becoming overheated melting the plastic around the terminals then catching fire. The connections in the fuse box became overheated due to corroded connections and more load on terminals due to cold day and customer heaters etc this location is by the sea so in high salt area that would have contributed to corroding connections over time"]
[{"$f":"COUNTA(C199:O199,Q199,T199:V199)","v":17},162,"2020-06-28T17:34:00",44010.731944444444,-38.699080983496295,146.10889000817801,"25 WORFOLKS ROAD, FISH CREEK VIC 3959",2024170,"FTR21","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","HBRA only",{"$f":"IF(O199=\"\",\"\",IF(O199=\"LBRA only\",0.2,IF(O199=\"HBRA only\",1,IF(O199=\"within electric line construction area\",19.8,IF(O199=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"NO FORECAST",{"$f":"IF(Q199=\"\",\"\",IF(Q199=\"No forecast\",0.1,IF(Q199=\"Low-moderate\",0.2,IF(Q199=\"High\",0.5,IF(Q199=\"Very high\",1,IF(Q199=\"Severe\",2,IF(Q199=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P199=\"\",R199=\"\"),\"\",IF(AND(O199=\"within electric line construction area\",Q199=\"No forecast\"),1,P199*R199))","v":0.1},"E0050727","20200629SPN_06","22kv BA fuse failed to eject."]
[17,163,"2019-12-21T18:30:00",43820.770833333336,145.26724236145401,-37.917858666733792,"2 JENHILL COURT, ROWVILLE VIC 3178",260075464,"FGY12","Low voltage AC (<1kV)","URBAN"," - LV pillar","three phase","Otherwise started by a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,"E0033007","20200107SPN_12","low voltage paralleling pillar in the open position  failed ; It is suspected the failure was caused by a loose connection or insulation breakdown causing a phase to ground earth fault"]
[{"$f":"COUNTA(C201:O201,Q201,T201:V201)","v":17},164,"2020-04-03T16:46:00",43924.698611111111,145.932943770935,-38.164278675962102,"112-118 QUEEN STREET, WARRAGUL VIC 3820",2717552,"WGL15","Low voltage AC (<1kV)","RURAL SHORT"," - overhead conductor (insulated)","three phase","Otherwise started by a distribution system","LBRA only",{"$f":"IF(O201=\"\",\"\",IF(O201=\"LBRA only\",0.2,IF(O201=\"HBRA only\",1,IF(O201=\"within electric line construction area\",19.8,IF(O201=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"LOW-MODERATE",{"$f":"IF(Q201=\"\",\"\",IF(Q201=\"No forecast\",0.1,IF(Q201=\"Low-moderate\",0.2,IF(Q201=\"High\",0.5,IF(Q201=\"Very high\",1,IF(Q201=\"Severe\",2,IF(Q201=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P201=\"\",R201=\"\"),\"\",IF(AND(O201=\"within electric line construction area\",Q201=\"No forecast\"),1,P201*R201))","v":4.0000000000000008E-2},"E0046584","20200417SPN_01","Fire at LV switchboard ; Likely cause electrical breakdown of insulation within the switchboard."]

{"sheet":"3. Systems and Audit","index":4,"n_rows":29,"n_cols":5,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,1,29,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4],[19,4,21,4]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"AusNet Services"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2019/20"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"AusNet Services must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","Poweron (OMS)","Yes","ISO 9001\nISO55000\nElectricity Safey (Bushfire Mitigation) Regulations\nElectricity Safety (Management) Regulations"]
[null,"System 2","ENABLON","Yes"]
[null,"System 3 ","Smallworld GIS (SDME) /SAP","Yes"]
[null,"System 4","EM-COP","Unknown","https://scc.em.vic.gov.au/cgi-bin/scc/fdrhistory/home"]
[null,"System 5"]
[null,"System 6"]
[null,"System 7"]
[null,"System 8"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]