## Overview
Appendix 7B - Network Capability Incentive Parameter Action Plan (NCIPAP) Attachment 1 (Excel file)
PUBLIC
This spreadsheet contains:
1) | Injection Points (Transformers)
Refer to columns "Z" and "AA" for assessment of whether projects are to be included as part of the NCIPAP
The list was complied by AusNet Services and reviewed by AEMO
It includes assets from 22kV to 500kV
2) | Transmission Circuits
Refer to columns "N" and "O" for assessment of whether projects are to be included as part of the NCIPAP
The source of the data is from AusNet Services RDB and the list was compiled by AusNet Services and reviewed by AEMO
It includes assets from 220kV to 500kV
3) | Reference Sheet
Contains definitions of technical column headings used in the Injection Points and Transmission Circuits sheets, and a reference list of terminal station acronyms

## Injection Points
Number | Terminal Station (TS) / Power Station (PS) | Transformer | Transformer Primary Voltage (HV) | Transformer Secondary Voltage (MV) | Transformer Tertiary Voltage (LV) | Transformer Rating (MVA) | Summer/Winter HV Continuous Rating (Amps) | Summer HV Cyclic Rating (Amps) | Winter HV Cyclic Rating (Amps) | Summer/Winter MV Continuous Rating (Amps) | Summer MV Cyclic Rating (Amps) | Winter MV Cyclic Rating (Amps) | Summer/Winter LV Continuous Rating (Amps) | Summer LV Cyclic Rating (Amps) | Winter LV Cyclic Rating (Amps) | From Node | To Node | Equipment Limiting the Transformer Capacity | Voltage of Limiting Equipment | Summer Rating of Limiting Equipment (Amps) | Winter Rating of Limiting Equipment (Amps) | Summer Limitations (Amps) [Transformer Cyclic Rating[Note 1] - Limiting Element Rating] | Winter Limitations (Amps) [Transformer Cyclic Rating[Note 1] - Limiting Element Rating] | Reason for the Limit | AusNet Services-AEMO NCIPAP joint outcome (Project justification was reviewed by AEMO) | Project to be included as part of NCIPAP 2022-2027
1 | ATS | B2 220/66KV TRANS AT ATS | [21 empty] | Transformer rating | No limiting element | NO
2 | ATS | B3 220/66KV TRANS AT ATS | [21 empty] | Transformer rating | No limiting element | NO
3 | ATS | B4 220/66KV TRANS AT ATS | [21 empty] | Transformer rating | No limiting element | NO
4 | BATS | B1 220/66KV TRANS AT BATS | [21 empty] | Transformer rating | No limiting element | NO
5 | BATS | B2 220/66KV TRANS AT BATS | [21 empty] | Transformer rating | No limiting element | NO
6 | BETS | L4 220/22KV TRANS AT BETS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
6 | BETS | L4 220/22KV TRANS AT BETS | [21 empty] | Cable termination with lower rating than transformer | Not Worth Upgrading | NO
7 | BETS | L2 220/22KV TRANS AT BETS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
7 | BETS | L2 220/22KV TRANS AT BETS | [21 empty] | Cable termination with lower rating than transformer | Not Worth Upgrading | NO
8 | BETS | B3 220/66KV TRANS AT BETS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
8 | BETS | B3 220/66KV TRANS AT BETS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
8 | BETS | B3 220/66KV TRANS AT BETS | [21 empty] | Isolator with lower rating than transformer | Not Worth Upgrading | NO
8 | BETS | B3 220/66KV TRANS AT BETS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
8 | BETS | B3 220/66KV TRANS AT BETS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
8 | BETS | B3 220/66KV TRANS AT BETS | [21 empty] | Isolator with lower rating than transformer | Not Worth Upgrading | NO
8 | BETS | B3 220/66KV TRANS AT BETS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
9 | BETS | B4 220/66KV TRANS AT BETS | [21 empty] | Transformer rating | No limiting element | NO
10 | BLTS | B1 220/66KV TRANS AT BLTS | [21 empty] | Transformer rating | No limiting element | NO
11 | BLTS | B3 220/66KV TRANS AT BLTS | [21 empty] | Transformer rating | No limiting element | NO
12 | BLTS | B5 220/66KV TRANS AT BLTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
13 | BLTS | L1 220/22KV TRANS AT BLTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
13 | BLTS | L1 220/22KV TRANS AT BLTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
13 | BLTS | L1 220/22KV TRANS AT BLTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
13 | BLTS | L1 220/22KV TRANS AT BLTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
14 | BLTS | L3 220/22KV TRANS AT BLTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
14 | BLTS | L3 220/22KV TRANS AT BLTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
14 | BLTS | L3 220/22KV TRANS AT BLTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
14 | BLTS | L3 220/22KV TRANS AT BLTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
15 | BTS | L1 220/22KV TRANS AT BTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
15 | BTS | L1 220/22KV TRANS AT BTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
16 | BTS | L2 220/22KV TRANS AT BTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
16 | BTS | L2 220/22KV TRANS AT BTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
16 | BTS | L2 220/22KV TRANS AT BTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
16 | BTS | L2 220/22KV TRANS AT BTS | [21 empty] | CT with lower rating than transformer | Not Worth Upgrading | NO
17 | BTS | L3 220/22KV TRANS AT BTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
17 | BTS | L3 220/22KV TRANS AT BTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
17 | BTS | L3 220/22KV TRANS AT BTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
17 | BTS | L3 220/22KV TRANS AT BTS | [21 empty] | CT with lower rating than transformer | Not Worth Upgrading | NO
18 | BTS | B1 220/66/11kV TRANS AT BTS | [21 empty] | Transformer rating | No limiting element | NO
19 | BTS | B2 220/66/11kV TRANS AT BTS | [21 empty] | Transformer rating | No limiting element | NO
20 | BTS | B3 220/66/11kV TRANS AT BTS | [21 empty] | Transformer rating | No limiting element | NO
21 | CBTS | B1 220/66KV TRANS AT CBTS | [21 empty] | Transformer rating | No limiting element | NO
22 | CBTS | B2 220/66KV TRANS AT CBTS | [21 empty] | Transformer rating | No limiting element | NO
23 | CBTS | B3 220/66KV TRANS AT CBTS | [21 empty] | Transformer rating | No limiting element | NO
24 | ERTS | B1 220/66KV TRANS AT ERTS | [21 empty] | Transformer rating | No limiting element | NO
25 | ERTS | B2 220/66KV TRANS AT ERTS | [21 empty] | Transformer rating | No limiting element | NO
26 | ERTS | B3 220/66KV TRANS AT ERTS | [21 empty] | Transformer rating | No limiting element | NO
27 | ERTS | B4 220/66KV TRANS AT ERTS | [21 empty] | Transformer rating | No limiting element | NO
28 | FBTS | B1 220/66KV TRANS AT FBTS | [21 empty] | Transformer rating | No limiting element | NO
29 | FBTS | B3 220/66KV TRANS AT FBTS | [21 empty] | CB with lower rating than transformer | Not Worth Upgrading | NO
29 | FBTS | B3 220/66KV TRANS AT FBTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
29 | FBTS | B3 220/66KV TRANS AT FBTS | [21 empty] | Isolator with lower rating than transformer | Not Worth Upgrading | NO
29 | FBTS | B3 220/66KV TRANS AT FBTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
29 | FBTS | B3 220/66KV TRANS AT FBTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
30 | FBTS | B4 220/66KV TRANS AT FBTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
30 | FBTS | B4 220/66KV TRANS AT FBTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
30 | FBTS | B4 220/66KV TRANS AT FBTS | [21 empty] | Isolator with lower rating than transformer | Not Worth Upgrading | NO
30 | FBTS | B4 220/66KV TRANS AT FBTS | [21 empty] | CB with lower rating than transformer | Not Worth Upgrading | NO
30 | FBTS | B4 220/66KV TRANS AT FBTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
30 | FBTS | B4 220/66KV TRANS AT FBTS | [21 empty] | Not a limiting element - paper uprate (bus rating is limiting and this would not increase the capability.) | Not Worth Upgrading | NO
31 | GNTS | B2 220/66KV TRANS AT GNTS | [21 empty] | Transformer rating | No limiting element | NO
32 | GNTS | B3 220/66KV TRANS AT GNTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
32 | GNTS | B3 220/66KV TRANS AT GNTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
33 | GTS | B1 220/66KV TRANS AT GTS | [21 empty] | Transformer rating | No limiting element | NO
34 | GTS | B2 220/66KV TRANS AT GTS | [21 empty] | Transformer rating | No limiting element | NO
35 | GTS | B3 220/66KV TRANS AT GTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
36 | GTS | B4 220/66KV TRANS AT GTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
37 | HOTS | B2 220/66KV TRANS AT HOTS | [21 empty] | Transformer rating | No limiting element | NO
38 | HOTS | B3 220/66KV TRANS AT HOTS | [21 empty] | Transformer rating | No limiting element | NO
39 | HTS | B1 220/66KV TRANS AT HTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
39 | HTS | B1 220/66KV TRANS AT HTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
39 | HTS | B1 220/66KV TRANS AT HTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
39 | HTS | B1 220/66KV TRANS AT HTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
39 | HTS | B1 220/66KV TRANS AT HTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
39 | HTS | B1 220/66KV TRANS AT HTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
39 | HTS | B1 220/66KV TRANS AT HTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
40 | HTS | B2 220/66KV TRANS AT HTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
40 | HTS | B2 220/66KV TRANS AT HTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
40 | HTS | B2 220/66KV TRANS AT HTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
40 | HTS | B2 220/66KV TRANS AT HTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
40 | HTS | B2 220/66KV TRANS AT HTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
40 | HTS | B2 220/66KV TRANS AT HTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
41 | HTS | B3 220/66KV TRANS AT HTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
41 | HTS | B3 220/66KV TRANS AT HTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
41 | HTS | B3 220/66KV TRANS AT HTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
42 | KGTS | B1 220/66/22KV TRANS AT KGTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
42 | KGTS | B1 220/66/22KV TRANS AT KGTS | [21 empty] | Isolator with lower rating than transformer | Not Worth Upgrading | NO
43 | KGTS | B2 220/66/22KV TRANS AT KGTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
43 | KGTS | B2 220/66/22KV TRANS AT KGTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
44 | KGTS | B3 220/66/22KV TRANS AT KGTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
44 | KGTS | B3 220/66/22KV TRANS AT KGTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
44 | KGTS | B3 220/66/22KV TRANS AT KGTS | [21 empty] | Isolator with lower rating than transformer | Not Worth Upgrading | NO
44 | KGTS | B3 220/66/22KV TRANS AT KGTS | [21 empty] | Isolator with lower rating than transformer | Not Worth Upgrading | NO
45 | KTS | B1 220/66KV TRANS AT KTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
45 | KTS | B1 220/66KV TRANS AT KTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
45 | KTS | B1 220/66KV TRANS AT KTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
45 | KTS | B1 220/66KV TRANS AT KTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
46 | KTS | B2 220/66KV TRANS AT KTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
46 | KTS | B2 220/66KV TRANS AT KTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
46 | KTS | B2 220/66KV TRANS AT KTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
47 | KTS | B3 220/66KV TRANS AT KTS | [21 empty] | Transformer rating | No limiting element | NO
48 | KTS | B4 220/66KV TRANS AT KTS | [21 empty] | Transformer rating | No limiting element | NO
49 | KTS | B5 220/66KV TRANS AT KTS | [21 empty] | Transformer rating | No limiting element | NO
50 | MBTS | B1 220/66KV TRANS (HOT SPARE) AT MBTS | [21 empty] | Transformer rating | No limiting element | NO
51 | MBTS | B2 220/66KV TRANS AT MBTS | [21 empty] | Transformer rating | No limiting element | NO
52 | MTS | B1 220/66KV TRANS AT MTS | [21 empty] | Transformer rating | No limiting element | NO
53 | MTS | B3 220/66KV TRANS AT MTS | [21 empty] | Transformer rating | No limiting element | NO
54 | MTS | U1 66/22KV TRANS AT MTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
55 | MTS | U2 66/22KV TRANS AT MTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
55 | MTS | U2 66/22KV TRANS AT MTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
55 | MTS | U2 66/22KV TRANS AT MTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
56 | MWTS | B1 220/66KV TRANS AT MWTS | [21 empty] | Transformer rating | No limiting element | NO
57 | MWTS | B2 220/66KV TRANS AT MWTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
57 | MWTS | B2 220/66KV TRANS AT MWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
57 | MWTS | B2 220/66KV TRANS AT MWTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
58 | MWTS | B3 220/66KV TRANS AT MWTS | [21 empty] | Secondary equipment settings/plant limitations | No limiting element | NO
59 | RCTS | R1A 220/66/22KV TRANS AT RCTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
59 | RCTS | R1A 220/66/22KV TRANS AT RCTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
59 | RCTS | R1A 220/66/22KV TRANS AT RCTS | [21 empty] | Reactor with lower rating than transformer | Not Worth Upgrading | NO
59 | RCTS | R1A 220/66/22KV TRANS AT RCTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
60 | RCTS | R1B 220/66/22KV TRANS AT RCTS | [21 empty] | Transformer rating | No limiting element | NO
61 | RCTS | R2A 220/66/22KV TRANS AT RCTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
61 | RCTS | R2A 220/66/22KV TRANS AT RCTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
61 | RCTS | R2A 220/66/22KV TRANS AT RCTS | [21 empty] | Reactor with lower rating than transformer | Not Worth Upgrading | NO
61 | RCTS | R2A 220/66/22KV TRANS AT RCTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
62 | RCTS | R2B 220/66/22KV TRANS AT RCTS | [21 empty] | Transformer rating | No limiting element | NO
63 | RCTS | R3 220/66/22KV TRANS AT RCTS | [21 empty] | Transformer rating | No limiting element | NO
64 | RTS | B1 220/66KV TRANS AT RTS | [21 empty] | Transformer rating | No limiting element | NO
65 | RTS | B2 220/66KV TRANS AT RTS | [21 empty] | Transformer rating | No limiting element | NO
66 | RTS | B5 220/66KV TRANS AT RTS | [21 empty] | Transformer rating | No limiting element | NO
67 | RTS | L1 220/22KV TRANS AT RTS | [21 empty] | Transformer rating | No limiting element | NO
68 | RTS | L2 220/22KV TRANS AT RTS | [21 empty] | Transformer rating | No limiting element | NO
69 | RWTS | B1 220/66KV TRANS AT RWTS | [21 empty] | Transformer rating | No limiting element | NO
70 | RWTS | B2 220/66KV TRANS AT RWTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
70 | RWTS | B2 220/66KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
70 | RWTS | B2 220/66KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
71 | RWTS | B3 220/66KV TRANS AT RWTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
71 | RWTS | B3 220/66KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
71 | RWTS | B3 220/66KV TRANS AT RWTS | [21 empty] | Isolator with lower rating than transformer | Not Worth Upgrading | NO
71 | RWTS | B3 220/66KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
72 | RWTS | B4 220/66KV TRANS AT RWTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
72 | RWTS | B4 220/66KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
72 | RWTS | B4 220/66KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
73 | RWTS | L2 220/22KV TRANS AT RWTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
73 | RWTS | L2 220/22KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
73 | RWTS | L2 220/22KV TRANS AT RWTS | [21 empty] | CB with lower rating than transformer | Not Worth Upgrading | NO
73 | RWTS | L2 220/22KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
73 | RWTS | L2 220/22KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
73 | RWTS | L2 220/22KV TRANS AT RWTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
74 | RWTS | L3 220/22KV TRANS AT RWTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
74 | RWTS | L3 220/22KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
74 | RWTS | L3 220/22KV TRANS AT RWTS | [21 empty] | CB with lower rating than transformer | Not Worth Upgrading | NO
74 | RWTS | L3 220/22KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
74 | RWTS | L3 220/22KV TRANS AT RWTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
74 | RWTS | L3 220/22KV TRANS AT RWTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
75 | SHTS | B2 220/66KV TRANS AT SHTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
76 | SHTS | B3 220/66KV TRANS AT SHTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
77 | SHTS | B4 220/66KV TRANS AT SHTS | [21 empty] | Transformer rating | No limiting element | NO
78 | SMTS | B1 220/66KV TRANS AT SMTS | [21 empty] | Transformer rating | No limiting element | NO
79 | SMTS | B3 220/66KV TRANS AT SMTS | [21 empty] | Transformer rating | No limiting element | NO
80 | SVTS | B1 220/66KV TRANS AT SVTS | [21 empty] | Transformer rating | No limiting element | NO
81 | SVTS | B2 220/66KV TRANS AT SVTS | [21 empty] | Transformer rating | No limiting element | NO
82 | SVTS | B3 220/66KV TRANS AT SVTS | [21 empty] | Transformer rating | No limiting element | NO
83 | SVTS | B4 220/66KV TRANS AT SVTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
83 | SVTS | B4 220/66KV TRANS AT SVTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
84 | TBTS | B1 220/66KV TRANS AT TBTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
85 | TBTS | B2 220/66KV TRANS AT TBTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
86 | TBTS | B3 220/66KV TRANS AT TBTS | [21 empty] | Transformer rating | No limiting element | NO
87 | TGTS | B1 220/66KV TRANS AT TGTS | [21 empty] | Transformer rating | No limiting element | NO
88 | TGTS | B2 220/66KV TRANS AT TGTS | [21 empty] | Transformer rating | No limiting element | NO
89 | TSTS | B1 220/66KV TRANS AT TSTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
89 | TSTS | B1 220/66KV TRANS AT TSTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
89 | TSTS | B1 220/66KV TRANS AT TSTS | [21 empty] | Isolator with lower rating than transformer | Not Worth Upgrading | NO
89 | TSTS | B1 220/66KV TRANS AT TSTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
89 | TSTS | B1 220/66KV TRANS AT TSTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
89 | TSTS | B1 220/66KV TRANS AT TSTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
89 | TSTS | B1 220/66KV TRANS AT TSTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
89 | TSTS | B1 220/66KV TRANS AT TSTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
90 | TSTS | B2 220/66KV TRANS AT TSTS | [21 empty] | Transformer rating | No limiting element | NO
91 | TSTS | B3 220/66KV TRANS AT TSTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
91 | TSTS | B3 220/66KV TRANS AT TSTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
91 | TSTS | B3 220/66KV TRANS AT TSTS | [21 empty] | Isolator with lower rating than transformer | Not Worth Upgrading | NO
91 | TSTS | B3 220/66KV TRANS AT TSTS | [21 empty] | CB with lower rating than transformer | Not Worth Upgrading | NO
91 | TSTS | B3 220/66KV TRANS AT TSTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
91 | TSTS | B3 220/66KV TRANS AT TSTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
91 | TSTS | B3 220/66KV TRANS AT TSTS | [21 empty] | Secondary equipment settings/plant limitations | Not Worth Upgrading | NO
92 | TTS | B1 220/66KV TRANS AT TTS | [21 empty] | Busbar with lower rating than transformer | Not Worth Upgrading | NO
92 | TTS | B1 220/66KV TRANS AT TTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
92 | TTS | B1 220/66KV TRANS AT TTS | [21 empty] | Isolator with lower rating than transformer | Not Worth Upgrading | NO
92 | TTS | B1 220/66KV TRANS AT TTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
92 | TTS | B1 220/66KV TRANS AT TTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
92 | TTS | B1 220/66KV TRANS AT TTS | [21 empty] | Not a limiting element - paper uprate | Not Worth Upgrading | NO
92 | TTS | B1 220/66KV TRANS AT TTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
92 | TTS | B1 220/66KV TRANS AT TTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
93 | TTS | B2 220/66KV TRANS AT TTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
94 | TTS | B3 220/66KV TRANS AT TTS | [21 empty] | Transformer rating | No limiting element | NO
95 | TTS | B4 220/66KV TRANS AT TTS | [21 empty] | Transformer rating | No limiting element | NO
96 | TTS | B5 220/66KV TRANS AT TTS | [21 empty] | Not a limiting element - paper uprate | Not Worth Upgrading | NO
97 | TTS | B5 220/66KV TRANS AT TTS | [21 empty] | Not a limiting element - paper uprate | Not Worth Upgrading | NO
98 | WBTS | B1 220/66KV TRANS AT WBTS | [21 empty] | Transformer rating | No limiting element | NO
99 | WBTS | B2 220/66KV TRANS AT WBTS | [21 empty] | Transformer rating | No limiting element | NO
100 | WETS | B1 220/66KV TRANS AT WETS | [21 empty] | Transformer rating | No limiting element | NO
101 | WETS | B2 220/66KV TRANS AT WETS | [21 empty] | Transformer rating | No limiting element | NO
102 | WMTS | B1 220/66KV TRANS AT WMTS | [21 empty] | Transformer rating | No limiting element | NO
103 | WMTS | B2 220/66KV TRANS AT WMTS | [21 empty] | Transformer rating | No limiting element | NO
104 | WMTS | B3 220/66KV TRANS AT WMTS | [21 empty] | Transformer rating | No limiting element | NO
105 | WMTS | B4 220/66KV TRANS AT WMTS | [21 empty] | Transformer rating | No limiting element | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Busbar with lower rating than transformer | To be retired after WMTS rebuild project | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | CB with lower rating than transformer | To be retired after WMTS rebuild project | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | To be retired after WMTS rebuild project | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Reactor with rating lower than transformer | To be retired after WMTS rebuild project | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Busbar with lower rating than transformer | To be retired after WMTS rebuild project | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | CB with lower rating than transformer | To be retired after WMTS rebuild project | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | To be retired after WMTS rebuild project | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
106 | WMTS | L1 220/22KV TRANS AT WMTS | [21 empty] | Reactor with rating lower than transformer | To be retired after WMTS rebuild project | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Busbar with lower rating than transformer | To be retired after WMTS rebuild project | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | CB with lower rating than transformer | To be retired after WMTS rebuild project | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | To be retired after WMTS rebuild project | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Reactor with rating lower than transformer | To be retired after WMTS rebuild project | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Secondary equipment settings/plant limitations | To be retired after WMTS rebuild project | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Busbar with lower rating than transformer | To be retired after WMTS rebuild project | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | CB with lower rating than transformer | To be retired after WMTS rebuild project | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | To be retired after WMTS rebuild project | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Interplant connection with lower rating than transformer | Not Worth Upgrading | NO
107 | WMTS | L3 220/22KV TRANS AT WMTS | [21 empty] | Reactor with rating lower than transformer | To be retired after WMTS rebuild project | NO
108 | WOTS | X1 330/66/22KV TRANS AT WOTS | [21 empty] | Transformer rating | No limiting element | NO
109 | WOTS | X2 330/66/22KV TRANS AT WOTS | [21 empty] | Transformer rating | No limiting element | NO
110 | CBTS | A1 500/220KV TRANS BANK AT CBTS | [21 empty] | Transformer rating | No limiting element | NO
111 | DDTS | H1 330/220KV TRANS AT DDTS | [21 empty] | Secondary equipment settings/plant limitations | Potential economic merit – pending further investigation | Pending further investigation
112 | DDTS | H2 330/220KV TRANS AT DDTS | [21 empty] | Transformer rating | No limiting element | NO
113 | DDTS | H3 330/220KV TRANS AT DDTS | [21 empty] | Transformer rating | No limiting element | NO
114 | HWTS | A1 515/230KV TRANS AT HWTS | [21 empty] | Transformer rating | No limiting element | NO
115 | HWTS | A2 515/230KV TRANS BANK AT HWTS | [21 empty] | Transformer rating | No limiting element | NO
116 | HWTS | A3 515/230KV TRANS BANK AT HWTS | [21 empty] | Transformer rating | No limiting element | NO
117 | HWTS | A4 515/230KV TRANS BANK AT HWTS | [21 empty] | Transformer rating | No limiting element | NO
118 | HYTS | M1 500/275KV TRANS AT HYTS | [21 empty] | Transformer rating | No limiting element | NO
119 | HYTS | M2 500/275KV TRANS AT HYTS | [21 empty] | Transformer rating | No limiting element | NO
120 | HYTS | M3 500/275KV TRANS AT HYTS | [21 empty] | Transformer rating | No limiting element | NO
121 | KTS | A2 500/220KV TRANS BANK AT KTS | [21 empty] | Transformer rating | No limiting element | NO
122 | KTS | A3 500/220KV TRANS BANK AT KTS | [21 empty] | Transformer rating | No limiting element | NO
123 | KTS | A4 500/220KV TRANS BANK AT KTS | [21 empty] | Transformer rating | No limiting element | NO
124 | MLTS | A1 500/220KV TRANS BANK AT MLTS | [21 empty] | Interplant connection with lower rating than transformer | Potential economic merit – pending further investigation | Pending further investigation
125 | MLTS | A2 500/220KV TRANS BANK AT MLTS | [21 empty] | Transformer rating | No limiting element | NO
126 | ROTS | A1 515/220KV TRANS BANK AT ROTS (RTF) | [21 empty] | Transformer rating | No limiting element | NO
127 | ROTS | A2 515/220KV TRANS BANK AT ROTS | [21 empty] | Transformer rating | No limiting element | NO
128 | SMTS | F2 500/330KV TRANS BANK AT SMTS | [21 empty] | Transformer rating | No limiting element | NO
129 | SMTS | H1 330/220KV TRANS BANK AT SMTS | [21 empty] | Transformer rating | No limiting element | NO
130 | SMTS | H2 330/220KV TRANS BANK AT SMTS | [21 empty] | Transformer rating | No limiting element | NO
131 | SMTS | H3 330/220KV TRANS BANK AT SMTS | [21 empty] | Transformer rating | No limiting element | NO

## Transmission Circuits
Number | Transmission Circuit/ Transformer | Summer Line Rating (MVA) | Winter Line Rating (MVA) | Location of Limiting Equipment [Terminal Station (TS) /Power Station (PS) /Gas Station (GS)] | Node 1 | Node 2 | Equipment Limiting the Line Capacity | Summer Rating of Limiting Equipment (MVA) | Winter Rating of Limiting Equipment (MVA) | Limiting in Summer? | Limiting in Winter? | Reason for the Limit | AusNet Services-AEMO NCIPAP joint outcome (Project justification was reviewed by AEMO) | Project to be included as part of NCIPAP 2022-2027 | Comments
1 | ATS - BLTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
2 | BATS - BETS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
3 | BATS - MLTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
4 | BATS - MLTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
5 | BATS - ELTS 220 kV line | [10 empty] | Line rating | No limiting element | NO
6 | ELTS - MLTS 220 kV line | [10 empty] | Line rating | No limiting element | NO
7 | BATS - BBTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
8 | BBTS - TGTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
9 | BATS - WBTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
10 | BETS - KGTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Potential economic merit – pending further investigation | Pending further investigation
10 | BETS - KGTS No.1 220 kV line | [10 empty] | Reactor with lower rating than line | Potential economic merit – pending further investigation | Pending further investigation
11 | BETS -FVTS- SHTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
12 | BTS - RTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
13 | DDTS - GNTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
14 | DDTS - GNTS No.3 220 kV line | [10 empty] | Interplant connection with lower rating than line | Potential economic merit – pending further investigation | Pending further investigation
14 | DDTS - GNTS No.3 220 kV line | [10 empty] | Interplant connection with lower rating than line | Potential economic merit – pending further investigation | Pending further investigation
14 | DDTS - GNTS No.3 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Potential economic merit – pending further investigation | Pending further investigation
14 | DDTS - GNTS No.3 220 kV line | [10 empty] | Interplant connection with lower rating than line | Potential economic merit – pending further investigation | Pending further investigation
15 | DDTS - MBTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
16 | DDTS - MBTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
17 | DDTS - MSS No.1 330 kV line | [10 empty] | Line rating | No limiting element | NO
18 | DDTS - MSS No.2 330 kV line | [10 empty] | Line rating | No limiting element | NO
19 | DDTS - SHTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Potential economic merit – pending further investigation | Pending further investigation
20 | DDTS - WOTS No.1 330 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
20 | DDTS - WOTS No.1 330 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
20 | DDTS - WOTS No.1 330 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
21 | EPSY - MBTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
22 | EPSY - MBTS No.2 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
23 | ERTS - CBTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
24 | ERTS - CBTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
25 | FBTS - BLTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
26 | FBTS - NPSD No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
27 | FBTS - WMTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
28 | FBTS - WMTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
29 | GNTS - SHTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Potential economic merit – pending further investigation | Pending further investigation
30 | GNTS - SHTS No.3 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Potential economic merit – pending further investigation | Pending further investigation
31 | GTS - MLTS No.1 220 kV line | [10 empty] | Isolator with lower rating than line | Potential economic merit – pending further investigation | Pending further investigation
31 | GTS - MLTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Potential economic merit – pending further investigation | Pending further investigation
32 | GTS - MLTS No.2 220 kV line | [10 empty] | Isolator with lower rating than line | Potential economic merit – pending further investigation | Pending further investigation
33 | GTS - PTH No.1 220 kV line OOS | [10 empty] | Line rating | No limiting element | NO
34 | GTS - PTH No.2 220 kV line OOS | [10 empty] | Line rating | No limiting element | NO
35 | HOTS - MRTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
36 | MRTS - KMTS No.1 220 kV line | [11 empty] | No limiting element | No
37 | KMTS -RCTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
38 | HOTS - BGTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Potential economic merit – pending further investigation | Pending further investigation
39 | BGTS - CWTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
40 | CWTS - ARTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
41 | ARTS - WBTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
42 | HTS - SVTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
43 | HTS - SVTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
44 | HWPS - JLTS No.1 220 kV line | [10 empty] | Busbar with lower rating than line | Low priority - currently not worth upgrading | No
45 | HWPS - JLTS No.2 220 kV line | [10 empty] | Busbar with lower rating than line | Low priority - currently not worth upgrading | No
46 | HWPS - JLTS No.3 220 kV line | [10 empty] | Line rating | No limiting element | NO
47 | HWPS - JLTS No.4 220 kV line | [10 empty] | Line rating | No limiting element | NO
47 | HWPS - JLTS No.4 220 kV line | [10 empty] | Interplant connection with lower rating than line short term rating | Low priority - currently not worth upgrading | No
48 | HWPS - MWTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
49 | HWPS - YPS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
50 | HWPS - YPS No.2 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
51 | HWTS - CBTS No.4 500 kV line | [10 empty] | CT with lower rating than line | Low priority - currently not worth upgrading | No
51 | HWTS - CBTS No.4 500 kV line | [10 empty] | CB with lower rating than line | Low priority - currently not worth upgrading | No
51 | HWTS - CBTS No.4 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
51 | HWTS - CBTS No.4 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
52 | HWTS - HWPS No.1 220 kV line | [10 empty] | Busbar with lower rating than line | Low priority - currently not worth upgrading | No
52 | HWTS - HWPS No.1 220 kV line | [10 empty] | Transformer with lower rating than line | Low priority - currently not worth upgrading | No
52 | HWTS - HWPS No.1 220 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
53 | HWTS - HWPS No.2 220 kV line | [10 empty] | Busbar with lower rating than line | Low priority - currently not worth upgrading | No
53 | HWTS - HWPS No.2 220 kV line | [10 empty] | Transformer with lower rating than line | Low priority - currently not worth upgrading | No
54 | HWTS - HWPS No.3 220 kV line | [10 empty] | Busbar with lower rating than line | Low priority - currently not worth upgrading | No
54 | HWTS - HWPS No.3 220 kV line | [10 empty] | Transformer with lower rating than line | Low priority - currently not worth upgrading | No
55 | HWTS - HWPS No.4 220 kV line | [10 empty] | Busbar with lower rating than line | Low priority - currently not worth upgrading | No
55 | HWTS - HWPS No.4 220 kV line | [10 empty] | Transformer with lower rating than line | Low priority - currently not worth upgrading | No
55 | HWTS - HWPS No.4 220 kV line | [10 empty] | Interplant connection with lower rating than line short term rating | Low priority - currently not worth upgrading | No
56 | HWTS - LYPS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
56 | HWTS - LYPS No.1 500 kV line | [10 empty] | Busbar with lower rating than line | Low priority - currently not worth upgrading | No
56 | HWTS - LYPS No.1 500 kV line | [10 empty] | CB with lower rating than line | Low priority - currently not worth upgrading | No
56 | HWTS - LYPS No.1 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
57 | HWTS - LYPS No.2 500 kV line | [10 empty] | CB with lower rating than line | Low priority - currently not worth upgrading | No
57 | HWTS - LYPS No.2 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
57 | HWTS - LYPS No.2 500 kV line | [10 empty] | CB with lower rating than line | Low priority - currently not worth upgrading | No
57 | HWTS - LYPS No.2 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
57 | HWTS - LYPS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
58 | HWTS - LYPS No.3 500 kV line | [10 empty] | CB with lower rating than line | Low priority - currently not worth upgrading | No
58 | HWTS - LYPS No.3 500 kV line | [10 empty] | CB with lower rating than line | Low priority - currently not worth upgrading | No
58 | HWTS - LYPS No.3 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
58 | HWTS - LYPS No.3 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
59 | HYTS - APD No.1 500 kV line | [10 empty] | CB with lower rating than line | Low priority - currently not worth upgrading | No
59 | HYTS - APD No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
59 | HYTS - APD No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
59 | HYTS - APD No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
59 | HYTS - APD No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
60 | HYTS - APD No.2 500 kV line | [10 empty] | CB with lower rating than line | Low priority - currently not worth upgrading | No
60 | HYTS - APD No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
60 | HYTS - APD No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
60 | HYTS - APD No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
60 | HYTS - APD No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | CB with lower rating than line | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
61 | HYTS - MOPS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
62 | HYTS - SESS No.1 275 kV line | [10 empty] | Transformer with lower rating than line | Low priority - currently not worth upgrading | No
63 | HYTS - SESS No.2 275 kV line | [10 empty] | Transformer with lower rating than line | Low priority - currently not worth upgrading | No
64 | HYTS - TRTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
64 | HYTS - TRTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
64 | HYTS - TRTS No.1 500 kV line | [10 empty] | CB with lower rating than line | Low priority - currently not worth upgrading | No
64 | HYTS - TRTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
65 | JLGA - JLTS No.1 220 kV line | [10 empty] | Busbar with lower rating than line | Low priority - currently not worth upgrading | No
65 | JLGA - JLTS No.1 220 kV line | [10 empty] | Reactor with lower rating than line | Low priority - currently not worth upgrading | No
66 | JLTS - JLGB No.1 220 kV line | [10 empty] | Reactor with lower rating than line | Low priority - currently not worth upgrading | No
67 | JLTS - MWTS No.1 220 kV line | [10 empty] | Transformer with lower rating than line | Low priority - currently not worth upgrading | No
67 | JLTS - MWTS No.1 220 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
67 | JLTS - MWTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
68 | JLTS - MWTS No.2 220 kV line | [10 empty] | Transformer with lower rating than line | Low priority - currently not worth upgrading | No
68 | JLTS - MWTS No.2 220 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
69 | KGTS - WETS No.1 220 kV line | [10 empty] | Reactor with lower rating than line | Potential economic merit – pending further investigation | Pending further investigation
70 | KTS - ATS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
71 | KTS - BLTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
72 | KTS - GTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
73 | KTS - DPTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
74 | DPTS - GTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
75 | KTS - GTS No.3 220 kV line | [10 empty] | Line rating | No limiting element | NO
76 | KTS - SMTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
76 | KTS - SMTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
76 | KTS - SMTS No.1 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
76 | KTS - SMTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
76 | KTS - SMTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
76 | KTS - SMTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
76 | KTS - SMTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
76 | KTS - SMTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
76 | KTS - SMTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
76 | KTS - SMTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
77 | KTS - SYTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
78 | KTS - WMTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
79 | KTS - WMTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
80 | LYPS - LYPB No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
81 | LYPS - LYPB No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
82 | MBTS - DPS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
83 | MBTS - MKPS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
84 | MBTS - WKPS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
85 | MLTS - MOPS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
85 | MLTS - MOPS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
85 | MLTS - MOPS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
86 | MLTS - HGTS No. 1 500kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
87 | HGTS -TRTS No. 1 500kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
88 | MLTS - TGTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
89 | NPSD - BLTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
89 | NPSD - BLTS No.1 220 kV line | [10 empty] | Reactor with lower rating than line | Low priority - currently not worth upgrading | No
90 | RCTS - WETS No.1 220 kV line | [10 empty] | Reactor with lower rating than line | Potential economic merit – pending further investigation | Pending further investigation
91 | ROTS - CBTS No.4 500 kV line | [10 empty] | CT with lower rating than line | Low priority - currently not worth upgrading | No
91 | ROTS - CBTS No.4 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
91 | ROTS - CBTS No.4 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
91 | ROTS - CBTS No.4 500 kV line | [10 empty] | Line Trap with lower rating than line | Low priority - currently not worth upgrading | No
92 | ROTS - ERTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
93 | ROTS - ERTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
94 | ROTS - HWPS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
95 | ROTS - HWPS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
96 | ROTS - HWTS No.3 500 kV line | [10 empty] | CB with lower rating than line | Low priority - currently not worth upgrading | No
96 | ROTS - HWTS No.3 500 kV line | [10 empty] | CT with lower rating than line | Low priority - currently not worth upgrading | No
96 | ROTS - HWTS No.3 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
96 | ROTS - HWTS No.3 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
96 | ROTS - HWTS No.3 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
97 | ROTS - MTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
98 | ROTS - MTS No.3 220 kV line | [10 empty] | Line rating | No limiting element | NO
99 | ROTS - RTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
100 | ROTS - RTS No.4 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
101 | ROTS - RWTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
102 | ROTS - SMTS No.3 500 kV line | [10 empty] | Line rating | No limiting element | NO
103 | ROTS - SVTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
103 | ROTS - SVTS No.1 220 kV line | [10 empty] | Interplant connection with lower rating than line short term rating | Low priority - currently not worth upgrading | No
103 | ROTS - SVTS No.1 220 kV line | [10 empty] | Interplant connection with lower rating than line short term rating | Low priority - currently not worth upgrading | No
104 | ROTS - SVTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
104 | ROTS - SVTS No.2 220 kV line | [10 empty] | Interplant connection with lower rating than line short term rating | Low priority - currently not worth upgrading | No
104 | ROTS - SVTS No.2 220 kV line | [10 empty] | Interplant connection with lower rating than line short term rating (under outage conditions) | Low priority - currently not worth upgrading | No
104 | ROTS - SVTS No.2 220 kV line | [10 empty] | CB with lower rating than line short term rating (under outage conditions) | Low priority - currently not worth upgrading | No
105 | ROTS - TSTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
105 | ROTS - TSTS No.1 220 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
105 | ROTS - TSTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
105 | ROTS - TSTS No.1 220 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
106 | ROTS - TTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
107 | ROTS - YPS No.5 220 kV line | [10 empty] | Line rating | No limiting element | NO
108 | ROTS - YPS No.6 220 kV line | [10 empty] | Line rating | No limiting element | NO
109 | ROTS - YPS No.7 220 kV line | [10 empty] | Line rating | No limiting element | NO
110 | ROTS - YPS No.8 220 kV line | [10 empty] | Line rating | No limiting element | NO
111 | SMTS - DDTS No.1 330 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
111 | SMTS - DDTS No.1 330 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
111 | SMTS - DDTS No.1 330 kV line | [10 empty] | Capacitor bank with lower rating than line | Low priority - currently not worth upgrading | No
112 | SMTS - DDTS No.2 330 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
112 | SMTS - DDTS No.2 330 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
112 | SMTS - DDTS No.2 330 kV line | [10 empty] | Capacitor bank with lower rating than line | Low priority - currently not worth upgrading | No
113 | SMTS - HWTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
113 | SMTS - HWTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
113 | SMTS - HWTS No.1 500 kV line | [10 empty] | Busbar with lower rating than line | Low priority - currently not worth upgrading | No
113 | SMTS - HWTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
113 | SMTS - HWTS No.1 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
113 | SMTS - HWTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
113 | SMTS - HWTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
113 | SMTS - HWTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
113 | SMTS - HWTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
113 | SMTS - HWTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
113 | SMTS - HWTS No.1 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
114 | SMTS - HWTS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
114 | SMTS - HWTS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
114 | SMTS - HWTS No.2 500 kV line | [10 empty] | Busbar with lower rating than line | Low priority - currently not worth upgrading | No
114 | SMTS - HWTS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
114 | SMTS - HWTS No.2 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
114 | SMTS - HWTS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
114 | SMTS - HWTS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
114 | SMTS - HWTS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
114 | SMTS - HWTS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
114 | SMTS - HWTS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
114 | SMTS - HWTS No.2 500 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
115 | SMTS - SYTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
115 | SMTS - SYTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
116 | SMTS - SYTS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
116 | SMTS - SYTS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
117 | SYTS - MLTS No.1 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
117 | SYTS - MLTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
117 | SYTS - MLTS No.1 500 kV line | [10 empty] | Reactor with lower rating than line | Low priority - currently not worth upgrading | No
117 | SYTS - MLTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
117 | SYTS - MLTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
117 | SYTS - MLTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
117 | SYTS - MLTS No.1 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
118 | SYTS - MLTS No.2 500 kV line | [10 empty] | Isolator with lower rating than line | Low priority - currently not worth upgrading | No
118 | SYTS - MLTS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
118 | SYTS - MLTS No.2 500 kV line | [10 empty] | Reactor with lower rating than line | Low priority - currently not worth upgrading | No
118 | SYTS - MLTS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
118 | SYTS - MLTS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
118 | SYTS - MLTS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
118 | SYTS - MLTS No.2 500 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
119 | TBTS - CBTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
120 | TBTS - CBTS No.2 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
121 | TBTS - JLA No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
122 | TBTS - JLA No.2 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
123 | TSTS - TTS No.1 220 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
123 | TSTS - TTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
124 | TTS - BTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
125 | TTS - BTS No.3 220 kV line | [10 empty] | Line rating | No limiting element | NO
126 | TTS - EPSY No.1 220 kV line | [10 empty] | Interplant connection with lower rating than line | Low priority - currently not worth upgrading | No
127 | TTS - KTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
128 | TTS - KTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
129 | TTS - RWTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
129 | TTS - RWTS No.1 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
130 | TTS - SMTS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
131 | TTS - SMTS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
132 | WOTS - JDSS No.1 330 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
133 | YPS - YWPS No.1 220 kV line | [10 empty] | Line rating | No limiting element | NO
134 | YPS - YWPS No.2 220 kV line | [10 empty] | Line rating | No limiting element | NO
135 | YPS - YWPS No.3 220 kV line | [10 empty] | Line rating | No limiting element | NO
136 | YPS - YWPS No.4 220 kV line | [10 empty] | Line rating | No limiting element | NO
137 | YPS - YWPS No.5 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
138 | YPS - YWPS No.6 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No
139 | YPS - YWPS No.7 220 kV line | [10 empty] | Secondary equipment settings/plant limitations | Low priority - currently not worth upgrading | No

## Reference Sheet
Terminal Stations |  | Technical Definitions
APD | Portland Aluminium Customer Substation | Continuous Rating | A transformer's continuous rating is the power the transformer is capable of carrying in continuous service without exceeding the temperature-rise limitations.
ARTS | Ararat Terminal Station
ATS | Altona Terminal Station | Cyclic Rating | A transformer's cyclic rating allows for variation in the load profile. This cyclic rating allows the transformer to be overloaded at peak times so long as there is a sufficient cooling down period at the lower point in the load profile.
BATS | Ballarat Terminal Station
BBTS | Berrybank Terminal Station
BETS | Bendigo Terminal Station
BGTS | Bulgana Terminal Station
BLTS | Brooklyn Terminal Station
BTS | Brunswick Terminal Station
CBTS | Cranbourne Terminal Station
CWTS | Crowlands Terminal Station
DDTS | Dederang Terminal Station
DPS | Dartmouth Power Station
DPTS | Deerpark Terminal Station
ELTS | Elaine Terminal Station
EPSY | Eildon Power Station Yard
ERTS | East Rowville Terminal Station
FBTS | Fisherman's Bend Terminal Station
GNTS | Glenrowan Terminal Station
GTS | Geelong Terminal Station
HGTS | Haunted Gully Terminal Station
HOTS | Horsham Terminal Station
HTS | Heatherton Terminal Station
HWPS | Hazelwood Power Station
HWTS | Hazelwood Terminal Station
HYTS | Heywood Terminal Station
JDSS | Jinderra Switching Station
JLA | Bluescope Steel Customer Substation
JLGA | Jeeralang A Gas Station
JLGB | Jeeralang B Gas Station
JLTS | Jeeralang Terminal Station
KGTS | Kerang Terminal Station
KMTS | Kiamal Terminal Station
KTS | Keilor Terminal Station
LYPB | Loy Yang B Power Station
LYPS | Loy Yang Power Station
MBTS | Mount Beauty Terminal Station
MKPS | Mc Kay Creek Power Station
MLTS | Moorabool Terminal Station
MOPS | Morlake Power Station
MPS | Morwell Power Station
MRTS | Murrawarra Terminal Station
MSS | Murray Switching Station
MTS | Malvern Terminal Station
MWTS | Morwell Terminal Station
NPSD | Newport D Power Station
PTH | Point Henry Customer Substation
RCTS | Red Cliff Terminal Station
ROTS | Rowville Terminal Station
RTS | Richmond Terminal Station
RWTS | Ringwood Terminal Station
SESS | South East Switching Station
SHTS | Shepparton Terminal Station
SMTS | South Morang Terminal Station
SVTS | Springvale Terminal Station
SYTS | Sydenham Terminal Station
TBTS | Tyabb Terminal Station
TGTS | Terang Terminal Station
TRTS | Taronne Terminal Station
TSTS | Templestowe Terminal Station
TTS | Thomastown Terminal Station
WBTS | Waubra Terminal Station
WETS | Wemen Terminal Station
WKPS | West Kiewa Power Station
WMTS | West Melbourne Terminal Station
WOTS | Wodonga Terminal Station
YPS | Yallourn Power Station
YWPS | Yallourn West Power Station

## Table 7.7.3 (hidden)
Table 7.7.3 – Limits identified for proposed priority projects
Limit identification | Define limit | Reason for the limit | Is limit addressed by priority project
HWPS - JLTS No.4 220 kV line | 23 MVA lower than line short term rating | Interplant connection at HWPS with lower rating than line short term rating | Yes
SESS - HYTS No.1 275 kV line | The short term (15 min) rating of this line is 58MVA lower than the short term rating of the Tailem Bend to South East 275 kV line at 35°C | The South East to Heywood lines will become the limiting elements constraining flows on the interconnector between Victoria and South Australia following the interconnector upgrade project and ElectraNet’s proposed NCIPAP project to uprate the 275 kV lines between South East and Tailem Bend to 120°C. | Yes
SESS - HYTS No.2 275 kV line | The short term (15 min) rating of this line is 58MVA lower than the short term rating of the Tailem Bend to South East 275 kV line at 35°C | The South East to Heywood lines will become the limiting elements constraining flows on the interconnector between Victoria and South Australia following the interconnector upgrade project and ElectraNet’s proposed NCIPAP project to uprate the 275 kV lines between South East and Tailem Bend to 120°C. | Yes