{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Contents","Cover","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":2,"defined_names":97,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Contents","index":0,"n_rows":12,"n_cols":6,"rows_kept":12,"cut":false,"hidden":false,"merged":[[8,2,9,3],[2,1,2,10],[4,1,4,10]]}
[" "]
[]
[null,"Electricity Distribution Network Service Provider\nF-factor Reporting Template"]
[]
[null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]

{"sheet":"Cover","index":1,"n_rows":49,"n_cols":7,"rows_kept":49,"cut":false,"hidden":false,"merged":[[10,1,11,8],[13,1,13,8],[48,2,48,6],[42,2,42,3],[42,4,42,7],[46,2,46,6],[47,2,47,6],[38,2,38,3],[38,4,38,7],[41,2,41,3],[41,4,41,7],[37,2,37,3],[37,4,37,7],[32,3,32,8],[30,3,30,8],[15,1,15,8],[26,3,26,8],[28,3,28,8],[26,1,26,2],[31,3,31,5],[14,1,14,8],[16,1,16,8],[17,1,17,8],[21,1,21,8],[19,1,19,8]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Distribution Network Service Provider"]
[null,"Fire start report"]
[]
[null,"This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
[]
[null,"Colour coding of input sheets:"]
[null,"Dark blue = AER headings"]
[null,"Grey = AER instructions"]
[null,"Yellow = Input cells"]
[null,"Light orange = Automatically-generated cells"]
[]
[null,"Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
[null,"The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings."]
[null,"All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
[null,"DNSP:",null,"AusNet Services"]
[]
[null,"DNSP - trading name:"]
[]
[null,"DNSP - Australian business number: ",null,"91 064 651 118"]
[]
[null,"Reporting year:",null,"2017/18"]
[]
[]
[]
[]
[null,"Business address","Address",null,"Level 31, 2 Southbank Boulevard"]
[null,null,"Suburb",null,"Southbank"]
[null,null,null,"State","Victoria","Postcode",3006]
[]
[null,"Postal address","Address",null,"Locked Bag 14051 MCMC"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode",8001]
[]
[]
[null,"Contact name/s","Hawaii Ho"]
[null,"Contact phone/s","03 9695 6350"]
[null,"Contact email address/s","Hawaii.Ho@ausnetservices.com.au"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":14,"n_cols":15,"rows_kept":14,"cut":false,"hidden":false,"merged":[[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[11,2,11,3],[12,2,12,3],[13,2,13,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"AusNet Services"},"IRU target:",{"$f":"IF(SUM(K6:O6)=0,\"\",SUM(K6:O6))","v":247.7},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!S38:S188)=0,\"\",SUM('2. Individual fire start info'!S38:S188))","v":268.60000000000002},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2017/18"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":-313500.00000000052},null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 2: Summary of total fire starts by F factor Order definition",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,null,{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J2:$J5,K2:K5))","v":247.7},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J2:$J5,L2:L5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>M1),\"\",LOOKUP($B3,$J2:$J5,M2:M5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>N1),\"\",LOOKUP($B3,$J2:$J5,N2:N5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>O1),\"\",LOOKUP($B3,$J2:$J5,O2:O5))","v":""}]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause"]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$769,'1. F-Factor summary'!$B8)","v":0}]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$769,'1. F-Factor summary'!$B9)","v":29}]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$769,'1. F-Factor summary'!$B10)","v":19}]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$769,'1. F-Factor summary'!$B11)","v":4}]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$769,'1. F-Factor summary'!$B12)","v":7}]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$769,'1. F-Factor summary'!$B13)","v":92}]
[null,"Total",{"$f":"SUM(C8:C13)","v":151}]

{"sheet":"2. Individual fire start info","index":3,"n_rows":188,"n_cols":25,"rows_kept":188,"cut":false,"hidden":false,"merged":[[25,1,25,18],[27,1,27,20],[26,1,26,21],[35,19,35,21],[33,1,33,4],[35,2,35,10],[28,1,28,18],[29,1,29,18],[35,11,35,13],[35,14,35,17],[13,1,13,11],[22,1,22,21],[24,1,24,21],[14,1,14,20],[15,1,15,18],[16,1,16,18],[18,1,18,18],[21,1,21,18],[19,1,19,18],[23,1,23,18],[20,1,20,18],[17,1,17,18],[3,22,3,24],[4,22,4,24],[5,22,5,24],[7,1,7,21],[11,1,11,2],[9,1,9,21]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"AusNet Services"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2017/18"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by AusNet Services. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"AusNet Services must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Address of the property on which the incident occurred or closest to the incident"]
[null,"   (5) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the AusNet Services network"}]
[null,"   (7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (8) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council"]
[null,"   (12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website)"]
[null,{"$f":"\"   (14) \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\"'s record number for the incident\"","v":"   (14) AusNet Services's record number for the incident"}]
[null,"   (15) ESV's OSIRIS reference number for the incident"]
[null,"   (16) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 2: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,null,"Fire Type",null,null,"Risk Factors",null,null,null,"IRU \namount","Additional information"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","Address of incident 4","ID of \nnearest \nasset 5","ID of nearest \npolyphase \nline 6","Voltage of line in which \nfire start \noccurred 7","Network categorisation 8","Type of primary asset \ninvolved in fire start 9","Phase(s) of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","Location \narea 12","Location\nmultiplier","Fire \ndanger \nrating 13","Danger multiplier","Product of multipliers","DNSP record number 14","OSIRIS \n(ESV) reference \nnumber 15","Fault \ndescription 16"]
[{"$f":"COUNTA(C38:O38,Q38,T38:V38)","v":17},1,"2017-07-01T13:25:00",42917.559027777781,-38.096054011319097,146.549085010716,"19 HAKEA COURT, GLENGARRY NORTH VIC 3854",2602078,"TGN31","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",{"$f":"IF(O38=\"\",\"\",IF(O38=\"LBRA only\",0.2,IF(O38=\"HBRA only\",1,IF(O38=\"within electric line construction area\",19.8,IF(O38=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"NO FORECAST",{"$f":"IF(Q38=\"\",\"\",IF(Q38=\"No forecast\",0.1,IF(Q38=\"Low-moderate\",0.2,IF(Q38=\"High\",0.5,IF(Q38=\"Very high\",1,IF(Q38=\"Severe\",2,IF(Q38=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P38=\"\",R38=\"\"),\"\",IF(AND(O38=\"within electric line construction area\",Q38=\"No forecast\"),1,P38*R38))","v":0.1},228880,"20170824SPN_01","EDO fuse tube burnt off",null,null,"Overhead conductors"]
[17,2,"2017-07-01T15:37:00",42917.650694444441,-37.984701981995698,145.46375399231601,"80 BLUE RIDGE ROAD, DEWHURST VIC 3808",521902,"BWN14","Low voltage AC (<1kV)","RURAL SHORT"," - connection box","three phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,228875,"20170824SPN_02","suspected loose connection within the FOLCB",null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[17,3,"2017-07-06T08:49:00",42922.367361111108,-37.893660939032998,145.291897497435,"61 GLENFERN ROAD, FERNTREE GULLY VIC 3156",1302470,"FGY22","22kV AC","URBAN","Other ","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,229035,"20170706SPN_03","Investigation completed with following findings:\nThe root cause of the intermittent internal capacitor can failure is believed to be due to insulation failure between\ncapacitor foils within the can. Intermittent nature of the capacitor fault does not last long enough to trigger the circuit breaker to trip.\nThe non-operation of the No2 Cap Bank protection relay was confirmed to be correct and as expected for an\nintermittent type fault. The Cap Bank protection relay was subsequently tested and found to operate as designed.",null,null," - overhead conductor (bare; all aluminium conductor)"]
[17,4,"2017-07-08T07:36:00",42924.316666666666,-36.232944017990995,147.847585974731,"234 WATERS LANE, COLAC COLAC VIC 3707",5215357,"WOTS24","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,229085,"20171025SPN_01","EDO fuse hung up",null,null," - overhead conductor (bare; copper)"]
[17,5,"2017-07-19T10:06:00",42935.42083333333,-36.364866012135401,146.48628700409,"501 RUSHOLME ROAD, TARRAWINGEE VIC 3678",5111668,"WN5","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,229279,"20170911SPN_02","EDO fuse candling.\nMaybe attributable to bird found nearby.",null,null," - overhead conductor (bare; steel)"]
[17,6,"2017-08-02T05:40:00",42949.236111111109,-38.287018989932996,146.19073502126801,"1159 MORWELL-THORPDALE ROAD, THORPDALE VIC 3835",2207558,"MOE31","22kV AC","RURAL LONG"," - dropper / bridge","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,229555,"20170803SPN_01","Defective dropper.",null,null," - overhead conductor (ABC)"]
[17,7,"2017-08-02T18:35:00",42949.774305555555,-38.476527004663197,145.94651700860101,"2 BAIR STREET, LEONGATHA VIC 3953",2003702,"LGA22","Low voltage AC (<1kV)","RURAL SHORT"," - connection box","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,229563,"20170803SPN_02","There were no visible causes for krone box failing.  Probable high customer volts or/and poor connection.",null,null," - overhead conductor (covered uninsulated)"]
[17,8,"2017-08-03T19:50:00",42950.826388888891,-38.180781004897796,147.090091993736,"10 ANDREWS ROAD, LONGFORD VIC 3851",2505283,"SLE31","22kV AC","RURAL LONG"," - fuse (EDO fuse)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,229580,"20170807SPN_01","On arrival - fault crew observed candling BA on SL245 LIs No 2505283, \nNil fire damage to ground.\nNote blown EDO fuse also at Sub pole LIS 1614360 WELLINGTON COBB SUB.\nCause of Fault determined to be defective Surge Divertor on Wellington Cobb Substation.",null,null," - overhead conductor (insulated)"]
[17,9,"2017-08-14T10:53:00",42961.453472222223,-35.9998739927087,146.494783981398,"445 UP RIVER ROAD, CARLYLE VIC 3685",5209079,"BWA23","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,229737,"20170911SPN_01","EDO fuse hung up - moisture ingress and incorrect type (fixed fire chokes) previously fitted.",null,null,"Service lines"]
[17,10,"2017-08-25T19:27:00",42972.810416666667,-37.888471228068596,145.29450780270199,"CAR YARD, 1097 BURWOOD HIGHWAY, FERNTREE GULLY VIC 3156",1312538,"FGY23","Low voltage AC (<1kV)","URBAN"," - lamps (major road)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,229982,"20170830SPN_01","the street light PE cell had failed and caught fire",null,null," - overhead service conductor (residential)"]
[17,11,"2017-09-02T06:35:00",42980.274305555555,-36.6631379813183,145.47099502691299,"1549 ARCADIA TWO CHAIN ROAD, MIEPOLL VIC 3666",3904466,"BN1","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,230120,"20170904SPN_02","EDO fuse hung up. \nLikely interference of bird - no photo to support.",null,null," - overhead service conductor (commercial / industrial)"]
[17,12,"2017-09-03T14:05:00",42981.586805555555,-37.052534501678799,148.808570382753,"1900 BONANG ROAD, DELEGATE RIVER VIC 3888",5768315,"BM8B31","22kV AC","RURAL SHORT"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,230123,"20170904SPN_01","Fault crew observed evidence of fire onsite but extinguished. \nTree fell over mains and conductor fell to the ground in the area.",null,null," - overhead service conductor (subdivision / construction)"]
[17,13,"2017-09-04T23:54:00",42982.995833333334,-37.860889007970997,148.034363016051,"45 LAKE BUNGA BEACH ROAD, LAKE BUNGA VIC 3909",1902793,"NLA34","Low voltage AC (<1kV)","RURAL SHORT"," - connection box","two phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,230171,"20170905SPN_03","likely caused by polluted insulator (salt )",null,null," - overhead service conductor (other)"]
[17,14,"2017-09-05T15:03:00",42983.627083333333,-38.560888023722093,145.71319802881999,"590 INVERLOCH-KONGWAK ROAD, WATTLE BANK VIC 3995",5656096,"WGI22","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,230177,"20171023SPN_02","BA fuse candled.",null,null," - underground service cable (residential)"]
[17,15,"2017-09-07T17:00:00",42985.708333333336,-38.100231986977604,146.032458007564,"1965 OLD SALE ROAD, SHADY CREEK VIC 3821",2706751,"WGL24","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,230207,"20170912SPN_01","BA fuse candling",null,null," - underground service cable (commercial / industrial)"]
[17,16,"2017-09-11T18:46:00",42989.781944444447,-37.672089003156501,145.12651503008701,"311 YAN YEAN ROAD, PLENTY VIC 3090",926107,"ELM15","Low voltage AC (<1kV)","RURAL SHORT"," - overhead conductor (bare; copper)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,230242,"20171023SPN_03","Heat generated from the poor connection caused the cable to fail and fall to the ground.\nThe hot particles of the IPC and/ or copper cable could have made contact with the ground. \nno photo is available.",null,null," - underground service cable (subdivision / construction)"]
[17,17,"2017-09-19T08:32:00",42997.355555555558,-38.492963016444897,145.29682497600302,"128 MCFEES ROAD, RHYLL VIC 3923",2805565,"PHI11","22kV AC","RURAL SHORT"," - overhead conductor (bare; aluminium core steel reinforced)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"NO FORECAST",0.1,{"$f":"IF(OR(P54=\"\",R54=\"\"),\"\",IF(AND(O54=\"within electric line construction area\",Q54=\"No forecast\"),1,P54*R54))","v":0.1},230386,"20171024SPN_01","vegetation contact",null,null," - underground service cable (other)"]
[17,18,"2017-10-08T16:03:00",43016.668749999997,-38.077512750847504,145.28571682147302,"46 MARINER CLOSE, CRANBOURNE NORTH VIC 3977",594816,"CRE23","22kV AC","URBAN"," - transformer (kiosk mounted)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,230654,"20171020SPN_01","The root cause could not be determined.",null,null,"Underground cables"]
[17,19,"2017-10-10T10:40:00",43018.444444444445,-36.136218023154505,146.90179798529601,"169 CHAPPLE STREET, WODONGA VIC 3690",5219216,"WOTS12","22kV AC","RURAL SHORT"," - fuse (powder filled)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,230691,"20171129SPN_02","Fuse candling",null,null," - underground cable"]
[17,20,"2017-10-12T17:40:00",43020.736111111109,-37.947987990863695,145.48728575683,"8 FERN GULLY ROAD, COCKATOO VIC 3781",417489,"BGE22","22kV AC","RURAL SHORT"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,230730,"20171129SPN_03","candled fuse\nno photo available",null,null," - underground communications cable"]
[17,21,"2017-10-15T10:00:00",43023.416666666664,-37.724654982049401,147.80194200149703,"1881 GREAT ALPINE ROAD, WISELEIGH VIC 3885",1604421,"BDL8","22kV AC","RURAL LONG"," - switch (disconnector/isolator)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"NO FORECAST",0.1,0.45999999999999996,230752,"20171023SPN_01","22kV Blade isolator failed with fixed jaw burnt out.",null,null,"Poles"]
[17,22,"2017-10-19T11:17:00",43027.470138888886,-38.037919001097599,145.248642988911,"108-110 ROBJANT STREET, HAMPTON PARK VIC 3976",505186,"HPK23","22kV AC","URBAN"," - switch (disconnector/isolator)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,230821,"20171114SPN_03","bird nest on the gas switch open point",null,null," - pole (concrete)"]
[17,23,"2017-10-24T10:15:00",43032.427083333336,-37.631646984249393,145.045362009651,"QUARRY ROAD, EPPING VIC 3076",914098,"EPG32","22kV AC","RURAL SHORT"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,230893,"20171114SPN_02","bird strike, conductor down.",null,null," - pole (steel)"]
[17,24,"2017-10-24T11:40:00",43032.486111111109,-38.017227982639298,147.004803025152,"36 COBAINS ROAD, BUNDALAGUAH VIC 3851",2511666,"MFA23","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","single phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,230896,"20171102SPN_02","bird likely killed by a flashover fell to the ground and started the fire",null,null," - pole (wood)"]
[17,25,"2017-10-27T20:30:00",43035.854166666664,-37.798773003516494,147.87721197789901,"197 CUNNINGHAM ROAD, SWAN REACH VIC 3903",1911236,"BDL41","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,230961,"20171128SPN_01","Burnt EDO fuse tube.",null,null,"Crossarms"]
[17,26,"2017-11-10T20:16:00",43049.844444444447,-36.095375624929396,146.31995519960202,"1447 LILLIPUT-NORONG ROAD, NORONG VIC 3682",5235554,"WN3","12.7kV AC (SWER)","RURAL LONG"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,231154,"20171114SPN_01","A tree on the customer's property fell over and contacted the overhead HV conductor.",null,null," - crossarm (wood)"]
[17,27,"2017-11-16T18:33:00",43055.772916666669,-38.151965964234897,145.57413297997601,"165 BUNYIP RIVER ROAD, NAR NAR GOON VIC 3812",512440,"PHM33","Low voltage AC (<1kV)","RURAL LONG"," - connection box","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,231255,"20171117SPN_01","Burnt out pole junction box.",null,null," - crossarm (steel)"]
[17,28,"2017-11-21T07:20:00",43060.305555555555,-37.606406981219202,145.41247397390802,"35 LORIMERS LANE, DIXONS CREEK VIC 3775",1007063,"LDL14","Low voltage AC (<1kV)","RURAL SHORT"," - underground service cable (residential)","two phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,231317,"20171123SPN_03","Underground service cable fault.",null,null," - crossarm (other)"]
[17,29,"2017-11-21T10:15:00",43060.427083333336,-37.716548430080501,145.09861002916699,"152 ELDER STREET, GREENSBOROUGH VIC 3088",928045,"WT15","Low voltage AC (<1kV)","URBAN"," - overhead conductor (bare; aluminium core steel reinforced)","two phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,231318,"20171127SPN_02","A truck contacted Telstra overhead assets which caused them to make contact with AusNet Services' overhead LV distribution conductors.",null,null,"Overhead assets"]
[17,30,"2017-11-22T07:03:00",43061.293749999997,-37.436743981532594,144.977824014346,"20 MACSFIELD ROAD, WALLAN VIC 3756",912838,"KLO24","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,231358,"20171220SPN_01","Candled EDO fuse tube.",null,null," - capacity balancing units"]
[17,31,"2017-11-22T18:30:00",43061.770833333336,-37.674168007250302,145.859786013194,"20 UPPER YARRA DAM ROAD, REEFTON VIC 3799",1409238,"WYK13","Low voltage AC (<1kV)","RURAL SHORT"," - overhead service conductor (residential)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,231367,"20171123SPN_04","Street light service cable fell to ground due to burnt through wrap-on preform termination.",null,null," - connector / termination"]
[17,32,"2017-11-25T12:10:00",43064.506944444445,-36.440419982325096,146.37400298717199,"MIRANDA HIGH COUNTRY WINE, 1019 SNOW ROAD, OXLEY VIC 3678",5103451,"WN5","22kV AC","RURAL LONG"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,231400,"20180111SPN_04","Candled BA fuse tube.",null,null," - dropper / bridge"]
[17,33,"2017-11-26T10:00:00",43065.416666666664,-38.4336349946852,146.037147982806,"105 STRZELECKI HWY, BOOROOl VIC 3953",2002447,"LGA11","22kV AC","RURAL LONG"," - fuse (EDO fuse)","three phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,231401,"20171220SPN_04","Burnt EDO fuse tube.",null,null," - guy wire"]
[17,34,"2017-11-27T11:16:00",43066.469444444447,-36.892870008495393,145.207467981067,"ROSEDALE FARM, 729 AERODROME ROAD, AVENEL VIC 3664",4706126,"SMR8","22kV AC","RURAL LONG"," - overhead conductor (bare; steel)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,231422,"20171204SPN_01","A tip truck trailer made contact with overhead 22kV line.",null,null," - insulator tie wires / connections"]
[17,35,"2017-11-28T06:31:00",43067.271527777775,-38.551901472229297,146.126673026182,"20 BUTTERWORTHS ROAD, STONY CREEK VIC 3957",2013243,"LGA13","12.7kV AC (SWER)","RURAL LONG"," - fuse (EDO fuse)","single wire earth return (SWER)","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,231444,"20180111SPN_06","EDO fuse tube candled.",null,null," - insulators"]
[17,36,"2017-11-28T13:45:00",43067.572916666664,-37.826407000808693,145.451056013998,"90 MONBULK-SEVILLE ROAD, WANDIN EAST VIC 3139",1012337,"LDL13","22kV AC","RURAL SHORT"," - transformer (pole mounted)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,231451,"20171129SPN_01","Transformer internal fault. Oil leak - Mechanical damage (leaking gasket/broken bushing etc.).",null,null," - tower"]
[17,37,"2017-11-29T14:45:00",43068.614583333336,-37.628548792235101,145.09679151373399,"1079 PLENTY ROAD, SOUTH MORANG VIC 3752",917432,"DRN11","22kV AC","RURAL SHORT"," - underground cable","three phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,231481,"20171130SPN_01","Underground asset failure - fault at the Cable Head Pole (CHP).",null,null," - traction lines"]
[17,38,"2017-11-29T16:05:00",43068.670138888891,-38.294636004268995,146.59766501558499,"55 WHITELAWS TRACK, CALLIGNEE VIC 3844",2605775,"TGN23","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"HIGH",0.5,{"$f":"IF(OR(P75=\"\",R75=\"\"),\"\",IF(AND(O75=\"within electric line construction area\",Q75=\"No forecast\"),1,P75*R75))","v":0.5},231480,"20171130SPN_02","Bird flew into EDO fuse unit on concrete pole resulting in a flashover and deceased bird.",null,null,"Underground assets"]
[{"$f":"COUNTA(C76:O76,Q76,T76:V76)","v":17},39,"2017-11-30T21:17:00",43069.886805555558,-37.064311016894699,146.075562016817,"82 STONELEIGH ROAD, MANSFIELD VIC 3722",3918752,"MSD1","22kV AC","RURAL LONG"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O76=\"\",\"\",IF(O76=\"LBRA only\",0.2,IF(O76=\"HBRA only\",1,IF(O76=\"within electric line construction area\",19.8,IF(O76=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"HIGH",{"$f":"IF(Q76=\"\",\"\",IF(Q76=\"No forecast\",0.1,IF(Q76=\"Low-moderate\",0.2,IF(Q76=\"High\",0.5,IF(Q76=\"Very high\",1,IF(Q76=\"Severe\",2,IF(Q76=\"Extreme\",3.5,5)))))))","v":0.5},2.2999999999999998,231500,"20171204SPN_02","Bird caused a flashover. No photos are available.",null,null," - LV pillar"]
[17,40,"2017-12-01T03:39:00",43070.152083333334,-38.477900019000494,146.02073002594202,"15 PORS ROAD, NERRENA VIC 3953",2008120,"LGA14","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,231499,"20180115SPN_03","EDO fuse candled.",null,null," - services pit"]
[17,41,"2017-12-02T19:39:00",43071.818749999999,-38.133186015167894,145.736073992775,"105 KNIGHTS ROAD, LONGWARRY VIC 3816",2716128,"WGL12","Low voltage AC (<1kV)","RURAL LONG"," - connection box","single phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,231507,"20180116SPN_02","Cause not identified but most likely due to high impedance fault.",null,null,"Transformers"]
[17,42,"2017-12-04T11:35:00",43073.482638888891,-37.780750985728801,145.42722901403599,"7 UNION ROAD, WANDIN NORTH VIC 3139",1002142,"LDL23","Low voltage AC (<1kV)","RURAL LONG"," - lamps (minor road)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,231520,"20180117SPN_01","Burnt out street light fitting. The damage was contained within the light head.",null,null," - transformer (pole mounted)"]
[17,43,"2017-12-08T09:09:00",43077.381249999999,-38.630741737606598,146.349146065664,"465 SILCOCKS HILL ROAD, TOORA NORTH VIC 3962",2014437,"FTR12","12.7kV AC (SWER)","RURAL LONG"," - pole (wood)","single wire earth return (SWER)","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,231603,"20180117SPN_02","Broken pole stay wire.",null,null," - transformer (kiosk mounted)"]
[17,44,"2017-12-09T13:09:00",43078.54791666667,-37.756471006450901,145.22527098667001,"254 Gold Memorial Rd, Warrandyte VIC 3113",1224905,"RWN33","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,231784,"20171213SPN_01","Tree fell onto overhead HV line.",null,null," - transformer (ground outdoor mounted)"]
[17,45,"2017-12-13T15:28:00",43082.644444444442,-38.196637016567294,146.325348995902,"Haunted Hills Road, Newborough VIC 3825",5614362,"MOE31","Low voltage AC (<1kV)","RURAL LONG"," - switch (disconnector/isolator)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,231688,"20171214SPN_01","Loose fuse in LV fuse isolator.",null,null," - transformer (indoor chamber mounted)"]
[17,46,"2017-12-13T21:46:00",43082.906944444447,-38.018375556869202,145.29977406708201,"Magid Drive, Narre Warren VIC 3805",593824,"HPK12","Low voltage AC (<1kV)","URBAN"," - lamps (major road)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,231963,"20180201SPN_01","HPS street lantern head caught fire due to faulty capacitor.",null,null," - transformer (any other type)"]
[17,47,"2017-12-14T11:14:00",43083.468055555553,-37.600550988783297,145.09558097697402,"575 BRIDGE INN ROAD, MERNDA VIC 3754",917516,"DRN12","Low voltage AC (<1kV)","RURAL SHORT"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,231699,"20171215SPN_01","Broken LV copper conductor.",null,null," - measurement transformer (current transformer)"]
[17,48,"2017-12-18T16:19:00",43087.679861111108,-38.134255693101395,147.095439402545,"Sale Common Nature Reserve",1613390,"SLE-LFD 66kV","66kV AC","UNCLASSIFIED"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,231768,"20171219SPN_02","An Eagle caused a flashover to earth on a 66kV pole structure.",null,null," - measurement transformer (voltage transformer)"]
[17,49,"2017-12-18T18:26:00",43087.768055555556,-38.200177985701494,146.31675901353299,"3-7 HAUNTED HILLS ROAD, NEWBOROUGH VIC 3825",596942,"MOE13","Low voltage AC (<1kV)","RURAL SHORT"," - fuse (any other type)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,231769,"20171219SPN_03","Loose LV fuse hinge at pole.",null,null," - measurement transformer (capacitive voltage transformer)"]
[17,50,"2017-12-18T22:38:00",43087.943055555559,-37.690546931536694,145.103604314394,"2 GOONYAH COURT, GREENSBOROUGH VIC 3088",5720887,"ELM31","Low voltage AC (<1kV)","URBAN"," - LV pillar","three phase","Otherwise started by a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,231770,"20171219SPN_04","Root cause not designated in IMS but appears to be a 3 phase short circuit. Request made to Engineering to investigate.",null,null,"Fuses and switchgear"]
[17,51,"2017-12-19T18:30:00",43088.770833333336,-37.7757515577755,145.337535725468,"456-458 HULL ROAD, MOOROOLBARK VIC 3138",1014723,"LDL24","22kV AC","URBAN"," - pole (concrete)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"VERY HIGH",1,0.2,231792,"20171221SPN_02","Lightning strike to concrete HV pole",null,null," - fuse (boric acid)"]
[17,52,"2017-12-26T14:30:00",43095.604166666664,-36.383118005090992,146.25752999471899,"235 GRAVEL PIT ROAD, WANGARATTA SOUTH VIC 3678",5121021,"WN4","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,231819,"20180102SPN_01","EDO fuse candling",null,null," - fuse (EDO fuse)"]
[17,53,"2017-12-27T11:35:00",43096.482638888891,-38.135523018466799,146.55766097471201,"675 TRARALGON-MAFFRA ROAD, GLENGARRY VIC 3854",2601158,"TGN31","22kV AC","RURAL LONG"," - dropper / bridge","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"HIGH",0.5,0.5,231820,"20180102SPN_02","Bird strike",null,null," - fuse (Fault Tamer)"]
[17,54,"2017-12-27T11:58:00",43096.498611111114,-37.781683000767202,145.209708991414,"2-4 DRAYTON CRESCENT, PARK ORCHARDS VIC 3114",1205256,"RWN26","22kV AC","RURAL SHORT"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,231822,"20180102SPN_03","trees brought down HV line and caused HV to contact LV lines",null,null," - fuse (powder filled)"]
[17,55,"2017-12-29T21:13:00",43098.884027777778,-37.987704018604006,147.07688197687102,"71 AIRLY ROAD, STRATFORD VIC 3862",2511827,"MFA21","22kV AC","RURAL LONG"," - transformer (pole mounted)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,231828,"20180102SPN_05","Lightning strike to substation transformer.",null,null," - fuse (any other type)"]
[17,56,"2017-12-31T11:21:00",43100.472916666666,-37.856597123066997,145.23757920600301,"20 MARIEMONT AVENUE, WANTIRNA VIC 3152",5804164,"BRA32","Low voltage AC (<1kV)","URBAN"," - LV pillar","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,231962,"20180214SPN_02","Electrical breakdown of old HRC fuse fittings inside LV pillar.",null,null," - circuit breaker"]
[17,57,"2018-01-04T13:29:00",43104.561805555553,-38.100633998981095,145.74470601713099,"260 COOK ROAD, LONGWARRY VIC 3816",2709198,"WGL12","22kV AC","RURAL LONG"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,231845,"20180111SPN_03","Bird caused a flashover at pole top.",null,null," - switch (disconnector/isolator)"]
[17,58,"2018-01-04T17:35:00",43104.732638888891,-38.160898008453394,145.613903018787,"215 NUMBER SEVEN DRAIN ROAD, CORA LYNN VIC 3814",512759,"PHM33","22kV AC","RURAL LONG"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,231839,"20180214SPN_04","Burnt BA fuse tube / candled.",null,null," - switch (earth)"]
[17,59,"2018-01-04T18:23:00",43104.765972222223,-37.378360994026202,144.963635980947,"LAURENVALE, 1935 OLD SYDNEY ROAD, WALLAN VIC 3756",4718426,"SMTS-KMS 66kV","66kV AC","UNCLASSIFIED"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,231863,"20180111SPN_02","Tree leaning on 66 kV overhead conductors.",null,null," - switch (FuseSaver)"]
[17,60,"2018-01-06T09:24:00",43106.39166666667,-37.735639612673701,145.22237003907,"2 KANGAROO GROUND-WARRANDYTE ROAD, NORTH WARRANDYTE VIC 3113",1206325,"RWN34","22kV AC","RURAL SHORT"," - overhead conductor (ABC)","three phase","Otherwise started by a distribution system","within electric line construction area",19.8,"EXTREME",3.5,69.3,231899,"20180108SPN_01","The catenary wire shorted to HVABC conductor.",null,null," - switch (any other type)"]
[17,61,"2018-01-12T06:22:00",43112.265277777777,-37.925319019471303,145.497474007769,"137 WOORI YALLOCK ROAD, COCKATOO VIC 3781",420317,"BGE22","22kV AC","RURAL SHORT"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"VERY HIGH",1,0.2,231978,"20180112SPN_01","A large branch failed from a large gum tree due to decay from an old wound fell into overhead HV and LV conductors.",null,null,"SCADA, network control and protection systems"]
[17,62,"2018-01-12T16:26:00",43112.68472222222,-37.691764928892795,144.96048209194299,"metropolitan ring road",5642607,"SMTS-KMS 66kV","66kV AC","UNCLASSIFIED"," - pole (wood)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,231993,"20180205SPN_01","insulator tracking",null,null," - audio frequency load controller (AFLC)"]
[17,63,"2018-01-15T17:08:00",43115.713888888888,-38.586799019735999,146.01233899504402,"100 MCILWAINE STREET, MEENIYAN VIC 3956",2001927,"LGA14","22kV AC","RURAL LONG"," - overhead conductor (bare; steel)","three phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,232036,"20180116SPN_01","HV conductor on ground. Some signs of corrosion.",null,null," - arc suppresion coil"]
[17,64,"2018-01-16T20:34:00",43116.856944444444,-36.693186019874602,146.86346398788402,"457 MOUNT BUFFALO ROAD, POREPUNKAH VIC 3740",4505257,"BRT22","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","three phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,232052,"20180220SPN_01","Burnt EDO Fuse Tube",null,null," - automatic circuit recloser (ACR)"]
[17,65,"2018-01-19T18:37:00",43119.775694444441,-37.6786230219872,145.14430997645701,"1 PLEASANT VIEW COURT, DIAMOND CREEK VIC 3089",924181,"ELM32","Low voltage AC (<1kV)","URBAN"," - switch (disconnector/isolator)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"SEVERE",2,0.4,232087,"20180122SPN_02","Hot connections at crossarm mounted LV fuse isolator.",null,null," - communications linear assets"]
[17,66,"2018-01-20T21:20:00",43120.888888888891,-37.937245978188798,145.488909988404,"10 NEVILLE STREET, COCKATOO VIC 3781",417268,"BGE22","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,232090,"20180122SPN_01","Tree branch fell onto overhead HV line.",null,null," - communications network assets"]
[17,67,"2018-01-21T22:46:00",43121.948611111111,-37.814365993694793,145.25448198403899,"32 VICTORIA STREET, RINGWOOD EAST VIC 3135",1217471,"RWT32","Low voltage AC (<1kV)","URBAN"," - fuse (any other type)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,232095,"20180202SPN_01","Burnt out LV FSD Krone box.",null,null," - communications site infrastructure"]
[17,68,"2018-01-23T02:00:00",43123.083333333336,-38.233901019311695,146.29258401386403,"60 YASMIN DRIVE, HERNES OAK VIC 3825",2208544,"MOE31","Low voltage AC (<1kV)","RURAL LONG"," - connection box","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,232114,"20180123SPN_01","Burnt out LV fuse Mains box. High impedance fault.",null,null," - field devices"]
[17,69,"2018-01-24T20:19:00",43124.84652777778,-38.576061994256591,145.845697014009,"965 KOONWARRA-INVERLOCH ROAD, LEONGATHA SOUTH VIC 3953",2010941,"LGA23","22kV AC","RURAL LONG"," - connector / termination","three phase","Otherwise started by a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,232136,"20180125SPN_01","Corroded and loose PG clamps on bridges lead to arcing.",null,null," - local network wiring assets"]
[17,70,"2018-01-28T05:18:00",43128.220833333333,-37.726043016705496,145.14041897785899,"32 ELY STREET, ELTHAM VIC 3095",900437,"ELM34","Low voltage AC (<1kV)","RURAL SHORT"," - overhead conductor (covered uninsulated)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"VERY HIGH",1,{"$f":"IF(OR(P107=\"\",R107=\"\"),\"\",IF(AND(O107=\"within electric line construction area\",Q107=\"No forecast\"),1,P107*R107))","v":0.2},232161,"20180129SPN_02","LV transformer lead burned through IPC which dripped hot metal which started a small fire.",null,null," - master station assets"]
[17,71,"2018-01-28T13:05:00",43128.545138888891,-36.222888986537804,147.25747799784102,"201 YABBA ROAD, TALLANGATTA EAST VIC 3700",5211158,"WOTS24","22kV AC","RURAL LONG"," - insulators","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,232160,"20180129SPN_01","Broken HV insulator.",null,null," - neutral earthing resistor"]
[17,72,"2018-01-28T20:10:00",43128.840277777781,-37.774700012316096,145.24038999851001,"3 DELATITE COURT, WARRANWOOD VIC 3134",1218137,"RWN31","Low voltage AC (<1kV)","RURAL SHORT"," - connector / termination","three phase","Otherwise started by a distribution system","LBRA only",0.2,"VERY HIGH",1,0.2,232162,"20180129SPN_03","Red phase conductor D burn through connection (loose connection) and lead from isolator at substation pole.",null,null," - oil-filled circuit recloser (OCR)"]
[17,73,"2018-01-29T02:18:00",43129.095833333333,-36.084060996937296,146.73377401751901,"998 PLUNKETTS ROAD, BARNAWARTHA NORTH VIC 3691",5208299,"BWA22","22kV AC","RURAL LONG"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,232163,"20180129SPN_04","A bat caused a flashover between a steel crossarm and a HV conductor.",null,null," - rapid earth fault current limiter (REFCL)"]
[17,74,"2018-01-29T05:35:00",43129.232638888891,-38.508286992337496,145.59246800456799,"430 KOETSVELDT ROAD, RYANSTON VIC 3992",2809269,"WGI22","Low voltage AC (<1kV)","RURAL LONG"," - connection box","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,232174,"20180130SPN_01","Pole mounted FOLCB caught fire. High impedance fault.",null,null," - surge diverter"]
[17,75,"2018-01-30T01:42:00",43130.070833333331,-37.8172939838255,147.73682599364301,"910 PRINCES HIGHWAY, NICHOLSON VIC 3882",1611151,"BDL6","22kV AC","RURAL SHORT"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,232190,"20180130SPN_03","A burnt bird was found at base of pole which indicates a flashover at the pole.",null,null," - voltage regulator"]
[17,76,"2018-01-31T15:23:00",43131.640972222223,-36.159165024308798,146.51586102081001,"88 BENNETTS ROAD, LILLIPUT VIC 3682",5105092,"WN3","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,232237,"20180308SPN_08","Candled BA fuse.",null,null,"Public lighting"]
[17,77,"2018-01-31T21:02:00",43131.876388888886,-38.224191981027595,146.06136801610202,"1 SAND PIT ROAD, YARRAGON VIC 3823",2203792,"MOE22","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,232238,"20180313SPN_04","Candled EDO fuse tube.",null,null," - brackets (major road)"]
[17,78,"2018-02-06T18:00:00",43137.75,-36.387311005158701,147.041357981484,"DUNDEE, 3162 KIEWA VALLEY HIGHWAY, KERGUNYAH VIC 3691",5200908,"WOTS11","22kV AC","RURAL LONG"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,232306,"20180207SPN_01","Raised trailer of a fertiliser truck has allegedly contacted overhead HV conductors.",null,null," - brackets (minor road)"]
[17,79,"2018-02-07T18:24:00",43138.76666666667,-37.662629005771194,145.01520599727098,"18 KIAMA DRIVE, LALOR VIC 3075",911324,"EPG31","Low voltage AC (<1kV)","URBAN"," - connector / termination","three phase","Otherwise started by a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,232325,"20180208SPN_01","LV ABC connector failed.",null,null," - lamps (major road)"]
[17,80,"2018-02-07T19:51:00",43138.82708333333,-37.683222997143702,144.98726100456699,"58 SHERWOOD DRIVE, THOMASTOWN VIC 3074",907631,"TT6","Low voltage AC (<1kV)","URBAN"," - switch (disconnector/isolator)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,232327,"20180208SPN_03","Failed / burnt out LV isolator on pole.",null,null," - lamps (minor road)"]
[17,81,"2018-02-10T19:59:00",43141.832638888889,-37.830650022914597,145.67619802171302,"85 BLACKSANDS ROAD, THREE BRIDGES VIC 3797",1411451,"WYK23","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,232381,"20180212SPN_03","Tall tree fell into overhead HV conductor.",null,null," - luminaires (major road)"]
[17,82,"2018-02-12T21:58:00",43143.915277777778,-38.649047003046697,146.219526999903,"5 JACKSONS ROAD, FOSTER VIC 3960",2024724,"FTR21","22kV AC","RURAL LONG"," - transformer (pole mounted)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,232394,"20180213SPN_01","A possum made contact with live HV on transformer which resulted in a small ground fire.",null,null," - luminaires (minor road)"]
[17,83,"2018-02-14T07:20:00",43145.305555555555,-37.690644542898895,145.01005503574703,"19 HIGH STREET, THOMASTOWN VIC 3074",907481,"TT7","22kV AC","URBAN"," - overhead conductor (bare; all aluminium conductor)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"VERY HIGH",1,0.2,232493,"20180222SPN_01","Burnt HV lead on pole mounted Gas Switch.",null,null," - poles / columns (major road)"]
[17,84,"2018-02-14T09:38:00",43145.401388888888,-38.221193711614198,145.59216779290801,"185 OBRIENS ROAD, BAYLES VIC 3981",513344,"LLG11","22kV AC","RURAL SHORT"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,232492,"20180307SPN_01","Large tree branch fell into overhead HV conductor.",null,null," - poles / columns (minor road)"]
[17,85,"2018-02-14T10:03:00",43145.418749999997,-38.324153986152595,146.46026601547803,"36 DUSTING ROAD, HAZELWOOD SOUTH VIC 3840",2614828,"MWT24","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","single phase","Otherwise started by a distribution system","HBRA only",1,"VERY HIGH",1,1,232416,"20180215SPN_01","Cause is possibly due to corrosion",null,null,"Other "]
[17,86,"2018-02-14T12:58:00",43145.540277777778,-38.255665019105003,146.48979498451999,"582 FIRMINS LANE, HAZELWOOD NORTH VIC 3840",2577249,"TGN23","22kV AC","RURAL SHORT"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"VERY HIGH",1,1,233532,"20180511SPN_02","private tree failed at root base (below ground) from extreme winds and brought down HV line.\nInvestigation confirms\n•\tTree outside clearance space – span is compliant re vegetation – trunk was approximately 7 metres west of the nearest overhead conductors\n•\tSpecies of tree – Radiata/Monterey Pine (Pinus radiata).\n•\tHeight approximately 21 metres – Diameter at Breast Height (DBH) 700mm wide \n•\tNo obvious structural hazards with tree\n•\tTree failed at root base via root shearing below ground level from extreme winds.\n•\tTree located on Private property.",null,null," - connection box"]
[17,87,"2018-02-14T20:15:00",43145.84375,-38.241321981758304,145.87558298437003,"1729 LARDNERS TRACK, LARDNER VIC 3821",2705277,"WGL23","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"VERY HIGH",1,1,232421,"20180215SPN_02","Tree branch fell into overhead HV line.",null,null," - earth / earthing"]
[17,88,"2018-02-18T15:12:00",43149.633333333331,-37.860747020083394,148.03282500587702,"33 LAKE BUNGA BEACH ROAD, LAKE BUNGA VIC 3909",1902792,"NLA34","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,232467,"20180219SPN_01","Suspect lightning strike caused LA to fail with subsequent mal-operation of an EDO fuse which candled, burnt in half with a section falling to ground."]
[17,89,"2018-02-19T19:00:00",43150.791666666664,-37.725746659784704,145.400221825486,"86 KILLARA ROAD, COLDSTREAM VIC 3770",1009667,"LDL23","22kV AC","RURAL LONG"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,232489,"20180221SPN_01","Large tree branch into overhead HV line."]
[17,90,"2018-02-20T16:39:00",43151.693749999999,-38.669140624387801,145.615890047806,"18 SPEAR STREET, CAPE PATERSON VIC 3995",2810983,"WGI33","Low voltage AC (<1kV)","RURAL SHORT"," - overhead service conductor (residential)","two phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"VERY HIGH",1,0.2,232491,"20180221SPN_02","Customer's tree branch rubbed through overhead service cable.",null,null,"Extra low voltage AC (<50V)"]
[17,91,"2018-02-23T16:44:00",43154.697222222225,-37.813152980803494,145.32414402308802,"95 CHERYLNNE CRESCENT, KILSYTH VIC 3137",1004182,"CYN21","Low voltage AC (<1kV)","URBAN"," - connector / termination","three phase","Otherwise started by a distribution system","LBRA only",0.2,"VERY HIGH",1,0.2,232545,"20180226SPN_03","Loose LV bridge clamp.",null,null,"Low voltage AC (<1kV)"]
[17,92,"2018-02-23T21:57:00",43154.914583333331,-38.703816004385097,145.81919001454702,"90 JUPITER BOULEVARD, VENUS BAY VIC 3956",2804943,"WGI14","Low voltage AC (<1kV)","RURAL SHORT"," - connection box","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,232547,"20180226SPN_02","The root cause not determined but considered to be an overheated connection at FOLCB.",null,null,"2.2kV AC"]
[17,93,"2018-02-24T06:59:00",43155.290972222225,-37.641658007751403,144.977832986615,"480 COOPER STREET, EPPING VIC 3076",928777,"EPG35","22kV AC","URBAN"," - overhead conductor (bare; steel)","single phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,232692,"20180308SPN_04","Investigation has shown that the HV line has not been constructed as per any of the plans stored in our system. The pole stay was not lowered as per the work instruction when the HV line was extended.",null,null,"6.6kV AC"]
[17,94,"2018-02-24T17:37:00",43155.734027777777,-37.744143996752697,148.40431800405301,"BURRAGAH, 138 JOINERS ROAD, NEWMERELLA VIC 3886",1905975,"NLA34","22kV AC","RURAL SHORT"," - dropper / bridge","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"HIGH",0.5,0.5,232554,"20180226SPN_05","22kV insulator holding a bridge to Drop Out Fuse broke and the bridge became free and clashed with another phase of the 22kV network.",null,null,"11kV AC"]
[17,95,"2018-02-25T11:15:00",43156.46875,-37.278191999666703,146.13150298169103,"42 OLD EILDON ROAD, JAMIESON VIC 3723",3919353,"MSD1","22kV AC","RURAL LONG"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,232548,"20180226SPN_08","Tree into overhead HV conductors.",null,null,"12.7kV AC (SWER)"]
[17,96,"2018-02-26T13:37:00",43157.567361111112,-36.6364761102583,145.51950578669297,"59 MOGLONEMBY HALL ROAD, MOGLONEMBY VIC 3666",3901466,"BN1","12.7kV AC (SWER)","RURAL LONG"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,232571,"20180227SPN_01","Tip truck driver caused the rear trailer to make contact with a SWER line.",null,null,"22kV AC"]
[17,97,"2018-02-28T12:11:00",43159.507638888892,-37.1014419817689,145.97439197770601,"185 BANUMUM ROAD, MANSFIELD VIC 3722",3918933,"MSD2","22kV AC","RURAL LONG"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,232621,"20180307SPN_02","Tree fell into overhead HV conductor.",null,null,"33kV AC"]
[17,98,"2018-02-28T12:56:00",43159.538888888892,-37.851300999651698,145.25066598547701,"1 STRATTON COURT, BAYSWATER VIC 3153",1218733,"BRA11","Low voltage AC (<1kV)","URBAN"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"VERY HIGH",1,0.2,232626,"20180306SPN_01","Broken LV crossarm.",null,null,"66kV AC"]
[17,99,"2018-02-28T16:56:00",43159.705555555556,-38.2414739926487,145.88589698248302,"54 MAXWELLS ROAD, LARDNER VIC 3821",2705329,"WGL23","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"VERY HIGH",1,1,232633,"20180301SPN_04","In strong wind conditions a tree branch broke and fell into overhead HV conductors.",null,null,"132kV AC"]
[17,100,"2018-02-28T17:15:00",43159.71875,-38.433281987083404,145.79227101387701,"200 BENA ROAD, KORUMBURRA VIC 3950",2006456,"LGA12","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"VERY HIGH",1,1,232627,"20180301SPN_01","A tall tree fell into a HV line.",null,null,"220kV AC"]
[17,101,"2018-02-28T17:54:00",43159.745833333334,-38.138225008674098,146.29484298136501,"200 PURVIS ROAD, TANJIL SOUTH VIC 3825",2210545,"MOE14","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,232631,"20180301SPN_02","Tree fell into HV conductor during windy conditions.",null,null,"330kV AC"]
[17,102,"2018-02-28T18:30:00",43159.770833333336,-38.040853992580701,147.10134397371201,"288 HAGANS ROAD, AIRLY VIC 3851",2503668,"SLE32","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"VERY HIGH",1,{"$f":"IF(OR(P139=\"\",R139=\"\"),\"\",IF(AND(O139=\"within electric line construction area\",Q139=\"No forecast\"),1,P139*R139))","v":0.2},232630,"20180328SPN_01","Burnt EDO fuse tube.",null,null,"500kV AC"]
[{"$f":"COUNTA(C140:O140,Q140,T140:V140)","v":17},103,"2018-02-28T19:51:00",43159.82708333333,-38.075928020740797,146.89176102325501,"604 NAMBROK HALL ROAD, NAMBROK VIC 3847",2509549,"MFA22","22kV AC","RURAL LONG"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",{"$f":"IF(O140=\"\",\"\",IF(O140=\"LBRA only\",0.2,IF(O140=\"HBRA only\",1,IF(O140=\"within electric line construction area\",19.8,IF(O140=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"VERY HIGH",{"$f":"IF(Q140=\"\",\"\",IF(Q140=\"No forecast\",0.1,IF(Q140=\"Low-moderate\",0.2,IF(Q140=\"High\",0.5,IF(Q140=\"Very high\",1,IF(Q140=\"Severe\",2,IF(Q140=\"Extreme\",3.5,5)))))))","v":1},0.2,232632,"20180301SPN_03","In windy conditions a HV conductor was brought down by a fallen tree.",null,null,"Extra low voltage DC (<120V ripple free)"]
[17,104,"2018-03-02T02:57:00",43161.122916666667,-38.251583992204694,145.657987021682,"1060 WESTERNPORT ROAD, LANG LANG EAST VIC 3984",519170,"LLG11","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,232664,"20180412SPN_01","Candled EDO fuse tube.",null,null,"Low voltage DC (<1.5kV)"]
[17,105,"2018-03-02T17:13:00",43161.717361111114,-37.970650987339305,145.38719099124901,"Duffys Road, Narre Warren East VIC 3804",523041,"BGE12","Low voltage AC (<1kV)","RURAL SHORT"," - switch (disconnector/isolator)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,232690,"20180411SPN_01","Poor LV (high impedance) connection at LV fuse isolator.",null,null,"600V DC"]
[17,106,"2018-03-02T20:03:00",43161.835416666669,-38.1582660038246,146.23574500070401,"L1 WALSHES ROAD, WESTBURY VIC 3825",2201653,"MOE22","22kV AC","RURAL LONG"," - crossarm (steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,232689,"20180308SPN_03","Appears a bird caused a flashover between a HV conductor to a LA and a steel crossarm/concrete pole causing the bird to catch fire and resulting in a ground fire.",null,null,"1500V DC"]
[17,107,"2018-03-07T10:38:00",43166.443055555559,-36.316633009101899,146.36797202675803,"25 MORRISON ROAD, BOWSER VIC 3678",5103947,"WN3","22kV AC","RURAL LONG"," - pole (concrete)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,232756,"20180308SPN_05","A magpie nest in a ACR pole resulted in flashover.",null,null,"Earthing cable"]
[17,108,"2018-03-07T20:15:00",43166.84375,-37.063260003696399,146.084376004002,"7 GRIFFIN AVENUE, MANSFIELD VIC 3722",3917722,"MSD4","22kV AC","RURAL LONG"," - fuse (EDO fuse)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,232770,"20180313SPN_02","A magpie has caused a flashover between EDO fuses at pole substation."]
[17,109,"2018-03-09T22:45:00",43168.947916666664,-36.30035899484389,147.23099600725803,"1077 OMEO HIGHWAY, TALLANGATTA SOUTH VIC 3701",5211317,"WOTS24","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,232791,"20180416SPN_03","Arcing and burnt EDO fuse tube."]
[17,110,"2018-03-10T09:34:00",43169.398611111108,-38.506896978512799,146.117559975137,"1315 MEENIYAN-MIRBOO NORTH ROAD, DUMBALK VIC 3956",2002195,"LGA13","Low voltage AC (<1kV)","RURAL LONG"," - overhead conductor (insulated)","single phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,232793,"20180313SPN_03","Damaged LV transformer leads cable.",null,null,"single wire earth return (SWER)"]
[17,111,"2018-03-15T01:34:00",43174.06527777778,-36.240806020163099,147.09581398389798,"1522 MURRAY VALLEY HIGHWAY, HUON VIC 3695",5214098,"WOTS13","22kV AC","RURAL LONG"," - transformer (pole mounted)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,232843,"20180315SPN_01","A bat was between EDO fuse unit and earth system on a substation pole.",null,null,"single phase"]
[17,112,"2018-03-16T11:03:00",43175.460416666669,-37.953543980314599,145.50428399472,"1 LISHEEN ROAD, COCKATOO VIC 3781",408391,"OFR23","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","HBRA only",1,"HIGH",0.5,0.5,232869,"20180416SPN_04","Candled BA fuse tube.",null,null,"two phase"]
[17,113,"2018-03-17T13:40:00",43176.569444444445,-38.461773999856,145.64385400119801,"1415 LOCH-WONTHAGGI ROAD, GLEN ALVIE VIC 3979",2008155,"LGA23","22kV AC","RURAL LONG"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","HBRA only",1,"SEVERE",2,2,232874,"20180417SPN_01","Faulty substation transformer resulted in EDO fuse operation with one EDO fuse hung-up and candled.",null,null,"three phase"]
[17,114,"2018-03-17T16:00:00",43176.666666666664,-38.624925991217893,146.63514299392799,"FEN FARM, 7890 SOUTH GIPPSLAND HIGHWAY, ALBERTON VIC 3971",2608311,"FTR23","12.7kV AC (SWER)","RURAL LONG"," - overhead conductor (bare; aluminium core steel reinforced)","single wire earth return (SWER)","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"VERY HIGH",1,1,232875,"20180319SPN_02","Bird caused a flashover at pole, fell to ground and started a small grass fire."]
[17,115,"2018-03-17T18:39:00",43176.777083333334,-37.7490020037554,145.70066102874702,"15 VIEW STREET, HEALESVILLE VIC 3777",1403721,"WYK24","Low voltage AC (<1kV)","RURAL SHORT"," - connector / termination","three phase","Otherwise started by a distribution system","within electric line construction area",19.8,"SEVERE",2,39.6,232876,"20180319SPN_01","Burnt off LV bushing on transformer - faulty connection."]
[17,116,"2018-03-18T10:30:00",43177.4375,-37.839124612663497,146.69311145797101,"LICOLA ROAD, GLENMAGGIE VIC 3858",2510936,"MFA22","22kV AC","RURAL LONG"," - pole (wood)","single phase","Otherwise started by a distribution system","HBRA only",1,"VERY HIGH",1,1,232878,"20180319SPN_03","Lightning strike on HV wood pole.",null,null,"Negligible: no ground fire"]
[17,117,"2018-03-18T11:01:00",43177.459027777775,-37.379415186940498,145.436235605929,"437 LARRITTS LANE, GLENBURN VIC 3717",1401222,"KLK1","12.7kV AC (SWER)","RURAL SHORT"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within electric line construction area",19.8,"VERY HIGH",1,19.8,232883,"20180319SPN_06","Tree branch fell into overhead SWER line.",null,null,"Localised: less than 10 sq.m"]
[17,118,"2018-03-18T11:59:00",43177.499305555553,-38.0721500084206,145.47589597668102,"1 MAIN STREET, PAKENHAM VIC 3810",500606,"PHM32","Low voltage AC (<1kV)","URBAN"," - crossarm (wood)","three phase","Otherwise started by a distribution system","LBRA only",0.2,"SEVERE",2,0.4,232880,"20180417SPN_02","Burnt LV cross arm due to voltage / current tracking from polluted LV insulator",null,null,"Small: 10 - 1000 aq.m"]
[17,119,"2018-03-18T12:47:00",43177.532638888886,-36.281009768673194,145.81895536845701,"ALMARU, 2365 BENALLA-TOCUMWAL ROAD, YUNDOOL VIC 3727",3911226,"BN2","22kV AC","RURAL LONG"," - overhead conductor (bare; copper)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,232877,"20180319SPN_05","During gusty wind conditions a large tree limb fell into overhead HV conductors.",null,null,"Medium: 1000 sq.m - 10 ha"]
[17,120,"2018-03-18T17:40:00",43177.736111111109,-38.219574990992704,145.977882986553,"906 BONA VISTA ROAD, GAINSBOROUGH VIC 3822",2705515,"WGL23","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"VERY HIGH",1,1,232881,"20180319SPN_04","Tree into overhead HV line.",null,null,"Large: more than 10 ha"]
[17,121,"2018-03-19T12:11:00",43178.507638888892,-38.60905084833189,146.485709824472,"327 Hedley Range Rd BINGINWARRA VIC 3966",2611459,"FTR12","12.7kV AC (SWER)","RURAL LONG"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"HIGH",0.5,0.5,232913,"20180320SPN_01","Tree fell into SWER conductor."]
[17,122,"2018-03-19T12:21:00",43178.51458333333,-38.209930358736301,146.32509545573501,"Hernes Oak Vic 3825",7700545,"MWTS-YPS1","66kV AC","UNCLASSIFIED"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,232898,"20180319SPN_08","HV conductor on ground."]
[17,123,"2018-03-21T12:42:00",43180.529166666667,-38.192756016594394,145.34579901055199,"2470 SOUTH GIPPSLAND HIGHWAY, DEVON MEADOWS VIC 3977",517096,"CRE33","22kV AC","RURAL SHORT"," - overhead conductor (bare; steel)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"VERY HIGH",1,1,232936,"20180326SPN_01","A large tree branch fell into overhead HV conductor.",null,null,"Started in or originated from a distribution system"]
[17,124,"2018-03-21T15:57:00",43180.664583333331,-38.518526974830699,145.72176002373399,"105 KORUMBURRA-INVERLOCH ROAD, KONGWAK VIC 3951",2804133,"WGI22","22kV AC","RURAL LONG"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,232941,"20180322SPN_02","Tree fell into overhead HV conductors.",null,null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system"]
[17,125,"2018-03-21T17:27:00",43180.727083333331,-38.592086018828297,145.79757199798701,"6870 BASS HIGHWAY, POUND CREEK VIC 3996",5725063,"LGA23","22kV AC","RURAL LONG"," - dropper / bridge","three phase","Otherwise started by a distribution system","HBRA only",1,"VERY HIGH",1,1,232938,"20180326SPN_02","Flexible HV T-off dropper at 5725063 was blowing in strong wind and contacting base of insulator on steel x-arm & concrete pole causing arcing and burnt spiral dampers on conductors.",null,null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system"]
[17,126,"2018-03-21T17:36:00",43180.73333333333,-38.379944013376594,146.531905999939,"2225 TRARALGON CREEK ROAD, KOORNALLA VIC 3844",2605374,"TGN23","22kV AC","RURAL SHORT"," - overhead conductor (bare; all aluminium conductor)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"HIGH",0.5,0.5,232942,"20180322SPN_03","During extreme winds a large tree fell into the single phase overhead HV conductors.",null,null,"Started by lightning striking a distribution system or a part of a distribution system "]
[17,127,"2018-03-21T20:09:00",43180.839583333334,-37.900105037185597,145.31415901868999,"28 ALBERT STREET, UPPER FERNTREE GULLY VIC 3156",1032892,"FGY33","Low voltage AC (<1kV)","URBAN"," - overhead service conductor (other)","single phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"VERY HIGH",1,4.5999999999999996,232937,"20180322SPN_01","Service cable damaged by cockatoos chewing insulation causing a short circuit.",null,null,"Started by any other thing forming part of or coming into contact with a distribution system"]
[17,128,"2018-03-22T12:26:00",43181.518055555556,-38.020553000494502,146.962375011668,"696 RIVERSDALE ROAD, RIVERSLEA VIC 3860",2511542,"MFA34","Low voltage AC (<1kV)","RURAL SHORT"," - overhead conductor (bare; all aluminium conductor)","two phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"HIGH",0.5,0.1,232960,"20180322SPN_04","Tractor contacted overhead LV line / pole stay.",null,null,"Otherwise started by a distribution system"]
[17,129,"2018-03-24T11:00:00",43183.458333333336,-38.414182960491992,147.10919869290302,"295 COSTELLOS ROAD, GIFFARD VIC 3851",2504316,"SLE31","12.7kV AC (SWER)","RURAL LONG"," - fuse (boric acid)","single wire earth return (SWER)","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,232998,"20180507SPN_04","Burnt Boric Acid HV fuse tube."]
[17,130,"2018-03-24T18:00:00",43183.75,-37.915358016341102,145.299505997127,"351 LYSTERFIELD ROAD, LYSTERFIELD VIC 3156",1302523,"FGY21","Low voltage AC (<1kV)","URBAN"," - overhead conductor (insulated)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,233000,"20180326SPN_04","A 4 core LV service mains to a FOLCB on pole for a customer's UG service was worn through and faulted phase to phase."]
[17,131,"2018-03-24T19:08:00",43183.797222222223,-36.487138999167001,146.143137007116,"677 Glenrowan Rd, Wangaratta South VIC 3678",3909511,"WN6","66kV AC","UNCLASSIFIED"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,233001,"20180507SPN_03","Lightning strike to pole.",null,null,1]
[17,132,"2018-03-27T12:00:00",43186.5,-37.746719995043399,147.67733902863799,"80 WATERHOLES ROAD, GRANITE ROCK VIC 3875",1600885,"BDL8","22kV AC","RURAL LONG"," - fuse (boric acid)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,233044,"20180508SPN_02","Burnt Boric Acid fuse tube.",null,null,2]
[17,133,"2018-03-28T08:44:00",43187.363888888889,-38.251583992204694,145.657987021682,"1060 WESTERNPORT ROAD, LANG LANG EAST VIC 3984",519170,"LLG11","22kV AC","RURAL SHORT"," - fuse (EDO fuse)","single phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,233053,"20180508SPN_03","Burnt EDO fuse tube.",null,null,3]
[17,134,"2018-04-04T20:13:00",43194.842361111114,-37.926600982899807,145.50855901564699,"32 MOUNTAIN ROAD, COCKATOO VIC 3781",420555,"BGE22","Low voltage AC (<1kV)","RURAL SHORT"," - connection box","two phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,{"$f":"IF(OR(P171=\"\",R171=\"\"),\"\",IF(AND(O171=\"within electric line construction area\",Q171=\"No forecast\"),1,P171*R171))","v":0.91999999999999993},233125,"20180515SPN_02","Pole FMB burnt out. Fire on pole.",null,null,4]
[17,135,"2018-04-05T09:55:00",43195.413194444445,-36.8234590106523,145.111050010447,"MULLERS ROAD, TABILK VIC 3607",4705544,"SMR8","22kV AC","RURAL LONG"," - fuse (EDO fuse)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,233134,"20180510SPN_01","EDO fuse candling",null,null,5]
[17,136,"2018-04-06T06:33:00",43196.272916666669,-37.689408008992302,145.42003100196601,"717 MAROONDAH HIGHWAY, COLDSTREAM VIC 3770",1409569,"LDL23","Low voltage AC (<1kV)","RURAL LONG"," - connection box","two phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,233147,"20180406SPN_02","LV fuse box.",null,null,6]
[17,137,"2018-04-09T00:27:00",43199.018750000003,-37.737207737470293,145.12772169875001,"38 ROSEHILL ROAD, LOWER PLENTY VIC 3093",905963,"ELM34","Low voltage AC (<1kV)","RURAL SHORT"," - lamps (major road)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,233155,"20180529SPN_01","Street light head caught fire. Exact cause uncertain but it is common for such older street lights to fail due to either faulty ignitors with repetitive striking or failed plastic clad capacitors.",null,null,7]
[17,138,"2018-04-14T17:00:00",43204.708333333336,-37.754146052336793,148.324164220564,"MEKKENVILLE, 4301 PRINCES HIGHWAY, WAYGARA VIC 3888",1905903,"NLA34","22kV AC","RURAL SHORT"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"VERY HIGH",1,1,233218,"20180416SPN_01","Tree branch into conductors.",null,null,8]
[17,139,"2018-04-17T12:56:00",43207.538888888892,-37.649179997843696,145.02526499458901,"763 HIGH STREET, EPPING VIC 3076",915175,"EPG32","Low voltage AC (<1kV)","RURAL SHORT"," - connection box","three phase","Otherwise started by a distribution system","LBRA only",0.2,"LOW-MODERATE",0.2,4.0000000000000008E-2,233230,"20180517SPN_01","Burnt out LV Fuse Switch Disconnector on the load side.",null,null,9]
[17,140,"2018-04-20T13:08:00",43210.547222222223,-38.065236014820897,146.62376502644202,"1 SEMMENS STREET, TOONGABBIE VIC 3856",2602911,"TGN31","Low voltage AC (<1kV)","RURAL LONG"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"LOW-MODERATE",0.2,0.2,233305,"20180420SPN_01","Contact with overhead LVconductor by an excavator.",null,null,10]
[17,141,"2018-04-24T11:03:00",43214.460416666669,-37.891668020260092,147.67619101105402,"4 FORGE CREEK ROAD, EAGLE POINT VIC 3878",1610710,"BDL42","22kV AC","RURAL SHORT"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"HIGH",0.5,2.2999999999999998,233328,"20180426SPN_01","It appears a magpie shorted out on a BA fuse unit and earth.",null,null,{"$f":"Y177+1","v":11}]
[17,142,"2018-04-27T17:48:00",43217.741666666669,-37.671739951071494,145.50711421917401,"20 ARGOON ROAD, HEALESVILLE VIC 3777",1402987,"LDL23","22kV AC","RURAL LONG"," - overhead conductor (bare; all aluminium conductor)","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,233378,"20180430SPN_01","The incident is currently under investigation.",null,null,{"$f":"Y178+1","v":12}]
[17,143,"2018-04-30T10:00:00",43220.416666666664,-36.325429990531504,146.296937993569,"68 WALDARA DRIVE, WALDARA VIC 3678",5106454,"WN2","Low voltage AC (<1kV)","RURAL LONG"," - connection box","three phase","Otherwise started by a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"LOW-MODERATE",0.2,0.91999999999999993,233388,"20180528SPN_03","Melted and burnt out three phase LV connection box.",null,null,13]
[17,144,"2018-05-01T11:12:00",43221.466666666667,-37.324891024200397,147.777484986183,"5870 GREAT ALPINE ROAD, ENSAY VIC 3895",1602484,"BDL8","Low voltage AC (<1kV)","RURAL LONG"," - overhead service conductor (residential)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","within electric line construction area",19.8,"NO FORECAST",0.1,1,233408,"20180502SPN_01","A truck contacted a POEL.",null,null,14]
[17,145,"2018-05-01T14:19:00",43221.59652777778,-37.868070005682,148.02095999528902,"36 OCEAN VIEW PARADE, LAKES ENTRANCE VIC 3909",5622581,"BDL41","22kV AC","RURAL LONG"," - dropper / bridge","three phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,233413,"20180502SPN_02","HV dropper lead termination burnt off transformer bushing.",null,null,15]
[17,146,"2018-05-10T10:04:00",43230.419444444444,-38.028222013397503,145.80190599863201,"100 ALCORN ROAD, LABERTOUCHE VIC 3816",2716712,"WGL21","22kV AC","RURAL LONG"," - fuse (boric acid)","three phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,233507,"20180605SPN_02","Candled Boric Acid fuse tube.",null,null,16]
[17,147,"2018-05-14T07:45:00",43234.322916666664,-38.502003018768292,145.95551197829801,"50 CARMODYS ROAD, LEONGATHA SOUTH VIC 3953",2001147,"LGA14","22kV AC","RURAL LONG"," - overhead conductor (bare; steel)","single phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,233540,"20180515SPN_05","Corroded steel conductor broke at existing sleeve on conductor which fell to ground & burnt small area of grass on nature strip",null,null,17]
[17,148,"2018-05-19T23:47:00",43239.990972222222,-37.872882453273299,145.40642716140903,"538 MONBULK ROAD, MONBULK VIC 3793",1321115,"LDL13","Low voltage AC (<1kV)","RURAL SHORT"," - lamps (major road)","single phase","Otherwise started by a distribution system","within electric line construction area",19.8,"NO FORECAST",0.1,1,233644,"20180628SPN_01","Failed light identified as an older style unit where the igniter/starter has failed resulting in fire.",null,null,18]
[17,149,"2018-06-04T05:19:00",43255.22152777778,-37.689750991842097,145.00524002923999,"13 CHAFFEY STREET, THOMASTOWN VIC 3074",907501,"TT7","22kV AC","URBAN"," - fuse (powder filled)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,233830,"20180626SPN_03","Bird made contact with Overhead 22kV resulting in fuse operation",null,null,19]
[17,150,"2018-06-19T18:58:00",43270.790277777778,-38.2239870075148,145.31345298760201,"23 KALLARA ROAD, WARNEET VIC 3980",517474,"CRE33","Low voltage AC (<1kV)","RURAL SHORT"," - connection box","three phase","Otherwise started by a distribution system","HBRA only",1,"NO FORECAST",0.1,0.1,234031,"20180620SPN_01","Krone box failure resulting from overload",null,null,20]
[17,151,"2018-06-26T13:00:00",43277.541666666664,-37.757380997276201,145.35218400226901,"250 MAIN STREET, LILYDALE VIC 3140",1006146,"LDL12","Low voltage AC (<1kV)","URBAN"," - overhead conductor (ABC)","single phase","Otherwise started by a distribution system","LBRA only",0.2,"NO FORECAST",0.1,2.0000000000000004E-2,234128,"20180628SPN_02","Fault crew attended to find faulty/failed IPC connection on LV ABC mains"]

{"sheet":"3. Systems and Audit","index":4,"n_rows":29,"n_cols":5,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,1,29,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4],[19,4,21,4]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"AusNet Services"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2017/18"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"AusNet Services must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","Poweron (OMS)","Yes","ISO 9001\nISO55000\nElectricity Safey (Bushfire Mitigation) Regulations\nElectricity Safety (Management) Regulations"]
[null,"System 2","IMS","Yes"]
[null,"System 3 ","Smallworld GIS (SDME) /SAP","Yes"]
[null,"System 4","EM-COP","Unknown","https://scc.em.vic.gov.au/cgi-bin/scc/fdrhistory/home"]
[null,"System 5"]
[null,"System 6"]
[null,"System 7"]
[null,"System 8"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]