## Inclusions and Exclusions
Sydney Forecast Inclusions and Exclusions
Date Printed |  | 08JUL14:11:21:24
| Description | Value
Season |  | Winter | Winter
Either Summer or Winter
Year |  | 2014 | 2014
Year that the forecast starts
POE |  | 50% | 0.5
10%, 50%, 90%
Spots and Transfers |  | Y | Y
Are Spots and Transfers Included?
BBDM Spots |  | Y | Y
Is BBDM included?
Spots Coefficient |  | 55% | 0.55
Scaling factor applied to spot loads in the future
Aligned ROGs |  | Capped | Capped
Have ROGs been aligned to econometric forecast?
Committed Projects |  | Y | Y
Are Committed Projects Included?
Major Customers Scaling Factor |  | 100% | 1
Scaling factor applied to major customer connections in the future
Future Transfers |  | Y | Y
Are future transfers included?
Future Spots |  | 4 | 4
Future spots are cleared from the following forecast year

## Castle Cove 132_11kV
| Castle Cove 132_11kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 3796 | 3807 | 3492 | 3484 | 3359 | 3100 | 2861 |  | 2686.632 | 2770.973 | 2705.46 | 2674.675 | 2671.158 | 2667.126 | 2692.085 | 2729.882 | 2763.585 | 2798.609 | 2824.991 | 2863.476 | 2901.724 | 2948.636 | 3000.233 | 3050.572 | 3098.86 | 3148.242 | 3198.732 | 3250.347 | 3303.103 | 3357.016 | 3412.103 | 3468.381 | 3525.866 |  |  | Total | 0 | 0 | 0 | 0 | -97 | -142 | 17.2 | 114.9418 | 175.0277 | -5.616 | -1.484 | -3.5854 | -4.1109 | 25.4427 | 38.5137 | 34.3246 | 35.6533 | 26.8459 | 39.1456 | 38.8864 | 47.6726 | 52.4057 | 51.1003 | 48.995 | 50.0812 | 51.183 | 52.3006 | 53.4341 | 54.5838 | 55.7499 | 56.9326 | 58.1322
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 5052 |  | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052 | 5052
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 8000 |  | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 |  |  | Castle Cove 132_11kV Tx1 | 159 | 44 | 0 | 13 | 23 | 38 | 0 | -3.7608 | 91.3054 | -1.3152 | -0.34754 | -0.83968 | -0.96276 | 5.9586 | 9.0198 | 8.0387 | 8.3499 | 6.2872 | 9.1678 | 9.1071 | 11.1648 | 12.2733 | 11.9676 | 11.4745 | 11.7289 | 11.9869 | 12.2487 | 12.5141 | 12.7834 | 13.0565 | 13.3335 | 13.6144
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Castle Cove 132_11kV Tx2 | 608 | 0 | 0 | 223 | 0 | -153 | -8 | -26.9841 | -1.7422 | -1.3933 | -0.36818 | -0.88954 | -1.0199 | 6.3124 | 9.5554 | 8.5161 | 8.8457 | 6.6606 | 9.7122 | 9.6479 | 11.8277 | 13.002 | 12.6782 | 12.1558 | 12.4253 | 12.6987 | 12.976 | 13.2572 | 13.5424 | 13.8318 | 14.1252 | 14.4228
| Transformer Loads | [35 empty] | Castle Cove 132_11kV Tx3 | -1020 | 0 | 0 | 0 | -97 | 59 | 0 | -3.7303 | -1.6313 | -1.3046 | -0.34473 | -0.83288 | -0.95497 | 5.9104 | 8.9468 | 7.9736 | 8.2823 | 6.2363 | 9.0936 | 9.0334 | 11.0744 | 12.1739 | 11.8707 | 11.3816 | 11.6339 | 11.8899 | 12.1495 | 12.4128 | 12.6799 | 12.9508 | 13.2255 | 13.5042
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | Castle Cove 132_11kV Tx4 | 253 | -44 | 0 | -236 | -23 | -86 | 25.2 | 149.417 | 87.0959 | -1.6028 | -0.42353 | -1.0233 | -1.1732 | 7.2613 | 10.9918 | 9.7962 | 10.1754 | 7.6618 | 11.1721 | 11.0981 | 13.6057 | 14.9565 | 14.5839 | 13.9831 | 14.2931 | 14.6075 | 14.9265 | 15.25 | 15.5781 | 15.9109 | 16.2485 | 16.5908
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Castle Cove 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6090. Load Balance of Transformer Groups at Castle Cove Zone Substation. | Castle Cove 132_11kV Tx1 | Castle Cove 132_11kV Tx2 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6090. Load Balance of Transformer Groups at Castle Cove Zone Substation. | Castle Cove 132_11kV Tx3 | Castle Cove 132_11kV Tx1 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6090. Load Balance of Transformer Groups at Castle Cove Zone Substation. | Castle Cove 132_11kV Tx3 | Castle Cove 132_11kV Tx2 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6090. Load Balance of Transformer Groups at Castle Cove Zone Substation. | Castle Cove 132_11kV Tx3 | Castle Cove 132_11kV Tx4 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6149. Remedial relief of Panel 11, 16, 17, 34 & 40 Feeders Castle Cove. | Castle Cove 132_11kV Tx1 | Castle Cove 132_11kV Tx4 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6149. Remedial relief of Panel 11, 16, 17, 34 & 40 Feeders Castle Cove. | Castle Cove 132_11kV Tx3 | Castle Cove 132_11kV Tx1 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6149. Remedial relief of Panel 11, 16, 17, 34 & 40 Feeders Castle Cove. | Castle Cove 132_11kV Tx4 | Castle Cove 132_11kV Tx1 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6393. Castle Cove Zone Development - 2008 (Chatswood Business District) | Castle Cove 132_11kV Tx1 | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6393. Castle Cove Zone Development - 2008 (Chatswood Business District) | Castle Cove 132_11kV Tx2 | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6393. Castle Cove Zone Development - 2008 (Chatswood Business District) | Castle Cove 132_11kV Tx4 | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6401. Chatswood Chase Redevelopment (LLC) | Castle Cove 132_11kV Tx4 | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6464. Relieve Remedial Castle Cove Panel 12,24 and 30 Feeders Amend A has been replaced to improve network pick ups for PA 24 and associated panels for futre DNP (DNP 6473). Amend B was issued due to an open point change DNP6885 | Castle Cove 132_11kV Tx1 | Lindfield 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6464. Relieve Remedial Castle Cove Panel 12,24 and 30 Feeders Amend A has been replaced to improve network pick ups for PA 24 and associated panels for futre DNP (DNP 6473). Amend B was issued due to an open point change DNP6885 | Castle Cove 132_11kV Tx2 | Lindfield 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6464. Relieve Remedial Castle Cove Panel 12,24 and 30 Feeders Amend A has been replaced to improve network pick ups for PA 24 and associated panels for futre DNP (DNP 6473). Amend B was issued due to an open point change DNP6885 | Castle Cove 132_11kV Tx4 | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6464. Relieve Remedial Castle Cove Panel 12,24 and 30 Feeders Amend A has been replaced to improve network pick ups for PA 24 and associated panels for futre DNP (DNP 6473). Amend B was issued due to an open point change DNP6885 | Castle Cove 132_11kV Tx4 | Castle Cove 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6473. Castle Cove Zone Development - 2009 (Pa 15, 43 & 44 Feeders) | Castle Cove 132_11kV Tx3 | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2006127. Establish customer substation S.35214 Chatswood Station (3x1500kVA), Victoria Ave, Chatswood. Additional load to be added to S.6667 in 2010. |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2007651. Load increases on S.234 Victoria Chatswood Chase, S.5884 Mills Myer and S.5885 Archer David Jones. Load increases are 62A , 27 A and 23 A respectively for a total of 112 A increase |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010022. Establishment of S.47700 Fullers Pacific, Fullers Rd, Chatswood (dealership on Pacific Hwy) | Castle Cove 132_11kV Tx2 | Lindfield 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010793. Establishment of S.49416 Help Cambridge, 7 Railway Street, Chatswood |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 25.2 | 0 | 55.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2011427. C/S SELF ASSESSED DNP - Uprate Existing S.554 Glencroft AV & Loop in HV, Glencroft Road, Roseville | Castle Cove 132_11kV Tx2 | Lindfield 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2011444. Increase load at existing S.7166 Smith Gibbes, 26 Smith St, Chatswood | Castle Cove 132_11kV Tx2 | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011721. Establishment of S.61404 Fleet Thomas No 2, between S.4391 Fleet Thomas and S.6947 Thomas Telecom, 73 Albert Ave, Chatswood |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 15.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012280. Establishment of 3 x Kiosks S.64164 Fleet Albert No 2, S.64163 Fleet Albert No 1 and S.64165 Fleet Thomas No.3, 79-85 Albert Ave, Chatswood |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2014137. Establish S.64881 VICTORIA WESTFIELD, Victoria Avenue, Chatswood |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Econometric |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0275 | 9.2657 | 13.9184 | 14.1465 | 14.3873 | 13.9782 | 14.2019 | 14.4289 | 14.6592 | 14.8927 | 15.1296 | 15.37 | 15.6137 | 15.861 | 16.1118 | 16.3662 | 16.6242 | 16.886 | 17.1514 | 17.4207 | 17.6938 | 17.9708 | 18.2517
[35 empty] | Econometric |  | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.326 | 9.8159 | 14.7449 | 14.9865 | 15.2416 | 14.8082 | 15.0452 | 15.2857 | 15.5296 | 15.777 | 16.028 | 16.2826 | 16.5409 | 16.8028 | 17.0685 | 17.338 | 17.6114 | 17.8886 | 18.1699 | 18.4551 | 18.7444 | 19.0379 | 19.3355
[35 empty] | Econometric |  | Castle Cove 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9868 | 9.1907 | 13.8057 | 14.0319 | 14.2708 | 13.865 | 14.087 | 14.3121 | 14.5405 | 14.7721 | 15.0071 | 15.2455 | 15.4873 | 15.7326 | 15.9813 | 16.2337 | 16.4896 | 16.7492 | 17.0126 | 17.2796 | 17.5505 | 17.8253 | 18.1039
[35 empty] | Econometric |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1266 | 11.2914 | 16.9613 | 17.2392 | 17.5327 | 17.0342 | 17.3068 | 17.5834 | 17.864 | 18.1486 | 18.4373 | 18.7302 | 19.0273 | 19.3286 | 19.6342 | 19.9442 | 20.2587 | 20.5776 | 20.9011 | 21.2293 | 21.5621 | 21.8996 | 22.242
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Energy Efficiency |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7608 | -1.6446 | -6.3427 | -9.6132 | -14.7581 | -15.1092 | -8.4287 | -4.9584 | -6.1632 | -6.079 | -8.3719 | -5.7249 | -6.0225 | -4.2052 | -3.3405 | -3.8934 | -4.6373 | -4.6373 | -4.6373 | -4.6373 | -4.6373 | -4.6373 | -4.6373 | -4.6373 | -4.6373
[10 empty] | ROG Justification | [24 empty] | Energy Efficiency |  | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9841 | -1.7422 | -6.7194 | -10.1841 | -15.6344 | -16.0064 | -8.9292 | -5.2528 | -6.5292 | -6.44 | -8.8691 | -6.0649 | -6.3802 | -4.4549 | -3.5388 | -4.1246 | -4.9127 | -4.9127 | -4.9127 | -4.9127 | -4.9127 | -4.9127 | -4.9127 | -4.9127 | -4.9127
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0.43% |  | 7 year ROG ok | [24 empty] | Energy Efficiency |  | Castle Cove 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7303 | -1.6313 | -6.2914 | -9.5354 | -14.6386 | -14.9869 | -8.3605 | -4.9182 | -6.1133 | -6.0298 | -8.3041 | -5.6786 | -5.9738 | -4.1711 | -3.3134 | -3.8619 | -4.5998 | -4.5998 | -4.5998 | -4.5998 | -4.5998 | -4.5998 | -4.5998 | -4.5998 | -4.5998 | 7 year ROG ok
[35 empty] | Energy Efficiency |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.583 | -2.0041 | -7.7294 | -11.7149 | -17.9845 | -18.4124 | -10.2714 | -6.0424 | -7.5106 | -7.408 | -10.2022 | -6.9766 | -7.3392 | -5.1245 | -4.0708 | -4.7446 | -5.6511 | -5.6511 | -5.6511 | -5.6511 | -5.6511 | -5.6511 | -5.6511 | -5.6511 | -5.6511
[35 empty] | Solar PV |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Solar PV |  | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.97021 | 0.94131 | 0.92261 | 0.91345 | 0.91345 | 0.91345 | 0.91345 | 0.91345 | 0.91345 | 0.91345 | -2.979% | -2.979% | -1.986% | -0.993% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Solar PV |  | Castle Cove 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Castle Cove 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 2861 | 2964 | 2686.632 | 2770.973 | 2705.46 | 2674.675 | 2671.158 | 2667.126 | 2692.085 | 2729.882 | 2763.585 | 2798.609 | 2824.991 | 2863.476 | 2901.724 | 2948.636 | 3000.233 | 3050.572 | 3098.86 | 3148.242 | 3198.732 | 3250.347 | 3303.103 | 3357.016 | 3412.103 | 3468.381 | 3525.866
|  |  |  | Apparent Power |  |  | MVA | 54.5094 |  | 51.1872 | 52.7941 | 51.5459 | 50.9594 | 50.8924 | 50.8156 | 51.2911 | 52.0112 | 52.6534 | 53.3207 | 53.8233 | 54.5566 | 55.2853 | 56.1791 | 57.1621 | 58.1212 | 59.0412 | 59.9821 | 60.944 | 61.9274 | 62.9326 | 63.9597 | 65.0093 | 66.0815 | 67.1768
|  |  |  | Real Power |  |  | MW | 45.0339 | 46.6552 | 47.0742 | 48.4267 | 47.3763 | 46.8824 | 46.8259 | 46.7612 | 47.1617 | 47.7679 | 48.3082 | 48.8695 | 49.292 | 49.9082 | 50.5203 | 51.2707 | 52.0956 | 52.8999 | 53.6711 | 54.4594 | 55.2651 | 56.0883 | 56.9294 | 57.7886 | 58.6662 | 59.5623 | 60.4773
|  |  |  | Reactive Power |  |  | MVAr | 30.7119 |  | 20.1034 | 21.0257 | 20.3094 | 19.9726 | 19.9341 | 19.8899 | 20.1631 | 20.5765 | 20.945 | 21.3277 | 21.6159 | 22.0361 | 22.4535 | 22.9653 | 23.5278 | 24.0764 | 24.6023 | 25.1399 | 25.6894 | 26.2508 | 26.8244 | 27.4103 | 28.0088 | 28.6199 | 29.244
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
|  |  |  | PF |  |  |  | 0.82617 |  | 0.91965 | 0.91727 | 0.91911 | 0.91999 | 0.9201 | 0.92021 | 0.91949 | 0.91841 | 0.91748 | 0.91652 | 0.91581 | 0.9148 | 0.91381 | 0.91263 | 0.91136 | 0.91017 | 0.90904 | 0.90793 | 0.90682 | 0.90571 | 0.90461 | 0.90351 | 0.90243 | 0.90134 | 0.90027
0.96565 | Diversity Factor: 0.97 | Uncompensated |  | Reactive Power |  |  | MVAr | 30.7119 | 31.8176 | 32.1034 | 33.0257 | 32.3094 | 31.9726 | 31.9341 | 31.8899 | 32.1631 | 32.5765 | 32.945 | 33.3277 | 33.6159 | 34.0361 | 34.4535 | 34.9653 | 35.5278 | 36.0764 | 36.6023 | 37.1399 | 37.6894 | 38.2508 | 38.8244 | 39.4103 | 40.0088 | 40.6199 | 41.244
|  |  |  | PF |  |  |  | 0.82617 |  | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617 | 0.82617
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Chatswood 33_11kV
| Chatswood 33_11kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 2679 | 2580 | 2295 | 2340 | 2226 | 2202 | 2317 |  | 2263.446 | 2269.185 | 2305.211 | 2293.489 | 2304.983 | 2310.637 | 2336.045 | 2366.873 | 2395.466 | 2425.366 | 2451.317 | 2484.837 | 2518.578 | 2557.171 | 2598.659 | 2639.673 | 2680.027 | 2721.305 | 2763.521 | 2806.689 | 2850.824 | 2895.938 | 2942.046 | 2989.163 | 3037.303 |  |  | Total | 87.3 | 0 | 0 | 0 | 0 | 91 | 0 | 42.837 | 67.5954 | 77.3678 | 9.2772 | 11.4936 | 5.6539 | 25.4086 | 30.8278 | 28.5928 | 29.9004 | 25.9506 | 33.52 | 33.7408 | 38.5936 | 41.4878 | 41.0141 | 40.3533 | 41.2781 | 42.2163 | 43.1683 | 44.1341 | 45.1141 | 46.1083 | 47.117 | 48.1403
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 3701 |  | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701 | 3701
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 6410 |  | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 |  |  | Chatswood 33_11kV Tx1 | 0 | -593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Chatswood 33_11kV Tx11 | 0 | 690 | 172 | 0 | 0 | 116 | 0 | -1.1584 | 69.4708 | 75.9322 | 4.0907 | 5.0679 | 2.493 | 11.2035 | 13.5931 | 12.6076 | 13.1841 | 11.4425 | 14.7801 | 14.8775 | 17.0172 | 18.2934 | 18.0846 | 17.7932 | 18.2009 | 18.6146 | 19.0344 | 19.4603 | 19.8924 | 20.3307 | 20.7755 | 21.2267
| Transformer Loads | [35 empty] | Chatswood 33_11kV Tx12 | 0 | 0 | -172 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | Chatswood 33_11kV Tx13 | 0 | 1643 | 0 | 0 | 0 | -25 | 0 | -6.0046 | -1.8755 | 1.4355 | 5.1866 | 6.4257 | 3.1609 | 14.2051 | 17.2348 | 15.9852 | 16.7163 | 14.5081 | 18.7398 | 18.8633 | 21.5763 | 23.1944 | 22.9296 | 22.5602 | 23.0771 | 23.6017 | 24.1339 | 24.6739 | 25.2217 | 25.7775 | 26.3415 | 26.9136
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  | Chatswood 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [35 empty] | Chatswood 33_11kV Tx3 | 87.3 | -760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [35 empty] | Chatswood 33_11kV Tx4 | -87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | Chatswood 33_11kV Tx5 | 87 | -980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.027878 | -0.030976 | -0.058854 | -0.45225 | -0.60712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Chatswood 33_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Chatswood 33_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.035347 | -0.039274 | -0.074621 | -0.57341 | -0.76978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx1 | Chatswood 33_11kV Tx11 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx1 | Chatswood 33_11kV Tx13 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx11 | Chatswood 33_11kV Tx12 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx12 | Chatswood 33_11kV Tx11 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx3 | Chatswood 33_11kV Tx11 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx3 | Chatswood 33_11kV Tx13 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx5 | Chatswood 33_11kV Tx11 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx5 | Chatswood 33_11kV Tx13 | 0 | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6143. Chatswood Westfields Pa14 Rearrangement | Chatswood 33_11kV Tx4 | Chatswood 33_11kV Tx5 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6885. Lindfield Tx1 load transfer to Chatswood PA31 | Lindfield 33_11kV Tx1 | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 7086. Re-conductor OH at PA 28 Lindfield Zone | Lindfield 33_11kV Tx4 | Chatswood 33_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2005306. Stage 2 of Channel 9 Load Increase, Est S.7712 Artarmon Edwards |  | Chatswood 33_11kV Tx3 | 87.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010502. Uprate S.2385, Greenwich Rd, Greenwich. Recover existing OH mains and supply new sub via UG cable | Chatswood 33_11kV Tx13 | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2011190. Establishment of S.49284 Archer Albert No 2, 38 Albert Ave, Chatswood |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2011533. Establishment of S.50669 Devonshire Johnson, 31-35 Devonshire Street, Chatswood |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012280. Establishment of 3 x Kiosks S.64164 Fleet Albert No 2, S.64163 Fleet Albert No 1 and S.64165 Fleet Thomas No.3, 79-85 Albert Ave, Chatswood |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012539. Establishment of S.63266 Mindarie Pinaroo, 31-39 Mindarie Street, Lane Cove | Chatswood 33_11kV Tx13 | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2014131. Establishment of 2 x Kisosk - S.64871 Centennial Mowbray No1 and S.64872 Centennial Mowbray No 2, 7-13 Centennial Avenue, Lane Cove |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Econometric |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5734 | 15.7466 | 23.4515 | 21.8812 | 22.273 | 21.3063 | 21.6638 | 22.0267 | 22.3949 | 22.7686 | 23.1477 | 23.5324 | 23.9227 | 24.3188 | 24.7206 | 25.1284 | 25.5421 | 25.9619 | 26.3877 | 26.8198 | 27.2582 | 27.703 | 28.1542
[35 empty] | Econometric |  | Chatswood 33_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Chatswood 33_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8703 | 19.9652 | 29.7344 | 27.7434 | 28.2402 | 27.0144 | 27.4678 | 27.9279 | 28.3947 | 28.8685 | 29.3492 | 29.8369 | 30.3318 | 30.834 | 31.3435 | 31.8605 | 32.3851 | 32.9173 | 33.4573 | 34.0051 | 34.5609 | 35.1249 | 35.697
| 0 | [33 empty] | Energy Efficiency |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1584 | -1.4513 | -7.4102 | -11.597 | -17.9314 | -18.781 | -11.0695 | -7.7132 | -9.0563 | -8.8426 | -10.9524 | -7.9884 | -8.2702 | -6.5151 | -5.6293 | -6.2342 | -6.9275 | -6.9275 | -6.9275 | -6.9275 | -6.9275 | -6.9275 | -6.9275 | -6.9275 | -6.9275
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Chatswood 33_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Energy Efficiency |  | Chatswood 33_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0046 | -1.8401 | -9.3955 | -14.704 | -22.7353 | -23.8127 | -14.0351 | -9.7796 | -11.4826 | -11.2116 | -13.8867 | -10.1286 | -10.4858 | -8.2606 | -7.1374 | -7.9044 | -8.7834 | -8.7834 | -8.7834 | -8.7834 | -8.7834 | -8.7834 | -8.7834 | -8.7834 | -8.7834
[35 empty] | Solar PV |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Solar PV |  | Chatswood 33_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Chatswood 33_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 2.29% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.97268 | 0.94611 | 0.92888 | 0.92042 | 0.92042 | 0.92042 | 0.92042 | 0.92042 | 0.92042 | 0.92042 | -2.732% | -2.732% | -1.821% | -0.91% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Chatswood 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 2317 | 2283 | 2263.446 | 2269.185 | 2305.211 | 2293.489 | 2304.983 | 2310.637 | 2336.045 | 2366.873 | 2395.466 | 2425.366 | 2451.317 | 2484.837 | 2518.578 | 2557.171 | 2598.659 | 2639.673 | 2680.027 | 2721.305 | 2763.521 | 2806.689 | 2850.824 | 2895.938 | 2942.046 | 2989.163 | 3037.303
|  |  |  | Apparent Power |  |  | MVA | 44.1448 |  | 43.1244 | 43.2338 | 43.9202 | 43.6968 | 43.9158 | 44.0236 | 44.5076 | 45.095 | 45.6398 | 46.2094 | 46.7039 | 47.3425 | 47.9854 | 48.7207 | 49.5111 | 50.2925 | 51.0614 | 51.8478 | 52.6521 | 53.4746 | 54.3155 | 55.175 | 56.0535 | 56.9512 | 57.8684
|  |  |  | Real Power |  |  | MW | 39.7303 | 39.1473 | 38.812 | 38.9104 | 39.5282 | 39.3272 | 39.5242 | 39.6212 | 40.0569 | 40.5855 | 41.0758 | 41.5885 | 42.0335 | 42.6083 | 43.1868 | 43.8486 | 44.56 | 45.2633 | 45.9552 | 46.663 | 47.3869 | 48.1272 | 48.8839 | 49.6575 | 50.4482 | 51.2561 | 52.0816
|  |  |  | Reactive Power |  |  | MVAr | 19.2423 |  | 18.7975 | 18.8452 | 19.1444 | 19.047 | 19.1425 | 19.1894 | 19.4004 | 19.6564 | 19.8939 | 20.1422 | 20.3577 | 20.6361 | 20.9163 | 21.2368 | 21.5814 | 21.922 | 22.2571 | 22.5999 | 22.9505 | 23.309 | 23.6756 | 24.0502 | 24.4332 | 24.8244 | 25.2243
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.92234 | Diversity Factor: 0.92 | Uncompensated |  | Reactive Power |  |  | MVAr | 19.2423 | 18.9599 | 18.7975 | 18.8452 | 19.1444 | 19.047 | 19.1425 | 19.1894 | 19.4004 | 19.6564 | 19.8939 | 20.1422 | 20.3577 | 20.6361 | 20.9163 | 21.2368 | 21.5814 | 21.922 | 22.2571 | 22.5999 | 22.9505 | 23.309 | 23.6756 | 24.0502 | 24.4332 | 24.8244 | 25.2243
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Crows Nest 132_11kV
| Crows Nest 132_11kV | [16 empty] | 2014 | WINTER
[6 empty] | Zone commissioned |  | 2016-05-31
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | [8 empty] | 0 | 0 | 1858.623 | 1842.019 | 1852.87 | 1864.039 | 1892.329 | 1924.577 | 1954.794 | 1986.069 | 2013.331 | 2047.419 | 2081.647 | 2120.516 | 2162.07 | 2203.17 | 2243.528 | 2284.709 | 2326.724 | 2369.585 | 2413.303 | 2457.892 | 2503.362 | 2549.727 | 2596.998 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1858.6432 | 8.5911 | 10.9554 | 11.2758 | 28.5537 | 32.5397 | 30.4816 | 31.5401 | 27.487 | 34.3601 | 34.4921 | 39.1581 | 41.8511 | 41.384 | 40.6258 | 41.4442 | 42.2742 | 43.1158 | 43.9693 | 44.8348 | 45.7125 | 46.6025 | 47.5049
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 |  |  | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 929.3216 | 4.2955 | 5.4777 | 5.6379 | 14.2769 | 16.2698 | 15.2408 | 15.77 | 13.7435 | 17.1801 | 17.246 | 19.5791 | 20.9255 | 20.692 | 20.3129 | 20.7221 | 21.1371 | 21.5579 | 21.9847 | 22.4174 | 22.8562 | 23.3012 | 23.7525
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 929.3216 | 4.2955 | 5.4777 | 5.6379 | 14.2769 | 16.2698 | 15.2408 | 15.77 | 13.7435 | 17.1801 | 17.246 | 19.5791 | 20.9255 | 20.692 | 20.3129 | 20.7221 | 21.1371 | 21.5579 | 21.9847 | 22.4174 | 22.8562 | 23.3012 | 23.7525
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.01981 | -0.03764 | -0.28923 | -0.38828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.01981 | -0.03764 | -0.28923 | -0.38828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx1 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.0832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx1 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.0832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx2 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.7334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx2 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.7334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx3 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx3 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx4 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280.4419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx4 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280.4419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5109 | 15.9091 | 23.6088 | 24.527 | 24.9258 | 23.1998 | 23.5604 | 23.9262 | 24.2971 | 24.6733 | 25.0548 | 25.4417 | 25.8341 | 26.232 | 26.6355 | 27.0447 | 27.4597 | 27.8805 | 28.3073 | 28.74 | 29.1789 | 29.6239 | 30.0751
[35 empty] | Econometric |  | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5109 | 15.9091 | 23.6088 | 24.527 | 24.9258 | 23.1998 | 23.5604 | 23.9262 | 24.2971 | 24.6733 | 25.0548 | 25.4417 | 25.8341 | 26.232 | 26.6355 | 27.0447 | 27.4597 | 27.8805 | 28.3073 | 28.74 | 29.1789 | 29.6239 | 30.0751
| 0 | [33 empty] | Energy Efficiency |  | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.504 | -11.5759 | -17.8419 | -18.5008 | -10.6489 | -6.93 | -8.3196 | -8.1561 | -10.5536 | -7.4932 | -7.8088 | -5.8626 | -4.9085 | -5.54 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.504 | -11.5759 | -17.8419 | -18.5008 | -10.6489 | -6.93 | -8.3196 | -8.1561 | -10.5536 | -7.4932 | -7.8088 | -5.8626 | -4.9085 | -5.54 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226
[35 empty] | Solar PV |  | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [8 empty] | 0 | [59 empty] | 0%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.95947 | 0.92058 | 0.89571 | 0.88361 | 0.88361 | 0.88361 | 0.88361 | 0.88361 | 0.88361 | 0.88361 | -4.053% | -4.053% | -2.702% | -1.351% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Crows Nest 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 | 0 | 0 | 0 | 1858.623 | 1842.019 | 1852.87 | 1864.039 | 1892.329 | 1924.577 | 1954.794 | 1986.069 | 2013.331 | 2047.419 | 2081.647 | 2120.516 | 2162.07 | 2203.17 | 2243.528 | 2284.709 | 2326.724 | 2369.585 | 2413.303 | 2457.892 | 2503.362 | 2549.727 | 2596.998
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 35.4115 | 35.0952 | 35.3019 | 35.5147 | 36.0537 | 36.6681 | 37.2438 | 37.8397 | 38.3591 | 39.0086 | 39.6607 | 40.4013 | 41.193 | 41.976 | 42.745 | 43.5296 | 44.33 | 45.1467 | 45.9796 | 46.8291 | 47.6955 | 48.5788 | 49.4795
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 29.4145 | 29.1644 | 29.3523 | 29.5456 | 30.0352 | 30.5932 | 31.1159 | 31.6567 | 32.128 | 32.7172 | 33.3087 | 33.9801 | 34.6978 | 35.4074 | 36.104 | 36.8147 | 37.5395 | 38.2789 | 39.0328 | 39.8016 | 40.5855 | 41.3846 | 42.1992
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 19.7171 | 19.522 | 19.613 | 19.7066 | 19.9438 | 20.214 | 20.4672 | 20.7291 | 20.9574 | 21.2427 | 21.5292 | 21.8544 | 22.2019 | 22.5456 | 22.883 | 23.2272 | 23.5783 | 23.9363 | 24.3015 | 24.6738 | 25.0535 | 25.4405 | 25.835
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0.83065 | 0.83101 | 0.83146 | 0.83193 | 0.83307 | 0.83433 | 0.83546 | 0.8366 | 0.83756 | 0.83872 | 0.83984 | 0.84106 | 0.84232 | 0.84351 | 0.84464 | 0.84574 | 0.84682 | 0.84788 | 0.84892 | 0.84993 | 0.85093 | 0.85191 | 0.85286
0.98073 | Diversity Factor: 0.98 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 19.7171 | 19.522 | 19.613 | 19.7066 | 19.9438 | 20.214 | 20.4672 | 20.7291 | 20.9574 | 21.2427 | 21.5292 | 21.8544 | 22.2019 | 22.5456 | 22.883 | 23.2272 | 23.5783 | 23.9363 | 24.3015 | 24.6738 | 25.0535 | 25.4405 | 25.835
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0.83065 | 0.83101 | 0.83146 | 0.83193 | 0.83307 | 0.83433 | 0.83546 | 0.8366 | 0.83756 | 0.83872 | 0.83984 | 0.84106 | 0.84232 | 0.84351 | 0.84464 | 0.84574 | 0.84682 | 0.84788 | 0.84892 | 0.84993 | 0.85093 | 0.85191 | 0.85286
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Crows Nest 33_11kV
| Crows Nest 33_11kV | [16 empty] | 2014 | WINTER
[6 empty] | Zone decommissioned |  | 2016-05-31
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 2403 | 2338 | 2001 | 2171 | 2070 | 1904 | 1836 |  | 1869.412 | 1874.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 20.52 | 83.2901 | -1824.2189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 3151 |  | 3151 | 3151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 4965 |  | 4965 | 4965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Crows Nest 33_11kV Tx1 | 0 | 0 | -442 | -42 | 0 | 64 | 86 | -2.0123 | 30.1151 | -496.1664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Crows Nest 33_11kV Tx2 | -50 | 0 | -68 | 0 | -106 | -63 | -86 | -33.4556 | -1.3239 | -605.4668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Crows Nest 33_11kV Tx3 | 25 | 0 | 100 | 0 | 137 | 29 | 0 | -0.78741 | 25.7255 | -194.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  | Crows Nest 33_11kV Tx4 | 25 | 0 | 410 | 50 | -31 | -12 | 0 | 56.7753 | 28.7735 | -528.4337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.18421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.072082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.20824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 5981. Minor Works to resolve Overload on Panel 14R Crows Nest | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx3 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 5981. Minor Works to resolve Overload on Panel 14R Crows Nest | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx4 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6382. Change of Open Points to Relieve Panel 2 + 7 Crows Nest Remedial Feeders. | Crows Nest 33_11kV Tx4 | Crows Nest 33_11kV Tx3 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6439. Relieve remedial Crows Nest Panel 30 feeder. | Crows Nest 33_11kV Tx1 | Crows Nest 33_11kV Tx2 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6455. NOP change to balance tx loads at Crows Nest Zone. | Crows Nest 33_11kV Tx1 | Crows Nest 33_11kV Tx3 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6455. NOP change to balance tx loads at Crows Nest Zone. | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx3 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6463. Connection of feeders to new S/G at Crows Nest | Crows Nest 33_11kV Tx1 | Crows Nest 33_11kV Tx4 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6463. Connection of feeders to new S/G at Crows Nest | Crows Nest 33_11kV Tx3 | Crows Nest 33_11kV Tx2 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6463. Connection of feeders to new S/G at Crows Nest | Crows Nest 33_11kV Tx3 | Crows Nest 33_11kV Tx4 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6502. 11kV Supply Arrangements for the Sydney Harbour Tunnel | North Sydney 33_11kV Tx5 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6515. North Sydney Zone Conversion - Stage 1 of 4 | Crows Nest 33_11kV Tx1 | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6515. North Sydney Zone Conversion - Stage 1 of 4 | North Sydney 33_11kV Tx5 | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6731. Crows Nest - Change of Open Points to relieve Panel 4L | Crows Nest 33_11kV Tx4 | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6819. Relieve Tx2 at Crows Nest Zone | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6831. Crows Nest Zone Development | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6916. Open Point Change to Releive Overloaded Crows Nest Tx2 | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6916. Open Point Change to Releive Overloaded Crows Nest Tx2 | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx1 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.0832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx1 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.0832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx2 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.7334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx2 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.7334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx3 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx3 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx4 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280.4419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx4 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280.4419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2010068. Establishment of S.47793 Miller Palmer, 520 Miller Street, Cammeray |  | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010695. Establishment of S.49221 Belmont Shirley, Belmont Ave, Wollstonecraft and Decommission S.1394. Uprate of S.4897 Morton Gilles. | Crows Nest 33_11kV Tx4 | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011308. Establishment of S.49960 West Church No 2, 8 West Street, North Sydney | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011450. Establishment of 2 x Unit Chamber Subs; S.49977 Walker Berry No 1; and S.50280 Walker Berry No 2; 136-142 Walker Street, North Sydney |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | 0: Forecast ROG | HVCON_ID: 2011774. Establishment of new S.61541 Oxley Pacific for Commercial/Residential Development, 545-553 Pacific Hwy, St Leonards |  | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0: ROG Justification | HVCON_ID: 2011774. Establishment of new S.61541 Oxley Pacific for Commercial/Residential Development, 545-553 Pacific Hwy, St Leonards | Crows Nest 33_11kV Tx4 | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 2.095% |  | 0: 7 year ROG ok | HVCON_ID: 2012284. Establishment of S.48184 Willoughby Walter, DP586037 (Between 2-4 Artarmon Rd and 460 Willoughby Rd) Mosman | Crows Nest 33_11kV Tx1 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 year ROG ok
[35 empty] | HVCON_ID: 2012423. Establishment of S.62947 Angelo Berry No 2, 211-215 Pacific Hwy, North Sydney NSW 2060 |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012423. Establishment of S.62947 Angelo Berry No 2, 211-215 Pacific Hwy, North Sydney NSW 2060 | North Sydney 33_11kV Tx2 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | HVCON_ID: 2012423. Establishment of S.62947 Angelo Berry No 2, 211-215 Pacific Hwy, North Sydney NSW 2060 | North Sydney 33_11kV Tx3 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.95947 | 0.92058 | 0.89571 | 0.88361 | 0.88361 | 0.88361 | 0.88361 | 0.88361 | 0.88361 | 0.88361 | -4.053% | -4.053% | -2.702% | -1.351% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | HVCON_ID: 2013050. Establishment of S.63443 Atchison Zig Zag No 1 and S.63444 Atchison Zig Zag No 2, 103-111 Willoughby Rd, Crows Nest |  | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2014104. Relocate S.2316 NORTH SYDNEY ANZAC CLUB, Anzac Avenue, Cammeray Load Increase at S.35329 ERNEST MILLER | North Sydney 33_11kV Tx4 | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Substation Load Detail | [33 empty] | Econometric |  | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Econometric |  | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Crows Nest 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1836 | 1927 | 1869.412 | 1874.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Econometric |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 34.9805 |  | 35.6171 | 35.7213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0123 | -0.90073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 28.9239 | 30.3575 | 29.4503 | 29.6689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4556 | -1.0991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 19.6734 |  | 20.0314 | 19.8939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.78741 | -0.35246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2747 | -1.0182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.82686 |  | 0.82686 | 0.83056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.9523 | Diversity Factor: 0.95 | Uncompensated |  | Reactive Power |  |  | MVAr | 19.6734 | 20.6485 | 20.0314 | 19.8939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.82686 |  | 0.82686 | 0.83056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | Solar PV |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Gore Hill 33_11kV
| Gore Hill 33_11kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 3767 | 3654 | 3499 | 3575 | 3549 | 3204 | 2925.75 |  | 2871.286 | 2807.952 | 2748.512 | 2716.532 | 2697.993 | 2676.076 | 2689.949 | 2717.235 | 2740.588 | 2764.469 | 2779.058 | 2804.06 | 2828.395 | 2860.904 | 2897.474 | 2932.563 | 2965.1 | 2998.268 | 3032.076 | 3066.532 | 3101.646 | 3137.425 | 3173.879 | 3211.017 | 3248.848 |  |  | Total | 0 | 27 | 45 | 111.6 | 0 | -255 | -107.1 | -17.0747 | 13.7103 | -9.2101 | -7.3968 | -18.539 | -21.9171 | 13.8727 | 27.286 | 23.3537 | 23.8809 | 14.5893 | 25.0017 | 24.3349 | 32.509 | 36.57 | 35.089 | 32.5369 | 33.1681 | 33.8079 | 34.4563 | 35.1133 | 35.7792 | 36.4541 | 37.138 | 37.831
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 5086 |  | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 7939 |  | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 |  |  | Gore Hill 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4226 | -2.4247 | -1.3067 | -1.0495 | -2.6303 | -3.1096 | 1.9683 | 3.8714 | 3.3134 | 3.3882 | 2.0699 | 3.5473 | 3.4527 | 4.6124 | 5.1886 | 4.9785 | 4.6164 | 4.7059 | 4.7967 | 4.8887 | 4.9819 | 5.0764 | 5.1721 | 5.2692 | 5.3675
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Gore Hill 33_11kV Tx2 | 0 | 27 | 0 | 62.1 | 0 | 25 | -107.1 | -5.5397 | 25.2554 | -2.9881 | -2.3998 | -6.0148 | -7.1107 | 4.5008 | 8.8526 | 7.5768 | 7.7479 | 4.7333 | 8.1115 | 7.8952 | 10.5472 | 11.8647 | 11.3842 | 10.5562 | 10.761 | 10.9686 | 11.1789 | 11.3921 | 11.6082 | 11.8271 | 12.049 | 12.2738
| Transformer Loads | [35 empty] | Gore Hill 33_11kV Tx3 | 0 | 0 | 45 | 0 | 0 | -280 | 0 | -3.2782 | -3.2811 | -1.7683 | -1.4201 | -3.5594 | -4.208 | 2.6635 | 5.2388 | 4.4838 | 4.585 | 2.8011 | 4.8002 | 4.6722 | 6.2416 | 7.0213 | 6.7369 | 6.2469 | 6.3681 | 6.4909 | 6.6154 | 6.7416 | 6.8694 | 6.999 | 7.1303 | 7.2634
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | Gore Hill 33_11kV Tx4 | 0 | 0 | 0 | 49.5 | 0 | 0 | 0 | -5.8342 | -5.8393 | -3.147 | -2.5274 | -6.3345 | -7.4887 | 4.7401 | 9.3233 | 7.9796 | 8.1598 | 4.9849 | 8.5427 | 8.3149 | 11.1079 | 12.4955 | 11.9894 | 11.1174 | 11.3331 | 11.5517 | 11.7732 | 11.9977 | 12.2252 | 12.4558 | 12.6895 | 12.9263
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | Gore Hill 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3947 | -0.080165 | -0.15231 | -1.1704 | -1.5712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1893 | -0.18331 | -0.34829 | -2.6764 | -3.5929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Gore Hill 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8873 | -0.10848 | -0.20611 | -1.5838 | -2.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Gore Hill 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3588 | -0.19306 | -0.36681 | -2.8186 | -3.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning | Gore Hill 33_11kV Tx3 | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning | Gore Hill 33_11kV Tx3 | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2005136. Est S.36123 "Herbert Frederick No4" for JGRT Holdings - St Leonards. |  | Gore Hill 33_11kV Tx4 | 0 | 0 | 0 | 49.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2007061. Establishment of S.35551 RNS Hospital No. 7, Westbourne St (Cnr Reserve Rd) St Leonards |  | Gore Hill 33_11kV Tx3 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2007088. LOAD INCREASE AT S.6425 TELECOM Herbert No1 -GORE HILL. (NOTE: Load on S.6425 has not increased anywhere near the amount of 140A that was originally requested) |  | Gore Hill 33_11kV Tx2 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2007155. Establishment of S.35608 Reserve Frederick No. 2, 1A Frederick St, Artarmon |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010502. Uprate S.2385, Greenwich Rd, Greenwich. Recover existing OH mains and supply new sub via UG cable | Chatswood 33_11kV Tx13 | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012396. Decommission S.1770 RNS Hospital No 2 and S.7346 RNS Hospital No 4, RNS Hospital - Westbourne St, St Leonards |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | -107.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2012543. Establishment of S.63282 Atchison Ln Christie No. 1 and S.63283 Atchison Ln Christie No 2, 6-16 Atchison Street, St Leonards |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Econometric |  | Gore Hill 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9863 | 3.8191 | 5.7269 | 5.6422 | 5.7258 | 5.5785 | 5.6579 | 5.7384 | 5.8199 | 5.9026 | 5.9863 | 6.0712 | 6.1573 | 6.2445 | 6.3329 | 6.4224 | 6.5132 | 6.6052 | 6.6984 | 6.7929 | 6.8886 | 6.9857 | 7.084
[35 empty] | Econometric |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5421 | 8.7331 | 13.0956 | 12.9019 | 13.0931 | 12.7563 | 12.9379 | 13.1219 | 13.3084 | 13.4974 | 13.689 | 13.8831 | 14.0799 | 14.2793 | 14.4814 | 14.6862 | 14.8937 | 15.1041 | 15.3173 | 15.5333 | 15.7523 | 15.9741 | 16.199
[35 empty] | Econometric |  | Gore Hill 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6879 | 5.168 | 7.7497 | 7.635 | 7.7482 | 7.5489 | 7.6563 | 7.7652 | 7.8756 | 7.9874 | 8.1008 | 8.2157 | 8.3321 | 8.4501 | 8.5697 | 8.6909 | 8.8137 | 8.9382 | 9.0644 | 9.1922 | 9.3218 | 9.4531 | 9.5862
| 0 | [33 empty] | Econometric |  | Gore Hill 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7836 | 9.1974 | 13.7918 | 13.5878 | 13.7891 | 13.4344 | 13.6256 | 13.8194 | 14.0158 | 14.2149 | 14.4167 | 14.6211 | 14.8283 | 15.0383 | 15.2512 | 15.4669 | 15.6855 | 15.907 | 16.1315 | 16.3591 | 16.5896 | 16.8233 | 17.0601
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Gore Hill 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4226 | -1.03 | -3.2129 | -4.7163 | -7.1868 | -7.1805 | -3.7575 | -1.7071 | -2.3444 | -2.3501 | -3.75 | -2.3553 | -2.5337 | -1.4588 | -0.9687 | -1.266 | -1.7165 | -1.7165 | -1.7165 | -1.7165 | -1.7165 | -1.7165 | -1.7165 | -1.7165 | -1.7165
[35 empty] | Energy Efficiency |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.5397 | -2.3553 | -7.3469 | -10.7846 | -16.434 | -16.4197 | -8.5922 | -3.9037 | -5.361 | -5.374 | -8.5751 | -5.3859 | -5.7938 | -3.3359 | -2.2151 | -2.895 | -3.9251 | -3.9251 | -3.9251 | -3.9251 | -3.9251 | -3.9251 | -3.9251 | -3.9251 | -3.9251
[35 empty] | Energy Efficiency |  | Gore Hill 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2782 | -1.3938 | -4.3477 | -6.3821 | -9.7253 | -9.7168 | -5.0847 | -2.3101 | -3.1725 | -3.1802 | -5.0745 | -3.1872 | -3.4286 | -1.9741 | -1.3109 | -1.7132 | -2.3228 | -2.3228 | -2.3228 | -2.3228 | -2.3228 | -2.3228 | -2.3228 | -2.3228 | -2.3228
| 0 | [33 empty] | Energy Efficiency |  | Gore Hill 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8342 | -2.4805 | -7.7375 | -11.3579 | -17.3077 | -17.2926 | -9.049 | -4.1112 | -5.646 | -5.6597 | -9.0309 | -5.6722 | -6.1018 | -3.5133 | -2.3329 | -3.0489 | -4.1338 | -4.1338 | -4.1338 | -4.1338 | -4.1338 | -4.1338 | -4.1338 | -4.1338 | -4.1338
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Gore Hill 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Gore Hill 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Solar PV |  | Gore Hill 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | -1.162% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.97317 | 0.94706 | 0.93013 | 0.92181 | 0.92181 | 0.92181 | 0.92181 | 0.92181 | 0.92181 | 0.92181 | -2.683% | -2.683% | -1.788% | -0.894% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Gore Hill 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 2925.75 | 2968 | 2871.286 | 2807.952 | 2748.512 | 2716.532 | 2697.993 | 2676.076 | 2689.949 | 2717.235 | 2740.588 | 2764.469 | 2779.058 | 2804.06 | 2828.395 | 2860.904 | 2897.474 | 2932.563 | 2965.1 | 2998.268 | 3032.076 | 3066.532 | 3101.646 | 3137.425 | 3173.879 | 3211.017 | 3248.848
|  |  |  | Apparent Power |  |  | MVA | 55.743 |  | 54.7053 | 53.4987 | 52.3662 | 51.7569 | 51.4037 | 50.9861 | 51.2504 | 51.7703 | 52.2152 | 52.6702 | 52.9482 | 53.4245 | 53.8882 | 54.5076 | 55.2043 | 55.8728 | 56.4928 | 57.1247 | 57.7688 | 58.4253 | 59.0943 | 59.776 | 60.4705 | 61.1781 | 61.8989
|  |  |  | Real Power |  |  | MW | 49.7862 | 50.5052 | 48.8594 | 47.7817 | 46.7702 | 46.2261 | 45.9106 | 45.5376 | 45.7737 | 46.238 | 46.6354 | 47.0418 | 47.29 | 47.7155 | 48.1296 | 48.6828 | 49.3051 | 49.9022 | 50.4558 | 51.0202 | 51.5955 | 52.1819 | 52.7794 | 53.3882 | 54.0085 | 54.6405 | 55.2842
|  |  |  | Reactive Power |  |  | MVAr | 25.0722 |  | 24.6055 | 24.0628 | 23.5534 | 23.2793 | 23.1205 | 22.9326 | 23.0515 | 23.2854 | 23.4855 | 23.6901 | 23.8152 | 24.0294 | 24.238 | 24.5165 | 24.8299 | 25.1306 | 25.4094 | 25.6937 | 25.9834 | 26.2787 | 26.5796 | 26.8862 | 27.1986 | 27.5168 | 27.841
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.89314 |  | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314
0.91324 | Diversity Factor: 0.91 | Uncompensated |  | Reactive Power |  |  | MVAr | 25.0722 | 25.4343 | 24.6055 | 24.0628 | 23.5534 | 23.2793 | 23.1205 | 22.9326 | 23.0515 | 23.2854 | 23.4855 | 23.6901 | 23.8152 | 24.0294 | 24.238 | 24.5165 | 24.8299 | 25.1306 | 25.4094 | 25.6937 | 25.9834 | 26.2787 | 26.5796 | 26.8862 | 27.1986 | 27.5168 | 27.841
|  |  |  | PF |  |  |  | 0.89314 |  | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314 | 0.89314
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer33
| Customer33 | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | [5 empty] | 68 | 57.3779 |  | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 |  |  | Total | Historical Spots & Transfers 2012: 52; Historical Spots & Transfers 2013: 157
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Major Customer Connection |  | Gore Hill Technology Park Data-Centre 1 33kV | Historical Spots & Transfers 2012: 3; Historical Spots & Transfers 2013: 9
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Customer33 | Compensated |  | Load (LV side) |  |  | Amps | 57 |  | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
|  |  |  | Apparent Power |  |  | MVA | 3.2796 |  | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796 | 3.2796
|  |  |  | Real Power |  |  | MW | 2.9516 |  | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516 | 2.9516
|  |  |  | Reactive Power |  |  | MVAr | 1.4295 |  | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.74942 | Diversity Factor: 0.75 | Uncompensated |  | Reactive Power |  |  | MVAr | 1.4295 |  | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295 | 1.4295
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer34
| Customer34 | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Customer34 | Compensated |  | Load (LV side) |  |  | Amps | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| #VALUE! | Uncompensated |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer35
| Customer35 | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total |  |  |  |  | 77 | 67 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Customer35 | Compensated |  | Load (LV side) |  |  | Amps | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
|  |  |  | Apparent Power |  |  | MVA | 4.6298 |  | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298 | 4.6298
|  |  |  | Real Power |  |  | MW | 4.1668 |  | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668 | 4.1668
|  |  |  | Reactive Power |  |  | MVAr | 2.0181 |  | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.647 | Diversity Factor: 0.65 | Uncompensated |  | Reactive Power |  |  | MVAr | 2.0181 |  | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Mosman 132_11kV
| Mosman 132_11kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 4960 | 5010 | 4410 | 4511 | 4557 | 4171.308 | 3956 |  | 4031.436 | 3914.764 | 3846.806 | 3829.567 | 3858.365 | 3888.092 | 3944.267 | 4002.592 | 4058.511 | 4117.374 | 4173.915 | 4241.186 | 4309.619 | 4380.507 | 4458.306 | 4536.181 | 4614.545 | 4694.797 | 4776.966 | 4861.079 | 4947.165 | 5035.255 | 5125.378 | 5217.563 | 5311.842 |  |  | Total | 0 | 64.8 | 0 | 0 | 97 | 0 | 0 | -43.2143 | 4.3667 | 10.0429 | 21.2028 | 29.0133 | 29.9455 | 56.5802 | 58.7322 | 56.2993 | 59.2516 | 56.9034 | 67.6904 | 68.8453 | 74.5106 | 78.5843 | 78.6338 | 79.1016 | 80.9814 | 82.8892 | 84.8255 | 86.7905 | 88.7847 | 90.8085 | 92.8623 | 94.9466
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 4674 |  | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674 | 4674
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 8008 |  | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 | 8008 |  |  | Mosman 132_11kV Tx1 | 0 | 64.8 | 0 | 0 | -6 | 24 | 0 | 17.8372 | -47.6736 | 2.8383 | 5.9923 | 8.1997 | 8.4632 | 15.9907 | 16.5989 | 15.9113 | 16.7457 | 16.082 | 19.1306 | 19.457 | 21.0581 | 22.2094 | 22.2234 | 22.3556 | 22.8869 | 23.4261 | 23.9733 | 24.5287 | 25.0923 | 25.6643 | 26.2447 | 26.8337
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Mosman 132_11kV Tx2 | 0 | 0 | -75 | 0 | 6 | -65 | 0 | -46.0524 | 117.3904 | 2.5688 | 5.4234 | 7.4212 | 7.6596 | 14.4724 | 15.0228 | 14.4005 | 15.1557 | 14.5551 | 17.3142 | 17.6096 | 19.0587 | 20.1007 | 20.1134 | 20.233 | 20.7139 | 21.2018 | 21.6971 | 22.1997 | 22.7098 | 23.2275 | 23.7528 | 24.2859
| Transformer Loads | [35 empty] | Mosman 132_11kV Tx3 | 0 | 0 | 75 | 0 | 0 | -29 | 0 | -208.3265 | 86.2712 | 2.0175 | 4.2593 | 5.8284 | 6.0156 | 11.3662 | 11.7985 | 11.3098 | 11.9028 | 11.4311 | 13.5981 | 13.8301 | 14.9681 | 15.7865 | 15.7964 | 15.8904 | 16.268 | 16.6513 | 17.0403 | 17.435 | 17.8356 | 18.2422 | 18.6548 | 19.0735
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 97 | 70 | 0 | 193.3274 | -151.6213 | 2.6183 | 5.5278 | 7.564 | 7.8071 | 14.751 | 15.312 | 14.6777 | 15.4474 | 14.8352 | 17.6475 | 17.9486 | 19.4256 | 20.4876 | 20.5005 | 20.6225 | 21.1126 | 21.61 | 22.1148 | 22.6271 | 23.147 | 23.6746 | 24.2101 | 24.7534
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6245. Mosman Zone Development 2006 / 2007 (Stage 3) - Augmentation of Panel 21, 29 & 31 Feeders. | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx3 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6473. Castle Cove Zone Development - 2009 (Pa 15, 43 & 44 Feeders) | Castle Cove 132_11kV Tx3 | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6883. Change in open points only - Mosman Zone PA24 and PA43 | Mosman 132_11kV Tx3 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7054. DNP7054 Mosman Zone Development East | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 7054. DNP7054 Mosman Zone Development East | Mosman 132_11kV Tx4 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 7108. Mosman Zone Development North West | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7108. Mosman Zone Development North West | Mosman 132_11kV Tx3 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx3 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx3 | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx3 | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx4 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2005060. Taronga zoo upgrade to 80 HVA (at this stage) |  | Mosman 132_11kV Tx1 | 0 | 64.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2009653. Establishment of S.47389 Spit Medusa to replace S.1416 Parrawi Park controlled by CP.791 Parriwi Rd, Within Road Reserve of Spit Rd, Opposite Medusa St, Mosman - Cater for 200amp supply to Beauty Point Public School and g | Mosman 132_11kV Tx1 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2009653. Establishment of S.47389 Spit Medusa to replace S.1416 Parrawi Park controlled by CP.791 Parriwi Rd, Within Road Reserve of Spit Rd, Opposite Medusa St, Mosman - Cater for 200amp supply to Beauty Point Public School and g | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011104. C/S SELF ASSESSED DNP - Establishment of S.48386 Plunkett Bayview, Plunkett Rd, Mosman | Mosman 132_11kV Tx3 | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2011184. Replacement of S.1620 and S.1623 with proposed S.49772 Courallie Minnamurra and S.49773 Woonona Narani, Courallie Rd & Woonona Rd, Northbridge. | Mosman 132_11kV Tx4 | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2011333. Establishment of S.36129 Bellambi Marooba, Bellambi St, Northbridge and decommission S.695 Bellambi St | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011703. Establishment of S.48587 Cowles Holt to relieve overloaded sub S.1332 and distributor S.35441, within Mosman Council Park Reserve off Cowles Rd (nr Holt Ave), Mosman | Mosman 132_11kV Tx1 | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012284. Establishment of S.48184 Willoughby Walter, DP586037 (Between 2-4 Artarmon Rd and 460 Willoughby Rd) Mosman | Crows Nest 33_11kV Tx1 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2012294. S.6012 Cowles Military is to be looped in during LV augmentation works. Email advice | Mosman 132_11kV Tx4 | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2012308. Navy upgrade facilities - Establishment of HVC CP.49007 HMAS Middle Head and Decomm of S.763 Hunters Bay |  | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9 | 2.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013247. Establishment of S.63994 Gurrigal Military, 507 Military Rd, Mosman | Mosman 132_11kV Tx1 | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7039 | 17.2593 | 25.7973 | 27.4754 | 27.9913 | 26.4865 | 26.9512 | 27.4229 | 27.9017 | 28.3877 | 28.881 | 29.3817 | 29.8898 | 30.4056 | 30.9291 | 31.4603 | 31.9995 | 32.5468 | 33.1021 | 33.6657 | 34.2377 | 34.8181 | 35.4072
| 0 | [33 empty] | Econometric |  | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7825 | 15.6206 | 23.3479 | 24.8667 | 25.3336 | 23.9716 | 24.3922 | 24.8192 | 25.2525 | 25.6924 | 26.1388 | 26.5919 | 27.0519 | 27.5187 | 27.9924 | 28.4733 | 28.9613 | 29.4565 | 29.9591 | 30.4692 | 30.9869 | 31.5122 | 32.0453
| Diversity Factor: 0 | [33 empty] | Econometric |  | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8975 | 12.2679 | 18.3368 | 19.5295 | 19.8963 | 18.8266 | 19.1569 | 19.4922 | 19.8326 | 20.178 | 20.5287 | 20.8845 | 21.2457 | 21.6123 | 21.9844 | 22.3621 | 22.7453 | 23.1343 | 23.529 | 23.9296 | 24.3362 | 24.7488 | 25.1675
[35 empty] | Econometric |  | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9516 | 15.9212 | 23.7974 | 25.3453 | 25.8212 | 24.4331 | 24.8618 | 25.2969 | 25.7386 | 26.1869 | 26.642 | 27.1038 | 27.5726 | 28.0484 | 28.5313 | 29.0213 | 29.5187 | 30.0235 | 30.5358 | 31.0557 | 31.5834 | 32.1188 | 32.6622
[35 empty] | Energy Efficiency |  | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1628 | -0.67356 | -6.8656 | -11.267 | -17.5976 | -19.0122 | -12.0006 | -9.8876 | -11.0399 | -10.6772 | -11.8197 | -9.2571 | -9.424 | -8.3235 | -7.6804 | -8.1822 | -8.5734 | -8.5734 | -8.5734 | -8.5734 | -8.5734 | -8.5734 | -8.5734 | -8.5734 | -8.5734
[35 empty] | Energy Efficiency |  | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0524 | -0.60961 | -6.2137 | -10.1972 | -15.9268 | -17.2071 | -10.8612 | -8.9488 | -9.9917 | -9.6635 | -10.6974 | -8.3781 | -8.5292 | -7.5332 | -6.9512 | -7.4053 | -7.7594 | -7.7594 | -7.7594 | -7.7594 | -7.7594 | -7.7594 | -7.7594 | -7.7594 | -7.7594
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Energy Efficiency |  | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.82651 | -0.47877 | -4.8801 | -8.0086 | -12.5084 | -13.5139 | -8.5301 | -7.0281 | -7.8472 | -7.5894 | -8.4015 | -6.58 | -6.6986 | -5.9164 | -5.4592 | -5.8159 | -6.094 | -6.094 | -6.094 | -6.094 | -6.094 | -6.094 | -6.094 | -6.094 | -6.094
[10 empty] | ROG Justification | [24 empty] | Energy Efficiency |  | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0726 | -0.62135 | -6.3333 | -10.3935 | -16.2333 | -17.5383 | -11.0703 | -9.121 | -10.184 | -9.8495 | -10.9034 | -8.5394 | -8.6934 | -7.6782 | -7.085 | -7.5478 | -7.9088 | -7.9088 | -7.9088 | -7.9088 | -7.9088 | -7.9088 | -7.9088 | -7.9088 | -7.9088
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 5.984% |  | 7 year ROG ok | [24 empty] | Solar PV |  | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 year ROG ok
[35 empty] | Solar PV |  | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Solar PV |  | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.97023 | 0.94135 | 0.92267 | 0.91352 | 0.91352 | 0.91352 | 0.91352 | 0.91352 | 0.91352 | 0.91352 | -2.977% | -2.977% | -1.984% | -0.992% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Mosman 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 3956 | 4222 | 4031.436 | 3914.764 | 3846.806 | 3829.567 | 3858.365 | 3888.092 | 3944.267 | 4002.592 | 4058.511 | 4117.374 | 4173.915 | 4241.186 | 4309.619 | 4380.507 | 4458.306 | 4536.181 | 4614.545 | 4694.797 | 4776.966 | 4861.079 | 4947.165 | 5035.255 | 5125.378 | 5217.563 | 5311.842
|  |  |  | Apparent Power |  |  | MVA | 75.3719 |  | 76.8092 | 74.5863 | 73.2915 | 72.963 | 73.5117 | 74.0781 | 75.1484 | 76.2596 | 77.325 | 78.4465 | 79.5238 | 80.8054 | 82.1093 | 83.4599 | 84.9421 | 86.4259 | 87.9189 | 89.4479 | 91.0134 | 92.616 | 94.2562 | 95.9345 | 97.6516 | 99.4079 | 101.2041
|  |  |  | Real Power |  |  | MW | 74.935 | 79.9736 | 76.7782 | 74.5623 | 73.2717 | 72.9443 | 73.4912 | 74.0558 | 75.1225 | 76.2297 | 77.2911 | 78.4081 | 79.4809 | 80.757 | 82.0549 | 83.4596 | 84.9412 | 86.4236 | 87.9149 | 89.4416 | 91.0042 | 92.6034 | 94.2396 | 95.9134 | 97.6254 | 99.3761 | 101.166
|  |  |  | Reactive Power |  |  | MVAr | 8.1035 |  | 2.1809 | 1.8919 | 1.7034 | 1.6555 | 1.7354 | 1.8179 | 1.9737 | 2.1355 | 2.2905 | 2.4537 | 2.6104 | 2.7968 | 2.9864 | 0.19161 | 0.40802 | 0.62458 | 0.84242 | 1.0654 | 1.2937 | 1.5273 | 1.7663 | 2.0108 | 2.2609 | 2.5166 | 2.7781
|  |  |  | Capacitors In Service |  |  | MVAr | 3 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
|  |  |  | PF |  |  |  | 0.9942 |  | 0.9996 | 0.99968 | 0.99973 | 0.99974 | 0.99972 | 0.9997 | 0.99965 | 0.99961 | 0.99956 | 0.99951 | 0.99946 | 0.9994 | 0.99934 | 1 | 0.99999 | 0.99997 | 0.99995 | 0.99993 | 0.9999 | 0.99986 | 0.99982 | 0.99978 | 0.99973 | 0.99968 | 0.99962
0.89808 | Diversity Factor: 0.9 | Uncompensated |  | Reactive Power |  |  | MVAr | 11.1035 | 11.6484 | 11.1809 | 10.8919 | 10.7034 | 10.6555 | 10.7354 | 10.8179 | 10.9737 | 11.1355 | 11.2905 | 11.4537 | 11.6104 | 11.7968 | 11.9864 | 12.1916 | 12.408 | 12.6246 | 12.8424 | 13.0654 | 13.2937 | 13.5273 | 13.7663 | 14.0108 | 14.2609 | 14.5166 | 14.7781
|  |  |  | PF |  |  |  | 0.9892 |  | 0.98956 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895 | 0.9895
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## North Sydney 132_11kV
| North Sydney 132_11kV | [16 empty] | 2014 | WINTER
[6 empty] | Zone commissioned |  | 2015-03-31
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | [8 empty] | 0 | 2840.554 | 2964.398 | 2914.276 | 2909.873 | 2906.475 | 2938.438 | 2984.871 | 3026.428 | 3069.023 | 3100.291 | 3145.301 | 3189.731 | 3244.699 | 3305.095 | 3363.825 | 3419.638 | 3476.518 | 3534.481 | 3593.54 | 3653.71 | 3715.006 | 3777.442 | 3841.035 | 3905.799 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2840.3512 | 222.1334 | -0.72531 | -4.4705 | -3.4501 | 32.4472 | 47.1194 | 42.1524 | 43.188 | 31.6926 | 45.6069 | 45.0014 | 55.6534 | 61.1223 | 59.4112 | 56.4378 | 57.4965 | 58.5695 | 59.657 | 60.7591 | 61.8761 | 63.0082 | 64.1554 | 65.3181
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 |  |  | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 935.7837 | -20.4055 | -0.24177 | -1.4902 | -1.15 | 10.8157 | 15.7065 | 14.0508 | 14.396 | 10.5642 | 15.2023 | 15.0005 | 18.5511 | 20.3741 | 19.8037 | 18.8126 | 19.1655 | 19.5232 | 19.8857 | 20.253 | 20.6254 | 21.0027 | 21.3851 | 21.7727
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 952.7837 | 60.8445 | -0.24177 | -1.4902 | -1.15 | 10.8157 | 15.7065 | 14.0508 | 14.396 | 10.5642 | 15.2023 | 15.0005 | 18.5511 | 20.3741 | 19.8037 | 18.8126 | 19.1655 | 19.5232 | 19.8857 | 20.253 | 20.6254 | 21.0027 | 21.3851 | 21.7727
| Transformer Loads | [35 empty] | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 951.7837 | 181.6945 | -0.24177 | -1.4902 | -1.15 | 10.8157 | 15.7065 | 14.0508 | 14.396 | 10.5642 | 15.2023 | 15.0005 | 18.5511 | 20.3741 | 19.8037 | 18.8126 | 19.1655 | 19.5232 | 19.8857 | 20.253 | 20.6254 | 21.0027 | 21.3851 | 21.7727
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.84771 | -0.048725 | -0.092577 | -0.71138 | -0.95501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.84771 | -0.048725 | -0.092577 | -0.71138 | -0.95501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.84771 | -0.048725 | -0.092577 | -0.71138 | -0.95501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.3447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.3447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.3447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012286. Establishment of S.62446 Spring Walker No 2 & Decommissioning of S.6063 Spring Little Spring, 100 Mount Street, North Sydney |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012286. Establishment of S.62446 Spring Walker No 2 & Decommissioning of S.6063 Spring Little Spring, 100 Mount Street, North Sydney | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013384. Establishment of S.64403 Berry Pacific No 2 and S.64403 Berry Pacific No 3, 177 Pacific Hwy, North Sydney and Decomm S.5532 Berry Angelo |  | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013384. Establishment of S.64403 Berry Pacific No 2 and S.64403 Berry Pacific No 3, 177 Pacific Hwy, North Sydney and Decomm S.5532 Berry Angelo | North Sydney 132_11kV Tx11 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2014027. New Chamber S.64679 Little Walker Arthur No.2 and Decomm S.2713 Arthur Standards House, 80 Arthur Street, North Sydney, 1000kVA chamber substation | North Sydney 132_11kV Tx12 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.696 | 14.7533 | 21.9829 | 22.7223 | 23.0599 | 21.8137 | 22.1265 | 22.4434 | 22.7647 | 23.0903 | 23.4203 | 23.7547 | 24.0937 | 24.4373 | 24.7855 | 25.1384 | 25.4961 | 25.8586 | 26.2259 | 26.5983 | 26.9756 | 27.358 | 27.7456
| 0 | [33 empty] | Econometric |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.696 | 14.7533 | 21.9829 | 22.7223 | 23.0599 | 21.8137 | 22.1265 | 22.4434 | 22.7647 | 23.0903 | 23.4203 | 23.7547 | 24.0937 | 24.4373 | 24.7855 | 25.1384 | 25.4961 | 25.8586 | 26.2259 | 26.5983 | 26.9756 | 27.358 | 27.7456
| Diversity Factor: 0 | [33 empty] | Econometric |  | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.696 | 14.7533 | 21.9829 | 22.7223 | 23.0599 | 21.8137 | 22.1265 | 22.4434 | 22.7647 | 23.0903 | 23.4203 | 23.7547 | 24.0937 | 24.4373 | 24.7855 | 25.1384 | 25.4961 | 25.8586 | 26.2259 | 26.5983 | 26.9756 | 27.358 | 27.7456
[35 empty] | Energy Efficiency |  | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0353 | -10.0528 | -14.9025 | -22.7616 | -22.9173 | -12.2442 | -6.1073 | -8.0757 | -8.0474 | -12.2005 | -7.888 | -8.4198 | -5.2036 | -3.7196 | -4.6335 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729
[35 empty] | Energy Efficiency |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0353 | -10.0528 | -14.9025 | -22.7616 | -22.9173 | -12.2442 | -6.1073 | -8.0757 | -8.0474 | -12.2005 | -7.888 | -8.4198 | -5.2036 | -3.7196 | -4.6335 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729
| 0 | [33 empty] | Energy Efficiency |  | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0353 | -10.0528 | -14.9025 | -22.7616 | -22.9173 | -12.2442 | -6.1073 | -8.0757 | -8.0474 | -12.2005 | -7.888 | -8.4198 | -5.2036 | -3.7196 | -4.6335 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729
| Diversity Factor: 0 | [33 empty] | Solar PV |  | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [8 empty] | Rog Capped +/-5% | [59 empty] | Rog Capped +/-5%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | North Sydney 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 | 0 | 0 | 2840.554 | 2964.398 | 2914.276 | 2909.873 | 2906.475 | 2938.438 | 2984.871 | 3026.428 | 3069.023 | 3100.291 | 3145.301 | 3189.731 | 3244.699 | 3305.095 | 3363.825 | 3419.638 | 3476.518 | 3534.481 | 3593.54 | 3653.71 | 3715.006 | 3777.442 | 3841.035 | 3905.799
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 54.1198 | 56.4794 | 55.5244 | 55.4405 | 55.3758 | 55.9848 | 56.8694 | 57.6612 | 58.4727 | 59.0685 | 59.926 | 60.7725 | 61.8198 | 62.9705 | 64.0895 | 65.1529 | 66.2366 | 67.3409 | 68.4661 | 69.6125 | 70.7804 | 71.9699 | 73.1816 | 74.4155
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 52.2518 | 54.319 | 53.4013 | 53.3246 | 53.2655 | 53.8218 | 54.6298 | 55.3526 | 56.0932 | 56.6366 | 57.4186 | 58.1903 | 59.1446 | 60.1927 | 61.2114 | 62.1792 | 63.1651 | 64.1694 | 65.1924 | 66.2342 | 67.2952 | 68.3756 | 69.4757 | 70.5957
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 14.0965 | 15.4713 | 15.2075 | 15.1703 | 15.1417 | 15.4112 | 15.8025 | 16.1526 | 16.5112 | 16.7744 | 17.1532 | 17.5269 | 17.9891 | 18.4967 | 18.9901 | 19.4588 | 19.9363 | 20.4227 | 20.9182 | 21.4228 | 21.9366 | 22.4599 | 22.9927 | 23.5352
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0.96548 | 0.96175 | 0.96176 | 0.96183 | 0.96189 | 0.96137 | 0.96062 | 0.95996 | 0.9593 | 0.95883 | 0.95816 | 0.95751 | 0.95673 | 0.95589 | 0.95509 | 0.95436 | 0.95363 | 0.9529 | 0.95218 | 0.95147 | 0.95076 | 0.95006 | 0.94936 | 0.94867
0.94989 | Diversity Factor: 0.95 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 14.0965 | 15.4713 | 15.2075 | 15.1703 | 15.1417 | 15.4112 | 15.8025 | 16.1526 | 16.5112 | 16.7744 | 17.1532 | 17.5269 | 17.9891 | 18.4967 | 18.9901 | 19.4588 | 19.9363 | 20.4227 | 20.9182 | 21.4228 | 21.9366 | 22.4599 | 22.9927 | 23.5352
|  |  |  | PF |  |  |  | 0 |  | 0 | 0.96548 | 0.96175 | 0.96176 | 0.96183 | 0.96189 | 0.96137 | 0.96062 | 0.95996 | 0.9593 | 0.95883 | 0.95816 | 0.95751 | 0.95673 | 0.95589 | 0.95509 | 0.95436 | 0.95363 | 0.9529 | 0.95218 | 0.95147 | 0.95076 | 0.95006 | 0.94936 | 0.94867
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## North Sydney 33_11kV
| North Sydney 33_11kV | [16 empty] | 2014 | WINTER
[6 empty] | Zone decommissioned |  | 2015-03-31
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 4091 | 4002 | 3683 | 3607 | 3485 | 3317 | 3178 |  | 3007.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | 0 | 19.8 | 0 | 58.6 | 23.4 | 0 | 0 | 30.4883 | -2857.0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 6282 |  | 6282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 8015 |  | 8015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | North Sydney 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | North Sydney 33_11kV Tx2 | -75 | 19.8 | 0 | 16.2 | 23.4 | 0 | 22 | -25.1043 | -796.1974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | North Sydney 33_11kV Tx3 | 75 | 61 | 0 | 0 | 0 | 0 | 0 | 65.9365 | -681.3516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  | North Sydney 33_11kV Tx4 | 0 | -61 | 0 | 0 | -85 | -18 | -26 | -5.9691 | -799.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 42.4 | 85 | 18 | 4 | -4.3748 | -580.0342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | North Sydney 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | North Sydney 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Broad based demand management |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 5948. Minor Zone Development on Panels 4, 8, 9, 10, and 13 Feeders at North Sydney Zone | North Sydney 33_11kV Tx2 | North Sydney 33_11kV Tx3 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6405. Change of Open Points to Relieve Panel 26L North Sydney Remedial Feeder. | North Sydney 33_11kV Tx4 | North Sydney 33_11kV Tx3 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6502. 11kV Supply Arrangements for the Sydney Harbour Tunnel | North Sydney 33_11kV Tx5 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6515. North Sydney Zone Conversion - Stage 1 of 4 | Crows Nest 33_11kV Tx1 | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6515. North Sydney Zone Conversion - Stage 1 of 4 | North Sydney 33_11kV Tx5 | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6764. North Sydney Open Point Changes | North Sydney 33_11kV Tx4 | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx3 | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.3447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.3447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.3447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2004450. Est Basement S.8190 "Wheeler Mount" - North Sydney Embedded Generation, Generator |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 50.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2004459. Est S.8223 'Little Walker Arthur 98' |  | North Sydney 33_11kV Tx2 | 0 | 19.8 | 0 | 16.2 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2010198. Replace S.3057 Wheeler William with 48069 Wheeler Lane, North Sydney. Transfer 450A (LV) from S.3057 (PA26) to existing S.8190 (PA42). No new load, only LV load transfer. | North Sydney 33_11kV Tx4 | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011501. Establishment of S.50434 Carabella Parker, Premises of Loreto College, Carrabella St, Kirribilli | North Sydney 33_11kV Tx4 | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012286. Establishment of S.62446 Spring Walker No 2 & Decommissioning of S.6063 Spring Little Spring, 100 Mount Street, North Sydney |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012286. Establishment of S.62446 Spring Walker No 2 & Decommissioning of S.6063 Spring Little Spring, 100 Mount Street, North Sydney | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Weather Corrected Forecast Loads 2014: Forecast ROG | HVCON_ID: 2012305. Uprate chamber S.373 Middle St and LV UG, Middle Street, North Sydney Zone | North Sydney 33_11kV Tx4 | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | Weather Corrected Forecast Loads 2014: ROG Justification | HVCON_ID: 2012423. Establishment of S.62947 Angelo Berry No 2, 211-215 Pacific Hwy, North Sydney NSW 2060 | North Sydney 33_11kV Tx2 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | -0.6269% |  | Weather Corrected Forecast Loads 2014: Rog Capped +/-5% | HVCON_ID: 2012423. Establishment of S.62947 Angelo Berry No 2, 211-215 Pacific Hwy, North Sydney NSW 2060 | North Sydney 33_11kV Tx3 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rog Capped +/-5%
[35 empty] | HVCON_ID: 2012432. Decommission and remove S.2813 and reconfigure LV network, 211-215 Pacific Hwy, North Sydney |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012432. Decommission and remove S.2813 and reconfigure LV network, 211-215 Pacific Hwy, North Sydney | North Sydney 33_11kV Tx2 | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | HVCON_ID: 2014104. Relocate S.2316 NORTH SYDNEY ANZAC CLUB, Anzac Avenue, Cammeray Load Increase at S.35329 ERNEST MILLER | North Sydney 33_11kV Tx4 | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Econometric |  | North Sydney 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Substation Load Detail | [33 empty] | Econometric |  | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | North Sydney 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Econometric |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | North Sydney 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 3178 | 3134 | 3007.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | North Sydney 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 60.549 |  | 57.2981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 58.4092 | 57.6005 | 55.3089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 15.9546 |  | 14.9664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | North Sydney 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.96466 |  | 0.96528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | North Sydney 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.96412 | Diversity Factor: 0.96 | Uncompensated |  | Reactive Power |  |  | MVAr | 15.9546 | 15.7337 | 14.9664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.96466 |  | 0.96528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | Solar PV |  | North Sydney 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Load Detail | [33 empty] | Solar PV |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## RNS Hospital 132_11kV
| RNS Hospital 132_11kV | [16 empty] | 2014 | WINTER
[6 empty] | Zone commissioned |  | 2011-11-30
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | [5 empty] | 383 | 470 |  | 484.2126 | 575.5728 | 568.625 | 564.2322 | 561.2228 | 558.2405 | 559.0048 | 561.9521 | 564.3112 | 566.6884 | 567.6031 | 569.9711 | 572.2027 | 575.6369 | 579.6395 | 583.3977 | 586.7278 | 590.1166 | 593.5648 | 597.0733 | 600.6427 | 604.2738 | 607.9674 | 611.7242 | 615.5452 |  |  | Total | 0 | 0 | 0 | 0 | 45 | 280 | 225.9 | 2.8118 | 97.8566 | -1.7998 | -1.8498 | -3.0093 | -2.9823 | 0.76428 | 2.9473 | 2.3591 | 2.3772 | 0.91469 | 2.368 | 2.2316 | 3.4342 | 4.0026 | 3.7582 | 3.3301 | 3.3888 | 3.4482 | 3.5084 | 3.5694 | 3.6311 | 3.6936 | 3.7569 | 3.8209
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2810 |  | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 5108 |  | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 |  |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 100 | 95.4 | 4.1855 | 73.1409 | -0.88007 | -0.90453 | -1.4715 | -1.4583 | 0.37372 | 1.4412 | 1.1535 | 1.1624 | 0.44726 | 1.1579 | 1.0912 | 1.6793 | 1.9572 | 1.8377 | 1.6283 | 1.657 | 1.6861 | 1.7156 | 1.7454 | 1.7755 | 1.8061 | 1.837 | 1.8683
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 45 | 180 | 130.5 | -1.3737 | 24.7157 | -0.91975 | -0.94531 | -1.5378 | -1.524 | 0.39056 | 1.5061 | 1.2056 | 1.2148 | 0.46743 | 1.2101 | 1.1404 | 1.755 | 2.0454 | 1.9205 | 1.7017 | 1.7317 | 1.7621 | 1.7929 | 1.824 | 1.8556 | 1.8875 | 1.9198 | 1.9526
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0071263 | -0.0079181 | -0.015044 | -0.1156 | -0.1552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0074476 | -0.0082751 | -0.015723 | -0.12082 | -0.16219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning | Gore Hill 33_11kV Tx3 | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning | Gore Hill 33_11kV Tx3 | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2007061. Establishment of S.35551 RNS Hospital No. 7, Westbourne St (Cnr Reserve Rd) St Leonards |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2008464. Establishment of 6 x Kiosks & 1x Chamber Sub: S.36151 Spine Campbell No 1; S.36152 Spine Campbell No 2; S.36153 Spine Campbell No 3 (Chamber); S.36161 Spine Pacific No 1; S.36162 Spine Pacific No 2; S.36163 Spine Pacif |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9 | 0 | 6.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2008464. Establishment of 6 x Kiosks & 1x Chamber Sub: S.36151 Spine Campbell No 1; S.36152 Spine Campbell No 2; S.36153 Spine Campbell No 3 (Chamber); S.36161 Spine Pacific No 1; S.36162 Spine Pacific No 2; S.36163 Spine Pacif |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8 | 0 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2009492. New S.47161 RNSH Comm Health No.1 and S.47162 RNSH Comm Health No.2 |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011785. Establishment of S.50040 Westbourne NS TAFE, North Sydney TAFE, 213 Pacific Hway, St Leongards (site fronts Westbourne St) |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6 | 0 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012395. Establishment of S.62445 RNSH Clinical Services, RNS Hospital Clinical Service Bldg - Westbourne St, St Leonards |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66654 | 1.3235 | 1.9998 | 1.9948 | 2.0206 | 2.0189 | 2.0446 | 2.0706 | 2.0969 | 2.1235 | 2.1505 | 2.1778 | 2.2055 | 2.2335 | 2.2618 | 2.2906 | 2.3196 | 2.3491 | 2.3789 | 2.409 | 2.4396 | 2.4705 | 2.5019
| Diversity Factor: 0 | [33 empty] | Econometric |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69659 | 1.3832 | 2.09 | 2.0847 | 2.1117 | 2.1099 | 2.1367 | 2.1639 | 2.1914 | 2.2193 | 2.2474 | 2.276 | 2.3049 | 2.3342 | 2.3638 | 2.3938 | 2.4242 | 2.455 | 2.4861 | 2.5177 | 2.5496 | 2.5819 | 2.6146
[35 empty] | Energy Efficiency |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3145 | -0.55199 | -1.5387 | -2.213 | -3.3557 | -3.2979 | -1.6469 | -0.57773 | -0.89101 | -0.90813 | -1.6496 | -0.96563 | -1.0593 | -0.49855 | -0.24828 | -0.39581 | -0.63351 | -0.63351 | -0.63351 | -0.63351 | -0.63351 | -0.63351 | -0.63351 | -0.63351 | -0.63351
[35 empty] | Energy Efficiency |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3737 | -0.57688 | -1.6081 | -2.3127 | -3.507 | -3.4465 | -1.7211 | -0.60378 | -0.93118 | -0.94907 | -1.724 | -1.0092 | -1.1071 | -0.52103 | -0.25948 | -0.41366 | -0.66207 | -0.66207 | -0.66207 | -0.66207 | -0.66207 | -0.66207 | -0.66207 | -0.66207 | -0.66207
| 0 | [33 empty] | Solar PV |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Solar PV |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 3.819% |  | Weighted ROG calc, half customer load with 0% ROG, check HVCON2009492, DNP6469 | [59 empty] | Weighted ROG calc, half customer load with 0% ROG, check HVCON2009492, DNP6469
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.98659 | 0.97336 | 0.96466 | 0.96035 | 0.96035 | 0.96035 | 0.96035 | 0.96035 | 0.96035 | 0.96035 | -1.341% | -1.341% | -0.894% | -0.447% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | RNS Hospital 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 470 | 487.9473 | 484.2126 | 575.5728 | 568.625 | 564.2322 | 561.2228 | 558.2405 | 559.0048 | 561.9521 | 564.3112 | 566.6884 | 567.6031 | 569.9711 | 572.2027 | 575.6369 | 579.6395 | 583.3977 | 586.7278 | 590.1166 | 593.5648 | 597.0733 | 600.6427 | 604.2738 | 607.9674 | 611.7242 | 615.5452
|  |  |  | Apparent Power |  |  | MVA | 8.9547 |  | 9.2255 | 10.9661 | 10.8338 | 10.7501 | 10.6927 | 10.6359 | 10.6505 | 10.7066 | 10.7516 | 10.7969 | 10.8143 | 10.8594 | 10.9019 | 10.9673 | 11.0436 | 11.1152 | 11.1787 | 11.2432 | 11.3089 | 11.3758 | 11.4438 | 11.513 | 11.5833 | 11.6549 | 11.7277
|  |  |  | Real Power |  |  | MW | 7.6281 | 7.9193 | 7.8587 | 9.3415 | 9.2287 | 9.1574 | 9.1086 | 9.0602 | 9.0726 | 9.1204 | 9.1587 | 9.1973 | 9.2121 | 9.2506 | 9.2868 | 9.3425 | 9.4075 | 9.4685 | 9.5225 | 9.5775 | 9.6335 | 9.6904 | 9.7484 | 9.8073 | 9.8673 | 9.9282 | 9.9902
|  |  |  | Reactive Power |  |  | MVAr | 4.6904 |  | 4.8322 | 5.7439 | 5.6746 | 5.6307 | 5.6007 | 5.571 | 5.5786 | 5.608 | 5.6315 | 5.6553 | 5.6644 | 5.688 | 5.7103 | 5.7446 | 5.7845 | 5.822 | 5.8552 | 5.8891 | 5.9235 | 5.9585 | 5.9941 | 6.0303 | 6.0672 | 6.1047 | 6.1428
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.85185 |  | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185
0.80804 | Diversity Factor: 0.81 | Uncompensated |  | Reactive Power |  |  | MVAr | 4.6904 | 4.8695 | 4.8322 | 5.7439 | 5.6746 | 5.6307 | 5.6007 | 5.571 | 5.5786 | 5.608 | 5.6315 | 5.6553 | 5.6644 | 5.688 | 5.7103 | 5.7446 | 5.7845 | 5.822 | 5.8552 | 5.8891 | 5.9235 | 5.9585 | 5.9941 | 6.0303 | 6.0672 | 6.1047 | 6.1428
|  |  |  | PF |  |  |  | 0.85185 |  | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185 | 0.85185
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer36
| Customer36 | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total |  |  |  |  | 172 | 147 | 134 |  | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Customer36 | Compensated |  | Load (LV side) |  |  | Amps | 134 |  | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
|  |  |  | Apparent Power |  |  | MVA | 7.6591 |  | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591 | 7.6591
|  |  |  | Real Power |  |  | MW | 6.8932 |  | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932 | 6.8932
|  |  |  | Reactive Power |  |  | MVAr | 3.3385 |  | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.59787 | Diversity Factor: 0.6 | Uncompensated |  | Reactive Power |  |  | MVAr | 3.3385 |  | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385 | 3.3385
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer37
| Customer37 | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total |  |  |  |  | 179 | 178 | 158 |  | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Customer37 | Compensated |  | Load (LV side) |  |  | Amps | 158 |  | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
|  |  |  | Apparent Power |  |  | MVA | 9.0309 |  | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309 | 9.0309
|  |  |  | Real Power |  |  | MW | 8.1278 |  | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278 | 8.1278
|  |  |  | Reactive Power |  |  | MVAr | 3.9365 |  | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.68346 | Diversity Factor: 0.68 | Uncompensated |  | Reactive Power |  |  | MVAr | 3.9365 |  | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365 | 3.9365
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF