## Inclusions and Exclusions
Sydney Forecast Inclusions and Exclusions
Date Printed |  | 08JUL14:11:21:24
| Description | Value
Season |  | Summer | Summer
Either Summer or Winter
Year |  | 2015 | 2015
Year that the forecast starts
POE |  | 50% | 0.5
10%, 50%, 90%
Spots and Transfers |  | Y | Y
Are Spots and Transfers Included?
BBDM Spots |  | Y | Y
Is BBDM included?
Spots Coefficient |  | 55% | 0.55
Scaling factor applied to spot loads in the future
Aligned ROGs |  | Capped | Capped
Have ROGs been aligned to econometric forecast?
Committed Projects |  | Y | Y
Are Committed Projects Included?
Major Customers Scaling Factor |  | 100% | 1
Scaling factor applied to major customer connections in the future
Future Transfers |  | Y | Y
Are future transfers included?
Future Spots |  | 4 | 4
Future spots are cleared from the following forecast year

## Epping 66_11kV
| Epping 66_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 3058 | 3392 | 3509 | 3507 | 2841 | 3207 | 2853.9 |  | 3080.788 | 2930.138 | 2805.762 | 2757.727 | 2751.239 | 2756.286 | 2783.387 | 2819.001 | 2850.299 | 2883.691 | 2911.467 | 2947.663 | 2983.957 | 3025.948 | 3071.203 | 3115.813 | 3159.417 | 3203.963 | 3249.463 | 3295.931 | 3343.38 | 3388.028 | 3437.116 | 3487.229 | 3538.382 |  |  | Total | -228 | 48.6 | 94.6 | 44.691 | -4.1784 | -2.9943 | 113.2847 | 156.6099 | -16.2692 | -39.6514 | -7.3518 | -6.583 | 5.1208 | 27.4904 | 36.1131 | 31.7266 | 33.8387 | 28.1396 | 36.6602 | 36.7468 | 42.5019 | 45.7887 | 45.1216 | 44.0896 | 45.0277 | 45.9787 | 46.9428 | 47.9203 | 48.9113 | 49.9159 | 50.9343 | 51.9668
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 3932 |  | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932 | 3932
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 5956 |  | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 |  |  | Epping 66_11kV Tx1 | -209 | 55.6 | 94.6 | 46.1955 | -2.0892 | -1.4972 | -494.8576 | 54.655 | -8.1346 | -4.8257 | -3.6759 | -3.2915 | 2.5604 | 13.7452 | 18.0565 | 15.8633 | 16.9193 | 14.0698 | 18.3301 | 18.3734 | 21.251 | 22.8943 | 22.5608 | 22.0448 | 22.5138 | 22.9893 | 23.4714 | 23.9601 | 24.4556 | 24.9579 | 25.4672 | 25.9834
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Epping 66_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | -874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Epping 66_11kV Tx3 | -19 | -7 | 0 | -1.5045 | -2.0892 | -1.4972 | 1482.1424 | 101.955 | -8.1346 | -34.8257 | -3.6759 | -3.2915 | 2.5604 | 13.7452 | 18.0565 | 15.8633 | 16.9193 | 14.0698 | 18.3301 | 18.3734 | 21.251 | 22.8943 | 22.5608 | 22.0448 | 22.5138 | 22.9893 | 23.4714 | 23.9601 | 24.4556 | 24.9579 | 25.4672 | 25.9834
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Epping 66_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7506 | -5.0361 | -8.3606 | -7.6611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7506 | -5.0361 | -8.3606 | -7.6611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6131. Relief of Feeders from Epping Zone Substation Panels 1,10,11 and 12 | Epping 66_11kV Tx1 | Pennant Hills 132_11kV Tx1 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6313. Works required to supply Macquarie Uni Hospital Load (LLC) | Epping 66_11kV Tx1 | Macquarie Park 132_11kV Tx1 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6416. Works required to relieve Remedial Panel 41 Feeder - Meadowbank. | Meadowbank 132_11kV Tx3 | Epping 66_11kV Tx1 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6827. Epping Zone 11kV switchgear replacement | Epping 66_11kV Tx1 | Epping 66_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6827. Epping Zone 11kV switchgear replacement | Epping 66_11kV Tx1 | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6827. Epping Zone 11kV switchgear replacement | Epping 66_11kV Tx2 | Epping 66_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6827. Epping Zone 11kV switchgear replacement | Epping 66_11kV Tx2 | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2005039. Est S.8723 'Macquarie Uni No.9', Est S.8421 'Macquarie Uni No.10',Est S.8422 'Macquarie Uni No.11', Recover S.2517 'Macquarie University 2' |  | Epping 66_11kV Tx1 | 0 | 48.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2005039. Est S.8723 'Macquarie Uni No.9', Est S.8421 'Macquarie Uni No.10',Est S.8422 'Macquarie Uni No.11', Recover S.2517 'Macquarie University 2' | Epping 66_11kV Tx1 | Epping 66_11kV Tx3 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2005039. Est S.8723 'Macquarie Uni No.9', Est S.8421 'Macquarie Uni No.10',Est S.8422 'Macquarie Uni No.11', Recover S.2517 'Macquarie University 2' | Epping 66_11kV Tx3 | Epping 66_11kV Tx1 | 110 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2007215. Establishment of S.35642-& S.35643 Talavera Christie No.2-3, 2 Technology Place, Macquarie Park |  | Epping 66_11kV Tx1 | 0 | 0 | 21.6 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2008172. Establishment of 2 x 800kVA L type kiosks - S.36012 Macquarie Uni No 12 and S.36013 Macquarie Uni No 13, Macquarie Drive (Macquarie Uni) Macquarie Park - This load considered with other projects can be considered a LLC - |  | Epping 66_11kV Tx1 | 0 | 0 | 0 | 33.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010129. Establishment of S.47527 Talavera Khartoum No 8, 54-60 Talavera Rd, Macquarie Park |  | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010129. Establishment of S.47527 Talavera Khartoum No 8, 54-60 Talavera Rd, Macquarie Park | Macquarie Park 132_11kV Tx3 | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2010678. Establishment of S.49162 Waterloo Herring and S.49163 Macquarie Eastern, Macquarie University NSW 2109. Decommission and recover S.3673 Macquarie University No.3 - LLC | Epping 66_11kV Tx3 | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2012216. Establishment of S.62143 Herring Windsor No 1, 120-128 Herring Rd, Macquarie Park |  | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012231. Establishment of S.62278 Talavera Herring No.1 & S.62279 Talavera Herring No.2, 84-92 Talavera Road Macquarie Park NSW 21113 |  | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012262. Establishment of S.62347 Dayman Epping, 7 Dayman Pl, Marsfield | Epping 66_11kV Tx1 | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013043. Establishment of S.63380 Herring Windsor No 2 and S.63381 Herring Windsor No 3, Toga Macquarie Developments P/L Residential Apartments, 120-128 Herring Rd, Macquarie Park |  | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013066. New commercial development AFC requesting 2800A, Establishment of 2 x Kiosks, S.63508 Talavera Christie No 5 and S.63509 Talavera Christie No 6, 118 Talavera Road, Macquarie Park |  | Epping 66_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Epping 66_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.0407 | 20.7508 | 28.3871 | 27.4942 | 28.9397 | 28.5388 | 28.1127 | 28.5328 | 28.9588 | 29.3907 | 29.8285 | 30.2725 | 30.7226 | 31.1789 | 31.6415 | 32.1105 | 32.586 | 33.0681 | 33.5568 | 34.0523 | 34.5546 | 35.0639 | 35.5801
[35 empty] | Econometric |  | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.0407 | 20.7508 | 28.3871 | 27.4942 | 28.9397 | 28.5388 | 28.1127 | 28.5328 | 28.9588 | 29.3907 | 29.8285 | 30.2725 | 30.7226 | 31.1789 | 31.6415 | 32.1105 | 32.586 | 33.0681 | 33.5568 | 34.0523 | 34.5546 | 35.0639 | 35.5801
| 0 | [33 empty] | Energy Efficiency |  | Epping 66_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7065 | -2.107 | -9.3881 | -14.4835 | -22.3238 | -23.1495 | -13.3264 | -8.6758 | -10.4142 | -10.2093 | -13.207 | -9.3786 | -9.7732 | -7.3395 | -6.1463 | -6.9361 | -7.9147 | -7.9147 | -7.9147 | -7.9147 | -7.9147 | -7.9147 | -7.9147 | -7.9147 | -7.9147
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7065 | -2.107 | -9.3881 | -14.4835 | -22.3238 | -23.1495 | -13.3264 | -8.6758 | -10.4142 | -10.2093 | -13.207 | -9.3786 | -9.7732 | -7.3395 | -6.1463 | -6.9361 | -7.9147 | -7.9147 | -7.9147 | -7.9147 | -7.9147 | -7.9147 | -7.9147 | -7.9147 | -7.9147
[35 empty] | Solar PV |  | Epping 66_11kV Tx1 | 0 | 0 | 0 | -1.5045 | -2.0892 | -1.4972 | -0.85763 | -1.1385 | -1.277 | -1.4422 | -1.5825 | -1.6937 | -1.7843 | -1.8681 | -1.8065 | -1.8352 | -1.4042 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682
[35 empty] | Solar PV |  | Epping 66_11kV Tx3 | 0 | 0 | 0 | -1.5045 | -2.0892 | -1.4972 | -0.85763 | -1.1385 | -1.277 | -1.4422 | -1.5825 | -1.6937 | -1.7843 | -1.8681 | -1.8065 | -1.8352 | -1.4042 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682 | -1.682
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 11.78% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95652 | 0.91493 | 0.88841 | 0.87553 | 0.87553 | 0.87553 | 0.87553 | 0.87553 | 0.87553 | 0.87553 | -4.348% | -4.348% | -2.899% | -1.449% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Epping 66_11kV | Compensated |  | Load (LV side) |  |  | Amps | 2853.9 | 3111 | 3080.788 | 2930.138 | 2805.762 | 2757.727 | 2751.239 | 2756.286 | 2783.387 | 2819.001 | 2850.299 | 2883.691 | 2911.467 | 2947.663 | 2983.957 | 3025.948 | 3071.203 | 3115.813 | 3159.417 | 3203.963 | 3249.463 | 3295.931 | 3343.38 | 3388.028 | 3437.116 | 3487.229 | 3538.382
|  |  |  | Apparent Power |  |  | MVA | 54.3741 |  | 58.6969 | 55.8266 | 53.457 | 52.5418 | 52.4181 | 52.5143 | 53.0307 | 53.7092 | 54.3055 | 54.9417 | 55.4709 | 56.1605 | 56.852 | 57.6521 | 58.5143 | 59.3642 | 60.195 | 61.0437 | 61.9106 | 62.7959 | 63.7 | 64.5506 | 65.4859 | 66.4406 | 67.4152
|  |  |  | Real Power |  |  | MW | 53.4497 | 58.2649 | 58.6642 | 55.8085 | 53.4479 | 52.5355 | 52.4122 | 52.5081 | 53.023 | 53.6993 | 54.2935 | 54.9273 | 55.4543 | 56.1409 | 56.8291 | 57.6251 | 58.4826 | 59.3277 | 60.1535 | 60.9968 | 61.8579 | 62.7371 | 63.6345 | 64.5506 | 65.4855 | 66.4394 | 67.4126
|  |  |  | Reactive Power |  |  | MVAr | 9.9834 |  | 1.9574 | 1.424 | 0.98311 | 0.81268 | 0.78965 | 0.80756 | 0.90373 | 1.0301 | 1.141 | 1.2594 | 1.3579 | 1.4861 | 1.6146 | 1.7633 | 1.9235 | 2.0813 | 2.2356 | 2.3931 | 2.5539 | 2.7182 | 2.8858 | 0.056885 | 0.2315 | 0.40968 | 0.59147
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 12 | 12 | 12
|  |  |  | PF |  |  |  | 0.983 |  | 0.99944 | 0.99967 | 0.99983 | 0.99988 | 0.99989 | 0.99988 | 0.99985 | 0.99982 | 0.99978 | 0.99974 | 0.9997 | 0.99965 | 0.9996 | 0.99953 | 0.99946 | 0.99938 | 0.99931 | 0.99923 | 0.99915 | 0.99906 | 0.99897 | 1 | 0.99999 | 0.99998 | 0.99996
0.94372 | Diversity Factor: 0.94 | Uncompensated |  | Reactive Power |  |  | MVAr | 9.9834 | 10.8828 | 10.9574 | 10.424 | 9.9831 | 9.8127 | 9.7897 | 9.8076 | 9.9037 | 10.0301 | 10.141 | 10.2594 | 10.3578 | 10.4861 | 10.6146 | 10.7633 | 10.9235 | 11.0813 | 11.2356 | 11.3931 | 11.5539 | 11.7181 | 11.8858 | 12.0569 | 12.2315 | 12.4097 | 12.5915
|  |  |  | PF |  |  |  | 0.983 |  | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Hunters Hill 66_11kV
| Hunters Hill 66_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 2965 | 3157 | 3194 | 3504 | 2538 | 2540 | 2239 |  | 2240.196 | 2115.647 | 2039.524 | 2003.786 | 2005.185 | 2011.786 | 2037.069 | 2067.789 | 2094.937 | 2124.015 | 2149.899 | 2182.648 | 2215.74 | 2252.887 | 2292.597 | 2331.981 | 2371.038 | 2411.005 | 2451.895 | 2493.722 | 2536.498 | 2580.237 | 2624.953 | 2670.659 | 2717.371 |  |  | Total | 0 | 0 | 0 | -2.6311 | -3.3922 | -467.1557 | -0.62879 | 37.1467 | -12.539 | -5.602 | -1.7459 | 1.3989 | 6.6013 | 25.2835 | 30.7191 | 27.1485 | 29.0775 | 25.8847 | 32.7488 | 33.0919 | 37.1469 | 39.7104 | 39.3834 | 39.0573 | 39.9672 | 40.8902 | 41.8264 | 42.7759 | 43.739 | 44.7159 | 45.7067 | 46.7117
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 3665 |  | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 5956 |  | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 | 5956 |  |  | Hunters Hill 66_11kV Tx1 | 0 | -85 | -28 | -1.2019 | -1.5496 | -191.3427 | -0.28723 | -3.6331 | -5.7278 | -2.559 | -0.79753 | 0.63902 | 3.0155 | 11.5495 | 14.0325 | 12.4015 | 13.2826 | 11.8241 | 14.9597 | 15.1164 | 16.9687 | 18.1397 | 17.9904 | 17.8414 | 18.2571 | 18.6787 | 19.1063 | 19.5401 | 19.98 | 20.4263 | 20.8789 | 21.3379
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Hunters Hill 66_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Hunters Hill 66_11kV Tx3 | 0 | 85 | 28 | -1.4292 | -1.8426 | -275.813 | -0.34156 | 40.7798 | -6.8112 | -3.043 | -0.94838 | 0.75988 | 3.5858 | 13.7339 | 16.6866 | 14.747 | 15.7948 | 14.0605 | 17.7891 | 17.9755 | 20.1782 | 21.5706 | 21.393 | 21.2159 | 21.7102 | 22.2115 | 22.72 | 23.2358 | 23.759 | 24.2896 | 24.8278 | 25.3737
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Hunters Hill 66_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.71076 | -3.9102 | -4.7885 | -7.3244 | -5.8612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Hunters Hill 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.84519 | -4.6498 | -5.6942 | -8.7097 | -6.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6168. Hunters Hill Zone Development - New Feeder to Woolwich Peninsular. | Hunters Hill 66_11kV Tx1 | Hunters Hill 66_11kV Tx3 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6168. Hunters Hill Zone Development - New Feeder to Woolwich Peninsular. | Hunters Hill 66_11kV Tx3 | Hunters Hill 66_11kV Tx1 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6366. Relieve Hunters Hill Panel 9 & Panel 28 Feeders | Hunters Hill 66_11kV Tx1 | Hunters Hill 66_11kV Tx3 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6766. Hunters Hill to Top Ryde 11kV Load Transfer | Hunters Hill 66_11kV Tx1 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6766. Hunters Hill to Top Ryde 11kV Load Transfer | Hunters Hill 66_11kV Tx1 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6766. Hunters Hill to Top Ryde 11kV Load Transfer | Hunters Hill 66_11kV Tx3 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2011612. Establishment of S.35386 Stansell Victoria No 2, 297-307 Victoria Road, Gladesville |  | Hunters Hill 66_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013386. Establishment of 2 x Kiosks S.64396 Epping Mowbray No 1 and S.64397 Epping Mowbray No 2, Meriton Apartments, 150 Epping Rd, Lane Cove |  | Hunters Hill 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Hunters Hill 66_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1019 | 18.6877 | 24.9584 | 22.5923 | 23.8664 | 23.5203 | 23.1494 | 23.5203 | 23.8964 | 24.278 | 24.6651 | 25.0577 | 25.456 | 25.86 | 26.2698 | 26.6854 | 27.107 | 27.5347 | 27.9684 | 28.4084 | 28.8546 | 29.3072 | 29.7663
[35 empty] | Econometric |  | Hunters Hill 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0126 | 22.2223 | 29.679 | 26.8653 | 28.3804 | 27.9688 | 27.5278 | 27.9688 | 28.4161 | 28.8699 | 29.3301 | 29.797 | 30.2706 | 30.751 | 31.2383 | 31.7326 | 32.234 | 32.7425 | 33.2583 | 33.7815 | 34.3121 | 34.8503 | 35.3962
| 0 | [33 empty] | Energy Efficiency |  | Hunters Hill 66_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2915 | -1.1101 | -7.0733 | -11.2841 | -17.5199 | -18.5882 | -11.2819 | -8.4869 | -9.7312 | -9.4596 | -11.1404 | -8.3864 | -8.6167 | -7.1571 | -6.3843 | -6.9377 | -7.4965 | -7.4965 | -7.4965 | -7.4965 | -7.4965 | -7.4965 | -7.4965 | -7.4965 | -7.4965
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Hunters Hill 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.725 | -1.32 | -8.4112 | -13.4183 | -20.8335 | -22.1039 | -13.4157 | -10.0921 | -11.5717 | -11.2488 | -13.2474 | -9.9726 | -10.2465 | -8.5107 | -7.5919 | -8.2499 | -8.9143 | -8.9143 | -8.9143 | -8.9143 | -8.9143 | -8.9143 | -8.9143 | -8.9143 | -8.9143
[35 empty] | Solar PV |  | Hunters Hill 66_11kV Tx1 | 0 | 0 | 0 | -1.2019 | -1.5496 | 0.15728 | -0.28723 | -0.63078 | -0.70752 | -0.79907 | -0.87679 | -0.93837 | -0.98857 | -1.035 | -1.0009 | -1.0168 | -0.77799 | -0.93188 | -0.93188 | -0.93188 | -0.93188 | -0.93188 | -0.93188 | -0.93188 | -0.93188 | -0.93188 | -0.93188 | -0.93188 | -0.93188 | -0.93188 | -0.93188 | -0.93188
[35 empty] | Solar PV |  | Hunters Hill 66_11kV Tx3 | 0 | 0 | 0 | -1.4292 | -1.8426 | 0.18703 | -0.34156 | -0.75009 | -0.84134 | -0.9502 | -1.0426 | -1.1159 | -1.1755 | -1.2308 | -1.1902 | -1.2091 | -0.92514 | -1.1081 | -1.1081 | -1.1081 | -1.1081 | -1.1081 | -1.1081 | -1.1081 | -1.1081 | -1.1081 | -1.1081 | -1.1081 | -1.1081 | -1.1081 | -1.1081 | -1.1081
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 4.195% |  | Rog Capped +/-5% | [59 empty] | Rog Capped +/-5%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Hunters Hill 66_11kV | Compensated |  | Load (LV side) |  |  | Amps | 2239 | 2319 | 2240.196 | 2115.647 | 2039.524 | 2003.786 | 2005.185 | 2011.786 | 2037.069 | 2067.789 | 2094.937 | 2124.015 | 2149.899 | 2182.648 | 2215.74 | 2252.887 | 2292.597 | 2331.981 | 2371.038 | 2411.005 | 2451.895 | 2493.722 | 2536.498 | 2580.237 | 2624.953 | 2670.659 | 2717.371
|  |  |  | Apparent Power |  |  | MVA | 42.6587 |  | 42.6815 | 40.3085 | 38.8582 | 38.1773 | 38.2039 | 38.3297 | 38.8114 | 39.3967 | 39.9139 | 40.4679 | 40.9611 | 41.585 | 42.2155 | 42.9233 | 43.6799 | 44.4302 | 45.1743 | 45.9358 | 46.7149 | 47.5118 | 48.3268 | 49.1601 | 50.0121 | 50.8829 | 51.7729
|  |  |  | Real Power |  |  | MW | 37.5075 | 38.8477 | 37.5276 | 35.4411 | 34.1659 | 33.5672 | 33.5907 | 33.7013 | 34.1248 | 34.6394 | 35.0942 | 35.5813 | 36.0149 | 36.5635 | 37.1179 | 37.7401 | 38.4054 | 39.0651 | 39.7194 | 40.3889 | 41.0739 | 41.7746 | 42.4912 | 43.2239 | 43.973 | 44.7386 | 45.5211
|  |  |  | Reactive Power |  |  | MVAr | 20.3212 |  | 20.332 | 19.2016 | 18.5107 | 18.1864 | 18.199 | 18.259 | 18.4884 | 18.7672 | 19.0136 | 19.2775 | 19.5125 | 19.8097 | 20.11 | 20.4472 | 20.8076 | 21.165 | 21.5195 | 21.8823 | 22.2534 | 22.633 | 23.0212 | 23.4182 | 23.824 | 24.2389 | 24.6628
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.87925 |  | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925
0.95287 | Diversity Factor: 0.95 | Uncompensated |  | Reactive Power |  |  | MVAr | 20.3212 | 21.0472 | 20.332 | 19.2016 | 18.5107 | 18.1864 | 18.199 | 18.259 | 18.4884 | 18.7672 | 19.0136 | 19.2775 | 19.5125 | 19.8097 | 20.11 | 20.4472 | 20.8076 | 21.165 | 21.5195 | 21.8823 | 22.2534 | 22.633 | 23.0212 | 23.4182 | 23.824 | 24.2389 | 24.6628
|  |  |  | PF |  |  |  | 0.87925 |  | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925 | 0.87925
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Macquarie Park 132_11kV
| Macquarie Park 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 2809 | 3573 | 3565 | 4241 | 3449 | 3584 | 3285 |  | 4338.944 | 4658.145 | 4158.728 | 4134.334 | 4101.664 | 4098.287 | 4122.353 | 4163.3 | 4199.464 | 4236.376 | 4262.29 | 4299.722 | 4336.39 | 4382.48 | 4433.197 | 4482.3 | 4528.441 | 4575.317 | 4622.936 | 4671.307 | 4720.44 | 4770.344 | 4821.029 | 4872.504 | 4924.78 |  |  | Total | 403.2 | 257.4 | 196.8 | 199.2868 | -489.1647 | 173.584 | -25.2064 | 704.4905 | 298.2643 | -514.298 | -31.0826 | -32.67 | -3.3777 | 24.0659 | 40.9473 | 36.1638 | 36.9124 | 25.9139 | 37.4321 | 36.6675 | 46.0907 | 50.7162 | 49.103 | 46.1416 | 46.8756 | 47.6188 | 48.3712 | 49.1329 | 49.9041 | 50.6849 | 51.4754 | 52.2757
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 6000 |  | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 9000 |  | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 |  |  | Macquarie Park 132_11kV Tx1 | 136.8 | -50 | -675.5 | 21.8777 | -0.27779 | 34.1579 | 17.5981 | 302.1875 | 42.4727 | -139.6226 | -11.2911 | -11.8677 | -1.227 | 8.7422 | 14.8745 | 13.1369 | 13.4088 | 9.4135 | 13.5976 | 13.3199 | 16.7429 | 18.4232 | 17.8372 | 16.7614 | 17.0281 | 17.298 | 17.5713 | 17.848 | 18.1282 | 18.4118 | 18.699 | 18.9897
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Macquarie Park 132_11kV Tx2 | 266.4 | 307.4 | -371 | 86.66 | -0.2857 | 91.7567 | 155.4866 | 213.6867 | 64.1163 | -316.9818 | -11.6124 | -12.2054 | -1.2619 | 8.9909 | 15.2978 | 13.5107 | 13.7904 | 9.6814 | 13.9845 | 13.6989 | 17.2194 | 18.9474 | 18.3447 | 17.2384 | 17.5126 | 17.7902 | 18.0713 | 18.3559 | 18.644 | 18.9357 | 19.2311 | 19.53
| Transformer Loads | [35 empty] | Macquarie Park 132_11kV Tx3 | 0 | 0 | 1243.3 | 90.7492 | -488.6012 | 47.6695 | -198.2911 | 188.6163 | 191.6754 | -57.6937 | -8.1791 | -8.5969 | -0.88881 | 6.3328 | 10.775 | 9.5162 | 9.7132 | 6.819 | 9.85 | 9.6488 | 12.1284 | 13.3456 | 12.9211 | 12.1418 | 12.335 | 12.5305 | 12.7285 | 12.9289 | 13.1319 | 13.3373 | 13.5453 | 13.7559
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1898 | -9.1223 | -9.8141 | -10.8411 | -10.8264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Macquarie Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2237 | -9.3819 | -10.0934 | -11.1496 | -11.1344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.86189 | -6.6081 | -7.1093 | -7.8532 | -7.8425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6198. Remedial Feeder Relief - Pymble Pa25, Turramurra Pa4, Macquarie Park Pa6. | Macquarie Park 132_11kV Tx1 | Macquarie Park 132_11kV Tx2 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6208. Macquarie Park Zone Development - Populating Tx.3 Switchgear Group | Macquarie Park 132_11kV Tx1 | Macquarie Park 132_11kV Tx3 | 0 | 0 | 740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6208. Macquarie Park Zone Development - Populating Tx.3 Switchgear Group | Macquarie Park 132_11kV Tx2 | Macquarie Park 132_11kV Tx3 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6313. Works required to supply Macquarie Uni Hospital Load (LLC) | Epping 66_11kV Tx1 | Macquarie Park 132_11kV Tx1 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6322. Works required to supply new large customer load (LLC) at Giffnock Ave, Macquarie Park. (CUSTOMER FUNDED) | North Ryde 66_11kV Tx3 | Macquarie Park 132_11kV Tx2 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | Macquarie Park 132_11kV Tx3 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | Macquarie Park 132_11kV Tx3 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2005098. Est 'Centre Court' Development - 12 DCs - 11MVA - Request guidance from AIM (Terry). Establishes the following 12 subs: S.35010 Lyonpark Epping No.1, S.35011, S.35012, S.35013, S.35014, S.35015, S.35016, S.35017, S.35018, |  | Macquarie Park 132_11kV Tx1 | 136.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2005098. Est 'Centre Court' Development - 12 DCs - 11MVA - Request guidance from AIM (Terry). Establishes the following 12 subs: S.35010 Lyonpark Epping No.1, S.35011, S.35012, S.35013, S.35014, S.35015, S.35016, S.35017, S.35018, |  | Macquarie Park 132_11kV Tx2 | 191.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2005342. Est S.35183 "Giffnock Coolinga No2" and S.35184 "Giffnock Coolinga No3" for Sonic Health Care (Douglass Hanly Moir Pathology) - Macquarie Park. |  | Macquarie Park 132_11kV Tx2 | 74.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 |  | Macquarie Park 132_11kV Tx3 | 0 | 0 | 69.3 | 43.2 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 | Macquarie Park 132_11kV Tx3 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 | Macquarie Park 132_11kV Tx3 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 | Meadowbank 132_11kV Tx1 | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2007075. Establishment of S.35081, S.35082, S.35083 Eden Park Waterloo No.3, 4, 5 |  | Macquarie Park 132_11kV Tx2 | 0 | 57.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2007188. Establishment of S.35579 Lane Cove Giffnock No. 1 and S.35580 Lane Cove Giffnock No. 2, 394 Lane Cove Road, Macquarie Park |  | Macquarie Park 132_11kV Tx2 | 0 | 0 | 39.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2007238. Establishment 6xKiosks - Riverside Corp Park No1 S.35681; Riverside Corp Park No2 S.35682; Riverside Corp Park No3 S.35683; Riverside Corp Park No4 S.35684; Riverside Corp Park No5 S.35685; Riverside Corp Park No6 S.3 |  | Macquarie Park 132_11kV Tx2 | 0 | 80.1 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2007395. Establishment of S.35744 Delhi Julius No. 4 and S.35745 Delhi Julius No. 5, 105 Delhi Road, North Ryde |  | Macquarie Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 28.8 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2007408. Establishment of multiple (4) kiosks - S.35752 Kittys Giffnock No. 2; S.35753 Kittys Giffnock No 3; S.35754 Kittys Giffnock No. 4; S.35755 Kittys Giffnock No. 5, 6 Giffnock Ave, Macquarie Park |  | Macquarie Park 132_11kV Tx2 | 0 | 56.7 | 6.3 | 9.9 | 0 | 28.8 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2007552. Establishment of chamber sub - S.35844 Talavera Christie No 4; 2 Technology Place, Macquarie Park |  | Macquarie Park 132_11kV Tx1 | 0 | 0 | 22.5 | 22.5 | 0 | 34.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2008171. Establishment of 2 x 1500 kVA Chamber Type Sub - S.36014 Macquarie Uni No 14, Macquarie Drive (Macquarie Uni) Macquarie Park |  | Macquarie Park 132_11kV Tx2 | 0 | 0 | 0 | 51.3 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2010129. Establishment of S.47527 Talavera Khartoum No 8, 54-60 Talavera Rd, Macquarie Park |  | Macquarie Park 132_11kV Tx2 | 0 | 0 | 0 | 26.1 | 0 | 0 | 4.5 | 13.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2010129. Establishment of S.47527 Talavera Khartoum No 8, 54-60 Talavera Rd, Macquarie Park |  | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 49.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010129. Establishment of S.47527 Talavera Khartoum No 8, 54-60 Talavera Rd, Macquarie Park | Macquarie Park 132_11kV Tx3 | Epping 66_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010142. Establish S.47942 Macquarie Uni Western. Previous request was 3 x kiosks S.47942, S.47943 and S.47944. |  | Macquarie Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 34.2 | 9 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2010404. Establishment of 2 x Kiosks - S.48540 Talavera Macquarie Shops No 1 and S.48541 Talavera Macquarie Shops No 2, 55-61 Talavera Road, Macquarie Park |  | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2010404. Establishment of 2 x Kiosks - S.48540 Talavera Macquarie Shops No 1 and S.48541 Talavera Macquarie Shops No 2, 55-61 Talavera Road, Macquarie Park |  | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010404. Establishment of 2 x Kiosks - S.48540 Talavera Macquarie Shops No 1 and S.48541 Talavera Macquarie Shops No 2, 55-61 Talavera Road, Macquarie Park | Macquarie Park 132_11kV Tx3 | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010665. Establishment of 2 x Kiosks - S.49138 21 Talavera Rd No 1; and S.49139 21 Talavera Rd No 2; 21 Talavera Road, Macqarie Park |  | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 47.7 | 0 | 78.65 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010678. Establishment of S.49162 Waterloo Herring and S.49163 Macquarie Eastern, Macquarie University NSW 2109. Decommission and recover S.3673 Macquarie University No.3 - LLC |  | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.25 | 131.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | HVCON_ID: 2010678. Establishment of S.49162 Waterloo Herring and S.49163 Macquarie Eastern, Macquarie University NSW 2109. Decommission and recover S.3673 Macquarie University No.3 - LLC | Epping 66_11kV Tx3 | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | ROG Justification | [24 empty] | HVCON_ID: 2011517. Next DC Data Centre - 4 Eden Park Drive, Macquarie Park |  | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 3.134% |  | 7 year ROG ok | [24 empty] | HVCON_ID: 2011517. Next DC Data Centre - 4 Eden Park Drive, Macquarie Park |  | Macquarie Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.5 | 49.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 year ROG ok
[35 empty] | HVCON_ID: 2011517. Next DC Data Centre - 4 Eden Park Drive, Macquarie Park |  | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.5 | 49.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011517. Next DC Data Centre - 4 Eden Park Drive, Macquarie Park | Macquarie Park 132_11kV Tx3 | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | HVCON_ID: 2012230. Establishment of S.62281 Giffnock Lyon Park No.3, 22 Giffnock Avenue, Macquarie Park |  | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.0048 | 1.0097 | 1.0129 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 0.4825% | 0.4825% | 0.3216% | 0.1608% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | HVCON_ID: 2012553. Establishment of 2 x Kiosks; S.63297 Talavera Lane Cove No 1, and S.63298 Talavera Lane Cove No 2, 5 Talavera Rd, Macquarie Park |  | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012553. Establishment of 2 x Kiosks; S.63297 Talavera Lane Cove No 1, and S.63298 Talavera Lane Cove No 2, 5 Talavera Rd, Macquarie Park |  | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2: Substation Load Detail | HVCON_ID: 2013276. Temporary Connection for NextDC Standby feeder, 4 Eden Park Drive Macquarie Park. | Macquarie Park 132_11kV Tx1 | Macquarie Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013276. Temporary Connection for NextDC Standby feeder, 4 Eden Park Drive Macquarie Park. | Macquarie Park 132_11kV Tx3 | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | HVCON_ID: 2013331. 15MVA Load Transfer from Macquarie Park Zone to Top Ryde Zone due to LLC NextDC, 4 Eden Park Dr Macquarie Park | Macquarie Park 132_11kV Tx1 | Top Ryde 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Macquarie Park 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 3285 | 3617 | 4338.944 | 4658.145 | 4158.728 | 4134.334 | 4101.664 | 4098.287 | 4122.353 | 4163.3 | 4199.464 | 4236.376 | 4262.29 | 4299.722 | 4336.39 | 4382.48 | 4433.197 | 4482.3 | 4528.441 | 4575.317 | 4622.936 | 4671.307 | 4720.44 | 4770.344 | 4821.029 | 4872.504 | 4924.78 | HVCON_ID: 2013331. 15MVA Load Transfer from Macquarie Park Zone to Top Ryde Zone due to LLC NextDC, 4 Eden Park Dr Macquarie Park | Macquarie Park 132_11kV Tx2 | Top Ryde 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 62.5877 |  | 82.668 | 88.7496 | 79.2344 | 78.7696 | 78.1472 | 78.0828 | 78.5414 | 79.3215 | 80.0105 | 80.7138 | 81.2075 | 81.9207 | 82.6193 | 83.4975 | 84.4637 | 85.3993 | 86.2784 | 87.1715 | 88.0788 | 89.0003 | 89.9365 | 90.8873 | 91.8529 | 92.8337 | 93.8297 | HVCON_ID: 2013331. 15MVA Load Transfer from Macquarie Park Zone to Top Ryde Zone due to LLC NextDC, 4 Eden Park Dr Macquarie Park | Macquarie Park 132_11kV Tx2 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 60.3483 | 66.4475 | 79.7102 | 85.5742 | 76.4121 | 75.9639 | 75.3637 | 75.3016 | 75.7438 | 76.4962 | 77.1606 | 77.8389 | 78.315 | 79.0028 | 79.6765 | 80.5234 | 81.4552 | 82.3574 | 83.2052 | 84.0665 | 84.9415 | 85.8302 | 86.733 | 87.6499 | 88.5812 | 89.527 | 90.4875 | HVCON_ID: 2013331. 15MVA Load Transfer from Macquarie Park Zone to Top Ryde Zone due to LLC NextDC, 4 Eden Park Dr Macquarie Park | Macquarie Park 132_11kV Tx3 | Top Ryde 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 16.5919 |  | 21.9152 | 23.5274 | 20.9589 | 20.836 | 20.6713 | 20.6543 | 20.7756 | 20.9819 | 21.1642 | 21.3502 | 21.4808 | 21.6695 | 21.8543 | 22.0865 | 22.3421 | 22.5896 | 22.8221 | 23.0584 | 23.2984 | 23.5421 | 23.7898 | 24.0413 | 24.2967 | 24.5561 | 24.8196 | HVCON_ID: 2014039. Establish two new kiosk substations (KL) S.64706 Waterloo Novartis No.1 and S.64707 Waterloo Novartis No.2, Lot 2, 54 Waterloo Rd, Macquarie Park |  | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HVCON_ID: 2014095. Establish New 3x1500kVA Chamber Sub S.64810 ‘Delhi Epping’, 27-31 Delhi road – North Ryde |  | Macquarie Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.96422 |  | 0.96422 | 0.96422 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | Econometric |  | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4599 | 12.8417 | 18.9729 | 18.5706 | 19.0101 | 19.0839 | 19.155 | 19.3965 | 19.6411 | 19.8887 | 20.1393 | 20.3931 | 20.65 | 20.9102 | 21.1735 | 21.4402 | 21.7101 | 21.9834 | 22.2601 | 22.5403 | 22.8239 | 23.1111 | 23.4018
0.96178 | Diversity Factor: 0.96 | Uncompensated |  | Reactive Power |  |  | MVAr | 16.5919 | 18.2688 | 21.9152 | 23.5274 | 20.9589 | 20.836 | 20.6713 | 20.6543 | 20.7756 | 20.9819 | 21.1642 | 21.3502 | 21.4808 | 21.6695 | 21.8543 | 22.0865 | 22.3421 | 22.5896 | 22.8221 | 23.0584 | 23.2984 | 23.5421 | 23.7898 | 24.0413 | 24.2967 | 24.5561 | 24.8196 | Econometric |  | Macquarie Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6437 | 13.2071 | 19.5127 | 19.099 | 19.551 | 19.627 | 19.7001 | 19.9485 | 20.2 | 20.4546 | 20.7124 | 20.9734 | 21.2376 | 21.5052 | 21.776 | 22.0502 | 22.3279 | 22.609 | 22.8935 | 23.1817 | 23.4734 | 23.7687 | 24.0677
|  |  |  | PF |  |  |  | 0.96422 |  | 0.96422 | 0.96422 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | 0.96438 | Econometric |  | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6795 | 9.3024 | 13.7437 | 13.4523 | 13.7707 | 13.8242 | 13.8757 | 14.0507 | 14.2278 | 14.4071 | 14.5887 | 14.7726 | 14.9587 | 15.1471 | 15.3379 | 15.531 | 15.7266 | 15.9246 | 16.125 | 16.328 | 16.5334 | 16.7414 | 16.952
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | Energy Efficiency |  | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3473 | -3.0961 | -8.9195 | -12.9089 | -19.6046 | -19.366 | -9.8161 | -3.7725 | -5.5743 | -5.6481 | -9.8208 | -5.8842 | -6.4127 | -3.2434 | -1.82 | -2.6662 | -4.0053 | -4.0053 | -4.0053 | -4.0053 | -4.0053 | -4.0053 | -4.0053 | -4.0053 | -4.0053
2: Transformer Load Detail | Energy Efficiency |  | Macquarie Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5564 | -3.1842 | -9.1733 | -13.2762 | -20.1625 | -19.9171 | -10.0954 | -3.8798 | -5.7329 | -5.8088 | -10.1002 | -6.0517 | -6.5951 | -3.3357 | -1.8718 | -2.742 | -4.1193 | -4.1193 | -4.1193 | -4.1193 | -4.1193 | -4.1193 | -4.1193 | -4.1193 | -4.1193
[35 empty] | Energy Efficiency |  | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3223 | -2.2428 | -6.4612 | -9.3511 | -14.2014 | -14.0285 | -7.1107 | -2.7328 | -4.038 | -4.0914 | -7.1141 | -4.2625 | -4.6453 | -2.3495 | -1.3184 | -1.9314 | -2.9014 | -2.9014 | -2.9014 | -2.9014 | -2.9014 | -2.9014 | -2.9014 | -2.9014 | -2.9014
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | Solar PV |  | Macquarie Park 132_11kV Tx1 | 0 | 0 | 0 | -0.62232 | -0.27779 | -0.042136 | -0.40192 | -0.27535 | -0.30885 | -0.34881 | -0.38274 | -0.40963 | -0.43154 | -0.45181 | -0.43691 | -0.44385 | -0.33961 | -0.40679 | -0.40679 | -0.40679 | -0.40679 | -0.40679 | -0.40679 | -0.40679 | -0.40679 | -0.40679 | -0.40679 | -0.40679 | -0.40679 | -0.40679 | -0.40679 | -0.40679
| 0 | Compensated |  | Load (LV side) |  |  | Amps | [27 empty] | Solar PV |  | Macquarie Park 132_11kV Tx2 | 0 | 0 | 0 | -0.64003 | -0.2857 | -0.043335 | -0.41335 | -0.28319 | -0.31764 | -0.35874 | -0.39363 | -0.42128 | -0.44382 | -0.46467 | -0.44934 | -0.45648 | -0.34928 | -0.41837 | -0.41837 | -0.41837 | -0.41837 | -0.41837 | -0.41837 | -0.41837 | -0.41837 | -0.41837 | -0.41837 | -0.41837 | -0.41837 | -0.41837 | -0.41837 | -0.41837
|  |  |  | Apparent Power |  |  | MVA | [27 empty] | Solar PV |  | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | -0.4508 | -0.20123 | -0.030523 | -0.29114 | -0.19946 | -0.22373 | -0.25268 | -0.27725 | -0.29673 | -0.3126 | -0.32729 | -0.31649 | -0.32152 | -0.24601 | -0.29468 | -0.29468 | -0.29468 | -0.29468 | -0.29468 | -0.29468 | -0.29468 | -0.29468 | -0.29468 | -0.29468 | -0.29468 | -0.29468 | -0.29468 | -0.29468 | -0.29468
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Meadowbank 132_11kV
| Meadowbank 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 3596 | 3947 | 4034 | 4235 | 3035 | 3480 | 3300 |  | 3654.675 | 3675.457 | 3699.042 | 3685.955 | 3706.58 | 3729.977 | 3783.189 | 3843.672 | 3897.038 | 3953.584 | 4004.495 | 4065.761 | 4127.536 | 4195.868 | 4268.232 | 4340.158 | 4411.464 | 4484.205 | 4558.402 | 4634.074 | 4711.241 | 4789.925 | 4870.146 | 4951.924 | 5035.282 |  |  | Total | -126 | 0 | 13.7 | -62.8411 | -267.0777 | -11.31 | 9.1504 | 236.2463 | 88.05 | 68.6857 | 9.6074 | 20.6252 | 23.3972 | 53.2118 | 60.4837 | 53.3653 | 56.5468 | 50.9108 | 61.2653 | 61.7757 | 68.3316 | 72.3645 | 71.926 | 71.3055 | 72.7412 | 74.1966 | 75.672 | 77.1677 | 78.6838 | 80.2206 | 81.7785 | 83.3577
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 5450 |  | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450 | 5450
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 8021 |  | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 | 8021 |  |  | Meadowbank 132_11kV Tx1 | -126 | 93 | 85.5 | -52.6321 | -127.5797 | -4.0031 | 10.2851 | 23.0981 | 18.7924 | 13.4566 | 2.9986 | 6.4374 | 7.3026 | 16.6081 | 18.8777 | 16.656 | 17.649 | 15.8899 | 19.1217 | 19.281 | 21.3272 | 22.5859 | 22.449 | 22.2553 | 22.7035 | 23.1577 | 23.6182 | 24.085 | 24.5582 | 25.0379 | 25.5241 | 26.017
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Meadowbank 132_11kV Tx2 | 0 | 116 | 43.2 | -6.081 | -149.8923 | -76.0041 | -0.67593 | 179.3211 | 64.0569 | 39.9708 | 3.9365 | 8.451 | 9.5868 | 21.8031 | 24.7827 | 21.866 | 23.1696 | 20.8603 | 25.1029 | 25.3121 | 27.9983 | 29.6507 | 29.4711 | 29.2168 | 29.8051 | 30.4014 | 31.006 | 31.6188 | 32.24 | 32.8697 | 33.5081 | 34.1551
| Transformer Loads | [35 empty] | Meadowbank 132_11kV Tx3 | 0 | -209 | -115 | -4.128 | 10.3943 | 68.6972 | -0.45884 | 33.8271 | 5.2007 | 15.2583 | 2.6723 | 5.7368 | 6.5078 | 14.8006 | 16.8233 | 14.8433 | 15.7283 | 14.1606 | 17.0407 | 17.1826 | 19.0061 | 20.1279 | 20.0059 | 19.8333 | 20.2326 | 20.6375 | 21.0478 | 21.4639 | 21.8856 | 22.313 | 22.7463 | 23.1856
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Meadowbank 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.60421 | -4.1033 | -4.838 | -7.0982 | -6.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.7932 | -5.3868 | -6.3514 | -9.3184 | -7.9313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Meadowbank 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.53845 | -3.6568 | -4.3115 | -6.3257 | -5.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6176. Change of Open Points Due to Forecasted Overload on Panels 36,40 and 41. | Meadowbank 132_11kV Tx2 | Meadowbank 132_11kV Tx3 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6176. Change of Open Points Due to Forecasted Overload on Panels 36,40 and 41. | Meadowbank 132_11kV Tx3 | Meadowbank 132_11kV Tx1 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6176. Change of Open Points Due to Forecasted Overload on Panels 36,40 and 41. | Meadowbank 132_11kV Tx3 | Meadowbank 132_11kV Tx2 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | Meadowbank 132_11kV Tx1 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | Meadowbank 132_11kV Tx2 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6416. Works required to relieve Remedial Panel 41 Feeder - Meadowbank. | Meadowbank 132_11kV Tx3 | Epping 66_11kV Tx1 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6531. North Concord Zone Development | Concord 33_11kV Tx4 | Meadowbank 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6697. Meadowbank West Zone Development | Meadowbank 132_11kV Tx2 | Meadowbank 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6697. Meadowbank West Zone Development | Meadowbank 132_11kV Tx2 | Meadowbank 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6735. Meadowbank North Zone Development | Meadowbank 132_11kV Tx3 | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6766. Hunters Hill to Top Ryde 11kV Load Transfer | Meadowbank 132_11kV Tx1 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006347. TBS for Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde (sub actually located on road reserve in Ope Street). Est S.35435 Pope Smith and recovery of S.972 Tucker St, S.4694 Tucker Pope, S.2112 Pope St & S.6416 Dev |  | Meadowbank 132_11kV Tx1 | -126 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 |  | Meadowbank 132_11kV Tx1 | 0 | 0 | 64.8 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 |  | Meadowbank 132_11kV Tx2 | 0 | 0 | 43.2 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 | Meadowbank 132_11kV Tx1 | Macquarie Park 132_11kV Tx3 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 | Meadowbank 132_11kV Tx1 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 | Meadowbank 132_11kV Tx2 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2010283. Establishment of S.47941 Falconer Parkes, Falconer Street, West Ryde | Meadowbank 132_11kV Tx1 | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2010529. Establishment of S.48211 Tramway Brush, 38-42 Tramway Street, West Ryde | Meadowbank 132_11kV Tx2 | Meadowbank 132_11kV Tx3 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011235. Establishment of S.47010 Anthony Betts, 2-12 Anthony Rd, West Ryde |  | Meadowbank 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 11.7 | 0 | 13.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012189. Stage 1: Establishment of S.50101 Dress Circle Main and S.62140 Road 5 Road 16; and Stage 2: Establishment of S.62141 Road 5 Victoria, Charles Street, Ryde. Decomission S.2576 Royal Ryde Homes |  | Meadowbank 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013079. Establishment of S.63481 Belmore Junction, 74-76 Belmore Street, Ryde - new 135 residential uni development - application 950amps |  | Meadowbank 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013267. Stage 1 : Decommission S.3387 and close links to supply existing lightly loaded LV overhead; and Stage 2: when development construction begins install new 1000kVA kiosk substation, 9 Angas Street, Meadowbank |  | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 13.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013329. Establishment S.64027 Hamilton Belmore, 41-46 Belmore Street, Ryde |  | Meadowbank 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 14.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013349. Establishment of S.64028 Rothesay Belmore No 1 and Decommission S.5400 Rothesay Belmore, 6-10 Nancarrow Road, Ryde |  | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013391. Establishment of S.64408 Church Riverside No 1 and S.64409 Church Riverside No 2, decommission and remove S.6287 Church Addis, 125-135 Church Street, and 21-27 Porter Street, Ryde |  | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013402. Establishment of S.64463 Nancarrow Hamilton No 2, 12-18 Nancarrow Road, Ryde |  | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 13.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2014010. Establish S.64687 Betts Chatham, Lot 13 Chatham Rd West Ryde |  | Meadowbank 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2014043. Establish New 1000kVA Kiosk Sub S.64730 ‘Constitution Belmore’, 2-6 Constitution Rd - Ryde |  | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2014044. Establish New 1000kVA Kiosk Sub S.64731 ‘Constitution Hamilton’, decommission S.5274 'Constitution Gale' and decommission S.4979 'Hamilton Nancarrow', 16-18 Constitution Rd - Ryde |  | Meadowbank 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | HVCON_ID: 2014044. Establish New 1000kVA Kiosk Sub S.64731 ‘Constitution Hamilton’, decommission S.5274 'Constitution Gale' and decommission S.4979 'Hamilton Nancarrow', 16-18 Constitution Rd - Ryde |  | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.15 | 14.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | ROG Justification | [24 empty] | Econometric |  | Meadowbank 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7752 | 22.6176 | 31.2159 | 27.0021 | 29.0059 | 28.1203 | 27.1995 | 27.6012 | 28.0084 | 28.4213 | 28.8398 | 29.2641 | 29.6943 | 30.1303 | 30.5724 | 31.0205 | 31.4748 | 31.9352 | 32.402 | 32.8752 | 33.3549 | 33.8412 | 34.3341
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 6.351% |  | 7 year ROG ok | [24 empty] | Econometric |  | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.4585 | 29.6924 | 40.9802 | 35.4483 | 38.0789 | 36.9163 | 35.7074 | 36.2348 | 36.7695 | 37.3115 | 37.8609 | 38.418 | 38.9826 | 39.5551 | 40.1354 | 40.7237 | 41.32 | 41.9246 | 42.5374 | 43.1586 | 43.7883 | 44.4267 | 45.0737 | 7 year ROG ok
[35 empty] | Econometric |  | Meadowbank 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4937 | 20.1561 | 27.8186 | 24.0635 | 25.8492 | 25.06 | 24.2394 | 24.5974 | 24.9603 | 25.3282 | 25.7012 | 26.0793 | 26.4627 | 26.8513 | 27.2452 | 27.6445 | 28.0494 | 28.4597 | 28.8757 | 29.2974 | 29.7249 | 30.1582 | 30.5975
[35 empty] | Energy Efficiency |  | Meadowbank 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8261 | -1.3144 | -7.0997 | -11.1703 | -17.2915 | -18.1767 | -10.8034 | -7.7008 | -8.9772 | -8.7538 | -10.683 | -7.8641 | -8.1234 | -6.5015 | -5.6729 | -6.2458 | -6.8815 | -6.8815 | -6.8815 | -6.8815 | -6.8815 | -6.8815 | -6.8815 | -6.8815 | -6.8815
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | Energy Efficiency |  | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.71 | -1.7255 | -9.3204 | -14.6643 | -22.7002 | -23.8624 | -14.1828 | -10.1096 | -11.7853 | -11.4919 | -14.0247 | -10.324 | -10.6644 | -8.5352 | -7.4474 | -8.1995 | -9.0341 | -9.0341 | -9.0341 | -9.0341 | -9.0341 | -9.0341 | -9.0341 | -9.0341 | -9.0341
0.9816 | 0.96354 | 0.95172 | 0.94588 | 0.94588 | 0.94588 | 0.94588 | 0.94588 | 0.94588 | 0.94588 | -1.84% | -1.84% | -1.227% | -0.613% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Energy Efficiency |  | Meadowbank 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5185 | -1.1713 | -6.327 | -9.9546 | -15.4097 | -16.1985 | -9.6277 | -6.8627 | -8.0002 | -7.8011 | -9.5204 | -7.0083 | -7.2393 | -5.7939 | -5.0555 | -5.5661 | -6.1326 | -6.1326 | -6.1326 | -6.1326 | -6.1326 | -6.1326 | -6.1326 | -6.1326 | -6.1326
[35 empty] | Solar PV |  | Meadowbank 132_11kV Tx1 | 0 | 0 | 0 | -4.6321 | -0.67968 | -0.0031125 | -0.51488 | -0.97167 | -1.0899 | -1.2309 | -1.3506 | -1.4455 | -1.5228 | -1.5944 | -1.5418 | -1.5663 | -1.1984 | -1.4355 | -1.4355 | -1.4355 | -1.4355 | -1.4355 | -1.4355 | -1.4355 | -1.4355 | -1.4355 | -1.4355 | -1.4355 | -1.4355 | -1.4355 | -1.4355 | -1.4355
2: Substation Load Detail | Solar PV |  | Meadowbank 132_11kV Tx2 | 0 | 0 | 0 | -6.081 | -0.89228 | -0.0040861 | -0.67593 | -1.2756 | -1.4308 | -1.6159 | -1.7731 | -1.8976 | -1.9992 | -2.0931 | -2.024 | -2.0562 | -1.5733 | -1.8845 | -1.8845 | -1.8845 | -1.8845 | -1.8845 | -1.8845 | -1.8845 | -1.8845 | -1.8845 | -1.8845 | -1.8845 | -1.8845 | -1.8845 | -1.8845 | -1.8845
[35 empty] | Solar PV |  | Meadowbank 132_11kV Tx3 | 0 | 0 | 0 | -4.128 | -0.60571 | -0.0027738 | -0.45884 | -0.86593 | -0.97127 | -1.0969 | -1.2036 | -1.2882 | -1.3571 | -1.4208 | -1.374 | -1.3958 | -1.068 | -1.2793 | -1.2793 | -1.2793 | -1.2793 | -1.2793 | -1.2793 | -1.2793 | -1.2793 | -1.2793 | -1.2793 | -1.2793 | -1.2793 | -1.2793 | -1.2793 | -1.2793
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Meadowbank 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 3300 | 3483 | 3654.675 | 3675.457 | 3699.042 | 3685.955 | 3706.58 | 3729.977 | 3783.189 | 3843.672 | 3897.038 | 3953.584 | 4004.495 | 4065.761 | 4127.536 | 4195.868 | 4268.232 | 4340.158 | 4411.464 | 4484.205 | 4558.402 | 4634.074 | 4711.241 | 4789.925 | 4870.146 | 4951.924 | 5035.282
|  |  |  | Apparent Power |  |  | MVA | 62.8734 |  | 69.6309 | 70.0269 | 70.4762 | 70.2269 | 70.6198 | 71.0656 | 72.0794 | 73.2318 | 74.2485 | 75.3259 | 76.2959 | 77.4631 | 78.6401 | 79.942 | 81.3208 | 82.6911 | 84.0497 | 85.4356 | 86.8492 | 88.291 | 89.7612 | 91.2603 | 92.7887 | 94.3468 | 95.935
|  |  |  | Real Power |  |  | MW | 60.3212 | 63.6663 | 66.7339 | 67.1134 | 67.5441 | 67.3051 | 67.6817 | 68.109 | 69.0806 | 70.185 | 71.1595 | 72.192 | 73.1216 | 74.2403 | 75.3683 | 76.6161 | 77.9374 | 79.2508 | 80.5528 | 81.8811 | 83.2359 | 84.6177 | 86.0267 | 87.4635 | 88.9283 | 90.4216 | 91.9437
|  |  |  | Reactive Power |  |  | MVAr | 17.7319 |  | 19.8757 | 19.9887 | 20.117 | 20.0458 | 20.158 | 20.2852 | 20.5746 | 20.9035 | 21.1938 | 21.5013 | 21.7782 | 22.1114 | 22.4473 | 22.819 | 23.2125 | 23.6037 | 23.9915 | 24.387 | 24.7906 | 25.2021 | 25.6218 | 26.0497 | 26.486 | 26.9307 | 27.384
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.95941 |  | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839
0.9117 | Diversity Factor: 0.91 | Uncompensated |  | Reactive Power |  |  | MVAr | 17.7319 | 18.7152 | 19.8757 | 19.9887 | 20.117 | 20.0458 | 20.158 | 20.2852 | 20.5746 | 20.9035 | 21.1938 | 21.5013 | 21.7782 | 22.1114 | 22.4473 | 22.819 | 23.2125 | 23.6037 | 23.9915 | 24.387 | 24.7906 | 25.2021 | 25.6218 | 26.0497 | 26.486 | 26.9307 | 27.384
|  |  |  | PF |  |  |  | 0.95941 |  | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839 | 0.95839
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## North Ryde 66_11kV
| North Ryde 66_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone decommissioned |  | 2012-04-30
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 1778 | 1700 | 1698 | 1672 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | 0 | -6.3 | 85.5 | 15.0484 | -2005.9699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | North Ryde 66_11kV Tx1 | 0 | 50 | 63 | -0.57578 | -1001.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | North Ryde 66_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | North Ryde 66_11kV Tx3 | 0 | -56.3 | 22.5 | 15.6242 | -1004.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | DNP_ID: 6322. Works required to supply new large customer load (LLC) at Giffnock Ave, Macquarie Park. (CUSTOMER FUNDED) | North Ryde 66_11kV Tx3 | Macquarie Park 132_11kV Tx2 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | North Ryde 66_11kV Tx1 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | North Ryde 66_11kV Tx1 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | North Ryde 66_11kV Tx3 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | North Ryde 66_11kV Tx3 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6372. Change of Open Points for relief of Remedial Feeder North Ryde Zone Panel Feeder 14 | North Ryde 66_11kV Tx3 | North Ryde 66_11kV Tx1 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006257. Establishment of S.35393 Rivett Julius No.1 and S.35394 Rivett Julius No.2. 1 Rivett Road North Ryde. |  | North Ryde 66_11kV Tx1 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2007408. Establishment of multiple (4) kiosks - S.35752 Kittys Giffnock No. 2; S.35753 Kittys Giffnock No 3; S.35754 Kittys Giffnock No. 4; S.35755 Kittys Giffnock No. 5, 6 Giffnock Ave, Macquarie Park |  | North Ryde 66_11kV Tx3 | 0 | 56.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2008087. Establishment of S.35919 Epping Lane Cove No 3, 67 Epping Rd, Macquarie Park |  | North Ryde 66_11kV Tx3 | 0 | 0 | 22.5 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Solar PV |  | North Ryde 66_11kV Tx1 | 0 | 0 | 0 | -0.57578 | -8.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | North Ryde 66_11kV Tx3 | 0 | 0 | 0 | -0.57578 | -8.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | North Ryde 66_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.83448 | Diversity Factor: 0.83 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Top Ryde 132_11kV
| Top Ryde 132_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone commissioned |  | 2011-09-30
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  |  | 2105 | 2905 | 2432 |  | 2582.996 | 2595.882 | 3455.96 | 3444.31 | 3450.995 | 3458.977 | 3487.046 | 3522.529 | 3553.813 | 3586.809 | 3614.725 | 3650.157 | 3685.66 | 3726.336 | 3769.944 | 3812.972 | 3855.057 | 3897.979 | 3941.751 | 3986.384 | 4031.888 | 4078.278 | 4125.563 | 4173.757 | 4222.872 |  |  | Total | 0 | 0 | 0 | 0 | 2867.4 | 651.5452 | 48.5852 | 72.1764 | 43.8895 | 881.1396 | 2.1768 | 6.685 | 7.9824 | 28.0683 | 35.4833 | 31.284 | 32.9964 | 27.916 | 35.432 | 35.503 | 40.6752 | 43.6086 | 43.028 | 42.0848 | 42.9225 | 43.7717 | 44.6324 | 45.5048 | 46.3891 | 47.2854 | 48.1939 | 49.1147
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 3215 |  | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215 | 3215
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 5946 |  | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 | 5946 |  |  | Top Ryde 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 1329.4 | 287.7301 | 22.0462 | 41.3793 | 8.2389 | 138.5316 | 1.0797 | 3.3159 | 3.9594 | 13.9225 | 17.6005 | 15.5176 | 16.367 | 13.847 | 17.5751 | 17.6103 | 20.1758 | 21.6308 | 21.3428 | 20.875 | 21.2905 | 21.7117 | 22.1387 | 22.5714 | 23.01 | 23.4546 | 23.9052 | 24.362
| Transformer Loads | [35 empty] | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 1538 | 363.8151 | 26.5389 | 30.7971 | 35.6505 | -1.492 | 1.097 | 3.3691 | 4.0229 | 14.1458 | 17.8828 | 15.7664 | 16.6295 | 14.0691 | 17.857 | 17.8927 | 20.4994 | 21.9778 | 21.6851 | 21.2098 | 21.632 | 22.06 | 22.4937 | 22.9334 | 23.3791 | 23.8308 | 24.2887 | 24.7527
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6676 | -2.9345 | -5.7354 | -4.6606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7104 | -2.9816 | -5.8274 | -4.7353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | Macquarie Park 132_11kV Tx3 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | Macquarie Park 132_11kV Tx3 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | Meadowbank 132_11kV Tx1 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | Meadowbank 132_11kV Tx2 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | North Ryde 66_11kV Tx1 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | North Ryde 66_11kV Tx1 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | North Ryde 66_11kV Tx3 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6364. Top Ryde Zone Development - Relieving North Ryde of 43MVA and providing a permanent 17MVA supply to Top Ryde Shopping Centre. | North Ryde 66_11kV Tx3 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6766. Hunters Hill to Top Ryde 11kV Load Transfer | Hunters Hill 66_11kV Tx1 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6766. Hunters Hill to Top Ryde 11kV Load Transfer | Hunters Hill 66_11kV Tx1 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6766. Hunters Hill to Top Ryde 11kV Load Transfer | Hunters Hill 66_11kV Tx3 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6766. Hunters Hill to Top Ryde 11kV Load Transfer | Meadowbank 132_11kV Tx1 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6766. Hunters Hill to Top Ryde 11kV Load Transfer | Top Ryde 132_11kV Tx3 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7086. Re-conductor OH at PA 28 Lindfield Zone | Top Ryde 132_11kV Tx3 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 |  | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 23.4 | 72.9 | 22.5 | 27.5 | 13.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 |  | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 80.1 | 27 | 55 | 41.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 | Macquarie Park 132_11kV Tx3 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 | Macquarie Park 132_11kV Tx3 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 | Meadowbank 132_11kV Tx1 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2006348. Top Ryde Shopping Centre, 115-121 Blaxland Rd, Top Ryde - 6 new substations. Temp supply to Top Ryde S.35427 Blaxland Devlin, S.35431 Pope Tucker from new group. (To be followed up with S.35428, S.35429, S.35430, & S.3543 | Meadowbank 132_11kV Tx2 | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012457. North Ryde Station Precinct - Group Development LLC Projct, North Ryde - Wicks Rd, Epping Rd, Delhi Rd |  | Top Ryde 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013331. 15MVA Load Transfer from Macquarie Park Zone to Top Ryde Zone due to LLC NextDC, 4 Eden Park Dr Macquarie Park | Macquarie Park 132_11kV Tx1 | Top Ryde 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013331. 15MVA Load Transfer from Macquarie Park Zone to Top Ryde Zone due to LLC NextDC, 4 Eden Park Dr Macquarie Park | Macquarie Park 132_11kV Tx2 | Top Ryde 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013331. 15MVA Load Transfer from Macquarie Park Zone to Top Ryde Zone due to LLC NextDC, 4 Eden Park Dr Macquarie Park | Macquarie Park 132_11kV Tx2 | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013331. 15MVA Load Transfer from Macquarie Park Zone to Top Ryde Zone due to LLC NextDC, 4 Eden Park Dr Macquarie Park | Macquarie Park 132_11kV Tx3 | Top Ryde 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6793 | 20.4982 | 28.4984 | 25.195 | 26.6746 | 26.1577 | 25.6158 | 25.9886 | 26.3666 | 26.7497 | 27.138 | 27.5316 | 27.9306 | 28.3351 | 28.745 | 29.1606 | 29.5818 | 30.0087 | 30.4414 | 30.8801 | 31.3247 | 31.7753 | 32.232
| 0 | [33 empty] | Econometric |  | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8505 | 20.8269 | 28.9554 | 25.5991 | 27.1024 | 26.5773 | 26.0266 | 26.4055 | 26.7894 | 27.1787 | 27.5732 | 27.9732 | 28.3786 | 28.7895 | 29.2061 | 29.6283 | 30.0562 | 30.49 | 30.9297 | 31.3753 | 31.8271 | 32.2849 | 32.749
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.2835 | -1.9044 | -8.1526 | -12.5193 | -19.2764 | -19.9235 | -11.3783 | -7.2288 | -8.7487 | -8.5891 | -11.2827 | -7.9377 | -8.2908 | -6.1189 | -5.0629 | -5.7554 | -6.6332 | -6.6332 | -6.6332 | -6.6332 | -6.6332 | -6.6332 | -6.6332 | -6.6332 | -6.6332
[35 empty] | Energy Efficiency |  | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3522 | -1.935 | -8.2833 | -12.7201 | -19.5855 | -20.243 | -11.5608 | -7.3447 | -8.889 | -8.7268 | -11.4637 | -8.065 | -8.4238 | -6.2171 | -5.1441 | -5.8477 | -6.7395 | -6.7395 | -6.7395 | -6.7395 | -6.7395 | -6.7395 | -6.7395 | -6.7395 | -6.7395
[35 empty] | Solar PV |  | Top Ryde 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Top Ryde 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | -7.1699 | -0.45378 | -0.83723 | -0.93908 | -1.0606 | -1.1637 | -1.2455 | -1.3121 | -1.3738 | -1.3284 | -1.3496 | -1.0326 | -1.2369 | -1.2369 | -1.2369 | -1.2369 | -1.2369 | -1.2369 | -1.2369 | -1.2369 | -1.2369 | -1.2369 | -1.2369 | -1.2369 | -1.2369 | -1.2369 | -1.2369
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Solar PV |  | Top Ryde 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | -7.2849 | -0.46106 | -0.85066 | -0.95414 | -1.0776 | -1.1824 | -1.2655 | -1.3332 | -1.3958 | -1.3498 | -1.3712 | -1.0492 | -1.2567 | -1.2567 | -1.2567 | -1.2567 | -1.2567 | -1.2567 | -1.2567 | -1.2567 | -1.2567 | -1.2567 | -1.2567 | -1.2567 | -1.2567 | -1.2567 | -1.2567
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 4.495% |  | Weighted ROG calc | [59 empty] | Weighted ROG calc
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.988 | 0.97614 | 0.96833 | 0.96446 | 0.96446 | 0.96446 | 0.96446 | 0.96446 | 0.96446 | 0.96446 | -1.2% | -1.2% | -0.8% | -0.4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Top Ryde 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 2432 | 2541.3235 | 2582.996 | 2595.882 | 3455.96 | 3444.31 | 3450.995 | 3458.977 | 3487.046 | 3522.529 | 3553.813 | 3586.809 | 3614.725 | 3650.157 | 3685.66 | 3726.336 | 3769.944 | 3812.972 | 3855.057 | 3897.979 | 3941.751 | 3986.384 | 4031.888 | 4078.278 | 4125.563 | 4173.757 | 4222.872
|  |  |  | Apparent Power |  |  | MVA | 46.3358 |  | 49.2127 | 49.4582 | 65.8449 | 65.6229 | 65.7503 | 65.9024 | 66.4372 | 67.1132 | 67.7092 | 68.3379 | 68.8698 | 69.5448 | 70.2213 | 70.9962 | 71.8271 | 72.6469 | 73.4487 | 74.2665 | 75.1004 | 75.9508 | 76.8178 | 77.7016 | 78.6025 | 79.5208 | 80.4565
|  |  |  | Real Power |  |  | MW | 45.0448 | 47.0697 | 47.8415 | 48.0802 | 63.9057 | 63.6903 | 63.8139 | 63.9615 | 64.4805 | 65.1367 | 65.7152 | 66.3253 | 66.8415 | 67.4967 | 68.1532 | 68.9054 | 69.7117 | 70.5074 | 71.2856 | 72.0793 | 72.8887 | 73.714 | 74.5555 | 75.4133 | 76.2877 | 77.1788 | 78.087
|  |  |  | Reactive Power |  |  | MVAr | 10.8615 |  | 11.5358 | 11.5934 | 15.8621 | 15.8087 | 15.8393 | 15.876 | 16.0048 | 16.1677 | 16.3113 | 16.4627 | 16.5908 | 16.7535 | 16.9164 | 17.1031 | 17.3032 | 17.5007 | 17.6939 | 17.8909 | 18.0918 | 18.2967 | 18.5055 | 18.7184 | 18.9355 | 19.1567 | 19.3821
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.97214 |  | 0.97214 | 0.97214 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055
0.99101 | Diversity Factor: 0.99 | Uncompensated |  | Reactive Power |  |  | MVAr | 10.8615 | 11.3497 | 11.5358 | 11.5934 | 15.8621 | 15.8087 | 15.8393 | 15.876 | 16.0048 | 16.1677 | 16.3113 | 16.4627 | 16.5908 | 16.7535 | 16.9164 | 17.1031 | 17.3032 | 17.5007 | 17.6939 | 17.8909 | 18.0918 | 18.2967 | 18.5055 | 18.7184 | 18.9355 | 19.1567 | 19.3821
|  |  |  | PF |  |  |  | 0.97214 |  | 0.97214 | 0.97214 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055 | 0.97055
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF