## Inclusions and Exclusions
Sydney Forecast Inclusions and Exclusions
Date Printed |  | 08JUL14:11:21:24
| Description | Value
Season |  | Summer | Summer
Either Summer or Winter
Year |  | 2015 | 2015
Year that the forecast starts
POE |  | 50% | 0.5
10%, 50%, 90%
Spots and Transfers |  | Y | Y
Are Spots and Transfers Included?
BBDM Spots |  | Y | Y
Is BBDM included?
Spots Coefficient |  | 55% | 0.55
Scaling factor applied to spot loads in the future
Aligned ROGs |  | Capped | Capped
Have ROGs been aligned to econometric forecast?
Committed Projects |  | Y | Y
Are Committed Projects Included?
Major Customers Scaling Factor |  | 100% | 1
Scaling factor applied to major customer connections in the future
Future Transfers |  | Y | Y
Are future transfers included?
Future Spots |  | 4 | 4
Future spots are cleared from the following forecast year

## Argenton 132_11kV
| Argenton 132_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone commissioned |  | 2009-05-04
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV MVA) | [20 empty] | Spots & Transfers Summary | (11kV MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  | 16.8 | 34.123 | 33.554 | 35.836 | 31.249 |  | 35.6714 | 34.7059 | 29.1963 | 28.6829 | 28.4265 | 28.3562 | 28.5175 | 28.7628 | 28.9533 | 29.213 | 29.3857 | 29.6468 | 29.9094 | 30.232 | 30.5892 | 30.9401 | 31.2809 | 31.6321 | 31.9937 | 32.3659 | 32.7488 | 33.1427 | 33.5475 | 33.9636 | 34.391 |  |  | Total | 0 | 0 | 17.0139 | 18.7793 | 5.0978 | 0.59935 | -0.05786 | 1.2983 | -0.21043 | -5.0198 | -0.30739 | -0.25642 | -0.070343 | 0.16138 | 0.2453 | 0.19048 | 0.25969 | 0.17266 | 0.26111 | 0.26259 | 0.32263 | 0.35716 | 0.35091 | 0.34085 | 0.35116 | 0.36161 | 0.37221 | 0.38295 | 0.39383 | 0.40486 | 0.41604 | 0.42738
| Firm Rating | 0 | 0 | 60 | 60 | 60 | 60.8 | 60.8 |  | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8
| Total Capacity | 0 | 0 | 100 | 100 | 100 | 121.4 | 121.4 |  | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 |  |  | Argenton 132_11kV Tx4 | 0 | 0 | 9.0448 | 9.9832 | 2.71 | 0.31862 | -0.030759 | -0.30891 | -0.11186 | -4.3649 | -0.16341 | -0.13631 | -0.037395 | 0.085789 | 0.1304 | 0.10126 | 0.13805 | 0.091788 | 0.13881 | 0.1396 | 0.17151 | 0.18987 | 0.18654 | 0.1812 | 0.18668 | 0.19224 | 0.19787 | 0.20358 | 0.20936 | 0.21523 | 0.22117 | 0.2272
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Argenton 132_11kV Tx5 | 0 | 0 | 7.9692 | 8.7961 | 2.3878 | 0.28073 | -0.027101 | 1.6072 | -0.098562 | -0.6549 | -0.14398 | -0.1201 | -0.032948 | 0.075587 | 0.11489 | 0.089217 | 0.12164 | 0.080873 | 0.1223 | 0.123 | 0.15112 | 0.16729 | 0.16436 | 0.15965 | 0.16448 | 0.16938 | 0.17434 | 0.17937 | 0.18447 | 0.18963 | 0.19487 | 0.20018
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.12492 | -0.0045071 | -0.029296 | -0.10629 | -0.058592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.11006 | -0.0039711 | -0.025812 | -0.093654 | -0.051625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2288. To Edgeworth SAO Nov 11 | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0.13167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2288. To Edgeworth SAO Nov 11 | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0.11601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2288. To Edgeworth SAO Nov 11 | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0.13167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2288. To Edgeworth SAO Nov 11 | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0.11601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 0.53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0.46703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 0.53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0.46703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx4 | 0 | 0 | 0.53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx5 | 0 | 0 | 0.46703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 2.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 2.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 2.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 2.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 2.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 2.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0.95546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0.84184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0.95546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0.84184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0.95546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0.84184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2299. To Argenton (-9.7) | Cardiff 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 2.5574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2299. To Argenton (-9.7) | Cardiff 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 2.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2299. To Argenton (-9.7) | Cardiff 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 2.5574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2299. To Argenton (-9.7) | Cardiff 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 2.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2301. To Argenton (-9.7) | Cardiff 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2301. To Argenton (-9.7) | Cardiff 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2310. To Argenton (-8.4) | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 1.1698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2310. To Argenton (-8.4) | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 1.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2310. To Argenton (-8.4) | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 1.1698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | DNP_ID: 2310. To Argenton (-8.4) | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 1.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | ROG Justification | [24 empty] | DNP_ID: 2311. To Argenton (-8.4) | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 1.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 12.38% |  | weighted ROG calc | [24 empty] | DNP_ID: 2311. To Argenton (-8.4) | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 1.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | weighted ROG calc
[35 empty] | DNP_ID: 2311. To Argenton (-8.4) | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 1.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2311. To Argenton (-8.4) | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 1.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | DNP_ID: 2313. From Argenton to Edgeworth (SAO Nov 11) | Argenton 132_11kV Tx4 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0.13167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.97884 | 0.95813 | 0.94461 | 0.93795 | 0.93795 | 0.93795 | 0.93795 | 0.93795 | 0.93795 | 0.93795 | -2.116% | -2.116% | -1.411% | -0.705% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | DNP_ID: 2313. From Argenton to Edgeworth (SAO Nov 11) | Argenton 132_11kV Tx4 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0.13167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2313. From Argenton to Edgeworth (SAO Nov 11) | Argenton 132_11kV Tx5 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0.11601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2: Substation Load Detail | DNP_ID: 2313. From Argenton to Edgeworth (SAO Nov 11) | Argenton 132_11kV Tx5 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0.11601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6909. Cardiff Zone Substation - New 11kV Feeder to Warners Bay | Argenton 132_11kV Tx5 | Cardiff 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | DNP_ID: 6933. Toronto 11kV New Feeder Connections | Argenton 132_11kV Tx4 | Toronto West 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Argenton 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 |  | 1872.261 | 1821.586 | 1532.409 | 1505.463 | 1492.004 | 1488.312 | 1496.782 | 1509.657 | 1519.654 | 1533.285 | 1542.347 | 1556.052 | 1569.834 | 1586.768 | 1605.514 | 1623.932 | 1641.822 | 1660.253 | 1679.233 | 1698.769 | 1718.869 | 1739.539 | 1760.789 | 1782.626 | 1805.057 | DNP_ID: 6933. Toronto 11kV New Feeder Connections | Argenton 132_11kV Tx4 | Toronto West 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 31.249 | 35.1189 | 35.6714 | 34.7059 | 29.1963 | 28.6829 | 28.4265 | 28.3562 | 28.5175 | 28.7628 | 28.9533 | 29.213 | 29.3857 | 29.6468 | 29.9094 | 30.232 | 30.5892 | 30.9401 | 31.2809 | 31.6321 | 31.9937 | 32.3659 | 32.7488 | 33.1427 | 33.5475 | 33.9636 | 34.391 | DNP_ID: 6933. Toronto 11kV New Feeder Connections | Argenton 132_11kV Tx5 | Toronto West 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 29.367 | 33.0038 | 33.5638 | 32.6554 | 27.4713 | 26.9883 | 26.747 | 26.6808 | 26.8327 | 27.0635 | 27.2427 | 27.487 | 27.6495 | 27.8952 | 28.1423 | 28.4458 | 28.7819 | 29.1121 | 29.4328 | 29.7632 | 30.1034 | 30.4536 | 30.814 | 31.1845 | 31.5655 | 31.9569 | 32.3591 | DNP_ID: 7094. Edgeworth - New 11kV feeder and upgrade works | Argenton 132_11kV Tx4 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 12.0796 | 11.7526 | 9.8869 | 9.713 | 9.6262 | 9.6024 | 9.657 | 9.7401 | 9.8046 | 9.8926 | 9.951 | 10.0394 | 10.1284 | 10.2376 | 10.3586 | 10.4774 | 10.5928 | 10.7117 | 10.8342 | 10.9602 | 11.0899 | 11.2233 | 11.3604 | 11.5013 | 11.646 | DNP_ID: 7094. Edgeworth - New 11kV feeder and upgrade works | Argenton 132_11kV Tx4 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HVCON_ID: 2000153. Munibung Industrial Development (ex Pasminco) |  | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0.47401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.93977 |  | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | HVCON_ID: 2000153. Munibung Industrial Development (ex Pasminco) |  | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0.41765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.94691 | Diversity Factor: 0.95 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 12.0035 | 12.0796 | 11.7526 | 9.8869 | 9.713 | 9.6262 | 9.6024 | 9.657 | 9.7401 | 9.8046 | 9.8926 | 9.951 | 10.0394 | 10.1284 | 10.2376 | 10.3586 | 10.4774 | 10.5928 | 10.7117 | 10.8342 | 10.9602 | 11.0899 | 11.2233 | 11.3604 | 11.5013 | 11.646 | Econometric |  | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11106 | 0.20585 | 0.27843 | 0.3337 | 0.35476 | 0.34425 | 0.33605 | 0.34221 | 0.34719 | 0.35224 | 0.35737 | 0.36256 | 0.36782 | 0.37316 | 0.37856 | 0.38404 | 0.3896 | 0.39523 | 0.40094 | 0.40673 | 0.41259 | 0.41853 | 0.42456
|  |  |  | PF |  |  |  | 0.93977 |  | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | 0.94092 | Econometric |  | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097849 | 0.18137 | 0.24532 | 0.29402 | 0.31258 | 0.30331 | 0.29609 | 0.30151 | 0.30591 | 0.31036 | 0.31487 | 0.31944 | 0.32408 | 0.32878 | 0.33355 | 0.33838 | 0.34327 | 0.34823 | 0.35326 | 0.35836 | 0.36353 | 0.36876 | 0.37407
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | Energy Efficiency |  | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.051771 | -0.023163 | -0.10286 | -0.15863 | -0.24448 | -0.25345 | -0.14581 | -0.094741 | -0.1138 | -0.11157 | -0.14451 | -0.10254 | -0.10688 | -0.080153 | -0.067058 | -0.075719 | -0.08647 | -0.08647 | -0.08647 | -0.08647 | -0.08647 | -0.08647 | -0.08647 | -0.08647 | -0.08647
| Transformer Load Detail | [33 empty] | Energy Efficiency |  | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.045615 | -0.020408 | -0.09063 | -0.13977 | -0.21541 | -0.22331 | -0.12847 | -0.083475 | -0.10027 | -0.098305 | -0.12733 | -0.09035 | -0.094168 | -0.070621 | -0.059083 | -0.066714 | -0.076187 | -0.076187 | -0.076187 | -0.076187 | -0.076187 | -0.076187 | -0.076187 | -0.076187 | -0.076187
[35 empty] | Solar PV |  | Argenton 132_11kV Tx4 | 0 | 0 | 0 | -0.13512 | -0.15632 | -0.15539 | -0.030759 | -0.075063 | -0.084194 | -0.095088 | -0.10434 | -0.11167 | -0.11764 | -0.12317 | -0.1191 | -0.121 | -0.09258 | -0.11089 | -0.11089 | -0.11089 | -0.11089 | -0.11089 | -0.11089 | -0.11089 | -0.11089 | -0.11089 | -0.11089 | -0.11089 | -0.11089 | -0.11089 | -0.11089 | -0.11089
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | Solar PV |  | Argenton 132_11kV Tx5 | 0 | 0 | 0 | -0.11906 | -0.13774 | -0.13692 | -0.027101 | -0.066136 | -0.074182 | -0.083781 | -0.091929 | -0.098387 | -0.10365 | -0.10852 | -0.10494 | -0.10661 | -0.081571 | -0.097706 | -0.097706 | -0.097706 | -0.097706 | -0.097706 | -0.097706 | -0.097706 | -0.097706 | -0.097706 | -0.097706 | -0.097706 | -0.097706 | -0.097706 | -0.097706 | -0.097706
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Boolaroo 33_11kV
| Boolaroo 33_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone decommissioned |  | 2011-06-28
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV MVA) | [20 empty] | Spots & Transfers Summary | (11kV MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 22.4 | 26.828 | 19.5 | 5.189 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | 0.66874 | 1.749 | -2.9913 | -14.4609 | -5.3919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 25.4 | 25.4 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 28.6 | 28.6 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Boolaroo 33_11kV Tx1 | 0.22291 | 0.58301 | -0.99708 | -4.8203 | -1.7973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Boolaroo 33_11kV Tx2 | 0.22291 | 0.58301 | -0.99708 | -4.8203 | -1.7973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Boolaroo 33_11kV Tx3 | 0.22291 | 0.58301 | -0.99708 | -4.8203 | -1.7973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV MVA) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 0.53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0.46703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 0.53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0.46703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx4 | 0 | 0 | 0.53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2294. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx5 | 0 | 0 | 0.46703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 2.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 2.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 2.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 2.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 2.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2295. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 2.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0.95546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0.84184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0.95546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0.84184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0.95546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2296. To Argenton 2010 | Boolaroo 33_11kV Tx3 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0.84184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2000158. Premier Metals Teralba - Nov 07 |  | Boolaroo 33_11kV Tx1 | 0.22291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2000158. Premier Metals Teralba - Nov 07 |  | Boolaroo 33_11kV Tx2 | 0.22291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2000158. Premier Metals Teralba - Nov 07 |  | Boolaroo 33_11kV Tx3 | 0.22291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2000159. LMCC Depot |  | Boolaroo 33_11kV Tx1 | 0 | 0.22291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2000159. LMCC Depot |  | Boolaroo 33_11kV Tx2 | 0 | 0.22291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2000159. LMCC Depot |  | Boolaroo 33_11kV Tx3 | 0 | 0.22291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2000160. Cockle Creek Pump Station |  | Boolaroo 33_11kV Tx1 | 0 | 0.36009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2000160. Cockle Creek Pump Station |  | Boolaroo 33_11kV Tx2 | 0 | 0.36009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2000160. Cockle Creek Pump Station |  | Boolaroo 33_11kV Tx3 | 0 | 0.36009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Boolaroo 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.98805 | Diversity Factor: 0.99 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Cardiff 33_11kV
| Cardiff 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV MVA) | [20 empty] | Spots & Transfers Summary | (11kV MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 26.741 | 30.037 | 21.7 | 23.327 | 17.457 | 22.69 | 18.553 |  | 17.8283 | 17.5969 | 17.4311 | 17.2579 | 17.1711 | 17.0908 | 17.1277 | 17.2144 | 17.2773 | 17.3748 | 17.4322 | 17.5359 | 17.6411 | 17.7747 | 17.9255 | 18.0736 | 18.2184 | 18.3688 | 18.5251 | 18.6871 | 18.8551 | 19.0291 | 19.2092 | 19.3955 | 19.588 |  |  | Total | 0 | 0.75448 | -9.6215 | -0.12218 | -0.12101 | -0.1089 | -1.6713 | -0.47166 | -0.10214 | -0.080778 | -0.13114 | -0.086782 | -0.080224 | 0.036837 | 0.086692 | 0.062891 | 0.09751 | 0.05744 | 0.10364 | 0.10528 | 0.13356 | 0.15085 | 0.14807 | 0.14477 | 0.15045 | 0.15621 | 0.16206 | 0.16798 | 0.174 | 0.1801 | 0.18628 | 0.19256
| Firm Rating | 0 | 0 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 |  | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86
| Total Capacity | 0 | 0 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 |  | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 | 45.73 |  |  | Cardiff 33_11kV Tx1 | 0 | 0.37724 | -4.8108 | -0.06109 | -0.060505 | -0.05445 | -1.9598 | 2.4125 | -0.051071 | -0.040389 | -0.065569 | -0.043391 | -0.040112 | 0.018419 | 0.043346 | 0.031446 | 0.048755 | 0.02872 | 0.051819 | 0.052642 | 0.066778 | 0.075423 | 0.074037 | 0.072384 | 0.075225 | 0.078106 | 0.081028 | 0.083992 | 0.086999 | 0.090048 | 0.093141 | 0.096278
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Cardiff 33_11kV Tx2 | 0 | 0.37724 | -4.8108 | -0.06109 | -0.060505 | -0.05445 | 0.28844 | -2.8841 | -0.051071 | -0.040389 | -0.065569 | -0.043391 | -0.040112 | 0.018419 | 0.043346 | 0.031446 | 0.048755 | 0.02872 | 0.051819 | 0.052642 | 0.066778 | 0.075423 | 0.074037 | 0.072384 | 0.075225 | 0.078106 | 0.081028 | 0.083992 | 0.086999 | 0.090048 | 0.093141 | 0.096278
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Cardiff 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.083861 | 0 | 0 | -0.037606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Cardiff 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.083861 | 0 | 0 | -0.037606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2299. To Argenton (-9.7) | Cardiff 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 2.5574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2299. To Argenton (-9.7) | Cardiff 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 2.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2299. To Argenton (-9.7) | Cardiff 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 2.5574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2299. To Argenton (-9.7) | Cardiff 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 2.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2301. To Argenton (-9.7) | Cardiff 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2301. To Argenton (-9.7) | Cardiff 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6909. Cardiff Zone Substation - New 11kV Feeder to Warners Bay | Argenton 132_11kV Tx5 | Cardiff 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6909. Cardiff Zone Substation - New 11kV Feeder to Warners Bay | Cardiff 33_11kV Tx1 | Cardiff 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6909. Cardiff Zone Substation - New 11kV Feeder to Warners Bay | Cardiff 33_11kV Tx2 | Cardiff 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6909. Cardiff Zone Substation - New 11kV Feeder to Warners Bay | Charlestown 132_11kV Tx2 | Cardiff 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6909. Cardiff Zone Substation - New 11kV Feeder to Warners Bay | Croudace Bay 33_11kV Tx2 | Cardiff 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 7120. Charlestown Zone - Garden Suburb N-1 | Cardiff 33_11kV Tx1 | Charlestown 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7120. Charlestown Zone - Garden Suburb N-1 | Cardiff 33_11kV Tx2 | Charlestown 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7152. Load Trasnfer Cardiff 11kV Feeder 8669 to Kotara 11kV feeder 12205 Load Trasnfer complete (4/06/2013) await related projects to be completed to restore system to orginal configuration | Cardiff 33_11kV Tx1 | Kotara 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 7152. Load Trasnfer Cardiff 11kV Feeder 8669 to Kotara 11kV feeder 12205 Load Trasnfer complete (4/06/2013) await related projects to be completed to restore system to orginal configuration | Cardiff 33_11kV Tx2 | Kotara 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2000161. Cardiff Woolworths Shopping Complex |  | Cardiff 33_11kV Tx1 | 0 | 0.37724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2000161. Cardiff Woolworths Shopping Complex |  | Cardiff 33_11kV Tx2 | 0 | 0.37724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Cardiff 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059009 | 0.10627 | 0.13968 | 0.15293 | 0.16034 | 0.16132 | 0.15964 | 0.16101 | 0.16358 | 0.16619 | 0.16883 | 0.17151 | 0.17424 | 0.177 | 0.1798 | 0.18264 | 0.18552 | 0.18844 | 0.19141 | 0.19441 | 0.19746 | 0.20055 | 0.20369
| 0 | [33 empty] | Econometric |  | Cardiff 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059009 | 0.10627 | 0.13968 | 0.15293 | 0.16034 | 0.16132 | 0.15964 | 0.16101 | 0.16358 | 0.16619 | 0.16883 | 0.17151 | 0.17424 | 0.177 | 0.1798 | 0.18264 | 0.18552 | 0.18844 | 0.19141 | 0.19441 | 0.19746 | 0.20055 | 0.20369
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Cardiff 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.019276 | -0.0090845 | -0.05198 | -0.082202 | -0.12739 | -0.13437 | -0.080497 | -0.058581 | -0.067852 | -0.066084 | -0.079557 | -0.059066 | -0.060889 | -0.049436 | -0.043512 | -0.04766 | -0.052112 | -0.052112 | -0.052112 | -0.052112 | -0.052112 | -0.052112 | -0.052112 | -0.052112 | -0.052112
[35 empty] | Energy Efficiency |  | Cardiff 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.019276 | -0.0090845 | -0.05198 | -0.082202 | -0.12739 | -0.13437 | -0.080497 | -0.058581 | -0.067852 | -0.066084 | -0.079557 | -0.059066 | -0.060889 | -0.049436 | -0.043512 | -0.04766 | -0.052112 | -0.052112 | -0.052112 | -0.052112 | -0.052112 | -0.052112 | -0.052112 | -0.052112 | -0.052112
[35 empty] | Solar PV |  | Cardiff 33_11kV Tx1 | 0 | 0 | 0 | -0.06109 | -0.060505 | -0.05445 | -0.02593 | -0.037432 | -0.041986 | -0.047419 | -0.052031 | -0.055686 | -0.058664 | -0.06142 | -0.059395 | -0.060339 | -0.046168 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553
| 0 | [33 empty] | Solar PV |  | Cardiff 33_11kV Tx2 | 0 | 0 | 0 | -0.06109 | -0.060505 | -0.05445 | -0.02593 | -0.037432 | -0.041986 | -0.047419 | -0.052031 | -0.055686 | -0.058664 | -0.06142 | -0.059395 | -0.060339 | -0.046168 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553 | -0.0553
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 9.143% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.99276 | 0.98557 | 0.98081 | 0.97845 | 0.97845 | 0.97845 | 0.97845 | 0.97845 | 0.97845 | 0.97845 | -0.724% | -0.724% | -0.483% | -0.241% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Cardiff 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 |  | 935.7447 | 923.6 | 914.8965 | 905.8027 | 901.2478 | 897.0372 | 898.9706 | 903.5208 | 906.8217 | 911.9396 | 914.9545 | 920.394 | 925.92 | 932.9298 | 940.8472 | 948.6191 | 956.2174 | 964.114 | 972.3129 | 980.8187 | 989.6356 | 998.7681 | 1008.22 | 1017.997 | 1028.104
|  |  |  | Apparent Power |  |  | MVA | 18.553 | 18.45 | 17.8283 | 17.5969 | 17.4311 | 17.2579 | 17.1711 | 17.0908 | 17.1277 | 17.2144 | 17.2773 | 17.3748 | 17.4322 | 17.5359 | 17.6411 | 17.7747 | 17.9255 | 18.0736 | 18.2184 | 18.3688 | 18.5251 | 18.6871 | 18.8551 | 19.0291 | 19.2092 | 19.3955 | 19.588
|  |  |  | Real Power |  |  | MW | 17.6996 | 17.6013 | 16.9228 | 16.7032 | 16.5457 | 16.3813 | 16.2989 | 16.2228 | 16.2577 | 16.34 | 16.3997 | 16.4923 | 16.5468 | 16.6452 | 16.7451 | 16.8719 | 17.0151 | 17.1556 | 17.293 | 17.4358 | 17.5841 | 17.7379 | 17.8974 | 18.0626 | 18.2335 | 18.4103 | 18.5931
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 5.6097 | 5.5369 | 5.4847 | 5.4302 | 5.4029 | 5.3777 | 5.3892 | 5.4165 | 5.4363 | 5.467 | 5.4851 | 5.5177 | 5.5508 | 5.5928 | 5.6403 | 5.6869 | 5.7324 | 5.7798 | 5.8289 | 5.8799 | 5.9328 | 5.9875 | 6.0442 | 6.1028 | 6.1634
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.954 |  | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921
0.97624 | Diversity Factor: 0.98 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 5.5314 | 5.6097 | 5.5369 | 5.4847 | 5.4302 | 5.4029 | 5.3777 | 5.3892 | 5.4165 | 5.4363 | 5.467 | 5.4851 | 5.5177 | 5.5508 | 5.5928 | 5.6403 | 5.6869 | 5.7324 | 5.7798 | 5.8289 | 5.8799 | 5.9328 | 5.9875 | 6.0442 | 6.1028 | 6.1634
|  |  |  | PF |  |  |  | 0.954 |  | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921 | 0.94921
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Edgeworth 33_11kV
| Edgeworth 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV MVA) | [20 empty] | Spots & Transfers Summary | (11kV MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 19.417 | 26.913 | 21.2 | 18.026 | 17.074 | 22.168 | 18.723 |  | 22.2415 | 22.9372 | 23.0921 | 23.2038 | 23.309 | 23.4917 | 23.7331 | 23.9786 | 24.1928 | 24.4274 | 24.6505 | 24.9066 | 25.1671 | 25.4444 | 25.7345 | 26.0256 | 26.3193 | 26.6196 | 26.9263 | 27.2398 | 27.5599 | 27.8869 | 28.2208 | 28.5617 | 28.9097 |  |  | Total | -1.2003 | 0.99073 | -4.4011 | -4.6545 | 2.5268 | -0.02928 | -1.3857 | 1.1953 | 0.50727 | 0.025299 | 0.046444 | 0.10521 | 0.18278 | 0.24133 | 0.24555 | 0.21413 | 0.23468 | 0.22309 | 0.25606 | 0.26048 | 0.27734 | 0.29006 | 0.2911 | 0.29377 | 0.30023 | 0.30678 | 0.31342 | 0.32015 | 0.32698 | 0.3339 | 0.34091 | 0.34803
| Firm Rating | 0 | 0 | 22.9 | 22.9 | 22.9 | 22.86 | 22.86 |  | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86 | 22.86
| Total Capacity | 0 | 0 | 50.45 | 50.45 | 50.45 | 37.45 | 37.46 |  | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 | 37.46 |  |  | Edgeworth 33_11kV Tx1 | -0.60016 | 0.49537 | -2.2006 | -2.3272 | 1.2634 | -0.01464 | -0.69286 | 0.59767 | 0.25363 | 0.01265 | 0.023222 | 0.052604 | 0.091391 | 0.12066 | 0.12278 | 0.10706 | 0.11734 | 0.11154 | 0.12803 | 0.13024 | 0.13867 | 0.14503 | 0.14555 | 0.14689 | 0.15012 | 0.15339 | 0.15671 | 0.16008 | 0.16349 | 0.16695 | 0.17046 | 0.17401
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Edgeworth 33_11kV Tx2 | -0.60016 | 0.49537 | -2.2006 | -2.3272 | 1.2634 | -0.01464 | -0.69286 | 0.59767 | 0.25363 | 0.01265 | 0.023222 | 0.052604 | 0.091391 | 0.12066 | 0.12278 | 0.10706 | 0.11734 | 0.11154 | 0.12803 | 0.13024 | 0.13867 | 0.14503 | 0.14555 | 0.14689 | 0.15012 | 0.15339 | 0.15671 | 0.16008 | 0.16349 | 0.16695 | 0.17046 | 0.17401
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.046882 | -0.00019706 | -0.0012809 | -0.023957 | -0.0025617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.046882 | -0.00019706 | -0.0012809 | -0.023957 | -0.0025617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2288. To Edgeworth SAO Nov 11 | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0.13167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2288. To Edgeworth SAO Nov 11 | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0.11601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2288. To Edgeworth SAO Nov 11 | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0.13167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2288. To Edgeworth SAO Nov 11 | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0.11601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2308. To Maryland 1.2MVA Tasman DNP 30/5/07 | Edgeworth 33_11kV Tx1 | Maryland 132_11kV Tx1 | 0.23935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2308. To Maryland 1.2MVA Tasman DNP 30/5/07 | Edgeworth 33_11kV Tx1 | Maryland 132_11kV Tx2 | 0.36081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2308. To Maryland 1.2MVA Tasman DNP 30/5/07 | Edgeworth 33_11kV Tx2 | Maryland 132_11kV Tx1 | 0.23935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2308. To Maryland 1.2MVA Tasman DNP 30/5/07 | Edgeworth 33_11kV Tx2 | Maryland 132_11kV Tx2 | 0.36081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2309. From Maryland to Edgeworth Oct 2008 - SAO due to high feeder loads | Maryland 132_11kV Tx1 | Edgeworth 33_11kV Tx1 | 0 | 0.19756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2309. From Maryland to Edgeworth Oct 2008 - SAO due to high feeder loads | Maryland 132_11kV Tx1 | Edgeworth 33_11kV Tx2 | 0 | 0.19756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2309. From Maryland to Edgeworth Oct 2008 - SAO due to high feeder loads | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx1 | 0 | 0.29781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2309. From Maryland to Edgeworth Oct 2008 - SAO due to high feeder loads | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx2 | 0 | 0.29781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2310. To Argenton (-8.4) | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 1.1698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2310. To Argenton (-8.4) | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 1.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2310. To Argenton (-8.4) | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 1.1698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2310. To Argenton (-8.4) | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 1.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2311. To Argenton (-8.4) | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 1.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2311. To Argenton (-8.4) | Edgeworth 33_11kV Tx1 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 1.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2311. To Argenton (-8.4) | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx4 | 0 | 0 | 0 | 1.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2311. To Argenton (-8.4) | Edgeworth 33_11kV Tx2 | Argenton 132_11kV Tx5 | 0 | 0 | 0 | 1.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2312. From Maryland to Edgeworth (SAO Nov 11) | Maryland 132_11kV Tx1 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0.51668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2312. From Maryland to Edgeworth (SAO Nov 11) | Maryland 132_11kV Tx1 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0.51668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2312. From Maryland to Edgeworth (SAO Nov 11) | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0.77889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2312. From Maryland to Edgeworth (SAO Nov 11) | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0.77889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2313. From Argenton to Edgeworth (SAO Nov 11) | Argenton 132_11kV Tx4 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0.13167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2313. From Argenton to Edgeworth (SAO Nov 11) | Argenton 132_11kV Tx4 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0.13167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2313. From Argenton to Edgeworth (SAO Nov 11) | Argenton 132_11kV Tx5 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0.11601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2313. From Argenton to Edgeworth (SAO Nov 11) | Argenton 132_11kV Tx5 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0.11601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7094. Edgeworth - New 11kV feeder and upgrade works | Argenton 132_11kV Tx4 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7094. Edgeworth - New 11kV feeder and upgrade works | Argenton 132_11kV Tx4 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7094. Edgeworth - New 11kV feeder and upgrade works | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | DNP_ID: 7094. Edgeworth - New 11kV feeder and upgrade works | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | ROG Justification | [24 empty] | HVCON_ID: 2000165. Cameron Park Market Place |  | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 14.26% |  | 5 year ROG ok | [24 empty] | HVCON_ID: 2000165. Cameron Park Market Place |  | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 year ROG ok
[35 empty] | HVCON_ID: 2000166. Cameron Park Market Place |  | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2000166. Cameron Park Market Place |  | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | HVCON_ID: 2014196. HV Customer Disconnection - Tasman Mine. Mine load ramped down over 2 months from June to Aug. |  | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | -0.68589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.0085 | 1.017 | 1.0228 | 1.0256 | 1.0256 | 1.0256 | 1.0256 | 1.0256 | 1.0256 | 1.0256 | 0.8472% | 0.8472% | 0.5648% | 0.2824% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | HVCON_ID: 2014196. HV Customer Disconnection - Tasman Mine. Mine load ramped down over 2 months from June to Aug. |  | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | -0.68589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068303 | 0.12729 | 0.1709 | 0.2164 | 0.20937 | 0.2004 | 0.19111 | 0.194 | 0.19693 | 0.19991 | 0.20292 | 0.20598 | 0.20907 | 0.21222 | 0.2154 | 0.21863 | 0.22191 | 0.22523 | 0.22859 | 0.232 | 0.23546 | 0.23897 | 0.24253
2: Substation Load Detail | Econometric |  | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068303 | 0.12729 | 0.1709 | 0.2164 | 0.20937 | 0.2004 | 0.19111 | 0.194 | 0.19693 | 0.19991 | 0.20292 | 0.20598 | 0.20907 | 0.21222 | 0.2154 | 0.21863 | 0.22191 | 0.22523 | 0.22859 | 0.232 | 0.23546 | 0.23897 | 0.24253
[35 empty] | Energy Efficiency |  | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0045114 | -0.0029512 | -0.036675 | -0.060691 | -0.094954 | -0.10312 | -0.065789 | -0.055462 | -0.061529 | -0.059432 | -0.064752 | -0.05124 | -0.052041 | -0.046669 | -0.043404 | -0.046028 | -0.047876 | -0.047876 | -0.047876 | -0.047876 | -0.047876 | -0.047876 | -0.047876 | -0.047876 | -0.047876
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | Energy Efficiency |  | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0045114 | -0.0029512 | -0.036675 | -0.060691 | -0.094954 | -0.10312 | -0.065789 | -0.055462 | -0.061529 | -0.059432 | -0.064752 | -0.05124 | -0.052041 | -0.046669 | -0.043404 | -0.046028 | -0.047876 | -0.047876 | -0.047876 | -0.047876 | -0.047876 | -0.047876 | -0.047876 | -0.047876 | -0.047876
1 | Edgeworth 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 |  | 1167.378 | 1203.893 | 1212.021 | 1217.881 | 1223.403 | 1232.997 | 1245.663 | 1258.552 | 1269.79 | 1282.108 | 1293.817 | 1307.256 | 1320.928 | 1335.484 | 1350.709 | 1365.987 | 1381.406 | 1397.164 | 1413.266 | 1429.717 | 1446.52 | 1463.682 | 1481.207 | 1499.101 | 1517.368 | Solar PV |  | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | -0.040925 | -0.032165 | -0.01464 | -0.00697 | -0.01397 | -0.015669 | -0.017697 | -0.019418 | -0.020782 | -0.021894 | -0.022922 | -0.022166 | -0.022519 | -0.01723 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638
|  |  |  | Apparent Power |  |  | MVA | 18.723 | 20.87 | 22.2415 | 22.9372 | 23.0921 | 23.2038 | 23.309 | 23.4917 | 23.7331 | 23.9786 | 24.1928 | 24.4274 | 24.6505 | 24.9066 | 25.1671 | 25.4444 | 25.7345 | 26.0256 | 26.3193 | 26.6196 | 26.9263 | 27.2398 | 27.5599 | 27.8869 | 28.2208 | 28.5617 | 28.9097 | Solar PV |  | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | -0.040925 | -0.032165 | -0.01464 | -0.00697 | -0.01397 | -0.015669 | -0.017697 | -0.019418 | -0.020782 | -0.021894 | -0.022922 | -0.022166 | -0.022519 | -0.01723 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638 | -0.020638
|  |  |  | Real Power |  |  | MW | 17.7869 | 19.8265 | 21.1197 | 21.7803 | 21.9273 | 22.0333 | 22.1332 | 22.3068 | 22.5359 | 22.7691 | 22.9724 | 23.1953 | 23.4071 | 23.6503 | 23.8976 | 24.1609 | 24.4364 | 24.7128 | 24.9917 | 25.2768 | 25.5681 | 25.8658 | 26.1698 | 26.4803 | 26.7973 | 27.121 | 27.4515
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 6.9747 | 7.1929 | 7.2414 | 7.2764 | 7.3094 | 7.3668 | 7.4424 | 7.5194 | 7.5866 | 7.6602 | 7.7301 | 7.8104 | 7.8921 | 7.9791 | 8.07 | 8.1613 | 8.2535 | 8.3476 | 8.4438 | 8.5421 | 8.6425 | 8.745 | 8.8497 | 8.9566 | 9.0658
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.95 |  | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956
0.96019 | Diversity Factor: 0.96 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 6.5167 | 6.9747 | 7.1929 | 7.2414 | 7.2764 | 7.3094 | 7.3668 | 7.4424 | 7.5194 | 7.5866 | 7.6602 | 7.7301 | 7.8104 | 7.8921 | 7.9791 | 8.07 | 8.1613 | 8.2535 | 8.3476 | 8.4438 | 8.5421 | 8.6425 | 8.745 | 8.8497 | 8.9566 | 9.0658
|  |  |  | PF |  |  |  | 0.95 |  | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Maryland 132_11kV
| Maryland 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV MVA) | [20 empty] | Spots & Transfers Summary | (11kV MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 29.1 | 30.561 | 27.7 | 31.283 | 17.685 | 24.329 | 20.756 |  | 22.3489 | 21.4994 | 20.9982 | 20.7726 | 20.8429 | 21.029 | 21.4159 | 21.8038 | 22.142 | 22.5098 | 22.8582 | 23.2506 | 23.6489 | 24.0715 | 24.5118 | 24.9538 | 25.3989 | 25.8529 | 26.316 | 26.7883 | 27.2699 | 27.7609 | 28.2615 | 28.7717 | 29.2918 |  |  | Total | 5.6967 | -0.42106 | 0 | -1.6215 | -3.8563 | 0.39721 | -0.02101 | -0.90012 | -0.060418 | 0.0048903 | 0.021491 | 0.070269 | 0.18618 | 0.38683 | 0.38798 | 0.33818 | 0.36777 | 0.34841 | 0.39236 | 0.39831 | 0.4226 | 0.44029 | 0.44198 | 0.4451 | 0.45404 | 0.4631 | 0.47228 | 0.48159 | 0.49102 | 0.50057 | 0.51026 | 0.52008
| Firm Rating | 0 | 0 | 38 | 38 | 38 | 38.11 | 38.11 |  | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11 | 38.11
| Total Capacity | 0 | 0 | 76 | 76 | 76 | 76.21 | 76.21 |  | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 | 76.21 |  |  | Maryland 132_11kV Tx1 | 2.2719 | -0.16792 | 0 | -0.031223 | -1.5379 | 0.15841 | -0.0083789 | -0.070237 | -0.024095 | 0.0019503 | 0.0085708 | 0.028024 | 0.074249 | 0.15427 | 0.15473 | 0.13487 | 0.14667 | 0.13895 | 0.15648 | 0.15885 | 0.16854 | 0.17559 | 0.17626 | 0.17751 | 0.18107 | 0.18469 | 0.18835 | 0.19206 | 0.19582 | 0.19963 | 0.20349 | 0.20741
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Maryland 132_11kV Tx2 | 3.4248 | -0.25314 | 0 | -1.5903 | -2.3184 | 0.2388 | -0.012631 | -0.82988 | -0.036323 | 0.00294 | 0.01292 | 0.042245 | 0.11193 | 0.23256 | 0.23325 | 0.20331 | 0.2211 | 0.20946 | 0.23589 | 0.23946 | 0.25407 | 0.2647 | 0.26572 | 0.26759 | 0.27297 | 0.27841 | 0.28393 | 0.28953 | 0.2952 | 0.30094 | 0.30676 | 0.31267
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Maryland 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.045429 | -0.00032585 | -0.002118 | -0.023225 | -0.0042361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Maryland 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.068483 | -0.00049121 | -0.0031929 | -0.035011 | -0.0063858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2182. From Maryland | Maryland 132_11kV Tx1 | Jesmond 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0.3939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2182. From Maryland | Maryland 132_11kV Tx1 | Jesmond 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0.40392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2182. From Maryland | Maryland 132_11kV Tx2 | Jesmond 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0.5938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2182. From Maryland | Maryland 132_11kV Tx2 | Jesmond 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0.6089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2308. To Maryland 1.2MVA Tasman DNP 30/5/07 | Edgeworth 33_11kV Tx1 | Maryland 132_11kV Tx1 | 0.23935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2308. To Maryland 1.2MVA Tasman DNP 30/5/07 | Edgeworth 33_11kV Tx1 | Maryland 132_11kV Tx2 | 0.36081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2308. To Maryland 1.2MVA Tasman DNP 30/5/07 | Edgeworth 33_11kV Tx2 | Maryland 132_11kV Tx1 | 0.23935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2308. To Maryland 1.2MVA Tasman DNP 30/5/07 | Edgeworth 33_11kV Tx2 | Maryland 132_11kV Tx2 | 0.36081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2309. From Maryland to Edgeworth Oct 2008 - SAO due to high feeder loads | Maryland 132_11kV Tx1 | Edgeworth 33_11kV Tx1 | 0 | 0.19756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2309. From Maryland to Edgeworth Oct 2008 - SAO due to high feeder loads | Maryland 132_11kV Tx1 | Edgeworth 33_11kV Tx2 | 0 | 0.19756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2309. From Maryland to Edgeworth Oct 2008 - SAO due to high feeder loads | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx1 | 0 | 0.29781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2309. From Maryland to Edgeworth Oct 2008 - SAO due to high feeder loads | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx2 | 0 | 0.29781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2312. From Maryland to Edgeworth (SAO Nov 11) | Maryland 132_11kV Tx1 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0.51668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2312. From Maryland to Edgeworth (SAO Nov 11) | Maryland 132_11kV Tx1 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0.51668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2312. From Maryland to Edgeworth (SAO Nov 11) | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0.77889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2312. From Maryland to Edgeworth (SAO Nov 11) | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0.77889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2321. Maryland to Wallsend - SAO Oct 08 | Maryland 132_11kV Tx1 | Wallsend 33_11kV Tx2 | 0 | 0.19756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2321. Maryland to Wallsend - SAO Oct 08 | Maryland 132_11kV Tx1 | Wallsend 33_11kV Tx3 | 0 | 0.19756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2321. Maryland to Wallsend - SAO Oct 08 | Maryland 132_11kV Tx2 | Wallsend 33_11kV Tx2 | 0 | 0.29781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2321. Maryland to Wallsend - SAO Oct 08 | Maryland 132_11kV Tx2 | Wallsend 33_11kV Tx3 | 0 | 0.29781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2330. Wallsend to Maryland 16/11/06 | Wallsend 33_11kV Tx2 | Maryland 132_11kV Tx1 | 0.8966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2330. Wallsend to Maryland 16/11/06 | Wallsend 33_11kV Tx2 | Maryland 132_11kV Tx2 | 1.3516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2330. Wallsend to Maryland 16/11/06 | Wallsend 33_11kV Tx3 | Maryland 132_11kV Tx1 | 0.8966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2330. Wallsend to Maryland 16/11/06 | Wallsend 33_11kV Tx3 | Maryland 132_11kV Tx2 | 1.3516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7094. Edgeworth - New 11kV feeder and upgrade works | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7094. Edgeworth - New 11kV feeder and upgrade works | Maryland 132_11kV Tx2 | Edgeworth 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2000167. Blue Gum Hills |  | Maryland 132_11kV Tx1 | 0 | 0.3556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2000167. Blue Gum Hills |  | Maryland 132_11kV Tx2 | 0 | 0.53606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2000168. 295/07 - Cameron Park, Kalinya Close Walter Mining Workshop |  | Maryland 132_11kV Tx1 | 0 | 0.2667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2000168. 295/07 - Cameron Park, Kalinya Close Walter Mining Workshop |  | Maryland 132_11kV Tx2 | 0 | 0.40204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2000169. 75/09 - "HDWB Wallsend" |  | Maryland 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0.32141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | HVCON_ID: 2000169. 75/09 - "HDWB Wallsend" |  | Maryland 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0.48452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | ROG Justification | [24 empty] | HVCON_ID: 2000170. HP310/11 Fletcher Supermarket |  | Maryland 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0.20515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 20.1% |  | 7 year ROG ok | [24 empty] | HVCON_ID: 2000170. HP310/11 Fletcher Supermarket |  | Maryland 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0.30927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 year ROG ok
[35 empty] | HVCON_ID: 2013143. Summerhill Generator 2MW on Maryland feeder 33777 was installed during 2009/10. It remains connected to Maryland feeder 33777. It exports approximately 2MW consistently. System number is 44112. |  | Maryland 132_11kV Tx2 | 0 | 0 | 0 | -1.5433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Maryland 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064311 | 0.1183 | 0.15526 | 0.20619 | 0.24871 | 0.2361 | 0.22309 | 0.22629 | 0.22954 | 0.23283 | 0.23616 | 0.23954 | 0.24296 | 0.24643 | 0.24995 | 0.25352 | 0.25713 | 0.26079 | 0.2645 | 0.26826 | 0.27207 | 0.27594 | 0.27985
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | Econometric |  | Maryland 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096947 | 0.17833 | 0.23404 | 0.31082 | 0.37492 | 0.35592 | 0.33631 | 0.34113 | 0.34603 | 0.35098 | 0.35601 | 0.3611 | 0.36626 | 0.3715 | 0.3768 | 0.38217 | 0.38762 | 0.39314 | 0.39873 | 0.4044 | 0.41015 | 0.41597 | 0.42187
0.9647 | 0.93065 | 0.90875 | 0.89806 | 0.89806 | 0.89806 | 0.89806 | 0.89806 | 0.89806 | 0.89806 | -3.53% | -3.53% | -2.353% | -1.176% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Energy Efficiency |  | Maryland 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0071972 | -0.0040155 | -0.037932 | -0.062022 | -0.096796 | -0.10434 | -0.065539 | -0.053428 | -0.059835 | -0.057903 | -0.064571 | -0.050333 | -0.051296 | -0.044986 | -0.041354 | -0.044152 | -0.046424 | -0.046424 | -0.046424 | -0.046424 | -0.046424 | -0.046424 | -0.046424 | -0.046424 | -0.046424
[35 empty] | Energy Efficiency |  | Maryland 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.01085 | -0.0060533 | -0.057182 | -0.093496 | -0.14592 | -0.15729 | -0.098799 | -0.080542 | -0.0902 | -0.087288 | -0.09734 | -0.075875 | -0.077327 | -0.067815 | -0.062341 | -0.066559 | -0.069983 | -0.069983 | -0.069983 | -0.069983 | -0.069983 | -0.069983 | -0.069983 | -0.069983 | -0.069983
2: Substation Load Detail | Solar PV |  | Maryland 132_11kV Tx1 | 0 | 0 | 0 | -0.031223 | -0.02812 | -0.046744 | -0.0083789 | -0.017611 | -0.019754 | -0.02231 | -0.02448 | -0.026199 | -0.027601 | -0.028897 | -0.027944 | -0.028388 | -0.021721 | -0.026018 | -0.026018 | -0.026018 | -0.026018 | -0.026018 | -0.026018 | -0.026018 | -0.026018 | -0.026018 | -0.026018 | -0.026018 | -0.026018 | -0.026018 | -0.026018 | -0.026018
[35 empty] | Solar PV |  | Maryland 132_11kV Tx2 | 0 | 0 | 0 | -0.047067 | -0.04239 | -0.070466 | -0.012631 | -0.026549 | -0.029778 | -0.033631 | -0.036903 | -0.039495 | -0.041607 | -0.043562 | -0.042125 | -0.042795 | -0.032744 | -0.039221 | -0.039221 | -0.039221 | -0.039221 | -0.039221 | -0.039221 | -0.039221 | -0.039221 | -0.039221 | -0.039221 | -0.039221 | -0.039221 | -0.039221 | -0.039221 | -0.039221
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Maryland 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 |  | 1173.015 | 1128.427 | 1102.121 | 1090.278 | 1093.966 | 1103.738 | 1124.041 | 1144.405 | 1162.155 | 1181.458 | 1199.745 | 1220.339 | 1241.244 | 1263.425 | 1286.535 | 1309.733 | 1333.094 | 1356.925 | 1381.232 | 1406.02 | 1431.297 | 1457.069 | 1483.342 | 1510.124 | 1537.42
|  |  |  | Apparent Power |  |  | MVA | 20.756 | 24.1 | 22.3489 | 21.4994 | 20.9982 | 20.7726 | 20.8429 | 21.029 | 21.4159 | 21.8038 | 22.142 | 22.5098 | 22.8582 | 23.2506 | 23.6489 | 24.0715 | 24.5118 | 24.9538 | 25.3989 | 25.8529 | 26.316 | 26.7883 | 27.2699 | 27.7609 | 28.2615 | 28.7717 | 29.2918
|  |  |  | Real Power |  |  | MW | 19.437 | 22.5685 | 20.9287 | 20.1332 | 19.6638 | 19.4525 | 19.5183 | 19.6927 | 20.0549 | 20.4183 | 20.735 | 21.0794 | 21.4056 | 21.7731 | 22.146 | 22.5418 | 22.9541 | 23.368 | 23.7848 | 24.21 | 24.6437 | 25.086 | 25.5369 | 25.9967 | 26.4655 | 26.9433 | 27.4304
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 7.8399 | 7.5419 | 7.3661 | 7.2869 | 7.3116 | 7.3769 | 7.5126 | 7.6487 | 7.7673 | 7.8963 | 8.0186 | 8.1562 | 8.2959 | 8.4442 | 8.5986 | 8.7537 | 8.9098 | 9.0691 | 9.2315 | 9.3972 | 9.5661 | 9.7384 | 9.914 | 10.093 | 10.2754
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.93645 |  | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645
0.98447 | Diversity Factor: 0.98 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 8.4542 | 7.8399 | 7.5419 | 7.3661 | 7.2869 | 7.3116 | 7.3769 | 7.5126 | 7.6487 | 7.7673 | 7.8963 | 8.0186 | 8.1562 | 8.2959 | 8.4442 | 8.5986 | 8.7537 | 8.9098 | 9.0691 | 9.2315 | 9.3972 | 9.5661 | 9.7384 | 9.914 | 10.093 | 10.2754
|  |  |  | PF |  |  |  | 0.93645 |  | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645 | 0.93645
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer45
| Customer45 | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | MVA | [7 empty] | Weather Corrected Forecast Loads |  |  |  | MVA | [20 empty] | Spots & Transfers Summary | MVA |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  | 5.135 | 5.179 | 5.083 | 5.012 |  | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | MVA | [7 empty] | Weather Corrected Forecast Loads |  |  |  | MVA | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Customer45 | Compensated |  | Load (LV side) |  |  | Amps | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
|  |  |  | Apparent Power |  |  | MVA | 5.012 |  | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012 | 5.012
|  |  |  | Real Power |  |  | MW | 4.5108 |  | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108 | 4.5108
|  |  |  | Reactive Power |  |  | MVAr | 2.1847 |  | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.76131 | Diversity Factor: 0.76 | Uncompensated |  | Reactive Power |  |  | MVAr | 2.1847 |  | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847 | 2.1847
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Wallsend 33_11kV
| Wallsend 33_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone decommissioned |  | 2012-03-30
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV MVA) | [20 empty] | Spots & Transfers Summary | (11kV MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 12.345 | 17.539 | 16.109 | 9.432 | 5.383 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | -3.862 | 0.99073 | 0 | -6.0968 | -4.001 | -6.6303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 15.2 | 15.2 | 15.2 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 29.47 | 29.47 | 29.47 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Wallsend 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Wallsend 33_11kV Tx2 | -1.931 | 0.49537 | 0 | -3.0484 | -2.0005 | -3.3151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Wallsend 33_11kV Tx3 | -1.931 | 0.49537 | 0 | -3.0484 | -2.0005 | -3.3151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV MVA) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | DNP_ID: 2179. From Wallsend | Wallsend 33_11kV Tx2 | Jesmond 132_11kV Tx1 | 0 | 0 | 0 | 1.5051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2179. From Wallsend | Wallsend 33_11kV Tx2 | Jesmond 132_11kV Tx2 | 0 | 0 | 0 | 1.5433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2179. From Wallsend | Wallsend 33_11kV Tx3 | Jesmond 132_11kV Tx1 | 0 | 0 | 0 | 1.5051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2179. From Wallsend | Wallsend 33_11kV Tx3 | Jesmond 132_11kV Tx2 | 0 | 0 | 0 | 1.5433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2321. Maryland to Wallsend - SAO Oct 08 | Maryland 132_11kV Tx1 | Wallsend 33_11kV Tx2 | 0 | 0.19756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2321. Maryland to Wallsend - SAO Oct 08 | Maryland 132_11kV Tx1 | Wallsend 33_11kV Tx3 | 0 | 0.19756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2321. Maryland to Wallsend - SAO Oct 08 | Maryland 132_11kV Tx2 | Wallsend 33_11kV Tx2 | 0 | 0.29781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2321. Maryland to Wallsend - SAO Oct 08 | Maryland 132_11kV Tx2 | Wallsend 33_11kV Tx3 | 0 | 0.29781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2330. Wallsend to Maryland 16/11/06 | Wallsend 33_11kV Tx2 | Maryland 132_11kV Tx1 | 0.8966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2330. Wallsend to Maryland 16/11/06 | Wallsend 33_11kV Tx2 | Maryland 132_11kV Tx2 | 1.3516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2330. Wallsend to Maryland 16/11/06 | Wallsend 33_11kV Tx3 | Maryland 132_11kV Tx1 | 0.8966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2330. Wallsend to Maryland 16/11/06 | Wallsend 33_11kV Tx3 | Maryland 132_11kV Tx2 | 1.3516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2333. All Load to Jesmond | Wallsend 33_11kV Tx2 | Jesmond 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0.9877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2333. All Load to Jesmond | Wallsend 33_11kV Tx2 | Jesmond 132_11kV Tx2 | 0 | 0 | 0 | 0 | 1.0128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2333. All Load to Jesmond | Wallsend 33_11kV Tx3 | Jesmond 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0.9877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2333. All Load to Jesmond | Wallsend 33_11kV Tx3 | Jesmond 132_11kV Tx2 | 0 | 0 | 0 | 0 | 1.0128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 2334. All Load to Jesmond | Wallsend 33_11kV Tx2 | Jesmond 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 1.6368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 2334. All Load to Jesmond | Wallsend 33_11kV Tx2 | Jesmond 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 1.6784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2334. All Load to Jesmond | Wallsend 33_11kV Tx3 | Jesmond 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 1.6368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 2334. All Load to Jesmond | Wallsend 33_11kV Tx3 | Jesmond 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 1.6784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2000171. Wallsend Retirement, Lake Rd |  | Wallsend 33_11kV Tx2 | 0.31723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2000171. Wallsend Retirement, Lake Rd |  | Wallsend 33_11kV Tx3 | 0.31723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Wallsend 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.60088 | Diversity Factor: 0.6 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer46
| Customer46 | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | MVA | [7 empty] | Weather Corrected Forecast Loads |  |  |  | MVA | [20 empty] | Spots & Transfers Summary | MVA |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  | 9.045 | 8.733 | 8.875 | 8.47 |  | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | MVA | [7 empty] | Weather Corrected Forecast Loads |  |  |  | MVA | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Customer46 | Compensated |  | Load (LV side) |  |  | Amps | 148 |  | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
|  |  |  | Apparent Power |  |  | MVA | 8.47 |  | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47
|  |  |  | Real Power |  |  | MW | 7.623 |  | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623 | 7.623
|  |  |  | Reactive Power |  |  | MVAr | 3.692 |  | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.53249 | Diversity Factor: 0.53 | Uncompensated |  | Reactive Power |  |  | MVAr | 3.692 |  | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692 | 3.692
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF