## Inclusions and Exclusions
Sydney Forecast Inclusions and Exclusions
Date Printed |  | 08JUL14:11:21:24
| Description | Value
Season |  | Summer | Summer
Either Summer or Winter
Year |  | 2015 | 2015
Year that the forecast starts
POE |  | 50% | 0.5
10%, 50%, 90%
Spots and Transfers |  | Y | Y
Are Spots and Transfers Included?
BBDM Spots |  | Y | Y
Is BBDM included?
Spots Coefficient |  | 55% | 0.55
Scaling factor applied to spot loads in the future
Aligned ROGs |  | Capped | Capped
Have ROGs been aligned to econometric forecast?
Committed Projects |  | Y | Y
Are Committed Projects Included?
Major Customers Scaling Factor |  | 100% | 1
Scaling factor applied to major customer connections in the future
Future Transfers |  | Y | Y
Are future transfers included?
Future Spots |  | 4 | 4
Future spots are cleared from the following forecast year

## Balgowlah 33_11kV
| Balgowlah 33_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone decommissioned |  | 2011-11-01
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 882 | 976 | 1186 | 1214 | 0 | 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | -436 | 0 | 155.7 | -4.1611 | -1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Balgowlah 33_11kV Tx1 | -218 | 0 | 77.85 | -2.0806 | -500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Balgowlah 33_11kV Tx2 | -218 | 0 | 77.85 | -2.0806 | -500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Commissioning Transfers | Balgowlah 33_11kV Tx1 | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | Balgowlah 33_11kV Tx2 | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6132. Relief of Balgowlah Zone Substation | Balgowlah 33_11kV Tx1 | Harbord 33_11kV Tx1 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6132. Relief of Balgowlah Zone Substation | Balgowlah 33_11kV Tx1 | Harbord 33_11kV Tx2 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6132. Relief of Balgowlah Zone Substation | Balgowlah 33_11kV Tx2 | Harbord 33_11kV Tx1 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6132. Relief of Balgowlah Zone Substation | Balgowlah 33_11kV Tx2 | Harbord 33_11kV Tx2 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006007. Install (1) 2x1500kVA chamber substation S.16984 Condamine Griffiths No.1, establish 2x KL substations S.16985 & S.16986 Sydney Condamine No.1 and No.2 |  | Balgowlah 33_11kV Tx1 | 0 | 0 | 77.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006007. Install (1) 2x1500kVA chamber substation S.16984 Condamine Griffiths No.1, establish 2x KL substations S.16985 & S.16986 Sydney Condamine No.1 and No.2 |  | Balgowlah 33_11kV Tx2 | 0 | 0 | 77.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Solar PV |  | Balgowlah 33_11kV Tx1 | 0 | 0 | 0 | -2.0806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Balgowlah 33_11kV Tx2 | 0 | 0 | 0 | -2.0806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Balgowlah 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.87828 | Diversity Factor: 0.88 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Balgowlah North 132_11kV
| Balgowlah North 132_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone commissioned |  | 2011-10-19
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  |  | 1300.5 | 1559.1 | 1137.3 |  | 1225.371 | 1212.119 | 1204.77 | 1193.669 | 1187.325 | 1191.779 | 1208.061 | 1226.667 | 1243.196 | 1261.118 | 1278.134 | 1299.375 | 1321.028 | 1344.711 | 1369.895 | 1395.028 | 1420.342 | 1446.325 | 1472.985 | 1500.333 | 1528.379 | 1557.134 | 1586.607 | 1616.81 | 1647.753 |  |  | Total | 0 | 0 | 0 | 0 | 1225 | 291.9753 | -0.49862 | -1.8301 | -5.7834 | -2.4243 | -8.6534 | -6.344 | 4.4539 | 16.2823 | 18.6064 | 16.5291 | 17.9216 | 17.0164 | 21.2404 | 21.6532 | 23.6829 | 25.184 | 25.1327 | 25.3147 | 25.9825 | 26.6603 | 27.3481 | 28.0461 | 28.7544 | 29.4733 | 30.2027 | 30.9429
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 1989 |  | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989 | 1989
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 2793 |  | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 | 2793 |  |  | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 1225 | 291.9753 | -0.49862 | -1.8301 | -5.7834 | -2.4243 | -8.6534 | -6.344 | 4.4539 | 16.2823 | 18.6064 | 16.5291 | 17.9216 | 17.0164 | 21.2404 | 21.6532 | 23.6829 | 25.184 | 25.1327 | 25.3147 | 25.9825 | 26.6603 | 27.3481 | 28.0461 | 28.7544 | 29.4733 | 30.2027 | 30.9429
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Balgowlah North 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Balgowlah North 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.16952 | -4.3827 | -5.8817 | -16.1482 | -10.9504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | Balgowlah 33_11kV Tx1 | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Balgowlah 33_11kV Tx2 | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6475. S.36300 Balgowlah North 132/33/11 kV Hybrid Zone - 11 kV Development Works | Harbord 33_11kV Tx1 | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 225 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6475. S.36300 Balgowlah North 132/33/11 kV Hybrid Zone - 11 kV Development Works | Harbord 33_11kV Tx2 | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Econometric |  | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.0508 | 24.6498 | 31.0541 | 33.1897 | 35.0514 | 34.6507 | 34.2096 | 34.8028 | 35.405 | 36.0161 | 36.6364 | 37.2659 | 37.9048 | 38.5532 | 39.2113 | 39.8791 | 40.5569 | 41.2447 | 41.9427 | 42.6511 | 43.3699 | 44.0993 | 44.8395
[35 empty] | Energy Efficiency |  | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0705 | -0.73874 | -9.8458 | -16.3347 | -25.5698 | -27.8109 | -17.8007 | -15.1079 | -16.7292 | -16.1534 | -17.5167 | -13.9038 | -14.1113 | -12.7111 | -11.8489 | -12.5486 | -13.0248 | -13.0248 | -13.0248 | -13.0248 | -13.0248 | -13.0248 | -13.0248 | -13.0248 | -13.0248
[35 empty] | Solar PV |  | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | -0.024669 | -0.49862 | -0.59017 | -0.66196 | -0.74761 | -0.82033 | -0.87795 | -0.92492 | -0.96837 | -0.93643 | -0.95131 | -0.7279 | -0.87188 | -0.87188 | -0.87188 | -0.87188 | -0.87188 | -0.87188 | -0.87188 | -0.87188 | -0.87188 | -0.87188 | -0.87188 | -0.87188 | -0.87188 | -0.87188 | -0.87188
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 8.566% |  | weighted ROG calc | [59 empty] | weighted ROG calc
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.99391 | 0.98786 | 0.98385 | 0.98185 | 0.98185 | 0.98185 | 0.98185 | 0.98185 | 0.98185 | 0.98185 | -0.609% | -0.609% | -0.406% | -0.203% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Balgowlah North 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1137.3 | 1234.7265 | 1225.371 | 1212.119 | 1204.77 | 1193.669 | 1187.325 | 1191.779 | 1208.061 | 1226.667 | 1243.196 | 1261.118 | 1278.134 | 1299.375 | 1321.028 | 1344.711 | 1369.895 | 1395.028 | 1420.342 | 1446.325 | 1472.985 | 1500.333 | 1528.379 | 1557.134 | 1586.607 | 1616.81 | 1647.753
|  |  |  | Apparent Power |  |  | MVA | 21.6685 |  | 23.3465 | 23.094 | 22.9539 | 22.7425 | 22.6216 | 22.7064 | 23.0167 | 23.3712 | 23.6861 | 24.0275 | 24.3517 | 24.7564 | 25.169 | 25.6202 | 26.1 | 26.5788 | 27.0612 | 27.5562 | 28.0641 | 28.5852 | 29.1195 | 29.6674 | 30.2289 | 30.8044 | 31.3939
|  |  |  | Real Power |  |  | MW | 21.1744 | 22.9883 | 22.8141 | 22.5674 | 22.4306 | 22.2239 | 22.1058 | 22.1887 | 22.4918 | 22.8382 | 23.146 | 23.4796 | 23.7965 | 24.1919 | 24.5951 | 25.036 | 25.5049 | 25.9728 | 26.4441 | 26.9278 | 27.4242 | 27.9334 | 28.4555 | 28.9909 | 29.5396 | 30.102 | 30.6781
|  |  |  | Reactive Power |  |  | MVAr | 4.6009 |  | 4.9572 | 4.9036 | 4.8738 | 4.8289 | 4.8033 | 4.8213 | 4.8871 | 4.9624 | 5.0293 | 5.1018 | 5.1706 | 5.2565 | 5.3441 | 5.4399 | 5.5418 | 5.6435 | 5.7459 | 5.851 | 5.9589 | 6.0695 | 6.183 | 6.2993 | 6.4185 | 6.5407 | 6.6659
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9772 |  | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772
0.81285 | Diversity Factor: 0.81 | Uncompensated |  | Reactive Power |  |  | MVAr | 4.6009 | 4.995 | 4.9572 | 4.9036 | 4.8738 | 4.8289 | 4.8033 | 4.8213 | 4.8871 | 4.9624 | 5.0293 | 5.1018 | 5.1706 | 5.2565 | 5.3441 | 5.4399 | 5.5418 | 5.6435 | 5.7459 | 5.851 | 5.9589 | 6.0695 | 6.183 | 6.2993 | 6.4185 | 6.5407 | 6.6659
|  |  |  | PF |  |  |  | 0.9772 |  | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772 | 0.9772
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Beacon Hill 33_11kV
| Beacon Hill 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 1281 | 1290 | 1284 | 1346 | 1247 | 1291 | 988 |  | 1048.356 | 978.7755 | 932.8251 | 901.4585 | 890.8502 | 888.9475 | 896.5531 | 908.5783 | 918.8689 | 930.4445 | 938.9629 | 951.3031 | 963.6247 | 978.6263 | 995.1175 | 1011.264 | 1026.851 | 1042.826 | 1059.194 | 1075.962 | 1093.135 | 1110.718 | 1128.717 | 1147.139 | 1165.988 |  |  | Total | 0 | 0 | 0 | -4.1837 | 64.0224 | -90.1168 | 38.4915 | 47.9963 | -10.0552 | -8.8082 | -13.9448 | -10.9967 | -1.9733 | 7.8862 | 12.4589 | 10.6521 | 11.9723 | 8.8037 | 12.7441 | 12.714 | 15.4654 | 16.9841 | 16.6133 | 16.0226 | 16.4075 | 16.7978 | 17.1934 | 17.5944 | 18.001 | 18.4132 | 18.8311 | 19.2548
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 1400 |  | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 2841 |  | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 | 2841 |  |  | Beacon Hill 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | -4.1837 | 64.0224 | -90.1168 | 38.4915 | 47.9963 | -10.0552 | -8.8082 | -13.9448 | -10.9967 | -1.9733 | 7.8862 | 12.4589 | 10.6521 | 11.9723 | 8.8037 | 12.7441 | 12.714 | 15.4654 | 16.9841 | 16.6133 | 16.0226 | 16.4075 | 16.7978 | 17.1934 | 17.5944 | 18.001 | 18.4132 | 18.8311 | 19.2548
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4745 | -5.9545 | -13.6586 | -9.2375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6496. Beacon Hill to Belrose 11kV load transfer | Beacon Hill 33_11kV Tx2 | Belrose 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 68.9199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6496. Beacon Hill to Belrose 11kV load transfer | Beacon Hill 33_11kV Tx2 | Belrose 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 70.0801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6900. Load Transfer to relieve Dee Why West Zone as initial part of ION SI-10021 | Dee Why West 33_11kV Tx1 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 35.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6900. Load Transfer to relieve Dee Why West Zone as initial part of ION SI-10021 | Dee Why West 33_11kV Tx3 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 31.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6920. Augmentation to transfer load from Dee Why West Zone to Beacon Hill Zone initiated by ION SI-10021 | Dee Why West 33_11kV Tx1 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 21.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6920. Augmentation to transfer load from Dee Why West Zone to Beacon Hill Zone initiated by ION SI-10021 | Dee Why West 33_11kV Tx3 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7018. TERREY HILLS ZONE DEVELOPMENT | Belrose 33_11kV Tx1 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 7018. TERREY HILLS ZONE DEVELOPMENT | Belrose 33_11kV Tx2 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2010355. Replace 11kV OH mains of P10L ZN15011 Beacon Hill, On Frenchs Forest Rd East & Warringah Rd, Beacon Hill | Belrose 33_11kV Tx1 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 25.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010355. Replace 11kV OH mains of P10L ZN15011 Beacon Hill, On Frenchs Forest Rd East & Warringah Rd, Beacon Hill | Belrose 33_11kV Tx2 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 25.7129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5966 | 16.0051 | 21.8694 | 22.4275 | 23.3363 | 23.2309 | 23.11 | 23.4548 | 23.8043 | 24.1588 | 24.5181 | 24.8824 | 25.2518 | 25.6263 | 26.0059 | 26.3908 | 26.7811 | 27.1767 | 27.5777 | 27.9843 | 28.3965 | 28.8144 | 29.238
| 0 | [33 empty] | Energy Efficiency |  | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8129 | -2.1235 | -8.675 | -13.2461 | -20.3695 | -20.9674 | -11.8554 | -7.2959 | -8.9264 | -8.7804 | -11.7641 | -8.1782 | -8.5676 | -6.1805 | -5.0311 | -5.7764 | -6.7468 | -6.7468 | -6.7468 | -6.7468 | -6.7468 | -6.7468 | -6.7468 | -6.7468 | -6.7468
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | -4.1837 | -2.9776 | -2.1168 | -1.5085 | -2.1908 | -2.4573 | -2.7752 | -3.0452 | -3.2591 | -3.4334 | -3.5947 | -3.4761 | -3.5314 | -2.702 | -3.2365 | -3.2365 | -3.2365 | -3.2365 | -3.2365 | -3.2365 | -3.2365 | -3.2365 | -3.2365 | -3.2365 | -3.2365 | -3.2365 | -3.2365 | -3.2365 | -3.2365
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 4.225% |  | Rog Capped +/-5% | [59 empty] | Rog Capped +/-5%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Beacon Hill 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 988 | 1061 | 1048.356 | 978.7755 | 932.8251 | 901.4585 | 890.8502 | 888.9475 | 896.5531 | 908.5783 | 918.8689 | 930.4445 | 938.9629 | 951.3031 | 963.6247 | 978.6263 | 995.1175 | 1011.264 | 1026.851 | 1042.826 | 1059.194 | 1075.962 | 1093.135 | 1110.718 | 1128.717 | 1147.139 | 1165.988
|  |  |  | Apparent Power |  |  | MVA | 18.8239 |  | 19.9739 | 18.6482 | 17.7727 | 17.1751 | 16.973 | 16.9367 | 17.0816 | 17.3107 | 17.5068 | 17.7274 | 17.8896 | 18.1247 | 18.3595 | 18.6453 | 18.9595 | 19.2672 | 19.5641 | 19.8685 | 20.1804 | 20.4998 | 20.827 | 21.162 | 21.505 | 21.8559 | 22.2151
|  |  |  | Real Power |  |  | MW | 16.3768 | 17.5868 | 17.5635 | 16.5418 | 15.8646 | 15.401 | 15.244 | 15.2158 | 15.3284 | 15.5063 | 15.6585 | 15.8294 | 15.9551 | 16.1371 | 16.3187 | 16.5395 | 16.7821 | 17.0193 | 17.2481 | 17.4825 | 17.7223 | 17.9679 | 18.2191 | 18.4762 | 18.7391 | 19.008 | 19.283
|  |  |  | Reactive Power |  |  | MVAr | 9.2812 |  | 9.512 | 8.6096 | 8.0115 | 7.6021 | 7.4634 | 7.4385 | 7.538 | 7.6951 | 7.8295 | 7.9805 | 8.0915 | 8.2522 | 8.4126 | 8.6076 | 8.8219 | 9.0314 | 9.2335 | 9.4404 | 9.6523 | 9.8691 | 10.091 | 10.3181 | 10.5503 | 10.7878 | 11.0306
|  |  |  | Capacitors In Service |  |  | MVAr | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | PF |  |  |  | 0.87 |  | 0.87932 | 0.88704 | 0.89264 | 0.89671 | 0.89813 | 0.89839 | 0.89736 | 0.89576 | 0.89442 | 0.89294 | 0.89187 | 0.89034 | 0.88884 | 0.88706 | 0.88515 | 0.88333 | 0.88162 | 0.87991 | 0.8782 | 0.87649 | 0.87478 | 0.87308 | 0.87138 | 0.8697 | 0.86801
0.93751 | Diversity Factor: 0.94 | Uncompensated |  | Reactive Power |  |  | MVAr | 15.2812 | 15.9669 | 15.512 | 14.6096 | 14.0115 | 13.6021 | 13.4634 | 13.4385 | 13.538 | 13.6951 | 13.8295 | 13.9805 | 14.0915 | 14.2522 | 14.4126 | 14.6076 | 14.8218 | 15.0314 | 15.2335 | 15.4404 | 15.6523 | 15.8691 | 16.091 | 16.3181 | 16.5503 | 16.7878 | 17.0306
|  |  |  | PF |  |  |  | 0.73114 |  | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952 | 0.74952
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Belrose 33_11kV
| Belrose 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 1034 | 1247 | 1351 | 1406 | 1110 | 1426 | 1209 |  | 1171.348 | 1110.894 | 1073.282 | 1041.542 | 1035.836 | 1039.466 | 1052.106 | 1066.77 | 1079.878 | 1093.824 | 1106.978 | 1123.384 | 1140.062 | 1158.393 | 1177.89 | 1197.313 | 1216.794 | 1236.763 | 1257.227 | 1278.193 | 1299.669 | 1321.662 | 1344.18 | 1367.23 | 1390.821 |  |  | Total | 0 | 0 | 0 | -0.013122 | -0.012072 | 118.9953 | -0.003674 | -6.8434 | -5.6697 | -2.9739 | -15.0077 | -5.7062 | 3.6297 | 12.6402 | 14.6639 | 13.1081 | 13.9458 | 13.1542 | 16.4057 | 16.6785 | 18.3306 | 19.4976 | 19.4227 | 19.4812 | 19.969 | 20.4639 | 20.9662 | 21.4759 | 21.9931 | 22.5179 | 23.0504 | 23.5907
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2259 |  | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259 | 2259
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 3699 |  | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 | 3699 |  |  | Belrose 33_11kV Tx1 | 0 | 0 | 0 | -0.006506 | -0.0059856 | 59.001 | -0.0018217 | -3.3931 | -2.8112 | -1.4745 | -7.4412 | -2.8293 | 1.7997 | 6.2674 | 7.2708 | 6.4994 | 6.9147 | 6.5222 | 8.1344 | 8.2696 | 9.0888 | 9.6674 | 9.6303 | 9.6593 | 9.9011 | 10.1466 | 10.3956 | 10.6483 | 10.9047 | 11.165 | 11.429 | 11.6969
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Belrose 33_11kV Tx2 | 0 | 0 | 0 | -0.0066156 | -0.0060863 | 59.9943 | -0.0018524 | -3.4502 | -2.8585 | -1.4993 | -7.5665 | -2.8769 | 1.83 | 6.3729 | 7.3932 | 6.6088 | 7.0311 | 6.632 | 8.2713 | 8.4089 | 9.2418 | 9.8302 | 9.7924 | 9.8219 | 10.0678 | 10.3174 | 10.5706 | 10.8276 | 11.0883 | 11.3529 | 11.6214 | 11.8938
| Transformer Loads | [35 empty] | Belrose 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Belrose 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.055535 | -2.4514 | -2.9591 | -10.5483 | -5.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Belrose 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05647 | -2.4927 | -3.0089 | -10.7258 | -5.1085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6496. Beacon Hill to Belrose 11kV load transfer | Beacon Hill 33_11kV Tx2 | Belrose 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 68.9199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6496. Beacon Hill to Belrose 11kV load transfer | Beacon Hill 33_11kV Tx2 | Belrose 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 70.0801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6496. Beacon Hill to Belrose 11kV load transfer | Killarney 33_11kV Tx2 | Belrose 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 35.2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6496. Beacon Hill to Belrose 11kV load transfer | Killarney 33_11kV Tx2 | Belrose 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 35.7963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7018. TERREY HILLS ZONE DEVELOPMENT | Belrose 33_11kV Tx1 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7018. TERREY HILLS ZONE DEVELOPMENT | Belrose 33_11kV Tx2 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2009142. Establishment of S.17155 Optus Crozier, Crozier Road (Satellite Facility), Belrose and Decommission S.16298 Linden Crozier | Belrose 33_11kV Tx1 | Terrey Hills 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 19.8331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2009142. Establishment of S.17155 Optus Crozier, Crozier Road (Satellite Facility), Belrose and Decommission S.16298 Linden Crozier | Belrose 33_11kV Tx2 | Terrey Hills 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 20.1669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010355. Replace 11kV OH mains of P10L ZN15011 Beacon Hill, On Frenchs Forest Rd East & Warringah Rd, Beacon Hill | Belrose 33_11kV Tx1 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 25.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010355. Replace 11kV OH mains of P10L ZN15011 Beacon Hill, On Frenchs Forest Rd East & Warringah Rd, Beacon Hill | Belrose 33_11kV Tx2 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 25.7129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013100. Redevelopment - Belrose Shopping Centre, Establish S.63568 GLEN GLENROSE No.1, establish S.63569 GLEN GLENROSE No.2 and decommission S.16613 GLENROSE SHOPS, 56-58 Glen Street, Belrose |  | Belrose 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013100. Redevelopment - Belrose Shopping Centre, Establish S.63568 GLEN GLENROSE No.1, establish S.63569 GLEN GLENROSE No.2 and decommission S.16613 GLENROSE SHOPS, 56-58 Glen Street, Belrose |  | Belrose 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.9566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Belrose 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2205 | 9.2434 | 11.7795 | 12.1625 | 12.82 | 12.6881 | 12.542 | 12.7569 | 12.9751 | 13.1965 | 13.4212 | 13.6492 | 13.8806 | 14.1155 | 14.3538 | 14.5956 | 14.8411 | 15.0901 | 15.3428 | 15.5992 | 15.8595 | 16.1235 | 16.3914
[35 empty] | Econometric |  | Belrose 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3084 | 9.3991 | 11.9778 | 12.3673 | 13.0358 | 12.9017 | 12.7531 | 12.9717 | 13.1935 | 13.4187 | 13.6471 | 13.879 | 14.1143 | 14.3531 | 14.5954 | 14.8414 | 15.0909 | 15.3441 | 15.6011 | 15.8619 | 16.1264 | 16.3949 | 16.6673
| 0 | [33 empty] | Energy Efficiency |  | Belrose 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.60807 | -0.35703 | -3.7328 | -6.133 | -9.5813 | -10.359 | -6.5486 | -5.4134 | -6.0386 | -5.8392 | -6.4492 | -5.0585 | -5.1479 | -4.5568 | -4.2096 | -4.4816 | -4.6909 | -4.6909 | -4.6909 | -4.6909 | -4.6909 | -4.6909 | -4.6909 | -4.6909 | -4.6909
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Belrose 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.61831 | -0.36304 | -3.7956 | -6.2362 | -9.7426 | -10.5333 | -6.6588 | -5.5045 | -6.1403 | -5.9375 | -6.5578 | -5.1436 | -5.2346 | -4.6335 | -4.2804 | -4.557 | -4.7698 | -4.7698 | -4.7698 | -4.7698 | -4.7698 | -4.7698 | -4.7698 | -4.7698 | -4.7698
[35 empty] | Solar PV |  | Belrose 33_11kV Tx1 | 0 | 0 | 0 | -0.006506 | -0.0059856 | -0.0023422 | -0.0018217 | -0.0024698 | -0.0027702 | -0.0031287 | -0.003433 | -0.0036741 | -0.0038707 | -0.0040525 | -0.0039188 | -0.0039811 | -0.0030462 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487 | -0.0036487
[35 empty] | Solar PV |  | Belrose 33_11kV Tx2 | 0 | 0 | 0 | -0.0066156 | -0.0060863 | -0.0023816 | -0.0018524 | -0.0025114 | -0.0028169 | -0.0031813 | -0.0034908 | -0.003736 | -0.0039358 | -0.0041207 | -0.0039848 | -0.0040481 | -0.0030974 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101 | -0.0037101
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 1.052% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95323 | 0.90865 | 0.88032 | 0.86659 | 0.86659 | 0.86659 | 0.86659 | 0.86659 | 0.86659 | 0.86659 | -4.677% | -4.677% | -3.118% | -1.559% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Belrose 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1209 | 1236 | 1171.348 | 1110.894 | 1073.282 | 1041.542 | 1035.836 | 1039.466 | 1052.106 | 1066.77 | 1079.878 | 1093.824 | 1106.978 | 1123.384 | 1140.062 | 1158.393 | 1177.89 | 1197.313 | 1216.794 | 1236.763 | 1257.227 | 1278.193 | 1299.669 | 1321.662 | 1344.18 | 1367.23 | 1390.821
|  |  |  | Apparent Power |  |  | MVA | 23.0345 |  | 22.3172 | 21.1654 | 20.4488 | 19.844 | 19.7353 | 19.8045 | 20.0453 | 20.3247 | 20.5744 | 20.8401 | 21.0908 | 21.4033 | 21.7211 | 22.0704 | 22.4418 | 22.8119 | 23.1831 | 23.5635 | 23.9534 | 24.3529 | 24.762 | 25.181 | 25.6101 | 26.0492 | 26.4987
|  |  |  | Real Power |  |  | MW | 20.9614 | 21.4296 | 20.3086 | 19.2605 | 18.6084 | 18.0581 | 17.9592 | 18.0221 | 18.2412 | 18.4955 | 18.7227 | 18.9645 | 19.1926 | 19.477 | 19.7662 | 20.084 | 20.4221 | 20.7588 | 21.0966 | 21.4428 | 21.7976 | 22.1611 | 22.5334 | 22.9148 | 23.3052 | 23.7048 | 24.1138
|  |  |  | Reactive Power |  |  | MVAr | 9.5503 |  | 9.2529 | 8.7753 | 8.4782 | 8.2275 | 8.1824 | 8.2111 | 8.311 | 8.4268 | 8.5303 | 8.6405 | 8.7444 | 8.874 | 9.0058 | 9.1506 | 9.3046 | 9.458 | 9.6119 | 9.7696 | 9.9313 | 10.0969 | 10.2665 | 10.4403 | 10.6181 | 10.8002 | 10.9866
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.91 |  | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
0.83208 | Diversity Factor: 0.83 | Uncompensated |  | Reactive Power |  |  | MVAr | 9.5503 | 9.7636 | 9.2529 | 8.7753 | 8.4782 | 8.2275 | 8.1824 | 8.2111 | 8.311 | 8.4268 | 8.5303 | 8.6405 | 8.7444 | 8.874 | 9.0058 | 9.1506 | 9.3046 | 9.458 | 9.6119 | 9.7696 | 9.9313 | 10.0969 | 10.2665 | 10.4403 | 10.6181 | 10.8002 | 10.9866
|  |  |  | PF |  |  |  | 0.91 |  | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Brookvale 33_11kV
| Brookvale 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 2403 | 2485 | 2366 | 2602 | 2333 | 2305.118 | 2087 |  | 1996.011 | 2105.146 | 2011.46 | 1953.41 | 1939.511 | 1937.658 | 1954.003 | 1979.844 | 2002.29 | 2026.395 | 2043.966 | 2068.939 | 2093.676 | 2124.041 | 2157.354 | 2189.846 | 2220.878 | 2252.548 | 2284.864 | 2317.835 | 2351.47 | 2385.777 | 2420.766 | 2456.445 | 2492.823 |  |  | Total | 0 | -152 | 0 | 66.385 | -3.8509 | 6.1297 | -1.9866 | 98.7007 | 230.5626 | -13.3587 | -19.9036 | -14.3054 | -1.9085 | 16.8247 | 26.5816 | 23.0727 | 24.763 | 18.0391 | 25.6261 | 25.3672 | 31.1176 | 34.1137 | 33.2486 | 31.733 | 32.3647 | 33.0048 | 33.6534 | 34.3105 | 34.9763 | 35.6509 | 36.3343 | 37.0268
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2852 |  | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 4596 |  | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 | 4596 |  |  | Brookvale 33_11kV Tx1 | 0 | -143 | 0 | -2.1881 | -1.5007 | -1.5082 | 22.2258 | 66.0446 | -26.3073 | -5.2057 | -7.7562 | -5.5747 | -0.74373 | 6.5564 | 10.3585 | 8.9912 | 9.6499 | 7.0296 | 9.9862 | 9.8853 | 12.1262 | 13.2937 | 12.9566 | 12.366 | 12.6122 | 12.8616 | 13.1143 | 13.3704 | 13.6299 | 13.8927 | 14.1591 | 14.4289
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Brookvale 33_11kV Tx2 | 0 | -4.5479 | 0 | 34.6519 | -1.1877 | 3.8596 | -0.61268 | 16.502 | 129.8034 | -4.1199 | -6.1384 | -4.4119 | -0.5886 | 5.1889 | 8.1979 | 7.1158 | 7.6371 | 5.5634 | 7.9033 | 7.8234 | 9.5969 | 10.5209 | 10.2541 | 9.7867 | 9.9815 | 10.1789 | 10.3789 | 10.5816 | 10.7869 | 10.995 | 11.2058 | 11.4193
| Transformer Loads | [35 empty] | Brookvale 33_11kV Tx3 | 0 | -4.4521 | 0 | 33.9212 | -1.1626 | 3.7783 | -23.5998 | 16.1541 | 127.0666 | -4.033 | -6.009 | -4.3189 | -0.57619 | 5.0794 | 8.0251 | 6.9658 | 7.4761 | 5.4461 | 7.7366 | 7.6585 | 9.3946 | 10.2991 | 10.0379 | 9.5803 | 9.7711 | 9.9643 | 10.1601 | 10.3585 | 10.5595 | 10.7631 | 10.9695 | 11.1785
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Brookvale 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8689 | -3.0736 | -7.5328 | -4.6933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2705 | -2.4325 | -5.9616 | -3.7144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2227 | -2.3812 | -5.8359 | -3.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6224. RELIEF OF SWITCHING CONSTRAINTS, BROOKVALE PANEL 4, 10L & 17 FEEDERS | Brookvale 33_11kV Tx1 | Brookvale 33_11kV Tx2 | 0 | 72.2618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6224. RELIEF OF SWITCHING CONSTRAINTS, BROOKVALE PANEL 4, 10L & 17 FEEDERS | Brookvale 33_11kV Tx1 | Brookvale 33_11kV Tx3 | 0 | 70.7382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6288. Change of open points due to progressive completion of Harbord Switchgear Replacement | Brookvale 33_11kV Tx2 | Harbord 33_11kV Tx1 | 0 | 76.8097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6288. Change of open points due to progressive completion of Harbord Switchgear Replacement | Brookvale 33_11kV Tx3 | Harbord 33_11kV Tx1 | 0 | 75.1903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7035. Brookvale Zone Development | Brookvale 33_11kV Tx1 | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 7035. Brookvale Zone Development | Brookvale 33_11kV Tx3 | Brookvale 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2006519. Establishment of S.17043 Sturdee Pittwater, 834 Pittwater Rd, Dee Why |  | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | 36.3836 | 0 | 0 | 0 | 0 | 38.0764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006519. Establishment of S.17043 Sturdee Pittwater, 834 Pittwater Rd, Dee Why |  | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 35.6164 | 0 | 0 | 0 | 0 | 37.2736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012031. Move O/P on S.16418 WARRINGAH MALL CINEMA | Harbord 33_11kV Tx2 | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 5.0533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2012031. Move O/P on S.16418 WARRINGAH MALL CINEMA | Harbord 33_11kV Tx2 | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 4.9467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013186. Westfield Warringah Mall redevelopment Stage 1 proposal of 3MVA (existing car park conversion to retail etc + new car park) Stage 2 proposal 4MVA (extension to shopping mall + new car park) Stage 1 - Establish S.64170 C |  | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2289 | 96.4417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013186. Westfield Warringah Mall redevelopment Stage 1 proposal of 3MVA (existing car park conversion to retail etc + new car park) Stage 2 proposal 4MVA (extension to shopping mall + new car park) Stage 1 - Establish S.64170 C |  | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.9711 | 94.4083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013186. Westfield Warringah Mall redevelopment Stage 1 proposal of 3MVA (existing car park conversion to retail etc + new car park) Stage 2 proposal 4MVA (extension to shopping mall + new car park) Stage 1 - Establish S.64170 C |  | Brookvale 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5 | -20.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013453. New KL S.61621 Pittwater St David | Dee Why West 33_11kV Tx1 | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013453. New KL S.61621 Pittwater St David | Dee Why West 33_11kV Tx1 | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013453. New KL S.61621 Pittwater St David | Dee Why West 33_11kV Tx3 | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013453. New KL S.61621 Pittwater St David | Dee Why West 33_11kV Tx3 | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Brookvale 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6231 | 10.7858 | 15.2637 | 15.6312 | 16.2332 | 16.1465 | 16.0513 | 16.2729 | 16.4975 | 16.725 | 16.9556 | 17.1891 | 17.4258 | 17.6656 | 17.9086 | 18.1548 | 18.4042 | 18.657 | 18.913 | 19.1725 | 19.4354 | 19.7017 | 19.9715
| Diversity Factor: 0 | [33 empty] | Econometric |  | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4502 | 8.5361 | 12.08 | 12.3708 | 12.8472 | 12.7786 | 12.7033 | 12.8787 | 13.0564 | 13.2365 | 13.4189 | 13.6038 | 13.7911 | 13.9809 | 14.1732 | 14.368 | 14.5655 | 14.7655 | 14.9681 | 15.1735 | 15.3815 | 15.5923 | 15.8058
[35 empty] | Econometric |  | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3564 | 8.3561 | 11.8253 | 12.11 | 12.5764 | 12.5092 | 12.4355 | 12.6072 | 12.7811 | 12.9574 | 13.136 | 13.317 | 13.5003 | 13.6861 | 13.8744 | 14.0651 | 14.2583 | 14.4542 | 14.6525 | 14.8535 | 15.0572 | 15.2635 | 15.4726
[35 empty] | Energy Efficiency |  | Brookvale 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3796 | -1.8818 | -6.3924 | -9.514 | -14.5447 | -14.6889 | -7.9116 | -4.081 | -5.3261 | -5.2962 | -7.8786 | -5.1496 | -5.481 | -3.4737 | -2.5428 | -3.1198 | -3.9534 | -3.9534 | -3.9534 | -3.9534 | -3.9534 | -3.9534 | -3.9534 | -3.9534 | -3.9534
| 0 | [33 empty] | Energy Efficiency |  | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4661 | -1.4893 | -5.0591 | -7.5295 | -11.511 | -11.6251 | -6.2614 | -3.2298 | -4.2152 | -4.1915 | -6.2353 | -4.0755 | -4.3377 | -2.7491 | -2.0125 | -2.469 | -3.1288 | -3.1288 | -3.1288 | -3.1288 | -3.1288 | -3.1288 | -3.1288 | -3.1288 | -3.1288
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.393 | -1.4579 | -4.9524 | -7.3708 | -11.2683 | -11.38 | -6.1294 | -3.1617 | -4.1263 | -4.1032 | -6.1038 | -3.9895 | -4.2463 | -2.6912 | -1.97 | -2.417 | -3.0628 | -3.0628 | -3.0628 | -3.0628 | -3.0628 | -3.0628 | -3.0628 | -3.0628 | -3.0628
[35 empty] | Solar PV |  | Brookvale 33_11kV Tx1 | 0 | 0 | 0 | -2.1881 | -1.5007 | -1.5082 | -0.77416 | -1.0758 | -1.2066 | -1.3628 | -1.4953 | -1.6003 | -1.6859 | -1.7651 | -1.7069 | -1.7341 | -1.3268 | -1.5893 | -1.5893 | -1.5893 | -1.5893 | -1.5893 | -1.5893 | -1.5893 | -1.5893 | -1.5893 | -1.5893 | -1.5893 | -1.5893 | -1.5893 | -1.5893 | -1.5893
[35 empty] | Solar PV |  | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | -1.7317 | -1.1877 | -1.1936 | -0.61268 | -0.85138 | -0.95495 | -1.0785 | -1.1834 | -1.2665 | -1.3343 | -1.397 | -1.3509 | -1.3724 | -1.0501 | -1.2578 | -1.2578 | -1.2578 | -1.2578 | -1.2578 | -1.2578 | -1.2578 | -1.2578 | -1.2578 | -1.2578 | -1.2578 | -1.2578 | -1.2578 | -1.2578 | -1.2578
| 0 | [33 empty] | Solar PV |  | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | -1.6952 | -1.1626 | -1.1685 | -0.59977 | -0.83343 | -0.93481 | -1.0558 | -1.1585 | -1.2398 | -1.3062 | -1.3675 | -1.3224 | -1.3434 | -1.0279 | -1.2313 | -1.2313 | -1.2313 | -1.2313 | -1.2313 | -1.2313 | -1.2313 | -1.2313 | -1.2313 | -1.2313 | -1.2313 | -1.2313 | -1.2313 | -1.2313 | -1.2313
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0.5868% |  | Rog Capped +/-5% | [59 empty] | Rog Capped +/-5%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Brookvale 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 2087 | 2016 | 1996.011 | 2105.146 | 2011.46 | 1953.41 | 1939.511 | 1937.658 | 1954.003 | 1979.844 | 2002.29 | 2026.395 | 2043.966 | 2068.939 | 2093.676 | 2124.041 | 2157.354 | 2189.846 | 2220.878 | 2252.548 | 2284.864 | 2317.835 | 2351.47 | 2385.777 | 2420.766 | 2456.445 | 2492.823
|  |  |  | Apparent Power |  |  | MVA | 39.7627 |  | 38.0291 | 40.1084 | 38.3235 | 37.2175 | 36.9527 | 36.9173 | 37.2288 | 37.7211 | 38.1487 | 38.608 | 38.9428 | 39.4186 | 39.8899 | 40.4684 | 41.1031 | 41.7222 | 42.3134 | 42.9168 | 43.5325 | 44.1607 | 44.8015 | 45.4552 | 46.1218 | 46.8016 | 47.4947
|  |  |  | Real Power |  |  | MW | 34.4615 | 33.2891 | 33.0693 | 34.6314 | 33.2907 | 32.4582 | 32.2587 | 32.2321 | 32.4668 | 32.8375 | 33.1593 | 33.5046 | 33.7562 | 34.1136 | 34.4674 | 34.9014 | 35.3772 | 35.8409 | 36.2834 | 36.7348 | 37.1951 | 37.6645 | 38.143 | 38.6308 | 39.128 | 39.6347 | 40.1511
|  |  |  | Reactive Power |  |  | MVAr | 19.8362 |  | 18.7786 | 20.2325 | 18.9847 | 18.2099 | 18.0242 | 17.9994 | 18.2178 | 18.5629 | 18.8624 | 19.1838 | 19.418 | 19.7506 | 20.0799 | 20.4838 | 20.9266 | 21.3582 | 21.7701 | 22.1902 | 22.6186 | 23.0555 | 23.5009 | 23.9549 | 24.4176 | 24.8893 | 25.3699
|  |  |  | Capacitors In Service |  |  | MVAr | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
|  |  |  | PF |  |  |  | 0.86668 |  | 0.86958 | 0.86344 | 0.86868 | 0.87212 | 0.87297 | 0.87309 | 0.87209 | 0.87053 | 0.86921 | 0.86782 | 0.86682 | 0.86542 | 0.86406 | 0.86243 | 0.86069 | 0.85904 | 0.85749 | 0.85595 | 0.85442 | 0.85289 | 0.85138 | 0.84986 | 0.84836 | 0.84687 | 0.84538
0.80778 | Diversity Factor: 0.81 | Uncompensated |  | Reactive Power |  |  | MVAr | 31.8362 | 31.1614 | 30.7786 | 32.2325 | 30.9847 | 30.2099 | 30.0242 | 29.9994 | 30.2178 | 30.5629 | 30.8624 | 31.1838 | 31.418 | 31.7506 | 32.0799 | 32.4838 | 32.9266 | 33.3582 | 33.7701 | 34.1902 | 34.6187 | 35.0555 | 35.5009 | 35.9549 | 36.4176 | 36.8893 | 37.3699
|  |  |  | PF |  |  |  | 0.73453 |  | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732 | 0.732
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Dee Why West 33_11kV
| Dee Why West 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 1639 | 1685 | 2002 | 2058 | 1648 | 1977 | 1426 |  | 1637.462 | 1592.193 | 1564.846 | 1530.432 | 1526.237 | 1535.534 | 1560.457 | 1588.982 | 1614.413 | 1641.225 | 1666.136 | 1696.591 | 1727.435 | 1761.368 | 1797.356 | 1833.174 | 1868.924 | 1905.48 | 1942.855 | 1981.06 | 2020.108 | 2060.01 | 2100.778 | 2142.425 | 2184.965 |  |  | Total | 0 | 0 | 108 | -2.5026 | -52.6126 | -0.003674 | -26.5047 | 44.6532 | -9.8746 | -4.4025 | -23.1385 | -4.1953 | 9.297 | 24.9228 | 28.525 | 25.4317 | 26.8114 | 24.9111 | 30.4548 | 30.8449 | 33.9322 | 35.988 | 35.8184 | 35.7494 | 36.5564 | 37.375 | 38.2053 | 39.0475 | 39.9019 | 40.7685 | 41.6475 | 42.539
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2805 |  | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805 | 2805
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 4735 |  | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 | 4735 |  |  | Dee Why West 33_11kV Tx1 | 0 | 0 | 56.7905 | -1.3159 | -27.6657 | -0.001932 | -13.9372 | 23.4804 | -5.1924 | -2.315 | -12.1671 | -2.2061 | 4.8887 | 13.1054 | 14.9995 | 13.3729 | 14.0985 | 13.0992 | 16.0143 | 16.2194 | 17.8428 | 18.9239 | 18.8347 | 18.7984 | 19.2227 | 19.6532 | 20.0898 | 20.5327 | 20.9819 | 21.4376 | 21.8998 | 22.3686
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Dee Why West 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Dee Why West 33_11kV Tx3 | 0 | 0 | 51.2095 | -1.1866 | -24.9469 | -0.0017421 | -12.5675 | 21.1729 | -4.6822 | -2.0875 | -10.9714 | -1.9893 | 4.4083 | 11.8175 | 13.5255 | 12.0587 | 12.713 | 11.8119 | 14.4405 | 14.6255 | 16.0894 | 17.0642 | 16.9837 | 16.951 | 17.3337 | 17.7218 | 18.1155 | 18.5149 | 18.92 | 19.3309 | 19.7476 | 20.1704
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Dee Why West 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.49186 | -4.1919 | -4.8617 | -18.2039 | -7.4868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Dee Why West 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.44353 | -3.78 | -4.3839 | -16.415 | -6.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5778. Network Augmentation in the Vicinity of the Dee Why / Narrabeen Zone Boundary (Connections for DNPs 5775 & 5776) | Narrabeen 33_11kV Tx2 | Dee Why West 33_11kV Tx1 | 0 | 0 | 56.7905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5778. Network Augmentation in the Vicinity of the Dee Why / Narrabeen Zone Boundary (Connections for DNPs 5775 & 5776) | Narrabeen 33_11kV Tx2 | Dee Why West 33_11kV Tx3 | 0 | 0 | 51.2095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6900. Load Transfer to relieve Dee Why West Zone as initial part of ION SI-10021 | Dee Why West 33_11kV Tx1 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 35.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6900. Load Transfer to relieve Dee Why West Zone as initial part of ION SI-10021 | Dee Why West 33_11kV Tx3 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 31.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6920. Augmentation to transfer load from Dee Why West Zone to Beacon Hill Zone initiated by ION SI-10021 | Dee Why West 33_11kV Tx1 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 21.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6920. Augmentation to transfer load from Dee Why West Zone to Beacon Hill Zone initiated by ION SI-10021 | Dee Why West 33_11kV Tx3 | Beacon Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2006272. Establish customer sub, S.17009 Dee Why Clarence, 8 Dee why Pde, Dee Why. |  | Dee Why West 33_11kV Tx1 | 0 | 0 | 0 | 0 | 7.5721 | 0 | 0 | 8.6763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2006272. Establish customer sub, S.17009 Dee Why Clarence, 8 Dee why Pde, Dee Why. |  | Dee Why West 33_11kV Tx3 | 0 | 0 | 0 | 0 | 6.8279 | 0 | 0 | 7.8237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010653. Establishment of S.47135 Homestead Pittwater, 8 Homestead Ave, Collaroy - Customer Funded |  | Dee Why West 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0988 | 12.4361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010653. Establishment of S.47135 Homestead Pittwater, 8 Homestead Ave, Collaroy - Customer Funded |  | Dee Why West 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4012 | 11.2139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013453. New KL S.61621 Pittwater St David |  | Dee Why West 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013453. New KL S.61621 Pittwater St David |  | Dee Why West 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013453. New KL S.61621 Pittwater St David | Dee Why West 33_11kV Tx1 | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013453. New KL S.61621 Pittwater St David | Dee Why West 33_11kV Tx1 | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013453. New KL S.61621 Pittwater St David | Dee Why West 33_11kV Tx3 | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013453. New KL S.61621 Pittwater St David | Dee Why West 33_11kV Tx3 | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Dee Why West 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3243 | 16.9095 | 22.1225 | 22.9098 | 24.3393 | 23.8826 | 23.398 | 23.7763 | 24.1602 | 24.5496 | 24.9446 | 25.3453 | 25.7518 | 26.1642 | 26.5825 | 27.0068 | 27.4372 | 27.8739 | 28.3167 | 28.766 | 29.2217 | 29.6839 | 30.1527
[35 empty] | Econometric |  | Dee Why West 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.408 | 15.2477 | 19.9485 | 20.6584 | 21.9474 | 21.5356 | 21.0986 | 21.4398 | 21.7859 | 22.137 | 22.4932 | 22.8545 | 23.2211 | 23.5929 | 23.9701 | 24.3528 | 24.7409 | 25.1346 | 25.534 | 25.9391 | 26.35 | 26.7667 | 27.1895
| 0 | [33 empty] | Energy Efficiency |  | Dee Why West 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6653 | -0.85636 | -6.6148 | -10.694 | -16.6507 | -17.8197 | -11.0231 | -8.6792 | -9.8179 | -9.5194 | -10.8711 | -8.3454 | -8.5353 | -7.3126 | -6.6381 | -7.1397 | -7.5942 | -7.5942 | -7.5942 | -7.5942 | -7.5942 | -7.5942 | -7.5942 | -7.5942 | -7.5942
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Dee Why West 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5017 | -0.7722 | -5.9647 | -9.6431 | -15.0144 | -16.0685 | -9.9398 | -7.8263 | -8.8531 | -8.5839 | -9.8028 | -7.5253 | -7.6965 | -6.594 | -5.9857 | -6.438 | -6.8479 | -6.8479 | -6.8479 | -6.8479 | -6.8479 | -6.8479 | -6.8479 | -6.8479 | -6.8479
[35 empty] | Solar PV |  | Dee Why West 33_11kV Tx1 | 0 | 0 | 0 | -1.3159 | -0.0066238 | -0.001932 | -0.0024839 | -0.1285 | -0.14414 | -0.16279 | -0.17862 | -0.19117 | -0.20139 | -0.21085 | -0.2039 | -0.20714 | -0.15849 | -0.18984 | -0.18984 | -0.18984 | -0.18984 | -0.18984 | -0.18984 | -0.18984 | -0.18984 | -0.18984 | -0.18984 | -0.18984 | -0.18984 | -0.18984 | -0.18984 | -0.18984
[35 empty] | Solar PV |  | Dee Why West 33_11kV Tx3 | 0 | 0 | 0 | -1.1866 | -0.0059729 | -0.0017421 | -0.0022398 | -0.11588 | -0.12997 | -0.14679 | -0.16107 | -0.17238 | -0.1816 | -0.19013 | -0.18386 | -0.18678 | -0.14292 | -0.17119 | -0.17119 | -0.17119 | -0.17119 | -0.17119 | -0.17119 | -0.17119 | -0.17119 | -0.17119 | -0.17119 | -0.17119 | -0.17119 | -0.17119 | -0.17119 | -0.17119
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 4.032% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.97839 | 0.95725 | 0.94345 | 0.93666 | 0.93666 | 0.93666 | 0.93666 | 0.93666 | 0.93666 | 0.93666 | -2.161% | -2.161% | -1.441% | -0.72% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Dee Why West 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1426 | 1628 | 1637.462 | 1592.193 | 1564.846 | 1530.432 | 1526.237 | 1535.534 | 1560.457 | 1588.982 | 1614.413 | 1641.225 | 1666.136 | 1696.591 | 1727.435 | 1761.368 | 1797.356 | 1833.174 | 1868.924 | 1905.48 | 1942.855 | 1981.06 | 2020.108 | 2060.01 | 2100.778 | 2142.425 | 2184.965
|  |  |  | Apparent Power |  |  | MVA | 27.1689 |  | 31.1978 | 30.3353 | 29.8143 | 29.1587 | 29.0787 | 29.2558 | 29.7307 | 30.2742 | 30.7587 | 31.2695 | 31.7442 | 32.3244 | 32.9121 | 33.5586 | 34.2442 | 34.9267 | 35.6078 | 36.3043 | 37.0164 | 37.7443 | 38.4882 | 39.2485 | 40.0252 | 40.8187 | 41.6292
|  |  |  | Real Power |  |  | MW | 25.2671 | 28.8463 | 29.014 | 28.2119 | 27.7273 | 27.1176 | 27.0432 | 27.2079 | 27.6496 | 28.155 | 28.6056 | 29.0807 | 29.5221 | 30.0617 | 30.6082 | 31.2095 | 31.8471 | 32.4818 | 33.1152 | 33.763 | 34.4252 | 35.1022 | 35.794 | 36.5011 | 37.2234 | 37.9614 | 38.7151
|  |  |  | Reactive Power |  |  | MVAr | 9.9862 |  | 11.4671 | 11.15 | 10.9585 | 10.7175 | 10.6882 | 10.7533 | 10.9278 | 11.1276 | 11.3056 | 11.4934 | 11.6679 | 11.8811 | 12.0971 | 12.3348 | 12.5868 | 12.8376 | 13.088 | 13.344 | 13.6057 | 13.8733 | 14.1467 | 14.4261 | 14.7116 | 15.0033 | 15.3012
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.93 |  | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93
0.9314 | Diversity Factor: 0.93 | Uncompensated |  | Reactive Power |  |  | MVAr | 9.9862 | 11.4008 | 11.4671 | 11.15 | 10.9585 | 10.7175 | 10.6882 | 10.7533 | 10.9278 | 11.1276 | 11.3056 | 11.4934 | 11.6679 | 11.8811 | 12.0971 | 12.3348 | 12.5868 | 12.8376 | 13.088 | 13.344 | 13.6057 | 13.8733 | 14.1467 | 14.4261 | 14.7116 | 15.0033 | 15.3012
|  |  |  | PF |  |  |  | 0.93 |  | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Harbord 33_11kV
| Harbord 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 1147 | 1415 | 1433 | 1479 | 1278 | 959 | 728 |  | 815.0592 | 797.8014 | 788.7677 | 770.9825 | 771.2336 | 777.4285 | 790.8139 | 804.8267 | 817.3687 | 830.6835 | 843.9003 | 859.4967 | 875.4156 | 892.3595 | 910.1494 | 927.9899 | 946.0794 | 964.6073 | 983.5801 | 1003.004 | 1022.886 | 1043.234 | 1064.053 | 1085.35 | 1107.133 |  |  | Total | 436 | 152 | 0 | -0.010497 | -225.01 | -302.0031 | -0.0031492 | -0.097599 | -2.6818 | 0.47781 | -13.0833 | 0.25108 | 6.1949 | 13.3853 | 14.0128 | 12.542 | 13.3149 | 13.2167 | 15.5964 | 15.9189 | 16.9439 | 17.7899 | 17.8406 | 18.0894 | 18.5279 | 18.9728 | 19.4243 | 19.8825 | 20.3473 | 20.819 | 21.2975 | 21.7831
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 1956 |  | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 3870 |  | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 |  |  | Harbord 33_11kV Tx1 | 330 | 152 | 0 | -0.0042275 | -225.004 | -165.0013 | -0.0012682 | -0.039305 | -1.08 | 0.19242 | -5.2689 | 0.10112 | 2.4948 | 5.3906 | 5.6433 | 5.0509 | 5.3622 | 5.3227 | 6.281 | 6.4109 | 6.8237 | 7.1644 | 7.1848 | 7.285 | 7.4616 | 7.6408 | 7.8226 | 8.0071 | 8.1943 | 8.3842 | 8.577 | 8.7725
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Harbord 33_11kV Tx2 | 106 | 0 | 0 | -0.0062698 | -0.0059563 | -137.0019 | -0.0018809 | -0.058294 | -1.6018 | 0.28539 | -7.8144 | 0.14996 | 3.7001 | 7.9948 | 8.3696 | 7.4911 | 7.9527 | 7.8941 | 9.3154 | 9.508 | 10.1202 | 10.6255 | 10.6558 | 10.8044 | 11.0663 | 11.3321 | 11.6017 | 11.8754 | 12.153 | 12.4347 | 12.7206 | 13.0106
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Harbord 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.036573 | -1.0024 | -1.3996 | -8.3082 | -2.6404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Harbord 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.054242 | -1.4866 | -2.0758 | -12.322 | -3.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6132. Relief of Balgowlah Zone Substation | Balgowlah 33_11kV Tx1 | Harbord 33_11kV Tx1 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6132. Relief of Balgowlah Zone Substation | Balgowlah 33_11kV Tx1 | Harbord 33_11kV Tx2 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6132. Relief of Balgowlah Zone Substation | Balgowlah 33_11kV Tx2 | Harbord 33_11kV Tx1 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6132. Relief of Balgowlah Zone Substation | Balgowlah 33_11kV Tx2 | Harbord 33_11kV Tx2 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6288. Change of open points due to progressive completion of Harbord Switchgear Replacement | Brookvale 33_11kV Tx2 | Harbord 33_11kV Tx1 | 0 | 76.8097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6288. Change of open points due to progressive completion of Harbord Switchgear Replacement | Brookvale 33_11kV Tx3 | Harbord 33_11kV Tx1 | 0 | 75.1903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6475. S.36300 Balgowlah North 132/33/11 kV Hybrid Zone - 11 kV Development Works | Harbord 33_11kV Tx1 | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 225 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6475. S.36300 Balgowlah North 132/33/11 kV Hybrid Zone - 11 kV Development Works | Harbord 33_11kV Tx2 | Balgowlah North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012031. Move O/P on S.16418 WARRINGAH MALL CINEMA | Harbord 33_11kV Tx2 | Brookvale 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 5.0533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012031. Move O/P on S.16418 WARRINGAH MALL CINEMA | Harbord 33_11kV Tx2 | Brookvale 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 4.9467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Harbord 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8339 | 6.8292 | 8.6959 | 9.0454 | 9.6824 | 9.4594 | 9.2233 | 9.3803 | 9.5397 | 9.7014 | 9.8655 | 10.032 | 10.201 | 10.3725 | 10.5465 | 10.7231 | 10.9023 | 11.0841 | 11.2686 | 11.4558 | 11.6458 | 11.8385 | 12.0341
| Diversity Factor: 0 | [33 empty] | Econometric |  | Harbord 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6861 | 10.1285 | 12.897 | 13.4153 | 14.3601 | 14.0294 | 13.6791 | 13.912 | 14.1484 | 14.3882 | 14.6316 | 14.8786 | 15.1292 | 15.3836 | 15.6417 | 15.9036 | 16.1693 | 16.439 | 16.7126 | 16.9902 | 17.272 | 17.5578 | 17.8478
[35 empty] | Energy Efficiency |  | Harbord 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0010978 | -0.075804 | -2.2397 | -3.7876 | -5.9519 | -6.548 | -4.2892 | -3.8136 | -4.1697 | -4.0161 | -4.2146 | -3.418 | -3.4522 | -3.206 | -3.0342 | -3.1853 | -3.2591 | -3.2591 | -3.2591 | -3.2591 | -3.2591 | -3.2591 | -3.2591 | -3.2591 | -3.2591
[35 empty] | Energy Efficiency |  | Harbord 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0016282 | -0.11243 | -3.3218 | -5.6175 | -8.8274 | -9.7114 | -6.3613 | -5.656 | -6.1842 | -5.9563 | -6.2507 | -5.0692 | -5.12 | -4.7548 | -4.5001 | -4.7242 | -4.8337 | -4.8337 | -4.8337 | -4.8337 | -4.8337 | -4.8337 | -4.8337 | -4.8337 | -4.8337
| 0 | [33 empty] | Solar PV |  | Harbord 33_11kV Tx1 | 0 | 0 | 0 | -0.0042275 | -0.0040161 | -0.0012682 | -0.0012682 | -0.0016344 | -0.0018332 | -0.0020704 | -0.0022718 | -0.0024314 | -0.0025614 | -0.0026818 | -0.0025933 | -0.0026345 | -0.0020158 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146 | -0.0024146
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Harbord 33_11kV Tx2 | 0 | 0 | 0 | -0.0062698 | -0.0059563 | -0.0018809 | -0.0018809 | -0.002424 | -0.0027189 | -0.0030707 | -0.0033693 | -0.003606 | -0.0037989 | -0.0039773 | -0.0038462 | -0.0039073 | -0.0029897 | -0.003581 | -0.003581 | -0.003581 | -0.003581 | -0.003581 | -0.003581 | -0.003581 | -0.003581 | -0.003581 | -0.003581 | -0.003581 | -0.003581 | -0.003581 | -0.003581 | -0.003581
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 4.343% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.98212 | 0.96456 | 0.95306 | 0.94738 | 0.94738 | 0.94738 | 0.94738 | 0.94738 | 0.94738 | 0.94738 | -1.788% | -1.788% | -1.192% | -0.596% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Harbord 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 728 | 830 | 815.0592 | 797.8014 | 788.7677 | 770.9825 | 771.2336 | 777.4285 | 790.8139 | 804.8267 | 817.3687 | 830.6835 | 843.9003 | 859.4967 | 875.4156 | 892.3595 | 910.1494 | 927.9899 | 946.0794 | 964.6073 | 983.5801 | 1003.004 | 1022.886 | 1043.234 | 1064.053 | 1085.35 | 1107.133
|  |  |  | Apparent Power |  |  | MVA | 13.8703 |  | 15.529 | 15.2002 | 15.028 | 14.6892 | 14.694 | 14.812 | 15.067 | 15.334 | 15.573 | 15.8266 | 16.0785 | 16.3756 | 16.6789 | 17.0017 | 17.3407 | 17.6806 | 18.0252 | 18.3782 | 18.7397 | 19.1098 | 19.4886 | 19.8763 | 20.2729 | 20.6787 | 21.0937
|  |  |  | Real Power |  |  | MW | 12.7606 | 14.5485 | 14.2866 | 13.9841 | 13.8258 | 13.514 | 13.5184 | 13.627 | 13.8617 | 14.1073 | 14.3271 | 14.5605 | 14.7922 | 15.0656 | 15.3446 | 15.6416 | 15.9534 | 16.2661 | 16.5832 | 16.908 | 17.2405 | 17.581 | 17.9295 | 18.2862 | 18.6511 | 19.0244 | 19.4062
|  |  |  | Reactive Power |  |  | MVAr | 5.436 |  | 6.0861 | 5.9572 | 5.8898 | 5.757 | 5.7588 | 5.8051 | 5.905 | 6.0097 | 6.1033 | 6.2028 | 6.3014 | 6.4179 | 6.5368 | 6.6633 | 6.7961 | 6.9293 | 7.0644 | 7.2028 | 7.3444 | 7.4895 | 7.6379 | 7.7899 | 7.9453 | 8.1044 | 8.267
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.92 |  | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
0.86584 | Diversity Factor: 0.87 | Uncompensated |  | Reactive Power |  |  | MVAr | 5.436 | 6.1976 | 6.0861 | 5.9572 | 5.8898 | 5.757 | 5.7588 | 5.8051 | 5.905 | 6.0097 | 6.1033 | 6.2028 | 6.3014 | 6.4179 | 6.5368 | 6.6633 | 6.7961 | 6.9293 | 7.0644 | 7.2028 | 7.3444 | 7.4895 | 7.6379 | 7.7899 | 7.9453 | 8.1044 | 8.267
|  |  |  | PF |  |  |  | 0.92 |  | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Killarney 33_11kV
| Killarney 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 699 | 869 | 903 | 926 | 692 | 752 | 617 |  | 657.2675 | 637.1198 | 624.9226 | 612.0662 | 610.3262 | 612.6978 | 619.5513 | 627.0571 | 633.7594 | 640.9698 | 648.021 | 656.6299 | 665.4235 | 674.9053 | 684.934 | 694.9699 | 705.1307 | 715.5574 | 726.254 | 737.2247 | 748.4733 | 760.0042 | 771.8214 | 783.9293 | 796.332 |  |  | Total | 0 | 0 | 0 | -0.0089227 | -0.035166 | -71.0026 | -0.13646 | -0.27526 | -2.2019 | -0.60013 | -7.1688 | -1.74 | 2.3717 | 6.8535 | 7.5058 | 6.7024 | 7.2103 | 7.0512 | 8.6089 | 8.7936 | 9.4818 | 10.0287 | 10.036 | 10.1607 | 10.4267 | 10.6967 | 10.9706 | 11.2487 | 11.5309 | 11.8172 | 12.1078 | 12.4028
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 1107 |  | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 1107 |  | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 | 1107 |  |  | Killarney 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Killarney 33_11kV Tx2 | 0 | 0 | 0 | -0.0089227 | -0.035166 | -71.0026 | -0.13646 | -0.27526 | -2.2019 | -0.60013 | -7.1688 | -1.74 | 2.3717 | 6.8535 | 7.5058 | 6.7024 | 7.2103 | 7.0512 | 8.6089 | 8.7936 | 9.4818 | 10.0287 | 10.036 | 10.1607 | 10.4267 | 10.6967 | 10.9706 | 11.2487 | 11.5309 | 11.8172 | 12.1078 | 12.4028
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Killarney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.072652 | -1.9396 | -2.5512 | -10.9495 | -4.6041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6496. Beacon Hill to Belrose 11kV load transfer | Killarney 33_11kV Tx2 | Belrose 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 35.2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6496. Beacon Hill to Belrose 11kV load transfer | Killarney 33_11kV Tx2 | Belrose 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 35.7963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Killarney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7181 | 10.0536 | 12.6523 | 13.0991 | 13.8859 | 13.6901 | 13.4771 | 13.7133 | 13.953 | 14.1963 | 14.4432 | 14.6939 | 14.9483 | 15.2065 | 15.4686 | 15.7345 | 16.0045 | 16.2785 | 16.5565 | 16.8387 | 17.1251 | 17.4157 | 17.7106
| 0 | [33 empty] | Energy Efficiency |  | Killarney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.11896 | -0.1685 | -3.6611 | -6.1566 | -9.6638 | -10.5964 | -6.8952 | -6.0516 | -6.6399 | -6.3997 | -6.7782 | -5.4638 | -5.526 | -5.0885 | -4.796 | -5.0469 | -5.1843 | -5.1843 | -5.1843 | -5.1843 | -5.1843 | -5.1843 | -5.1843 | -5.1843 | -5.1843
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Killarney 33_11kV Tx2 | 0 | 0 | 0 | -0.0089227 | -0.035166 | -0.0026243 | -0.13646 | -0.083647 | -0.093822 | -0.10596 | -0.11627 | -0.12444 | -0.13109 | -0.13725 | -0.13272 | -0.13483 | -0.10317 | -0.12357 | -0.12357 | -0.12357 | -0.12357 | -0.12357 | -0.12357 | -0.12357 | -0.12357 | -0.12357 | -0.12357 | -0.12357 | -0.12357 | -0.12357 | -0.12357 | -0.12357
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | -0.1305% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.9727 | 0.94615 | 0.92893 | 0.92047 | 0.92047 | 0.92047 | 0.92047 | 0.92047 | 0.92047 | 0.92047 | -2.73% | -2.73% | -1.82% | -0.91% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Killarney 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 617 | 676 | 657.2675 | 637.1198 | 624.9226 | 612.0662 | 610.3262 | 612.6978 | 619.5513 | 627.0571 | 633.7594 | 640.9698 | 648.021 | 656.6299 | 665.4235 | 674.9053 | 684.934 | 694.9699 | 705.1307 | 715.5574 | 726.254 | 737.2247 | 748.4733 | 760.0042 | 771.8214 | 783.9293 | 796.332
|  |  |  | Apparent Power |  |  | MVA | 11.7554 |  | 12.5226 | 12.1388 | 11.9064 | 11.6614 | 11.6283 | 11.6735 | 11.804 | 11.947 | 12.0747 | 12.2121 | 12.3465 | 12.5105 | 12.678 | 12.8587 | 13.0497 | 13.2409 | 13.4345 | 13.6332 | 13.837 | 14.046 | 14.2603 | 14.48 | 14.7052 | 14.9359 | 15.1722
|  |  |  | Real Power |  |  | MW | 10.5799 | 11.5916 | 11.2704 | 10.9249 | 10.7157 | 10.4953 | 10.4654 | 10.5061 | 10.6236 | 10.7523 | 10.8673 | 10.9909 | 11.1118 | 11.2594 | 11.4102 | 11.5728 | 11.7448 | 11.9169 | 12.0911 | 12.2699 | 12.4533 | 12.6414 | 12.8343 | 13.032 | 13.2347 | 13.4423 | 13.6549
|  |  |  | Reactive Power |  |  | MVAr | 5.1241 |  | 5.4585 | 5.2912 | 5.1899 | 5.0831 | 5.0686 | 5.0883 | 5.1453 | 5.2076 | 5.2633 | 5.3231 | 5.3817 | 5.4532 | 5.5262 | 5.605 | 5.6883 | 5.7716 | 5.856 | 5.9426 | 6.0314 | 6.1225 | 6.2159 | 6.3117 | 6.4098 | 6.5104 | 6.6134
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.86191 | Diversity Factor: 0.86 | Uncompensated |  | Reactive Power |  |  | MVAr | 5.1241 | 5.6141 | 5.4585 | 5.2912 | 5.1899 | 5.0831 | 5.0686 | 5.0883 | 5.1453 | 5.2076 | 5.2633 | 5.3231 | 5.3817 | 5.4532 | 5.5262 | 5.605 | 5.6883 | 5.7716 | 5.856 | 5.9426 | 6.0314 | 6.1225 | 6.2159 | 6.3117 | 6.4098 | 6.5104 | 6.6134
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Manly 33_11kV
| Manly 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 985 | 975 | 987 | 980 | 869 | 923 | 838 |  | 793.5024 | 749.9246 | 721.455 | 699.3997 | 693.3229 | 694.7602 | 705.3362 | 719.5081 | 731.9879 | 745.2777 | 756.3164 | 770.871 | 785.465 | 802.3979 | 820.6751 | 838.6758 | 856.265 | 874.2389 | 892.6029 | 911.3623 | 930.5228 | 950.0899 | 970.0693 | 990.4667 | 1011.287 |  |  | Total | 0 | 0 | 0 | -0.70542 | -2.7183 | -0.00052486 | -1.6727 | -5.5709 | -7.6221 | -5.8155 | -11.1583 | -6.0768 | 1.4373 | 10.576 | 14.1719 | 12.4798 | 13.2898 | 11.0386 | 14.5547 | 14.594 | 16.9329 | 18.2771 | 18.0007 | 17.5892 | 17.9739 | 18.364 | 18.7595 | 19.1605 | 19.5671 | 19.9794 | 20.3974 | 20.8213
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 1200 |  | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 2400 |  | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 |  |  | Manly 33_11kV Tx1 | 0 | 0 | 0 | -0.26225 | -91.0106 | -0.00019513 | -0.62187 | -2.071 | -2.8336 | -2.162 | -4.1483 | -2.2591 | 0.53435 | 3.9318 | 5.2686 | 4.6396 | 4.9407 | 4.1038 | 5.4109 | 5.4255 | 6.2951 | 6.7948 | 6.692 | 6.5391 | 6.6821 | 6.8271 | 6.9741 | 7.1232 | 7.2744 | 7.4276 | 7.583 | 7.7406
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Manly 33_11kV Tx3 | 0 | 0 | 0 | -0.44317 | 88.2923 | -0.00032974 | -1.0509 | -3.4998 | -4.7885 | -3.6535 | -7.0101 | -3.8177 | 0.90299 | 6.6442 | 8.9033 | 7.8403 | 8.3491 | 6.9349 | 9.1437 | 9.1685 | 10.6378 | 11.4823 | 11.3087 | 11.0502 | 11.2918 | 11.5369 | 11.7854 | 12.0373 | 12.2927 | 12.5517 | 12.8144 | 13.0806
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Manly 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.39839 | -1.8947 | -1.9904 | -4.9312 | -2.5256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Manly 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.67322 | -3.2018 | -3.3636 | -8.3331 | -4.2679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010504. Establishment of S.48718 The Corso 8-28, Coles Manly Redevlopment, 8-28 The Corso Manly | Manly 33_11kV Tx1 | Manly 33_11kV Tx3 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Manly 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0758 | 5.6535 | 7.5982 | 8.163 | 8.5537 | 8.4721 | 8.3836 | 8.5115 | 8.6413 | 8.7728 | 8.9062 | 9.0415 | 9.1787 | 9.3178 | 9.4588 | 9.6018 | 9.7468 | 9.8938 | 10.0429 | 10.1941 | 10.3474 | 10.5028 | 10.6603
| 0 | [33 empty] | Econometric |  | Manly 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1978 | 9.5537 | 12.84 | 13.7944 | 14.4546 | 14.3169 | 14.1672 | 14.3834 | 14.6027 | 14.825 | 15.0504 | 15.279 | 15.5108 | 15.7458 | 15.9842 | 16.2258 | 16.4709 | 16.7193 | 16.9713 | 17.2267 | 17.4857 | 17.7484 | 18.0146
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Manly 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3961 | -0.62879 | -2.8971 | -4.4862 | -6.9204 | -7.1952 | -4.1681 | -2.7648 | -3.2983 | -3.2298 | -4.129 | -2.9534 | -3.0722 | -2.3379 | -1.9754 | -2.2172 | -2.5112 | -2.5112 | -2.5112 | -2.5112 | -2.5112 | -2.5112 | -2.5112 | -2.5112 | -2.5112
[35 empty] | Energy Efficiency |  | Manly 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3593 | -1.0626 | -4.8957 | -7.5811 | -11.6946 | -12.159 | -7.0436 | -4.6721 | -5.5737 | -5.458 | -6.9775 | -4.9909 | -5.1916 | -3.9508 | -3.3381 | -3.7468 | -4.2436 | -4.2436 | -4.2436 | -4.2436 | -4.2436 | -4.2436 | -4.2436 | -4.2436 | -4.2436
[35 empty] | Solar PV |  | Manly 33_11kV Tx1 | 0 | 0 | 0 | -0.26225 | -1.0106 | -0.00019513 | -0.62187 | -0.27652 | -0.31016 | -0.35029 | -0.38436 | -0.41136 | -0.43337 | -0.45372 | -0.43876 | -0.44573 | -0.34105 | -0.40851 | -0.40851 | -0.40851 | -0.40851 | -0.40851 | -0.40851 | -0.40851 | -0.40851 | -0.40851 | -0.40851 | -0.40851 | -0.40851 | -0.40851 | -0.40851 | -0.40851
| 0 | [33 empty] | Solar PV |  | Manly 33_11kV Tx3 | 0 | 0 | 0 | -0.44317 | -1.7077 | -0.00032974 | -1.0509 | -0.46728 | -0.52413 | -0.59195 | -0.64952 | -0.69515 | -0.73233 | -0.76674 | -0.74145 | -0.75323 | -0.57634 | -0.69034 | -0.69034 | -0.69034 | -0.69034 | -0.69034 | -0.69034 | -0.69034 | -0.69034 | -0.69034 | -0.69034 | -0.69034 | -0.69034 | -0.69034 | -0.69034 | -0.69034
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | -0.4426% |  | 5 year ROG ok | [59 empty] | 5 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95469 | 0.91143 | 0.88391 | 0.87056 | 0.87056 | 0.87056 | 0.87056 | 0.87056 | 0.87056 | 0.87056 | -4.531% | -4.531% | -3.02% | -1.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Manly 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 838 | 837 | 793.5024 | 749.9246 | 721.455 | 699.3997 | 693.3229 | 694.7602 | 705.3362 | 719.5081 | 731.9879 | 745.2777 | 756.3164 | 770.871 | 785.465 | 802.3979 | 820.6751 | 838.6758 | 856.265 | 874.2389 | 892.6029 | 911.3623 | 930.5228 | 950.0899 | 970.0693 | 990.4667 | 1011.287
|  |  |  | Apparent Power |  |  | MVA | 15.966 |  | 15.1182 | 14.288 | 13.7456 | 13.3254 | 13.2096 | 13.237 | 13.4385 | 13.7085 | 13.9462 | 14.1994 | 14.4098 | 14.6871 | 14.9651 | 15.2877 | 15.636 | 15.9789 | 16.314 | 16.6565 | 17.0064 | 17.3638 | 17.7288 | 18.1016 | 18.4823 | 18.8709 | 19.2676
|  |  |  | Real Power |  |  | MW | 14.5896 | 14.5722 | 13.8149 | 13.0562 | 12.5606 | 12.1766 | 12.0708 | 12.0958 | 12.2799 | 12.5267 | 12.7439 | 12.9753 | 13.1675 | 13.4209 | 13.675 | 13.9698 | 14.288 | 14.6014 | 14.9076 | 15.2205 | 15.5403 | 15.8668 | 16.2004 | 16.5411 | 16.8889 | 17.2441 | 17.6066
|  |  |  | Reactive Power |  |  | MVAr | 6.4852 |  | 6.1408 | 5.8036 | 5.5833 | 5.4126 | 5.3656 | 5.3767 | 5.4585 | 5.5682 | 5.6648 | 5.7676 | 5.853 | 5.9657 | 6.0786 | 6.2097 | 6.3511 | 6.4904 | 6.6265 | 6.7656 | 6.9078 | 7.0529 | 7.2012 | 7.3526 | 7.5073 | 7.6651 | 7.8262
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.91379 |  | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379
0.91819 | Diversity Factor: 0.92 | Uncompensated |  | Reactive Power |  |  | MVAr | 6.4852 | 6.4775 | 6.1408 | 5.8036 | 5.5833 | 5.4126 | 5.3656 | 5.3767 | 5.4585 | 5.5682 | 5.6648 | 5.7676 | 5.853 | 5.9657 | 6.0786 | 6.2097 | 6.3511 | 6.4904 | 6.6265 | 6.7656 | 6.9078 | 7.0529 | 7.2012 | 7.3526 | 7.5073 | 7.6651 | 7.8262
|  |  |  | PF |  |  |  | 0.91379 |  | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379 | 0.91379
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## North Head 33_11kV
| North Head 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 1165 | 1134 | 1141 | 1082 | 1124 | 1067 | 1114 |  | 1094.284 | 1092.601 | 1091.341 | 1088.456 | 1086.623 | 1087.212 | 1089.834 | 1093.118 | 1096.031 | 1099.12 | 1101.836 | 1105.314 | 1108.821 | 1112.792 | 1117.047 | 1121.258 | 1125.418 | 1129.673 | 1134.024 | 1138.473 | 1143.021 | 1147.669 | 1152.42 | 1157.274 | 1162.232 |  |  | Total | 0 | 0 | 0 | -1.1531 | -0.00052486 | 0 | 0 | -0.71503 | -1.6835 | -1.2597 | -2.8848 | -1.8331 | 0.58831 | 2.6223 | 3.2837 | 2.9137 | 3.0884 | 2.7166 | 3.4779 | 3.507 | 3.9703 | 4.2552 | 4.2112 | 4.1599 | 4.2549 | 4.3512 | 4.4489 | 4.548 | 4.6485 | 4.7504 | 4.8538 | 4.9586
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 1227 |  | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227 | 1227
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 2255 |  | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 | 2255 |  |  | North Head 33_11kV Tx1 | 0 | 0 | 0 | -0.57346 | -0.00026102 | 0 | 0 | -0.35559 | -0.83723 | -0.62646 | -1.4346 | -0.91159 | 0.29257 | 1.3041 | 1.633 | 1.449 | 1.5359 | 1.351 | 1.7296 | 1.744 | 1.9745 | 2.1162 | 2.0943 | 2.0688 | 2.116 | 2.1639 | 2.2125 | 2.2617 | 2.3117 | 2.3624 | 2.4138 | 2.466
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | North Head 33_11kV Tx2 | 0 | 0 | 0 | -0.57967 | -0.00026385 | 0 | 0 | -0.35944 | -0.84629 | -0.63324 | -1.4502 | -0.92146 | 0.29574 | 1.3182 | 1.6507 | 1.4647 | 1.5525 | 1.3656 | 1.7483 | 1.7629 | 1.9958 | 2.1391 | 2.117 | 2.0912 | 2.1389 | 2.1873 | 2.2364 | 2.2862 | 2.3368 | 2.388 | 2.44 | 2.4927
| Transformer Loads | [35 empty] | North Head 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | North Head 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0060217 | -0.64579 | -0.7256 | -1.8383 | -1.1334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | North Head 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0060869 | -0.65279 | -0.73346 | -1.8582 | -1.1457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | North Head 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0021 | 1.809 | 2.3736 | 2.5644 | 2.6961 | 2.6672 | 2.6359 | 2.678 | 2.7207 | 2.7641 | 2.8081 | 2.8527 | 2.8979 | 2.9438 | 2.9904 | 3.0376 | 3.0855 | 3.1341 | 3.1833 | 3.2333 | 3.284 | 3.3354 | 3.3876
[35 empty] | Econometric |  | North Head 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.013 | 1.8286 | 2.3993 | 2.5921 | 2.7253 | 2.6961 | 2.6644 | 2.707 | 2.7502 | 2.794 | 2.8385 | 2.8836 | 2.9293 | 2.9757 | 3.0228 | 3.0705 | 3.1189 | 3.168 | 3.2178 | 3.2683 | 3.3196 | 3.3715 | 3.4243
| 0 | [33 empty] | Energy Efficiency |  | North Head 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.30946 | -0.14644 | -0.85217 | -1.3496 | -2.0921 | -2.2089 | -1.3262 | -0.97057 | -1.1222 | -1.0926 | -1.3105 | -0.97523 | -1.0048 | -0.81896 | -0.7225 | -0.79028 | -0.86235 | -0.86235 | -0.86235 | -0.86235 | -0.86235 | -0.86235 | -0.86235 | -0.86235 | -0.86235
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | North Head 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.31281 | -0.14803 | -0.8614 | -1.3642 | -2.1147 | -2.2328 | -1.3405 | -0.98109 | -1.1344 | -1.1045 | -1.3247 | -0.9858 | -1.0156 | -0.82783 | -0.73033 | -0.79884 | -0.87169 | -0.87169 | -0.87169 | -0.87169 | -0.87169 | -0.87169 | -0.87169 | -0.87169 | -0.87169
[35 empty] | Solar PV |  | North Head 33_11kV Tx1 | 0 | 0 | 0 | -0.57346 | -0.00026102 | 0 | 0 | -0.040111 | -0.044991 | -0.050813 | -0.055755 | -0.059671 | -0.062863 | -0.065816 | -0.063646 | -0.064657 | -0.049472 | -0.059258 | -0.059258 | -0.059258 | -0.059258 | -0.059258 | -0.059258 | -0.059258 | -0.059258 | -0.059258 | -0.059258 | -0.059258 | -0.059258 | -0.059258 | -0.059258 | -0.059258
[35 empty] | Solar PV |  | North Head 33_11kV Tx2 | 0 | 0 | 0 | -0.57967 | -0.00026385 | 0 | 0 | -0.040546 | -0.045478 | -0.051363 | -0.056359 | -0.060317 | -0.063544 | -0.066529 | -0.064335 | -0.065357 | -0.050008 | -0.0599 | -0.0599 | -0.0599 | -0.0599 | -0.0599 | -0.0599 | -0.0599 | -0.0599 | -0.0599 | -0.0599 | -0.0599 | -0.0599 | -0.0599 | -0.0599 | -0.0599
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | Load driven by large non temperature dependent customer | [59 empty] | Load driven by large non temperature dependent customer
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | North Head 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1114 | 1095 | 1094.284 | 1092.601 | 1091.341 | 1088.456 | 1086.623 | 1087.212 | 1089.834 | 1093.118 | 1096.031 | 1099.12 | 1101.836 | 1105.314 | 1108.821 | 1112.792 | 1117.047 | 1121.258 | 1125.418 | 1129.673 | 1134.024 | 1138.473 | 1143.021 | 1147.669 | 1152.42 | 1157.274 | 1162.232
|  |  |  | Apparent Power |  |  | MVA | 21.2246 |  | 20.8489 | 20.8168 | 20.7929 | 20.7379 | 20.703 | 20.7142 | 20.7641 | 20.8267 | 20.8822 | 20.9411 | 20.9928 | 21.0591 | 21.1259 | 21.2015 | 21.2826 | 21.3628 | 21.4421 | 21.5232 | 21.6061 | 21.6908 | 21.7775 | 21.866 | 21.9566 | 22.049 | 22.1435
|  |  |  | Real Power |  |  | MW | 19.4214 | 19.0901 | 19.0777 | 19.0483 | 19.0264 | 18.9761 | 18.9441 | 18.9544 | 19.0001 | 19.0573 | 19.1081 | 19.162 | 19.2093 | 19.27 | 19.3311 | 19.4003 | 19.4745 | 19.5479 | 19.6205 | 19.6946 | 19.7705 | 19.8481 | 19.9273 | 20.0084 | 20.0912 | 20.1758 | 20.2623
|  |  |  | Reactive Power |  |  | MVAr | 8.561 |  | 8.4095 | 8.3966 | 8.3869 | 8.3647 | 8.3507 | 8.3552 | 8.3753 | 8.4006 | 8.423 | 8.4467 | 8.4676 | 8.4943 | 8.5212 | 8.5518 | 8.5845 | 8.6168 | 8.6488 | 8.6815 | 8.7149 | 8.7491 | 8.7841 | 8.8198 | 8.8563 | 8.8936 | 8.9317
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.91504 |  | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504
0.48198 | Diversity Factor: 0.48 | Uncompensated |  | Reactive Power |  |  | MVAr | 8.561 | 8.415 | 8.4095 | 8.3966 | 8.3869 | 8.3647 | 8.3507 | 8.3552 | 8.3753 | 8.4006 | 8.423 | 8.4467 | 8.4676 | 8.4943 | 8.5212 | 8.5518 | 8.5845 | 8.6168 | 8.6488 | 8.6815 | 8.7149 | 8.7491 | 8.7841 | 8.8198 | 8.8563 | 8.8936 | 8.9317
|  |  |  | PF |  |  |  | 0.91504 |  | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504 | 0.91504
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF