## Inclusions and Exclusions
Sydney Forecast Inclusions and Exclusions
Date Printed |  | 08JUL14:11:48:40
| Description | Value
Season |  | Winter | Winter
Either Summer or Winter
Year |  | 2014 | 2014
Year that the forecast starts
POE |  | 0%
10%, 50%, 90%
Spots and Transfers |  | Y | Y
Are Spots and Transfers Included?
BBDM Spots |  | Y | Y
Is BBDM included?
Spots Coefficient |  | 55% | 0.55
Scaling factor applied to spot loads in the future
Aligned ROGs |  | Capped | Capped
Have ROGs been aligned to econometric forecast?
Committed Projects |  | Y | Y
Are Committed Projects Included?
Major Customers Scaling Factor |  | 100% | 1
Scaling factor applied to major customer connections in the future
Future Transfers |  | Y | Y
Are future transfers included?
Future Spots |  | 4 | 4
Future spots are cleared from the following forecast year

## Argenton 132_33kV
| Argenton 132_33kV | [16 empty] | 2014 | WINTER
[6 empty] | Commissioned |  | 2009-05-04
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total |  |  | 21.8 | 31.5 | 68.9199 | 68.338 | 64.418 |  | 66.0873 | 64.9281 | 64.2943 | 64.1611 | 64.4823 | 65.0157 | 65.8497 | 66.6982 | 67.5103 | 68.362 | 69.1841 | 70.148 | 71.1279 | 72.1825 | 73.2912 | 74.4016 | 75.519 | 76.662 | 77.8308 | 79.0259 | 80.2477 | 81.4965 | 82.7728 | 84.0769 | 85.4093 |  |  | Total | 0.84874 | 5.7374 | -3.8349 | 29.7964 | 33.4501 | 4.9044 | -1.7853 | -1.0748 | -0.0065985 | 0.10835 | 0.23072 | 0.32119 | 0.5335 | 0.83408 | 0.84861 | 0.81225 | 0.85174 | 0.82222 | 0.96398 | 0.98 | 1.0547 | 1.1088 | 1.1104 | 1.1176 | 1.1431 | 1.169 | 1.1952 | 1.2219 | 1.2489 | 1.2764 | 1.3042 | 1.3325
| Firm Rating | 0 | 0 | 0 | 142.9 | 142.9 | 142.89 | 142.89 |  | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89
| Total Capacity | 0 | 0 | 0 | 240 | 240 | 286 | 286 |  | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 |  |  | Argenton 132_33kV Tx1 | 0.42397 | 2.866 | -1.9157 | 14.8843 | 16.7095 | 2.4499 | -0.89184 | -0.53691 | -0.0032962 | 0.054124 | 0.11525 | 0.16045 | 0.2665 | 0.41665 | 0.42391 | 0.40574 | 0.42548 | 0.41073 | 0.48154 | 0.48954 | 0.52688 | 0.5539 | 0.55469 | 0.55826 | 0.571 | 0.58393 | 0.59705 | 0.61037 | 0.62388 | 0.63759 | 0.6515 | 0.66561
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Argenton 132_33kV Tx3 | 0.42476 | 2.8714 | -1.9193 | 14.9121 | 16.7406 | 2.4545 | -0.89351 | -0.53792 | -0.0033023 | 0.054225 | 0.11547 | 0.16075 | 0.267 | 0.41743 | 0.4247 | 0.4065 | 0.42627 | 0.41149 | 0.48244 | 0.49046 | 0.52786 | 0.55493 | 0.55573 | 0.5593 | 0.57206 | 0.58502 | 0.59817 | 0.61151 | 0.62504 | 0.63878 | 0.65271 | 0.66685
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Cardiff 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx1 | 0 | 0 | -2.945 | 0 | 0 | 0 | -0.53989 | -0.088348 | 0.010918 | 0.00027635 | 0.010038 | 0.012723 | 0.026027 | 0.082264 | 0.098066 | 0.089241 | 0.09347 | 0.083539 | 0.10529 | 0.10629 | 0.11969 | 0.12799 | 0.12695 | 0.12566 | 0.12856 | 0.13151 | 0.1345 | 0.13753 | 0.14061 | 0.14373 | 0.1469 | 0.15011
| Diversity Factor: 0 | [33 empty] | Cardiff 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx3 | 0 | 0 | -2.9505 | 0 | 0 | 0 | -0.54089 | -0.088513 | 0.010938 | 0.00027686 | 0.010057 | 0.012747 | 0.026075 | 0.082418 | 0.098248 | 0.089407 | 0.093644 | 0.083694 | 0.10548 | 0.10649 | 0.11992 | 0.12823 | 0.12718 | 0.12589 | 0.1288 | 0.13175 | 0.13475 | 0.13779 | 0.14087 | 0.144 | 0.14717 | 0.15039
[35 empty] | Croudace Bay 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx1 | 4.2705 | 5.4105 | 0 | 0 | 0 | 0 | 0 | -0.59374 | -0.26894 | 0.010536 | 0.019212 | 0.0254 | 0.039831 | 0.085918 | 0.091095 | 0.087133 | 0.092693 | 0.090425 | 0.10887 | 0.11116 | 0.11996 | 0.12675 | 0.12705 | 0.12849 | 0.13185 | 0.13527 | 0.13873 | 0.14225 | 0.14582 | 0.14944 | 0.15312 | 0.15686
[35 empty] | Croudace Bay 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx3 | 4.2784 | 5.4205 | 0 | 0 | 0 | 0 | 0 | -0.59484 | -0.26944 | 0.010555 | 0.019248 | 0.025447 | 0.039906 | 0.086079 | 0.091264 | 0.087296 | 0.092866 | 0.090594 | 0.10907 | 0.11136 | 0.12019 | 0.12699 | 0.12729 | 0.12873 | 0.1321 | 0.13552 | 0.13899 | 0.14251 | 0.14609 | 0.14972 | 0.15341 | 0.15715
| 0 | [33 empty] | Edgeworth 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx1 | 0.42397 | -0.55396 | -1.333 | -1.5666 | -0.17135 | 1.0237 | 0 | 0.14609 | 0.25619 | 0.032884 | 0.067898 | 0.09805 | 0.16346 | 0.17524 | 0.15916 | 0.15665 | 0.16195 | 0.16024 | 0.17649 | 0.17918 | 0.18778 | 0.19443 | 0.19553 | 0.19742 | 0.20112 | 0.20486 | 0.20866 | 0.21252 | 0.21643 | 0.22039 | 0.2244 | 0.22848
| Diversity Factor: 0 | [33 empty] | Edgeworth 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx3 | 0.42476 | -0.55499 | -1.3355 | -1.5696 | -0.17167 | 1.0256 | 0 | 0.14637 | 0.25667 | 0.032945 | 0.068025 | 0.098233 | 0.16376 | 0.17556 | 0.15946 | 0.15694 | 0.16225 | 0.16054 | 0.17682 | 0.17951 | 0.18813 | 0.1948 | 0.1959 | 0.19779 | 0.20149 | 0.20525 | 0.20905 | 0.21291 | 0.21683 | 0.2208 | 0.22482 | 0.2289
[35 empty] | Mt Hutton 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx1 | -4.2705 | -1.9905 | 2.3623 | 0 | 0 | 0 | -0.35196 | -0.00092297 | -0.0014623 | 0.010428 | 0.018104 | 0.024274 | 0.037185 | 0.07323 | 0.075589 | 0.072719 | 0.077361 | 0.07652 | 0.090895 | 0.092921 | 0.099439 | 0.10472 | 0.10516 | 0.10669 | 0.10947 | 0.11229 | 0.11516 | 0.11807 | 0.12103 | 0.12403 | 0.12707 | 0.13017
[35 empty] | Mt Hutton 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx3 | -4.2784 | -1.9942 | 2.3668 | 0 | 0 | 0 | -0.35261 | -0.00092469 | -0.001465 | 0.010447 | 0.018138 | 0.024319 | 0.037254 | 0.073367 | 0.07573 | 0.072854 | 0.077506 | 0.076662 | 0.091064 | 0.093094 | 0.099624 | 0.10491 | 0.10536 | 0.10688 | 0.10967 | 0.1125 | 0.11537 | 0.11829 | 0.12125 | 0.12426 | 0.12731 | 0.13041
| 0 | [33 empty] | STS Change: Cardiff 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx1 | 0 | 0 | 0 | 8.3376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Cardiff 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx3 | 0 | 0 | 0 | 8.3532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Croudace Bay 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx1 | 0 | 0 | 0 | 0 | 9.6874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Croudace Bay 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx3 | 0 | 0 | 0 | 0 | 9.7055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | STS Change: Edgeworth 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx1 | 0 | 0 | 0 | 5.9912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Edgeworth 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx3 | 0 | 0 | 0 | 6.0023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Mt Hutton 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx1 | 0 | 0 | 0 | 0 | 7.1934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Mt Hutton 33_11kV Spots and Transfers |  | Argenton 132_33kV Tx3 | 0 | 0 | 0 | 0 | 7.2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | STS Change: Stockton Borehole 33kV Spots and Transfers |  | Argenton 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 1.4262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Stockton Borehole 33kV Spots and Transfers |  | Argenton 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 1.4289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: West Wallsend 2 33kV Spots and Transfers |  | Argenton 132_33kV Tx1 | 0 | 0 | 0 | 2.1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: West Wallsend 2 33kV Spots and Transfers |  | Argenton 132_33kV Tx3 | 0 | 0 | 0 | 2.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 6.621% |  | Weighted ROG calculation based on downstream zone substations and customers | [59 empty] | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.98167 | 0.96455 | 0.95352 | 0.94813 | 0.94813 | 0.94813 | 0.94813 | 0.94813 | 0.94813 | 0.94813 | -1.833% | -1.744% | -1.143% | -0.566% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Argenton 132_33kV | Compensated |  | Load (LV side) |  |  | Amps | 1127 |  | 1156.22 | 1135.94 | 1124.85 | 1122.52 | 1128.14 | 1137.47 | 1152.07 | 1166.91 | 1181.12 | 1196.02 | 1210.4 | 1227.27 | 1244.41 | 1262.86 | 1282.26 | 1301.68 | 1321.23 | 1341.23 | 1361.68 | 1382.59 | 1403.97 | 1425.81 | 1448.14 | 1470.96 | 1494.27
|  |  |  | Apparent Power |  |  | MVA | 64.418 |  | 66.0873 | 64.9281 | 64.2943 | 64.1611 | 64.4823 | 65.0157 | 65.8497 | 66.6982 | 67.5103 | 68.362 | 69.1841 | 70.148 | 71.1279 | 72.1825 | 73.2912 | 74.4016 | 75.519 | 76.662 | 77.8308 | 79.0259 | 80.2477 | 81.4965 | 82.7728 | 84.0769 | 85.4093
|  |  |  | Real Power |  |  | MW | 62.179 | 66.3122 | 64.0592 | 62.9356 | 62.3209 | 62.1908 | 62.5008 | 63.0158 | 63.8209 | 64.64 | 65.424 | 66.2462 | 67.0398 | 67.9703 | 68.9162 | 69.9343 | 71.0046 | 72.0764 | 73.1551 | 74.2585 | 75.3868 | 76.5405 | 77.7199 | 78.9254 | 80.1574 | 81.4163 | 82.7024
|  |  |  | Reactive Power |  |  | MVAr | 16.836 |  | 16.2465 | 15.9614 | 15.8073 | 15.7781 | 15.8621 | 16.0015 | 16.2195 | 16.4413 | 16.6536 | 16.8762 | 17.0911 | 17.343 | 17.5991 | 17.8748 | 18.1646 | 18.4548 | 18.7469 | 19.0456 | 19.3511 | 19.6635 | 19.9829 | 20.3093 | 20.6429 | 20.9837 | 21.332
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.96524 |  | 0.96931 | 0.96931 | 0.96931 | 0.96929 | 0.96927 | 0.96924 | 0.96919 | 0.96914 | 0.9691 | 0.96905 | 0.96901 | 0.96896 | 0.96891 | 0.96885 | 0.9688 | 0.96875 | 0.9687 | 0.96865 | 0.9686 | 0.96855 | 0.9685 | 0.96845 | 0.9684 | 0.96835 | 0.96831
0.94384 | Diversity Factor: 0.94 | Uncompensated |  | Reactive Power |  |  | MVAr | 16.836 | 17.9551 | 16.2465 | 15.9614 | 15.8073 | 15.7781 | 15.8621 | 16.0015 | 16.2195 | 16.4413 | 16.6536 | 16.8762 | 17.0911 | 17.343 | 17.5991 | 17.8748 | 18.1646 | 18.4548 | 18.7469 | 19.0456 | 19.3511 | 19.6635 | 19.9829 | 20.3093 | 20.6429 | 20.9837 | 21.332
|  |  |  | PF |  |  |  | 0.96524 |  | 0.96931 | 0.96931 | 0.96931 | 0.96929 | 0.96927 | 0.96924 | 0.96919 | 0.96914 | 0.9691 | 0.96905 | 0.96901 | 0.96896 | 0.96891 | 0.96885 | 0.9688 | 0.96875 | 0.9687 | 0.96865 | 0.9686 | 0.96855 | 0.9685 | 0.96845 | 0.9684 | 0.96835 | 0.96831
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Awaba 132_33kV
| Awaba 132_33kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 120.1 | 123.5 | 94.5 | 64.7 | 25.8 | 22.45 | 19.015 |  | 14.8563 | 14.7416 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 |  |  | Total | 0 | -11.8037 | -0.29276 | -26.1567 | -37.4847 | -2.8551 | -3.5469 | -0.031456 | -0.014865 | -8.3216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 137.1 | 137.1 | 137.18 | 137.18 |  | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18 | 137.18
| Total Capacity | 0 | 0 | 0 | 180 | 180 | 206 | 206 |  | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 |  |  | Awaba 132_33kV Tx1 | 0 | -3.9058 | -0.096873 | -8.6551 | -12.4035 | -0.94474 | -1.1737 | -0.010409 | -0.0049189 | -2.7536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Awaba 132_33kV Tx2 | 0 | -3.9564 | -0.098127 | -8.7672 | -12.5641 | -0.95698 | -1.1889 | -0.010543 | -0.0049826 | -2.7892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Awaba 132_33kV Tx3 | 0 | -3.9416 | -0.09776 | -8.7344 | -12.5171 | -0.9534 | -1.1844 | -0.010504 | -0.004964 | -2.7788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Boolaroo 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx1 | 0 | 0.22128 | -0.096873 | -3.2808 | -1.2215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Boolaroo 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx2 | 0 | 0.22415 | -0.098127 | -3.3233 | -1.2373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Boolaroo 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx3 | 0 | 0.22331 | -0.09776 | -3.3108 | -1.2327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Croudace Bay 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx1 | 0 | 0 | 0 | 0 | -6.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | STS Change: Croudace Bay 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx2 | 0 | 0 | 0 | 0 | -6.5001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Croudace Bay 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx3 | 0 | 0 | 0 | 0 | -6.4758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Edgeworth 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx1 | 0 | 0 | 0 | -3.9686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Edgeworth 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx2 | 0 | 0 | 0 | -4.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | STS Change: Edgeworth 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx3 | 0 | 0 | 0 | -4.0049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Mt Hutton 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx1 | 0 | 0 | 0 | 0 | -4.7649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Mt Hutton 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx2 | 0 | 0 | 0 | 0 | -4.8267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Mt Hutton 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx3 | 0 | 0 | 0 | 0 | -4.8086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | STS Change: Stockton Borehole 33kV Spots and Transfers |  | Awaba 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | -0.94474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Stockton Borehole 33kV Spots and Transfers |  | Awaba 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | -0.95698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Stockton Borehole 33kV Spots and Transfers |  | Awaba 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | -0.9534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: West Wallsend 2 33kV Spots and Transfers |  | Awaba 132_33kV Tx1 | 0 | 0 | 0 | -1.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | STS Change: West Wallsend 2 33kV Spots and Transfers |  | Awaba 132_33kV Tx2 | 0 | 0 | 0 | -1.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: West Wallsend 2 33kV Spots and Transfers |  | Awaba 132_33kV Tx3 | 0 | 0 | 0 | -1.4186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Toronto 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx1 | 0 | -4.1271 | 0 | 0 | 0 | 0 | -1.1737 | -0.010409 | -0.0049189 | -2.7536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Toronto 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx2 | 0 | -4.1805 | 0 | 0 | 0 | 0 | -1.1889 | -0.010543 | -0.0049826 | -2.7892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Toronto 33_11kV Spots and Transfers |  | Awaba 132_33kV Tx3 | 0 | -4.1649 | 0 | 0 | 0 | 0 | -1.1844 | -0.010504 | -0.004964 | -2.7788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 5.106% |  | Weighted ROG calculation based on downstream zone substations and customers | [59 empty] | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.99318 | 0.98651 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | -0.682% | -0.672%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Awaba 132_33kV | Compensated |  | Load (LV side) |  |  | Amps | 333 |  | 259.918 | 257.9113 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209 | 112.3209
|  |  |  | Apparent Power |  |  | MVA | 19.015 |  | 14.8563 | 14.7416 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42
|  |  |  | Real Power |  |  | MW | 17.9311 | 14.1356 | 14.0095 | 13.9013 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541 | 6.0541
|  |  |  | Reactive Power |  |  | MVAr | 6.3281 |  | 4.9441 | 4.9059 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.943 |  | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943
0.88456 | Diversity Factor: 0.88 | Uncompensated |  | Reactive Power |  |  | MVAr | 6.3281 | 4.9886 | 4.9441 | 4.9059 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365
|  |  |  | PF |  |  |  | 0.943 |  | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943 | 0.943
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Beresfield 132_33kV
| Beresfield 132_33kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 108.7 | 78.1 | 83.3 | 71.1 | 69.317 | 79.913 | 73.222 |  | 71.6585 | 62.6813 | 63.49 | 63.6894 | 64.3311 | 65.4274 | 66.9291 | 68.3234 | 69.689 | 71.0922 | 72.441 | 73.943 | 75.4612 | 77.0759 | 78.7545 | 80.4357 | 82.1188 | 83.8307 | 85.5719 | 87.3429 | 89.1439 | 90.9754 | 92.8379 | 94.7317 | 96.6573 |  |  | Total | 0 | 3.9663 | -1.6653e-16 | 5.7532 | 0 | -0.35964 | 0.33173 | 1.1771 | -8.075 | 1.3195 | 0.45529 | 0.6417 | 1.0963 | 1.5017 | 1.3943 | 1.3656 | 1.4032 | 1.3488 | 1.5021 | 1.5181 | 1.6147 | 1.6786 | 1.6812 | 1.683 | 1.7119 | 1.7412 | 1.7709 | 1.801 | 1.8315 | 1.8625 | 1.8938 | 1.9256
| Firm Rating | 0 | 0 | 0 | 142.9 | 142.9 | 142.9 | 114.32 |  | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32 | 114.32
| Total Capacity | 0 | 0 | 0 | 240 | 240 | 240 | 229 |  | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 |  |  | Beresfield 132_33kV Tx1 | 0 | 1.9854 | 2e-10 | 2.8798 | 0 | -0.18002 | 0.16605 | 0.58921 | -4.042 | 0.66047 | 0.2279 | 0.32121 | 0.54875 | 0.7517 | 0.69793 | 0.68358 | 0.70238 | 0.67515 | 0.75187 | 0.75991 | 0.80827 | 0.84026 | 0.84156 | 0.84245 | 0.85692 | 0.87159 | 0.88646 | 0.90153 | 0.9168 | 0.93227 | 0.94796 | 0.96386
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Beresfield 132_33kV Tx3 | 0 | 1.9809 | -2e-10 | 2.8734 | 0 | -0.17962 | 0.16568 | 0.58789 | -4.033 | 0.65899 | 0.22739 | 0.32049 | 0.54753 | 0.75002 | 0.69637 | 0.68205 | 0.7008 | 0.67363 | 0.75019 | 0.75821 | 0.80646 | 0.83838 | 0.83968 | 0.84057 | 0.85501 | 0.86964 | 0.88448 | 0.89951 | 0.91475 | 0.93019 | 0.94584 | 0.9617
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | East Maitland 33_11kV Spots and Transfers |  | Beresfield 132_33kV Tx1 | 0 | 0.18847 | -0.41091 | 0.0054902 | 0 | -0.18002 | 0.16605 | -0.023423 | -8.4599 | 0.5708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | East Maitland 33_11kV Spots and Transfers |  | Beresfield 132_33kV Tx3 | 0 | 0.18805 | -0.40999 | 0.0054779 | 0 | -0.17962 | 0.16568 | -0.023371 | -8.4409 | 0.56952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Metford 33_11kV Spots and Transfers |  | Beresfield 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3874 | 0.019401 | 0.059095 | 0.083687 | 0.13988 | 0.22037 | 0.21441 | 0.20755 | 0.21395 | 0.20203 | 0.23102 | 0.23331 | 0.25168 | 0.26342 | 0.26313 | 0.2625 | 0.26731 | 0.27219 | 0.27714 | 0.28215 | 0.28724 | 0.29239 | 0.29762 | 0.30292
[35 empty] | Metford 33_11kV Spots and Transfers |  | Beresfield 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3687 | 0.019358 | 0.058962 | 0.0835 | 0.13957 | 0.21988 | 0.21393 | 0.20709 | 0.21347 | 0.20158 | 0.2305 | 0.23279 | 0.25111 | 0.26283 | 0.26254 | 0.26191 | 0.26671 | 0.27158 | 0.27652 | 0.28152 | 0.2866 | 0.29174 | 0.29695 | 0.30224
| 0 | [33 empty] | STS Change: Hexham Metal 33kV Spots and Transfers |  | Beresfield 132_33kV Tx1 | 0 | 0 | 0 | 2.4916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Hexham Metal 33kV Spots and Transfers |  | Beresfield 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Hexham Metal 33kV Spots and Transfers |  | Beresfield 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Hexham Metal 33kV Spots and Transfers |  | Beresfield 132_33kV Tx3 | 0 | 0 | 0 | 2.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Tarro 33_11kV Spots and Transfers |  | Beresfield 132_33kV Tx1 | 0 | 0.21526 | -0.96885 | 0 | 0 | 0 | 0 | -0.58813 | -0.074427 | 0.029658 | 0.077583 | 0.10718 | 0.22047 | 0.24107 | 0.20983 | 0.21723 | 0.22169 | 0.21073 | 0.23266 | 0.23442 | 0.2499 | 0.25941 | 0.25945 | 0.25857 | 0.26248 | 0.26645 | 0.27046 | 0.27453 | 0.27865 | 0.28282 | 0.28704 | 0.29132
| Diversity Factor: 0 | [33 empty] | Tarro 33_11kV Spots and Transfers |  | Beresfield 132_33kV Tx3 | 0 | 0.21478 | -0.96668 | 0 | 0 | 0 | 0 | -0.58681 | -0.07426 | 0.029592 | 0.077409 | 0.10694 | 0.21998 | 0.24053 | 0.20936 | 0.21674 | 0.22119 | 0.21026 | 0.23214 | 0.2339 | 0.24934 | 0.25883 | 0.25886 | 0.25799 | 0.26189 | 0.26585 | 0.26986 | 0.27391 | 0.27802 | 0.28219 | 0.2864 | 0.29067
[35 empty] | Thornton 33_11kV Spots and Transfers |  | Beresfield 132_33kV Tx1 | 0 | 1.5816 | 1.3798 | 0.38269 | 0 | 0 | 0 | 1.2008 | -0.006236 | 0.040616 | 0.091223 | 0.13034 | 0.1884 | 0.29026 | 0.27369 | 0.2588 | 0.26674 | 0.26238 | 0.2882 | 0.29218 | 0.30669 | 0.31743 | 0.31899 | 0.32139 | 0.32713 | 0.33296 | 0.33886 | 0.34484 | 0.35091 | 0.35706 | 0.3633 | 0.36962
[35 empty] | Thornton 33_11kV Spots and Transfers |  | Beresfield 132_33kV Tx3 | 0 | 1.5781 | 1.3767 | 0.38184 | 0 | 0 | 0 | 1.1981 | -0.006222 | 0.040525 | 0.091019 | 0.13005 | 0.18797 | 0.28961 | 0.27307 | 0.25822 | 0.26615 | 0.2618 | 0.28755 | 0.29152 | 0.306 | 0.31672 | 0.31827 | 0.32067 | 0.3264 | 0.33221 | 0.3381 | 0.34407 | 0.35013 | 0.35626 | 0.36248 | 0.36879
| 0 | [33 empty] | Wallalong 33_11kV Spots and Transfers |  | Beresfield 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Wallalong 33_11kV Spots and Transfers |  | Beresfield 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | -1.544% |  | Weighted ROG calculation based on downstream zone substations and customers | [59 empty] | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.98424 | 0.97185 | 0.96393 | 0.96004 | 0.96004 | 0.96004 | 0.96004 | 0.96004 | 0.96004 | 0.96004 | -1.576% | -1.259% | -0.815% | -0.403% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Beresfield 132_33kV | Compensated |  | Load (LV side) |  |  | Amps | 1281 |  | 1253.69 | 1096.63 | 1110.78 | 1114.27 | 1125.5 | 1144.68 | 1170.95 | 1195.34 | 1219.24 | 1243.79 | 1267.38 | 1293.66 | 1320.22 | 1348.47 | 1377.84 | 1407.26 | 1436.7 | 1466.65 | 1497.12 | 1528.1 | 1559.61 | 1591.65 | 1624.24 | 1657.37 | 1691.06
|  |  |  | Apparent Power |  |  | MVA | 73.222 |  | 71.6585 | 62.6813 | 63.49 | 63.6894 | 64.3311 | 65.4274 | 66.9291 | 68.3234 | 69.689 | 71.0922 | 72.441 | 73.943 | 75.4612 | 77.0759 | 78.7545 | 80.4357 | 82.1188 | 83.8307 | 85.5719 | 87.3429 | 89.1439 | 90.9754 | 92.8379 | 94.7317 | 96.6573
|  |  |  | Real Power |  |  | MW | 70.642 | 69.0868 | 69.1336 | 60.4727 | 61.2529 | 61.4453 | 62.0643 | 63.122 | 64.5708 | 65.916 | 67.2335 | 68.5872 | 69.8885 | 71.3376 | 72.8023 | 74.3601 | 75.9796 | 77.6016 | 79.2253 | 80.8769 | 82.5568 | 84.2653 | 86.0029 | 87.7699 | 89.5667 | 91.3938 | 93.2515
|  |  |  | Reactive Power |  |  | MVAr | 19.2658 |  | 18.8544 | 16.4923 | 16.7051 | 16.7576 | 16.9264 | 17.2149 | 17.61 | 17.9768 | 18.3362 | 18.7054 | 19.0602 | 19.4555 | 19.8549 | 20.2798 | 20.7214 | 21.1638 | 21.6066 | 22.0571 | 22.5152 | 22.9811 | 23.455 | 23.9369 | 24.427 | 24.9253 | 25.4319
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.96476 |  | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476
0.89725 | Diversity Factor: 0.9 | Uncompensated |  | Reactive Power |  |  | MVAr | 19.2658 | 18.8416 | 18.8544 | 16.4923 | 16.7051 | 16.7576 | 16.9264 | 17.2149 | 17.61 | 17.9768 | 18.3362 | 18.7054 | 19.0602 | 19.4555 | 19.8549 | 20.2798 | 20.7214 | 21.1638 | 21.6066 | 22.0571 | 22.5152 | 22.9811 | 23.455 | 23.9369 | 24.427 | 24.9253 | 25.4319
|  |  |  | PF |  |  |  | 0.96476 |  | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476 | 0.96476
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Eraring 132_33kV
| Eraring 132_33kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 54.3 | 38.8 | 30.8 | 29.3 | 30.842 | 28.144 | 28.885 |  | 26.8814 | 26.6971 | 26.6615 | 26.7725 | 27.0147 | 27.5233 | 28.0876 | 28.5631 | 29.0383 | 29.5225 | 30.0059 | 30.5122 | 31.0246 | 31.5514 | 32.0897 | 32.6323 | 33.1799 | 33.7351 | 34.298 | 34.8688 | 35.4475 | 36.0342 | 36.629 | 37.2321 | 37.8435 |  |  | Total | 0 | -7.6198 | -8.559 | 0.64698 | 0 | 0 | -2.4277 | -0.0087534 | -0.0050563 | 0.082679 | 0.17085 | 0.24227 | 0.50876 | 0.56451 | 0.47562 | 0.47536 | 0.48432 | 0.4836 | 0.50644 | 0.51251 | 0.52697 | 0.53841 | 0.54275 | 0.54768 | 0.55532 | 0.56305 | 0.57088 | 0.57881 | 0.58684 | 0.59497 | 0.60319 | 0.61153
| Firm Rating | 0 | 0 | 0 | 71 | 71 | 73.45 | 73.45 |  | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45 | 73.45
| Total Capacity | 0 | 0 | 0 | 120 | 120 | 134 | 134 |  | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 |  |  | Eraring 132_33kV Tx1 | 0 | -3.7261 | -4.1854 | 0.31638 | 0 | 0 | -1.1872 | -0.0042805 | -0.0024726 | 0.040431 | 0.083545 | 0.11847 | 0.24879 | 0.27605 | 0.23258 | 0.23246 | 0.23684 | 0.23649 | 0.24765 | 0.25062 | 0.25769 | 0.26329 | 0.26541 | 0.26782 | 0.27155 | 0.27534 | 0.27917 | 0.28304 | 0.28697 | 0.29094 | 0.29497 | 0.29904
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Eraring 132_33kV Tx2 | 0 | -3.8936 | -4.3736 | 0.3306 | 0 | 0 | -1.2405 | -0.0044729 | -0.0025837 | 0.042248 | 0.087301 | 0.1238 | 0.25997 | 0.28846 | 0.24304 | 0.24291 | 0.24748 | 0.24712 | 0.25879 | 0.26189 | 0.26928 | 0.27512 | 0.27734 | 0.27986 | 0.28376 | 0.28771 | 0.29172 | 0.29577 | 0.29987 | 0.30402 | 0.30823 | 0.31249
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Avondale 33_11kV Spots and Transfers |  | Eraring 132_33kV Tx1 | 0 | 0 | -4.1854 | 0.31638 | 0 | 0 | -1.1872 | -0.0042805 | -0.0024726 | 0.040431 | 0.083545 | 0.11847 | 0.24879 | 0.27605 | 0.23258 | 0.23246 | 0.23684 | 0.23649 | 0.24765 | 0.25062 | 0.25769 | 0.26329 | 0.26541 | 0.26782 | 0.27155 | 0.27534 | 0.27917 | 0.28304 | 0.28697 | 0.29094 | 0.29497 | 0.29904
| Diversity Factor: 0 | [33 empty] | Avondale 33_11kV Spots and Transfers |  | Eraring 132_33kV Tx2 | 0 | 0 | -4.3736 | 0.3306 | 0 | 0 | -1.2405 | -0.0044729 | -0.0025837 | 0.042248 | 0.087301 | 0.1238 | 0.25997 | 0.28846 | 0.24304 | 0.24291 | 0.24748 | 0.24712 | 0.25879 | 0.26189 | 0.26928 | 0.27512 | 0.27734 | 0.27986 | 0.28376 | 0.28771 | 0.29172 | 0.29577 | 0.29987 | 0.30402 | 0.30823 | 0.31249
[35 empty] | Morisset 33_11kV Temp Spots and Transfers |  | Eraring 132_33kV Tx1 | 0 | -3.7261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Morisset 33_11kV Temp Spots and Transfers |  | Eraring 132_33kV Tx2 | 0 | -3.8936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 3.131% |  | Weighted ROG calculation based on downstream zone substations and customers | [59 empty] | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.99323 | 0.98661 | 0.98223 | 0.98003 | 0.98003 | 0.98003 | 0.98003 | 0.98003 | 0.98003 | 0.98003 | -0.677% | -0.667% | -0.443% | -0.224% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Eraring 132_33kV | Compensated |  | Load (LV side) |  |  | Amps | 505 |  | 470.3031 | 467.0778 | 466.4546 | 468.3977 | 472.6349 | 481.5328 | 491.406 | 499.7245 | 508.0386 | 516.5095 | 524.9679 | 533.8258 | 542.79 | 552.0072 | 561.4246 | 570.9179 | 580.4976 | 590.2109 | 600.0595 | 610.0452 | 620.1697 | 630.4346 | 640.8417 | 651.3929 | 662.0899
|  |  |  | Apparent Power |  |  | MVA | 28.885 |  | 26.8814 | 26.6971 | 26.6615 | 26.7725 | 27.0147 | 27.5233 | 28.0876 | 28.5631 | 29.0383 | 29.5225 | 30.0059 | 30.5122 | 31.0246 | 31.5514 | 32.0897 | 32.6323 | 33.1799 | 33.7351 | 34.298 | 34.8688 | 35.4475 | 36.0342 | 36.629 | 37.2321 | 37.8435
|  |  |  | Real Power |  |  | MW | 26.8053 | 24.8426 | 24.6663 | 24.497 | 24.4652 | 24.569 | 24.7938 | 25.2659 | 25.7898 | 26.2312 | 26.6723 | 27.1218 | 27.5706 | 28.0405 | 28.5161 | 29.0052 | 29.5048 | 30.0085 | 30.5167 | 31.0321 | 31.5546 | 32.0844 | 32.6215 | 33.1661 | 33.7182 | 34.278 | 34.8455
|  |  |  | Reactive Power |  |  | MVAr | 10.762 |  | 10.6859 | 10.6127 | 10.5965 | 10.6364 | 10.7267 | 10.9162 | 11.1265 | 11.3038 | 11.4809 | 11.6613 | 11.8415 | 12.0302 | 12.2211 | 12.4175 | 12.6181 | 12.8203 | 13.0244 | 13.2312 | 13.441 | 13.6537 | 13.8694 | 14.088 | 14.3097 | 14.5344 | 14.7623
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.928 |  | 0.91759 | 0.91759 | 0.91763 | 0.91769 | 0.91779 | 0.91798 | 0.91819 | 0.91836 | 0.91852 | 0.91868 | 0.91884 | 0.91899 | 0.91915 | 0.9193 | 0.91945 | 0.91959 | 0.91974 | 0.91987 | 0.92001 | 0.92015 | 0.92028 | 0.92041 | 0.92053 | 0.92066 | 0.92078
0.82338 | Diversity Factor: 0.82 | Uncompensated |  | Reactive Power |  |  | MVAr | 10.762 | 9.974 | 10.6859 | 10.6127 | 10.5965 | 10.6364 | 10.7267 | 10.9162 | 11.1265 | 11.3038 | 11.4809 | 11.6613 | 11.8415 | 12.0302 | 12.2211 | 12.4175 | 12.6181 | 12.8203 | 13.0244 | 13.2312 | 13.441 | 13.6537 | 13.8694 | 14.088 | 14.3097 | 14.5344 | 14.7623
|  |  |  | PF |  |  |  | 0.928 |  | 0.91759 | 0.91759 | 0.91763 | 0.91769 | 0.91779 | 0.91798 | 0.91819 | 0.91836 | 0.91852 | 0.91868 | 0.91884 | 0.91899 | 0.91915 | 0.9193 | 0.91945 | 0.91959 | 0.91974 | 0.91987 | 0.92001 | 0.92015 | 0.92028 | 0.92041 | 0.92053 | 0.92066 | 0.92078
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Kooragang 132_33kV
| Kooragang 132_33kV | [16 empty] | 2014 | WINTER
[6 empty] | Commissioned |  | 2009-11-26
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total |  |  |  |  | 39.775 | 61.12 | 65.625 |  | 66.045 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 |  |  | Total | 0 | 0 | 0 | 0 | 19.7755 | 19.7755 | 0 | 0 | 4.9776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 142.9 | 142.9 | 142.89 | 142.89 |  | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89 | 142.89
| Total Capacity | 0 | 0 | 0 | 240 | 240 | 286 | 286 |  | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 |  |  | Kooragang 132_33kV Tx1 | 0 | 0 | 0 | 0 | 12.3187 | 12.3187 | 0 | 0 | 3.1007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Kooragang 132_33kV Tx3 | 0 | 0 | 0 | 0 | 7.4568 | 7.4568 | 0 | 0 | 1.8769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | STS Change: Hexham Metal 33kV Spots and Transfers |  | Kooragang 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Hexham Metal 33kV Spots and Transfers |  | Kooragang 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Kooragang 132_33kV Tx1 | 0 | 0 | 0 | 0 | 12.3187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Kooragang 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 12.3187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Kooragang 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 7.4568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Kooragang 132_33kV Tx3 | 0 | 0 | 0 | 0 | 7.4568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0.7749% |  | Weighted ROG calculation based on downstream zone substations and customers | [59 empty] | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Kooragang 132_33kV | Compensated |  | Load (LV side) |  |  | Amps | 1148 |  | 1155.48 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57 | 1242.57
|  |  |  | Apparent Power |  |  | MVA | 65.625 |  | 66.045 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226 | 71.0226
|  |  |  | Real Power |  |  | MW | 61.696 | 62.1426 | 62.1426 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222 | 66.8222
|  |  |  | Reactive Power |  |  | MVAr | 22.3661 |  | 22.3661 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.94013 |  | 0.94091 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086
0.55073 | Diversity Factor: 0.55 | Uncompensated |  | Reactive Power |  |  | MVAr | 22.3661 | 22.528 | 22.3661 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626 | 24.0626
|  |  |  | PF |  |  |  | 0.94013 |  | 0.94091 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086 | 0.94086
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Kurri 132_33kV
| Kurri 132_33kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 122.4 | 129.6 | 108.4 | 105.1 | 115.6438 | 91.98 | 86.49 |  | 88.8543 | 85.5854 | 84.7576 | 85.0166 | 86.2001 | 88.5181 | 91.4185 | 94.0178 | 96.5869 | 99.2166 | 101.7699 | 104.555 | 107.3694 | 110.3334 | 113.398 | 116.4725 | 119.5553 | 122.6869 | 125.868 | 129.0993 | 132.3814 | 130.6948 | 133.9623 | 137.2867 | 140.6684 |  |  | Total | 0.82949 | -2.4786 | 0.50111 | -0.14285 | -22.3863 | 0.69463 | 0.055371 | -0.17149 | -1.4404 | 0.34217 | 0.83702 | 1.1835 | 2.318 | 2.9004 | 2.5993 | 2.5691 | 2.6297 | 2.5534 | 2.7851 | 2.8144 | 2.964 | 3.0646 | 3.0745 | 3.0827 | 3.1316 | 3.1811 | 3.2313 | 3.2821 | 3.3336 | 3.3858 | 3.4386 | 3.4922
| Firm Rating | 0 | 0 | 0 | 137.1 | 137.1 | 164 | 161.98 |  | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98 | 161.98
| Total Capacity | 0 | 0 | 0 | 180 | 180 | 212 | 243 |  | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 |  |  | Kurri 132_33kV Tx1 | 0.27737 | -0.8288 | 0.16757 | -0.047766 | -7.4857 | 0.23227 | 0.018515 | -0.057345 | -0.48164 | 0.11442 | 0.27989 | 0.39576 | 0.7751 | 0.96984 | 0.86917 | 0.85909 | 0.87933 | 0.85381 | 0.93129 | 0.94111 | 0.99112 | 1.0248 | 1.0281 | 1.0308 | 1.0472 | 1.0637 | 1.0805 | 1.0975 | 1.1147 | 1.1322 | 1.1498 | 1.1677
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Kurri 132_33kV Tx2 | 0.27585 | -0.82426 | 0.16665 | -0.047505 | -7.4447 | 0.231 | 0.018414 | -0.057031 | -0.479 | 0.11379 | 0.27836 | 0.39359 | 0.77086 | 0.96453 | 0.86441 | 0.85438 | 0.87452 | 0.84914 | 0.92619 | 0.93596 | 0.9857 | 1.0192 | 1.0224 | 1.0252 | 1.0414 | 1.0579 | 1.0746 | 1.0915 | 1.1086 | 1.126 | 1.1435 | 1.1613
| Transformer Loads | [35 empty] | Kurri 132_33kV Tx3 | 0.27627 | -0.8255 | 0.1669 | -0.047576 | -7.4559 | 0.23135 | 0.018442 | -0.057117 | -0.47972 | 0.11396 | 0.27878 | 0.39419 | 0.77202 | 0.96599 | 0.86572 | 0.85567 | 0.87584 | 0.85042 | 0.92758 | 0.93737 | 0.98718 | 1.0207 | 1.024 | 1.0267 | 1.043 | 1.0595 | 1.0762 | 1.0931 | 1.1103 | 1.1277 | 1.1453 | 1.1631
| Historical Loads | (MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (MVA) |  |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Austar 1 (Southland) removal from 33kV Spots and Transfers |  | Kurri 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Austar 1 (Southland) removal from 33kV Spots and Transfers |  | Kurri 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Austar 1 (Southland) removal from 33kV Spots and Transfers |  | Kurri 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Austar 1 (Southland) removal from 33kV Spots and Transfers |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Austar 2 onto 33kV Spots and Transfers |  | Kurri 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Austar 2 onto 33kV Spots and Transfers |  | Kurri 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Austar 2 onto 33kV Spots and Transfers |  | Kurri 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Austar 2 onto 33kV Spots and Transfers |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Cessnock 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx1 | 0 | 0 | -0.081355 | 0 | 0 | 0 | -0.3556 | -0.0091809 | -0.0045909 | 0.021199 | 0.047662 | 0.066196 | 0.17506 | 0.21236 | 0.1891 | 0.18666 | 0.1913 | 0.18751 | 0.20341 | 0.20582 | 0.21558 | 0.22249 | 0.22353 | 0.22473 | 0.22836 | 0.23204 | 0.23577 | 0.23955 | 0.24338 | 0.24726 | 0.25119 | 0.25517
| Diversity Factor: 0 | [33 empty] | Cessnock 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx2 | 0 | 0 | -0.08091 | 0 | 0 | 0 | -0.35365 | -0.0091306 | -0.0045658 | 0.021083 | 0.047401 | 0.065833 | 0.1741 | 0.2112 | 0.18806 | 0.18564 | 0.19026 | 0.18648 | 0.2023 | 0.20469 | 0.2144 | 0.22128 | 0.2223 | 0.2235 | 0.22711 | 0.23077 | 0.23448 | 0.23824 | 0.24205 | 0.2459 | 0.24981 | 0.25377
[35 empty] | Cessnock 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx3 | 0 | 0 | -0.081032 | 0 | 0 | 0 | -0.35419 | -0.0091444 | -0.0045727 | 0.021114 | 0.047473 | 0.065933 | 0.17436 | 0.21152 | 0.18834 | 0.18592 | 0.19054 | 0.18676 | 0.2026 | 0.205 | 0.21472 | 0.22161 | 0.22264 | 0.22384 | 0.22746 | 0.23112 | 0.23483 | 0.2386 | 0.24241 | 0.24627 | 0.25019 | 0.25415
[35 empty] | Cessnock 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Kurri 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx1 | 0 | 0 | 0 | 0 | -7.4857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Kurri 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx2 | 0 | 0 | 0 | 0 | -7.4447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Kurri 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx3 | 0 | 0 | 0 | 0 | -7.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Kurri 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Maitland 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2327 | -0.0050858 | 0.017023 | 0.041223 | 0.057247 | 0.092764 | 0.12336 | 0.11558 | 0.11274 | 0.11567 | 0.11034 | 0.12329 | 0.12446 | 0.13292 | 0.13834 | 0.1384 | 0.13824 | 0.14057 | 0.14292 | 0.14531 | 0.14773 | 0.15018 | 0.15266 | 0.15518 | 0.15773
| Diversity Factor: 0 | [33 empty] | Maitland 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2041 | -0.0050579 | 0.01693 | 0.040998 | 0.056934 | 0.092257 | 0.12269 | 0.11494 | 0.11212 | 0.11504 | 0.10973 | 0.12262 | 0.12378 | 0.13219 | 0.13758 | 0.13765 | 0.13749 | 0.1398 | 0.14214 | 0.14451 | 0.14692 | 0.14936 | 0.15183 | 0.15433 | 0.15687
[35 empty] | Maitland 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2119 | -0.0050656 | 0.016956 | 0.04106 | 0.057019 | 0.092396 | 0.12287 | 0.11512 | 0.11229 | 0.11521 | 0.1099 | 0.1228 | 0.12397 | 0.13239 | 0.13779 | 0.13785 | 0.13769 | 0.14001 | 0.14235 | 0.14473 | 0.14714 | 0.14958 | 0.15205 | 0.15456 | 0.1571
[35 empty] | Maitland 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Maitland Central 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx1 | 0 | -1.0805 | 0 | -0.13311 | 0 | 0 | 0.20998 | -4.4737 | -0.002837 | -0.0071459 | -0.0077546 | -0.0072189 | -0.0069402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Maitland Central 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx2 | 0 | -1.0746 | 0 | -0.13238 | 0 | 0 | 0.20883 | -4.4493 | -0.0028215 | -0.0071068 | -0.0077121 | -0.0071794 | -0.0069022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Maitland Central 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx3 | 0 | -1.0762 | 0 | -0.13258 | 0 | 0 | 0.20915 | -4.456 | -0.0028257 | -0.0071175 | -0.0077237 | -0.0071903 | -0.0069126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Maitland Central 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Nulkaba 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx1 | 0.27737 | 0 | 0.24892 | 0.085344 | 0 | 0.11201 | 0.3556 | -0.014376 | -0.0065095 | -0.0022011 | 0.0036722 | 0.00361 | 0.028146 | 0.062098 | 0.069318 | 0.065225 | 0.06759 | 0.059851 | 0.073959 | 0.074378 | 0.083734 | 0.089251 | 0.08842 | 0.087112 | 0.088891 | 0.090695 | 0.092524 | 0.094379 | 0.096261 | 0.098169 | 0.1001 | 0.10207
| Diversity Factor: 0 | [33 empty] | Nulkaba 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx2 | 0.27585 | 0 | 0.24756 | 0.084877 | 0 | 0.1114 | 0.35365 | -0.014297 | -0.0064739 | -0.0021891 | 0.0036521 | 0.0035903 | 0.027992 | 0.061758 | 0.068938 | 0.064868 | 0.067221 | 0.059524 | 0.073555 | 0.073971 | 0.083275 | 0.088763 | 0.087936 | 0.086636 | 0.088404 | 0.090198 | 0.092018 | 0.093863 | 0.095734 | 0.097632 | 0.099556 | 0.10151
[35 empty] | Nulkaba 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx3 | 0.27627 | 0 | 0.24793 | 0.085005 | 0 | 0.11157 | 0.35419 | -0.014319 | -0.0064836 | -0.0021924 | 0.0036576 | 0.0035957 | 0.028034 | 0.061851 | 0.069042 | 0.064966 | 0.067322 | 0.059614 | 0.073666 | 0.074083 | 0.083401 | 0.088897 | 0.088069 | 0.086766 | 0.088538 | 0.090334 | 0.092156 | 0.094004 | 0.095878 | 0.097779 | 0.099706 | 0.10166
[35 empty] | Nulkaba 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Paxton 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00088304 | 0.00014106 | 0.0063466 | 0.011676 | 0.016367 | 0.036385 | 0.043011 | 0.03713 | 0.036994 | 0.038224 | 0.038879 | 0.041618 | 0.042358 | 0.043524 | 0.044682 | 0.045136 | 0.045897 | 0.046735 | 0.047585 | 0.048446 | 0.04932 | 0.050205 | 0.051103 | 0.052013 | 0.052936
| Diversity Factor: 0 | [33 empty] | Paxton 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00087821 | 0.00014029 | 0.0063118 | 0.011612 | 0.016277 | 0.036186 | 0.042776 | 0.036927 | 0.036792 | 0.038015 | 0.038666 | 0.04139 | 0.042126 | 0.043285 | 0.044438 | 0.044889 | 0.045646 | 0.04648 | 0.047324 | 0.048181 | 0.04905 | 0.04993 | 0.050823 | 0.051729 | 0.052647
[35 empty] | Paxton 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00087953 | 0.0001405 | 0.0063213 | 0.01163 | 0.016302 | 0.03624 | 0.04284 | 0.036982 | 0.036847 | 0.038072 | 0.038724 | 0.041452 | 0.04219 | 0.043351 | 0.044505 | 0.044957 | 0.045715 | 0.04655 | 0.047396 | 0.048254 | 0.049124 | 0.050006 | 0.0509 | 0.051807 | 0.052726
[35 empty] | Paxton 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Rutherford 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx1 | 0 | -0.11445 | -0.25255 | 0 | 1.1036 | 0 | 0.20065 | -0.021773 | 0.2497 | 0.048706 | 0.11795 | 0.16519 | 0.3 | 0.35833 | 0.30962 | 0.31151 | 0.31704 | 0.30777 | 0.33025 | 0.33316 | 0.34924 | 0.35963 | 0.36088 | 0.36133 | 0.36637 | 0.37147 | 0.37664 | 0.38187 | 0.38717 | 0.39253 | 0.39796 | 0.40346
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Rutherford 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx2 | 0 | -0.11382 | -0.25116 | 0 | 1.0976 | 0 | 0.19956 | -0.021654 | 0.24834 | 0.04844 | 0.1173 | 0.16428 | 0.29836 | 0.35637 | 0.30793 | 0.3098 | 0.3153 | 0.30609 | 0.32844 | 0.33133 | 0.34733 | 0.35766 | 0.35891 | 0.35935 | 0.36436 | 0.36944 | 0.37458 | 0.37978 | 0.38505 | 0.39038 | 0.39578 | 0.40125
[10 empty] | ROG Justification | [24 empty] | Rutherford 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx3 | 0 | -0.11399 | -0.25154 | 0 | 1.0992 | 0 | 0.19986 | -0.021686 | 0.24871 | 0.048513 | 0.11748 | 0.16453 | 0.29881 | 0.3569 | 0.30839 | 0.31027 | 0.31578 | 0.30655 | 0.32893 | 0.33183 | 0.34785 | 0.3582 | 0.35945 | 0.35989 | 0.36491 | 0.37 | 0.37514 | 0.38035 | 0.38563 | 0.39097 | 0.39638 | 0.40185
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 4.073% |  | Weighted ROG calculation based on downstream zone substations and customers | [24 empty] | Rutherford 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weighted ROG calculation based on downstream zone substations and customers
[35 empty] | Telarah 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx1 | 0 | 0.36619 | 0.25255 | 0 | -1.1036 | 0.12026 | 0.32427 | -0.77182 | -0.71243 | 0.030524 | 0.065501 | 0.094428 | 0.14974 | 0.17068 | 0.14838 | 0.14593 | 0.14947 | 0.14946 | 0.15873 | 0.1609 | 0.16608 | 0.1703 | 0.17165 | 0.17347 | 0.17619 | 0.17896 | 0.18176 | 0.18459 | 0.18747 | 0.19038 | 0.19333 | 0.19632
[35 empty] | Telarah 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx2 | 0 | 0.36419 | 0.25116 | 0 | -1.0976 | 0.1196 | 0.32249 | -0.76759 | -0.70854 | 0.030357 | 0.065143 | 0.093911 | 0.14892 | 0.16974 | 0.14757 | 0.14513 | 0.14865 | 0.14864 | 0.15786 | 0.16002 | 0.16517 | 0.16937 | 0.17071 | 0.17252 | 0.17523 | 0.17798 | 0.18076 | 0.18358 | 0.18644 | 0.18934 | 0.19227 | 0.19524
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Telarah 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx3 | 0 | 0.36474 | 0.25154 | 0 | -1.0992 | 0.11978 | 0.32298 | -0.76875 | -0.7096 | 0.030403 | 0.065241 | 0.094053 | 0.14915 | 0.17 | 0.14779 | 0.14535 | 0.14888 | 0.14886 | 0.1581 | 0.16026 | 0.16542 | 0.16962 | 0.17097 | 0.17278 | 0.17549 | 0.17825 | 0.18103 | 0.18386 | 0.18672 | 0.18962 | 0.19256 | 0.19554
0.97949 | 0.95933 | 0.94622 | 0.93976 | 0.93976 | 0.93976 | 0.93976 | 0.93976 | 0.93976 | 0.93976 | -2.051% | -2.058% | -1.367% | -0.682% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Telarah 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Tomalpin 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8107e-05 | -2.0125e-05 | -3.4258e-05 | -3.7117e-05 | -5.6014e-05 | -5.2564e-05 | 6.2834e-06 | 4.5666e-05 | 3.5312e-05 | 3.5286e-05 | 9.1176e-06 | 3.4112e-05 | 3.1503e-05 | 5.2568e-05 | 6.2355e-05 | 5.7922e-05 | 5.0121e-05 | 5.0953e-05 | 5.1795e-05 | 5.2647e-05 | 5.3509e-05 | 5.4382e-05 | 5.5264e-05 | 5.6158e-05 | 5.7062e-05
| Substation Load Detail | [33 empty] | Tomalpin 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7844e-05 | -2.0015e-05 | -3.4071e-05 | -3.6914e-05 | -5.5707e-05 | -5.2277e-05 | 6.2491e-06 | 4.5416e-05 | 3.5119e-05 | 3.5093e-05 | 9.0677e-06 | 3.3925e-05 | 3.1331e-05 | 5.228e-05 | 6.2014e-05 | 5.7606e-05 | 4.9846e-05 | 5.0674e-05 | 5.1512e-05 | 5.2359e-05 | 5.3216e-05 | 5.4084e-05 | 5.4962e-05 | 5.585e-05 | 5.6749e-05
[35 empty] | Tomalpin 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7916e-05 | -2.0045e-05 | -3.4122e-05 | -3.697e-05 | -5.5791e-05 | -5.2355e-05 | 6.2585e-06 | 4.5485e-05 | 3.5172e-05 | 3.5146e-05 | 9.0814e-06 | 3.3976e-05 | 3.1378e-05 | 5.2359e-05 | 6.2107e-05 | 5.7692e-05 | 4.9922e-05 | 5.075e-05 | 5.1589e-05 | 5.2438e-05 | 5.3297e-05 | 5.4166e-05 | 5.5045e-05 | 5.5934e-05 | 5.6835e-05
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Tomalpin 33_11kV Spots and Transfers |  | Kurri 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Kurri 132_33kV | Compensated |  | Load (LV side) |  |  | Amps | 1513 |  | 1554.54 | 1497.35 | 1482.87 | 1487.4 | 1508.11 | 1548.66 | 1599.4 | 1644.88 | 1689.83 | 1735.84 | 1780.51 | 1829.23 | 1878.47 | 1930.33 | 1983.95 | 2037.74 | 2091.67 | 2146.46 | 2202.12 | 2258.65 | 2316.07 | 2286.56 | 2343.73 | 2401.89 | 2461.05
|  |  |  | Apparent Power |  |  | MVA | 86.49 |  | 88.8543 | 85.5854 | 84.7576 | 85.0166 | 86.2001 | 88.5181 | 91.4185 | 94.0178 | 96.5869 | 99.2166 | 101.7699 | 104.555 | 107.3694 | 110.3334 | 113.398 | 116.4725 | 119.5553 | 122.6869 | 125.868 | 129.0993 | 132.3814 | 130.6948 | 133.9623 | 137.2867 | 140.6684
|  |  |  | Real Power |  |  | MW | 83.2899 | 87.5271 | 85.5667 | 82.4187 | 81.6216 | 81.8709 | 83.0107 | 85.2429 | 88.036 | 90.5391 | 93.0132 | 95.5456 | 98.0045 | 100.6864 | 103.3967 | 106.2511 | 109.2023 | 112.1631 | 115.1317 | 118.1475 | 121.2109 | 124.3226 | 127.4833 | 130.6936 | 133.9541 | 137.2654 | 140.6284
|  |  |  | Reactive Power |  |  | MVAr | 23.3092 |  | 23.9464 | 23.0654 | 22.8423 | 22.9121 | 23.231 | 23.8557 | 24.6374 | 25.3379 | 26.0303 | 26.739 | 27.4271 | 28.1777 | 28.9362 | 29.735 | 30.5609 | 31.3895 | 32.2203 | 33.0643 | 33.9216 | 34.7925 | 35.677 | 0.5754 | 1.4879 | 2.4146 | 3.3557
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36 | 36 | 36
|  |  |  | PF |  |  |  | 0.963 |  | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.99999 | 0.99994 | 0.99984 | 0.99972
0.99168 | Diversity Factor: 0.99 | Uncompensated |  | Reactive Power |  |  | MVAr | 23.3092 | 24.495 | 23.9464 | 23.0654 | 22.8423 | 22.9121 | 23.231 | 23.8557 | 24.6374 | 25.3379 | 26.0303 | 26.739 | 27.4271 | 28.1777 | 28.9362 | 29.735 | 30.5609 | 31.3895 | 32.2203 | 33.0643 | 33.9216 | 34.7925 | 35.677 | 36.5754 | 37.4879 | 38.4146 | 39.3557
|  |  |  | PF |  |  |  | 0.963 |  | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Merewether 132_33kV
| Merewether 132_33kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 274.4 | 275.5 | 238 | 204.8 | 187.885 | 168.822 | 141.453 |  | 140.8535 | 127.4694 | 125.6944 | 124.6716 | 124.9089 | 125.7563 | 127.7681 | 129.9227 | 131.9656 | 134.0751 | 135.9687 | 138.2548 | 140.5541 | 143.1167 | 145.8347 | 148.5318 | 151.1937 | 153.907 | 156.6724 | 159.4907 | 162.3626 | 165.2888 | 168.2701 | 171.3072 | 174.4009 |  |  | Total | 2.8966 | -5.4204 | -0.9526 | -20.4045 | -20.3743 | 5.6326 | -22.3828 | -3.013 | -14.3358 | 0.89299 | 0.29328 | 0.23732 | 0.84742 | 2.012 | 2.1547 | 2.043 | 2.1096 | 1.8938 | 2.2862 | 2.2995 | 2.5627 | 2.7181 | 2.6972 | 2.662 | 2.7134 | 2.7656 | 2.8184 | 2.872 | 2.9263 | 2.9814 | 3.0372 | 3.0939
| Firm Rating | 0 | 0 | 0 | 274 | 274 | 274.36 | 274.36 |  | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36 | 274.36
| Total Capacity | 0 | 0 | 0 | 360 | 360 | 412 | 412 |  | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 |  |  | Merewether 132_33kV Tx1 | 1.0067 | -1.8838 | -0.33106 | -7.0913 | -7.0808 | 1.9575 | -7.7788 | -1.0471 | -4.9822 | 0.31035 | 0.10193 | 0.082476 | 0.29451 | 0.69923 | 0.74883 | 0.71003 | 0.73315 | 0.65816 | 0.79454 | 0.79915 | 0.89062 | 0.94465 | 0.93737 | 0.92515 | 0.94302 | 0.96113 | 0.97949 | 0.99812 | 1.017 | 1.0361 | 1.0555 | 1.0752
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Merewether 132_33kV Tx2 | 1.0071 | -1.8846 | -0.33121 | -7.0945 | -7.084 | 1.9584 | -7.7823 | -1.0476 | -4.9844 | 0.31049 | 0.10197 | 0.082513 | 0.29464 | 0.69954 | 0.74916 | 0.71035 | 0.73347 | 0.65845 | 0.79489 | 0.7995 | 0.89102 | 0.94508 | 0.93779 | 0.92557 | 0.94344 | 0.96156 | 0.97993 | 0.99856 | 1.0175 | 1.0366 | 1.056 | 1.0757
| Transformer Loads | [35 empty] | Merewether 132_33kV Tx3 | 0.88282 | -1.652 | -0.29033 | -6.2187 | -6.2095 | 1.7167 | -6.8217 | -0.91827 | -4.3692 | 0.27216 | 0.089385 | 0.072327 | 0.25827 | 0.61319 | 0.65669 | 0.62267 | 0.64294 | 0.57717 | 0.69677 | 0.70081 | 0.78103 | 0.82842 | 0.82203 | 0.81132 | 0.82698 | 0.84287 | 0.85897 | 0.8753 | 0.89186 | 0.90864 | 0.92566 | 0.94292
| Historical Loads | (MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Adamstown 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | -0.6243 | -0.6243 | -0.19407 | -1.5095 | -6.6543 | -0.60493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Adamstown 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | -0.62458 | -0.62458 | -0.19415 | -1.5101 | -6.6573 | -0.60521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Adamstown 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | -0.54749 | -0.54749 | -0.17019 | -1.3237 | -5.8355 | -0.5305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broadmeadow 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | -0.27249 | 0.13256 | 0.23963 | 0 | -0.41481 | 1.1273 | -0.39753 | -2.0154 | -3.3184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Broadmeadow 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | -0.27261 | 0.13262 | 0.23974 | 0 | -0.415 | 1.1278 | -0.39771 | -2.0163 | -3.3198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broadmeadow 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | -0.23896 | 0.11625 | 0.21014 | 0 | -0.36377 | 0.98861 | -0.34861 | -1.7674 | -2.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Carrington 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | -0.016472 | 0.15134 | 0 | 0 | 0 | 0 | 0 | 0.49426 | 0.25472 | 0.0032414 | -7.3359 | 0 | 0 | -0.0085328 | -0.0086259 | -0.0069083 | -0.0069837 | -0.0070599 | -0.007137 | -0.0072149 | -0.0072936 | -0.0073732 | -0.0074537 | -0.0075351 | -0.0076173 | -0.0077005 | -0.0077845 | -0.0078695 | -0.0079554 | -0.0080422 | -0.00813 | -0.0082187
[35 empty] | Carrington 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | -0.016479 | 0.15141 | 0 | 0 | 0 | 0 | 0 | 0.49448 | 0.25483 | 0.0032429 | -7.3392 | 0 | 0 | -0.0085366 | -0.0086297 | -0.0069114 | -0.0069868 | -0.0070631 | -0.0071402 | -0.0072181 | -0.0072969 | -0.0073765 | -0.0074571 | -0.0075385 | -0.0076207 | -0.0077039 | -0.007788 | -0.007873 | -0.0079589 | -0.0080458 | -0.0081336 | -0.0082224
| 0 | [33 empty] | Carrington 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | -0.014445 | 0.13272 | 0 | 0 | 0 | 0 | 0 | 0.43344 | 0.22337 | 0.0028426 | -6.4333 | 0 | 0 | -0.0074828 | -0.0075645 | -0.0060583 | -0.0061244 | -0.0061912 | -0.0062588 | -0.0063271 | -0.0063962 | -0.006466 | -0.0065366 | -0.0066079 | -0.00668 | -0.0067529 | -0.0068267 | -0.0069012 | -0.0069765 | -0.0070526 | -0.0071296 | -0.0072074
| Diversity Factor: 0 | [33 empty] | Charlestown 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0 | -0.19111 | -0.2066 | 0.22212 | 0.29615 | 0.285 | -5.9502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Charlestown 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0 | -0.1912 | -0.20669 | 0.22222 | 0.29629 | 0.28512 | -5.9528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Charlestown 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0 | -0.1676 | -0.18118 | 0.19479 | 0.25971 | 0.24993 | -5.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Dudley 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7786 | -0.036729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Dudley 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7799 | -0.036746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Dudley 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4367 | -0.03221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Gateshead 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0 | -0.36682 | -1.3173 | 0 | 0 | 0 | 0.4953 | 0.069252 | 0.021124 | 0.036646 | 0.026151 | 0.028497 | 0.071222 | 0.11497 | 0.10909 | 0.10619 | 0.10939 | 0.10463 | 0.11793 | 0.11922 | 0.12747 | 0.13291 | 0.13301 | 0.13307 | 0.13547 | 0.13789 | 0.14036 | 0.14285 | 0.14538 | 0.14795 | 0.15055 | 0.15318
| 0 | [33 empty] | Gateshead 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0 | -0.36698 | -1.3179 | 0 | 0 | 0 | 0.49552 | 0.069283 | 0.021133 | 0.036662 | 0.026163 | 0.02851 | 0.071253 | 0.11502 | 0.10914 | 0.10624 | 0.10944 | 0.10467 | 0.11798 | 0.11927 | 0.12753 | 0.13297 | 0.13307 | 0.13313 | 0.13553 | 0.13796 | 0.14042 | 0.14292 | 0.14545 | 0.14801 | 0.15062 | 0.15325
| Diversity Factor: 0 | [33 empty] | Gateshead 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0 | -0.32168 | -1.1552 | 0 | 0 | 0 | 0.43435 | 0.06073 | 0.018525 | 0.032137 | 0.022933 | 0.024991 | 0.062458 | 0.10082 | 0.095666 | 0.093126 | 0.095929 | 0.091751 | 0.10342 | 0.10455 | 0.11179 | 0.11656 | 0.11664 | 0.1167 | 0.1188 | 0.12093 | 0.12309 | 0.12528 | 0.12749 | 0.12974 | 0.13202 | 0.13434
[35 empty] | Jewells 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0.30291 | -0.97165 | 0 | 0 | 0 | 0 | 0 | -0.0045201 | -0.0026705 | 0.015605 | 0.033138 | 0.044261 | 0.091441 | 0.12171 | 0.11104 | 0.10913 | 0.11261 | 0.11063 | 0.12206 | 0.12378 | 0.13016 | 0.13487 | 0.13549 | 0.13651 | 0.139 | 0.14152 | 0.14408 | 0.14667 | 0.1493 | 0.15197 | 0.15468 | 0.15742
[35 empty] | Jewells 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0.30304 | -0.97208 | 0 | 0 | 0 | 0 | 0 | -0.0045221 | -0.0026717 | 0.015612 | 0.033153 | 0.044281 | 0.091481 | 0.12176 | 0.11109 | 0.10918 | 0.11266 | 0.11068 | 0.12212 | 0.12383 | 0.13021 | 0.13493 | 0.13556 | 0.13657 | 0.13906 | 0.14158 | 0.14414 | 0.14674 | 0.14937 | 0.15204 | 0.15475 | 0.15749
| 0 | [33 empty] | Jewells 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0.26563 | -0.85209 | 0 | 0 | 0 | 0 | 0 | -0.0039639 | -0.0023419 | 0.013685 | 0.029061 | 0.038815 | 0.080189 | 0.10673 | 0.09738 | 0.095702 | 0.098754 | 0.097022 | 0.10705 | 0.10855 | 0.11414 | 0.11827 | 0.11882 | 0.11971 | 0.12189 | 0.12411 | 0.12635 | 0.12863 | 0.13093 | 0.13327 | 0.13564 | 0.13805
| Diversity Factor: 0 | [33 empty] | Kotara 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0.29298 | 0.96281 | -0.15982 | 0 | -0.59917 | 0.60598 | 0.069532 | -0.021914 | -0.01052 | -0.0070351 | -0.0012171 | -0.01416 | -0.0056446 | 0.056988 | 0.072883 | 0.06685 | 0.069477 | 0.057504 | 0.07653 | 0.076597 | 0.089631 | 0.096977 | 0.095381 | 0.092871 | 0.094886 | 0.096929 | 0.099002 | 0.1011 | 0.10324 | 0.1054 | 0.1076 | 0.10982
[35 empty] | Kotara 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0.29311 | 0.96324 | -0.15989 | 0 | -0.59944 | 0.60626 | 0.069563 | -0.021924 | -0.010525 | -0.0070383 | -0.0012176 | -0.014166 | -0.0056471 | 0.057014 | 0.072916 | 0.06688 | 0.069508 | 0.057529 | 0.076564 | 0.076631 | 0.089671 | 0.097021 | 0.095424 | 0.092912 | 0.094928 | 0.096973 | 0.099047 | 0.10115 | 0.10328 | 0.10545 | 0.10764 | 0.10987
[35 empty] | Kotara 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0.25693 | 0.84434 | -0.14015 | 0 | -0.52545 | 0.53142 | 0.060976 | -0.019217 | -0.0092258 | -0.0061695 | -0.0010673 | -0.012418 | -0.00495 | 0.049976 | 0.063915 | 0.058625 | 0.060928 | 0.050428 | 0.067113 | 0.067172 | 0.078602 | 0.085045 | 0.083645 | 0.081443 | 0.08321 | 0.085002 | 0.08682 | 0.088664 | 0.090535 | 0.092432 | 0.094356 | 0.096307
| 0 | [33 empty] | New Lambton 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0 | -0.7194 | 0.55505 | -0.3106 | 0 | 0 | -0.33545 | 0.13937 | -0.95584 | 0.0033184 | 0.009205 | 0.010294 | 0.018779 | 0.043632 | 0.046593 | 0.04434 | 0.046401 | 0.043252 | 0.052194 | 0.052869 | 0.058065 | 0.061489 | 0.061298 | 0.06119 | 0.062572 | 0.063974 | 0.065397 | 0.06684 | 0.068304 | 0.06979 | 0.071298 | 0.072827
| Diversity Factor: 0 | [33 empty] | New Lambton 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0 | -0.71972 | 0.55529 | -0.31074 | 0 | 0 | -0.3356 | 0.13943 | -0.95626 | 0.0033199 | 0.0092091 | 0.010298 | 0.018787 | 0.043651 | 0.046614 | 0.04436 | 0.046422 | 0.043271 | 0.052218 | 0.052893 | 0.058091 | 0.061517 | 0.061325 | 0.061218 | 0.0626 | 0.064003 | 0.065426 | 0.06687 | 0.068335 | 0.069822 | 0.07133 | 0.07286
[35 empty] | New Lambton 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0 | -0.63088 | 0.48675 | -0.27239 | 0 | 0 | -0.29418 | 0.12222 | -0.83822 | 0.0029101 | 0.0080723 | 0.0090271 | 0.016468 | 0.038263 | 0.04086 | 0.038884 | 0.040692 | 0.03793 | 0.045772 | 0.046364 | 0.05092 | 0.053923 | 0.053755 | 0.053661 | 0.054873 | 0.056102 | 0.05735 | 0.058615 | 0.0599 | 0.061203 | 0.062525 | 0.063866
[35 empty] | Newcastle CBD 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0 | 0 | 0.21913 | 0.16294 | 0.21913 | 0.47197 | 1.1181 | -0.06968 | 0.1347 | 0.24531 | -0.015452 | -0.027905 | 0.0040858 | 0.13019 | 0.1795 | 0.16067 | 0.16528 | 0.12757 | 0.1767 | 0.17529 | 0.21178 | 0.23103 | 0.2256 | 0.21633 | 0.22055 | 0.22482 | 0.22915 | 0.23354 | 0.238 | 0.24251 | 0.24709 | 0.25172
| 0 | [33 empty] | Newcastle CBD 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0 | 0 | 0.21923 | 0.16302 | 0.21923 | 0.47219 | 1.1186 | -0.069711 | 0.13477 | 0.24542 | -0.015459 | -0.027918 | 0.0040877 | 0.13025 | 0.17958 | 0.16075 | 0.16535 | 0.12763 | 0.17678 | 0.17536 | 0.21187 | 0.23113 | 0.2257 | 0.21643 | 0.22064 | 0.22492 | 0.22925 | 0.23365 | 0.2381 | 0.24262 | 0.2472 | 0.25184
| Diversity Factor: 0 | [33 empty] | Newcastle CBD 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0 | 0 | 0.19217 | 0.14289 | 0.19217 | 0.4139 | 0.98055 | -0.061106 | 0.11813 | 0.21513 | -0.013551 | -0.024471 | 0.0035831 | 0.11417 | 0.15741 | 0.1409 | 0.14494 | 0.11187 | 0.15496 | 0.15372 | 0.18572 | 0.2026 | 0.19784 | 0.18971 | 0.19341 | 0.19716 | 0.20096 | 0.20481 | 0.20871 | 0.21267 | 0.21668 | 0.22075
[35 empty] | Newcastle City Main 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0.86778 | 0.47297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Newcastle City Main 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0.86817 | 0.47318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Newcastle City Main 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0.76101 | 0.41477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Pelican 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0.45629 | -0.73017 | 0 | 0 | 0 | 0 | 0 | 0.40291 | -0.0040398 | -0.0013097 | 0.0013966 | -0.0041748 | 0.0012367 | 0.031693 | 0.037715 | 0.035126 | 0.036811 | 0.032481 | 0.041512 | 0.041868 | 0.047502 | 0.050943 | 0.050454 | 0.049825 | 0.050987 | 0.052166 | 0.053363 | 0.054577 | 0.055808 | 0.057058 | 0.058326 | 0.059613
[10 empty] | ROG Justification | [24 empty] | Pelican 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0.45649 | -0.7305 | 0 | 0 | 0 | 0 | 0 | 0.40309 | -0.0040416 | -0.0013102 | 0.0013972 | -0.0041767 | 0.0012372 | 0.031707 | 0.037731 | 0.035142 | 0.036827 | 0.032496 | 0.041531 | 0.041887 | 0.047523 | 0.050965 | 0.050477 | 0.049848 | 0.05101 | 0.05219 | 0.053387 | 0.054601 | 0.055833 | 0.057084 | 0.058353 | 0.05964
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 4.042% |  | Weighted ROG calculation based on downstream zone substations and customers | [24 empty] | Pelican 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0.40014 | -0.64033 | 0 | 0 | 0 | 0 | 0 | 0.35333 | -0.0035427 | -0.0011485 | 0.0012247 | -0.0036611 | 0.0010845 | 0.027793 | 0.033074 | 0.030804 | 0.032281 | 0.028484 | 0.036404 | 0.036716 | 0.041657 | 0.044674 | 0.044246 | 0.043694 | 0.044713 | 0.045747 | 0.046797 | 0.047861 | 0.048941 | 0.050037 | 0.05115 | 0.052278 | Weighted ROG calculation based on downstream zone substations and customers
[35 empty] | STS Change: Cardiff 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0 | 0 | 0 | -5.8006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Cardiff 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0 | 0 | 0 | -5.8032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | STS Change: Cardiff 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0 | 0 | 0 | -5.0869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.96793 | 0.93733 | 0.91772 | 0.90811 | 0.90811 | 0.90811 | 0.90811 | 0.90811 | 0.90811 | 0.90811 | -3.207% | -3.161% | -2.093% | -1.047% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Swansea 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0 | 0 | 0.53295 | 0.14434 | 0.07217 | 0.07217 | 0 | -0.0046659 | -0.0024991 | 0.014569 | 0.031465 | 0.043725 | 0.090342 | 0.11463 | 0.10397 | 0.10228 | 0.10531 | 0.10329 | 0.11347 | 0.11498 | 0.12084 | 0.12509 | 0.12566 | 0.12648 | 0.12871 | 0.13097 | 0.13326 | 0.13558 | 0.13793 | 0.14032 | 0.14274 | 0.14519
[35 empty] | Swansea 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0 | 0 | 0.53319 | 0.1444 | 0.072202 | 0.072202 | 0 | -0.004668 | -0.0025003 | 0.014576 | 0.031479 | 0.043744 | 0.090382 | 0.11469 | 0.10401 | 0.10232 | 0.10536 | 0.10334 | 0.11352 | 0.11503 | 0.12089 | 0.12515 | 0.12571 | 0.12654 | 0.12877 | 0.13103 | 0.13332 | 0.13564 | 0.138 | 0.14038 | 0.1428 | 0.14525
| Substation Load Detail | [33 empty] | Swansea 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0 | 0 | 0.46737 | 0.12658 | 0.06329 | 0.06329 | 0 | -0.0040918 | -0.0021916 | 0.012777 | 0.027593 | 0.038345 | 0.079226 | 0.10053 | 0.091174 | 0.089691 | 0.092355 | 0.09058 | 0.099511 | 0.10083 | 0.10597 | 0.1097 | 0.1102 | 0.11092 | 0.11288 | 0.11486 | 0.11686 | 0.1189 | 0.12096 | 0.12305 | 0.12517 | 0.12732
[35 empty] | Tighes Hill 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3532 | 0.0019382 | 0.023049 | 0.093944 | 0.096668 | 0.092351 | 0.094848 | 0.085862 | 0.10127 | 0.10177 | 0.11248 | 0.11872 | 0.11792 | 0.11641 | 0.11847 | 0.12055 | 0.12267 | 0.12481 | 0.12698 | 0.12918 | 0.13141 | 0.13367
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Tighes Hill 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3564 | 0.0019391 | 0.023059 | 0.093986 | 0.096711 | 0.092392 | 0.094891 | 0.0859 | 0.10132 | 0.10182 | 0.11253 | 0.11877 | 0.11797 | 0.11646 | 0.11852 | 0.12061 | 0.12272 | 0.12487 | 0.12704 | 0.12924 | 0.13147 | 0.13373
1 | Merewether 132_33kV | Compensated |  | Load (LV side) |  |  | Amps | 2475 |  | 2464.29 | 2230.13 | 2199.08 | 2181.18 | 2185.34 | 2200.16 | 2235.36 | 2273.05 | 2308.8 | 2345.7 | 2378.83 | 2418.83 | 2459.06 | 2503.89 | 2551.44 | 2598.63 | 2645.2 | 2692.67 | 2741.05 | 2790.36 | 2840.6 | 2891.8 | 2943.96 | 2997.09 | 3051.22 | Tighes Hill 33_11kV Spots and Transfers |  | Merewether 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4484 | 0.0016997 | 0.020213 | 0.082384 | 0.084773 | 0.080987 | 0.083177 | 0.075297 | 0.088809 | 0.089247 | 0.098638 | 0.10411 | 0.10341 | 0.10209 | 0.10389 | 0.10572 | 0.10757 | 0.10945 | 0.11136 | 0.11329 | 0.11524 | 0.11722
|  |  |  | Apparent Power |  |  | MVA | 141.453 |  | 140.8535 | 127.4694 | 125.6944 | 124.6716 | 124.9089 | 125.7563 | 127.7681 | 129.9227 | 131.9656 | 134.0751 | 135.9687 | 138.2548 | 140.5541 | 143.1167 | 145.8347 | 148.5318 | 151.1937 | 153.907 | 156.6724 | 159.4907 | 162.3626 | 165.2888 | 168.2701 | 171.3072 | 174.4009 | Tubemakers 33kV transferred to 11kV connectio Spots and Transfers |  | Merewether 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 141.061 | 148.4375 | 140.789 | 122.5972 | 120.8872 | 119.9026 | 120.1301 | 120.9424 | 122.8709 | 124.9363 | 126.8946 | 128.9167 | 130.732 | 132.9234 | 135.1275 | 137.584 | 140.1894 | 142.7748 | 145.3265 | 147.9274 | 150.5783 | 153.2799 | 156.0328 | 158.8378 | 161.6956 | 164.6069 | 167.5725 | Tubemakers 33kV transferred to 11kV connectio Spots and Transfers |  | Merewether 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 10.5238 |  | 4.2631 | 34.9054 | 34.4293 | 34.1524 | 34.22 | 34.4615 | 35.0348 | 35.6488 | 36.2309 | 36.8321 | 37.3717 | 38.0231 | 38.6784 | 39.4086 | 40.1831 | 40.9517 | 41.7103 | 42.4834 | 43.2715 | 44.0746 | 44.893 | 45.7268 | 46.5763 | 47.4418 | 48.3234 | Tubemakers 33kV transferred to 11kV connectio Spots and Transfers |  | Merewether 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.96362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 31.41 |  | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.99723 |  | 0.99954 | 0.96178 | 0.96176 | 0.96175 | 0.96174 | 0.96172 | 0.96167 | 0.96162 | 0.96157 | 0.96153 | 0.96149 | 0.96144 | 0.96139 | 0.96134 | 0.96129 | 0.96124 | 0.96119 | 0.96115 | 0.9611 | 0.96106 | 0.96101 | 0.96097 | 0.96093 | 0.96089 | 0.96085
0.92394 | Diversity Factor: 0.92 | Uncompensated |  | Reactive Power |  |  | MVAr | 41.9338 | 42.4841 | 40.2631 | 34.9054 | 34.4293 | 34.1524 | 34.22 | 34.4615 | 35.0348 | 35.6488 | 36.2309 | 36.8321 | 37.3717 | 38.0231 | 38.6784 | 39.4086 | 40.1831 | 40.9517 | 41.7103 | 42.4834 | 43.2715 | 44.0746 | 44.893 | 45.7268 | 46.5763 | 47.4418 | 48.3234
|  |  |  | PF |  |  |  | 0.95854 |  | 0.96146 | 0.96178 | 0.96176 | 0.96175 | 0.96174 | 0.96172 | 0.96167 | 0.96162 | 0.96157 | 0.96153 | 0.96149 | 0.96144 | 0.96139 | 0.96134 | 0.96129 | 0.96124 | 0.96119 | 0.96115 | 0.9611 | 0.96106 | 0.96101 | 0.96097 | 0.96093 | 0.96089 | 0.96085
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Mitchell Line 132_66kV
| Mitchell Line 132_66kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 34.6 | 38.2 | 40.3 | 54 | 65.618 | 65.479 | 70.99 |  | 69.9618 | 78.015 | 77.7292 | 78.95 | 79.1725 | 79.375 | 79.8298 | 80.3224 | 80.7888 | 81.2724 | 81.7085 | 82.2385 | 82.7723 | 83.3671 | 83.9987 | 84.6257 | 85.2458 | 85.8786 | 86.5242 | 87.1828 | 87.8546 | 88.5398 | 89.2385 | 89.951 | 90.6774 |  |  | Total | 0 | 0 | 3.8574 | 12.329 | 9.6221 | 3.1749 | 0.70523 | 0.30765 | 8.5262 | 0.06058 | 1.3925 | 0.22258 | 0.20252 | 0.45479 | 0.4926 | 0.46644 | 0.48356 | 0.43608 | 0.52997 | 0.53389 | 0.59478 | 0.63155 | 0.62704 | 0.62014 | 0.63279 | 0.64561 | 0.65861 | 0.6718 | 0.68517 | 0.69873 | 0.71249 | 0.72644
| Firm Rating | 0 | 0 | 0 | 149 | 149 | 149.64 | 149.64 |  | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64 | 149.64
| Total Capacity | 0 | 0 | 0 | 240 | 240 | 299 | 299 |  | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 299 |  |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 1.9349 | 6.1844 | 4.8266 | 1.5926 | 0.35376 | 0.15432 | 4.2769 | 0.030388 | 0.69851 | 0.11165 | 0.10159 | 0.22813 | 0.24709 | 0.23397 | 0.24256 | 0.21875 | 0.26584 | 0.26781 | 0.29835 | 0.3168 | 0.31453 | 0.31108 | 0.31742 | 0.32385 | 0.33037 | 0.33698 | 0.34369 | 0.3505 | 0.3574 | 0.36439
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 1.9225 | 6.1446 | 4.7955 | 1.5823 | 0.35147 | 0.15333 | 4.2493 | 0.030192 | 0.694 | 0.11093 | 0.10093 | 0.22666 | 0.2455 | 0.23246 | 0.241 | 0.21734 | 0.26413 | 0.26608 | 0.29643 | 0.31475 | 0.3125 | 0.30907 | 0.31537 | 0.32176 | 0.32824 | 0.33481 | 0.34148 | 0.34824 | 0.35509 | 0.36204
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Aberdeen 66_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35376 | -0.0074888 | 1.6681 | 0.001198 | 0.0068704 | 0.0089589 | 0.0087742 | 0.025751 | 0.030523 | 0.028396 | 0.029494 | 0.025423 | 0.032465 | 0.032596 | 0.037307 | 0.040037 | 0.039545 | 0.038783 | 0.039607 | 0.040443 | 0.041291 | 0.042151 | 0.043024 | 0.043909 | 0.044806 | 0.045716
| Diversity Factor: 0 | [33 empty] | Aberdeen 66_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35147 | -0.0074406 | 1.6574 | 0.0011903 | 0.0068261 | 0.0089011 | 0.0087176 | 0.025585 | 0.030326 | 0.028212 | 0.029304 | 0.025259 | 0.032255 | 0.032386 | 0.037066 | 0.039779 | 0.03929 | 0.038532 | 0.039351 | 0.040182 | 0.041025 | 0.041879 | 0.042746 | 0.043625 | 0.044517 | 0.045422
[35 empty] | Baerami 33_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 0 | 0.030413 | 0 | 0 | 0 | -0.0011573 | -0.0005011 | -0.00017346 | 0.00039391 | 0.00046062 | 0.00039022 | 0.0023678 | 0.0031286 | 0.0028467 | 0.0029286 | 0.0023033 | 0.0031332 | 0.0031129 | 0.0037258 | 0.0040515 | 0.0039632 | 0.003812 | 0.0038859 | 0.0039608 | 0.0040367 | 0.0041137 | 0.0041917 | 0.0042708 | 0.004351 | 0.0044323
[35 empty] | Baerami 33_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 0 | 0.030217 | 0 | 0 | 0 | -0.0011498 | -0.00049787 | -0.00017234 | 0.00039137 | 0.00045765 | 0.00038771 | 0.0023525 | 0.0031084 | 0.0028283 | 0.0029098 | 0.0022884 | 0.003113 | 0.0030928 | 0.0037018 | 0.0040254 | 0.0039376 | 0.0037875 | 0.0038609 | 0.0039353 | 0.0040107 | 0.0040872 | 0.0041647 | 0.0042433 | 0.004323 | 0.0044037
| 0 | [33 empty] | Bengalla Mine 4MVA Increase Spots and Transfers |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 1.5926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Bengalla Mine 4MVA Increase Spots and Transfers |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 1.5823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Denman 66_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 0.12835 | 0 | 0 | 0 | 0 | -0.0060025 | -0.002742 | 0.0053712 | 0.014525 | 0.019956 | 0.018231 | 0.033249 | 0.035168 | 0.033449 | 0.034591 | 0.031402 | 0.037655 | 0.037928 | 0.042024 | 0.044495 | 0.044213 | 0.043759 | 0.044618 | 0.045489 | 0.046373 | 0.047269 | 0.048178 | 0.049099 | 0.050033 | 0.05098
[35 empty] | Denman 66_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 0.12752 | 0 | 0 | 0 | 0 | -0.0059638 | -0.0027244 | 0.0053366 | 0.014432 | 0.019827 | 0.018113 | 0.033035 | 0.034941 | 0.033233 | 0.034367 | 0.0312 | 0.037412 | 0.037684 | 0.041753 | 0.044208 | 0.043928 | 0.043477 | 0.04433 | 0.045196 | 0.046074 | 0.046964 | 0.047867 | 0.048782 | 0.04971 | 0.050652
| 0 | [33 empty] | Drayton South Mine Development (onto new 66kV Spots and Transfers |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Drayton South Mine Development (onto new 66kV Spots and Transfers |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Mangoola (Anvil Hill) Spots and Transfers |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 0 | 0 | 4.8266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Mangoola (Anvil Hill) Spots and Transfers |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 0 | 0 | 4.7955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Merriwa 33_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0022974 | -0.0011263 | 0.0032861 | 0.007816 | 0.010747 | 0.010485 | 0.018733 | 0.019425 | 0.018583 | 0.019358 | 0.018121 | 0.021513 | 0.021773 | 0.023784 | 0.0251 | 0.025037 | 0.02499 | 0.025524 | 0.026066 | 0.026615 | 0.027173 | 0.027738 | 0.028312 | 0.028894 | 0.029484
| Diversity Factor: 0 | [33 empty] | Merriwa 33_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0022826 | -0.001119 | 0.0032649 | 0.0077656 | 0.010678 | 0.010417 | 0.018613 | 0.019299 | 0.018463 | 0.019233 | 0.018004 | 0.021374 | 0.021632 | 0.02363 | 0.024938 | 0.024876 | 0.024829 | 0.02536 | 0.025898 | 0.026444 | 0.026998 | 0.027559 | 0.028129 | 0.028707 | 0.029294
[35 empty] | Mitchell Line 66_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 1.8066 | 0 | 0 | 0 | 0 | 0.18323 | 0.11072 | 0.01166 | 0.033452 | 0.037985 | 0.030952 | 0.079257 | 0.083886 | 0.079726 | 0.082212 | 0.074026 | 0.088772 | 0.089276 | 0.099237 | 0.10511 | 0.10434 | 0.103 | 0.10495 | 0.10692 | 0.10893 | 0.11096 | 0.11301 | 0.1151 | 0.11721 | 0.11936
[35 empty] | Mitchell Line 66_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 1.7949 | 0 | 0 | 0 | 0 | 0.18205 | 0.11001 | 0.011585 | 0.033236 | 0.03774 | 0.030753 | 0.078746 | 0.083345 | 0.079212 | 0.081682 | 0.073549 | 0.0882 | 0.0887 | 0.098597 | 0.10443 | 0.10366 | 0.10234 | 0.10427 | 0.10624 | 0.10822 | 0.11024 | 0.11228 | 0.11436 | 0.11646 | 0.11859
| 0 | [33 empty] | STS Change: Moonan 33_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Moonan 33_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Rouchel 33_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Rouchel 33_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Scone 66_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx1 | 0 | 0 | 0 | 6.154 | 0 | 0 | 0 | -0.011964 | -0.0056562 | 0.0090462 | 0.024745 | 0.033541 | 0.032756 | 0.068772 | 0.074964 | 0.070973 | 0.073979 | 0.067471 | 0.082305 | 0.083122 | 0.092273 | 0.098003 | 0.097437 | 0.096728 | 0.098831 | 0.10096 | 0.10313 | 0.10532 | 0.10755 | 0.10981 | 0.1121 | 0.11443
| Diversity Factor: 0 | [33 empty] | Scone 66_11kV Spots and Transfers |  | Mitchell Line 132_66kV Tx2 | 0 | 0 | 0 | 6.1144 | 0 | 0 | 0 | -0.011887 | -0.0056197 | 0.0089878 | 0.024585 | 0.033325 | 0.032545 | 0.068328 | 0.074481 | 0.070515 | 0.073502 | 0.067036 | 0.081774 | 0.082586 | 0.091678 | 0.097371 | 0.096808 | 0.096104 | 0.098193 | 0.10031 | 0.10246 | 0.10464 | 0.10686 | 0.1091 | 0.11138 | 0.11369
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 3.967% |  | Weighted ROG calculation based on downstream zone substations and customers | [59 empty] | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.99496 | 0.98823 | 0.98385 | 0.98167 | 0.98167 | 0.98167 | 0.98167 | 0.98167 | 0.98167 | 0.98167 | -0.504% | -0.676% | -0.444% | -0.221% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Mitchell Line 132_66kV | Compensated |  | Load (LV side) |  |  | Amps | 621 |  | 612.0073 | 682.4546 | 679.9544 | 690.6329 | 692.58 | 694.3515 | 698.3299 | 702.6389 | 706.7192 | 710.9492 | 714.7639 | 719.3999 | 724.0702 | 729.2731 | 734.7977 | 740.2828 | 745.7076 | 751.243 | 756.8906 | 762.6519 | 768.5286 | 774.5222 | 780.6345 | 786.8671 | 793.2218
|  |  |  | Apparent Power |  |  | MVA | 70.99 |  | 69.9618 | 78.015 | 77.7292 | 78.95 | 79.1725 | 79.375 | 79.8298 | 80.3224 | 80.7888 | 81.2724 | 81.7085 | 82.2385 | 82.7723 | 83.3671 | 83.9987 | 84.6257 | 85.2458 | 85.8786 | 86.5242 | 87.1828 | 87.8546 | 88.5398 | 89.2385 | 89.951 | 90.6774
|  |  |  | Real Power |  |  | MW | 67.4405 | 66.405 | 66.3626 | 74.0139 | 73.7428 | 74.9027 | 75.1142 | 75.3066 | 75.7386 | 76.2066 | 76.6497 | 77.1091 | 77.5234 | 78.0268 | 78.534 | 79.0991 | 79.699 | 80.2947 | 80.8839 | 81.485 | 82.0983 | 82.724 | 83.3622 | 84.0131 | 84.6769 | 85.3538 | 86.0439
|  |  |  | Reactive Power |  |  | MVAr | 22.1666 |  | 22.151 | 24.6635 | 24.5729 | 24.9535 | 25.023 | 25.0862 | 25.2282 | 25.382 | 25.5277 | 25.6786 | 25.8148 | 25.9803 | 26.147 | 26.3327 | 26.5299 | 26.7257 | 26.9194 | 27.1169 | 27.3185 | 27.5242 | 27.734 | 27.9479 | 28.1661 | 28.3885 | 28.6154
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.95 |  | 0.94855 | 0.94871 | 0.94871 | 0.94874 | 0.94874 | 0.94874 | 0.94875 | 0.94876 | 0.94877 | 0.94877 | 0.94878 | 0.94879 | 0.9488 | 0.9488 | 0.94881 | 0.94882 | 0.94883 | 0.94884 | 0.94885 | 0.94886 | 0.94887 | 0.94888 | 0.94888 | 0.94889 | 0.9489
0.87499 | Diversity Factor: 0.87 | Uncompensated |  | Reactive Power |  |  | MVAr | 22.1666 | 21.8263 | 22.151 | 24.6635 | 24.5729 | 24.9535 | 25.023 | 25.0862 | 25.2282 | 25.382 | 25.5277 | 25.6786 | 25.8148 | 25.9803 | 26.147 | 26.3327 | 26.5299 | 26.7257 | 26.9194 | 27.1169 | 27.3185 | 27.5242 | 27.734 | 27.9479 | 28.1661 | 28.3885 | 28.6154
|  |  |  | PF |  |  |  | 0.95 |  | 0.94855 | 0.94871 | 0.94871 | 0.94874 | 0.94874 | 0.94874 | 0.94875 | 0.94876 | 0.94877 | 0.94877 | 0.94878 | 0.94879 | 0.9488 | 0.9488 | 0.94881 | 0.94882 | 0.94883 | 0.94884 | 0.94885 | 0.94886 | 0.94887 | 0.94888 | 0.94888 | 0.94889 | 0.9489
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Muswellbrook 132_33kV
| Muswellbrook 132_33kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 40.1 | 40.3 | 32.3 | 23.6 | 19.271 | 18.587 | 16.56 |  | 15.5885 | 11.6878 | 11.4474 | 1.1632 | 1.1656 | 1.1679 | 1.1796 | 1.1945 | 1.2082 | 1.2223 | 1.2341 | 1.2497 | 1.2653 | 1.2835 | 1.3033 | 1.3228 | 1.3417 | 1.361 | 1.3808 | 1.4009 | 1.4215 | 1.4425 | 1.464 | 1.4859 | 1.5082 |  |  | Total | 0.40505 | 0.40505 | -2.9149 | -11.3668 | 0 | 0 | -0.70523 | -0.036818 | -3.349 | 0.034633 | -10.2255 | 0.0023772 | 0.002356 | 0.011691 | 0.014927 | 0.013693 | 0.01422 | 0.011752 | 0.01563 | 0.015638 | 0.018308 | 0.019807 | 0.019478 | 0.018956 | 0.019363 | 0.019777 | 0.020196 | 0.020622 | 0.021053 | 0.021491 | 0.021935 | 0.022385
| Firm Rating | 0 | 0 | 0 | 45.4 | 45.4 | 50.87 | 50.87 |  | 50.87 | 50.87 | 50.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 56 | 56 | 76 | 76 |  | 76 | 76 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Muswellbrook 132_33kV Tx1 | 0.10868 | 0.10868 | -0.78206 | -3.0497 | 0 | 0 | -0.18921 | -0.0098783 | -0.89852 | 0.009292 | -2.7435 | 0.00063781 | 0.00063211 | 0.0031366 | 0.0040048 | 0.0036738 | 0.0038152 | 0.003153 | 0.0041935 | 0.0041957 | 0.004912 | 0.0053143 | 0.0052259 | 0.0050858 | 0.0051951 | 0.0053061 | 0.0054186 | 0.0055328 | 0.0056485 | 0.0057659 | 0.005885 | 0.0060058
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Muswellbrook 132_33kV Tx2 | 0.10787 | 0.10787 | -0.77628 | -3.0272 | 0 | 0 | -0.18781 | -0.0098053 | -0.89188 | 0.0092233 | -2.7232 | 0.0006331 | 0.00062744 | 0.0031134 | 0.0039752 | 0.0036467 | 0.003787 | 0.0031297 | 0.0041625 | 0.0041647 | 0.0048756 | 0.005275 | 0.0051873 | 0.0050482 | 0.0051567 | 0.0052669 | 0.0053786 | 0.0054919 | 0.0056068 | 0.0057233 | 0.0058415 | 0.0059614
| Transformer Loads | [35 empty] | Muswellbrook 132_33kV Tx3 | 0.18851 | 0.18851 | -1.3565 | -5.29 | 0 | 0 | -0.3282 | -0.017135 | -1.5586 | 0.016118 | -4.7588 | 0.0011063 | 0.0010965 | 0.0054407 | 0.0069467 | 0.0063725 | 0.0066178 | 0.0054692 | 0.007274 | 0.0072778 | 0.0085202 | 0.0092181 | 0.0090647 | 0.0088217 | 0.0090114 | 0.0092039 | 0.009399 | 0.009597 | 0.0097978 | 0.010002 | 0.010208 | 0.010418
| Historical Loads | (MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Aberdeen 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx1 | 0 | 0 | 0.047303 | 0.076631 | 0 | 0 | -0.18921 | 0 | -0.89403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Aberdeen 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx2 | 0 | 0 | 0.046953 | 0.076064 | 0 | 0 | -0.18781 | 0 | -0.88742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Aberdeen 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx3 | 0 | 0 | 0.082051 | 0.13292 | 0 | 0 | -0.3282 | 0 | -1.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Moonan 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx1 | 0 | 0 | 0 | 0.056574 | 0 | 0 | 0 | -0.00084305 | -0.00037336 | -0.00010966 | 0.00028882 | 0.00032725 | 0.00032465 | 0.0020326 | 0.0026506 | 0.0024223 | 0.0025156 | 0.0020551 | 0.0027649 | 0.0027638 | 0.0032552 | 0.0035294 | 0.0034668 | 0.0033672 | 0.0034399 | 0.0035137 | 0.0035885 | 0.0036644 | 0.0037414 | 0.0038195 | 0.0038987 | 0.003979
| 0 | [33 empty] | Moonan 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx2 | 0 | 0 | 0 | 0.056156 | 0 | 0 | 0 | -0.00083682 | -0.0003706 | -0.00010885 | 0.00028669 | 0.00032483 | 0.00032225 | 0.0020176 | 0.002631 | 0.0024044 | 0.002497 | 0.0020399 | 0.0027445 | 0.0027434 | 0.0032312 | 0.0035034 | 0.0034412 | 0.0033423 | 0.0034145 | 0.0034877 | 0.003562 | 0.0036373 | 0.0037137 | 0.0037912 | 0.0038698 | 0.0039496
| Diversity Factor: 0 | [33 empty] | Moonan 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx3 | 0 | 0 | 0 | 0.098133 | 0 | 0 | 0 | -0.0014623 | -0.00064762 | -0.00019022 | 0.00050098 | 0.00056763 | 0.00056313 | 0.0035257 | 0.0045976 | 0.0042016 | 0.0043636 | 0.0035648 | 0.0047959 | 0.004794 | 0.0056464 | 0.0061221 | 0.0060134 | 0.0058406 | 0.0059668 | 0.0060947 | 0.0062245 | 0.0063562 | 0.0064897 | 0.0066252 | 0.0067625 | 0.0069019
[35 empty] | Muswellbrook 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx1 | 0.10868 | 0.10868 | -0.87851 | 0.10868 | 0 | 0 | 0 | -0.0086649 | -0.0039554 | 0.0093902 | -2.4174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Muswellbrook 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx2 | 0.10787 | 0.10787 | -0.87201 | 0.10787 | 0 | 0 | 0 | -0.0086009 | -0.0039262 | 0.0093208 | -2.3995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Muswellbrook 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx3 | 0.18851 | 0.18851 | -1.5238 | 0.18851 | 0 | 0 | 0 | -0.01503 | -0.006861 | 0.016288 | -4.1931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Rouchel 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00037034 | -0.0001654 | 1.1442e-05 | 0.00024543 | 0.00031057 | 0.00030747 | 0.001104 | 0.0013542 | 0.0012515 | 0.0012996 | 0.0010979 | 0.0014286 | 0.0014319 | 0.0016567 | 0.0017849 | 0.0017591 | 0.0017186 | 0.0017553 | 0.0017924 | 0.0018301 | 0.0018684 | 0.0019071 | 0.0019465 | 0.0019864 | 0.0020268
[35 empty] | Rouchel 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0003676 | -0.00016417 | 1.1357e-05 | 0.00024361 | 0.00030827 | 0.0003052 | 0.0010958 | 0.0013442 | 0.0012423 | 0.00129 | 0.0010898 | 0.0014181 | 0.0014213 | 0.0016445 | 0.0017717 | 0.0017461 | 0.0017059 | 0.0017423 | 0.0017792 | 0.0018166 | 0.0018546 | 0.001893 | 0.0019321 | 0.0019717 | 0.0020119
[35 empty] | Rouchel 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00064238 | -0.0002869 | 1.9846e-05 | 0.00042572 | 0.0005387 | 0.00053333 | 0.001915 | 0.0023491 | 0.0021709 | 0.0022542 | 0.0019044 | 0.0024781 | 0.0024837 | 0.0028737 | 0.003096 | 0.0030513 | 0.0029811 | 0.0030446 | 0.0031091 | 0.0031745 | 0.0032408 | 0.0033081 | 0.0033763 | 0.0034455 | 0.0035157
| 0 | [33 empty] | STS Change: Moonan 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.20621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Moonan 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.20468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Moonan 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.35768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Rouchel 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.12044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | STS Change: Rouchel 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.11955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Rouchel 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.20891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Scone 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx1 | 0 | 0 | 0.049147 | -3.2916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Scone 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx2 | 0 | 0 | 0.048784 | -3.2673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Scone 33_11kV Spots and Transfers |  | Muswellbrook 132_33kV Tx3 | 0 | 0 | 0.08525 | -5.7095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | -1.065% |  | Weighted ROG calculation based on downstream zone substations and customers | [59 empty] | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.96442 | 0.93028 | 0.90839 | 0.90354 | 0.90354 | 0.90354 | 0.90354 | 0.90354 | 0.90354 | 0.90354 | -3.558% | -3.54% | -2.353% | -0.534% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Muswellbrook 132_33kV | Compensated |  | Load (LV side) |  |  | Amps | 290 |  | 272.7278 | 204.4828 | 200.2772 | 20.3509 | 20.3924 | 20.4335 | 20.6376 | 20.8982 | 21.1372 | 21.3854 | 21.5906 | 21.8635 | 22.1366 | 22.4563 | 22.8021 | 23.1423 | 23.4733 | 23.8115 | 24.1569 | 24.5097 | 24.8699 | 25.2377 | 25.6131 | 25.9963 | 26.3874
|  |  |  | Apparent Power |  |  | MVA | 16.56 |  | 15.5885 | 11.6878 | 11.4474 | 1.1632 | 1.1656 | 1.1679 | 1.1796 | 1.1945 | 1.2082 | 1.2223 | 1.2341 | 1.2497 | 1.2653 | 1.2835 | 1.3033 | 1.3228 | 1.3417 | 1.361 | 1.3808 | 1.4009 | 1.4215 | 1.4425 | 1.464 | 1.4859 | 1.5082
|  |  |  | Real Power |  |  | MW | 16.084 | 15.7149 | 15.12 | 11.3321 | 11.0991 | 1.1082 | 1.1106 | 1.1128 | 1.1242 | 1.1387 | 1.152 | 1.1658 | 1.1772 | 1.1924 | 1.2076 | 1.2254 | 1.2446 | 1.2635 | 1.2819 | 1.3007 | 1.32 | 1.3396 | 1.3596 | 1.38 | 1.4009 | 1.4222 | 1.444
|  |  |  | Reactive Power |  |  | MVAr | 3.9419 |  | 3.7929 | 2.8614 | 2.8023 | 0.35334 | 0.35391 | 0.35447 | 0.35725 | 0.3608 | 0.36406 | 0.36745 | 0.37024 | 0.37396 | 0.37769 | 0.38205 | 0.38676 | 0.3914 | 0.39591 | 0.40052 | 0.40523 | 0.41003 | 0.41494 | 0.41995 | 0.42507 | 0.43029 | 0.43562
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.97126 |  | 0.96995 | 0.96957 | 0.96957 | 0.95275 | 0.95279 | 0.95283 | 0.95304 | 0.95329 | 0.95352 | 0.95375 | 0.95393 | 0.95417 | 0.95441 | 0.95468 | 0.95495 | 0.95522 | 0.95547 | 0.95572 | 0.95596 | 0.95621 | 0.95645 | 0.95669 | 0.95692 | 0.95715 | 0.95738
0.93199 | Diversity Factor: 0.93 | Uncompensated |  | Reactive Power |  |  | MVAr | 3.9419 | 3.8514 | 3.7929 | 2.8614 | 2.8023 | 0.35334 | 0.35391 | 0.35447 | 0.35725 | 0.3608 | 0.36406 | 0.36745 | 0.37024 | 0.37396 | 0.37769 | 0.38205 | 0.38676 | 0.3914 | 0.39591 | 0.40052 | 0.40523 | 0.41003 | 0.41494 | 0.41995 | 0.42507 | 0.43029 | 0.43562
|  |  |  | PF |  |  |  | 0.97126 |  | 0.96995 | 0.96957 | 0.96957 | 0.95275 | 0.95279 | 0.95283 | 0.95304 | 0.95329 | 0.95352 | 0.95375 | 0.95393 | 0.95417 | 0.95441 | 0.95468 | 0.95495 | 0.95522 | 0.95547 | 0.95572 | 0.95596 | 0.95621 | 0.95645 | 0.95669 | 0.95692 | 0.95715 | 0.95738
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Muswellbrook North 132_33kV
| Muswellbrook North 132_33kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | [6 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Muswellbrook North 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0% |  | Weighted ROG calculation based on downstream zone substations and customers | [59 empty] | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Muswellbrook North 132_33kV | Compensated |  | Load (LV side) |  |  | Amps | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| #VALUE! | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Singleton 132_66kV
| Singleton 132_66kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 136.2 | 144.8 | 147.9 | 156.7 | 121.1717 | 138.7019 | 155.4949 |  | 131.7422 | 132.2721 | 135.9467 | 144.055 | 144.1767 | 144.3128 | 144.7775 | 145.2914 | 145.7767 | 146.283 | 146.7419 | 147.3062 | 147.8761 | 148.5113 | 149.1874 | 149.8591 | 150.5254 | 151.2064 | 151.9025 | 152.6137 | 153.3404 | 154.0828 | 154.841 | 155.6154 | 156.4062 |  |  | Total | 0 | 0.33132 | 0 | 0.49952 | 0.37941 | 0 | 18.1988 | -5.45 | 1.2807 | 4.2575 | 8.5637 | 0.12491 | 0.13972 | 0.47675 | 0.5273 | 0.4978 | 0.51921 | 0.47056 | 0.57855 | 0.58407 | 0.65102 | 0.69265 | 0.68812 | 0.68233 | 0.69731 | 0.7125 | 0.72792 | 0.74355 | 0.75942 | 0.77551 | 0.79184 | 0.8084
| Firm Rating | 0 | 0 | 0 | 156 | 240 | 300.65 | 300.65 |  | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65 | 300.65
| Total Capacity | 0 | 0 | 0 | 360 | 360 | 446 | 446 |  | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 |  |  | Singleton 132_66kV Tx1 | 0 | 0.11926 | 0 | 0.1798 | 0.13657 | 0 | 6.5507 | -1.9617 | 0.46101 | 1.5325 | 3.0825 | 0.044962 | 0.050292 | 0.17161 | 0.1898 | 0.17918 | 0.18689 | 0.16938 | 0.20825 | 0.21024 | 0.23434 | 0.24932 | 0.24769 | 0.24561 | 0.251 | 0.25647 | 0.26201 | 0.26764 | 0.27335 | 0.27915 | 0.28502 | 0.29098
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Singleton 132_66kV Tx2 | 0 | 0.1036 | 0 | 0.15619 | 0.11864 | 0 | 5.6905 | -1.7042 | 0.40047 | 1.3313 | 2.6778 | 0.039058 | 0.043689 | 0.14907 | 0.16488 | 0.15565 | 0.16235 | 0.14714 | 0.1809 | 0.18263 | 0.20357 | 0.21658 | 0.21517 | 0.21336 | 0.21804 | 0.22279 | 0.22761 | 0.2325 | 0.23746 | 0.24249 | 0.2476 | 0.25278
| Transformer Loads | [35 empty] | Singleton 132_66kV Tx3 | 0 | 0.10846 | 0 | 0.16352 | 0.1242 | 0 | 5.9576 | -1.7841 | 0.41927 | 1.3937 | 2.8034 | 0.040891 | 0.045739 | 0.15607 | 0.17262 | 0.16296 | 0.16997 | 0.15404 | 0.18939 | 0.1912 | 0.21312 | 0.22675 | 0.22526 | 0.22337 | 0.22827 | 0.23325 | 0.23829 | 0.24341 | 0.24861 | 0.25387 | 0.25922 | 0.26464
| Historical Loads | (MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Branxton 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3515 | -0.036421 | -1.0172 | 0.0090211 | 0.017556 | 0.024302 | 0.045173 | 0.061652 | 0.057097 | 0.056016 | 0.058286 | 0.05793 | 0.064659 | 0.065782 | 0.069083 | 0.071741 | 0.07217 | 0.073037 | 0.074536 | 0.076056 | 0.077598 | 0.079163 | 0.08075 | 0.08236 | 0.083993 | 0.085649
| Diversity Factor: 0 | [33 empty] | Branxton 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30535 | -0.031639 | -0.88365 | 0.0078365 | 0.015251 | 0.021111 | 0.039241 | 0.053556 | 0.0496 | 0.048661 | 0.050633 | 0.050324 | 0.056169 | 0.057144 | 0.060012 | 0.062321 | 0.062694 | 0.063446 | 0.064749 | 0.066069 | 0.067409 | 0.068768 | 0.070147 | 0.071546 | 0.072964 | 0.074403
[35 empty] | Branxton 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31968 | -0.033124 | -0.92513 | 0.0082043 | 0.015967 | 0.022102 | 0.041083 | 0.05607 | 0.051928 | 0.050945 | 0.053009 | 0.052686 | 0.058805 | 0.059826 | 0.062828 | 0.065246 | 0.065636 | 0.066424 | 0.067787 | 0.06917 | 0.070573 | 0.071996 | 0.073439 | 0.074903 | 0.076389 | 0.077895
[35 empty] | Bulga Coal Optimisation Load Increase Spots and Transfers |  | Singleton 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5182 | 3.0364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Bulga Coal Optimisation Load Increase Spots and Transfers |  | Singleton 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3188 | 2.6377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Bulga Coal Optimisation Load Increase Spots and Transfers |  | Singleton 132_66kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3807 | 2.7615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Bulga-Beltana Coal Methane Gas Generators 9MW Spots and Transfers |  | Singleton 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Bulga-Beltana Coal Methane Gas Generators 9MW Spots and Transfers |  | Singleton 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Bulga-Beltana Coal Methane Gas Generators 9MW Spots and Transfers |  | Singleton 132_66kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Lemington 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx1 | 0 | 0 | 0 | 0.069495 | 0 | 0 | 0 | -0.0012486 | -0.00054929 | -0.00045287 | -0.00013455 | -0.00038913 | -0.00051109 | 0.0018232 | 0.0028201 | 0.0025033 | 0.0025928 | 0.0019097 | 0.0028235 | 0.0027975 | 0.0034624 | 0.0038152 | 0.0037128 | 0.0035445 | 0.0036211 | 0.0036987 | 0.0037775 | 0.0038573 | 0.0039383 | 0.0040204 | 0.0041037 | 0.0041881
[35 empty] | Lemington 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx2 | 0 | 0 | 0 | 0.06037 | 0 | 0 | 0 | -0.0010847 | -0.00047716 | -0.00039341 | -0.00011688 | -0.00033804 | -0.00044398 | 0.0015838 | 0.0024498 | 0.0021746 | 0.0022524 | 0.001659 | 0.0024527 | 0.0024302 | 0.0030077 | 0.0033142 | 0.0032252 | 0.0030791 | 0.0031456 | 0.0032131 | 0.0032814 | 0.0033508 | 0.0034212 | 0.0034925 | 0.0035648 | 0.0036382
[35 empty] | Lemington 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx3 | 0 | 0 | 0 | 0.063203 | 0 | 0 | 0 | -0.0011356 | -0.00049956 | -0.00041187 | -0.00012237 | -0.0003539 | -0.00046481 | 0.0016581 | 0.0025648 | 0.0022767 | 0.0023581 | 0.0017368 | 0.0025679 | 0.0025443 | 0.0031489 | 0.0034698 | 0.0033766 | 0.0032236 | 0.0032932 | 0.0033639 | 0.0034355 | 0.0035081 | 0.0035817 | 0.0036564 | 0.0037322 | 0.003809
| 0 | [33 empty] | Mitchells Flat 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00038573 | 0.00010417 | 0.0015364 | 0.0026969 | 0.0037867 | 0.0032604 | 0.0046529 | 0.0042594 | 0.0042076 | 0.0044618 | 0.0046609 | 0.0052063 | 0.005345 | 0.0055086 | 0.0057084 | 0.0057796 | 0.0059389 | 0.0060871 | 0.0062376 | 0.0063904 | 0.0065455 | 0.0067029 | 0.0068627 | 0.0070249 | 0.0071896
| Diversity Factor: 0 | [33 empty] | Mitchells Flat 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00033508 | 9.0492e-05 | 0.0013347 | 0.0023428 | 0.0032895 | 0.0028323 | 0.0040419 | 0.0037001 | 0.0036551 | 0.0038759 | 0.0040489 | 0.0045227 | 0.0046432 | 0.0047853 | 0.0049588 | 0.0050207 | 0.0051591 | 0.0052879 | 0.0054186 | 0.0055513 | 0.005686 | 0.0058228 | 0.0059616 | 0.0061025 | 0.0062456
[35 empty] | Mitchells Flat 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0003508 | 9.4739e-05 | 0.0013973 | 0.0024528 | 0.0034439 | 0.0029652 | 0.0042316 | 0.0038738 | 0.0038267 | 0.0040578 | 0.0042389 | 0.004735 | 0.0048611 | 0.0050098 | 0.0051916 | 0.0052564 | 0.0054012 | 0.005536 | 0.0056729 | 0.0058118 | 0.0059529 | 0.006096 | 0.0062414 | 0.0063889 | 0.0065387
[35 empty] | Mt Thorley 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx1 | 0 | 0.11926 | 0 | 0 | 0 | 0 | 0 | -0.0082993 | 0.046088 | -0.004301 | -0.003339 | -0.013368 | -0.017 | 0.0095504 | 0.016195 | 0.014168 | 0.014619 | 0.010085 | 0.015732 | 0.015493 | 0.019722 | 0.021909 | 0.021209 | 0.020037 | 0.020458 | 0.020885 | 0.021318 | 0.021757 | 0.022202 | 0.022654 | 0.023111 | 0.023575
| 0 | [33 empty] | Mt Thorley 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx2 | 0 | 0.1036 | 0 | 0 | 0 | 0 | 0 | -0.0072095 | 0.040036 | -0.0037363 | -0.0029005 | -0.011613 | -0.014768 | 0.0082964 | 0.014069 | 0.012308 | 0.012699 | 0.008761 | 0.013666 | 0.013459 | 0.017133 | 0.019032 | 0.018424 | 0.017406 | 0.017772 | 0.018143 | 0.018519 | 0.0189 | 0.019287 | 0.019679 | 0.020077 | 0.02048
| Diversity Factor: 0 | [33 empty] | Mt Thorley 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx3 | 0 | 0.10846 | 0 | 0 | 0 | 0 | 0 | -0.0075479 | 0.041915 | -0.0039116 | -0.0030367 | -0.012158 | -0.015461 | 0.0086858 | 0.014729 | 0.012886 | 0.013295 | 0.0091722 | 0.014308 | 0.01409 | 0.017937 | 0.019926 | 0.019289 | 0.018223 | 0.018606 | 0.018994 | 0.019388 | 0.019787 | 0.020192 | 0.020603 | 0.021019 | 0.021441
[35 empty] | Newdell 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.68988 | -0.00070624 | -0.00082454 | -0.00064377 | -0.0015442 | -0.0017584 | 0.0013981 | 0.0026284 | 0.0022636 | 0.0023191 | 0.001466 | 0.0024425 | 0.0023845 | 0.003144 | 0.0035244 | 0.0033894 | 0.0031579 | 0.0032201 | 0.0032832 | 0.0033471 | 0.0034119 | 0.0034775 | 0.0035441 | 0.0036115 | 0.0036799
[35 empty] | Newdell 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.59929 | -0.0006135 | -0.00071627 | -0.00055924 | -0.0013414 | -0.0015275 | 0.0012146 | 0.0022832 | 0.0019664 | 0.0020146 | 0.0012735 | 0.0021218 | 0.0020714 | 0.0027311 | 0.0030616 | 0.0029444 | 0.0027432 | 0.0027973 | 0.0028521 | 0.0029076 | 0.0029639 | 0.0030209 | 0.0030787 | 0.0031373 | 0.0031967
| 0 | [33 empty] | Newdell 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.62742 | -0.0006423 | -0.00074989 | -0.00058549 | -0.0014044 | -0.0015992 | 0.0012716 | 0.0023904 | 0.0020587 | 0.0021091 | 0.0013333 | 0.0022214 | 0.0021687 | 0.0028593 | 0.0032053 | 0.0030826 | 0.002872 | 0.0029286 | 0.0029859 | 0.003044 | 0.003103 | 0.0031627 | 0.0032232 | 0.0032845 | 0.0033467
| Diversity Factor: 0 | [33 empty] | Ravensworth North Mine Development Spots and Transfers |  | Singleton 132_66kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0626 | 1.4435 | 1.4435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Ravensworth North Mine Development Spots and Transfers |  | Singleton 132_66kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2665 | 1.2539 | 1.2539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Ravensworth North Mine Development Spots and Transfers |  | Singleton 132_66kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5137 | 1.3128 | 1.3128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Singleton 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx1 | 0 | 0 | 0 | -0.47918 | 0.13657 | 0 | -0.11101 | 0.064348 | -0.0089891 | -0.0036898 | 0.0044207 | -0.003333 | -0.0090142 | 0.04043 | 0.054576 | 0.049554 | 0.051376 | 0.040948 | 0.056178 | 0.056015 | 0.066772 | 0.072666 | 0.071202 | 0.06883 | 0.070299 | 0.071788 | 0.073299 | 0.074831 | 0.076385 | 0.07796 | 0.079559 | 0.081179
| Diversity Factor: 0 | [33 empty] | Singleton 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx2 | 0 | 0 | 0 | -0.41626 | 0.11864 | 0 | -0.096437 | 0.055898 | -0.0078088 | -0.0032053 | 0.0038403 | -0.0028953 | -0.0078306 | 0.035121 | 0.04741 | 0.043047 | 0.04463 | 0.035571 | 0.048801 | 0.04866 | 0.058004 | 0.063125 | 0.061853 | 0.059792 | 0.061068 | 0.062362 | 0.063674 | 0.065005 | 0.066355 | 0.067724 | 0.069112 | 0.07052
[35 empty] | Singleton 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx3 | 0 | 0 | 0 | -0.4358 | 0.1242 | 0 | -0.10096 | 0.058522 | -0.0081753 | -0.0033557 | 0.0040205 | -0.0030312 | -0.0081981 | 0.03677 | 0.049635 | 0.045068 | 0.046725 | 0.03724 | 0.051092 | 0.050944 | 0.060726 | 0.066087 | 0.064756 | 0.062599 | 0.063934 | 0.065289 | 0.066663 | 0.068056 | 0.069469 | 0.070902 | 0.072356 | 0.07383
[35 empty] | Singleton North 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx1 | 0 | 0 | 0 | 0.58948 | 0 | 0 | 0.24758 | -0.0013756 | -0.0011971 | 0.013015 | 0.025602 | 0.035507 | 0.030143 | 0.052101 | 0.052224 | 0.050469 | 0.053236 | 0.052378 | 0.061207 | 0.06242 | 0.066644 | 0.069956 | 0.070225 | 0.071061 | 0.072776 | 0.074517 | 0.076284 | 0.078077 | 0.079898 | 0.081745 | 0.08362 | 0.085523
| 0 | [33 empty] | Singleton North 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx2 | 0 | 0 | 0 | 0.51208 | 0 | 0 | 0.21507 | -0.001195 | -0.0010399 | 0.011306 | 0.02224 | 0.030845 | 0.026185 | 0.045259 | 0.045366 | 0.043842 | 0.046246 | 0.0455 | 0.05317 | 0.054224 | 0.057893 | 0.06077 | 0.061004 | 0.06173 | 0.06322 | 0.064732 | 0.066267 | 0.067825 | 0.069407 | 0.071011 | 0.07264 | 0.074293
| Diversity Factor: 0 | [33 empty] | Singleton North 66_11kV Spots and Transfers |  | Singleton 132_66kV Tx3 | 0 | 0 | 0 | 0.53612 | 0 | 0 | 0.22517 | -0.0012511 | -0.0010888 | 0.011837 | 0.023284 | 0.032293 | 0.027414 | 0.047384 | 0.047496 | 0.0459 | 0.048416 | 0.047636 | 0.055666 | 0.056769 | 0.06061 | 0.063622 | 0.063867 | 0.064627 | 0.066187 | 0.067771 | 0.069378 | 0.071009 | 0.072664 | 0.074344 | 0.07605 | 0.07778
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | -0.0032% |  | Weighted ROG calculation based on downstream zone substations and customers | [59 empty] | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.99391 | 0.98882 | 0.98559 | 0.98406 | 0.98406 | 0.98406 | 0.98406 | 0.98406 | 0.98406 | 0.98406 | -0.609% | -0.512% | -0.327% | -0.155% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Singleton 132_66kV | Compensated |  | Load (LV side) |  |  | Amps | 1360 |  | 1152.44 | 1157.08 | 1189.22 | 1260.15 | 1261.21 | 1262.41 | 1266.47 | 1270.97 | 1275.21 | 1279.64 | 1283.65 | 1288.59 | 1293.58 | 1299.13 | 1305.05 | 1310.92 | 1316.75 | 1322.71 | 1328.8 | 1335.02 | 1341.38 | 1347.87 | 1354.5 | 1361.28 | 1368.19
|  |  |  | Apparent Power |  |  | MVA | 155.4949 |  | 131.7422 | 132.2721 | 135.9467 | 144.055 | 144.1767 | 144.3128 | 144.7775 | 145.2914 | 145.7767 | 146.283 | 146.7419 | 147.3062 | 147.8761 | 148.5113 | 149.1874 | 149.8591 | 150.5254 | 151.2064 | 151.9025 | 152.6137 | 153.3404 | 154.0828 | 154.841 | 155.6154 | 156.4062
|  |  |  | Real Power |  |  | MW | 139.9454 | 134.775 | 129.0491 | 129.5411 | 132.9492 | 140.4505 | 140.5629 | 140.6887 | 141.1178 | 141.5923 | 142.0403 | 142.5076 | 142.9311 | 143.4518 | 143.9775 | 144.5634 | 145.1868 | 145.8061 | 146.4202 | 147.0478 | 147.689 | 148.3441 | 149.0133 | 149.6968 | 150.3948 | 151.1074 | 151.835
|  |  |  | Reactive Power |  |  | MVAr | 67.7787 |  | 26.5014 | 26.7396 | 28.3903 | 32.0233 | 32.0778 | 32.1387 | 32.3465 | 32.5763 | 32.7933 | 33.0196 | 33.2247 | 33.4769 | 33.7315 | 34.0153 | 34.3172 | 34.6171 | 34.9146 | 35.2185 | 35.5291 | 35.8464 | 36.1705 | 36.5015 | 36.8395 | 37.1847 | 37.5371
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
|  |  |  | PF |  |  |  | 0.9 |  | 0.97956 | 0.97935 | 0.97795 | 0.97498 | 0.97493 | 0.97489 | 0.97472 | 0.97454 | 0.97437 | 0.97419 | 0.97403 | 0.97383 | 0.97364 | 0.97342 | 0.97318 | 0.97295 | 0.97273 | 0.9725 | 0.97226 | 0.97202 | 0.97178 | 0.97154 | 0.97128 | 0.97103 | 0.97077
0.93262 | Diversity Factor: 0.93 | Uncompensated |  | Reactive Power |  |  | MVAr | 67.7787 | 65.2745 | 62.5014 | 62.7396 | 64.3903 | 68.0233 | 68.0777 | 68.1387 | 68.3465 | 68.5763 | 68.7933 | 69.0196 | 69.2247 | 69.4769 | 69.7315 | 70.0153 | 70.3172 | 70.6171 | 70.9146 | 71.2185 | 71.5291 | 71.8464 | 72.1705 | 72.5015 | 72.8395 | 73.1847 | 73.5371
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Tomago 132_33kV
| Tomago 132_33kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 127.3 | 138.6 | 108 | 106.3 | 103.894 | 102.603 | 89.94 |  | 92.4409 | 91.8921 | 91.3941 | 91.324 | 91.8438 | 92.8668 | 94.4976 | 96.0929 | 97.642 | 99.2441 | 100.7603 | 102.5046 | 104.269 | 106.1753 | 108.1743 | 110.1729 | 112.1702 | 114.2068 | 116.2835 | 118.4006 | 120.5589 | 122.7587 | 125.0008 | 127.2856 | 129.6138 |  |  | Total | 0 | 0 | 1.485 | 3.2034 | 0.73544 | 0.73544 | -7.7484 | 1.2881 | 0.87215 | 0.38981 | 0.36594 | 0.53552 | 1.0536 | 1.678 | 1.6399 | 1.591 | 1.6439 | 1.5546 | 1.7869 | 1.8061 | 1.9496 | 2.0427 | 2.0408 | 2.0378 | 2.0765 | 2.1158 | 2.1556 | 2.196 | 2.237 | 2.2785 | 2.3206 | 2.3633
| Firm Rating | 0 | 0 | 0 | 137.1 | 137.1 | 91.45 | 161.76 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
| Total Capacity | 0 | 0 | 0 | 160 | 160 | 137 | 241 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  | Tomago 132_33kV Tx1 | 0 | 0 | 0.49186 | 1.061 | 0.24359 | 0.24359 | -2.5663 | 0.42664 | 0.28886 | 0.12911 | 0.1212 | 0.17737 | 0.34895 | 0.55576 | 0.54315 | 0.52695 | 0.54447 | 0.51491 | 0.59183 | 0.59819 | 0.64574 | 0.67658 | 0.67593 | 0.67493 | 0.68776 | 0.70077 | 0.71397 | 0.72735 | 0.74091 | 0.75466 | 0.76861 | 0.78275
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Tomago 132_33kV Tx2 | 0 | 0 | 0.49171 | 1.0607 | 0.24351 | 0.24351 | -2.5656 | 0.42651 | 0.28878 | 0.12907 | 0.12116 | 0.17732 | 0.34884 | 0.55559 | 0.54299 | 0.52679 | 0.54431 | 0.51475 | 0.59165 | 0.59801 | 0.64554 | 0.67637 | 0.67573 | 0.67472 | 0.68755 | 0.70056 | 0.71375 | 0.72713 | 0.74069 | 0.75444 | 0.76838 | 0.78251
| Transformer Loads | [35 empty] | Tomago 132_33kV Tx3 | 0 | 0 | 0.50147 | 1.0817 | 0.24835 | 0.24835 | -2.6165 | 0.43498 | 0.29451 | 0.13163 | 0.12357 | 0.18083 | 0.35577 | 0.56662 | 0.55376 | 0.53725 | 0.55511 | 0.52497 | 0.60339 | 0.60988 | 0.65835 | 0.6898 | 0.68914 | 0.68811 | 0.7012 | 0.71446 | 0.72792 | 0.74156 | 0.75539 | 0.76941 | 0.78363 | 0.79804
| Historical Loads | (MVA) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (MVA) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | AGL Gas Storage Facility Tomago Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | AGL Gas Storage Facility Tomago Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | AGL Gas Storage Facility Tomago Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Medowie 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0022502 | 2.1873 | 0.50491 | 0.0026919 | 0.0043287 | 0.0085827 | 0.025106 | 0.026289 | 0.025145 | 0.026422 | 0.025156 | 0.030056 | 0.030534 | 0.033189 | 0.035047 | 0.035031 | 0.035161 | 0.035985 | 0.036822 | 0.037671 | 0.038533 | 0.039407 | 0.040294 | 0.041194 | 0.042108
| 0 | [33 empty] | Medowie 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0022495 | 2.1866 | 0.50476 | 0.0026911 | 0.0043274 | 0.0085801 | 0.025099 | 0.026281 | 0.025137 | 0.026414 | 0.025149 | 0.030047 | 0.030525 | 0.033179 | 0.035037 | 0.03502 | 0.035151 | 0.035975 | 0.036811 | 0.03766 | 0.038521 | 0.039395 | 0.040282 | 0.041182 | 0.042095
| Diversity Factor: 0 | [33 empty] | Medowie 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0022942 | 2.23 | 0.51478 | 0.0027445 | 0.0044132 | 0.0087503 | 0.025597 | 0.026803 | 0.025636 | 0.026938 | 0.025648 | 0.030644 | 0.03113 | 0.033838 | 0.035732 | 0.035715 | 0.035848 | 0.036689 | 0.037541 | 0.038407 | 0.039285 | 0.040177 | 0.041081 | 0.041999 | 0.042931
[35 empty] | Nelson Bay 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0 | 0.56913 | 0 | 0 | -3.822 | 0.0094232 | 0.044639 | -0.00068187 | 0.01068 | 0.014106 | 0.03487 | 0.091415 | 0.10087 | 0.095262 | 0.099314 | 0.090009 | 0.11052 | 0.11156 | 0.12432 | 0.13224 | 0.13137 | 0.13025 | 0.13309 | 0.13598 | 0.13891 | 0.14187 | 0.14489 | 0.14794 | 0.15104 | 0.15418
[35 empty] | Nelson Bay 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0 | 0.56896 | 0 | 0 | -3.8209 | 0.0094203 | 0.044625 | -0.00068166 | 0.010677 | 0.014102 | 0.034859 | 0.091388 | 0.10084 | 0.095233 | 0.099284 | 0.089982 | 0.11049 | 0.11153 | 0.12428 | 0.1322 | 0.13133 | 0.13021 | 0.13305 | 0.13594 | 0.13886 | 0.14183 | 0.14484 | 0.1479 | 0.15099 | 0.15414
| 0 | [33 empty] | Nelson Bay 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0 | 0.58025 | 0 | 0 | -3.8967 | 0.0096073 | 0.045511 | -0.00069519 | 0.010888 | 0.014382 | 0.035551 | 0.093201 | 0.10284 | 0.097123 | 0.10125 | 0.091767 | 0.11268 | 0.11374 | 0.12675 | 0.13482 | 0.13394 | 0.1328 | 0.1357 | 0.13864 | 0.14162 | 0.14465 | 0.14772 | 0.15083 | 0.15399 | 0.15719
| Diversity Factor: 0 | [33 empty] | Raymond Terr NEW 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 6.0321 | 2.3021 | -0.016671 | -0.73286 | 0.018129 | 0.062583 | 0.09393 | 0.18256 | 0.23099 | 0.20883 | 0.20677 | 0.21167 | 0.20393 | 0.22421 | 0.22642 | 0.23976 | 0.24847 | 0.24897 | 0.24916 | 0.25314 | 0.25717 | 0.26126 | 0.26541 | 0.2696 | 0.27386 | 0.27816 | 0.28253
[35 empty] | Raymond Terr NEW 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 6.0303 | 2.3014 | -0.016666 | -0.73264 | 0.018124 | 0.062564 | 0.093902 | 0.18251 | 0.23092 | 0.20876 | 0.2067 | 0.2116 | 0.20386 | 0.22415 | 0.22635 | 0.23968 | 0.24839 | 0.2489 | 0.24908 | 0.25306 | 0.2571 | 0.26118 | 0.26533 | 0.26952 | 0.27377 | 0.27808 | 0.28244
[35 empty] | Raymond Terr NEW 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 6.15 | 2.3471 | -0.016996 | -0.74718 | 0.018483 | 0.063806 | 0.095766 | 0.18613 | 0.2355 | 0.21291 | 0.21081 | 0.2158 | 0.20791 | 0.22859 | 0.23084 | 0.24444 | 0.25332 | 0.25384 | 0.25402 | 0.25809 | 0.2622 | 0.26637 | 0.27059 | 0.27487 | 0.27921 | 0.2836 | 0.28805
| 0 | [33 empty] | Raymond Terrace 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0.49186 | 0.49186 | 0.24359 | -6.4941 | -4.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Raymond Terrace 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0.49171 | 0.49171 | 0.24351 | -6.4921 | -4.4877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Raymond Terrace 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0.50147 | 0.50147 | 0.24835 | -6.6209 | -4.5768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Salt Ash 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.7626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Salt Ash 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.76237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Salt Ash 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.7775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Stockton 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0013634 | -0.0013999 | 0.01201 | 0.026358 | 0.037597 | 0.063842 | 0.076369 | 0.066212 | 0.065786 | 0.067423 | 0.067122 | 0.071711 | 0.072672 | 0.075284 | 0.077336 | 0.07789 | 0.078631 | 0.079886 | 0.081158 | 0.082447 | 0.083753 | 0.085076 | 0.086416 | 0.087775 | 0.089151
[35 empty] | Stockton 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.001363 | -0.0013995 | 0.012006 | 0.02635 | 0.037585 | 0.063823 | 0.076346 | 0.066192 | 0.065766 | 0.067402 | 0.067102 | 0.071689 | 0.07265 | 0.075262 | 0.077313 | 0.077867 | 0.078607 | 0.079862 | 0.081134 | 0.082422 | 0.083727 | 0.08505 | 0.08639 | 0.087748 | 0.089124
| 0 | [33 empty] | Stockton 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0013901 | -0.0014273 | 0.012244 | 0.026873 | 0.038331 | 0.065089 | 0.077861 | 0.067506 | 0.067071 | 0.06874 | 0.068434 | 0.073112 | 0.074092 | 0.076755 | 0.078847 | 0.079412 | 0.080167 | 0.081447 | 0.082744 | 0.084058 | 0.085389 | 0.086738 | 0.088105 | 0.08949 | 0.090893
| Diversity Factor: 0 | [33 empty] | Tanilba Bay 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76062 | -0.0013726 | 0.0046042 | 0.010612 | 0.014813 | 0.024891 | 0.042888 | 0.041944 | 0.040677 | 0.042517 | 0.041457 | 0.047722 | 0.04852 | 0.051774 | 0.054191 | 0.054351 | 0.054794 | 0.055995 | 0.057213 | 0.058449 | 0.059703 | 0.060976 | 0.062267 | 0.063577 | 0.064906
[35 empty] | Tanilba Bay 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76039 | -0.0013722 | 0.0046028 | 0.010609 | 0.014809 | 0.024883 | 0.042876 | 0.041931 | 0.040664 | 0.042505 | 0.041445 | 0.047707 | 0.048505 | 0.051758 | 0.054174 | 0.054334 | 0.054778 | 0.055978 | 0.057196 | 0.058432 | 0.059685 | 0.060958 | 0.062248 | 0.063558 | 0.064886
[35 empty] | Tanilba Bay 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77548 | -0.0013994 | 0.0046942 | 0.010819 | 0.015103 | 0.025377 | 0.043726 | 0.042763 | 0.041471 | 0.043348 | 0.042267 | 0.048654 | 0.049468 | 0.052785 | 0.05525 | 0.055413 | 0.055865 | 0.057089 | 0.058331 | 0.059591 | 0.06087 | 0.062167 | 0.063484 | 0.064819 | 0.066174
| 0 | [33 empty] | Tea Gardens Spur 33kV transfer to Essentials Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Tea Gardens Spur 33kV transfer to Essentials Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Tea Gardens Spur 33kV transfer to Essentials Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | -2.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Tomago 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0.70553 | 2.0822 | 0.44859 | -0.0071498 | 0.090087 | -0.0077504 | -0.0091799 | -0.0060845 | 0.0073354 | 0.013821 | 0.011863 | 0.011975 | 0.0070615 | 0.012057 | 0.011642 | 0.015771 | 0.017751 | 0.016967 | 0.015565 | 0.015814 | 0.016066 | 0.016322 | 0.016581 | 0.016842 | 0.017107 | 0.017376 | 0.017647
| 0 | [33 empty] | Tomago 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0.70532 | 2.0816 | 0.44845 | -0.0071476 | 0.09006 | -0.007748 | -0.0091771 | -0.0060827 | 0.0073331 | 0.013817 | 0.011859 | 0.011972 | 0.0070594 | 0.012053 | 0.011638 | 0.015767 | 0.017746 | 0.016962 | 0.01556 | 0.015809 | 0.016062 | 0.016317 | 0.016576 | 0.016837 | 0.017102 | 0.01737 | 0.017642
| Diversity Factor: 0 | [33 empty] | Tomago 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0.71932 | 2.1229 | 0.45735 | -0.0072895 | 0.091848 | -0.0079018 | -0.0093593 | -0.0062034 | 0.0074787 | 0.014091 | 0.012095 | 0.012209 | 0.0071995 | 0.012293 | 0.011869 | 0.01608 | 0.018098 | 0.017299 | 0.015869 | 0.016123 | 0.01638 | 0.016641 | 0.016904 | 0.017171 | 0.017442 | 0.017715 | 0.017992
[35 empty] | Tomaree 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8871 | -0.0068535 | -0.0035857 | 0.0026088 | 0.010126 | 0.013905 | 0.027239 | 0.056552 | 0.058901 | 0.05631 | 0.058732 | 0.055021 | 0.065489 | 0.066307 | 0.072453 | 0.076501 | 0.076316 | 0.076208 | 0.07786 | 0.079537 | 0.081238 | 0.082964 | 0.084714 | 0.08649 | 0.088292 | 0.090119
[35 empty] | Tomaree 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8859 | -0.0068514 | -0.0035846 | 0.002608 | 0.010123 | 0.013901 | 0.027231 | 0.056535 | 0.058883 | 0.056293 | 0.058714 | 0.055004 | 0.065469 | 0.066287 | 0.072431 | 0.076478 | 0.076293 | 0.076185 | 0.077837 | 0.079513 | 0.081213 | 0.082938 | 0.084689 | 0.086464 | 0.088265 | 0.090092
[35 empty] | Tomaree 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 3.963 | -0.0069874 | -0.0036558 | 0.0026598 | 0.010324 | 0.014177 | 0.027772 | 0.057657 | 0.060051 | 0.05741 | 0.05988 | 0.056096 | 0.066768 | 0.067602 | 0.073869 | 0.077996 | 0.077807 | 0.077697 | 0.079381 | 0.081091 | 0.082825 | 0.084584 | 0.086369 | 0.08818 | 0.090017 | 0.09188
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Williamtown 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0022502 | -2.1903 | -0.50256 | 0.0059016 | 0.007869 | 0.013044 | 0.025106 | 0.026289 | 0.025145 | 0.026422 | 0.025156 | 0.030056 | 0.030534 | 0.033189 | 0.035047 | 0.035031 | 0.035161 | 0.035985 | 0.036822 | 0.037671 | 0.038533 | 0.039407 | 0.040294 | 0.041194 | 0.042108
[10 empty] | ROG Justification | [24 empty] | Williamtown 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0022495 | -2.1896 | -0.50241 | 0.0058998 | 0.0078666 | 0.01304 | 0.025099 | 0.026281 | 0.025137 | 0.026414 | 0.025149 | 0.030047 | 0.030525 | 0.033179 | 0.035037 | 0.03502 | 0.035151 | 0.035975 | 0.036811 | 0.03766 | 0.038521 | 0.039395 | 0.040282 | 0.041182 | 0.042095
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 2.804% |  | Weighted ROG calculation based on downstream zone substations and customers | [24 empty] | Williamtown 33_11kV Spots and Transfers |  | Tomago 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0022942 | -2.2331 | -0.51238 | 0.0060169 | 0.0080227 | 0.013299 | 0.025597 | 0.026803 | 0.025636 | 0.026938 | 0.025648 | 0.030644 | 0.03113 | 0.033838 | 0.035732 | 0.035715 | 0.035848 | 0.036689 | 0.037541 | 0.038407 | 0.039285 | 0.040177 | 0.041081 | 0.041999 | 0.042931 | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.9857 | 0.97162 | 0.96286 | 0.95862 | 0.95862 | 0.95862 | 0.95862 | 0.95862 | 0.95862 | 0.95862 | -1.43% | -1.428% | -0.902% | -0.44% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Tomago 132_33kV | Compensated |  | Load (LV side) |  |  | Amps | 1574 |  | 1617.29 | 1607.69 | 1598.98 | 1597.75 | 1606.84 | 1624.74 | 1653.27 | 1681.18 | 1708.29 | 1736.32 | 1762.84 | 1793.36 | 1824.23 | 1857.58 | 1892.55 | 1927.52 | 1962.46 | 1998.1 | 2034.43 | 2071.47 | 2109.23 | 2147.72 | 2186.94 | 2226.92 | 2267.65
|  |  |  | Apparent Power |  |  | MVA | 89.94 |  | 92.4409 | 91.8921 | 91.3941 | 91.324 | 91.8438 | 92.8668 | 94.4976 | 96.0929 | 97.642 | 99.2441 | 100.7603 | 102.5046 | 104.269 | 106.1753 | 108.1743 | 110.1729 | 112.1702 | 114.2068 | 116.2835 | 118.4006 | 120.5589 | 122.7587 | 125.0008 | 127.2856 | 129.6138
|  |  |  | Real Power |  |  | MW | 87.709 | 90.2933 | 90.1539 | 89.6464 | 89.1864 | 89.1212 | 89.6 | 90.5421 | 92.0426 | 93.509 | 94.9317 | 96.4017 | 97.7918 | 99.3897 | 101.0046 | 102.748 | 104.5746 | 106.3995 | 108.2217 | 110.0786 | 111.9705 | 113.8981 | 115.8618 | 117.8621 | 119.8996 | 121.9747 | 124.088
|  |  |  | Reactive Power |  |  | MVAr | 19.9082 |  | 20.4351 | 20.191 | 19.9669 | 19.9372 | 20.177 | 20.6486 | 21.3997 | 22.1338 | 22.846 | 23.5819 | 24.2779 | 25.0778 | 25.8863 | 26.759 | 27.6734 | 28.587 | 29.4992 | 30.4288 | 31.3759 | 32.3409 | 33.3239 | 34.3253 | 35.3453 | 36.3841 | 37.4421
|  |  |  | Capacitors In Service |  |  | MVAr | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  |  |  | PF |  |  |  | 0.9752 |  | 0.97526 | 0.97556 | 0.97584 | 0.97588 | 0.97557 | 0.97497 | 0.97402 | 0.97311 | 0.97224 | 0.97136 | 0.97054 | 0.96961 | 0.96869 | 0.96772 | 0.96672 | 0.96575 | 0.9648 | 0.96385 | 0.96291 | 0.96197 | 0.96104 | 0.96011 | 0.95919 | 0.95828 | 0.95737
0.93181 | Diversity Factor: 0.93 | Uncompensated |  | Reactive Power |  |  | MVAr | 43.9082 | 44.4947 | 44.4351 | 44.191 | 43.9669 | 43.9372 | 44.177 | 44.6486 | 45.3997 | 46.1338 | 46.846 | 47.5819 | 48.2779 | 49.0778 | 49.8862 | 50.759 | 51.6734 | 52.587 | 53.4992 | 54.4288 | 55.3759 | 56.3409 | 57.3239 | 58.3253 | 59.3453 | 60.3841 | 61.4421
|  |  |  | PF |  |  |  | 0.89421 |  | 0.89697 | 0.89694 | 0.89693 | 0.89692 | 0.89691 | 0.89688 | 0.89684 | 0.8968 | 0.89676 | 0.89672 | 0.89668 | 0.89664 | 0.8966 | 0.89656 | 0.89652 | 0.89648 | 0.89645 | 0.89641 | 0.89637 | 0.89633 | 0.8963 | 0.89626 | 0.89623 | 0.89619 | 0.89616
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer30
| Customer30 | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 58.9 | 58.7 | 58.4 | 59.5 | 57.665 | 58.6886 | 57.2936 |  | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Waratah (Comsteel) 132_33kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Waratah (Comsteel) 132_33kV Tx6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Waratah (Comsteel) 132_33kV Tx7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | -0.0063% |  | Weighted ROG calculation based on downstream zone substations and customers | [59 empty] | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Customer30 | Compensated |  | Load (LV side) |  |  | Amps | 1002 |  | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64 | 1017.64
|  |  |  | Apparent Power |  |  | MVA | 57.2936 |  | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166 | 58.166
|  |  |  | Real Power |  |  | MW | 53.856 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832 | 54.7832
|  |  |  | Reactive Power |  |  | MVAr | 19.5471 |  | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.94 |  | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184
0.64721 | Diversity Factor: 0.65 | Uncompensated |  | Reactive Power |  |  | MVAr | 19.5471 | 19.8836 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471 | 19.5471
|  |  |  | PF |  |  |  | 0.94 |  | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184 | 0.94184
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Waratah (Domestic) 132_33kV
| Waratah (Domestic) 132_33kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [20 empty] | Spots & Transfers Summary | (MVA) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 106.3 | 112.9 | 98.4 | 60.2 | 50.468 | 24.439 | 7.1 |  | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 |  |  | Total | -7.133 | 1.2866 | 1.7612 | -23.2276 | -35.2968 | -36.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 90 | 90 | 90 | 68.59 |  | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59 | 68.59
| Total Capacity | 0 | 0 | 0 | 120 | 120 | 120 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 |  |  | Waratah (Domestic) 132_33kV Tx1 | -1.7772 | 0.32056 | 0.43881 | -5.7873 | -8.7944 | -9.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Waratah (Domestic) 132_33kV Tx2 | -1.738 | 0.31349 | 0.42913 | -5.6596 | -8.6004 | -8.8103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Waratah (Domestic) 132_33kV Tx3 | -1.8453 | 0.33282 | 0.4556 | -6.0088 | -9.131 | -9.3538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (MVA) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (MVA) | [22 empty] | Waratah (Domestic) 132_33kV Tx5 | -1.7725 | 0.3197 | 0.43763 | -5.7718 | -8.7709 | -8.9849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Mayfield 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx1 | 0 | -0.39887 | 0.11184 | -4.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Mayfield 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx2 | 0 | -0.39007 | 0.10937 | -4.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Mayfield 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx3 | 0 | -0.41413 | 0.11612 | -4.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Mayfield 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx5 | 0 | -0.3978 | 0.11154 | -4.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | STS Change: Hexham Metal 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx1 | 0 | 0 | 0 | -1.2402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Hexham Metal 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx2 | 0 | 0 | 0 | -1.2129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Hexham Metal 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx3 | 0 | 0 | 0 | -1.2877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Hexham Metal 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx5 | 0 | 0 | 0 | -1.2369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx1 | 0 | 0 | 0 | 0 | 0 | -4.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx1 | 0 | 0 | 0 | 0 | -4.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx2 | 0 | 0 | 0 | 0 | 0 | -4.8185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx2 | 0 | 0 | 0 | 0 | -4.8185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx3 | 0 | 0 | 0 | 0 | 0 | -5.1158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx3 | 0 | 0 | 0 | 0 | -5.1158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx5 | 0 | 0 | 0 | 0 | 0 | -4.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | STS Change: Kooragang West 33kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx5 | 0 | 0 | 0 | 0 | -4.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Shortland 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx1 | 0.22268 | 0.71943 | 0.1853 | -0.22449 | -2.7498 | -2.1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Shortland 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx2 | 0.21777 | 0.70356 | 0.18121 | -0.21953 | -2.6892 | -2.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Shortland 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx3 | 0.2312 | 0.74696 | 0.19239 | -0.23308 | -2.8551 | -2.2168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Shortland 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx5 | 0.22208 | 0.7175 | 0.1848 | -0.22389 | -2.7425 | -2.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Wallsend 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx1 | -1.9999 | 0 | 0.14167 | 0 | -1.1174 | -1.9467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Wallsend 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx2 | -1.9558 | 0 | 0.13854 | 0 | -1.0927 | -1.9038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Wallsend 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx3 | -2.0765 | 0 | 0.14709 | 0 | -1.1602 | -2.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Wallsend 33_11kV Spots and Transfers |  | Waratah (Domestic) 132_33kV Tx5 | -1.9946 | 0 | 0.14129 | 0 | -1.1144 | -1.9415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0% |  | Weighted ROG calculation based on downstream zone substations and customers | [59 empty] | Weighted ROG calculation based on downstream zone substations and customers
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Waratah (Domestic) 132_33kV | Compensated |  | Load (LV side) |  |  | Amps | 124 |  | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177 | 124.2177
|  |  |  | Apparent Power |  |  | MVA | 7.1 |  | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1
|  |  |  | Real Power |  |  | MW | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39
|  |  |  | Reactive Power |  |  | MVAr | 3.0948 |  | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1 | Diversity Factor: 1 | Uncompensated |  | Reactive Power |  |  | MVAr | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948 | 3.0948
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF