## Inclusions and Exclusions
Sydney Forecast Inclusions and Exclusions
Date Printed |  | 08JUL14:11:21:24
| Description | Value
Season |  | Summer | Summer
Either Summer or Winter
Year |  | 2015 | 2015
Year that the forecast starts
POE |  | 50% | 0.5
10%, 50%, 90%
Spots and Transfers |  | Y | Y
Are Spots and Transfers Included?
BBDM Spots |  | Y | Y
Is BBDM included?
Spots Coefficient |  | 55% | 0.55
Scaling factor applied to spot loads in the future
Aligned ROGs |  | Capped | Capped
Have ROGs been aligned to econometric forecast?
Committed Projects |  | Y | Y
Are Committed Projects Included?
Major Customers Scaling Factor |  | 100% | 1
Scaling factor applied to major customer connections in the future
Future Transfers |  | Y | Y
Are future transfers included?
Future Spots |  | 4 | 4
Future spots are cleared from the following forecast year

## Castle Cove 132_11kV
| Castle Cove 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 3917 | 3934 | 4094 | 4227 | 3417 | 3669 | 3192 |  | 3357.162 | 3302.047 | 3207.038 | 3165.373 | 3158.588 | 3153.318 | 3177.973 | 3217.379 | 3251.57 | 3288.77 | 3316.303 | 3355.972 | 3395.439 | 3443.604 | 3496.487 | 3548.147 | 3597.794 | 3648.57 | 3700.49 | 3753.57 | 3807.826 | 3863.275 | 3919.933 | 3977.817 | 4036.943 |  |  | Total | 0 | 0 | 0 | -70.7986 | -132.7377 | 11.3346 | 13.8011 | 188.5982 | 80.9436 | -6.9062 | 1.1691 | -6.9178 | -5.3741 | 25.1373 | 40.1607 | 34.8313 | 37.8805 | 28.0273 | 40.3652 | 40.1443 | 48.9685 | 53.7396 | 52.4722 | 50.4047 | 51.5287 | 52.6681 | 53.8232 | 54.994 | 56.181 | 57.3842 | 58.6039 | 59.8403
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 4758 |  | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758 | 4758
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 8000 |  | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 |  |  | Castle Cove 132_11kV Tx1 | 16 | 0 | 0 | -29.8 | 124.7873 | -1.6766 | -1.2002 | -5.8604 | 89.518 | -1.9741 | 0.3342 | -1.9774 | -1.5362 | 7.1854 | 11.4798 | 9.9564 | 10.828 | 8.0115 | 11.5383 | 11.4751 | 13.9975 | 15.3613 | 14.999 | 14.408 | 14.7293 | 15.055 | 15.3852 | 15.7199 | 16.0592 | 16.4031 | 16.7517 | 17.1051
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 319.3522 | -166.4112 | -9.3576 | -0.97187 | -27.7453 | -2.779 | -1.5985 | 0.27061 | -1.6012 | -1.2439 | 5.8182 | 9.2955 | 8.062 | 8.7678 | 6.4872 | 9.3429 | 9.2917 | 11.3342 | 12.4385 | 12.1451 | 11.6666 | 11.9268 | 12.1905 | 12.4578 | 12.7288 | 13.0036 | 13.2821 | 13.5644 | 13.8505
| Transformer Loads | [35 empty] | Castle Cove 132_11kV Tx3 | 0 | 0 | 0 | -68.5267 | 35.2264 | -1.1038 | -0.79022 | -3.8583 | -2.2596 | -1.2997 | 0.22003 | -1.3019 | -1.0114 | 4.7307 | 7.558 | 6.5551 | 7.1289 | 5.2746 | 7.5965 | 7.555 | 9.2156 | 10.1135 | 9.875 | 9.4859 | 9.6975 | 9.9119 | 10.1293 | 10.3496 | 10.573 | 10.7994 | 11.029 | 11.2617
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  | Castle Cove 132_11kV Tx4 | -16 | 0 | 0 | -291.8242 | -126.3402 | 23.4727 | 16.7634 | 226.0622 | -3.5359 | -2.0339 | 0.34431 | -2.0373 | -1.5827 | 7.4029 | 11.8273 | 10.2578 | 11.1558 | 8.254 | 11.8875 | 11.8225 | 14.4212 | 15.8263 | 15.453 | 14.8442 | 15.1752 | 15.5107 | 15.8509 | 16.1957 | 16.5453 | 16.8996 | 17.2588 | 17.6229
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.93234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Castle Cove 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.75807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6149. Remedial relief of Panel 11, 16, 17, 34 & 40 Feeders Castle Cove. | Castle Cove 132_11kV Tx1 | Castle Cove 132_11kV Tx4 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6149. Remedial relief of Panel 11, 16, 17, 34 & 40 Feeders Castle Cove. | Castle Cove 132_11kV Tx4 | Castle Cove 132_11kV Tx1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6393. Castle Cove Zone Development - 2008 (Chatswood Business District) | Castle Cove 132_11kV Tx1 | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6393. Castle Cove Zone Development - 2008 (Chatswood Business District) | Castle Cove 132_11kV Tx2 | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6393. Castle Cove Zone Development - 2008 (Chatswood Business District) | Castle Cove 132_11kV Tx4 | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6401. Chatswood Chase Redevelopment (LLC) | Castle Cove 132_11kV Tx4 | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6464. Relieve Remedial Castle Cove Panel 12,24 and 30 Feeders Amend A has been replaced to improve network pick ups for PA 24 and associated panels for futre DNP (DNP 6473). Amend B was issued due to an open point change DNP6885 | Castle Cove 132_11kV Tx1 | Lindfield 33_11kV Tx1 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6464. Relieve Remedial Castle Cove Panel 12,24 and 30 Feeders Amend A has been replaced to improve network pick ups for PA 24 and associated panels for futre DNP (DNP 6473). Amend B was issued due to an open point change DNP6885 | Castle Cove 132_11kV Tx2 | Lindfield 33_11kV Tx1 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6464. Relieve Remedial Castle Cove Panel 12,24 and 30 Feeders Amend A has been replaced to improve network pick ups for PA 24 and associated panels for futre DNP (DNP 6473). Amend B was issued due to an open point change DNP6885 | Castle Cove 132_11kV Tx4 | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6464. Relieve Remedial Castle Cove Panel 12,24 and 30 Feeders Amend A has been replaced to improve network pick ups for PA 24 and associated panels for futre DNP (DNP 6473). Amend B was issued due to an open point change DNP6885 | Castle Cove 132_11kV Tx4 | Castle Cove 132_11kV Tx3 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6473. Castle Cove Zone Development - 2009 (Pa 15, 43 & 44 Feeders) | Castle Cove 132_11kV Tx3 | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006127. Establish customer substation S.35214 Chatswood Station (3x1500kVA), Victoria Ave, Chatswood. Additional load to be added to S.6667 in 2010. |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2007651. Load increases on S.234 Victoria Chatswood Chase, S.5884 Mills Myer and S.5885 Archer David Jones. Load increases are 62A , 27 A and 23 A respectively for a total of 112 A increase |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2010022. Establishment of S.47700 Fullers Pacific, Fullers Rd, Chatswood (dealership on Pacific Hwy) | Castle Cove 132_11kV Tx2 | Lindfield 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010793. Establishment of S.49416 Help Cambridge, 7 Railway Street, Chatswood |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 25.2 | 0 | 55.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011427. C/S SELF ASSESSED DNP - Uprate Existing S.554 Glencroft AV & Loop in HV, Glencroft Road, Roseville | Castle Cove 132_11kV Tx2 | Lindfield 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2011444. Increase load at existing S.7166 Smith Gibbes, 26 Smith St, Chatswood | Castle Cove 132_11kV Tx2 | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2011721. Establishment of S.61404 Fleet Thomas No 2, between S.4391 Fleet Thomas and S.6947 Thomas Telecom, 73 Albert Ave, Chatswood |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012280. Establishment of 3 x Kiosks S.64164 Fleet Albert No 2, S.64163 Fleet Albert No 1 and S.64165 Fleet Thomas No.3, 79-85 Albert Ave, Chatswood |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2014137. Establish S.64881 VICTORIA WESTFIELD, Victoria Avenue, Chatswood |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3765 | 13.8331 | 19.0764 | 18.8959 | 19.5572 | 19.5471 | 19.5263 | 19.8143 | 20.1063 | 20.4023 | 20.7024 | 21.0066 | 21.315 | 21.6276 | 21.9445 | 22.2658 | 22.5915 | 22.9217 | 23.2564 | 23.5957 | 23.9396 | 24.2883 | 24.6417
| Diversity Factor: 0 | [33 empty] | Econometric |  | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.973 | 11.201 | 15.4467 | 15.3005 | 15.836 | 15.8279 | 15.811 | 16.0442 | 16.2807 | 16.5203 | 16.7633 | 17.0096 | 17.2594 | 17.5125 | 17.7691 | 18.0293 | 18.293 | 18.5604 | 18.8314 | 19.1061 | 19.3846 | 19.6669 | 19.9531
[35 empty] | Econometric |  | Castle Cove 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8565 | 9.1074 | 12.5595 | 12.4406 | 12.876 | 12.8694 | 12.8557 | 13.0453 | 13.2375 | 13.4324 | 13.63 | 13.8303 | 14.0333 | 14.2391 | 14.4478 | 14.6593 | 14.8738 | 15.0911 | 15.3115 | 15.5349 | 15.7613 | 15.9909 | 16.2235
[35 empty] | Econometric |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5998 | 14.2518 | 19.6538 | 19.4678 | 20.1492 | 20.1388 | 20.1174 | 20.4141 | 20.7149 | 21.0199 | 21.329 | 21.6424 | 21.9602 | 22.2823 | 22.6088 | 22.9398 | 23.2754 | 23.6155 | 23.9604 | 24.3099 | 24.6643 | 25.0235 | 25.3876
| 0 | [33 empty] | Energy Efficiency |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5902 | -2.0073 | -7.7416 | -11.7333 | -18.0128 | -18.4414 | -10.2876 | -6.0519 | -7.5224 | -7.4197 | -10.2183 | -6.9875 | -7.3507 | -5.1326 | -4.0772 | -4.7521 | -5.66 | -5.66 | -5.66 | -5.66 | -5.66 | -5.66 | -5.66 | -5.66 | -5.66
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7168 | -1.6254 | -6.2686 | -9.5008 | -14.5855 | -14.9325 | -8.3302 | -4.9004 | -6.0911 | -6.0079 | -8.274 | -5.658 | -5.9521 | -4.156 | -3.3014 | -3.8479 | -4.5831 | -4.5831 | -4.5831 | -4.5831 | -4.5831 | -4.5831 | -4.5831 | -4.5831 | -4.5831
[35 empty] | Energy Efficiency |  | Castle Cove 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0221 | -1.3216 | -5.0969 | -7.725 | -11.8592 | -12.1414 | -6.7731 | -3.9844 | -4.9526 | -4.885 | -6.7275 | -4.6004 | -4.8396 | -3.3792 | -2.6843 | -3.1287 | -3.7264 | -3.7264 | -3.7264 | -3.7264 | -3.7264 | -3.7264 | -3.7264 | -3.7264 | -3.7264
[35 empty] | Energy Efficiency |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7291 | -2.068 | -7.9759 | -12.0885 | -18.5581 | -18.9996 | -10.599 | -6.2351 | -7.7502 | -7.6443 | -10.5276 | -7.199 | -7.5733 | -5.2879 | -4.2006 | -4.8959 | -5.8313 | -5.8313 | -5.8313 | -5.8313 | -5.8313 | -5.8313 | -5.8313 | -5.8313 | -5.8313
[35 empty] | Solar PV |  | Castle Cove 132_11kV Tx1 | 0 | 0 | 0 | -0.79996 | -4.2127 | -1.6766 | -1.2002 | -1.2702 | -1.4247 | -1.6091 | -1.7656 | -1.8896 | -1.9907 | -2.0842 | -2.0154 | -2.0475 | -1.5666 | -1.8765 | -1.8765 | -1.8765 | -1.8765 | -1.8765 | -1.8765 | -1.8765 | -1.8765 | -1.8765 | -1.8765 | -1.8765 | -1.8765 | -1.8765 | -1.8765 | -1.8765
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Solar PV |  | Castle Cove 132_11kV Tx2 | 0 | 0 | 0 | -0.64775 | -3.4112 | -1.3576 | -0.97187 | -1.0285 | -1.1536 | -1.3029 | -1.4296 | -1.53 | -1.6119 | -1.6876 | -1.632 | -1.6579 | -1.2685 | -1.5195 | -1.5195 | -1.5195 | -1.5195 | -1.5195 | -1.5195 | -1.5195 | -1.5195 | -1.5195 | -1.5195 | -1.5195 | -1.5195 | -1.5195 | -1.5195 | -1.5195
[10 empty] | ROG Justification | [24 empty] | Solar PV |  | Castle Cove 132_11kV Tx3 | 0 | 0 | 0 | -0.52668 | -2.7736 | -1.1038 | -0.79022 | -0.83626 | -0.938 | -1.0594 | -1.1624 | -1.2441 | -1.3106 | -1.3722 | -1.3269 | -1.348 | -1.0314 | -1.2354 | -1.2354 | -1.2354 | -1.2354 | -1.2354 | -1.2354 | -1.2354 | -1.2354 | -1.2354 | -1.2354 | -1.2354 | -1.2354 | -1.2354 | -1.2354 | -1.2354
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 4.899% |  | 7 year ROG ok | [24 empty] | Solar PV |  | Castle Cove 132_11kV Tx4 | 0 | 0 | 0 | -0.82418 | -4.3402 | -1.7273 | -1.2366 | -1.3086 | -1.4678 | -1.6578 | -1.819 | -1.9468 | -2.0509 | -2.1473 | -2.0764 | -2.1094 | -1.614 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | -1.9333 | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.96 | 0.9216 | 0.89703 | 0.88507 | 0.88507 | 0.88507 | 0.88507 | 0.88507 | 0.88507 | 0.88507 | -4% | -4% | -2.666% | -1.333% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Castle Cove 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 3192 | 3372 | 3357.162 | 3302.047 | 3207.038 | 3165.373 | 3158.588 | 3153.318 | 3177.973 | 3217.379 | 3251.57 | 3288.77 | 3316.303 | 3355.972 | 3395.439 | 3443.604 | 3496.487 | 3548.147 | 3597.794 | 3648.57 | 3700.49 | 3753.57 | 3807.826 | 3863.275 | 3919.933 | 3977.817 | 4036.943
|  |  |  | Apparent Power |  |  | MVA | 60.8158 |  | 63.9625 | 62.9124 | 61.1023 | 60.3085 | 60.1792 | 60.0788 | 60.5485 | 61.2993 | 61.9507 | 62.6595 | 63.1841 | 63.9399 | 64.6918 | 65.6095 | 66.617 | 67.6013 | 68.5472 | 69.5146 | 70.5038 | 71.5151 | 72.5488 | 73.6053 | 74.6848 | 75.7876 | 76.9141
|  |  |  | Real Power |  |  | MW | 59.591 | 62.9514 | 63.9542 | 62.9071 | 61.1006 | 60.3078 | 60.1786 | 60.0783 | 60.5476 | 61.2973 | 61.9476 | 62.6548 | 63.178 | 63.9316 | 64.681 | 65.5952 | 66.5985 | 67.5781 | 68.5191 | 69.481 | 70.4643 | 71.4691 | 72.4958 | 73.5446 | 74.6159 | 75.71 | 76.8272
|  |  |  | Reactive Power |  |  | MVAr | 12.1438 |  | 1.033 | 0.81963 | 0.45149 | 0.28992 | 0.2636 | 0.24315 | 0.33879 | 0.49158 | 0.62409 | 0.76821 | 0.87484 | 1.0284 | 1.1811 | 1.3674 | 1.5719 | 1.7715 | 1.9633 | 2.1593 | 2.3597 | 2.5645 | 2.7737 | 2.9874 | 3.2057 | 3.4287 | 3.6563
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
|  |  |  | PF |  |  |  | 0.97986 |  | 0.99987 | 0.99991 | 0.99997 | 0.99999 | 0.99999 | 0.99999 | 0.99998 | 0.99997 | 0.99995 | 0.99992 | 0.9999 | 0.99987 | 0.99983 | 0.99978 | 0.99972 | 0.99966 | 0.99959 | 0.99952 | 0.99944 | 0.99936 | 0.99927 | 0.99918 | 0.99908 | 0.99898 | 0.99887
0.96551 | Diversity Factor: 0.97 | Uncompensated |  | Reactive Power |  |  | MVAr | 12.1438 | 12.8286 | 13.033 | 12.8196 | 12.4515 | 12.2899 | 12.2636 | 12.2431 | 12.3388 | 12.4916 | 12.6241 | 12.7682 | 12.8748 | 13.0284 | 13.1811 | 13.3674 | 13.5719 | 13.7715 | 13.9633 | 14.1593 | 14.3597 | 14.5645 | 14.7737 | 14.9874 | 15.2057 | 15.4287 | 15.6563
|  |  |  | PF |  |  |  | 0.97986 |  | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986 | 0.97986
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Chatswood 33_11kV
| Chatswood 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 2243 | 2304 | 2357 | 2494 | 2113 | 2277 | 1976.358 |  | 2046.283 | 1968.452 | 1949.794 | 1926.447 | 1931.109 | 1933.627 | 1955.746 | 1985.179 | 2011.099 | 2038.885 | 2062.275 | 2093.181 | 2124.252 | 2160.119 | 2198.824 | 2236.996 | 2274.448 | 2312.763 | 2351.953 | 2392.033 | 2433.012 | 2474.906 | 2517.726 | 2561.486 | 2606.199 |  |  | Total | 87.3 | 0 | 0 | -0.95998 | -1.6491 | 92.8453 | -0.80147 | 112.1165 | 24.4825 | 46.9578 | 9.1492 | 4.6615 | 2.5187 | 22.1185 | 29.4332 | 25.9201 | 27.7858 | 23.3901 | 30.9055 | 31.0713 | 35.8677 | 38.7045 | 38.1721 | 37.4514 | 38.315 | 39.1909 | 40.0791 | 40.98 | 41.8936 | 42.8201 | 43.7598 | 44.7127
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 3524 |  | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 6400 |  | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 |  |  | Chatswood 33_11kV Tx1 | -593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Chatswood 33_11kV Tx11 | 690 | 119 | 0 | -0.45628 | -0.78383 | 120.55 | 1.6191 | 66.7514 | 27.2201 | 45.983 | 4.3486 | 2.2156 | 1.1971 | 10.513 | 13.9897 | 12.3199 | 13.2067 | 11.1174 | 14.6895 | 14.7682 | 17.048 | 18.3963 | 18.1433 | 17.8008 | 18.2112 | 18.6275 | 19.0497 | 19.4779 | 19.9121 | 20.3525 | 20.7991 | 21.252
| Transformer Loads | [35 empty] | Chatswood 33_11kV Tx12 | 0 | -119 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | Chatswood 33_11kV Tx13 | 1643 | 0 | 0 | -0.5037 | -0.86529 | -27.7047 | -2.4205 | -4.6349 | -2.7376 | 0.9748 | 4.8006 | 2.4459 | 1.3216 | 11.6055 | 15.4435 | 13.6002 | 14.5792 | 12.2728 | 16.216 | 16.303 | 18.8197 | 20.3082 | 20.0288 | 19.6507 | 20.1038 | 20.5633 | 21.0294 | 21.5021 | 21.9815 | 22.4676 | 22.9606 | 23.4606
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  | Chatswood 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [35 empty] | Chatswood 33_11kV Tx3 | -672.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [35 empty] | Chatswood 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | Chatswood 33_11kV Tx5 | -980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.028297 | -0.056593 | -0.08489 | -0.50934 | -2.1446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Chatswood 33_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Chatswood 33_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.031237 | -0.062475 | -0.093712 | -0.56227 | -2.3675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx1 | Chatswood 33_11kV Tx11 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx1 | Chatswood 33_11kV Tx13 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx11 | Chatswood 33_11kV Tx12 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx12 | Chatswood 33_11kV Tx11 | 0 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx3 | Chatswood 33_11kV Tx11 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx3 | Chatswood 33_11kV Tx13 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx5 | Chatswood 33_11kV Tx11 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5954. Connection of 11 kV Feeders to new Switchgear at Chatswood Zone | Chatswood 33_11kV Tx5 | Chatswood 33_11kV Tx13 | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6885. Lindfield Tx1 load transfer to Chatswood PA31 | Lindfield 33_11kV Tx1 | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 7086. Re-conductor OH at PA 28 Lindfield Zone | Lindfield 33_11kV Tx4 | Chatswood 33_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2005306. Stage 2 of Channel 9 Load Increase, Est S.7712 Artarmon Edwards |  | Chatswood 33_11kV Tx3 | 87.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010502. Uprate S.2385, Greenwich Rd, Greenwich. Recover existing OH mains and supply new sub via UG cable | Chatswood 33_11kV Tx13 | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011190. Establishment of S.49284 Archer Albert No 2, 38 Albert Ave, Chatswood |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2011533. Establishment of S.50669 Devonshire Johnson, 31-35 Devonshire Street, Chatswood |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2012280. Establishment of 3 x Kiosks S.64164 Fleet Albert No 2, S.64163 Fleet Albert No 1 and S.64165 Fleet Thomas No.3, 79-85 Albert Ave, Chatswood |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012539. Establishment of S.63266 Mindarie Pinaroo, 31-39 Mindarie Street, Lane Cove | Chatswood 33_11kV Tx13 | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2014131. Establishment of 2 x Kisosk - S.64871 Centennial Mowbray No1 and S.64872 Centennial Mowbray No 2, 7-13 Centennial Avenue, Lane Cove |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9257 | 18.4233 | 24.8283 | 22.6421 | 23.7017 | 23.519 | 23.3163 | 23.6829 | 24.0547 | 24.4318 | 24.8142 | 25.2022 | 25.5956 | 25.9947 | 26.3994 | 26.8098 | 27.2261 | 27.6483 | 28.0765 | 28.5107 | 28.9511 | 29.3977 | 29.8507
| Diversity Factor: 0 | [33 empty] | Econometric |  | Chatswood 33_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Chatswood 33_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9572 | 20.3379 | 27.4085 | 24.9951 | 26.1648 | 25.9632 | 25.7394 | 26.1441 | 26.5545 | 26.9708 | 27.393 | 27.8213 | 28.2556 | 28.6961 | 29.1429 | 29.596 | 30.0556 | 30.5216 | 30.9943 | 31.4737 | 31.9598 | 32.4529 | 32.9529
[35 empty] | Energy Efficiency |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4046 | -1.5644 | -7.9878 | -12.501 | -19.329 | -20.2449 | -11.9323 | -8.3144 | -9.7622 | -9.5318 | -11.8061 | -8.6111 | -8.9148 | -7.0229 | -6.0681 | -6.7201 | -7.4674 | -7.4674 | -7.4674 | -7.4674 | -7.4674 | -7.4674 | -7.4674 | -7.4674 | -7.4674
| 0 | [33 empty] | Energy Efficiency |  | Chatswood 33_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Chatswood 33_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7584 | -1.727 | -8.8179 | -13.8001 | -21.3377 | -22.3488 | -13.1723 | -9.1784 | -10.7767 | -10.5224 | -13.033 | -9.506 | -9.8412 | -7.7528 | -6.6987 | -7.4185 | -8.2434 | -8.2434 | -8.2434 | -8.2434 | -8.2434 | -8.2434 | -8.2434 | -8.2434 | -8.2434
[35 empty] | Solar PV |  | Chatswood 33_11kV Tx11 | 0 | 0 | 0 | -0.45628 | -0.78383 | -2.45 | -0.38094 | -0.76571 | -0.85886 | -0.96999 | -1.0643 | -1.1391 | -1.2 | -1.2564 | -1.215 | -1.2343 | -0.9444 | -1.1312 | -1.1312 | -1.1312 | -1.1312 | -1.1312 | -1.1312 | -1.1312 | -1.1312 | -1.1312 | -1.1312 | -1.1312 | -1.1312 | -1.1312 | -1.1312 | -1.1312
[35 empty] | Solar PV |  | Chatswood 33_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Solar PV |  | Chatswood 33_11kV Tx13 | 0 | 0 | 0 | -0.5037 | -0.86529 | -2.7047 | -0.42053 | -0.84528 | -0.94811 | -1.0708 | -1.1749 | -1.2575 | -1.3247 | -1.387 | -1.3412 | -1.3625 | -1.0425 | -1.2488 | -1.2488 | -1.2488 | -1.2488 | -1.2488 | -1.2488 | -1.2488 | -1.2488 | -1.2488 | -1.2488 | -1.2488 | -1.2488 | -1.2488 | -1.2488 | -1.2488
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Chatswood 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Chatswood 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Chatswood 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Chatswood 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 1.182% |  | Rog Capped +/-5% | [59 empty] | Rog Capped +/-5%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Chatswood 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1976.358 | 2036 | 2046.283 | 1968.452 | 1949.794 | 1926.447 | 1931.109 | 1933.627 | 1955.746 | 1985.179 | 2011.099 | 2038.885 | 2062.275 | 2093.181 | 2124.252 | 2160.119 | 2198.824 | 2236.996 | 2274.448 | 2312.763 | 2351.953 | 2392.033 | 2433.012 | 2474.906 | 2517.726 | 2561.486 | 2606.199
|  |  |  | Apparent Power |  |  | MVA | 37.6547 |  | 38.9869 | 37.504 | 37.1486 | 36.7037 | 36.7926 | 36.8406 | 37.262 | 37.8227 | 38.3166 | 38.846 | 39.2916 | 39.8805 | 40.4724 | 41.1558 | 41.8932 | 42.6205 | 43.334 | 44.0641 | 44.8107 | 45.5743 | 46.3551 | 47.1533 | 47.9691 | 48.8029 | 49.6548
|  |  |  | Real Power |  |  | MW | 34.4672 | 35.5073 | 35.6726 | 34.3158 | 33.9905 | 33.5835 | 33.6648 | 33.7087 | 34.0943 | 34.6074 | 35.0592 | 35.5436 | 35.9514 | 36.4902 | 37.0318 | 37.6571 | 38.3318 | 38.9973 | 39.6502 | 40.3181 | 41.0013 | 41.7 | 42.4144 | 43.1447 | 43.8912 | 44.6541 | 45.4335
|  |  |  | Reactive Power |  |  | MVAr | 15.1621 |  | 15.7304 | 15.1321 | 14.9887 | 14.8092 | 14.8451 | 14.8644 | 15.0344 | 15.2607 | 15.46 | 15.6736 | 15.8534 | 16.0909 | 16.3298 | 16.6055 | 16.9031 | 17.1965 | 17.4844 | 17.7789 | 18.0802 | 18.3883 | 18.7034 | 19.0254 | 19.3546 | 19.691 | 20.0347
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.91535 |  | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499
0.94012 | Diversity Factor: 0.94 | Uncompensated |  | Reactive Power |  |  | MVAr | 15.1621 | 15.6196 | 15.7304 | 15.1321 | 14.9887 | 14.8092 | 14.8451 | 14.8644 | 15.0344 | 15.2607 | 15.46 | 15.6736 | 15.8534 | 16.0909 | 16.3298 | 16.6055 | 16.9031 | 17.1965 | 17.4844 | 17.7789 | 18.0802 | 18.3883 | 18.7034 | 19.0254 | 19.3546 | 19.691 | 20.0347
|  |  |  | PF |  |  |  | 0.91535 |  | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499 | 0.91499
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Crows Nest 132_11kV
| Crows Nest 132_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone commissioned |  | 2016-05-31
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | [8 empty] | 0 | 0 | 1773.212 | 1751.22 | 1757.992 | 1763.891 | 1787.853 | 1818.4 | 1845.193 | 1873.851 | 1897.921 | 1928.776 | 1959.734 | 1995.292 | 2033.495 | 2071.206 | 2108.136 | 2145.847 | 2184.351 | 2223.658 | 2263.779 | 2304.726 | 2346.509 | 2389.14 | 2432.63 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1773.2156 | 7.6413 | 6.8431 | 5.9603 | 24.2071 | 30.8496 | 27.0499 | 28.9245 | 24.2885 | 31.1259 | 31.2213 | 35.8501 | 38.5049 | 37.9989 | 37.2009 | 37.9787 | 38.7672 | 39.5664 | 40.3767 | 41.198 | 42.0306 | 42.8745 | 43.73
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997 | 2997
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 |  |  | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 886.6078 | 3.8206 | 3.4215 | 2.9802 | 12.1036 | 15.4248 | 13.525 | 14.4623 | 12.1442 | 15.563 | 15.6107 | 17.925 | 19.2525 | 18.9995 | 18.6005 | 18.9894 | 19.3836 | 19.7832 | 20.1883 | 20.599 | 21.0153 | 21.4372 | 21.865
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 886.6078 | 3.8206 | 3.4215 | 2.9802 | 12.1036 | 15.4248 | 13.525 | 14.4623 | 12.1442 | 15.563 | 15.6107 | 17.925 | 19.2525 | 18.9995 | 18.6005 | 18.9894 | 19.3836 | 19.7832 | 20.1883 | 20.599 | 21.0153 | 21.4372 | 21.865
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.050365 | -0.30219 | -0.76205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.050365 | -0.30219 | -0.76205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx1 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.9199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx1 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.9199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx2 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.9701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx2 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.9701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx3 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx3 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx4 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx4 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1363 | 17.2597 | 23.6961 | 23.2409 | 24.5952 | 24.1367 | 23.6548 | 24.0035 | 24.3569 | 24.7152 | 25.0785 | 25.4468 | 25.8201 | 26.1985 | 26.5821 | 26.971 | 27.3653 | 27.7649 | 28.17 | 28.5807 | 28.997 | 29.4189 | 29.8467
[35 empty] | Econometric |  | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1363 | 17.2597 | 23.6961 | 23.2409 | 24.5952 | 24.1367 | 23.6548 | 24.0035 | 24.3569 | 24.7152 | 25.0785 | 25.4468 | 25.8201 | 26.1985 | 26.5821 | 26.971 | 27.3653 | 27.7649 | 28.17 | 28.5807 | 28.997 | 29.4189 | 29.8467
| 0 | [33 empty] | Energy Efficiency |  | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.504 | -11.5759 | -17.8419 | -18.5008 | -10.6489 | -6.93 | -8.3196 | -8.1561 | -10.5536 | -7.4932 | -7.8088 | -5.8626 | -4.9085 | -5.54 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.504 | -11.5759 | -17.8419 | -18.5008 | -10.6489 | -6.93 | -8.3196 | -8.1561 | -10.5536 | -7.4932 | -7.8088 | -5.8626 | -4.9085 | -5.54 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226 | -6.3226
[35 empty] | Solar PV |  | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4226 | -1.561 | -1.6706 | -1.76 | -1.8427 | -1.7819 | -1.8102 | -1.3851 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591
[35 empty] | Solar PV |  | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4226 | -1.561 | -1.6706 | -1.76 | -1.8427 | -1.7819 | -1.8102 | -1.3851 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591 | -1.6591
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [8 empty] | Rog Capped +/-5% | [59 empty] | Rog Capped +/-5%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Crows Nest 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 | 0 | 0 | 0 | 1773.212 | 1751.22 | 1757.992 | 1763.891 | 1787.853 | 1818.4 | 1845.193 | 1873.851 | 1897.921 | 1928.776 | 1959.734 | 1995.292 | 2033.495 | 2071.206 | 2108.136 | 2145.847 | 2184.351 | 2223.658 | 2263.779 | 2304.726 | 2346.509 | 2389.14 | 2432.63
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 33.7842 | 33.3652 | 33.4943 | 33.6066 | 34.0632 | 34.6452 | 35.1557 | 35.7017 | 36.1603 | 36.7481 | 37.338 | 38.0154 | 38.7433 | 39.4618 | 40.1654 | 40.8839 | 41.6175 | 42.3664 | 43.1308 | 43.9109 | 44.707 | 45.5192 | 46.3478
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 27.9588 | 27.6239 | 27.7412 | 27.8434 | 28.2585 | 28.7875 | 29.2513 | 29.7473 | 30.1638 | 30.6975 | 31.2329 | 31.8476 | 32.5079 | 33.1594 | 33.7973 | 34.4486 | 35.1133 | 35.7918 | 36.4841 | 37.1906 | 37.9113 | 38.6465 | 39.3963
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 18.9652 | 18.7126 | 18.7694 | 18.8189 | 19.0199 | 19.2761 | 19.5008 | 19.741 | 19.9427 | 20.2012 | 20.4605 | 20.7582 | 21.078 | 21.3936 | 21.7025 | 22.0179 | 22.3398 | 22.6684 | 23.0038 | 23.3459 | 23.695 | 24.051 | 24.4142
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0.82757 | 0.82792 | 0.82824 | 0.82851 | 0.82959 | 0.83092 | 0.83205 | 0.83322 | 0.83417 | 0.83535 | 0.83649 | 0.83775 | 0.83906 | 0.84029 | 0.84145 | 0.84259 | 0.84371 | 0.84481 | 0.84589 | 0.84695 | 0.84799 | 0.84901 | 0.85001
0.95379 | Diversity Factor: 0.95 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 18.9652 | 18.7126 | 18.7694 | 18.8189 | 19.0199 | 19.2761 | 19.5008 | 19.741 | 19.9427 | 20.2012 | 20.4605 | 20.7582 | 21.078 | 21.3936 | 21.7025 | 22.0179 | 22.3398 | 22.6684 | 23.0038 | 23.3459 | 23.695 | 24.051 | 24.4142
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0.82757 | 0.82792 | 0.82824 | 0.82851 | 0.82959 | 0.83092 | 0.83205 | 0.83322 | 0.83417 | 0.83535 | 0.83649 | 0.83775 | 0.83906 | 0.84029 | 0.84145 | 0.84259 | 0.84371 | 0.84481 | 0.84589 | 0.84695 | 0.84799 | 0.84901 | 0.85001
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Crows Nest 33_11kV
| Crows Nest 33_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone decommissioned |  | 2016-05-31
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 2281 | 2290 | 2495 | 2387 | 1988 | 2067 | 1773 |  | 1852.26 | 1834.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | 0 | 0 | 0 | 3.6653 | -4.8781 | 16.3561 | -2.9912 | 61.2825 | 74.6931 | -1772.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 3150 |  | 3150 | 3150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 4890 |  | 4890 | 4890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Crows Nest 33_11kV Tx1 | 0 | -180 | -271 | -81.3914 | -1.4303 | 34.518 | 46.1229 | -7.2012 | 33.4533 | -519.8397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Crows Nest 33_11kV Tx2 | 0 | -240 | 151 | 12.6658 | -113.2215 | -42.4116 | -47.749 | -33.7338 | -1.4916 | -443.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Crows Nest 33_11kV Tx3 | 0 | 485 | -456 | -0.10674 | 111.6099 | 36.8685 | -0.2392 | 17.277 | 12.5236 | -141.7745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | Crows Nest 33_11kV Tx4 | 0 | -65 | 576 | 72.4976 | -1.8362 | -12.6188 | -1.1259 | 84.9405 | 30.2077 | -667.3424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.3347 | -0.01969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.28583 | -0.016815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.091281 | -0.0053701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42966 | -0.025277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6382. Change of Open Points to Relieve Panel 2 + 7 Crows Nest Remedial Feeders. | Crows Nest 33_11kV Tx4 | Crows Nest 33_11kV Tx3 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6439. Relieve remedial Crows Nest Panel 30 feeder. | Crows Nest 33_11kV Tx1 | Crows Nest 33_11kV Tx2 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6455. NOP change to balance tx loads at Crows Nest Zone. | Crows Nest 33_11kV Tx1 | Crows Nest 33_11kV Tx3 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6455. NOP change to balance tx loads at Crows Nest Zone. | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx3 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6463. Connection of feeders to new S/G at Crows Nest | Crows Nest 33_11kV Tx1 | Crows Nest 33_11kV Tx4 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6463. Connection of feeders to new S/G at Crows Nest | Crows Nest 33_11kV Tx3 | Crows Nest 33_11kV Tx2 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6463. Connection of feeders to new S/G at Crows Nest | Crows Nest 33_11kV Tx3 | Crows Nest 33_11kV Tx4 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6502. 11kV Supply Arrangements for the Sydney Harbour Tunnel | North Sydney 33_11kV Tx5 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6515. North Sydney Zone Conversion - Stage 1 of 4 | Crows Nest 33_11kV Tx1 | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6515. North Sydney Zone Conversion - Stage 1 of 4 | North Sydney 33_11kV Tx5 | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6731. Crows Nest - Change of Open Points to relieve Panel 4L | Crows Nest 33_11kV Tx4 | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6819. Relieve Tx2 at Crows Nest Zone | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6831. Crows Nest Zone Development | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6916. Open Point Change to Releive Overloaded Crows Nest Tx2 | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6916. Open Point Change to Releive Overloaded Crows Nest Tx2 | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx1 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.9199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx1 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.9199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx2 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.9701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx2 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.9701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx3 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx3 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx4 | Crows Nest 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Crows Nest 33_11kV Tx4 | Crows Nest 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010068. Establishment of S.47793 Miller Palmer, 520 Miller Street, Cammeray |  | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2010695. Establishment of S.49221 Belmont Shirley, Belmont Ave, Wollstonecraft and Decommission S.1394. Uprate of S.4897 Morton Gilles. | Crows Nest 33_11kV Tx4 | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2011308. Establishment of S.49960 West Church No 2, 8 West Street, North Sydney | Crows Nest 33_11kV Tx2 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011450. Establishment of 2 x Unit Chamber Subs; S.49977 Walker Berry No 1; and S.50280 Walker Berry No 2; 136-142 Walker Street, North Sydney |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011774. Establishment of new S.61541 Oxley Pacific for Commercial/Residential Development, 545-553 Pacific Hwy, St Leonards |  | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011774. Establishment of new S.61541 Oxley Pacific for Commercial/Residential Development, 545-553 Pacific Hwy, St Leonards | Crows Nest 33_11kV Tx4 | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | HVCON_ID: 2012284. Establishment of S.48184 Willoughby Walter, DP586037 (Between 2-4 Artarmon Rd and 460 Willoughby Rd) Mosman | Crows Nest 33_11kV Tx1 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | ROG Justification | [24 empty] | HVCON_ID: 2012423. Establishment of S.62947 Angelo Berry No 2, 211-215 Pacific Hwy, North Sydney NSW 2060 |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 4.297% |  | Rog Capped +/-5% | [24 empty] | HVCON_ID: 2012423. Establishment of S.62947 Angelo Berry No 2, 211-215 Pacific Hwy, North Sydney NSW 2060 | North Sydney 33_11kV Tx2 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rog Capped +/-5%
[35 empty] | HVCON_ID: 2012423. Establishment of S.62947 Angelo Berry No 2, 211-215 Pacific Hwy, North Sydney NSW 2060 | North Sydney 33_11kV Tx3 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013050. Establishment of S.63443 Atchison Zig Zag No 1 and S.63444 Atchison Zig Zag No 2, 103-111 Willoughby Rd, Crows Nest |  | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | HVCON_ID: 2014104. Relocate S.2316 NORTH SYDNEY ANZAC CLUB, Anzac Avenue, Cammeray Load Increase at S.35329 ERNEST MILLER | North Sydney 33_11kV Tx4 | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Econometric |  | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2: Substation Load Detail | Econometric |  | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | Energy Efficiency |  | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2079 | -0.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Crows Nest 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1773 | 1886 | 1852.26 | 1834.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8855 | -0.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 33.7802 |  | 35.2903 | 34.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.60216 | -0.26954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 27.8579 | 29.6333 | 29.1741 | 28.9173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8344 | -1.2687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 19.106 |  | 19.8564 | 19.6164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | -0.39136 | -1.4303 | -0.48201 | -0.87706 | -0.65857 | -0.73868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | Crows Nest 33_11kV Tx2 | 0 | 0 | 0 | -0.33422 | -1.2215 | -0.41163 | -0.74901 | -0.56241 | -0.63083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.82468 |  | 0.82669 | 0.82756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | -0.10674 | -0.39009 | -0.13146 | -0.2392 | -0.17961 | -0.20146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.98114 | Diversity Factor: 0.98 | Uncompensated |  | Reactive Power |  |  | MVAr | 19.106 | 20.3237 | 19.8564 | 19.6164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | -0.50241 | -1.8362 | -0.61878 | -1.1259 | -0.84543 | -0.94828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.82468 |  | 0.82669 | 0.82756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Gore Hill 33_11kV
| Gore Hill 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 4129 | 4157 | 4136 | 4391 | 3818 | 3470.75 | 3097.25 |  | 3179.331 | 3085.955 | 3004.204 | 2959.717 | 2940.582 | 2937.575 | 2960.022 | 2997.073 | 3029.638 | 3063.463 | 3087.725 | 3122.522 | 3156.776 | 3199.331 | 3246.073 | 3291.463 | 3334.43 | 3378.16 | 3422.662 | 3467.946 | 3514.022 | 3560.9 | 3608.591 | 3657.106 | 3706.454 |  |  | Total | 27 | 45 | 84.6 | 24.0072 | -381.5729 | -74.8707 | -28.9098 | -34.9678 | 20.7712 | -7.8879 | -8.5339 | -19.1352 | -3.0067 | 22.4473 | 37.0501 | 32.5657 | 33.825 | 24.2613 | 34.797 | 34.2546 | 42.5545 | 46.7425 | 45.3899 | 42.9674 | 43.7297 | 44.5018 | 45.2839 | 46.0761 | 46.8785 | 47.6912 | 48.5144 | 49.3482
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 5086 |  | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086 | 5086
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 7939 |  | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 | 7939 |  |  | Gore Hill 33_11kV Tx1 | 0 | 0 | 0 | -0.41252 | -0.35464 | -0.12002 | -0.13919 | -4.8199 | -1.3823 | -1.0873 | -1.1763 | -2.6375 | -0.41443 | 3.0941 | 5.1069 | 4.4888 | 4.6623 | 3.3441 | 4.7963 | 4.7216 | 5.8656 | 6.4429 | 6.2564 | 5.9225 | 6.0276 | 6.134 | 6.2418 | 6.351 | 6.4616 | 6.5736 | 6.6871 | 6.802
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Gore Hill 33_11kV Tx2 | 27 | 0 | 62.1 | -0.95349 | -0.81971 | -74.2774 | -28.2217 | -11.1406 | 27.6048 | -2.5131 | -2.7189 | -6.0964 | -0.95792 | 7.1517 | 11.8041 | 10.3753 | 10.7766 | 7.7296 | 11.0862 | 10.9134 | 13.5577 | 14.8921 | 14.4611 | 13.6893 | 13.9322 | 14.1782 | 14.4273 | 14.6797 | 14.9354 | 15.1943 | 15.4566 | 15.7222
| Transformer Loads | [35 empty] | Gore Hill 33_11kV Tx3 | 0 | 45 | 0 | -0.59435 | -379.511 | -0.17293 | -0.20055 | -6.9444 | -1.9917 | -1.5665 | -1.6948 | -3.8001 | -0.59711 | 4.4579 | 7.3579 | 6.4674 | 6.7175 | 4.8182 | 6.9105 | 6.8028 | 8.4511 | 9.2828 | 9.0142 | 8.5331 | 8.6845 | 8.8378 | 8.9931 | 9.1504 | 9.3098 | 9.4712 | 9.6347 | 9.8003
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  | Gore Hill 33_11kV Tx4 | 0 | 0 | 22.5 | 25.9676 | -0.88757 | -0.30038 | -0.34836 | -12.0629 | -3.4596 | -2.7211 | -2.9439 | -6.6011 | -1.0372 | 7.7437 | 12.7812 | 11.2342 | 11.6686 | 8.3694 | 12.0039 | 11.8168 | 14.6801 | 16.1248 | 15.6582 | 14.8225 | 15.0855 | 15.3518 | 15.6216 | 15.8949 | 16.1717 | 16.4521 | 16.7361 | 17.0237
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Gore Hill 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2437 | -0.132 | -0.198 | -1.188 | -2.4036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1862 | -0.30511 | -0.45766 | -2.7459 | -5.5556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Gore Hill 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2327 | -0.19018 | -0.28528 | -1.7117 | -3.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Gore Hill 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6155 | -0.33036 | -0.49554 | -2.9733 | -6.0155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning | Gore Hill 33_11kV Tx3 | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning | Gore Hill 33_11kV Tx3 | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2005136. Est S.36123 "Herbert Frederick No4" for JGRT Holdings - St Leonards. |  | Gore Hill 33_11kV Tx4 | 0 | 0 | 22.5 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2007061. Establishment of S.35551 RNS Hospital No. 7, Westbourne St (Cnr Reserve Rd) St Leonards |  | Gore Hill 33_11kV Tx3 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2007088. LOAD INCREASE AT S.6425 TELECOM Herbert No1 -GORE HILL. (NOTE: Load on S.6425 has not increased anywhere near the amount of 140A that was originally requested) |  | Gore Hill 33_11kV Tx2 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2007155. Establishment of S.35608 Reserve Frederick No. 2, 1A Frederick St, Artarmon |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2010502. Uprate S.2385, Greenwich Rd, Greenwich. Recover existing OH mains and supply new sub via UG cable | Chatswood 33_11kV Tx13 | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012396. Decommission S.1770 RNS Hospital No 2 and S.7346 RNS Hospital No 4, RNS Hospital - Westbourne St, St Leonards |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | -99 | -27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2012543. Establishment of S.63282 Atchison Ln Christie No. 1 and S.63283 Atchison Ln Christie No 2, 6-16 Atchison Street, St Leonards |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Econometric |  | Gore Hill 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5141 | 4.903 | 7.0791 | 6.9103 | 7.1097 | 7.1186 | 7.1252 | 7.22 | 7.3161 | 7.4134 | 7.5119 | 7.6117 | 7.7128 | 7.8152 | 7.919 | 8.024 | 8.1305 | 8.2383 | 8.3475 | 8.4581 | 8.5701 | 8.6835 | 8.7985
[35 empty] | Econometric |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.811 | 11.3327 | 16.3628 | 15.9726 | 16.4335 | 16.4539 | 16.4693 | 16.6884 | 16.9104 | 17.1353 | 17.363 | 17.5938 | 17.8274 | 18.0642 | 18.3039 | 18.5468 | 18.7928 | 19.042 | 19.2943 | 19.55 | 19.8089 | 20.0712 | 20.3368
[35 empty] | Econometric |  | Gore Hill 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6222 | 7.0642 | 10.1996 | 9.9563 | 10.2436 | 10.2564 | 10.2659 | 10.4026 | 10.5409 | 10.6811 | 10.8231 | 10.9669 | 11.1126 | 11.2601 | 11.4096 | 11.5609 | 11.7143 | 11.8696 | 12.0269 | 12.1863 | 12.3477 | 12.5112 | 12.6768
| 0 | [33 empty] | Econometric |  | Gore Hill 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2921 | 12.2709 | 17.7173 | 17.2948 | 17.7938 | 17.8159 | 17.8326 | 18.0699 | 18.3102 | 18.5537 | 18.8004 | 19.0502 | 19.3032 | 19.5595 | 19.8191 | 20.0821 | 20.3485 | 20.6182 | 20.8915 | 21.1683 | 21.4487 | 21.7327 | 22.0203
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Gore Hill 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3535 | -1.0007 | -3.1213 | -4.5818 | -6.982 | -6.9759 | -3.6504 | -1.6585 | -2.2776 | -2.2831 | -3.6431 | -2.2882 | -2.4615 | -1.4173 | -0.94109 | -1.23 | -1.6676 | -1.6676 | -1.6676 | -1.6676 | -1.6676 | -1.6676 | -1.6676 | -1.6676 | -1.6676
[35 empty] | Energy Efficiency |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4399 | -2.3129 | -7.2146 | -10.5905 | -16.1381 | -16.1241 | -8.4375 | -3.8334 | -5.2645 | -5.2772 | -8.4207 | -5.2889 | -5.6895 | -3.2759 | -2.1752 | -2.8429 | -3.8545 | -3.8545 | -3.8545 | -3.8545 | -3.8545 | -3.8545 | -3.8545 | -3.8545 | -3.8545
[35 empty] | Energy Efficiency |  | Gore Hill 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3909 | -1.4417 | -4.4972 | -6.6015 | -10.0595 | -10.0508 | -5.2595 | -2.3895 | -3.2816 | -3.2895 | -5.2489 | -3.2968 | -3.5465 | -2.042 | -1.3559 | -1.7721 | -2.4026 | -2.4026 | -2.4026 | -2.4026 | -2.4026 | -2.4026 | -2.4026 | -2.4026 | -2.4026
| 0 | [33 empty] | Energy Efficiency |  | Gore Hill 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8903 | -2.5044 | -7.8119 | -11.4671 | -17.4741 | -17.4588 | -9.136 | -4.1507 | -5.7003 | -5.7141 | -9.1177 | -5.7267 | -6.1604 | -3.547 | -2.3553 | -3.0783 | -4.1735 | -4.1735 | -4.1735 | -4.1735 | -4.1735 | -4.1735 | -4.1735 | -4.1735 | -4.1735
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Gore Hill 33_11kV Tx1 | 0 | 0 | 0 | -0.41252 | -0.35464 | -0.12002 | -0.13919 | -0.22261 | -0.24969 | -0.282 | -0.30943 | -0.33116 | -0.34887 | -0.36526 | -0.35322 | -0.35883 | -0.27456 | -0.32887 | -0.32887 | -0.32887 | -0.32887 | -0.32887 | -0.32887 | -0.32887 | -0.32887 | -0.32887 | -0.32887 | -0.32887 | -0.32887 | -0.32887 | -0.32887 | -0.32887
[35 empty] | Solar PV |  | Gore Hill 33_11kV Tx2 | 0 | 0 | 0 | -0.95349 | -0.81971 | -0.27742 | -0.32173 | -0.51454 | -0.57713 | -0.65181 | -0.71521 | -0.76545 | -0.80639 | -0.84427 | -0.81643 | -0.8294 | -0.63462 | -0.76015 | -0.76015 | -0.76015 | -0.76015 | -0.76015 | -0.76015 | -0.76015 | -0.76015 | -0.76015 | -0.76015 | -0.76015 | -0.76015 | -0.76015 | -0.76015 | -0.76015
[35 empty] | Solar PV |  | Gore Hill 33_11kV Tx3 | 0 | 0 | 0 | -0.59435 | -0.51096 | -0.17293 | -0.20055 | -0.32073 | -0.35975 | -0.4063 | -0.44582 | -0.47713 | -0.50266 | -0.52627 | -0.50891 | -0.517 | -0.39558 | -0.47383 | -0.47383 | -0.47383 | -0.47383 | -0.47383 | -0.47383 | -0.47383 | -0.47383 | -0.47383 | -0.47383 | -0.47383 | -0.47383 | -0.47383 | -0.47383 | -0.47383
| 0 | [33 empty] | Solar PV |  | Gore Hill 33_11kV Tx4 | 0 | 0 | 0 | -1.0324 | -0.88757 | -0.30038 | -0.34836 | -0.55713 | -0.62491 | -0.70577 | -0.77441 | -0.82881 | -0.87314 | -0.91416 | -0.88401 | -0.89806 | -0.68715 | -0.82307 | -0.82307 | -0.82307 | -0.82307 | -0.82307 | -0.82307 | -0.82307 | -0.82307 | -0.82307 | -0.82307 | -0.82307 | -0.82307 | -0.82307 | -0.82307 | -0.82307
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 3.199% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.9641 | 0.92949 | 0.90725 | 0.8964 | 0.8964 | 0.8964 | 0.8964 | 0.8964 | 0.8964 | 0.8964 | -3.59% | -3.59% | -2.393% | -1.196% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Gore Hill 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 3097.25 | 3334 | 3179.331 | 3085.955 | 3004.204 | 2959.717 | 2940.582 | 2937.575 | 2960.022 | 2997.073 | 3029.638 | 3063.463 | 3087.725 | 3122.522 | 3156.776 | 3199.331 | 3246.073 | 3291.463 | 3334.43 | 3378.16 | 3422.662 | 3467.946 | 3514.022 | 3560.9 | 3608.591 | 3657.106 | 3706.454
|  |  |  | Apparent Power |  |  | MVA | 59.0105 |  | 60.5744 | 58.7953 | 57.2378 | 56.3902 | 56.0256 | 55.9683 | 56.396 | 57.1019 | 57.7224 | 58.3668 | 58.8291 | 59.492 | 60.1447 | 60.9554 | 61.846 | 62.7108 | 63.5294 | 64.3626 | 65.2105 | 66.0733 | 66.9511 | 67.8443 | 68.7529 | 69.6772 | 70.6174
|  |  |  | Real Power |  |  | MW | 55.0655 | 59.2746 | 56.5248 | 54.8647 | 53.4112 | 52.6203 | 52.2801 | 52.2266 | 52.6257 | 53.2844 | 53.8634 | 54.4648 | 54.8961 | 55.5148 | 56.1238 | 56.8803 | 57.7114 | 58.5183 | 59.2822 | 60.0597 | 60.8509 | 61.656 | 62.4752 | 63.3086 | 64.1565 | 65.019 | 65.8964
|  |  |  | Reactive Power |  |  | MVAr | 21.2141 |  | 21.7763 | 21.1368 | 20.5768 | 20.2721 | 20.141 | 20.1205 | 20.2742 | 20.528 | 20.751 | 20.9827 | 21.1489 | 21.3872 | 21.6218 | 21.9133 | 22.2335 | 22.5444 | 22.8387 | 23.1382 | 23.443 | 23.7531 | 24.0687 | 24.3898 | 24.7165 | 25.0488 | 25.3868
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.93315 |  | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315
0.95449 | Diversity Factor: 0.95 | Uncompensated |  | Reactive Power |  |  | MVAr | 21.2141 | 22.8357 | 21.7763 | 21.1368 | 20.5768 | 20.2721 | 20.141 | 20.1205 | 20.2742 | 20.528 | 20.751 | 20.9827 | 21.1489 | 21.3872 | 21.6218 | 21.9133 | 22.2335 | 22.5444 | 22.8387 | 23.1382 | 23.443 | 23.7531 | 24.0687 | 24.3898 | 24.7165 | 25.0488 | 25.3868
|  |  |  | PF |  |  |  | 0.93315 |  | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315 | 0.93315
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer33
| Customer33 | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | [5 empty] | 48 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 |  |  | Total | Historical Spots & Transfers 12/13: 52; Historical Spots & Transfers 13/14: 157
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Major Customer Connection |  | Gore Hill Technology Park Data-Centre 1 33kV | Historical Spots & Transfers 12/13: 3; Historical Spots & Transfers 13/14: 9
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Customer33 | Compensated |  | Load (LV side) |  |  | Amps | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
|  |  |  | Apparent Power |  |  | MVA | 4.5155 |  | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155 | 4.5155
|  |  |  | Real Power |  |  | MW | 4.0639 |  | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639 | 4.0639
|  |  |  | Reactive Power |  |  | MVAr | 1.9682 |  | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.93038 | Diversity Factor: 0.93 | Uncompensated |  | Reactive Power |  |  | MVAr | 1.9682 |  | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682 | 1.9682
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer34
| Customer34 | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Customer34 | Compensated |  | Load (LV side) |  |  | Amps | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| #VALUE! | Uncompensated |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer35
| Customer35 | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  | 97 | 64 | 124 | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Customer35 | Compensated |  | Load (LV side) |  |  | Amps | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
|  |  |  | Apparent Power |  |  | MVA | 7.1447 |  | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447 | 7.1447
|  |  |  | Real Power |  |  | MW | 6.4302 |  | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302 | 6.4302
|  |  |  | Reactive Power |  |  | MVAr | 3.1143 |  | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.51277 | Diversity Factor: 0.51 | Uncompensated |  | Reactive Power |  |  | MVAr | 3.1143 |  | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143 | 3.1143
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Mosman 132_11kV
| Mosman 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 3115 | 3423 | 3593 | 3899 | 3150 | 3349 | 2748 |  | 2875.041 | 2787.561 | 2741.496 | 2736.179 | 2748.655 | 2762.738 | 2805.702 | 2854.812 | 2898.647 | 2945.36 | 2989.443 | 3043.879 | 3099.241 | 3159.95 | 3224.449 | 3288.784 | 3353.359 | 3419.558 | 3487.403 | 3556.92 | 3628.131 | 3701.063 | 3775.74 | 3852.186 | 3930.429 |  |  | Total | 64.8 | 0 | 0 | 65.9095 | -0.0099724 | -0.0052486 | -0.96103 | -18.7355 | -0.21791 | 10.5502 | 22.9608 | 12.7967 | 14.4403 | 44.0339 | 50.2922 | 44.8551 | 47.7647 | 45.0453 | 55.5842 | 56.4871 | 61.896 | 65.7093 | 65.4941 | 65.6928 | 67.2992 | 68.9291 | 70.5829 | 72.2609 | 73.9635 | 75.6909 | 77.4436 | 79.2218
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 4328 |  | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328 | 4328
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 8000 |  | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 |  |  | Mosman 132_11kV Tx1 | 64.8 | 0 | 0 | -0.55593 | -6.0027 | 23.9986 | 3.7444 | -33.2327 | -0.78925 | 2.8056 | 6.1059 | 3.403 | 3.8401 | 11.7098 | 13.3741 | 11.9282 | 12.702 | 11.9788 | 14.7814 | 15.0215 | 16.4599 | 17.4739 | 17.4167 | 17.4695 | 17.8967 | 18.3302 | 18.77 | 19.2162 | 19.669 | 20.1283 | 20.5944 | 21.0673
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Mosman 132_11kV Tx2 | 0 | 0 | -75 | -0.56462 | 36.9973 | -89.0014 | -0.25956 | 52.748 | -0.80158 | 2.8494 | 6.2013 | 3.4562 | 3.9001 | 11.8928 | 13.5831 | 12.1146 | 12.9004 | 12.166 | 15.0124 | 15.2562 | 16.7171 | 17.747 | 17.6888 | 17.7425 | 18.1764 | 18.6166 | 19.0632 | 19.5165 | 19.9763 | 20.4428 | 20.9162 | 21.3965
| Transformer Loads | [35 empty] | Mosman 132_11kV Tx3 | 0 | 0 | 75 | -0.3974 | -31.0019 | -0.00099775 | 15.4173 | -68.9812 | 2.1858 | 2.0056 | 4.3648 | 2.4326 | 2.7451 | 8.3707 | 9.5604 | 8.5268 | 9.0799 | 8.563 | 10.5664 | 10.738 | 11.7662 | 12.4911 | 12.4502 | 12.488 | 12.7934 | 13.1032 | 13.4176 | 13.7366 | 14.0602 | 14.3886 | 14.7218 | 15.0598
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 67.4274 | -0.0027314 | 64.9986 | -19.8632 | 30.7304 | -0.81289 | 2.8896 | 6.2888 | 3.5049 | 3.9551 | 12.0605 | 13.7746 | 12.2854 | 13.0824 | 12.3375 | 15.2241 | 15.4714 | 16.9528 | 17.9972 | 17.9383 | 17.9927 | 18.4327 | 18.8791 | 19.3321 | 19.7917 | 20.258 | 20.7311 | 21.2112 | 21.6982
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6245. Mosman Zone Development 2006 / 2007 (Stage 3) - Augmentation of Panel 21, 29 & 31 Feeders. | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx3 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6473. Castle Cove Zone Development - 2009 (Pa 15, 43 & 44 Feeders) | Castle Cove 132_11kV Tx3 | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6883. Change in open points only - Mosman Zone PA24 and PA43 | Mosman 132_11kV Tx3 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7054. DNP7054 Mosman Zone Development East | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 7054. DNP7054 Mosman Zone Development East | Mosman 132_11kV Tx4 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 7108. Mosman Zone Development North West | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7108. Mosman Zone Development North West | Mosman 132_11kV Tx3 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx3 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx3 | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx3 | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx4 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2005060. Taronga zoo upgrade to 80 HVA (at this stage) |  | Mosman 132_11kV Tx1 | 64.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2009653. Establishment of S.47389 Spit Medusa to replace S.1416 Parrawi Park controlled by CP.791 Parriwi Rd, Within Road Reserve of Spit Rd, Opposite Medusa St, Mosman - Cater for 200amp supply to Beauty Point Public School and g | Mosman 132_11kV Tx1 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2009653. Establishment of S.47389 Spit Medusa to replace S.1416 Parrawi Park controlled by CP.791 Parriwi Rd, Within Road Reserve of Spit Rd, Opposite Medusa St, Mosman - Cater for 200amp supply to Beauty Point Public School and g | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011104. C/S SELF ASSESSED DNP - Establishment of S.48386 Plunkett Bayview, Plunkett Rd, Mosman | Mosman 132_11kV Tx3 | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2011184. Replacement of S.1620 and S.1623 with proposed S.49772 Courallie Minnamurra and S.49773 Woonona Narani, Courallie Rd & Woonona Rd, Northbridge. | Mosman 132_11kV Tx4 | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2011333. Establishment of S.36129 Bellambi Marooba, Bellambi St, Northbridge and decommission S.695 Bellambi St | Mosman 132_11kV Tx2 | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011703. Establishment of S.48587 Cowles Holt to relieve overloaded sub S.1332 and distributor S.35441, within Mosman Council Park Reserve off Cowles Rd (nr Holt Ave), Mosman | Mosman 132_11kV Tx1 | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012284. Establishment of S.48184 Willoughby Walter, DP586037 (Between 2-4 Artarmon Rd and 460 Willoughby Rd) Mosman | Crows Nest 33_11kV Tx1 | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2012294. S.6012 Cowles Military is to be looped in during LV augmentation works. Email advice | Mosman 132_11kV Tx4 | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2012308. Navy upgrade facilities - Establishment of HVC CP.49007 HMAS Middle Head and Decomm of S.763 Hunters Bay |  | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9 | 2.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013247. Establishment of S.63994 Gurrigal Military, 507 Military Rd, Mosman | Mosman 132_11kV Tx1 | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4413 | 16.9001 | 21.7647 | 21.9467 | 23.2291 | 22.8977 | 22.5395 | 22.9196 | 23.3052 | 23.6965 | 24.0936 | 24.4966 | 24.9055 | 25.3204 | 25.7414 | 26.1686 | 26.602 | 27.0418 | 27.4881 | 27.9408 | 28.4002 | 28.8663 | 29.3391
| 0 | [33 empty] | Econometric |  | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5888 | 17.1642 | 22.1048 | 22.2896 | 23.5921 | 23.2554 | 22.8917 | 23.2777 | 23.6694 | 24.0668 | 24.4701 | 24.8794 | 25.2946 | 25.716 | 26.1436 | 26.5775 | 27.0177 | 27.4643 | 27.9176 | 28.3774 | 28.8439 | 29.3173 | 29.7976
| Diversity Factor: 0 | [33 empty] | Econometric |  | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.749 | 12.081 | 15.5584 | 15.6884 | 16.6052 | 16.3683 | 16.1122 | 16.3839 | 16.6596 | 16.9393 | 17.2232 | 17.5112 | 17.8035 | 18.1001 | 18.4011 | 18.7064 | 19.0163 | 19.3307 | 19.6497 | 19.9733 | 20.3017 | 20.6349 | 20.9729
[35 empty] | Econometric |  | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.724 | 17.4063 | 22.4165 | 22.6039 | 23.9248 | 23.5834 | 23.2146 | 23.606 | 24.0031 | 24.4062 | 24.8152 | 25.2302 | 25.6514 | 26.0787 | 26.5123 | 26.9523 | 27.3987 | 27.8517 | 28.3113 | 28.7776 | 29.2507 | 29.7307 | 30.2178
[35 empty] | Energy Efficiency |  | Mosman 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0941 | -0.63378 | -6.4601 | -10.6016 | -16.5583 | -17.8894 | -11.2919 | -9.3036 | -10.3879 | -10.0466 | -11.1216 | -8.7104 | -8.8674 | -7.832 | -7.2268 | -7.6989 | -8.0671 | -8.0671 | -8.0671 | -8.0671 | -8.0671 | -8.0671 | -8.0671 | -8.0671 | -8.0671
[35 empty] | Energy Efficiency |  | Mosman 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1112 | -0.64369 | -6.561 | -10.7672 | -16.817 | -18.1689 | -11.4683 | -9.449 | -10.5502 | -10.2036 | -11.2954 | -8.8465 | -9.0059 | -7.9543 | -7.3397 | -7.8192 | -8.1931 | -8.1931 | -8.1931 | -8.1931 | -8.1931 | -8.1931 | -8.1931 | -8.1931 | -8.1931
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Energy Efficiency |  | Mosman 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.78212 | -0.45306 | -4.618 | -7.5785 | -11.8366 | -12.7881 | -8.0719 | -6.6506 | -7.4257 | -7.1818 | -7.9502 | -6.2266 | -6.3388 | -5.5986 | -5.166 | -5.5035 | -5.7667 | -5.7667 | -5.7667 | -5.7667 | -5.7667 | -5.7667 | -5.7667 | -5.7667 | -5.7667
[10 empty] | ROG Justification | [24 empty] | Energy Efficiency |  | Mosman 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1269 | -0.65276 | -6.6535 | -10.9191 | -17.0542 | -18.4251 | -11.63 | -9.5823 | -10.699 | -10.3475 | -11.4547 | -8.9712 | -9.1329 | -8.0665 | -7.4432 | -7.9295 | -8.3087 | -8.3087 | -8.3087 | -8.3087 | -8.3087 | -8.3087 | -8.3087 | -8.3087 | -8.3087
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 3.679% |  | 7 year ROG ok | [24 empty] | Solar PV |  | Mosman 132_11kV Tx1 | 0 | 0 | 0 | -0.55593 | -0.0026519 | -0.0013958 | -0.25556 | -0.13861 | -0.15547 | -0.17558 | -0.19266 | -0.20619 | -0.21722 | -0.22743 | -0.21993 | -0.22342 | -0.17095 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | -0.20477 | 7 year ROG ok
[35 empty] | Solar PV |  | Mosman 132_11kV Tx2 | 0 | 0 | 0 | -0.56462 | -0.0026934 | -0.0014176 | -0.25956 | -0.14077 | -0.1579 | -0.17833 | -0.19567 | -0.20942 | -0.22062 | -0.23098 | -0.22336 | -0.22691 | -0.17362 | -0.20797 | -0.20797 | -0.20797 | -0.20797 | -0.20797 | -0.20797 | -0.20797 | -0.20797 | -0.20797 | -0.20797 | -0.20797 | -0.20797 | -0.20797 | -0.20797 | -0.20797
[35 empty] | Solar PV |  | Mosman 132_11kV Tx3 | 0 | 0 | 0 | -0.3974 | -0.0018957 | -0.00099775 | -0.18269 | -0.099081 | -0.11113 | -0.12551 | -0.13772 | -0.1474 | -0.15528 | -0.16258 | -0.15721 | -0.15971 | -0.1222 | -0.14638 | -0.14638 | -0.14638 | -0.14638 | -0.14638 | -0.14638 | -0.14638 | -0.14638 | -0.14638 | -0.14638 | -0.14638 | -0.14638 | -0.14638 | -0.14638 | -0.14638
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | Solar PV |  | Mosman 132_11kV Tx4 | 0 | 0 | 0 | -0.57258 | -0.0027314 | -0.0014376 | -0.26322 | -0.14276 | -0.16012 | -0.18084 | -0.19843 | -0.21237 | -0.22373 | -0.23424 | -0.22651 | -0.23011 | -0.17607 | -0.2109 | -0.2109 | -0.2109 | -0.2109 | -0.2109 | -0.2109 | -0.2109 | -0.2109 | -0.2109 | -0.2109 | -0.2109 | -0.2109 | -0.2109 | -0.2109 | -0.2109
0.96988 | 0.94067 | 0.92178 | 0.91252 | 0.91252 | 0.91252 | 0.91252 | 0.91252 | 0.91252 | 0.91252 | -3.012% | -3.012% | -2.008% | -1.004% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Mosman 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 2748 | 3043 | 2875.041 | 2787.561 | 2741.496 | 2736.179 | 2748.655 | 2762.738 | 2805.702 | 2854.812 | 2898.647 | 2945.36 | 2989.443 | 3043.879 | 3099.241 | 3159.95 | 3224.449 | 3288.784 | 3353.359 | 3419.558 | 3487.403 | 3556.92 | 3628.131 | 3701.063 | 3775.74 | 3852.186 | 3930.429
|  |  |  | Apparent Power |  |  | MVA | 52.3564 |  | 54.7769 | 53.1102 | 52.2325 | 52.1312 | 52.3689 | 52.6372 | 53.4558 | 54.3915 | 55.2266 | 56.1166 | 56.9566 | 57.9937 | 59.0485 | 60.2052 | 61.434 | 62.6598 | 63.8901 | 65.1513 | 66.444 | 67.7684 | 69.1252 | 70.5147 | 71.9375 | 73.394 | 74.8847
|  |  |  | Real Power |  |  | MW | 51.2972 | 56.804 | 54.7368 | 53.0839 | 52.2125 | 52.1119 | 52.348 | 52.6144 | 53.4269 | 54.3548 | 55.1824 | 56.0637 | 56.8948 | 57.9203 | 58.9626 | 60.1046 | 61.3169 | 62.5253 | 63.7374 | 64.9791 | 66.2509 | 67.5532 | 68.8864 | 70.2511 | 71.6476 | 73.0765 | 74.5382
|  |  |  | Reactive Power |  |  | MVAr | 10.4782 |  | 2.0962 | 1.6706 | 1.4462 | 1.4202 | 1.481 | 1.5497 | 1.7589 | 1.9978 | 2.211 | 2.4379 | 2.652 | 2.9161 | 3.1845 | 3.4786 | 3.7908 | 4.102 | 4.4141 | 4.7339 | 5.0614 | 5.3968 | 5.7401 | 6.0916 | 6.4512 | 6.8192 | 7.1956
|  |  |  | Capacitors In Service |  |  | MVAr | 3 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
|  |  |  | PF |  |  |  | 0.97977 |  | 0.99927 | 0.9995 | 0.99962 | 0.99963 | 0.9996 | 0.99957 | 0.99946 | 0.99933 | 0.9992 | 0.99906 | 0.99891 | 0.99874 | 0.99854 | 0.99833 | 0.99809 | 0.99785 | 0.99761 | 0.99736 | 0.99709 | 0.99682 | 0.99655 | 0.99626 | 0.99597 | 0.99567 | 0.99537
0.93108 | Diversity Factor: 0.93 | Uncompensated |  | Reactive Power |  |  | MVAr | 13.4782 | 14.6031 | 14.0962 | 13.6706 | 13.4461 | 13.4202 | 13.481 | 13.5496 | 13.7589 | 13.9978 | 14.211 | 14.4379 | 14.652 | 14.9161 | 15.1845 | 15.4786 | 15.7908 | 16.102 | 16.4141 | 16.7339 | 17.0614 | 17.3968 | 17.7401 | 18.0916 | 18.4512 | 18.8192 | 19.1956
|  |  |  | PF |  |  |  | 0.96717 |  | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684 | 0.9684
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## North Sydney 132_11kV
| North Sydney 132_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone commissioned |  | 2015-03-31
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | [8 empty] | 0 | 3783.054 | 3653.041 | 3597.869 | 3600.452 | 3606.549 | 3647.809 | 3706.729 | 3758.931 | 3812.618 | 3854.719 | 3910.813 | 3966.413 | 4032.756 | 4104.67 | 4174.99 | 4242.456 | 4311.093 | 4380.918 | 4451.945 | 4524.191 | 4597.67 | 4672.4 | 4748.395 | 4825.674 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3783.6009 | -3.9209 | 5.7253 | 2.5892 | 6.1111 | 41.3559 | 59.0531 | 52.3158 | 53.801 | 42.1878 | 56.2079 | 55.7091 | 66.4688 | 72.0462 | 70.4447 | 67.5817 | 68.7518 | 69.9372 | 71.1381 | 72.3545 | 73.5869 | 74.8352 | 76.0998 | 77.3809
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999 | 5999
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 | 9001 |  |  | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1155.7503 | -1.307 | 1.9084 | 0.86306 | 2.037 | 13.7853 | 19.6844 | 17.4386 | 17.9337 | 14.0626 | 18.736 | 18.5697 | 22.1563 | 24.0154 | 23.4816 | 22.5272 | 22.9173 | 23.3124 | 23.7127 | 24.1182 | 24.529 | 24.9451 | 25.3666 | 25.7936
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.0003 | -1.307 | 1.9084 | 0.86306 | 2.037 | 13.7853 | 19.6844 | 17.4386 | 17.9337 | 14.0626 | 18.736 | 18.5697 | 22.1563 | 24.0154 | 23.4816 | 22.5272 | 22.9173 | 23.3124 | 23.7127 | 24.1182 | 24.529 | 24.9451 | 25.3666 | 25.7936
| Transformer Loads | [35 empty] | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1377.8503 | -1.307 | 1.9084 | 0.86306 | 2.037 | 13.7853 | 19.6844 | 17.4386 | 17.9337 | 14.0626 | 18.736 | 18.5697 | 22.1563 | 24.0154 | 23.4816 | 22.5272 | 22.9173 | 23.3124 | 23.7127 | 24.1182 | 24.529 | 24.9451 | 25.3666 | 25.7936
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.082584 | -0.12388 | -0.74326 | -1.5958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.082584 | -0.12388 | -0.74326 | -1.5958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.082584 | -0.12388 | -0.74326 | -1.5958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297.3639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297.3639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297.3639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304.9001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304.9001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304.9001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012286. Establishment of S.62446 Spring Walker No 2 & Decommissioning of S.6063 Spring Little Spring, 100 Mount Street, North Sydney |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012286. Establishment of S.62446 Spring Walker No 2 & Decommissioning of S.6063 Spring Little Spring, 100 Mount Street, North Sydney | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013384. Establishment of S.64403 Berry Pacific No 2 and S.64403 Berry Pacific No 3, 177 Pacific Hwy, North Sydney and Decomm S.5532 Berry Angelo |  | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013384. Establishment of S.64403 Berry Pacific No 2 and S.64403 Berry Pacific No 3, 177 Pacific Hwy, North Sydney and Decomm S.5532 Berry Angelo | North Sydney 132_11kV Tx11 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2014027. New Chamber S.64679 Little Walker Arthur No.2 and Decomm S.2713 Arthur Standards House, 80 Arthur Street, North Sydney, 1000kVA chamber substation | North Sydney 132_11kV Tx12 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2551 | 17.9772 | 25.6732 | 25.4312 | 26.5288 | 26.2744 | 26.0048 | 26.3564 | 26.7126 | 27.0734 | 27.439 | 27.8094 | 28.1845 | 28.5646 | 28.9496 | 29.3397 | 29.7348 | 30.1351 | 30.5406 | 30.9514 | 31.3675 | 31.789 | 32.216
| 0 | [33 empty] | Econometric |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2551 | 17.9772 | 25.6732 | 25.4312 | 26.5288 | 26.2744 | 26.0048 | 26.3564 | 26.7126 | 27.0734 | 27.439 | 27.8094 | 28.1845 | 28.5646 | 28.9496 | 29.3397 | 29.7348 | 30.1351 | 30.5406 | 30.9514 | 31.3675 | 31.789 | 32.216
| Diversity Factor: 0 | [33 empty] | Econometric |  | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2551 | 17.9772 | 25.6732 | 25.4312 | 26.5288 | 26.2744 | 26.0048 | 26.3564 | 26.7126 | 27.0734 | 27.439 | 27.8094 | 28.1845 | 28.5646 | 28.9496 | 29.3397 | 29.7348 | 30.1351 | 30.5406 | 30.9514 | 31.3675 | 31.789 | 32.216
[35 empty] | Energy Efficiency |  | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0353 | -10.0528 | -14.9025 | -22.7616 | -22.9173 | -12.2442 | -6.1073 | -8.0757 | -8.0474 | -12.2005 | -7.888 | -8.4198 | -5.2036 | -3.7196 | -4.6335 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729
[35 empty] | Energy Efficiency |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0353 | -10.0528 | -14.9025 | -22.7616 | -22.9173 | -12.2442 | -6.1073 | -8.0757 | -8.0474 | -12.2005 | -7.888 | -8.4198 | -5.2036 | -3.7196 | -4.6335 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729
| 0 | [33 empty] | Energy Efficiency |  | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0353 | -10.0528 | -14.9025 | -22.7616 | -22.9173 | -12.2442 | -6.1073 | -8.0757 | -8.0474 | -12.2005 | -7.888 | -8.4198 | -5.2036 | -3.7196 | -4.6335 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729 | -5.9729
| Diversity Factor: 0 | [33 empty] | Solar PV |  | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.34129 | -0.38545 | -0.42294 | -0.45265 | -0.47686 | -0.49926 | -0.4828 | -0.49047 | -0.37528 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951
[35 empty] | Solar PV |  | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.34129 | -0.38545 | -0.42294 | -0.45265 | -0.47686 | -0.49926 | -0.4828 | -0.49047 | -0.37528 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951
[35 empty] | Solar PV |  | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.34129 | -0.38545 | -0.42294 | -0.45265 | -0.47686 | -0.49926 | -0.4828 | -0.49047 | -0.37528 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951 | -0.44951
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [8 empty] | Rog Capped +/-5% | [59 empty] | Rog Capped +/-5%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | North Sydney 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 | 0 | 0 | 3783.054 | 3653.041 | 3597.869 | 3600.452 | 3606.549 | 3647.809 | 3706.729 | 3758.931 | 3812.618 | 3854.719 | 3910.813 | 3966.413 | 4032.756 | 4104.67 | 4174.99 | 4242.456 | 4311.093 | 4380.918 | 4451.945 | 4524.191 | 4597.67 | 4672.4 | 4748.395 | 4825.674
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 72.0769 | 69.5998 | 68.5486 | 68.5978 | 68.714 | 69.5001 | 70.6227 | 71.6173 | 72.6401 | 73.4423 | 74.511 | 75.5703 | 76.8343 | 78.2045 | 79.5443 | 80.8296 | 82.1374 | 83.4677 | 84.821 | 86.1974 | 87.5974 | 89.0212 | 90.4691 | 91.9414
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 66.869 | 64.5728 | 63.5948 | 63.6392 | 63.744 | 64.4531 | 65.4657 | 66.3628 | 67.2853 | 68.0088 | 68.9726 | 69.9278 | 71.0676 | 72.303 | 73.5109 | 74.6698 | 75.8487 | 77.0479 | 78.2677 | 79.5084 | 80.7702 | 82.0535 | 83.3584 | 84.6852
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 26.8999 | 25.9707 | 25.5854 | 25.6069 | 25.6577 | 26.0011 | 26.4915 | 26.926 | 27.3728 | 27.7232 | 28.19 | 28.6526 | 29.2046 | 29.803 | 30.388 | 30.9492 | 31.5202 | 32.101 | 32.6918 | 33.2927 | 33.9038 | 34.5253 | 35.1573 | 35.8
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0.92775 | 0.92777 | 0.92773 | 0.92771 | 0.92767 | 0.92738 | 0.92698 | 0.92663 | 0.92628 | 0.92602 | 0.92567 | 0.92533 | 0.92495 | 0.92454 | 0.92415 | 0.92379 | 0.92344 | 0.92309 | 0.92274 | 0.9224 | 0.92206 | 0.92173 | 0.9214 | 0.92108
0.96519 | Diversity Factor: 0.97 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 26.8999 | 25.9707 | 25.5854 | 25.6069 | 25.6577 | 26.0011 | 26.4915 | 26.926 | 27.3728 | 27.7232 | 28.19 | 28.6526 | 29.2046 | 29.803 | 30.388 | 30.9492 | 31.5202 | 32.101 | 32.6918 | 33.2927 | 33.9038 | 34.5253 | 35.1573 | 35.8
|  |  |  | PF |  |  |  | 0 |  | 0 | 0.92775 | 0.92777 | 0.92773 | 0.92771 | 0.92767 | 0.92738 | 0.92698 | 0.92663 | 0.92628 | 0.92602 | 0.92567 | 0.92533 | 0.92495 | 0.92454 | 0.92415 | 0.92379 | 0.92344 | 0.92309 | 0.92274 | 0.9224 | 0.92206 | 0.92173 | 0.9214 | 0.92108
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## North Sydney 33_11kV
| North Sydney 33_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone decommissioned |  | 2015-03-31
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 4744 | 4670 | 4629 | 4728 | 4223 | 4130 | 3653 |  | 3765.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | 19.8 | 0 | 0 | 83.1504 | -2.8805 | -0.46975 | -13.5562 | 15.6142 | -3577.6283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 5930 |  | 5930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 8000 |  | 8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | North Sydney 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | North Sydney 33_11kV Tx2 | -55.2 | 0 | 0 | 39.1328 | -0.7276 | 21.8813 | -13.5142 | -4.6651 | -925.0918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | North Sydney 33_11kV Tx3 | 75 | 35 | 0 | -0.47363 | -0.73759 | -0.12029 | -0.014381 | 33.2434 | -904.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | North Sydney 33_11kV Tx4 | 0 | -35 | 0 | -50.4791 | -0.74604 | -40.1217 | -4.0145 | -6.834 | -927.7002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 94.9703 | -0.66921 | 17.8909 | 3.987 | -6.1302 | -820.4983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | North Sydney 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | North Sydney 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Broad based demand management |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.9784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 5948. Minor Zone Development on Panels 4, 8, 9, 10, and 13 Feeders at North Sydney Zone | North Sydney 33_11kV Tx2 | North Sydney 33_11kV Tx3 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6405. Change of Open Points to Relieve Panel 26L North Sydney Remedial Feeder. | North Sydney 33_11kV Tx4 | North Sydney 33_11kV Tx3 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6502. 11kV Supply Arrangements for the Sydney Harbour Tunnel | North Sydney 33_11kV Tx5 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6515. North Sydney Zone Conversion - Stage 1 of 4 | Crows Nest 33_11kV Tx1 | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6515. North Sydney Zone Conversion - Stage 1 of 4 | North Sydney 33_11kV Tx5 | Crows Nest 33_11kV Tx1 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6764. North Sydney Open Point Changes | North Sydney 33_11kV Tx4 | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7117. Mosman Zone Review South West | Mosman 132_11kV Tx3 | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx1 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297.3639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297.3639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297.3639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx3 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304.9001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304.9001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx4 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304.9001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | North Sydney 33_11kV Tx5 | North Sydney 132_11kV Tx13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2004450. Est Basement S.8190 "Wheeler Mount" - North Sydney Embedded Generation, Generator |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 50.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2004459. Est S.8223 'Little Walker Arthur 98' |  | North Sydney 33_11kV Tx2 | 19.8 | 0 | 0 | 39.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2010198. Replace S.3057 Wheeler William with 48069 Wheeler Lane, North Sydney. Transfer 450A (LV) from S.3057 (PA26) to existing S.8190 (PA42). No new load, only LV load transfer. | North Sydney 33_11kV Tx4 | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011501. Establishment of S.50434 Carabella Parker, Premises of Loreto College, Carrabella St, Kirribilli | North Sydney 33_11kV Tx4 | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012286. Establishment of S.62446 Spring Walker No 2 & Decommissioning of S.6063 Spring Little Spring, 100 Mount Street, North Sydney |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012286. Establishment of S.62446 Spring Walker No 2 & Decommissioning of S.6063 Spring Little Spring, 100 Mount Street, North Sydney | North Sydney 33_11kV Tx2 | North Sydney 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | HVCON_ID: 2012305. Uprate chamber S.373 Middle St and LV UG, Middle Street, North Sydney Zone | North Sydney 33_11kV Tx4 | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | ROG Justification | [24 empty] | HVCON_ID: 2012423. Establishment of S.62947 Angelo Berry No 2, 211-215 Pacific Hwy, North Sydney NSW 2060 | North Sydney 33_11kV Tx2 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 5.658% |  | Rog Capped +/-5% | [24 empty] | HVCON_ID: 2012423. Establishment of S.62947 Angelo Berry No 2, 211-215 Pacific Hwy, North Sydney NSW 2060 | North Sydney 33_11kV Tx3 | Crows Nest 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rog Capped +/-5%
[35 empty] | HVCON_ID: 2012432. Decommission and remove S.2813 and reconfigure LV network, 211-215 Pacific Hwy, North Sydney |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | -13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012432. Decommission and remove S.2813 and reconfigure LV network, 211-215 Pacific Hwy, North Sydney | North Sydney 33_11kV Tx2 | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | HVCON_ID: 2014104. Relocate S.2316 NORTH SYDNEY ANZAC CLUB, Anzac Avenue, Cammeray Load Increase at S.35329 ERNEST MILLER | North Sydney 33_11kV Tx4 | Crows Nest 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Econometric |  | North Sydney 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2: Substation Load Detail | Econometric |  | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | North Sydney 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | Econometric |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | North Sydney 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 3653 | 3948 | 3765.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | North Sydney 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 69.599 |  | 71.7505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 64.6463 | 69.8669 | 66.6783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 25.7851 |  | 26.4978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | North Sydney 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Efficiency |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.9397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.92884 |  | 0.92931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | North Sydney 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.9785 | Diversity Factor: 0.98 | Uncompensated |  | Reactive Power |  |  | MVAr | 25.7851 | 27.8674 | 26.4978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | North Sydney 33_11kV Tx2 | 0 | 0 | 0 | -0.46722 | -0.7276 | -0.11866 | -0.014186 | -0.23058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.92884 |  | 0.92931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar PV |  | North Sydney 33_11kV Tx3 | 0 | 0 | 0 | -0.47363 | -0.73759 | -0.12029 | -0.014381 | -0.23374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | Solar PV |  | North Sydney 33_11kV Tx4 | 0 | 0 | 0 | -0.47906 | -0.74604 | -0.12167 | -0.014546 | -0.23642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Load Detail | [33 empty] | Solar PV |  | North Sydney 33_11kV Tx5 | 0 | 0 | 0 | -0.42972 | -0.66921 | -0.10914 | -0.013048 | -0.21207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## RNS Hospital 132_11kV
| RNS Hospital 132_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone commissioned |  | 2011-11-30
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  |  | 359 | 650 | 593 |  | 666.9897 | 651.2962 | 640.6484 | 635.2332 | 633.8778 | 633.1175 | 635.8282 | 640.7873 | 645.1585 | 649.6174 | 652.6111 | 657.084 | 661.447 | 667.0391 | 673.2266 | 679.197 | 684.7668 | 690.4232 | 696.1673 | 702.0001 | 707.9227 | 713.9363 | 720.0419 | 726.2407 | 732.5338 |  |  | Total | 0 | 0 | 0 | 45 | 379 | 295.2 | 8.0253 | 96.1813 | -1.2873 | -1.2697 | -0.80282 | -1.3554 | -0.76026 | 2.7107 | 4.9591 | 4.3712 | 4.459 | 2.9936 | 4.473 | 4.3629 | 5.5922 | 6.1875 | 5.9703 | 5.5698 | 5.6564 | 5.7441 | 5.8328 | 5.9227 | 6.0136 | 6.1056 | 6.1988 | 6.2931
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2810 |  | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810 | 2810
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 5108 |  | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 | 5108 |  |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 144 | 99 | 8.5602 | 72.4282 | -0.58082 | -0.57286 | -0.36222 | -0.61155 | -0.34302 | 1.223 | 2.2375 | 1.9722 | 2.0118 | 1.3507 | 2.0181 | 1.9685 | 2.5231 | 2.7917 | 2.6937 | 2.513 | 2.5521 | 2.5916 | 2.6317 | 2.6722 | 2.7132 | 2.7548 | 2.7968 | 2.8394
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 45 | 235 | 196.2 | -0.53491 | 23.753 | -0.70649 | -0.69681 | -0.4406 | -0.74388 | -0.41724 | 1.4877 | 2.7216 | 2.399 | 2.4471 | 1.6429 | 2.4548 | 2.3944 | 3.0691 | 3.3958 | 3.2766 | 3.0568 | 3.1043 | 3.1524 | 3.2011 | 3.2504 | 3.3003 | 3.3508 | 3.402 | 3.4537
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0061917 | -0.012383 | -0.018575 | -0.11145 | -0.2229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0075314 | -0.015063 | -0.022594 | -0.13557 | -0.27113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 80.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 145.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning | Gore Hill 33_11kV Tx3 | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6469. 11kV Component of Royal North Shore Hospital Zone Commissioning | Gore Hill 33_11kV Tx3 | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2007061. Establishment of S.35551 RNS Hospital No. 7, Westbourne St (Cnr Reserve Rd) St Leonards |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2008464. Establishment of 6 x Kiosks & 1x Chamber Sub: S.36151 Spine Campbell No 1; S.36152 Spine Campbell No 2; S.36153 Spine Campbell No 3 (Chamber); S.36161 Spine Pacific No 1; S.36162 Spine Pacific No 2; S.36163 Spine Pacif |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 18.9 | 0 | 6.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2008464. Establishment of 6 x Kiosks & 1x Chamber Sub: S.36151 Spine Campbell No 1; S.36152 Spine Campbell No 2; S.36153 Spine Campbell No 3 (Chamber); S.36161 Spine Pacific No 1; S.36162 Spine Pacific No 2; S.36163 Spine Pacif |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 37.8 | 0 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2009492. New S.47161 RNSH Comm Health No.1 and S.47162 RNSH Comm Health No.2 |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011785. Establishment of S.50040 Westbourne NS TAFE, North Sydney TAFE, 213 Pacific Hway, St Leongards (site fronts Westbourne St) |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 12.6 | 0 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012395. Establishment of S.62445 RNSH Clinical Services, RNS Hospital Clinical Service Bldg - Westbourne St, St Leonards |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93224 | 1.8644 | 2.7861 | 2.7825 | 2.8291 | 2.8542 | 2.8793 | 2.9148 | 2.9506 | 2.987 | 3.0238 | 3.061 | 3.0987 | 3.1368 | 3.1754 | 3.2145 | 3.254 | 3.2941 | 3.3346 | 3.3756 | 3.4172 | 3.4592 | 3.5017
| Diversity Factor: 0 | [33 empty] | Econometric |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.134 | 2.2678 | 3.389 | 3.3846 | 3.4412 | 3.4717 | 3.5023 | 3.5454 | 3.5891 | 3.6333 | 3.678 | 3.7233 | 3.7691 | 3.8155 | 3.8625 | 3.91 | 3.9582 | 4.0069 | 4.0562 | 4.1061 | 4.1566 | 4.2077 | 4.2594
[35 empty] | Energy Efficiency |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2129 | -0.50933 | -1.4198 | -2.0419 | -3.0964 | -3.043 | -1.5196 | -0.53308 | -0.82215 | -0.83795 | -1.5221 | -0.891 | -0.97743 | -0.46002 | -0.22909 | -0.36522 | -0.58455 | -0.58455 | -0.58455 | -0.58455 | -0.58455 | -0.58455 | -0.58455 | -0.58455 | -0.58455
[35 empty] | Energy Efficiency |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4753 | -0.61954 | -1.727 | -2.4838 | -3.7664 | -3.7014 | -1.8484 | -0.64843 | -1 | -1.0193 | -1.8515 | -1.0838 | -1.1889 | -0.55956 | -0.27867 | -0.44425 | -0.71104 | -0.71104 | -0.71104 | -0.71104 | -0.71104 | -0.71104 | -0.71104 | -0.71104 | -0.71104
| 0 | [33 empty] | Solar PV |  | RNS Hospital 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | -0.43976 | -0.052691 | -0.059101 | -0.066748 | -0.07324 | -0.078384 | -0.082577 | -0.086457 | -0.083605 | -0.084934 | -0.064987 | -0.077842 | -0.077842 | -0.077842 | -0.077842 | -0.077842 | -0.077842 | -0.077842 | -0.077842 | -0.077842 | -0.077842 | -0.077842 | -0.077842 | -0.077842 | -0.077842 | -0.077842
| Diversity Factor: 0 | [33 empty] | Solar PV |  | RNS Hospital 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | -0.53491 | -0.064092 | -0.071889 | -0.081191 | -0.089087 | -0.095345 | -0.10045 | -0.10516 | -0.1017 | -0.10331 | -0.079049 | -0.094686 | -0.094686 | -0.094686 | -0.094686 | -0.094686 | -0.094686 | -0.094686 | -0.094686 | -0.094686 | -0.094686 | -0.094686 | -0.094686 | -0.094686 | -0.094686 | -0.094686
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | -1.617% |  | Weighted ROG calc | [59 empty] | Weighted ROG calc
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.97841 | 0.95729 | 0.94351 | 0.93673 | 0.93673 | 0.93673 | 0.93673 | 0.93673 | 0.93673 | 0.93673 | -2.159% | -2.159% | -1.439% | -0.719% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | RNS Hospital 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 593 | 583.4094 | 666.9897 | 651.2962 | 640.6484 | 635.2332 | 633.8778 | 633.1175 | 635.8282 | 640.7873 | 645.1585 | 649.6174 | 652.6111 | 657.084 | 661.447 | 667.0391 | 673.2266 | 679.197 | 684.7668 | 690.4232 | 696.1673 | 702.0001 | 707.9227 | 713.9363 | 720.0419 | 726.2407 | 732.5338
|  |  |  | Apparent Power |  |  | MVA | 11.2982 |  | 12.7079 | 12.4089 | 12.206 | 12.1028 | 12.077 | 12.0625 | 12.1142 | 12.2086 | 12.2919 | 12.3769 | 12.4339 | 12.5191 | 12.6022 | 12.7088 | 12.8267 | 12.9404 | 13.0466 | 13.1543 | 13.2638 | 13.3749 | 13.4877 | 13.6023 | 13.7186 | 13.8367 | 13.9566
|  |  |  | Real Power |  |  | MW | 9.5363 | 9.3821 | 10.7262 | 10.4738 | 10.3026 | 10.2155 | 10.1937 | 10.1815 | 10.2251 | 10.3048 | 10.3751 | 10.4468 | 10.495 | 10.5669 | 10.6371 | 10.727 | 10.8265 | 10.9225 | 11.0121 | 11.1031 | 11.1954 | 11.2892 | 11.3845 | 11.4812 | 11.5794 | 11.6791 | 11.7803
|  |  |  | Reactive Power |  |  | MVAr | 6.0586 |  | 6.8145 | 6.6542 | 6.5454 | 6.4901 | 6.4762 | 6.4685 | 6.4962 | 6.5468 | 6.5915 | 6.6371 | 6.6676 | 6.7133 | 6.7579 | 6.8151 | 6.8783 | 6.9393 | 6.9962 | 7.054 | 7.1126 | 7.1722 | 7.2328 | 7.2942 | 7.3566 | 7.4199 | 7.4842
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.84406 |  | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406
0.90636 | Diversity Factor: 0.91 | Uncompensated |  | Reactive Power |  |  | MVAr | 6.0586 | 5.9606 | 6.8145 | 6.6542 | 6.5454 | 6.4901 | 6.4762 | 6.4685 | 6.4962 | 6.5468 | 6.5915 | 6.6371 | 6.6676 | 6.7133 | 6.7579 | 6.8151 | 6.8783 | 6.9393 | 6.9962 | 7.054 | 7.1126 | 7.1722 | 7.2328 | 7.2942 | 7.3566 | 7.4199 | 7.4842
|  |  |  | PF |  |  |  | 0.84406 |  | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406 | 0.84406
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer36
| Customer36 | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  | 309 | 201 | 161 | 192 |  | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Customer36 | Compensated |  | Load (LV side) |  |  | Amps | 192 |  | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192
|  |  |  | Apparent Power |  |  | MVA | 10.9743 |  | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743 | 10.9743
|  |  |  | Real Power |  |  | MW | 9.8768 |  | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768 | 9.8768
|  |  |  | Reactive Power |  |  | MVAr | 4.7836 |  | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.43736 | Diversity Factor: 0.44 | Uncompensated |  | Reactive Power |  |  | MVAr | 4.7836 |  | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836 | 4.7836
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer37
| Customer37 | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  | 164 | 201 | 197 | 218 |  | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Customer37 | Compensated |  | Load (LV side) |  |  | Amps | 218 |  | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218
|  |  |  | Apparent Power |  |  | MVA | 12.4604 |  | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604 | 12.4604
|  |  |  | Real Power |  |  | MW | 11.2143 |  | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143 | 11.2143
|  |  |  | Reactive Power |  |  | MVAr | 5.4314 |  | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.58814 | Diversity Factor: 0.59 | Uncompensated |  | Reactive Power |  |  | MVAr | 5.4314 |  | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314 | 5.4314
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF