## Inclusions and Exclusions
Sydney Forecast Inclusions and Exclusions
Date Printed |  | 08JUL14:11:21:24
| Description | Value
Season |  | Winter | Winter
Either Summer or Winter
Year |  | 2014 | 2014
Year that the forecast starts
POE |  | 50% | 0.5
10%, 50%, 90%
Spots and Transfers |  | Y | Y
Are Spots and Transfers Included?
BBDM Spots |  | Y | Y
Is BBDM included?
Spots Coefficient |  | 55% | 0.55
Scaling factor applied to spot loads in the future
Aligned ROGs |  | Capped | Capped
Have ROGs been aligned to econometric forecast?
Committed Projects |  | Y | Y
Are Committed Projects Included?
Major Customers Scaling Factor |  | 100% | 1
Scaling factor applied to major customer connections in the future
Future Transfers |  | Y | Y
Are future transfers included?
Future Spots |  | 4 | 4
Future spots are cleared from the following forecast year

## Belmore Park 132_11kV
| Belmore Park 132_11kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | [8 empty] | 0 | 0 | 382.7825 | 1954.468 | 2895.516 | 2889.698 | 2912.97 | 2950.863 | 2984.056 | 3017.554 | 3039.154 | 3072.895 | 3105.67 | 3148.515 | 3196.205 | 3242.042 | 3284.516 | 3327.639 | 3371.42 | 3415.867 | 3460.988 | 3506.791 | 3553.283 | 3600.475 | 3648.374 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.2979 | 1576.131 | 941.0481 | -5.8187 | 23.2719 | 37.8937 | 33.193 | 33.4974 | 21.6003 | 33.7413 | 32.7747 | 42.8446 | 47.6905 | 45.837 | 42.4735 | 43.1234 | 43.7811 | 44.4469 | 45.1207 | 45.8027 | 46.493 | 47.1916 | 47.8987
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739 | 6739
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 | 13479 |  |  | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3245 | 394.0327 | 235.262 | -1.4547 | 5.818 | 9.4734 | 8.2982 | 8.3744 | 5.4001 | 8.4353 | 8.1937 | 10.7112 | 11.9226 | 11.4592 | 10.6184 | 10.7808 | 10.9453 | 11.1117 | 11.2802 | 11.4507 | 11.6232 | 11.7979 | 11.9747
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3245 | 394.0327 | 235.262 | -1.4547 | 5.818 | 9.4734 | 8.2982 | 8.3744 | 5.4001 | 8.4353 | 8.1937 | 10.7112 | 11.9226 | 11.4592 | 10.6184 | 10.7808 | 10.9453 | 11.1117 | 11.2802 | 11.4507 | 11.6232 | 11.7979 | 11.9747
| Transformer Loads | [35 empty] | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3245 | 394.0327 | 235.262 | -1.4547 | 5.818 | 9.4734 | 8.2982 | 8.3744 | 5.4001 | 8.4353 | 8.1937 | 10.7112 | 11.9226 | 11.4592 | 10.6184 | 10.7808 | 10.9453 | 11.1117 | 11.2802 | 11.4507 | 11.6232 | 11.7979 | 11.9747
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3245 | 394.0327 | 235.262 | -1.4547 | 5.818 | 9.4734 | 8.2982 | 8.3744 | 5.4001 | 8.4353 | 8.1937 | 10.7112 | 11.9226 | 11.4592 | 10.6184 | 10.7808 | 10.9453 | 11.1117 | 11.2802 | 11.4507 | 11.6232 | 11.7979 | 11.9747
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.13886 | -0.15429 | -0.15429 | -0.15429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.13886 | -0.15429 | -0.15429 | -0.15429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.13886 | -0.15429 | -0.15429 | -0.15429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.13886 | -0.15429 | -0.15429 | -0.15429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx1 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6169 | 118.8926 | 78.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx1 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6169 | 118.8926 | 78.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx1 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6169 | 118.8926 | 78.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx1 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6169 | 118.8926 | 78.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx2 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx2 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx2 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx2 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx3 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3113 | 4.931 | 3.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx3 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3113 | 4.931 | 3.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx3 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3113 | 4.931 | 3.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx3 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3113 | 4.931 | 3.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx4 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx4 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx4 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx4 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Transfers | City Central 132_11kV Tx1 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Transfers | City Central 132_11kV Tx1 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx1 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx1 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Transfers | City Central 132_11kV Tx2 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Transfers | City Central 132_11kV Tx2 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx2 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx2 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Transfers | City Central 132_11kV Tx3 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Transfers | City Central 132_11kV Tx3 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx3 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx3 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx4 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Transfers | City Central 132_11kV Tx4 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | ROG Justification | [24 empty] | Transfers | City Central 132_11kV Tx4 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0% |  | 7 year ROG ok | [24 empty] | Transfers | City Central 132_11kV Tx4 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 year ROG ok
[35 empty] | Econometric |  | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76136 | 4.5891 | 11.3755 | 12.6177 | 12.7728 | 11.9235 | 12.0693 | 12.2168 | 12.3662 | 12.5173 | 12.6703 | 12.8251 | 12.9818 | 13.1404 | 13.3009 | 13.4634 | 13.6278 | 13.7943 | 13.9627 | 14.1332 | 14.3058 | 14.4804 | 14.6572
[35 empty] | Econometric |  | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76136 | 4.5891 | 11.3755 | 12.6177 | 12.7728 | 11.9235 | 12.0693 | 12.2168 | 12.3662 | 12.5173 | 12.6703 | 12.8251 | 12.9818 | 13.1404 | 13.3009 | 13.4634 | 13.6278 | 13.7943 | 13.9627 | 14.1332 | 14.3058 | 14.4804 | 14.6572
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Econometric |  | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76136 | 4.5891 | 11.3755 | 12.6177 | 12.7728 | 11.9235 | 12.0693 | 12.2168 | 12.3662 | 12.5173 | 12.6703 | 12.8251 | 12.9818 | 13.1404 | 13.3009 | 13.4634 | 13.6278 | 13.7943 | 13.9627 | 14.1332 | 14.3058 | 14.4804 | 14.6572
0.96525 | 0.93171 | 0.91012 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | -3.475% | -3.475% | -2.317% | -1.158% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Econometric |  | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76136 | 4.5891 | 11.3755 | 12.6177 | 12.7728 | 11.9235 | 12.0693 | 12.2168 | 12.3662 | 12.5173 | 12.6703 | 12.8251 | 12.9818 | 13.1404 | 13.3009 | 13.4634 | 13.6278 | 13.7943 | 13.9627 | 14.1332 | 14.3058 | 14.4804 | 14.6572
[35 empty] | Energy Efficiency |  | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.298 | -5.6021 | -14.1592 | -13.9181 | -6.9549 | -2.4501 | -3.771 | -3.8425 | -6.9661 | -4.082 | -4.4766 | -2.1139 | -1.0592 | -1.6812 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826
| Substation Load Detail | [33 empty] | Energy Efficiency |  | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.298 | -5.6021 | -14.1592 | -13.9181 | -6.9549 | -2.4501 | -3.771 | -3.8425 | -6.9661 | -4.082 | -4.4766 | -2.1139 | -1.0592 | -1.6812 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826
[35 empty] | Energy Efficiency |  | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.298 | -5.6021 | -14.1592 | -13.9181 | -6.9549 | -2.4501 | -3.771 | -3.8425 | -6.9661 | -4.082 | -4.4766 | -2.1139 | -1.0592 | -1.6812 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Energy Efficiency |  | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.298 | -5.6021 | -14.1592 | -13.9181 | -6.9549 | -2.4501 | -3.771 | -3.8425 | -6.9661 | -4.082 | -4.4766 | -2.1139 | -1.0592 | -1.6812 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826 | -2.6826
1 | Belmore Park 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 | 0 | 0 | 0 | 382.7825 | 1954.468 | 2895.516 | 2889.698 | 2912.97 | 2950.863 | 2984.056 | 3017.554 | 3039.154 | 3072.895 | 3105.67 | 3148.515 | 3196.205 | 3242.042 | 3284.516 | 3327.639 | 3371.42 | 3415.867 | 3460.988 | 3506.791 | 3553.283 | 3600.475 | 3648.374 | Solar PV |  | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 7.293 | 37.2376 | 55.167 | 55.0561 | 55.4995 | 56.2215 | 56.8539 | 57.4921 | 57.9037 | 58.5465 | 59.171 | 59.9873 | 60.8959 | 61.7692 | 62.5784 | 63.4 | 64.2342 | 65.081 | 65.9407 | 66.8133 | 67.6992 | 68.5983 | 69.5109 | Solar PV |  | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 6.5212 | 33.2224 | 49.2199 | 49.121 | 49.5166 | 50.1607 | 50.7249 | 51.2944 | 51.6615 | 52.2351 | 52.7922 | 53.5205 | 54.3312 | 55.1104 | 55.8323 | 56.5654 | 57.3096 | 58.0652 | 58.8321 | 59.6107 | 60.401 | 61.2032 | 62.0174 | Solar PV |  | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 3.2653 | 16.82 | 24.9159 | 24.8658 | 25.0661 | 25.3921 | 25.6777 | 25.966 | 26.1519 | 26.4422 | 26.7242 | 27.0929 | 27.5033 | 27.8977 | 28.2632 | 28.6343 | 29.011 | 29.3935 | 29.7817 | 30.1759 | 30.5759 | 30.982 | 31.3942 | Solar PV |  | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0.89417 | 0.89217 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922
0.77532 | Diversity Factor: 0.78 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 3.2653 | 16.82 | 24.9159 | 24.8658 | 25.0661 | 25.3921 | 25.6777 | 25.966 | 26.1519 | 26.4422 | 26.7242 | 27.0929 | 27.5033 | 27.8977 | 28.2632 | 28.6343 | 29.011 | 29.3935 | 29.7817 | 30.1759 | 30.5759 | 30.982 | 31.3942
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0.89417 | 0.89217 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922 | 0.8922
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## City Central 132_11kV
| City Central 132_11kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 6790 | 6386 | 5597 | 5786 | 5415 | 5708 | 5748 |  | 4736.469 | 4416.955 | 4289.174 | 3215.172 | 3185.228 | 3165.722 | 3205.363 | 3276.978 | 3339.052 | 3394.897 | 3431.848 | 3493.526 | 3553.376 | 3634.098 | 3725.124 | 3806.722 | 3885.496 | 3965.878 | 4047.876 | 4131.502 | 4216.764 | 4296.79 | 4383.446 | 4471.819 | 4561.919 |  |  | Total | 0 | 0 | 0 | 287 | 0 | 0 | 0 | -3.0343 | -173.8862 | -27.4167 | -1146.5177 | -32.85 | -21.4337 | 43.5297 | 78.3672 | 67.6587 | 68.2236 | 41.1624 | 68.4759 | 66.183 | 88.8819 | 99.7402 | 95.4497 | 87.7203 | 89.0827 | 90.4616 | 91.8572 | 93.2697 | 94.6994 | 96.1464 | 97.6109 | 99.0932
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 10236 |  | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 13350 |  | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 | 13350 |  |  | City Central 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.75858 | -43.4716 | -6.8542 | -286.6294 | -8.2125 | -5.3584 | 10.8824 | 19.5918 | 16.9147 | 17.0559 | 10.2906 | 17.119 | 16.5457 | 22.2205 | 24.9351 | 23.8624 | 21.9301 | 22.2707 | 22.6154 | 22.9643 | 23.3174 | 23.6748 | 24.0366 | 24.4027 | 24.7733
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | City Central 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.75858 | -43.4716 | -6.8542 | -286.6294 | -8.2125 | -5.3584 | 10.8824 | 19.5918 | 16.9147 | 17.0559 | 10.2906 | 17.119 | 16.5457 | 22.2205 | 24.9351 | 23.8624 | 21.9301 | 22.2707 | 22.6154 | 22.9643 | 23.3174 | 23.6748 | 24.0366 | 24.4027 | 24.7733
| Transformer Loads | [35 empty] | City Central 132_11kV Tx3 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | -0.75858 | -43.4716 | -6.8542 | -286.6294 | -8.2125 | -5.3584 | 10.8824 | 19.5918 | 16.9147 | 17.0559 | 10.2906 | 17.119 | 16.5457 | 22.2205 | 24.9351 | 23.8624 | 21.9301 | 22.2707 | 22.6154 | 22.9643 | 23.3174 | 23.6748 | 24.0366 | 24.4027 | 24.7733
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  | City Central 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.75858 | -43.4716 | -6.8542 | -286.6294 | -8.2125 | -5.3584 | 10.8824 | 19.5918 | 16.9147 | 17.0559 | 10.2906 | 17.119 | 16.5457 | 22.2205 | 24.9351 | 23.8624 | 21.9301 | 22.2707 | 22.6154 | 22.9643 | 23.3174 | 23.6748 | 24.0366 | 24.4027 | 24.7733
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | City Central 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.19011 | -0.21123 | -0.21123 | -0.21123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | City Central 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.19011 | -0.21123 | -0.21123 | -0.21123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | City Central 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.19011 | -0.21123 | -0.21123 | -0.21123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | City Central 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.19011 | -0.21123 | -0.21123 | -0.21123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx1 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7975 | 4.8734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx1 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx1 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx1 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7848 | 13.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx1 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75949 | 0.97468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx2 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7975 | 4.8734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx2 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx2 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx2 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7848 | 13.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx2 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75949 | 0.97468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx3 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7975 | 4.8734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx3 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx3 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx3 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7848 | 13.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx3 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75949 | 0.97468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx4 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7975 | 4.8734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx4 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx4 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx4 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7848 | 13.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx4 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75949 | 0.97468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6448. Relief of panel 1L, 3L and 12L feeders at Darling Harbour zone | Darling Harbour 132_11kV Tx11 | City Central 132_11kV Tx3 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6448. Relief of panel 1L, 3L and 12L feeders at Darling Harbour zone | Darling Harbour 132_11kV Tx12 | City Central 132_11kV Tx3 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Spot |  | City Central 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Spot |  | City Central 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Spot |  | City Central 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Spot |  | City Central 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx1 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx1 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx1 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Transfers | City Central 132_11kV Tx1 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | ROG Justification | [24 empty] | Transfers | City Central 132_11kV Tx1 | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | -10.54% |  | 7 year ROG ok | [24 empty] | Transfers | City Central 132_11kV Tx1 | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 year ROG ok
[35 empty] | Transfers | City Central 132_11kV Tx1 | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx1 | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Transfers | City Central 132_11kV Tx2 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.96525 | 0.93171 | 0.91012 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | -3.475% | -3.475% | -2.317% | -1.158% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Transfers | City Central 132_11kV Tx2 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx2 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Substation Load Detail | [33 empty] | Transfers | City Central 132_11kV Tx2 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx2 | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Transfers | City Central 132_11kV Tx2 | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | City Central 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 5748 | 5232.7357 | 4736.469 | 4416.955 | 4289.174 | 3215.172 | 3185.228 | 3165.722 | 3205.363 | 3276.978 | 3339.052 | 3394.897 | 3431.848 | 3493.526 | 3553.376 | 3634.098 | 3725.124 | 3806.722 | 3885.496 | 3965.878 | 4047.876 | 4131.502 | 4216.764 | 4296.79 | 4383.446 | 4471.819 | 4561.919 | Transfers | City Central 132_11kV Tx2 | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 109.5141 |  | 90.2418 | 84.1543 | 81.7197 | 61.2572 | 60.6868 | 60.3151 | 61.0704 | 62.4348 | 63.6175 | 64.6815 | 65.3855 | 66.5606 | 67.7009 | 69.2389 | 70.9731 | 72.5278 | 74.0286 | 75.5601 | 77.1224 | 78.7157 | 80.3401 | 81.8648 | 83.5159 | 85.1996 | 86.9162 | Transfers | City Central 132_11kV Tx2 | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 102.752 | 93.5411 | 90.2379 | 84.1347 | 81.7174 | 61.2094 | 60.6489 | 60.2832 | 61.0259 | 62.363 | 63.5173 | 64.6813 | 65.3836 | 66.5519 | 67.6811 | 69.1975 | 70.8993 | 72.5278 | 74.0244 | 75.5443 | 77.0877 | 78.6549 | 80.2463 | 81.862 | 83.5024 | 85.1678 | 86.8584 | Transfers | City Central 132_11kV Tx3 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 37.8862 |  | 0.84892 | 1.8156 | 0.6142 | 2.4215 | 2.143 | 1.9612 | 2.3303 | 2.9949 | 3.5686 | 0.14712 | 0.49616 | 1.0768 | 1.638 | 2.3917 | 3.2375 | 0.046874 | 0.79072 | 1.5461 | 2.3132 | 3.0921 | 3.883 | 0.68604 | 1.5013 | 2.329 | 3.1693 | Transfers | City Central 132_11kV Tx3 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 12 |  | 44 | 40 | 40 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 36 | 36 | 36 | 36 | 36 | 36 | 40 | 40 | 40 | 40 | Transfers | City Central 132_11kV Tx3 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.93825 |  | 0.99996 | 0.99977 | 0.99997 | 0.99922 | 0.99938 | 0.99947 | 0.99927 | 0.99885 | 0.99843 | 1 | 0.99997 | 0.99987 | 0.99971 | 0.9994 | 0.99896 | 1 | 0.99994 | 0.99979 | 0.99955 | 0.99923 | 0.99883 | 0.99996 | 0.99984 | 0.99963 | 0.99933 | Transfers | City Central 132_11kV Tx3 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.76392 | Diversity Factor: 0.76 | Uncompensated |  | Reactive Power |  |  | MVAr | 49.8862 | 46.49 | 44.8489 | 41.8156 | 40.6142 | 30.4215 | 30.143 | 29.9612 | 30.3303 | 30.9949 | 31.5686 | 32.1471 | 32.4962 | 33.0768 | 33.638 | 34.3917 | 35.2375 | 36.0469 | 36.7907 | 37.5461 | 38.3132 | 39.0921 | 39.883 | 40.686 | 41.5013 | 42.329 | 43.1693 | Transfers | City Central 132_11kV Tx3 | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.89958 |  | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | 0.8955 | Transfers | City Central 132_11kV Tx3 | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | Transfers | City Central 132_11kV Tx3 | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Load Detail | [33 empty] | Transfers | City Central 132_11kV Tx3 | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx4 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Transfers | City Central 132_11kV Tx4 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | Compensated |  | Load (LV side) |  |  | Amps | [27 empty] | Transfers | City Central 132_11kV Tx4 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | [27 empty] | Transfers | City Central 132_11kV Tx4 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | [27 empty] | Transfers | City Central 132_11kV Tx4 | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | [27 empty] | Transfers | City Central 132_11kV Tx4 | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | [27 empty] | Transfers | City Central 132_11kV Tx4 | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF | [30 empty] | Transfers | City Central 132_11kV Tx4 | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr | [27 empty] | Econometric |  | City Central 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9714 | 16.0143 | 23.8861 | 26.1698 | 26.4916 | 25.0003 | 25.3058 | 25.6151 | 25.9281 | 26.245 | 26.5656 | 26.8902 | 27.2187 | 27.5512 | 27.8877 | 28.2283 | 28.573 | 28.9219 | 29.275 | 29.6324 | 29.9942 | 30.3603 | 30.7309
|  |  |  | PF | [30 empty] | Econometric |  | City Central 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9714 | 16.0143 | 23.8861 | 26.1698 | 26.4916 | 25.0003 | 25.3058 | 25.6151 | 25.9281 | 26.245 | 26.5656 | 26.8902 | 27.2187 | 27.5512 | 27.8877 | 28.2283 | 28.573 | 28.9219 | 29.275 | 29.6324 | 29.9942 | 30.3603 | 30.7309
[35 empty] | Econometric |  | City Central 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9714 | 16.0143 | 23.8861 | 26.1698 | 26.4916 | 25.0003 | 25.3058 | 25.6151 | 25.9281 | 26.245 | 26.5656 | 26.8902 | 27.2187 | 27.5512 | 27.8877 | 28.2283 | 28.573 | 28.9219 | 29.275 | 29.6324 | 29.9942 | 30.3603 | 30.7309
| 0 | Compensated |  | Load (LV side) |  |  | Amps | [27 empty] | Econometric |  | City Central 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9714 | 16.0143 | 23.8861 | 26.1698 | 26.4916 | 25.0003 | 25.3058 | 25.6151 | 25.9281 | 26.245 | 26.5656 | 26.8902 | 27.2187 | 27.5512 | 27.8877 | 28.2283 | 28.573 | 28.9219 | 29.275 | 29.6324 | 29.9942 | 30.3603 | 30.7309
|  |  |  | Apparent Power |  |  | MVA | [27 empty] | Energy Efficiency |  | City Central 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.5586 | -5.2716 | -14.6355 | -21.0324 | -31.8874 | -31.317 | -15.6092 | -5.4085 | -8.3912 | -8.5592 | -15.6375 | -9.126 | -10.0199 | -4.6697 | -2.2836 | -3.6887 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576
|  |  |  | Real Power |  |  | MW | [27 empty] | Energy Efficiency |  | City Central 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.5586 | -5.2716 | -14.6355 | -21.0324 | -31.8874 | -31.317 | -15.6092 | -5.4085 | -8.3912 | -8.5592 | -15.6375 | -9.126 | -10.0199 | -4.6697 | -2.2836 | -3.6887 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576
|  |  |  | Reactive Power |  |  | MVAr | [27 empty] | Energy Efficiency |  | City Central 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.5586 | -5.2716 | -14.6355 | -21.0324 | -31.8874 | -31.317 | -15.6092 | -5.4085 | -8.3912 | -8.5592 | -15.6375 | -9.126 | -10.0199 | -4.6697 | -2.2836 | -3.6887 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576
|  |  |  | Capacitors In Service |  |  | MVAr | [27 empty] | Energy Efficiency |  | City Central 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.5586 | -5.2716 | -14.6355 | -21.0324 | -31.8874 | -31.317 | -15.6092 | -5.4085 | -8.3912 | -8.5592 | -15.6375 | -9.126 | -10.0199 | -4.6697 | -2.2836 | -3.6887 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576 | -5.9576
|  |  |  | PF | [30 empty] | Solar PV |  | City Central 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr | [27 empty] | Solar PV |  | City Central 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF | [30 empty] | Solar PV |  | City Central 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | City Central 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## City East 132_11kV
| City East 132_11kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV &units_label) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV &units_label) | [20 empty] | Spots & Transfers Summary | (11kV &units_label) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | [35 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV &units_label) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV &units_label) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.96525 | 0.93171 | 0.91012 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | -3.475% | -3.475% | -2.317% | -1.158% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | City East 132_11kV | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Diversity Factor: 0 | Uncompensated |  | Reactive Power |  |  | MVAr
PF
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## City East 33_11kV
| City East 33_11kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 2042 | 2005 | 2086 | 1786 | 1915 | 1895 | 1880 |  | 1627.652 | 1607.072 | 1559.749 | 1531.174 | 1515.812 | 1501.793 | 1505.519 | 1519.907 | 1531.412 | 1542.949 | 1547.216 | 1558.534 | 1569.153 | 1585.685 | 1604.985 | 1623.069 | 1639.007 | 1655.207 | 1671.673 | 1688.409 | 1705.416 | 1722.699 | 1740.262 | 1758.106 | 1776.237 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.8102 | 35.9923 | -10.0858 | -10.5039 | -15.3618 | -14.0188 | 3.7255 | 14.3883 | 11.5043 | 11.5379 | 4.2662 | 11.3185 | 10.6187 | 16.5319 | 19.3004 | 18.0843 | 15.9374 | 16.2002 | 16.4661 | 16.7353 | 17.0077 | 17.2833 | 17.5623 | 17.8446 | 18.1304
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 3910 |  | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910 | 3910
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 5637 |  | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 | 5637 |  |  | City East 33_11kV TxA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.352 | 6.0688 | -1.7006 | -1.7711 | -2.5902 | -2.3638 | 0.62817 | 2.4261 | 1.9398 | 1.9454 | 0.71935 | 1.9085 | 1.7905 | 2.7875 | 3.2543 | 3.0493 | 2.6873 | 2.7316 | 2.7764 | 2.8218 | 2.8677 | 2.9142 | 2.9612 | 3.0089 | 3.057
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | City East 33_11kV TxB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5373 | 4.9327 | -1.3823 | -1.4395 | -2.1053 | -1.9213 | 0.51057 | 1.9719 | 1.5767 | 1.5813 | 0.58468 | 1.5512 | 1.4553 | 2.2657 | 2.6451 | 2.4784 | 2.1842 | 2.2202 | 2.2567 | 2.2935 | 2.3309 | 2.3687 | 2.4069 | 2.4456 | 2.4847
| Transformer Loads | [35 empty] | City East 33_11kV TxC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5276 | 7.7082 | -2.16 | -2.2495 | -3.2899 | -3.0023 | 0.79786 | 3.0814 | 2.4638 | 2.471 | 0.91367 | 2.424 | 2.2741 | 3.5405 | 4.1334 | 3.873 | 3.4132 | 3.4695 | 3.5264 | 3.5841 | 3.6424 | 3.7015 | 3.7612 | 3.8217 | 3.8829
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  | City East 33_11kV TxD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9391 | 4.0986 | -1.1485 | -1.1961 | -1.7493 | -1.5964 | 0.42424 | 1.6385 | 1.31 | 1.3139 | 0.48581 | 1.2889 | 1.2092 | 1.8826 | 2.1978 | 2.0593 | 1.8149 | 1.8448 | 1.8751 | 1.9057 | 1.9367 | 1.9681 | 1.9999 | 2.032 | 2.0646
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  | City East 33_11kV TxE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0504 | 5.6483 | -1.5828 | -1.6484 | -2.4107 | -2.2 | 0.58464 | 2.258 | 1.8054 | 1.8106 | 0.6695 | 1.7762 | 1.6664 | 2.5944 | 3.0288 | 2.838 | 2.5011 | 2.5423 | 2.584 | 2.6263 | 2.669 | 2.7123 | 2.7561 | 2.8004 | 2.8452
| 0 | [35 empty] | City East 33_11kV TxF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4039 | 7.5357 | -2.1117 | -2.1992 | -3.2163 | -2.9351 | 0.78 | 3.0125 | 2.4086 | 2.4157 | 0.89322 | 2.3697 | 2.2232 | 3.4613 | 4.0409 | 3.7863 | 3.3368 | 3.3918 | 3.4475 | 3.5038 | 3.5609 | 3.6186 | 3.677 | 3.7361 | 3.7959
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | City East 33_11kV TxA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.17349 | -0.19277 | -0.19277 | -0.19277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | City East 33_11kV TxB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.14101 | -0.15668 | -0.15668 | -0.15668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | City East 33_11kV TxC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22036 | -0.24485 | -0.24485 | -0.24485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | City East 33_11kV TxD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.11717 | -0.13019 | -0.13019 | -0.13019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Broad based demand management |  | City East 33_11kV TxE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.16147 | -0.17941 | -0.17941 | -0.17941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | City East 33_11kV TxF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.21543 | -0.23936 | -0.23936 | -0.23936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Spot |  | City East 33_11kV TxA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6097 | 7.0143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Spot |  | City East 33_11kV TxB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3723 | 5.7012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Spot |  | City East 33_11kV TxC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3952 | 8.9092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Spot |  | City East 33_11kV TxD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4639 | 4.7372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Spot |  | City East 33_11kV TxE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1517 | 6.5283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Spot |  | City East 33_11kV TxF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2073 | 8.7097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | City East 33_11kV TxA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.04 | 2.0947 | 3.1652 | 3.2721 | 3.3119 | 3.2895 | 3.3293 | 3.3695 | 3.4103 | 3.4515 | 3.4932 | 3.5355 | 3.5782 | 3.6215 | 3.6653 | 3.7096 | 3.7544 | 3.7998 | 3.8457 | 3.8922 | 3.9392 | 3.9868 | 4.035
| Diversity Factor: 0 | [33 empty] | Econometric |  | City East 33_11kV TxB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84535 | 1.7025 | 2.5727 | 2.6596 | 2.6919 | 2.6737 | 2.706 | 2.7387 | 2.7719 | 2.8054 | 2.8393 | 2.8736 | 2.9084 | 2.9435 | 2.9791 | 3.0151 | 3.0516 | 3.0885 | 3.1258 | 3.1636 | 3.2018 | 3.2405 | 3.2796
[35 empty] | Econometric |  | City East 33_11kV TxC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.321 | 2.6605 | 4.0203 | 4.1561 | 4.2066 | 4.1781 | 4.2287 | 4.2798 | 4.3315 | 4.3839 | 4.4369 | 4.4906 | 4.5449 | 4.5998 | 4.6554 | 4.7117 | 4.7686 | 4.8263 | 4.8846 | 4.9436 | 5.0034 | 5.0639 | 5.125
[35 empty] | Econometric |  | City East 33_11kV TxD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7024 | 1.4147 | 2.1377 | 2.2098 | 2.2367 | 2.2216 | 2.2484 | 2.2756 | 2.3032 | 2.331 | 2.3592 | 2.3877 | 2.4166 | 2.4458 | 2.4754 | 2.5053 | 2.5356 | 2.5662 | 2.5972 | 2.6286 | 2.6604 | 2.6925 | 2.7251
| 0 | [33 empty] | Econometric |  | City East 33_11kV TxE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96798 | 1.9495 | 2.9459 | 3.0454 | 3.0824 | 3.0616 | 3.0986 | 3.1361 | 3.174 | 3.2124 | 3.2512 | 3.2905 | 3.3303 | 3.3705 | 3.4113 | 3.4525 | 3.4943 | 3.5365 | 3.5792 | 3.6225 | 3.6663 | 3.7106 | 3.7554
| Diversity Factor: 0 | [33 empty] | Econometric |  | City East 33_11kV TxF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2914 | 2.601 | 3.9303 | 4.063 | 4.1124 | 4.0846 | 4.134 | 4.184 | 4.2346 | 4.2858 | 4.3376 | 4.39 | 4.4431 | 4.4968 | 4.5512 | 4.6062 | 4.6619 | 4.7182 | 4.7752 | 4.833 | 4.8914 | 4.9505 | 5.0103
[35 empty] | Energy Efficiency |  | City East 33_11kV TxA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2577 | -0.94554 | -2.5672 | -3.673 | -5.5627 | -5.4431 | -2.6837 | -0.86344 | -1.3895 | -1.4241 | -2.6909 | -1.5431 | -1.7028 | -0.74797 | -0.32392 | -0.57221 | -0.97799 | -0.97799 | -0.97799 | -0.97799 | -0.97799 | -0.97799 | -0.97799 | -0.97799 | -0.97799
[35 empty] | Energy Efficiency |  | City East 33_11kV TxB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8351 | -0.76853 | -2.0866 | -2.9854 | -4.5213 | -4.4241 | -2.1813 | -0.7018 | -1.1294 | -1.1575 | -2.1872 | -1.2542 | -1.384 | -0.60795 | -0.26328 | -0.46509 | -0.7949 | -0.7949 | -0.7949 | -0.7949 | -0.7949 | -0.7949 | -0.7949 | -0.7949 | -0.7949
| 0 | [33 empty] | Energy Efficiency |  | City East 33_11kV TxC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8676 | -1.201 | -3.2607 | -4.6652 | -7.0654 | -6.9135 | -3.4087 | -1.0967 | -1.7648 | -1.8088 | -3.4179 | -1.9599 | -2.1628 | -0.95003 | -0.41142 | -0.72679 | -1.2422 | -1.2422 | -1.2422 | -1.2422 | -1.2422 | -1.2422 | -1.2422 | -1.2422 | -1.2422
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | City East 33_11kV TxD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5248 | -0.63858 | -1.7338 | -2.4806 | -3.7568 | -3.676 | -1.8125 | -0.58313 | -0.9384 | -0.96177 | -1.8173 | -1.0421 | -1.15 | -0.50515 | -0.21876 | -0.38644 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049
[35 empty] | Energy Efficiency |  | City East 33_11kV TxE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1013 | -0.88002 | -2.3893 | -3.4185 | -5.1772 | -5.066 | -2.4977 | -0.80361 | -1.2932 | -1.3254 | -2.5045 | -1.4361 | -1.5848 | -0.69615 | -0.30147 | -0.53256 | -0.91022 | -0.91022 | -0.91022 | -0.91022 | -0.91022 | -0.91022 | -0.91022 | -0.91022 | -0.91022
[35 empty] | Energy Efficiency |  | City East 33_11kV TxF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8034 | -1.1741 | -3.1877 | -4.5608 | -6.9072 | -6.7587 | -3.3324 | -1.0721 | -1.7253 | -1.7683 | -3.3413 | -1.916 | -2.1144 | -0.92876 | -0.40221 | -0.71051 | -1.2144 | -1.2144 | -1.2144 | -1.2144 | -1.2144 | -1.2144 | -1.2144 | -1.2144 | -1.2144
| 0 | [33 empty] | Solar PV |  | City East 33_11kV TxA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Solar PV |  | City East 33_11kV TxB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | City East 33_11kV TxC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | City East 33_11kV TxD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Solar PV |  | City East 33_11kV TxE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Solar PV |  | City East 33_11kV TxF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | -10.12% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0.96525 | 0.93171 | 0.91012 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | -3.475% | -3.475% | -2.317% | -1.158% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | City East 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1880 | 1659.5224 | 1627.652 | 1607.072 | 1559.749 | 1531.174 | 1515.812 | 1501.793 | 1505.519 | 1519.907 | 1531.412 | 1542.949 | 1547.216 | 1558.534 | 1569.153 | 1585.685 | 1604.985 | 1623.069 | 1639.007 | 1655.207 | 1671.673 | 1688.409 | 1705.416 | 1722.699 | 1740.262 | 1758.106 | 1776.237
|  |  |  | Apparent Power |  |  | MVA | 35.8188 |  | 31.0109 | 30.6188 | 29.7172 | 29.1728 | 28.8801 | 28.613 | 28.684 | 28.9581 | 29.1773 | 29.3971 | 29.4784 | 29.6941 | 29.8964 | 30.2114 | 30.5791 | 30.9236 | 31.2273 | 31.5359 | 31.8497 | 32.1685 | 32.4926 | 32.8218 | 33.1564 | 33.4964 | 33.8419
|  |  |  | Real Power |  |  | MW | 34.7442 | 30.6696 | 30.0806 | 29.7003 | 28.8257 | 28.2976 | 28.0137 | 27.7546 | 27.8235 | 28.0894 | 28.302 | 28.5152 | 28.5941 | 28.8032 | 28.9995 | 29.305 | 29.6617 | 29.9959 | 30.2905 | 30.5899 | 30.8942 | 31.2035 | 31.5178 | 31.8372 | 32.1617 | 32.4915 | 32.8266
|  |  |  | Reactive Power |  |  | MVAr | 8.7077 |  | 7.5389 | 7.4436 | 7.2244 | 7.092 | 7.0209 | 6.956 | 6.9732 | 7.0399 | 7.0931 | 7.1466 | 7.1664 | 7.2188 | 7.268 | 7.3445 | 7.4339 | 7.5177 | 7.5915 | 7.6665 | 7.7428 | 7.8203 | 7.8991 | 7.9792 | 8.0605 | 8.1431 | 8.2271
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.97 |  | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
0.64415 | Diversity Factor: 0.64 | Uncompensated |  | Reactive Power |  |  | MVAr | 8.7077 | 7.6865 | 7.5389 | 7.4436 | 7.2244 | 7.092 | 7.0209 | 6.956 | 6.9732 | 7.0399 | 7.0931 | 7.1466 | 7.1664 | 7.2188 | 7.268 | 7.3445 | 7.4339 | 7.5177 | 7.5915 | 7.6665 | 7.7428 | 7.8203 | 7.8991 | 7.9792 | 8.0605 | 8.1431 | 8.2271
|  |  |  | PF |  |  |  | 0.97 |  | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## City North 132_11kV
| City North 132_11kV | [16 empty] | 2014 | WINTER
[6 empty] | Zone commissioned |  | 2010-04-28
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total |  |  |  | 744 | 1206 | 1918 | 2577 |  | 2391.489 | 3507.478 | 3410.536 | 3357.961 | 3338.043 | 3323.339 | 3342.647 | 3380.706 | 3413.184 | 3445.919 | 3464.528 | 3497.297 | 3528.842 | 3572.188 | 3621.169 | 3667.898 | 3710.569 | 3753.924 | 3797.972 | 3842.721 | 3888.18 | 3934.358 | 3981.262 | 4028.902 | 4077.286 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.3797 | 1272.0308 | -15.7181 | -13.2108 | -20.2663 | -14.9644 | 19.6493 | 38.7188 | 33.0291 | 33.2803 | 18.9139 | 33.2979 | 32.0453 | 44.0181 | 49.7206 | 47.4154 | 43.2825 | 43.9623 | 44.6503 | 45.3467 | 46.0515 | 46.7649 | 47.4868 | 48.2176 | 48.9572
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 5876 |  | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876 | 5876
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 11214 |  | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 | 11214 |  |  | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3818 | 134.1805 | -1.658 | -1.3935 | -2.1378 | -1.5785 | 2.0727 | 4.0843 | 3.4841 | 3.5106 | 1.9951 | 3.5124 | 3.3803 | 4.6433 | 5.2448 | 5.0016 | 4.5657 | 4.6374 | 4.7099 | 4.7834 | 4.8578 | 4.933 | 5.0092 | 5.0862 | 5.1643
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.6786 | 364.9708 | -4.5098 | -3.7905 | -5.8148 | -4.2936 | 5.6378 | 11.1092 | 9.4767 | 9.5488 | 5.4268 | 9.5538 | 9.1944 | 12.6297 | 14.2658 | 13.6044 | 12.4186 | 12.6137 | 12.8111 | 13.0109 | 13.2131 | 13.4178 | 13.6249 | 13.8346 | 14.0468
| Transformer Loads | [35 empty] | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.6786 | 364.9708 | -4.5098 | -3.7905 | -5.8148 | -4.2936 | 5.6378 | 11.1092 | 9.4767 | 9.5488 | 5.4268 | 9.5538 | 9.1944 | 12.6297 | 14.2658 | 13.6044 | 12.4186 | 12.6137 | 12.8111 | 13.0109 | 13.2131 | 13.4178 | 13.6249 | 13.8346 | 14.0468
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.1644 | 381.0725 | -4.7088 | -3.9577 | -6.0714 | -4.483 | 5.8865 | 11.5993 | 9.8948 | 9.9701 | 5.6662 | 9.9753 | 9.6001 | 13.1869 | 14.8952 | 14.2046 | 12.9665 | 13.1701 | 13.3763 | 13.5849 | 13.796 | 14.0097 | 14.226 | 14.4449 | 14.6665
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4764 | 26.8361 | -0.33161 | -0.27871 | -0.42756 | -0.31571 | 0.41454 | 0.81685 | 0.69682 | 0.70212 | 0.39903 | 0.70249 | 0.67606 | 0.92865 | 1.049 | 1.0003 | 0.91313 | 0.92747 | 0.94199 | 0.95668 | 0.97155 | 0.9866 | 1.0018 | 1.0172 | 1.0329
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.078359 | -0.087065 | -0.087065 | -0.087065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.21314 | -0.23682 | -0.23682 | -0.23682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.21314 | -0.23682 | -0.23682 | -0.23682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.22254 | -0.24726 | -0.24726 | -0.24726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Broad based demand management |  | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.015672 | -0.017413 | -0.017413 | -0.017413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx1 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7975 | 4.8734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx1 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx1 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx1 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7848 | 13.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx1 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75949 | 0.97468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx2 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7975 | 4.8734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx2 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx2 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx2 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7848 | 13.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx2 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75949 | 0.97468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx3 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7975 | 4.8734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx3 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx3 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx3 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7848 | 13.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx3 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75949 | 0.97468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx4 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7975 | 4.8734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx4 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx4 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3291 | 13.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City Central 132_11kV Tx4 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7848 | 13.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City Central 132_11kV Tx4 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75949 | 0.97468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx1 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.2329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx1 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx1 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx1 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx1 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx2 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx2 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx2 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Commissioning Transfers | Dalley St 132_11kV Tx2 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | ROG Justification | [24 empty] | Commissioning Transfers | Dalley St 132_11kV Tx2 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | -3.132% |  | 7 year ROG ok | [24 empty] | Commissioning Transfers | Dalley St 132_11kV Tx3 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.4096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 year ROG ok
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx3 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx3 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Commissioning Transfers | Dalley St 132_11kV Tx3 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.96525 | 0.93171 | 0.91012 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | -3.475% | -3.475% | -2.317% | -1.158% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Commissioning Transfers | Dalley St 132_11kV Tx3 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx4 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Substation Load Detail | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx4 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx4 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Commissioning Transfers | Dalley St 132_11kV Tx4 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | City North 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 2577 | 2380.7668 | 2391.489 | 3507.478 | 3410.536 | 3357.961 | 3338.043 | 3323.339 | 3342.647 | 3380.706 | 3413.184 | 3445.919 | 3464.528 | 3497.297 | 3528.842 | 3572.188 | 3621.169 | 3667.898 | 3710.569 | 3753.924 | 3797.972 | 3842.721 | 3888.18 | 3934.358 | 3981.262 | 4028.902 | 4077.286 | Commissioning Transfers | Dalley St 132_11kV Tx4 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 49.0984 |  | 45.564 | 66.8264 | 64.9794 | 63.9778 | 63.5983 | 63.3181 | 63.686 | 64.4111 | 65.0299 | 65.6536 | 66.0081 | 66.6325 | 67.2335 | 68.0593 | 68.9925 | 69.8828 | 70.6958 | 71.5219 | 72.3611 | 73.2137 | 74.0798 | 74.9596 | 75.8532 | 76.7609 | 77.6827 | Spot |  | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 48.8713 | 45.1499 | 45.5438 | 66.8173 | 64.9752 | 63.9754 | 63.5965 | 63.3167 | 63.6841 | 64.408 | 65.0255 | 65.6478 | 66.0014 | 66.6239 | 67.2231 | 68.046 | 68.9756 | 69.8621 | 70.6714 | 71.4933 | 72.3281 | 73.1759 | 74.0369 | 74.9112 | 75.7991 | 76.7006 | 77.6159 | Spot |  | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 4.7173 |  | 1.3561 | 1.1045 | 0.74322 | 0.54714 | 0.47283 | 0.41796 | 0.49001 | 0.63198 | 0.75309 | 0.87513 | 0.94448 | 1.0666 | 1.1841 | 1.3455 | 1.5278 | 1.7017 | 1.8604 | 2.0216 | 2.1853 | 2.3516 | 2.5204 | 2.6919 | 2.866 | 3.0429 | 3.2224 | Spot |  | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 4 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Spot |  | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.99537 |  | 0.99956 | 0.99986 | 0.99993 | 0.99996 | 0.99997 | 0.99998 | 0.99997 | 0.99995 | 0.99993 | 0.99991 | 0.9999 | 0.99987 | 0.99984 | 0.9998 | 0.99975 | 0.9997 | 0.99965 | 0.9996 | 0.99954 | 0.99948 | 0.99942 | 0.99935 | 0.99928 | 0.99921 | 0.99914 | Spot |  | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.73729 | Diversity Factor: 0.74 | Uncompensated |  | Reactive Power |  |  | MVAr | 4.7173 | 4.3581 | 5.3561 | 13.1045 | 12.7432 | 12.5471 | 12.4728 | 12.4179 | 12.49 | 12.632 | 12.7531 | 12.8751 | 12.9445 | 13.0666 | 13.1841 | 13.3455 | 13.5278 | 13.7017 | 13.8604 | 14.0216 | 14.1853 | 14.3516 | 14.5204 | 14.6919 | 14.866 | 15.0428 | 15.2224 | Econometric |  | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6777 | 3.3708 | 5.0391 | 5.4668 | 5.534 | 5.2679 | 5.3322 | 5.3973 | 5.4632 | 5.53 | 5.5975 | 5.6658 | 5.735 | 5.805 | 5.8758 | 5.9475 | 6.0201 | 6.0936 | 6.1679 | 6.2431 | 6.3193 | 6.3964 | 6.4744
|  |  |  | PF |  |  |  | 0.99537 |  | 0.99316 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | 0.9813 | Econometric |  | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5633 | 9.1685 | 13.7063 | 14.8697 | 15.0524 | 14.3287 | 14.5037 | 14.6808 | 14.86 | 15.0415 | 15.2251 | 15.411 | 15.5991 | 15.7895 | 15.9822 | 16.1773 | 16.3747 | 16.5745 | 16.7767 | 16.9814 | 17.1885 | 17.3982 | 17.6104
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | Econometric |  | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5633 | 9.1685 | 13.7063 | 14.8697 | 15.0524 | 14.3287 | 14.5037 | 14.6808 | 14.86 | 15.0415 | 15.2251 | 15.411 | 15.5991 | 15.7895 | 15.9822 | 16.1773 | 16.3747 | 16.5745 | 16.7767 | 16.9814 | 17.1885 | 17.3982 | 17.6104
| Transformer Load Detail | [33 empty] | Econometric |  | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7646 | 9.573 | 14.311 | 15.5257 | 15.7165 | 14.9608 | 15.1435 | 15.3285 | 15.5156 | 15.7051 | 15.8968 | 16.0909 | 16.2873 | 16.4861 | 16.6873 | 16.891 | 17.0971 | 17.3057 | 17.5168 | 17.7305 | 17.9468 | 18.1657 | 18.3873
[35 empty] | Econometric |  | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33554 | 0.67416 | 1.0078 | 1.0934 | 1.1068 | 1.0536 | 1.0664 | 1.0795 | 1.0926 | 1.106 | 1.1195 | 1.1332 | 1.147 | 1.161 | 1.1752 | 1.1895 | 1.204 | 1.2187 | 1.2336 | 1.2486 | 1.2639 | 1.2793 | 1.2949
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Energy Efficiency |  | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.808 | -1.1782 | -3.2573 | -4.6773 | -7.0898 | -6.9583 | -3.4613 | -1.1836 | -1.8482 | -1.8868 | -3.4681 | -2.0175 | -2.2172 | -1.0225 | -0.49018 | -0.80334 | -1.3101 | -1.3101 | -1.3101 | -1.3101 | -1.3101 | -1.3101 | -1.3101 | -1.3101 | -1.3101
| 0 | Compensated |  | Load (LV side) |  |  | Amps | [27 empty] | Energy Efficiency |  | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.6379 | -3.2047 | -8.86 | -12.7222 | -19.2843 | -18.9265 | -9.4146 | -3.2195 | -5.027 | -5.132 | -9.4333 | -5.4876 | -6.0307 | -2.7813 | -1.3333 | -2.1851 | -3.5636 | -3.5636 | -3.5636 | -3.5636 | -3.5636 | -3.5636 | -3.5636 | -3.5636 | -3.5636
|  |  |  | Apparent Power |  |  | MVA | [27 empty] | Energy Efficiency |  | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.6379 | -3.2047 | -8.86 | -12.7222 | -19.2843 | -18.9265 | -9.4146 | -3.2195 | -5.027 | -5.132 | -9.4333 | -5.4876 | -6.0307 | -2.7813 | -1.3333 | -2.1851 | -3.5636 | -3.5636 | -3.5636 | -3.5636 | -3.5636 | -3.5636 | -3.5636 | -3.5636 | -3.5636
|  |  |  | Real Power |  |  | MW | [27 empty] | Energy Efficiency |  | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.9748 | -3.3461 | -9.2509 | -13.2834 | -20.1351 | -19.7615 | -9.83 | -3.3615 | -5.2487 | -5.3584 | -9.8494 | -5.7297 | -6.2967 | -2.904 | -1.3921 | -2.2815 | -3.7208 | -3.7208 | -3.7208 | -3.7208 | -3.7208 | -3.7208 | -3.7208 | -3.7208 | -3.7208
|  |  |  | Reactive Power |  |  | MVAr | [27 empty] | Energy Efficiency |  | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.56161 | -0.23564 | -0.65147 | -0.93545 | -1.418 | -1.3917 | -0.69225 | -0.23673 | -0.36963 | -0.37735 | -0.69362 | -0.4035 | -0.44343 | -0.20451 | -0.098035 | -0.16067 | -0.26203 | -0.26203 | -0.26203 | -0.26203 | -0.26203 | -0.26203 | -0.26203 | -0.26203 | -0.26203
|  |  |  | Capacitors In Service |  |  | MVAr | [27 empty] | Solar PV |  | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF | [30 empty] | Solar PV |  | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr | [27 empty] | Solar PV |  | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF | [30 empty] | Solar PV |  | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## City North 33_11kV
| City North 33_11kV | [16 empty] | 2014 | WINTER
[6 empty] | Zone decommissioned |  | 2012-06-30
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 1683 | 1575 | 1516 | 1643 | 1056.931 | 743 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | City North 33_11kV TxC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | City North 33_11kV TxD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | City North 33_11kV TxE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | City North 33_11kV TxF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | 0% |  | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | City North 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| #VALUE! | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## City South 132_11kV
| City South 132_11kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 7579 | 6646 | 6703 | 6568 | 5890 | 5750 | 5924 |  | 5078.17 | 4978.283 | 4502.366 | 4042.429 | 3180.243 | 3174.89 | 3195.972 | 3230.366 | 3260.557 | 3291.083 | 3310.798 | 3341.641 | 3366.189 | 3404.488 | 3447.246 | 3488.462 | 3526.756 | 3565.733 | 3605.4 | 3645.768 | 3686.843 | 3728.634 | 3765.605 | 3807.861 | 3850.868 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1126 | 86.9996 | -403.9599 | -465.3652 | -964.6456 | -5.9124 | 23.2719 | 37.8937 | 33.193 | 33.4974 | 21.6003 | 33.7413 | 32.7747 | 42.8446 | 47.6905 | 45.837 | 42.4735 | 43.1234 | 43.7811 | 44.4469 | 45.1207 | 45.8027 | 46.493 | 47.1916 | 47.8987
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 9072 |  | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072 | 9072
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 10496 |  | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 | 10496 |  |  | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3305 | 28.6526 | -133.0411 | -153.2645 | -317.6986 | -1.9472 | 7.6644 | 12.48 | 10.9318 | 11.0321 | 7.1139 | 11.1125 | 10.7941 | 14.1106 | 15.7065 | 15.0961 | 13.9883 | 14.2024 | 14.419 | 14.6382 | 14.8602 | 15.0848 | 15.3121 | 15.5422 | 15.7751
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.322 | 28.5793 | -132.7005 | -152.8721 | -316.8853 | -1.9422 | 7.6448 | 12.4481 | 10.9039 | 11.0039 | 7.0957 | 11.084 | 10.7665 | 14.0744 | 15.6663 | 15.0574 | 13.9525 | 14.166 | 14.3821 | 14.6008 | 14.8221 | 15.0462 | 15.2729 | 15.5024 | 15.7347
| Transformer Loads | [35 empty] | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13813 | 1.1884 | -5.5178 | -6.3566 | -13.1764 | -0.080759 | 0.31788 | 0.5176 | 0.45339 | 0.45755 | 0.29505 | 0.46089 | 0.44768 | 0.58523 | 0.65142 | 0.6261 | 0.58016 | 0.58904 | 0.59802 | 0.60712 | 0.61632 | 0.62564 | 0.63506 | 0.64461 | 0.65427
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.322 | 28.5793 | -132.7005 | -152.8721 | -316.8853 | -1.9422 | 7.6448 | 12.4481 | 10.9039 | 11.0039 | 7.0957 | 11.084 | 10.7665 | 14.0744 | 15.6663 | 15.0574 | 13.9525 | 14.166 | 14.3821 | 14.6008 | 14.8221 | 15.0462 | 15.2729 | 15.5024 | 15.7347
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.21069 | -0.2341 | -0.2341 | -0.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.21015 | -0.2335 | -0.2335 | -0.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0087383 | -0.0097092 | -0.0097092 | -0.0097092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.21015 | -0.2335 | -0.2335 | -0.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx1 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6169 | 118.8926 | 78.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx1 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6169 | 118.8926 | 78.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx1 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6169 | 118.8926 | 78.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx1 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6169 | 118.8926 | 78.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx2 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx2 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx2 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx2 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx3 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3113 | 4.931 | 3.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx3 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3113 | 4.931 | 3.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx3 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3113 | 4.931 | 3.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx3 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3113 | 4.931 | 3.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx4 | Belmore Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | City South 132_11kV Tx4 | Belmore Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx4 | Belmore Park 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | City South 132_11kV Tx4 | Belmore Park 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5359 | 118.5882 | 78.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Spot |  | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.9162 | 34.7785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Spot |  | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.8704 | 34.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Spot |  | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74307 | 1.4424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Spot |  | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.8704 | 34.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Transfers | City Central 132_11kV Tx1 | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Transfers | City Central 132_11kV Tx1 | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx1 | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx1 | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Transfers | City Central 132_11kV Tx2 | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Transfers | City Central 132_11kV Tx2 | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx2 | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx2 | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx3 | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Transfers | City Central 132_11kV Tx3 | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | ROG Justification | [24 empty] | Transfers | City Central 132_11kV Tx3 | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | -9.033% |  | 7 year ROG ok | [24 empty] | Transfers | City Central 132_11kV Tx3 | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 year ROG ok
[35 empty] | Transfers | City Central 132_11kV Tx4 | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Transfers | City Central 132_11kV Tx4 | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Transfers | City Central 132_11kV Tx4 | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.96525 | 0.93171 | 0.91012 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | -3.475% | -3.475% | -2.317% | -1.158% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Transfers | City Central 132_11kV Tx4 | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.027 | 14.1063 | 14.9857 | 16.6221 | 16.8265 | 15.7077 | 15.8997 | 16.0941 | 16.2908 | 16.4899 | 16.6914 | 16.8954 | 17.1018 | 17.3107 | 17.5222 | 17.7363 | 17.9529 | 18.1722 | 18.3941 | 18.6187 | 18.846 | 19.0761 | 19.309
| Substation Load Detail | [33 empty] | Econometric |  | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0039 | 14.0701 | 14.9473 | 16.5796 | 16.7835 | 15.6675 | 15.859 | 16.0529 | 16.2491 | 16.4477 | 16.6487 | 16.8521 | 17.058 | 17.2664 | 17.4774 | 17.6909 | 17.9069 | 18.1256 | 18.347 | 18.571 | 18.7978 | 19.0273 | 19.2595
[35 empty] | Econometric |  | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37439 | 0.58505 | 0.62153 | 0.6894 | 0.69787 | 0.65147 | 0.65944 | 0.6675 | 0.67565 | 0.68391 | 0.69227 | 0.70073 | 0.70929 | 0.71796 | 0.72673 | 0.73561 | 0.74459 | 0.75368 | 0.76289 | 0.7722 | 0.78163 | 0.79117 | 0.80083
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Econometric |  | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0039 | 14.0701 | 14.9473 | 16.5796 | 16.7835 | 15.6675 | 15.859 | 16.0529 | 16.2491 | 16.4477 | 16.6487 | 16.8521 | 17.058 | 17.2664 | 17.4774 | 17.6909 | 17.9069 | 18.1256 | 18.347 | 18.571 | 18.7978 | 19.0273 | 19.2595
1 | City South 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 5924 | 5526.3499 | 5078.17 | 4978.283 | 4502.366 | 4042.429 | 3180.243 | 3174.89 | 3195.972 | 3230.366 | 3260.557 | 3291.083 | 3310.798 | 3341.641 | 3366.189 | 3404.488 | 3447.246 | 3488.462 | 3526.756 | 3565.733 | 3605.4 | 3645.768 | 3686.843 | 3728.634 | 3765.605 | 3807.861 | 3850.868 | Energy Efficiency |  | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14.5857 | -6.1259 | -15.3899 | -17.22 | -18.6529 | -18.3352 | -9.1621 | -3.2277 | -4.9679 | -5.062 | -9.1769 | -5.3774 | -5.8973 | -2.7848 | -1.3953 | -2.2147 | -3.5339 | -3.5339 | -3.5339 | -3.5339 | -3.5339 | -3.5339 | -3.5339 | -3.5339 | -3.5339
|  |  |  | Apparent Power |  |  | MVA | 112.8674 |  | 96.7521 | 94.849 | 85.7816 | 77.0186 | 60.5918 | 60.4898 | 60.8915 | 61.5467 | 62.122 | 62.7036 | 63.0792 | 63.6668 | 64.1345 | 64.8642 | 65.6789 | 66.4641 | 67.1937 | 67.9363 | 68.6921 | 69.4612 | 70.2438 | 71.04 | 71.7444 | 72.5495 | 73.3689 | Energy Efficiency |  | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14.5484 | -6.1102 | -15.3505 | -17.1759 | -18.6051 | -18.2883 | -9.1387 | -3.2194 | -4.9551 | -5.049 | -9.1534 | -5.3637 | -5.8822 | -2.7777 | -1.3917 | -2.209 | -3.5249 | -3.5249 | -3.5249 | -3.5249 | -3.5249 | -3.5249 | -3.5249 | -3.5249 | -3.5249
|  |  |  | Real Power |  |  | MW | 107.224 | 100.0266 | 96.7225 | 94.8382 | 85.7805 | 76.9622 | 60.5635 | 60.463 | 60.8586 | 61.5028 | 62.0671 | 62.6365 | 63.0037 | 63.5773 | 64.1345 | 64.8628 | 65.6736 | 66.4528 | 67.1748 | 67.9079 | 68.6521 | 69.4077 | 70.1748 | 70.9534 | 71.7438 | 72.546 | 73.3603 | Energy Efficiency |  | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.60494 | -0.25407 | -0.63829 | -0.71419 | -0.77362 | -0.76045 | -0.38 | -0.13387 | -0.20604 | -0.20994 | -0.38061 | -0.22303 | -0.24459 | -0.1155 | -0.057869 | -0.091854 | -0.14657 | -0.14657 | -0.14657 | -0.14657 | -0.14657 | -0.14657 | -0.14657 | -0.14657 | -0.14657
|  |  |  | Reactive Power |  |  | MVAr | 35.2428 |  | 2.3945 | 1.4361 | 0.42924 | 2.9483 | 1.8494 | 1.7986 | 1.9988 | 2.3248 | 2.6103 | 2.8985 | 3.0843 | 3.3746 | 0.056572 | 0.42517 | 0.83545 | 1.2298 | 1.5952 | 1.9662 | 2.3428 | 2.7252 | 3.1134 | 3.5074 | 0.3074 | 0.71339 | 1.1255 | Energy Efficiency |  | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14.5484 | -6.1102 | -15.3505 | -17.1759 | -18.6051 | -18.2883 | -9.1387 | -3.2194 | -4.9551 | -5.049 | -9.1534 | -5.3637 | -5.8822 | -2.7777 | -1.3917 | -2.209 | -3.5249 | -3.5249 | -3.5249 | -3.5249 | -3.5249 | -3.5249 | -3.5249 | -3.5249 | -3.5249
|  |  |  | Capacitors In Service |  |  | MVAr | 18 |  | 46.8 | 46.8 | 43.2 | 36 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 36 | 36 | 36 | Solar PV |  | City South 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.95 |  | 0.99969 | 0.99989 | 0.99999 | 0.99927 | 0.99953 | 0.99956 | 0.99946 | 0.99929 | 0.99912 | 0.99893 | 0.9988 | 0.99859 | 1 | 0.99998 | 0.99992 | 0.99983 | 0.99972 | 0.99958 | 0.99942 | 0.99923 | 0.99902 | 0.99878 | 0.99999 | 0.99995 | 0.99988 | Solar PV |  | City South 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.77532 | Diversity Factor: 0.78 | Uncompensated |  | Reactive Power |  |  | MVAr | 53.2428 | 50.8771 | 49.1945 | 48.2361 | 43.6292 | 38.9483 | 30.6494 | 30.5985 | 30.7988 | 31.1248 | 31.4103 | 31.6985 | 31.8843 | 32.1746 | 32.4566 | 32.8252 | 33.2354 | 33.6298 | 33.9952 | 34.3662 | 34.7428 | 35.1252 | 35.5134 | 35.9074 | 36.3074 | 36.7134 | 37.1255 | Solar PV |  | City South 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.89566 |  | 0.89133 | 0.89133 | 0.89133 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | 0.89225 | Solar PV |  | City South 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Dalley St 132_11kV
| Dalley St 132_11kV | [16 empty] | 2014 | WINTER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| Total | 6839 | 6638 | 6650 | 6641 | 6080 | 5900 | 5363 |  | 4453.142 | 3266.871 | 3163.726 | 3100.428 | 3059.649 | 3024.558 | 3043.029 | 3094.466 | 3136.758 | 3179.156 | 3198.367 | 3240.27 | 3280.102 | 3339.107 | 3407.231 | 3470.543 | 3527.672 | 3585.773 | 3644.744 | 3704.66 | 3765.531 | 3827.369 | 3890.316 | 3954.359 | 4019.509 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.8523 | -1085.3164 | -28.8276 | -28.0361 | -42.9372 | -36.8882 | 19.4229 | 54.1335 | 44.444 | 44.6485 | 20.1836 | 44.126 | 41.8399 | 61.8829 | 71.3155 | 67.2789 | 60.1128 | 61.0808 | 62.0604 | 63.0518 | 64.0552 | 65.0706 | 66.0983 | 67.1383 | 68.1909
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 10236 |  | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236 | 10236
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 13542 |  | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 | 13542 |  |  | Dalley St 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.8259 | -272.3951 | -7.2352 | -7.0366 | -10.7765 | -9.2583 | 4.8748 | 13.5865 | 11.1547 | 11.206 | 5.0657 | 11.0748 | 10.5011 | 15.5315 | 17.8989 | 16.8858 | 15.0873 | 15.3302 | 15.5761 | 15.8249 | 16.0767 | 16.3316 | 16.5895 | 16.8505 | 17.1147
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Dalley St 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.2591 | -276.4887 | -7.344 | -7.1423 | -10.9384 | -9.3974 | 4.9481 | 13.7907 | 11.3223 | 11.3744 | 5.1418 | 11.2413 | 10.6589 | 15.7649 | 18.1679 | 17.1396 | 15.314 | 15.5606 | 15.8101 | 16.0627 | 16.3183 | 16.577 | 16.8388 | 17.1038 | 17.3719
| Transformer Loads | [35 empty] | Dalley St 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.0064 | -274.1008 | -7.2805 | -7.0806 | -10.8439 | -9.3163 | 4.9053 | 13.6716 | 11.2245 | 11.2761 | 5.0974 | 11.1442 | 10.5668 | 15.6288 | 18.011 | 16.9915 | 15.1817 | 15.4262 | 15.6736 | 15.924 | 16.1774 | 16.4338 | 16.6934 | 16.956 | 17.2219
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | Dalley St 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7609 | -262.3317 | -6.9679 | -6.7766 | -10.3783 | -8.9162 | 4.6947 | 13.0846 | 10.7426 | 10.792 | 4.8786 | 10.6657 | 10.1131 | 14.9577 | 17.2377 | 16.262 | 14.5299 | 14.7638 | 15.0006 | 15.2402 | 15.4828 | 15.7282 | 15.9766 | 16.228 | 16.4824
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | [33 empty] | Broad based demand management |  | Dalley St 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Dalley St 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Dalley St 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Dalley St 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx1 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.2329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx1 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx1 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx1 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx1 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx2 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx2 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx2 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx2 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx2 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx3 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.4096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx3 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx3 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx3 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx3 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx4 | City North 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx4 | City North 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Commissioning Transfers | Dalley St 132_11kV Tx4 | City North 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx4 | City North 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Commissioning Transfers | Dalley St 132_11kV Tx4 | City North 132_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Spot |  | Dalley St 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.1572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Spot |  | Dalley St 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.7606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Spot |  | Dalley St 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.4086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Spot |  | Dalley St 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.6736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Dalley St 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7108 | 11.5021 | 17.3059 | 18.2404 | 18.4621 | 18.025 | 18.2431 | 18.4638 | 18.6872 | 18.9133 | 19.1421 | 19.3737 | 19.6081 | 19.8453 | 20.0853 | 20.3283 | 20.5741 | 20.823 | 21.0748 | 21.3296 | 21.5876 | 21.8486 | 22.1128
| Diversity Factor: 0 | [33 empty] | Econometric |  | Dalley St 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7966 | 11.675 | 17.5659 | 18.5145 | 18.7396 | 18.2958 | 18.5172 | 18.7413 | 18.9681 | 19.1976 | 19.4298 | 19.6649 | 19.9028 | 20.1435 | 20.3872 | 20.6338 | 20.8833 | 21.1359 | 21.3915 | 21.6502 | 21.912 | 22.177 | 22.4451
[35 empty] | Econometric |  | Dalley St 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7466 | 11.5742 | 17.4142 | 18.3546 | 18.5777 | 18.1378 | 18.3573 | 18.5794 | 18.8042 | 19.0318 | 19.262 | 19.495 | 19.7309 | 19.9696 | 20.2111 | 20.4556 | 20.703 | 20.9534 | 21.2068 | 21.4632 | 21.7228 | 21.9854 | 22.2512
[35 empty] | Econometric |  | Dalley St 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4998 | 11.0772 | 16.6665 | 17.5665 | 17.78 | 17.359 | 17.5691 | 17.7817 | 17.9968 | 18.2146 | 18.435 | 18.658 | 18.8837 | 19.1121 | 19.3433 | 19.5773 | 19.814 | 20.0537 | 20.2962 | 20.5416 | 20.79 | 21.0414 | 21.2958
[35 empty] | Energy Efficiency |  | Dalley St 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.3313 | -4.7477 | -12.946 | -18.5387 | -28.0823 | -27.4987 | -13.5873 | -4.4384 | -7.0884 | -7.2578 | -13.6215 | -7.8385 | -8.6411 | -3.8422 | -1.7092 | -2.9595 | -4.9981 | -4.9981 | -4.9981 | -4.9981 | -4.9981 | -4.9981 | -4.9981 | -4.9981 | -4.9981
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Energy Efficiency |  | Dalley St 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.5016 | -4.819 | -13.1406 | -18.8173 | -28.5044 | -27.9119 | -13.7915 | -4.5051 | -7.1949 | -7.3669 | -13.8262 | -7.9563 | -8.7709 | -3.8999 | -1.7349 | -3.004 | -5.0732 | -5.0732 | -5.0732 | -5.0732 | -5.0732 | -5.0732 | -5.0732 | -5.0732 | -5.0732
[10 empty] | ROG Justification | [24 empty] | Energy Efficiency |  | Dalley St 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.4022 | -4.7774 | -13.0271 | -18.6548 | -28.2582 | -27.6708 | -13.6724 | -4.4662 | -7.1328 | -7.3033 | -13.7068 | -7.8876 | -8.6952 | -3.8663 | -1.7199 | -2.978 | -5.0294 | -5.0294 | -5.0294 | -5.0294 | -5.0294 | -5.0294 | -5.0294 | -5.0294 | -5.0294
| Actual loads for season 2013 have been weather corrected by the following: | [6 empty] | -13.47% |  | 7 year ROG ok | [24 empty] | Energy Efficiency |  | Dalley St 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.9127 | -4.5723 | -12.4677 | -17.8538 | -27.0448 | -26.4827 | -13.0853 | -4.2744 | -6.8265 | -6.9897 | -13.1183 | -7.5489 | -8.3218 | -3.7003 | -1.646 | -2.8501 | -4.8134 | -4.8134 | -4.8134 | -4.8134 | -4.8134 | -4.8134 | -4.8134 | -4.8134 | -4.8134 | 7 year ROG ok
[35 empty] | Solar PV |  | Dalley St 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Dalley St 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Solar PV |  | Dalley St 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.96525 | 0.93171 | 0.91012 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | 0.89958 | -3.475% | -3.475% | -2.317% | -1.158% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Solar PV |  | Dalley St 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Substation Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
1 | Dalley St 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 5363 | 4674.2252 | 4453.142 | 3266.871 | 3163.726 | 3100.428 | 3059.649 | 3024.558 | 3043.029 | 3094.466 | 3136.758 | 3179.156 | 3198.367 | 3240.27 | 3280.102 | 3339.107 | 3407.231 | 3470.543 | 3527.672 | 3585.773 | 3644.744 | 3704.66 | 3765.531 | 3827.369 | 3890.316 | 3954.359 | 4019.509
|  |  |  | Apparent Power |  |  | MVA | 102.1789 |  | 84.8438 | 62.2422 | 60.2771 | 59.0711 | 58.2942 | 57.6256 | 57.9775 | 58.9575 | 59.7633 | 60.571 | 60.9371 | 61.7354 | 62.4943 | 63.6185 | 64.9165 | 66.1227 | 67.2112 | 68.3182 | 69.4417 | 70.5833 | 71.743 | 72.9212 | 74.1205 | 75.3407 | 76.5819
|  |  |  | Real Power |  |  | MW | 98.3727 | 85.7386 | 84.8418 | 62.2411 | 60.2769 | 59.0709 | 58.2935 | 57.6255 | 57.9772 | 58.9574 | 59.7622 | 60.5706 | 60.9361 | 61.7351 | 62.4927 | 63.6132 | 64.9045 | 66.1227 | 67.2112 | 68.3172 | 69.4409 | 70.5826 | 71.7424 | 72.9207 | 74.1175 | 75.3332 | 76.5679
|  |  |  | Reactive Power |  |  | MVAr | 27.6285 |  | 0.57393 | 0.37533 | 0.13234 | 0.13754 | 0.28303 | 0.064372 | 0.1795 | 0.10038 | 0.36382 | 0.22848 | 0.34812 | 0.20968 | 0.45769 | 0.8245 | 1.2472 | 0.046022 | 0.002343 | 0.3644 | 0.33227 | 0.30601 | 0.2857 | 0.27141 | 0.66321 | 1.0612 | 1.4654
|  |  |  | Capacitors In Service |  |  | MVAr | 4 |  | 27.2 | 20 | 19.6 | 19.2 | 18.8 | 18.8 | 18.8 | 19.2 | 19.2 | 19.6 | 19.6 | 20 | 20 | 20 | 20 | 21.6 | 22 | 22 | 22.4 | 22.8 | 23.2 | 23.6 | 23.6 | 23.6 | 23.6
|  |  |  | PF |  |  |  | 0.96275 |  | 0.99998 | 0.99998 | 1 | 1 | 0.99999 | 1 | 0.99999 | 1 | 0.99998 | 0.99999 | 0.99998 | 0.99999 | 0.99997 | 0.99992 | 0.99982 | 1 | 1 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99996 | 0.9999 | 0.99982
0.73858 | Diversity Factor: 0.74 | Uncompensated |  | Reactive Power |  |  | MVAr | 31.6285 | 28.0801 | 27.7739 | 20.3753 | 19.7323 | 19.3375 | 19.083 | 18.8644 | 18.9795 | 19.3004 | 19.5638 | 19.8285 | 19.9481 | 20.2097 | 20.4577 | 20.8245 | 21.2472 | 21.646 | 22.0023 | 22.3644 | 22.7323 | 23.106 | 23.4857 | 23.8714 | 24.2632 | 24.6612 | 25.0654
|  |  |  | PF |  |  |  | 0.952 |  | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037 | 0.95037
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 2013 |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF