## Inclusions and Exclusions
Sydney Forecast Inclusions and Exclusions
Date Printed |  | 08JUL14:11:21:24
| Description | Value
Season |  | Summer | Summer
Either Summer or Winter
Year |  | 2015 | 2015
Year that the forecast starts
POE |  | 50% | 0.5
10%, 50%, 90%
Spots and Transfers |  | Y | Y
Are Spots and Transfers Included?
BBDM Spots |  | Y | Y
Is BBDM included?
Spots Coefficient |  | 55% | 0.55
Scaling factor applied to spot loads in the future
Aligned ROGs |  | Capped | Capped
Have ROGs been aligned to econometric forecast?
Committed Projects |  | Y | Y
Are Committed Projects Included?
Major Customers Scaling Factor |  | 100% | 1
Scaling factor applied to major customer connections in the future
Future Transfers |  | Y | Y
Are future transfers included?
Future Spots |  | 4 | 4
Future spots are cleared from the following forecast year

## Berowra 132_11kV
| Berowra 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 978 | 1098 | 1223 | 1383 | 915 | 1275 | 1003 |  | 1004.493 | 953.4984 | 923.8623 | 912.7389 | 910.2925 | 913.9196 | 924.867 | 937.4078 | 948.6029 | 960.4843 | 971.6656 | 985.4588 | 999.4673 | 1014.834 | 1031.149 | 1047.405 | 1063.694 | 1080.376 | 1097.457 | 1114.943 | 1132.841 | 1151.155 | 1169.892 | 1189.058 | 1208.659 |  |  | Total | 0 | 0 | 186.9 | -0.048812 | -60.0766 | -0.03674 | 17.8273 | 24.0937 | -0.77057 | 2.1472 | 4.2744 | -2.4464 | 3.627 | 10.9474 | 12.5408 | 11.195 | 11.8814 | 11.1813 | 13.7932 | 14.0085 | 15.3674 | 16.3152 | 16.2554 | 16.2888 | 16.6822 | 17.0813 | 17.4863 | 17.8971 | 18.314 | 18.737 | 19.1661 | 19.6015
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2222 |  | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222 | 2222
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 4349 |  | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 | 4349 |  |  | Berowra 132_11kV Tx1 | 53 | 0 | -91.1 | -0.025283 | -60.0397 | -0.01903 | -0.089442 | -0.62484 | -0.39913 | 1.1122 | 2.214 | -1.2672 | 1.8787 | 5.6704 | 6.4957 | 5.7986 | 6.1541 | 5.7915 | 7.1444 | 7.2559 | 7.9598 | 8.4507 | 8.4197 | 8.437 | 8.6408 | 8.8475 | 9.0573 | 9.2701 | 9.486 | 9.7051 | 9.9273 | 10.1529
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Berowra 132_11kV Tx2 | -53 | 0 | 278 | -0.023529 | -0.036938 | -0.01771 | 17.9168 | 24.7185 | -0.37144 | 1.035 | 2.0604 | -1.1793 | 1.7484 | 5.2771 | 6.0451 | 5.3964 | 5.7273 | 5.3898 | 6.6488 | 6.7526 | 7.4077 | 7.8645 | 7.8357 | 7.8518 | 8.0414 | 8.2338 | 8.429 | 8.6271 | 8.828 | 9.0319 | 9.2387 | 9.4486
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Berowra 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.018247 | -0.036494 | -0.054741 | -0.32845 | -3.1019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Berowra 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.016981 | -0.033963 | -0.050944 | -0.30567 | -2.8867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Berowra 132_11kV Tx1 | Galston 132_11kV Tx1 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Berowra 132_11kV Tx1 | Galston 132_11kV Tx2 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6277. 11KV Feeder Connections to the New Switchgear at Berowra Zone Substation. | Berowra 132_11kV Tx1 | Berowra 132_11kV Tx2 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6277. 11KV Feeder Connections to the New Switchgear at Berowra Zone Substation. | Berowra 132_11kV Tx2 | Berowra 132_11kV Tx1 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6400. South Berowra Zone Development - 2008. | Berowra 132_11kV Tx1 | Berowra 132_11kV Tx2 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6400. South Berowra Zone Development - 2008. | Hornsby 132_11kV Tx3 | Berowra 132_11kV Tx2 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2008108. Establishment of 2x Kiosks - S.35941 Beaumont Gundah No 1 and S.35942 Beaumont Gundah No 2, 22 Beaumont Rd, Mt Ku-ring-gai |  | Berowra 132_11kV Tx1 | 0 | 0 | 63.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2012128. Establishment of S.62060 WOODLAND MUNDOWI No.2, Woodland Way, Mount Kuring-gai |  | Berowra 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Berowra 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3256 | 7.6882 | 9.8428 | 10.5157 | 11.1282 | 10.9693 | 10.7978 | 10.9791 | 11.1631 | 11.3497 | 11.5392 | 11.7314 | 11.9264 | 12.1243 | 12.3251 | 12.5289 | 12.7356 | 12.9454 | 13.1582 | 13.3741 | 13.5932 | 13.8155 | 14.041
[35 empty] | Econometric |  | Berowra 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0255 | 7.1549 | 9.16 | 9.7862 | 10.3563 | 10.2084 | 10.0488 | 10.2175 | 10.3887 | 10.5625 | 10.7388 | 10.9177 | 11.0992 | 11.2833 | 11.4702 | 11.6598 | 11.8522 | 12.0474 | 12.2455 | 12.4464 | 12.6503 | 12.8572 | 13.067
| 0 | [33 empty] | Energy Efficiency |  | Berowra 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.57009 | -0.3217 | -3.1124 | -5.0951 | -7.9538 | -8.5798 | -5.3979 | -4.4157 | -4.9403 | -4.7799 | -5.3176 | -4.1514 | -4.2294 | -3.7177 | -3.4218 | -3.6507 | -3.8342 | -3.8342 | -3.8342 | -3.8342 | -3.8342 | -3.8342 | -3.8342 | -3.8342 | -3.8342
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Berowra 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.53055 | -0.29939 | -2.8966 | -4.7417 | -7.4021 | -7.9847 | -5.0235 | -4.1094 | -4.5976 | -4.4484 | -4.9488 | -3.8635 | -3.936 | -3.4598 | -3.1845 | -3.3975 | -3.5682 | -3.5682 | -3.5682 | -3.5682 | -3.5682 | -3.5682 | -3.5682 | -3.5682 | -3.5682
[35 empty] | Solar PV |  | Berowra 132_11kV Tx1 | 0 | 0 | 0 | -0.025283 | -0.039692 | -0.01903 | -0.089442 | -0.036495 | -0.040935 | -0.046231 | -0.050728 | -0.054291 | -0.057196 | -0.059882 | -0.057908 | -0.058828 | -0.045012 | -0.053916 | -0.053916 | -0.053916 | -0.053916 | -0.053916 | -0.053916 | -0.053916 | -0.053916 | -0.053916 | -0.053916 | -0.053916 | -0.053916 | -0.053916 | -0.053916 | -0.053916
[35 empty] | Solar PV |  | Berowra 132_11kV Tx2 | 0 | 0 | 0 | -0.023529 | -0.036938 | -0.01771 | -0.083238 | -0.033964 | -0.038095 | -0.043025 | -0.047209 | -0.050526 | -0.053228 | -0.055729 | -0.053891 | -0.054747 | -0.04189 | -0.050176 | -0.050176 | -0.050176 | -0.050176 | -0.050176 | -0.050176 | -0.050176 | -0.050176 | -0.050176 | -0.050176 | -0.050176 | -0.050176 | -0.050176 | -0.050176 | -0.050176
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | -0.6922% |  | Rog Capped +/-5% | [59 empty] | Rog Capped +/-5%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Berowra 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1003 | 1032 | 1004.493 | 953.4984 | 923.8623 | 912.7389 | 910.2925 | 913.9196 | 924.867 | 937.4078 | 948.6029 | 960.4843 | 971.6656 | 985.4588 | 999.4673 | 1014.834 | 1031.149 | 1047.405 | 1063.694 | 1080.376 | 1097.457 | 1114.943 | 1132.841 | 1151.155 | 1169.892 | 1189.058 | 1208.659
|  |  |  | Apparent Power |  |  | MVA | 19.1097 |  | 19.1382 | 18.1666 | 17.6019 | 17.39 | 17.3434 | 17.4125 | 17.6211 | 17.86 | 18.0733 | 18.2997 | 18.5127 | 18.7755 | 19.0424 | 19.3352 | 19.646 | 19.9557 | 20.2661 | 20.5839 | 20.9094 | 21.2425 | 21.5835 | 21.9324 | 22.2894 | 22.6546 | 23.0281
|  |  |  | Real Power |  |  | MW | 17.8735 | 18.3902 | 17.9001 | 16.9913 | 16.4632 | 16.265 | 16.2214 | 16.286 | 16.4811 | 16.7046 | 16.9041 | 17.1158 | 17.3151 | 17.5609 | 17.8105 | 18.0844 | 18.3751 | 18.6648 | 18.955 | 19.2523 | 19.5567 | 19.8683 | 20.1872 | 20.5136 | 20.8475 | 21.189 | 21.5383
|  |  |  | Reactive Power |  |  | MVAr | 6.7617 |  | 6.7718 | 6.428 | 6.2282 | 6.1532 | 6.1367 | 6.1612 | 6.235 | 6.3195 | 6.395 | 6.4751 | 6.5505 | 6.6434 | 6.7379 | 6.8415 | 6.9515 | 7.0611 | 7.1709 | 7.2833 | 7.3985 | 7.5164 | 7.637 | 7.7605 | 7.8868 | 8.016 | 8.1481
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.93531 |  | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531
0.84094 | Diversity Factor: 0.84 | Uncompensated |  | Reactive Power |  |  | MVAr | 6.7617 | 6.9572 | 6.7718 | 6.428 | 6.2282 | 6.1532 | 6.1367 | 6.1612 | 6.235 | 6.3195 | 6.395 | 6.4751 | 6.5505 | 6.6434 | 6.7379 | 6.8415 | 6.9515 | 7.0611 | 7.1709 | 7.2833 | 7.3985 | 7.5164 | 7.637 | 7.7605 | 7.8868 | 8.016 | 8.1481
|  |  |  | PF |  |  |  | 0.93531 |  | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531 | 0.93531
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Galston 132_11kV
| Galston 132_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone commissioned |  | 2011-05-05
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  |  | 435 | 498 | 495 |  | 526.1126 | 503.7902 | 490.3004 | 484.4181 | 482.0884 | 482.233 | 485.6232 | 489.9017 | 493.6512 | 497.841 | 501.5946 | 506.5627 | 511.6187 | 517.3069 | 523.4298 | 529.5117 | 535.5936 | 541.8474 | 548.2757 | 554.8811 | 561.6662 | 568.6336 | 575.7862 | 583.1265 | 590.6575 |  |  | Total | 0 | 0 | 0 | 0 | 510.196 | -0.44403 | 0 | -0.94704 | -0.77721 | 0.26421 | 0.81064 | -2.3297 | 0.14456 | 3.3902 | 4.2785 | 3.7495 | 4.1897 | 3.7536 | 4.9681 | 5.056 | 5.6883 | 6.1228 | 6.0819 | 6.0819 | 6.2538 | 6.4283 | 6.6054 | 6.7851 | 6.9675 | 7.1525 | 7.3403 | 7.5309
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2000 |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 4000 |  | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 |  |  | Galston 132_11kV Tx1 | 0 | 0 | 0 | 0 | 244.0805 | -0.22632 | 0 | -0.4827 | -0.39614 | 0.13467 | 0.41318 | -1.1874 | 0.073681 | 1.7279 | 2.1807 | 1.9111 | 2.1355 | 1.9132 | 2.5322 | 2.577 | 2.8992 | 3.1208 | 3.0999 | 3.0999 | 3.1875 | 3.2764 | 3.3667 | 3.4583 | 3.5512 | 3.6456 | 3.7413 | 3.8384
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Galston 132_11kV Tx2 | 0 | 0 | 0 | 0 | 266.1155 | -0.21771 | 0 | -0.46434 | -0.38108 | 0.12955 | 0.39747 | -1.1423 | 0.070879 | 1.6622 | 2.0978 | 1.8384 | 2.0543 | 1.8404 | 2.4359 | 2.479 | 2.789 | 3.0021 | 2.982 | 2.982 | 3.0663 | 3.1519 | 3.2387 | 3.3268 | 3.4162 | 3.507 | 3.599 | 3.6925
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Galston 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.012152 | -0.024303 | -0.036455 | -0.21873 | -1.3439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Galston 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.01169 | -0.023379 | -0.035069 | -0.21041 | -1.2928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Berowra 132_11kV Tx1 | Galston 132_11kV Tx1 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Berowra 132_11kV Tx1 | Galston 132_11kV Tx2 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Hornsby 132_11kV Tx3 | Galston 132_11kV Tx1 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Hornsby 132_11kV Tx3 | Galston 132_11kV Tx2 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Pennant Hills 132_11kV Tx1 | Galston 132_11kV Tx1 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Pennant Hills 132_11kV Tx1 | Galston 132_11kV Tx2 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Galston 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8527 | 3.2475 | 4.1053 | 4.3221 | 4.5231 | 4.5054 | 4.4832 | 4.561 | 4.64 | 4.7202 | 4.8016 | 4.8842 | 4.968 | 5.0531 | 5.1395 | 5.2271 | 5.316 | 5.4063 | 5.4979 | 5.5908 | 5.6852 | 5.7809 | 5.878
| Diversity Factor: 0 | [33 empty] | Econometric |  | Galston 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7822 | 3.124 | 3.9493 | 4.1577 | 4.3511 | 4.3341 | 4.3127 | 4.3876 | 4.4636 | 4.5407 | 4.619 | 4.6985 | 4.7791 | 4.861 | 4.944 | 5.0283 | 5.1139 | 5.2007 | 5.2888 | 5.3783 | 5.469 | 5.5611 | 5.6545
[35 empty] | Energy Efficiency |  | Galston 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.27558 | -0.15315 | -1.4346 | -2.3446 | -3.6588 | -3.9428 | -2.4753 | -2.0153 | -2.2578 | -2.1851 | -2.4388 | -1.9 | -1.9366 | -1.6969 | -1.5592 | -1.6652 | -1.7516 | -1.7516 | -1.7516 | -1.7516 | -1.7516 | -1.7516 | -1.7516 | -1.7516 | -1.7516
[35 empty] | Energy Efficiency |  | Galston 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.2651 | -0.14733 | -1.38 | -2.2554 | -3.5197 | -3.7929 | -2.3812 | -1.9387 | -2.172 | -2.102 | -2.3461 | -1.8277 | -1.8629 | -1.6324 | -1.5 | -1.6019 | -1.685 | -1.685 | -1.685 | -1.685 | -1.685 | -1.685 | -1.685 | -1.685 | -1.685
| 0 | [33 empty] | Solar PV |  | Galston 132_11kV Tx1 | 0 | 0 | 0 | 0 | -0.91946 | -0.22632 | 0 | -0.19496 | -0.21868 | -0.24698 | -0.271 | -0.29003 | -0.30555 | -0.3199 | -0.30935 | -0.31427 | -0.24046 | -0.28803 | -0.28803 | -0.28803 | -0.28803 | -0.28803 | -0.28803 | -0.28803 | -0.28803 | -0.28803 | -0.28803 | -0.28803 | -0.28803 | -0.28803 | -0.28803 | -0.28803
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Galston 132_11kV Tx2 | 0 | 0 | 0 | 0 | -0.8845 | -0.21771 | 0 | -0.18755 | -0.21037 | -0.23759 | -0.26069 | -0.27901 | -0.29393 | -0.30774 | -0.29759 | -0.30232 | -0.23132 | -0.27708 | -0.27708 | -0.27708 | -0.27708 | -0.27708 | -0.27708 | -0.27708 | -0.27708 | -0.27708 | -0.27708 | -0.27708 | -0.27708 | -0.27708 | -0.27708 | -0.27708
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 11.02% |  | Weighted ROG calc | [59 empty] | Weighted ROG calc
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95905 | 0.91978 | 0.89467 | 0.88245 | 0.88245 | 0.88245 | 0.88245 | 0.88245 | 0.88245 | 0.88245 | -4.095% | -4.095% | -2.73% | -1.365% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Galston 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 495 | 549.5653 | 526.1126 | 503.7902 | 490.3004 | 484.4181 | 482.0884 | 482.233 | 485.6232 | 489.9017 | 493.6512 | 497.841 | 501.5946 | 506.5627 | 511.6187 | 517.3069 | 523.4298 | 529.5117 | 535.5936 | 541.8474 | 548.2757 | 554.8811 | 561.6662 | 568.6336 | 575.7862 | 583.1265 | 590.6575
|  |  |  | Apparent Power |  |  | MVA | 9.431 |  | 10.0238 | 9.5985 | 9.3415 | 9.2294 | 9.185 | 9.1878 | 9.2524 | 9.3339 | 9.4053 | 9.4851 | 9.5567 | 9.6513 | 9.7476 | 9.856 | 9.9727 | 10.0885 | 10.2044 | 10.3236 | 10.446 | 10.5719 | 10.7012 | 10.8339 | 10.9702 | 11.11 | 11.2535
|  |  |  | Real Power |  |  | MW | 8.7537 | 9.7186 | 9.3039 | 8.9091 | 8.6706 | 8.5666 | 8.5254 | 8.5279 | 8.5879 | 8.6635 | 8.7298 | 8.8039 | 8.8703 | 8.9582 | 9.0476 | 9.1482 | 9.2565 | 9.364 | 9.4716 | 9.5822 | 9.6958 | 9.8126 | 9.9326 | 10.0558 | 10.1823 | 10.3121 | 10.4453
|  |  |  | Reactive Power |  |  | MVAr | 3.5096 |  | 3.7301 | 3.5719 | 3.4762 | 3.4345 | 3.418 | 3.419 | 3.4431 | 3.4734 | 3.5 | 3.5297 | 3.5563 | 3.5915 | 3.6274 | 3.6677 | 3.7111 | 3.7542 | 3.7974 | 3.8417 | 3.8873 | 3.9341 | 3.9822 | 4.0316 | 4.0823 | 4.1344 | 4.1878
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.92818 |  | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818
0.82148 | Diversity Factor: 0.82 | Uncompensated |  | Reactive Power |  |  | MVAr | 3.5096 | 3.8964 | 3.7301 | 3.5719 | 3.4762 | 3.4345 | 3.418 | 3.419 | 3.4431 | 3.4734 | 3.5 | 3.5297 | 3.5563 | 3.5915 | 3.6274 | 3.6677 | 3.7111 | 3.7542 | 3.7974 | 3.8417 | 3.8873 | 3.9341 | 3.9822 | 4.0316 | 4.0823 | 4.1344 | 4.1878
|  |  |  | PF |  |  |  | 0.92818 |  | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818 | 0.92818
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Hornsby 132_11kV
| Hornsby 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 3773 | 4127 | 4071 | 4224 | 3156 | 3692 | 3180 |  | 3215.578 | 3098.387 | 3028.643 | 3004.216 | 3001.595 | 3008.727 | 3043.259 | 3087.196 | 3125.863 | 3167.37 | 3202.932 | 3248.817 | 3295.021 | 3347.798 | 3404.521 | 3460.613 | 3515.839 | 3572.336 | 3630.123 | 3689.217 | 3749.637 | 3811.402 | 3874.531 | 3939.042 | 4004.955 |  |  | Total | 225 | 0 | -123 | -8.4981 | -244.5919 | 9.5583 | -1.5211 | 75.5211 | -7.5854 | 0.76389 | 10.2272 | -2.6735 | 7.2749 | 35.2155 | 44.7838 | 39.3914 | 42.2652 | 36.1953 | 46.6807 | 46.983 | 53.6392 | 57.6197 | 56.9481 | 56.0427 | 57.3059 | 58.587 | 59.8862 | 61.2036 | 62.5395 | 63.8943 | 65.268 | 66.6611
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 6000 |  | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 9000 |  | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 |  |  | Hornsby 132_11kV Tx1 | 225 | 1272 | 0 | -3.1904 | -2.0994 | -14.4798 | -0.57105 | -87.685 | -2.8478 | 0.28679 | 3.8396 | -1.0037 | 2.7312 | 13.221 | 16.8132 | 14.7888 | 15.8677 | 13.5888 | 17.5254 | 17.6389 | 20.1378 | 21.6322 | 21.3801 | 21.0401 | 21.5144 | 21.9954 | 22.4831 | 22.9777 | 23.4793 | 23.9879 | 24.5036 | 25.0266
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Hornsby 132_11kV Tx2 | 0 | -519 | 0 | -3.3582 | -2.2098 | 11.9423 | 262.3989 | 71.0687 | -2.9976 | 0.30187 | 4.0415 | -1.0565 | 2.8748 | 13.9163 | 17.6974 | 15.5665 | 16.7021 | 14.3034 | 18.447 | 18.5665 | 21.1968 | 22.7698 | 22.5044 | 22.1466 | 22.6458 | 23.1521 | 23.6655 | 24.1861 | 24.714 | 25.2493 | 25.7922 | 26.3427
| Transformer Loads | [35 empty] | Hornsby 132_11kV Tx3 | 0 | -753 | -123 | -1.9494 | -240.2828 | 12.0958 | -263.3489 | 92.1374 | -1.7401 | 0.17523 | 2.3461 | -0.61329 | 1.6688 | 8.0783 | 10.2732 | 9.0362 | 9.6954 | 8.303 | 10.7083 | 10.7777 | 12.3046 | 13.2177 | 13.0636 | 12.8559 | 13.1457 | 13.4396 | 13.7376 | 14.0398 | 14.3463 | 14.657 | 14.9722 | 15.2917
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Hornsby 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Hornsby 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Hornsby 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6128. Northern Turramurra Minor Zone Development (Load Transfer from Turramurra Pa13 & Pa18 to Hornsby Pa15) | Turramurra 33_11kV Tx2 | Hornsby 132_11kV Tx1 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6129. Hornsby Zone - Populating TX1 Switchgear Group. | Hornsby 132_11kV Tx2 | Hornsby 132_11kV Tx1 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6129. Hornsby Zone - Populating TX1 Switchgear Group. | Hornsby 132_11kV Tx2 | Hornsby 132_11kV Tx3 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6129. Hornsby Zone - Populating TX1 Switchgear Group. | Hornsby 132_11kV Tx3 | Hornsby 132_11kV Tx1 | 0 | 562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6154. Hornsby South Zone Development | Hornsby 132_11kV Tx2 | Hornsby 132_11kV Tx1 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6154. Hornsby South Zone Development | Hornsby 132_11kV Tx3 | Hornsby 132_11kV Tx1 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Hornsby 132_11kV Tx3 | Galston 132_11kV Tx1 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Hornsby 132_11kV Tx3 | Galston 132_11kV Tx2 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6400. South Berowra Zone Development - 2008. | Hornsby 132_11kV Tx3 | Berowra 132_11kV Tx2 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6832. Form New Interconnector for New Customer Substation S.48783 Neringah Warwilla No.2. | Hornsby 132_11kV Tx1 | Hornsby 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6947. Form New 11kV Feeder from S.847 Hornsby Zone | Hornsby 132_11kV Tx3 | Hornsby 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011244. Establishment of S.49774 Rosamond Watson, Manor Rd, Hornsby |  | Hornsby 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011538. Establishment of 4 x Kiosks, S.50749 Kelray Salisbury No 2, S.50750 Kelray Salisbury No 3, S.50751 Kelray Salisbury No 4 and S.50752 Kelray Salisbury No 5, 2 Kelray Place, Asquith - new load for National Boradbank Networ |  | Hornsby 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2011584. Establish new substation S.61022 Hornsby Aquatic, Pacific Hwy, Hornsby | Hornsby 132_11kV Tx1 | Hornsby 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2012313. Hornsby Hospital Redevelopment - Stage 1- Establishment of S.62458 Derby Burdett, Derby Road, Hornsby |  | Hornsby 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012313. Hornsby Hospital Redevelopment - Stage 1- Establishment of S.62458 Derby Burdett, Derby Road, Hornsby | Hornsby 132_11kV Tx1 | Hornsby 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Hornsby 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3786 | 19.0459 | 25.423 | 26.688 | 28.1282 | 27.7424 | 27.3299 | 27.7538 | 28.1837 | 28.6197 | 29.0618 | 29.5102 | 29.965 | 30.4262 | 30.8939 | 31.3681 | 31.8491 | 32.3368 | 32.8314 | 33.333 | 33.8416 | 34.3573 | 34.8803
| 0 | [33 empty] | Econometric |  | Hornsby 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9243 | 20.0474 | 26.76 | 28.0914 | 29.6074 | 29.2013 | 28.7671 | 29.2133 | 29.6658 | 30.1247 | 30.5901 | 31.0621 | 31.5408 | 32.0262 | 32.5185 | 33.0177 | 33.524 | 34.0373 | 34.558 | 35.0859 | 35.6212 | 36.1641 | 36.7146
| Diversity Factor: 0 | [33 empty] | Econometric |  | Hornsby 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3415 | 11.6374 | 15.5339 | 16.3068 | 17.1868 | 16.9511 | 16.6991 | 16.9581 | 17.2207 | 17.4871 | 17.7573 | 18.0313 | 18.3092 | 18.5909 | 18.8767 | 19.1665 | 19.4604 | 19.7584 | 20.0606 | 20.3671 | 20.6778 | 20.993 | 21.3125
[35 empty] | Energy Efficiency |  | Hornsby 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6465 | -1.683 | -8.7763 | -13.7628 | -21.2895 | -22.3293 | -13.2033 | -9.2814 | -10.8672 | -10.6053 | -13.0607 | -9.5602 | -9.8888 | -7.8383 | -6.7986 | -7.5119 | -8.3196 | -8.3196 | -8.3196 | -8.3196 | -8.3196 | -8.3196 | -8.3196 | -8.3196 | -8.3196
[35 empty] | Energy Efficiency |  | Hornsby 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8383 | -1.7715 | -9.2378 | -14.4866 | -22.409 | -23.5035 | -13.8976 | -9.7695 | -11.4387 | -11.163 | -13.7475 | -10.0629 | -10.4088 | -8.2505 | -7.1561 | -7.907 | -8.7571 | -8.7571 | -8.7571 | -8.7571 | -8.7571 | -8.7571 | -8.7571 | -8.7571 | -8.7571
| 0 | [33 empty] | Energy Efficiency |  | Hornsby 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2281 | -1.0284 | -5.3625 | -8.4093 | -13.0083 | -13.6436 | -8.0674 | -5.6711 | -6.6401 | -6.48 | -7.9803 | -5.8414 | -6.0422 | -4.7893 | -4.1541 | -4.5899 | -5.0834 | -5.0834 | -5.0834 | -5.0834 | -5.0834 | -5.0834 | -5.0834 | -5.0834 | -5.0834
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Hornsby 132_11kV Tx1 | 0 | 0 | 0 | -3.1904 | -2.0994 | -1.4798 | -0.57105 | -1.0385 | -1.1648 | -1.3155 | -1.4434 | -1.5448 | -1.6275 | -1.7039 | -1.6477 | -1.6739 | -1.2808 | -1.5341 | -1.5341 | -1.5341 | -1.5341 | -1.5341 | -1.5341 | -1.5341 | -1.5341 | -1.5341 | -1.5341 | -1.5341 | -1.5341 | -1.5341 | -1.5341 | -1.5341
[35 empty] | Solar PV |  | Hornsby 132_11kV Tx2 | 0 | 0 | 0 | -3.3582 | -2.2098 | -1.5577 | -0.60108 | -1.0931 | -1.226 | -1.3847 | -1.5193 | -1.6261 | -1.7131 | -1.7935 | -1.7344 | -1.7619 | -1.3481 | -1.6148 | -1.6148 | -1.6148 | -1.6148 | -1.6148 | -1.6148 | -1.6148 | -1.6148 | -1.6148 | -1.6148 | -1.6148 | -1.6148 | -1.6148 | -1.6148 | -1.6148
[35 empty] | Solar PV |  | Hornsby 132_11kV Tx3 | 0 | 0 | 0 | -1.9494 | -1.2828 | -0.90421 | -0.34892 | -0.63451 | -0.7117 | -0.80379 | -0.88197 | -0.94392 | -0.99441 | -1.0411 | -1.0068 | -1.0228 | -0.78259 | -0.93739 | -0.93739 | -0.93739 | -0.93739 | -0.93739 | -0.93739 | -0.93739 | -0.93739 | -0.93739 | -0.93739 | -0.93739 | -0.93739 | -0.93739 | -0.93739 | -0.93739
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 6.078% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.96687 | 0.93484 | 0.9142 | 0.9041 | 0.9041 | 0.9041 | 0.9041 | 0.9041 | 0.9041 | 0.9041 | -3.313% | -3.313% | -2.208% | -1.104% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Hornsby 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 3180 | 3317 | 3215.578 | 3098.387 | 3028.643 | 3004.216 | 3001.595 | 3008.727 | 3043.259 | 3087.196 | 3125.863 | 3167.37 | 3202.932 | 3248.817 | 3295.021 | 3347.798 | 3404.521 | 3460.613 | 3515.839 | 3572.336 | 3630.123 | 3689.217 | 3749.637 | 3811.402 | 3874.531 | 3939.042 | 4004.955
|  |  |  | Apparent Power |  |  | MVA | 60.5871 |  | 61.265 | 59.0322 | 57.7034 | 57.238 | 57.1881 | 57.324 | 57.9819 | 58.819 | 59.5557 | 60.3465 | 61.0241 | 61.8983 | 62.7786 | 63.7841 | 64.8649 | 65.9335 | 66.9857 | 68.0622 | 69.1631 | 70.289 | 71.4402 | 72.617 | 73.8197 | 75.0488 | 76.3046
|  |  |  | Real Power |  |  | MW | 58.6561 | 61.1831 | 60.5092 | 58.3682 | 57.0925 | 56.6455 | 56.5975 | 56.728 | 57.36 | 58.1636 | 58.8704 | 59.6288 | 60.2783 | 61.116 | 61.959 | 62.9216 | 63.9555 | 64.9774 | 65.983 | 67.0113 | 68.0626 | 69.1372 | 70.2355 | 71.3577 | 72.5042 | 73.6754 | 74.8716
|  |  |  | Reactive Power |  |  | MVAr | 15.1744 |  | 9.5934 | 8.8294 | 8.3741 | 8.2146 | 8.1975 | 8.2441 | 8.4696 | 8.7563 | 9.0086 | 9.2792 | 9.511 | 9.8099 | 10.1108 | 10.4543 | 10.8232 | 11.1879 | 11.5468 | 11.9138 | 12.2889 | 12.6724 | 13.0643 | 13.4648 | 13.874 | 14.2919 | 14.7188
|  |  |  | Capacitors In Service |  |  | MVAr | 6 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
|  |  |  | PF |  |  |  | 0.96813 |  | 0.98766 | 0.98875 | 0.98941 | 0.98965 | 0.98967 | 0.9896 | 0.98927 | 0.98886 | 0.98849 | 0.98811 | 0.98778 | 0.98736 | 0.98694 | 0.98648 | 0.98598 | 0.9855 | 0.98503 | 0.98456 | 0.98409 | 0.98361 | 0.98314 | 0.98266 | 0.98218 | 0.9817 | 0.98122
0.94813 | Diversity Factor: 0.95 | Uncompensated |  | Reactive Power |  |  | MVAr | 21.1744 | 21.8281 | 21.5934 | 20.8294 | 20.3741 | 20.2146 | 20.1975 | 20.2441 | 20.4696 | 20.7563 | 21.0086 | 21.2792 | 21.511 | 21.8099 | 22.1108 | 22.4543 | 22.8233 | 23.1879 | 23.5468 | 23.9138 | 24.2889 | 24.6724 | 25.0643 | 25.4648 | 25.874 | 26.2919 | 26.7188
|  |  |  | PF |  |  |  | 0.94059 |  | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183 | 0.94183
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Pennant Hills 132_11kV
| Pennant Hills 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 4228 | 4969 | 4627 | 4790 | 3218 | 4221 | 3579 |  | 3703.391 | 3527.544 | 3423.143 | 3380.333 | 3368.77 | 3376.725 | 3408.382 | 3445.507 | 3478.301 | 3513.998 | 3546.942 | 3588.445 | 3630.639 | 3677.287 | 3727.032 | 3776.567 | 3826.193 | 3877.094 | 3929.291 | 3982.802 | 4037.646 | 4093.842 | 4151.411 | 4210.372 | 4270.746 |  |  | Total | 228 | 0 | 0 | -6.2217 | -213.0304 | -2.0716 | -3.1082 | -5.7996 | -4.6199 | 4.3302 | 9.9458 | -11.5626 | 7.9551 | 31.6572 | 37.1242 | 32.7943 | 35.697 | 32.9443 | 41.5031 | 42.1942 | 46.6472 | 49.7457 | 49.5344 | 49.6258 | 50.902 | 52.1968 | 53.5107 | 54.8438 | 56.1964 | 57.5688 | 58.9612 | 60.374
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 5612 |  | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612 | 5612
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 8612 |  | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 | 8612 |  |  | Pennant Hills 132_11kV Tx1 | 119 | 0 | 0 | -2.5752 | -145.0126 | 28.1426 | 42.7135 | 190.5996 | -1.9122 | 1.7923 | 4.1165 | -4.7857 | 3.2926 | 13.1029 | 15.3657 | 13.5735 | 14.7749 | 13.6356 | 17.1781 | 17.4641 | 19.3072 | 20.5897 | 20.5022 | 20.54 | 21.0682 | 21.6042 | 22.148 | 22.6997 | 23.2596 | 23.8276 | 24.4039 | 24.9887
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Pennant Hills 132_11kV Tx2 | 90 | 0 | 0 | 70.0846 | -20.0094 | -29.6378 | -44.9569 | -190.7855 | -1.4223 | 1.3331 | 3.0619 | -3.5597 | 2.4491 | 9.7461 | 11.4292 | 10.0962 | 10.9898 | 10.1423 | 12.7773 | 12.99 | 14.3609 | 15.3149 | 15.2498 | 15.2779 | 15.6708 | 16.0695 | 16.4739 | 16.8844 | 17.3008 | 17.7233 | 18.152 | 18.5869
| Transformer Loads | [35 empty] | Pennant Hills 132_11kV Tx3 | 19 | 0 | 0 | -73.7311 | -48.0085 | -0.57641 | -0.86484 | -5.6137 | -1.2854 | 1.2048 | 2.7673 | -3.2172 | 2.2134 | 8.8083 | 10.3294 | 9.1247 | 9.9323 | 9.1664 | 11.5478 | 11.7401 | 12.9791 | 13.8412 | 13.7824 | 13.8078 | 14.1629 | 14.5232 | 14.8888 | 15.2597 | 15.636 | 16.0179 | 16.4053 | 16.7984
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.069834 | -0.13967 | -0.2095 | -1.257 | -8.1063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Pennant Hills 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.051944 | -0.10389 | -0.15583 | -0.93499 | -6.0296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Pennant Hills 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.046945 | -0.093891 | -0.14084 | -0.84502 | -5.4494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6131. Relief of Feeders from Epping Zone Substation Panels 1,10,11 and 12 | Epping 66_11kV Tx1 | Pennant Hills 132_11kV Tx1 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6155. Pennant Hills Development - Relief of Remedial Feeders Panels 3, 11 & 47, and improved Pickups for Panel 6. | Pennant Hills 132_11kV Tx1 | Pennant Hills 132_11kV Tx2 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6155. Pennant Hills Development - Relief of Remedial Feeders Panels 3, 11 & 47, and improved Pickups for Panel 6. | Pennant Hills 132_11kV Tx2 | Pennant Hills 132_11kV Tx3 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6155. Pennant Hills Development - Relief of Remedial Feeders Panels 3, 11 & 47, and improved Pickups for Panel 6. | Pennant Hills 132_11kV Tx3 | Pennant Hills 132_11kV Tx2 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Pennant Hills 132_11kV Tx1 | Galston 132_11kV Tx1 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6215. Galston Zone Development - Commissioning & Integration with the existing 11 kV Network. | Pennant Hills 132_11kV Tx1 | Galston 132_11kV Tx2 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6359. Pennant Hills Minor Zone Development 2008 - Panels 26 & 44 Feeders | Pennant Hills 132_11kV Tx2 | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6359. Pennant Hills Minor Zone Development 2008 - Panels 26 & 44 Feeders | Pennant Hills 132_11kV Tx2 | Pennant Hills 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6359. Pennant Hills Minor Zone Development 2008 - Panels 26 & 44 Feeders | Pennant Hills 132_11kV Tx3 | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6359. Pennant Hills Minor Zone Development 2008 - Panels 26 & 44 Feeders | Pennant Hills 132_11kV Tx3 | Pennant Hills 132_11kV Tx2 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6481. 11 kV Network Augmentation to relieve Pennant Hills feeders to the North of the Zone - Panel 4, 38 & 42 Feeders | Pennant Hills 132_11kV Tx1 | Pennant Hills 132_11kV Tx2 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6481. 11 kV Network Augmentation to relieve Pennant Hills feeders to the North of the Zone - Panel 4, 38 & 42 Feeders | Pennant Hills 132_11kV Tx2 | Pennant Hills 132_11kV Tx3 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6481. 11 kV Network Augmentation to relieve Pennant Hills feeders to the North of the Zone - Panel 4, 38 & 42 Feeders | Pennant Hills 132_11kV Tx3 | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2011086. Establishment of S.49499 Leith Malahide, Leith Rd, Pennant Hills | Pennant Hills 132_11kV Tx3 | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2012154. Establish S.62023 RAILWAY PENNANT, Pennant Hills Station Yarrara Rd, Pennant Hills | Pennant Hills 132_11kV Tx2 | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012156. Remove Sub S.5477 The Crescent Cheltenham and Establish new substation S.62030, Cheltenham Station, Cheltenham Railway Station, The Crescent Cheltenham. | Pennant Hills 132_11kV Tx2 | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2012258. Self Assessed DNP Pennant Hills Pa 47 Optimisation - Establish S.47575 Willis Stevens and recover PT717 Willis Stevens | Pennant Hills 132_11kV Tx2 | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013416. Pennant Hills Day Surgery, 361-363 Pennant Hills Rd, Pennant Hills 800kVA Kiosk Substation “S.64494 – George Pennant No2” | Pennant Hills 132_11kV Tx2 | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Econometric |  | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.206 | 19.8737 | 25.3928 | 27.0676 | 28.5958 | 28.2324 | 27.8371 | 28.3069 | 28.7837 | 29.2676 | 29.7586 | 30.2568 | 30.7624 | 31.2754 | 31.7959 | 32.3241 | 32.8601 | 33.4039 | 33.9557 | 34.5155 | 35.0835 | 35.6599 | 36.2446
[35 empty] | Econometric |  | Pennant Hills 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3352 | 14.7823 | 18.8875 | 20.1332 | 21.2699 | 20.9996 | 20.7056 | 21.055 | 21.4097 | 21.7696 | 22.1348 | 22.5054 | 22.8815 | 23.263 | 23.6502 | 24.0431 | 24.4418 | 24.8462 | 25.2567 | 25.6731 | 26.0956 | 26.5243 | 26.9592
[35 empty] | Econometric |  | Pennant Hills 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5331 | 13.3599 | 17.0701 | 18.1959 | 19.2232 | 18.979 | 18.7132 | 19.0291 | 19.3496 | 19.6749 | 20.0049 | 20.3399 | 20.6797 | 21.0246 | 21.3745 | 21.7296 | 22.0899 | 22.4555 | 22.8264 | 23.2027 | 23.5846 | 23.972 | 24.3651
| 0 | [33 empty] | Energy Efficiency |  | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5062 | -0.84779 | -8.1599 | -13.3543 | -20.8458 | -22.4829 | -14.1401 | -11.5586 | -12.9346 | -12.5152 | -13.9302 | -10.8716 | -11.0765 | -9.7316 | -8.9548 | -9.5553 | -10.038 | -10.038 | -10.038 | -10.038 | -10.038 | -10.038 | -10.038 | -10.038 | -10.038
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Pennant Hills 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1203 | -0.6306 | -6.0694 | -9.9331 | -15.5054 | -16.7231 | -10.5176 | -8.5974 | -9.6209 | -9.3089 | -10.3615 | -8.0864 | -8.2389 | -7.2385 | -6.6607 | -7.1073 | -7.4664 | -7.4664 | -7.4664 | -7.4664 | -7.4664 | -7.4664 | -7.4664 | -7.4664 | -7.4664
[35 empty] | Energy Efficiency |  | Pennant Hills 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0125 | -0.56992 | -5.4854 | -8.9773 | -14.0134 | -15.1139 | -9.5056 | -7.7702 | -8.6952 | -8.4132 | -9.3645 | -7.3083 | -7.4461 | -6.542 | -6.0198 | -6.4234 | -6.7479 | -6.7479 | -6.7479 | -6.7479 | -6.7479 | -6.7479 | -6.7479 | -6.7479 | -6.7479
[35 empty] | Solar PV |  | Pennant Hills 132_11kV Tx1 | 0 | 0 | 0 | -2.5752 | -0.0126 | -0.85745 | -1.2865 | -0.82443 | -0.92472 | -1.0444 | -1.146 | -1.2264 | -1.2921 | -1.3527 | -1.3081 | -1.3289 | -1.0168 | -1.218 | -1.218 | -1.218 | -1.218 | -1.218 | -1.218 | -1.218 | -1.218 | -1.218 | -1.218 | -1.218 | -1.218 | -1.218 | -1.218 | -1.218
| 0 | [33 empty] | Solar PV |  | Pennant Hills 132_11kV Tx2 | 0 | 0 | 0 | -1.9154 | -0.009372 | -0.63778 | -0.95691 | -0.61322 | -0.68782 | -0.77682 | -0.85237 | -0.91225 | -0.96104 | -1.0062 | -0.97301 | -0.98847 | -0.75633 | -0.90594 | -0.90594 | -0.90594 | -0.90594 | -0.90594 | -0.90594 | -0.90594 | -0.90594 | -0.90594 | -0.90594 | -0.90594 | -0.90594 | -0.90594 | -0.90594 | -0.90594
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Pennant Hills 132_11kV Tx3 | 0 | 0 | 0 | -1.7311 | -0.0084702 | -0.57641 | -0.86484 | -0.55421 | -0.62163 | -0.70207 | -0.77035 | -0.82447 | -0.86857 | -0.90937 | -0.87938 | -0.89336 | -0.68355 | -0.81876 | -0.81876 | -0.81876 | -0.81876 | -0.81876 | -0.81876 | -0.81876 | -0.81876 | -0.81876 | -0.81876 | -0.81876 | -0.81876 | -0.81876 | -0.81876 | -0.81876
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 9.659% |  | 5 year ROG ok | [59 empty] | 5 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95377 | 0.90968 | 0.88164 | 0.86805 | 0.86805 | 0.86805 | 0.86805 | 0.86805 | 0.86805 | 0.86805 | -4.623% | -4.623% | -3.082% | -1.541% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Pennant Hills 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 3579 | 3889 | 3703.391 | 3527.544 | 3423.143 | 3380.333 | 3368.77 | 3376.725 | 3408.382 | 3445.507 | 3478.301 | 3513.998 | 3546.942 | 3588.445 | 3630.639 | 3677.287 | 3727.032 | 3776.567 | 3826.193 | 3877.094 | 3929.291 | 3982.802 | 4037.646 | 4093.842 | 4151.411 | 4210.372 | 4270.746
|  |  |  | Apparent Power |  |  | MVA | 68.1891 |  | 70.5591 | 67.2087 | 65.2196 | 64.404 | 64.1837 | 64.3353 | 64.9384 | 65.6457 | 66.2705 | 66.9507 | 67.5783 | 68.3691 | 69.173 | 70.0617 | 71.0095 | 71.9533 | 72.8988 | 73.8686 | 74.8631 | 75.8826 | 76.9275 | 77.9982 | 79.095 | 80.2184 | 81.3687
|  |  |  | Real Power |  |  | MW | 65.4887 | 71.1611 | 67.7648 | 64.5472 | 62.6368 | 61.8535 | 61.6419 | 61.7875 | 62.3667 | 63.046 | 63.6461 | 64.2993 | 64.9021 | 65.6615 | 66.4336 | 67.2872 | 68.1974 | 69.1038 | 70.0118 | 70.9433 | 71.8984 | 72.8775 | 73.881 | 74.9093 | 75.9627 | 77.0416 | 78.1463
|  |  |  | Reactive Power |  |  | MVAr | 18.9996 |  | 19.6599 | 18.7264 | 18.1722 | 17.9449 | 17.8835 | 17.9258 | 18.0938 | 18.2909 | 18.465 | 18.6545 | 18.8294 | 19.0497 | 19.2737 | 19.5213 | 19.7854 | 20.0484 | 20.3118 | 20.582 | 20.8591 | 21.1432 | 21.4343 | 21.7327 | 22.0383 | 22.3513 | 22.6718
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9604 |  | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604
0.87395 | Diversity Factor: 0.87 | Uncompensated |  | Reactive Power |  |  | MVAr | 18.9996 | 20.6452 | 19.6599 | 18.7264 | 18.1722 | 17.9449 | 17.8835 | 17.9258 | 18.0938 | 18.2909 | 18.465 | 18.6545 | 18.8294 | 19.0497 | 19.2737 | 19.5213 | 19.7854 | 20.0484 | 20.3118 | 20.582 | 20.8591 | 21.1432 | 21.4343 | 21.7327 | 22.0383 | 22.3513 | 22.6718
|  |  |  | PF |  |  |  | 0.9604 |  | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604 | 0.9604
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer47
| Customer47 | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (66kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (66kV Amps) | [20 empty] | Spots & Transfers Summary | (66kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  | 110 | 98 | 92 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (66kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (66kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Customer47 | Compensated |  | Load (LV side) |  |  | Amps | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92
|  |  |  | Apparent Power |  |  | MVA | 10.517 |  | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517 | 10.517
|  |  |  | Real Power |  |  | MW | 9.4653 |  | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653 | 9.4653
|  |  |  | Reactive Power |  |  | MVAr | 4.5843 |  | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.68206 | Diversity Factor: 0.68 | Uncompensated |  | Reactive Power |  |  | MVAr | 4.5843 |  | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843 | 4.5843
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF