## Inclusions and Exclusions
Sydney Forecast Inclusions and Exclusions
Date Printed |  | 08JUL14:11:21:24
| Description | Value
Season |  | Summer | Summer
Either Summer or Winter
Year |  | 2015 | 2015
Year that the forecast starts
POE |  | 50% | 0.5
10%, 50%, 90%
Spots and Transfers |  | Y | Y
Are Spots and Transfers Included?
BBDM Spots |  | Y | Y
Is BBDM included?
Spots Coefficient |  | 55% | 0.55
Scaling factor applied to spot loads in the future
Aligned ROGs |  | Capped | Capped
Have ROGs been aligned to econometric forecast?
Committed Projects |  | Y | Y
Are Committed Projects Included?
Major Customers Scaling Factor |  | 100% | 1
Scaling factor applied to major customer connections in the future
Future Transfers |  | Y | Y
Are future transfers included?
Future Spots |  | 4 | 4
Future spots are cleared from the following forecast year

## Auburn 33_11kV
| Auburn 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 960 | 1199 | 1557 | 1446 | 1530 | 1461 | 1412 |  | 1517.668 | 1496.339 | 1479.006 | 1469.981 | 1466.678 | 1470.941 | 1486.314 | 1506.673 | 1524.367 | 1543.19 | 1557.964 | 1576.961 | 1595.824 | 1618.037 | 1641.981 | 1665.477 | 1688.101 | 1711.111 | 1734.511 | 1758.305 | 1782.499 | 1807.097 | 1832.105 | 1857.527 | 1883.37 |  |  | Total | 13.5 | 0 | 449 | -239.3967 | 150.2016 | -1.8969 | -3.3602 | 6.0249 | -13.9787 | -12.5028 | -6.6372 | -3.3027 | 4.2628 | 15.3733 | 20.3587 | 17.6938 | 18.8233 | 14.7744 | 18.9966 | 18.8633 | 22.2132 | 23.9438 | 23.4952 | 22.6247 | 23.0097 | 23.3996 | 23.7942 | 24.1938 | 24.5983 | 25.0079 | 25.4225 | 25.8424
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2152 |  | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 3985 |  | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 | 3985 |  |  | Auburn 33_11kV Tx3 | 0 | 0 | -161 | -364.6152 | 246.3268 | -13.8355 | -1.4801 | -5.0987 | -6.1575 | -5.5074 | -2.9236 | -1.4548 | 1.8777 | 6.7718 | 8.9678 | 7.794 | 8.2915 | 6.508 | 8.3678 | 8.3091 | 9.7847 | 10.547 | 10.3494 | 9.966 | 10.1356 | 10.3073 | 10.4811 | 10.6571 | 10.8353 | 11.0157 | 11.1984 | 11.3833
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Auburn 33_11kV Tx4 | 13.5 | 0 | -185 | 125.9966 | -0.0093213 | -0.0046549 | -0.0082458 | -0.028405 | -0.034303 | -0.030682 | -0.016287 | -0.0081047 | 0.010461 | 0.037726 | 0.04996 | 0.04342 | 0.046192 | 0.036256 | 0.046617 | 0.04629 | 0.054511 | 0.058758 | 0.057657 | 0.055521 | 0.056466 | 0.057422 | 0.058391 | 0.059371 | 0.060364 | 0.061369 | 0.062387 | 0.063417
| Transformer Loads | [35 empty] | Auburn 33_11kV Tx5 | 0 | 0 | 795 | -0.77802 | -96.1159 | 11.9433 | -1.8718 | 11.152 | -7.7869 | -6.9648 | -3.6973 | -1.8398 | 2.3746 | 8.5638 | 11.3409 | 9.8564 | 10.4856 | 8.2302 | 10.5821 | 10.5079 | 12.374 | 13.338 | 13.0882 | 12.6032 | 12.8177 | 13.0348 | 13.2547 | 13.4773 | 13.7026 | 13.9308 | 14.1618 | 14.3956
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Auburn 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2041 | -3.8548 | -4.6785 | -4.4402 | -3.7881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Auburn 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.006708 | -0.021475 | -0.026064 | -0.024737 | -0.021104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Auburn 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5227 | -4.8749 | -5.9165 | -5.6152 | -4.7905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5858. Auburn Zone Development - Stage 1 | Auburn 33_11kV Tx3 | Auburn 33_11kV Tx4 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 5858. Auburn Zone Development - Stage 1 | Auburn 33_11kV Tx3 | Flemington 132_11kV Tx4 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 5858. Auburn Zone Development - Stage 1 | Flemington 132_11kV Tx4 | Auburn 33_11kV Tx3 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6452. 11kV Feeder Transfers to new Switchgear at Auburn Zone. | Auburn 33_11kV Tx3 | Auburn 33_11kV Tx5 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6452. 11kV Feeder Transfers to new Switchgear at Auburn Zone. | Auburn 33_11kV Tx4 | Auburn 33_11kV Tx5 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6452. 11kV Feeder Transfers to new Switchgear at Auburn Zone. | Flemington 132_11kV Tx4 | Auburn 33_11kV Tx3 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6452. 11kV Feeder Transfers to new Switchgear at Auburn Zone. | Homebush Bay 132_11kV Tx2 | Auburn 33_11kV Tx3 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6452. 11kV Feeder Transfers to new Switchgear at Auburn Zone. | Homebush Bay 132_11kV Tx2 | Auburn 33_11kV Tx5 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6869. Newington 11kV Rearrangement (Smart Grid Smart City Energy Resource Management) | Homebush Bay 132_11kV Tx2 | Auburn 33_11kV Tx5 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6938. Auburn West Zone Development | Auburn 33_11kV Tx3 | Auburn 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 7026. Change in open points to relieve Tx5 at Auburn zone | Auburn 33_11kV Tx5 | Auburn 33_11kV Tx3 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2005074. Est Kiosks S.8437 "Parramatta Skarratt No1" and S.8446 "Parramatta Skarratt No2". Recover S.4201 "Parramatta Skarrat". |  | Auburn 33_11kV Tx4 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2009498. Establishment of S.47152 Parramatta John No.1 & S.48233 Parramatta John No.2, 15-21 Parramatta Rd, Lidcombe |  | Auburn 33_11kV Tx3 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2014103. Uprate S.268 Carnarvon St, 113 Carnarvon St, Silverwater with additional 750kVA Tx as part load growth |  | Auburn 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Econometric |  | Auburn 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2676 | 8.5585 | 12.4771 | 12.0842 | 12.8702 | 12.509 | 12.1366 | 12.2902 | 12.4457 | 12.6032 | 12.7626 | 12.924 | 13.0874 | 13.2529 | 13.4204 | 13.59 | 13.7617 | 13.9355 | 14.1115 | 14.2897 | 14.4702 | 14.6528 | 14.8377
[35 empty] | Econometric |  | Auburn 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023775 | 0.04768 | 0.06951 | 0.067321 | 0.0717 | 0.069688 | 0.067613 | 0.068469 | 0.069336 | 0.070213 | 0.071101 | 0.072 | 0.072911 | 0.073832 | 0.074765 | 0.07571 | 0.076667 | 0.077635 | 0.078616 | 0.079609 | 0.080614 | 0.081631 | 0.082661
[35 empty] | Econometric |  | Auburn 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3969 | 10.8233 | 15.7788 | 15.2819 | 16.276 | 15.8192 | 15.3482 | 15.5425 | 15.7392 | 15.9383 | 16.1399 | 16.344 | 16.5507 | 16.7599 | 16.9718 | 17.1862 | 17.4034 | 17.6232 | 17.8458 | 18.0711 | 18.2993 | 18.5303 | 18.7641
| 0 | [33 empty] | Energy Efficiency |  | Auburn 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9653 | -1.2603 | -3.9193 | -5.7502 | -8.7613 | -8.7501 | -4.5736 | -2.0667 | -2.8447 | -2.8526 | -4.5649 | -2.8625 | -3.0806 | -1.7665 | -1.1675 | -1.5306 | -2.0815 | -2.0815 | -2.0815 | -2.0815 | -2.0815 | -2.0815 | -2.0815 | -2.0815 | -2.0815
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Auburn 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.01652 | -0.0070213 | -0.021835 | -0.032035 | -0.048809 | -0.048747 | -0.02548 | -0.011514 | -0.015848 | -0.015892 | -0.025431 | -0.015947 | -0.017162 | -0.009841 | -0.0065044 | -0.0085269 | -0.011596 | -0.011596 | -0.011596 | -0.011596 | -0.011596 | -0.011596 | -0.011596 | -0.011596 | -0.011596
[35 empty] | Energy Efficiency |  | Auburn 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7501 | -1.5938 | -4.9564 | -7.2719 | -11.0797 | -11.0655 | -5.7839 | -2.6136 | -3.5975 | -3.6074 | -5.7728 | -3.62 | -3.8959 | -2.2339 | -1.4765 | -1.9356 | -2.6324 | -2.6324 | -2.6324 | -2.6324 | -2.6324 | -2.6324 | -2.6324 | -2.6324 | -2.6324
[35 empty] | Solar PV |  | Auburn 33_11kV Tx3 | 0 | 0 | 0 | -0.61522 | -1.6732 | -0.83555 | -1.4801 | -0.92928 | -1.0423 | -1.1772 | -1.2917 | -1.3824 | -1.4564 | -1.5248 | -1.4745 | -1.4979 | -1.1462 | -1.3729 | -1.3729 | -1.3729 | -1.3729 | -1.3729 | -1.3729 | -1.3729 | -1.3729 | -1.3729 | -1.3729 | -1.3729 | -1.3729 | -1.3729 | -1.3729 | -1.3729
| 0 | [33 empty] | Solar PV |  | Auburn 33_11kV Tx4 | 0 | 0 | 0 | -0.0034274 | -0.0093213 | -0.0046549 | -0.0082458 | -0.0051771 | -0.0058069 | -0.0065582 | -0.0071961 | -0.0077016 | -0.0081135 | -0.0084947 | -0.0082145 | -0.0083451 | -0.0063853 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483 | -0.0076483
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Auburn 33_11kV Tx5 | 0 | 0 | 0 | -0.77802 | -2.1159 | -1.0567 | -1.8718 | -1.1752 | -1.3182 | -1.4887 | -1.6335 | -1.7483 | -1.8418 | -1.9283 | -1.8647 | -1.8943 | -1.4495 | -1.7362 | -1.7362 | -1.7362 | -1.7362 | -1.7362 | -1.7362 | -1.7362 | -1.7362 | -1.7362 | -1.7362 | -1.7362 | -1.7362 | -1.7362 | -1.7362 | -1.7362
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | 0: Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 3.675% |  | 0: 7 year ROG ok | [35 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.99516 | 0.99034 | 0.98715 | 0.98557 | 0.98557 | 0.98557 | 0.98557 | 0.98557 | 0.98557 | 0.98557 | -0.484% | -0.484% | -0.322% | -0.161% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Auburn 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1412 | 1519 | 1517.668 | 1496.339 | 1479.006 | 1469.981 | 1466.678 | 1470.941 | 1486.314 | 1506.673 | 1524.367 | 1543.19 | 1557.964 | 1576.961 | 1595.824 | 1618.037 | 1641.981 | 1665.477 | 1688.101 | 1711.111 | 1734.511 | 1758.305 | 1782.499 | 1807.097 | 1832.105 | 1857.527 | 1883.37
|  |  |  | Apparent Power |  |  | MVA | 26.9022 |  | 28.9155 | 28.5091 | 28.1788 | 28.0069 | 27.944 | 28.0252 | 28.3181 | 28.706 | 29.0431 | 29.4017 | 29.6832 | 30.0451 | 30.4045 | 30.8278 | 31.284 | 31.7316 | 32.1626 | 32.6011 | 33.0469 | 33.5002 | 33.9612 | 34.4298 | 34.9063 | 35.3907 | 35.883
|  |  |  | Real Power |  |  | MW | 24.359 | 26.2049 | 26.1819 | 25.8139 | 25.5149 | 25.3592 | 25.3023 | 25.3758 | 25.641 | 25.9922 | 26.2975 | 26.6222 | 26.8771 | 27.2048 | 27.5302 | 27.9134 | 28.3265 | 28.7318 | 29.1221 | 29.5191 | 29.9227 | 30.3332 | 30.7506 | 31.1749 | 31.6064 | 32.045 | 32.4908
|  |  |  | Reactive Power |  |  | MVAr | 11.4179 |  | 12.2724 | 12.0999 | 11.9598 | 11.8868 | 11.8601 | 11.8946 | 12.0189 | 12.1835 | 12.3266 | 12.4788 | 12.5983 | 12.7519 | 12.9044 | 13.084 | 13.2776 | 13.4676 | 13.6506 | 13.8367 | 14.0259 | 14.2183 | 14.4139 | 14.6128 | 14.815 | 15.0206 | 15.2296
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.90546 |  | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546
0.87584 | Diversity Factor: 0.88 | Uncompensated |  | Reactive Power |  |  | MVAr | 11.4179 | 12.2832 | 12.2724 | 12.0999 | 11.9598 | 11.8868 | 11.8601 | 11.8946 | 12.0189 | 12.1835 | 12.3266 | 12.4788 | 12.5983 | 12.7519 | 12.9044 | 13.084 | 13.2776 | 13.4676 | 13.6506 | 13.8367 | 14.0259 | 14.2183 | 14.4139 | 14.6128 | 14.815 | 15.0206 | 15.2296
|  |  |  | PF |  |  |  | 0.90546 |  | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546 | 0.90546
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Burwood 132_11kV
| Burwood 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 3839 | 4110 | 4272 | 4417 | 3693 | 4095 | 3343 |  | 3246.133 | 3180.494 | 3124.814 | 3107.655 | 3122.723 | 3152.335 | 3214.932 | 3286.472 | 3349.949 | 3416.089 | 3475.349 | 3546.146 | 3617.347 | 3696.382 | 3780.04 | 3863.11 | 3945.135 | 4028.697 | 4113.814 | 4200.507 | 4288.796 | 4378.701 | 4470.243 | 4563.444 | 4658.325 |  |  | Total | 0 | 0 | -129 | -2.9398 | 57.4071 | 1.3862 | -1.0203 | -115.6184 | 5.3699 | -9.5139 | 5.7071 | 15.3387 | 30.1359 | 63.6734 | 72.7179 | 64.4798 | 67.1439 | 60.126 | 71.793 | 72.1633 | 80.0585 | 84.6938 | 84.0525 | 82.9552 | 84.4689 | 86.003 | 87.5576 | 89.133 | 90.7295 | 92.3473 | 93.9868 | 95.6481
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 4388 |  | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388 | 4388
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 8000 |  | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 |  |  | Burwood 132_11kV Tx1 | 0 | 0 | -137 | -0.74776 | 61.5774 | 3.3351 | -0.25953 | -4.6086 | -5.629 | -2.42 | 1.4517 | 3.9016 | 7.6654 | 16.1961 | 18.4966 | 16.4012 | 17.0788 | 15.2937 | 18.2614 | 18.3556 | 20.3638 | 21.5428 | 21.3797 | 21.1006 | 21.4856 | 21.8758 | 22.2713 | 22.672 | 23.0781 | 23.4896 | 23.9066 | 24.3292
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Burwood 132_11kV Tx2 | 0 | 0 | 25 | -0.86191 | -23.6398 | -0.76635 | -0.29915 | -102.8121 | 21.0117 | -2.7894 | 1.6733 | 4.4972 | 8.8356 | 18.6685 | 21.3202 | 18.9049 | 19.686 | 17.6284 | 21.0491 | 21.1576 | 23.4724 | 24.8315 | 24.6434 | 24.3217 | 24.7655 | 25.2153 | 25.6711 | 26.133 | 26.601 | 27.0754 | 27.5561 | 28.0432
| Transformer Loads | [35 empty] | Burwood 132_11kV Tx3 | 0 | 0 | -150 | -0.68655 | -1.3062 | -0.61043 | -0.23829 | -4.2314 | -5.1683 | -2.2219 | 1.3328 | 3.5822 | 7.0379 | 14.8703 | 16.9825 | 15.0586 | 15.6808 | 14.0418 | 16.7665 | 16.853 | 18.6968 | 19.7794 | 19.6296 | 19.3733 | 19.7268 | 20.0851 | 20.4482 | 20.8161 | 21.1889 | 21.5668 | 21.9496 | 22.3376
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  | Burwood 132_11kV Tx4 | 0 | 0 | 133 | -0.64354 | 20.7757 | -0.57219 | -0.22336 | -3.9663 | -4.8445 | -2.0827 | 1.2493 | 3.3578 | 6.597 | 13.9386 | 15.9185 | 14.1152 | 14.6984 | 13.1621 | 15.7161 | 15.7971 | 17.5255 | 18.5402 | 18.3998 | 18.1596 | 18.491 | 18.8268 | 19.1671 | 19.5119 | 19.8614 | 20.2156 | 20.5745 | 20.9382
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Burwood 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.97558 | -3.6694 | -4.4823 | -5.43 | -4.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Burwood 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1245 | -4.2296 | -5.1665 | -6.2589 | -4.9901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Burwood 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.89572 | -3.369 | -4.1154 | -4.9855 | -3.9748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Burwood 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.8396 | -3.158 | -3.8575 | -4.6732 | -3.7258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6123. Burwood Zone Development - 2008. | Burwood 132_11kV Tx1 | Burwood 132_11kV Tx4 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6123. Burwood Zone Development - 2008. | Burwood 132_11kV Tx3 | Burwood 132_11kV Tx4 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6123. Burwood Zone Development - 2008. | Burwood 132_11kV Tx4 | Burwood 132_11kV Tx3 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6320. North Enfield Zone Development - 2007 | Burwood 132_11kV Tx1 | Enfield 33_11kV Tx1 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6320. North Enfield Zone Development - 2007 | Burwood 132_11kV Tx3 | Enfield 33_11kV Tx1 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6320. North Enfield Zone Development - 2007 | Enfield 33_11kV Tx1 | Burwood 132_11kV Tx2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6821. Network Augmentation to replace Outdoor Enclosure S.3353 Weeroona Rd | Greenacre Park 132_11kV Tx3 | Burwood 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6862. Enfield to Campsie load transfer | Burwood 132_11kV Tx2 | Burwood 132_11kV Tx4 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6862. Enfield to Campsie load transfer | Enfield 33_11kV Tx1 | Burwood 132_11kV Tx1 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 7090. Burwood Zone Development 2012 | Burwood 132_11kV Tx2 | Five Dock 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013366. CBA Burwood- Reduction in load during refurbishment of data centre- S.6155 & S.6310- Pa 08 Burwood ZS |  | Burwood 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -27.5 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Burwood 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1039 | 17.4925 | 24.2743 | 24.3393 | 26.189 | 25.3229 | 24.4255 | 24.7716 | 25.1223 | 25.4778 | 25.838 | 26.2031 | 26.573 | 26.9479 | 27.3279 | 27.7129 | 28.1031 | 28.4986 | 28.8993 | 29.3054 | 29.7169 | 30.1339 | 30.5565
| 0 | [33 empty] | Econometric |  | Burwood 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4937 | 20.1628 | 27.9799 | 28.0548 | 30.1869 | 29.1886 | 28.1542 | 28.5531 | 28.9574 | 29.3671 | 29.7823 | 30.2031 | 30.6295 | 31.0617 | 31.4996 | 31.9434 | 32.3932 | 32.849 | 33.3109 | 33.779 | 34.2533 | 34.734 | 35.2211
| Diversity Factor: 0 | [33 empty] | Econometric |  | Burwood 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3587 | 16.0606 | 22.2873 | 22.3469 | 24.0453 | 23.25 | 22.4261 | 22.7438 | 23.0658 | 23.3922 | 23.7229 | 24.0581 | 24.3978 | 24.742 | 25.0909 | 25.4444 | 25.8027 | 26.1657 | 26.5336 | 26.9065 | 27.2843 | 27.6672 | 28.0552
[35 empty] | Econometric |  | Burwood 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.835 | 15.0544 | 20.8909 | 20.9469 | 22.5388 | 21.7934 | 21.0211 | 21.3189 | 21.6208 | 21.9267 | 22.2367 | 22.5509 | 22.8693 | 23.1919 | 23.5189 | 23.8503 | 24.1861 | 24.5264 | 24.8713 | 25.2208 | 25.5749 | 25.9338 | 26.2975
[35 empty] | Energy Efficiency |  | Burwood 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1461 | -1.4134 | -6.4248 | -9.934 | -15.3191 | -15.9108 | -9.194 | -6.0536 | -7.2394 | -7.0922 | -9.1092 | -6.497 | -6.7631 | -5.1199 | -4.3108 | -4.8488 | -5.5079 | -5.5079 | -5.5079 | -5.5079 | -5.5079 | -5.5079 | -5.5079 | -5.5079 | -5.5079
| 0 | [33 empty] | Energy Efficiency |  | Burwood 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6264 | -1.6292 | -7.4055 | -11.4505 | -17.6577 | -18.3397 | -10.5975 | -6.9778 | -8.3446 | -8.1749 | -10.4998 | -7.4888 | -7.7955 | -5.9015 | -4.9689 | -5.589 | -6.3487 | -6.3487 | -6.3487 | -6.3487 | -6.3487 | -6.3487 | -6.3487 | -6.3487 | -6.3487
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Burwood 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8886 | -1.2977 | -5.8988 | -9.1208 | -14.0651 | -14.6084 | -8.4414 | -5.5581 | -6.6468 | -6.5116 | -8.3636 | -5.9652 | -6.2094 | -4.7008 | -3.9579 | -4.4519 | -5.0571 | -5.0571 | -5.0571 | -5.0571 | -5.0571 | -5.0571 | -5.0571 | -5.0571 | -5.0571
[35 empty] | Energy Efficiency |  | Burwood 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7076 | -1.2164 | -5.5293 | -8.5494 | -13.184 | -13.6931 | -7.9125 | -5.2099 | -6.2304 | -6.1037 | -7.8396 | -5.5915 | -5.8204 | -4.4063 | -3.71 | -4.173 | -4.7402 | -4.7402 | -4.7402 | -4.7402 | -4.7402 | -4.7402 | -4.7402 | -4.7402 | -4.7402
[35 empty] | Solar PV |  | Burwood 132_11kV Tx1 | 0 | 0 | 0 | -0.74776 | -1.4226 | -0.66486 | -0.25953 | -0.48694 | -0.54617 | -0.61684 | -0.67684 | -0.72438 | -0.76313 | -0.79898 | -0.77263 | -0.78491 | -0.60057 | -0.71937 | -0.71937 | -0.71937 | -0.71937 | -0.71937 | -0.71937 | -0.71937 | -0.71937 | -0.71937 | -0.71937 | -0.71937 | -0.71937 | -0.71937 | -0.71937 | -0.71937
| 0 | [33 empty] | Solar PV |  | Burwood 132_11kV Tx2 | 0 | 0 | 0 | -0.86191 | -1.6398 | -0.76635 | -0.29915 | -0.56127 | -0.62955 | -0.71101 | -0.78016 | -0.83497 | -0.87963 | -0.92095 | -0.89058 | -0.90473 | -0.69226 | -0.82919 | -0.82919 | -0.82919 | -0.82919 | -0.82919 | -0.82919 | -0.82919 | -0.82919 | -0.82919 | -0.82919 | -0.82919 | -0.82919 | -0.82919 | -0.82919 | -0.82919
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Burwood 132_11kV Tx3 | 0 | 0 | 0 | -0.68655 | -1.3062 | -0.61043 | -0.23829 | -0.44708 | -0.50146 | -0.56635 | -0.62144 | -0.66509 | -0.70066 | -0.73358 | -0.70939 | -0.72066 | -0.55141 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049 | -0.66049
[35 empty] | Solar PV |  | Burwood 132_11kV Tx4 | 0 | 0 | 0 | -0.64354 | -1.2243 | -0.57219 | -0.22336 | -0.41907 | -0.47005 | -0.53087 | -0.5825 | -0.62342 | -0.65677 | -0.68762 | -0.66494 | -0.67551 | -0.51687 | -0.61911 | -0.61911 | -0.61911 | -0.61911 | -0.61911 | -0.61911 | -0.61911 | -0.61911 | -0.61911 | -0.61911 | -0.61911 | -0.61911 | -0.61911 | -0.61911 | -0.61911
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | 0: Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 2.858% |  | 0: 7 year ROG ok | [35 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.97899 | 0.95842 | 0.945 | 0.93839 | 0.93839 | 0.93839 | 0.93839 | 0.93839 | 0.93839 | 0.93839 | -2.101% | -2.101% | -1.4% | -0.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Burwood 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 3343 | 3624 | 3246.133 | 3180.494 | 3124.814 | 3107.655 | 3122.723 | 3152.335 | 3214.932 | 3286.472 | 3349.949 | 3416.089 | 3475.349 | 3546.146 | 3617.347 | 3696.382 | 3780.04 | 3863.11 | 3945.135 | 4028.697 | 4113.814 | 4200.507 | 4288.796 | 4378.701 | 4470.243 | 4563.444 | 4658.325
|  |  |  | Apparent Power |  |  | MVA | 63.6927 |  | 61.8471 | 60.5966 | 59.5357 | 59.2088 | 59.4959 | 60.06 | 61.2527 | 62.6157 | 63.8251 | 65.0852 | 66.2143 | 67.5631 | 68.9197 | 70.4255 | 72.0195 | 73.6021 | 75.1649 | 76.757 | 78.3787 | 80.0304 | 81.7125 | 83.4255 | 85.1696 | 86.9453 | 88.753
|  |  |  | Real Power |  |  | MW | 58.9353 | 63.8891 | 60.5085 | 59.3318 | 58.3329 | 58.025 | 58.2954 | 58.8267 | 59.9492 | 61.2312 | 62.3679 | 63.5517 | 64.6116 | 65.8773 | 67.1495 | 68.5609 | 70.054 | 71.5358 | 72.9983 | 74.4874 | 76.0036 | 77.5472 | 79.1185 | 80.7181 | 82.3461 | 84.003 | 85.6893
|  |  |  | Reactive Power |  |  | MVAr | 24.1536 |  | 12.7983 | 12.3161 | 11.9067 | 11.7805 | 11.8913 | 12.1091 | 12.5691 | 13.0945 | 13.5604 | 14.0455 | 14.4799 | 14.9986 | 15.52 | 16.0985 | 16.7104 | 17.3177 | 17.917 | 18.5273 | 19.1487 | 19.7813 | 20.4253 | 21.0809 | 21.7481 | 22.4271 | 23.1182
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
|  |  |  | PF |  |  |  | 0.92531 |  | 0.97835 | 0.97913 | 0.9798 | 0.98001 | 0.97982 | 0.97946 | 0.97872 | 0.97789 | 0.97717 | 0.97644 | 0.97579 | 0.97505 | 0.97431 | 0.97352 | 0.97271 | 0.97193 | 0.97117 | 0.97043 | 0.9697 | 0.96897 | 0.96825 | 0.96755 | 0.96685 | 0.96616 | 0.96548
0.97874 | Diversity Factor: 0.98 | Uncompensated |  | Reactive Power |  |  | MVAr | 24.1536 | 26.1838 | 24.7983 | 24.3161 | 23.9067 | 23.7805 | 23.8913 | 24.1091 | 24.5691 | 25.0945 | 25.5604 | 26.0455 | 26.4799 | 26.9986 | 27.52 | 28.0985 | 28.7104 | 29.3177 | 29.917 | 30.5273 | 31.1487 | 31.7813 | 32.4253 | 33.0808 | 33.7481 | 34.4271 | 35.1182
|  |  |  | PF |  |  |  | 0.92531 |  | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531 | 0.92531
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Concord 33_11kV
| Concord 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 2298 | 2389 | 2338 | 2395 | 1995 | 2259 | 1964 |  | 1623.96 | 1535.144 | 1486.911 | 1477.415 | 1500.192 | 1521.672 | 1561.331 | 1605.3 | 1644.357 | 1684.71 | 1721.288 | 1763.965 | 1806.843 | 1853.983 | 1903.602 | 1952.914 | 2001.626 | 2051.157 | 2101.52 | 2152.724 | 2204.781 | 2257.701 | 2311.496 | 2366.178 | 2421.757 |  |  | Total | 0 | 0 | 0 | -0.77103 | -1.2298 | -1.541 | -0.96627 | -248.489 | -7.6185 | 2.9387 | 15.2858 | 22.7773 | 21.4791 | 39.6596 | 43.969 | 39.0568 | 40.3533 | 36.5774 | 42.6769 | 42.8787 | 47.1399 | 49.619 | 49.3115 | 48.7119 | 49.5318 | 50.3625 | 51.2041 | 52.0566 | 52.9202 | 53.7952 | 54.6815 | 55.5795
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2856 |  | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856 | 2856
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 4320 |  | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 |  |  | Concord 33_11kV Tx1 | 0 | 0 | 0 | -0.25993 | -0.41457 | -0.5195 | -0.32575 | -92.8618 | -2.5683 | 0.9907 | 5.1532 | 7.6787 | 7.241 | 13.37 | 14.8228 | 13.1668 | 13.6039 | 12.331 | 14.3872 | 14.4552 | 15.8918 | 16.7275 | 16.6239 | 16.4217 | 16.6982 | 16.9782 | 17.2619 | 17.5493 | 17.8404 | 18.1354 | 18.4342 | 18.7369
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Concord 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Concord 33_11kV Tx3 | 0 | 0 | 0 | -0.25012 | -0.39893 | -0.4999 | -0.31346 | -67.7538 | -2.4714 | 0.95331 | 4.9587 | 7.3889 | 6.9678 | 12.8655 | 14.2635 | 12.6699 | 13.0905 | 11.8656 | 13.8443 | 13.9098 | 15.2921 | 16.0963 | 15.9966 | 15.802 | 16.068 | 16.3375 | 16.6105 | 16.8871 | 17.1672 | 17.4511 | 17.7386 | 18.0299
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | Concord 33_11kV Tx4 | 0 | 0 | 0 | -0.26098 | -0.41625 | -0.5216 | -0.32707 | -87.8734 | -2.5787 | 0.9947 | 5.174 | 7.7097 | 7.2703 | 13.4241 | 14.8827 | 13.22 | 13.6589 | 12.3808 | 14.4454 | 14.5137 | 15.956 | 16.7952 | 16.6911 | 16.4881 | 16.7657 | 17.0468 | 17.3317 | 17.6202 | 17.9126 | 18.2087 | 18.5087 | 18.8127
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Concord 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.26207 | -1.2276 | -1.4582 | -1.8778 | -1.5452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Concord 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Concord 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.25218 | -1.1812 | -1.4031 | -1.8069 | -1.4869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Concord 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.26313 | -1.2325 | -1.464 | -1.8854 | -1.5514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6531. North Concord Zone Development | Concord 33_11kV Tx1 | Concord 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6531. North Concord Zone Development | Concord 33_11kV Tx3 | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6531. North Concord Zone Development | Concord 33_11kV Tx4 | Meadowbank 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Concord 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1804 | 14.1376 | 19.9845 | 18.3637 | 19.9174 | 19.1121 | 18.2813 | 18.5304 | 18.7828 | 19.0385 | 19.2975 | 19.5599 | 19.8257 | 20.0951 | 20.3679 | 20.6444 | 20.9244 | 21.2081 | 21.4955 | 21.7866 | 22.0816 | 22.3804 | 22.6831
| 0 | [33 empty] | Econometric |  | Concord 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Econometric |  | Concord 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9095 | 13.6041 | 19.2304 | 17.6708 | 19.1658 | 18.3909 | 17.5915 | 17.8312 | 18.074 | 18.32 | 18.5693 | 18.8218 | 19.0776 | 19.3368 | 19.5993 | 19.8653 | 20.1348 | 20.4078 | 20.6843 | 20.9645 | 21.2483 | 21.5359 | 21.8272
[35 empty] | Econometric |  | Concord 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2095 | 14.1948 | 20.0653 | 18.438 | 19.9979 | 19.1894 | 18.3552 | 18.6053 | 18.8587 | 19.1154 | 19.3755 | 19.639 | 19.9059 | 20.1763 | 20.4503 | 20.7278 | 21.009 | 21.2938 | 21.5824 | 21.8747 | 22.1709 | 22.4709 | 22.7748
[35 empty] | Energy Efficiency |  | Concord 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3245 | -1.0321 | -4.383 | -6.7242 | -10.3512 | -10.6914 | -6.0958 | -3.8527 | -4.6709 | -4.5871 | -6.0453 | -4.2447 | -4.4357 | -3.2616 | -2.6916 | -3.0646 | -3.5396 | -3.5396 | -3.5396 | -3.5396 | -3.5396 | -3.5396 | -3.5396 | -3.5396 | -3.5396
| 0 | [33 empty] | Energy Efficiency |  | Concord 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Concord 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2368 | -0.99314 | -4.2176 | -6.4704 | -9.9606 | -10.288 | -5.8657 | -3.7073 | -4.4946 | -4.414 | -5.8171 | -4.0845 | -4.2683 | -3.1385 | -2.5901 | -2.949 | -3.4061 | -3.4061 | -3.4061 | -3.4061 | -3.4061 | -3.4061 | -3.4061 | -3.4061 | -3.4061
[35 empty] | Energy Efficiency |  | Concord 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3339 | -1.0363 | -4.4007 | -6.7514 | -10.3931 | -10.7346 | -6.1204 | -3.8682 | -4.6898 | -4.6057 | -6.0697 | -4.2618 | -4.4536 | -3.2747 | -2.7025 | -3.077 | -3.5539 | -3.5539 | -3.5539 | -3.5539 | -3.5539 | -3.5539 | -3.5539 | -3.5539 | -3.5539
[35 empty] | Solar PV |  | Concord 33_11kV Tx1 | 0 | 0 | 0 | -0.25993 | -0.41457 | -0.5195 | -0.32575 | -0.27521 | -0.30868 | -0.34863 | -0.38253 | -0.4094 | -0.4313 | -0.45157 | -0.43667 | -0.44361 | -0.33943 | -0.40657 | -0.40657 | -0.40657 | -0.40657 | -0.40657 | -0.40657 | -0.40657 | -0.40657 | -0.40657 | -0.40657 | -0.40657 | -0.40657 | -0.40657 | -0.40657 | -0.40657
| 0 | [33 empty] | Solar PV |  | Concord 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Concord 33_11kV Tx3 | 0 | 0 | 0 | -0.25012 | -0.39893 | -0.4999 | -0.31346 | -0.26482 | -0.29704 | -0.33547 | -0.3681 | -0.39396 | -0.41503 | -0.43453 | -0.4202 | -0.42687 | -0.32662 | -0.39123 | -0.39123 | -0.39123 | -0.39123 | -0.39123 | -0.39123 | -0.39123 | -0.39123 | -0.39123 | -0.39123 | -0.39123 | -0.39123 | -0.39123 | -0.39123 | -0.39123
[35 empty] | Solar PV |  | Concord 33_11kV Tx4 | 0 | 0 | 0 | -0.26098 | -0.41625 | -0.5216 | -0.32707 | -0.27632 | -0.30993 | -0.35004 | -0.38408 | -0.41106 | -0.43305 | -0.45339 | -0.43844 | -0.44541 | -0.3408 | -0.40822 | -0.40822 | -0.40822 | -0.40822 | -0.40822 | -0.40822 | -0.40822 | -0.40822 | -0.40822 | -0.40822 | -0.40822 | -0.40822 | -0.40822 | -0.40822 | -0.40822
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0.9039% |  | Rog Capped +/-5% | [59 empty] | Rog Capped +/-5%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.95 | 0.9025 | 0.87242 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | 0.85789 | -5% | -5% | -3.333% | -1.666% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Concord 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1964 | 1971 | 1623.96 | 1535.144 | 1486.911 | 1477.415 | 1500.192 | 1521.672 | 1561.331 | 1605.3 | 1644.357 | 1684.71 | 1721.288 | 1763.965 | 1806.843 | 1853.983 | 1903.602 | 1952.914 | 2001.626 | 2051.157 | 2101.52 | 2152.724 | 2204.781 | 2257.701 | 2311.496 | 2366.178 | 2421.757
|  |  |  | Apparent Power |  |  | MVA | 37.4192 |  | 30.9406 | 29.2484 | 28.3295 | 28.1485 | 28.5825 | 28.9917 | 29.7474 | 30.5851 | 31.3292 | 32.0981 | 32.7949 | 33.608 | 34.425 | 35.3231 | 36.2685 | 37.208 | 38.1361 | 39.0798 | 40.0393 | 41.0149 | 42.0067 | 43.015 | 44.0399 | 45.0817 | 46.1407
|  |  |  | Real Power |  |  | MW | 35.015 | 35.1398 | 28.9526 | 27.3692 | 26.5093 | 26.34 | 26.7461 | 27.129 | 27.8361 | 28.62 | 29.3163 | 30.0357 | 30.6878 | 31.4487 | 32.2131 | 33.0536 | 33.9382 | 34.8173 | 35.6858 | 36.5689 | 37.4668 | 38.3796 | 39.3077 | 40.2512 | 41.2103 | 42.1852 | 43.1761
|  |  |  | Reactive Power |  |  | MVAr | 13.1965 |  | 10.9117 | 10.3149 | 9.9909 | 9.9271 | 10.0801 | 10.2244 | 10.4909 | 10.7863 | 11.0488 | 11.3199 | 11.5657 | 11.8524 | 12.1405 | 12.4573 | 12.7907 | 13.122 | 13.4493 | 13.7821 | 14.1205 | 14.4646 | 14.8144 | 15.17 | 15.5314 | 15.8988 | 16.2723
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.93575 |  | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575
0.9772 | Diversity Factor: 0.98 | Uncompensated |  | Reactive Power |  |  | MVAr | 13.1965 | 13.2436 | 10.9117 | 10.3149 | 9.9909 | 9.9271 | 10.0801 | 10.2244 | 10.4909 | 10.7863 | 11.0488 | 11.3199 | 11.5657 | 11.8524 | 12.1405 | 12.4573 | 12.7907 | 13.122 | 13.4493 | 13.7821 | 14.1205 | 14.4646 | 14.8144 | 15.17 | 15.5314 | 15.8988 | 16.2723
|  |  |  | PF |  |  |  | 0.93575 |  | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575 | 0.93575
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Croydon 132_11kV
| Croydon 132_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone commissioned |  | 2016-10-31
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | [8 empty] | 0 | 0 | 1763.095 | 1764.751 | 1773.658 | 1785.903 | 1814.096 | 1845.622 | 1873.645 | 1903.2 | 1930.652 | 1963.627 | 1997 | 2033.542 | 2072.175 | 2110.662 | 2149.067 | 2188.3 | 2228.373 | 2269.297 | 2311.084 | 2353.746 | 2397.296 | 2441.746 | 2487.109 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1763.1004 | 6.342 | 8.9456 | 12.2979 | 28.312 | 31.6542 | 28.1334 | 29.6684 | 27.5543 | 33.0934 | 33.489 | 36.6649 | 38.7572 | 38.6069 | 38.5207 | 39.3467 | 40.1844 | 41.0339 | 41.8954 | 42.7691 | 43.6551 | 44.5536 | 45.4647
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267 | 3267
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 | 6542 |  |  | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 881.5502 | 3.171 | 4.4728 | 6.1489 | 14.156 | 15.8271 | 14.0667 | 14.8342 | 13.7771 | 16.5467 | 16.7445 | 18.3324 | 19.3786 | 19.3035 | 19.2604 | 19.6734 | 20.0922 | 20.517 | 20.9477 | 21.3846 | 21.8276 | 22.2768 | 22.7324
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 881.5502 | 3.171 | 4.4728 | 6.1489 | 14.156 | 15.8271 | 14.0667 | 14.8342 | 13.7771 | 16.5467 | 16.7445 | 18.3324 | 19.3786 | 19.3035 | 19.2604 | 19.6734 | 20.0922 | 20.517 | 20.9477 | 21.3846 | 21.8276 | 22.2768 | 22.7324
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3027 | -3.9722 | -2.9637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3027 | -3.9722 | -2.9637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx1 | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx1 | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx2 | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx2 | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx3 | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.4457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx3 | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.4457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx4 | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.9598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx4 | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.9598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx5 | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx5 | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5214 | 17.6315 | 23.5127 | 23.2934 | 24.9284 | 24.2858 | 23.6127 | 23.9816 | 24.3559 | 24.7354 | 25.1204 | 25.5108 | 25.9067 | 26.3083 | 26.7155 | 27.1285 | 27.5474 | 27.9721 | 28.4029 | 28.8397 | 29.2827 | 29.732 | 30.1875
| Diversity Factor: 0 | [33 empty] | Econometric |  | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5214 | 17.6315 | 23.5127 | 23.2934 | 24.9284 | 24.2858 | 23.6127 | 23.9816 | 24.3559 | 24.7354 | 25.1204 | 25.5108 | 25.9067 | 26.3083 | 26.7155 | 27.1285 | 27.5474 | 27.9721 | 28.4029 | 28.8397 | 29.2827 | 29.732 | 30.1875
[35 empty] | Energy Efficiency |  | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.2148 | -9.9989 | -15.5525 | -16.5927 | -10.1947 | -7.9001 | -8.9785 | -8.7132 | -10.0586 | -7.6686 | -7.8558 | -6.6582 | -6.008 | -6.4847 | -6.9351 | -6.9351 | -6.9351 | -6.9351 | -6.9351 | -6.9351 | -6.9351 | -6.9351 | -6.9351
[35 empty] | Energy Efficiency |  | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.2148 | -9.9989 | -15.5525 | -16.5927 | -10.1947 | -7.9001 | -8.9785 | -8.7132 | -10.0586 | -7.6686 | -7.8558 | -6.6582 | -6.008 | -6.4847 | -6.9351 | -6.9351 | -6.9351 | -6.9351 | -6.9351 | -6.9351 | -6.9351 | -6.9351 | -6.9351
| 0 | [33 empty] | Solar PV |  | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.44599 | -0.48936 | -0.52374 | -0.55175 | -0.57767 | -0.55862 | -0.5675 | -0.43422 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.44599 | -0.48936 | -0.52374 | -0.55175 | -0.57767 | -0.55862 | -0.5675 | -0.43422 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011 | -0.52011
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [8 empty] | Same as Five Dock 33/11kV | [59 empty] | Same as Five Dock 33/11kV
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.99208 | 0.98422 | 0.97903 | 0.97644 | 0.97644 | 0.97644 | 0.97644 | 0.97644 | 0.97644 | 0.97644 | -0.792% | -0.792% | -0.528% | -0.264% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Croydon 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 | 0 | 0 | 0 | 1763.095 | 1764.751 | 1773.658 | 1785.903 | 1814.096 | 1845.622 | 1873.645 | 1903.2 | 1930.652 | 1963.627 | 1997 | 2033.542 | 2072.175 | 2110.662 | 2149.067 | 2188.3 | 2228.373 | 2269.297 | 2311.084 | 2353.746 | 2397.296 | 2441.746 | 2487.109
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 33.5915 | 33.623 | 33.7927 | 34.026 | 34.5632 | 35.1638 | 35.6977 | 36.2608 | 36.7839 | 37.4121 | 38.048 | 38.7442 | 39.4802 | 40.2135 | 40.9452 | 41.6927 | 42.4562 | 43.2359 | 44.0321 | 44.8449 | 45.6746 | 46.5215 | 47.3858
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 31.4707 | 31.4963 | 31.6497 | 31.8606 | 32.3461 | 32.8888 | 33.3713 | 33.88 | 34.3525 | 34.9199 | 35.4942 | 36.1229 | 36.7875 | 37.4495 | 38.11 | 38.7847 | 39.4737 | 40.1774 | 40.8957 | 41.6291 | 42.3777 | 43.1417 | 43.9213
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 11.7465 | 11.7682 | 11.8425 | 11.9446 | 12.1797 | 12.4426 | 12.6762 | 12.9226 | 13.1515 | 13.4263 | 13.7044 | 14.0089 | 14.3308 | 14.6514 | 14.9713 | 15.2981 | 15.6318 | 15.9726 | 16.3205 | 16.6757 | 17.0383 | 17.4083 | 17.7858
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0.93687 | 0.93675 | 0.93658 | 0.93636 | 0.93585 | 0.9353 | 0.93483 | 0.93434 | 0.9339 | 0.93339 | 0.93288 | 0.93234 | 0.93179 | 0.93127 | 0.93075 | 0.93025 | 0.92975 | 0.92926 | 0.92877 | 0.92829 | 0.92782 | 0.92735 | 0.92689
0.93997 | Diversity Factor: 0.94 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 11.7465 | 11.7682 | 11.8425 | 11.9446 | 12.1797 | 12.4426 | 12.6762 | 12.9226 | 13.1515 | 13.4263 | 13.7044 | 14.0089 | 14.3308 | 14.6514 | 14.9713 | 15.2981 | 15.6318 | 15.9726 | 16.3205 | 16.6757 | 17.0383 | 17.4083 | 17.7858
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0.93687 | 0.93675 | 0.93658 | 0.93636 | 0.93585 | 0.9353 | 0.93483 | 0.93434 | 0.9339 | 0.93339 | 0.93288 | 0.93234 | 0.93179 | 0.93127 | 0.93075 | 0.93025 | 0.92975 | 0.92926 | 0.92877 | 0.92829 | 0.92782 | 0.92735 | 0.92689
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Drummoyne 132_11kV
| Drummoyne 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 2391 | 2687 | 2916 | 3049 | 2563 | 2663 | 2302 |  | 2405.528 | 2342.017 | 2316.693 | 2326.188 | 2364.272 | 2399.43 | 2459.781 | 2522.503 | 2578.481 | 2636.653 | 2692.615 | 2756.485 | 2821.17 | 2890.278 | 2962.459 | 3034.677 | 3107.118 | 3180.945 | 3256.177 | 3332.834 | 3410.936 | 3490.502 | 3571.552 | 3654.108 | 3738.189 |  |  | Total | 0 | 0 | 0 | -1.1348 | -0.0099724 | -0.025193 | -0.53064 | -4.8145 | -5.4118 | 12.3866 | 28.1458 | 38.0843 | 35.1581 | 60.3509 | 62.7215 | 55.9785 | 58.1722 | 55.9617 | 63.8705 | 64.6843 | 69.1085 | 72.181 | 72.2177 | 72.4407 | 73.8269 | 75.2323 | 76.6571 | 78.1016 | 79.566 | 81.0505 | 82.5555 | 84.0812
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2947 |  | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947 | 2947
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 5358 |  | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 | 5358 |  |  | Drummoyne 132_11kV Tx1 | 0 | 0 | 0 | -0.70546 | -0.0061997 | -0.015662 | -0.32989 | 7.0069 | -3.3644 | 7.7005 | 17.4977 | 23.6763 | 21.8571 | 37.519 | 38.9927 | 34.8007 | 36.1645 | 34.7903 | 39.707 | 40.2129 | 42.9634 | 44.8735 | 44.8963 | 45.0349 | 45.8968 | 46.7705 | 47.6562 | 48.5542 | 49.4646 | 50.3875 | 51.3231 | 52.2716
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Drummoyne 132_11kV Tx2 | 0 | 0 | 0 | -0.4293 | -0.0037728 | -0.0095312 | -0.20075 | -11.8214 | -2.0474 | 4.6861 | 10.6481 | 14.4081 | 13.301 | 22.8319 | 23.7288 | 21.1778 | 22.0077 | 21.1714 | 24.1635 | 24.4713 | 26.1451 | 27.3075 | 27.3214 | 27.4057 | 27.9302 | 28.4619 | 29.0009 | 29.5474 | 30.1014 | 30.663 | 31.2323 | 31.8095
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Drummoyne 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.29828 | -1.8201 | -2.5283 | -5.2218 | -3.8553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Drummoyne 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.18152 | -1.1076 | -1.5386 | -3.1777 | -2.3461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6973. Drummoyne ZD 2012 | Drummoyne 132_11kV Tx1 | Drummoyne 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6973. Drummoyne ZD 2012 | Drummoyne 132_11kV Tx2 | Drummoyne 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Drummoyne 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.3565 | 40.6467 | 55.3285 | 51.6788 | 56.21 | 53.9622 | 51.633 | 52.405 | 53.1878 | 53.9814 | 54.786 | 55.6017 | 56.4288 | 57.2672 | 58.1173 | 58.9791 | 59.8528 | 60.7386 | 61.6366 | 62.547 | 63.4699 | 64.4055 | 65.354
| Diversity Factor: 0 | [33 empty] | Econometric |  | Drummoyne 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9963 | 24.7353 | 33.6698 | 31.4488 | 34.2062 | 32.8383 | 31.4209 | 31.8907 | 32.3671 | 32.85 | 33.3396 | 33.8361 | 34.3393 | 34.8496 | 35.3669 | 35.8913 | 36.423 | 36.9621 | 37.5085 | 38.0625 | 38.6242 | 39.1935 | 39.7707
[35 empty] | Energy Efficiency |  | Drummoyne 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4882 | -1.3126 | -10.8659 | -17.6399 | -27.4895 | -29.4978 | -18.352 | -14.6416 | -16.4991 | -15.9857 | -18.0922 | -13.9691 | -14.2677 | -12.333 | -11.2499 | -12.0656 | -12.7771 | -12.7771 | -12.7771 | -12.7771 | -12.7771 | -12.7771 | -12.7771 | -12.7771 | -12.7771
[35 empty] | Energy Efficiency |  | Drummoyne 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5142 | -0.79875 | -6.6124 | -10.7347 | -16.7286 | -17.9507 | -11.168 | -8.91 | -10.0404 | -9.728 | -11.0099 | -8.5008 | -8.6825 | -7.5052 | -6.8461 | -7.3425 | -7.7754 | -7.7754 | -7.7754 | -7.7754 | -7.7754 | -7.7754 | -7.7754 | -7.7754 | -7.7754
| 0 | [33 empty] | Solar PV |  | Drummoyne 132_11kV Tx1 | 0 | 0 | 0 | -0.70546 | -0.0061997 | -0.015662 | -0.32989 | -0.20664 | -0.23178 | -0.26177 | -0.28723 | -0.30741 | -0.32385 | -0.33906 | -0.32788 | -0.33309 | -0.25487 | -0.30528 | -0.30528 | -0.30528 | -0.30528 | -0.30528 | -0.30528 | -0.30528 | -0.30528 | -0.30528 | -0.30528 | -0.30528 | -0.30528 | -0.30528 | -0.30528 | -0.30528
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Drummoyne 132_11kV Tx2 | 0 | 0 | 0 | -0.4293 | -0.0037728 | -0.0095312 | -0.20075 | -0.12575 | -0.14105 | -0.1593 | -0.17479 | -0.18707 | -0.19708 | -0.20634 | -0.19953 | -0.2027 | -0.1551 | -0.18578 | -0.18578 | -0.18578 | -0.18578 | -0.18578 | -0.18578 | -0.18578 | -0.18578 | -0.18578 | -0.18578 | -0.18578 | -0.18578 | -0.18578 | -0.18578 | -0.18578
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 3.126% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.97585 | 0.95228 | 0.93695 | 0.92941 | 0.92941 | 0.92941 | 0.92941 | 0.92941 | 0.92941 | 0.92941 | -2.415% | -2.415% | -1.61% | -0.805% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Drummoyne 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 2302 | 2470 | 2405.528 | 2342.017 | 2316.693 | 2326.188 | 2364.272 | 2399.43 | 2459.781 | 2522.503 | 2578.481 | 2636.653 | 2692.615 | 2756.485 | 2821.17 | 2890.278 | 2962.459 | 3034.677 | 3107.118 | 3180.945 | 3256.177 | 3332.834 | 3410.936 | 3490.502 | 3571.552 | 3654.108 | 3738.189
|  |  |  | Apparent Power |  |  | MVA | 43.859 |  | 45.8315 | 44.6214 | 44.1389 | 44.3198 | 45.0454 | 45.7153 | 46.8651 | 48.0601 | 49.1267 | 50.235 | 51.3012 | 52.5181 | 53.7505 | 55.0672 | 56.4424 | 57.8184 | 59.1985 | 60.6051 | 62.0385 | 63.499 | 64.9871 | 66.503 | 68.0472 | 69.6201 | 71.2221
|  |  |  | Real Power |  |  | MW | 40.9913 | 43.9829 | 42.8349 | 41.7039 | 41.253 | 41.422 | 42.1002 | 42.7263 | 43.8009 | 44.9178 | 45.9146 | 46.9504 | 47.947 | 49.0843 | 50.2361 | 51.4667 | 52.752 | 54.038 | 55.3279 | 56.6426 | 57.9822 | 59.3472 | 60.738 | 62.1548 | 63.598 | 65.0681 | 66.5653
|  |  |  | Reactive Power |  |  | MVAr | 15.5988 |  | 16.3003 | 15.8699 | 15.6983 | 15.7627 | 16.0207 | 16.259 | 16.6679 | 17.0929 | 17.4722 | 17.8664 | 18.2457 | 18.6784 | 19.1168 | 19.585 | 20.0742 | 20.5635 | 21.0544 | 21.5547 | 22.0644 | 22.5839 | 23.1131 | 23.6523 | 24.2015 | 24.7609 | 25.3306
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.93462 |  | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462
0.87372 | Diversity Factor: 0.87 | Uncompensated |  | Reactive Power |  |  | MVAr | 15.5988 | 16.7372 | 16.3003 | 15.8699 | 15.6983 | 15.7627 | 16.0207 | 16.259 | 16.6679 | 17.0929 | 17.4722 | 17.8664 | 18.2457 | 18.6784 | 19.1168 | 19.585 | 20.0742 | 20.5635 | 21.0544 | 21.5547 | 22.0644 | 22.5839 | 23.1131 | 23.6523 | 24.2015 | 24.7609 | 25.3306
|  |  |  | PF |  |  |  | 0.93462 |  | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462 | 0.93462
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Five Dock 33_11kV
| Five Dock 33_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone decommissioned |  | 2016-10-31
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 1451 | 1540 | 1763 | 2003 | 1576 | 1718 | 1740 |  | 1788.041 | 1771.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | 0 | 0 | 160 | -1.731 | -0.0083978 | -1.1652 | -0.5763 | 65.8394 | -2.5234 | -1761.9846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2165 |  | 2165 | 2165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 3392 |  | 3392 | 3392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Five Dock 33_11kV Tx1 | 0 | 0 | 0 | -0.13383 | -0.00064927 | -0.090086 | -0.044556 | -0.32167 | -0.1951 | -136.2257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Five Dock 33_11kV Tx2 | 0 | 100 | 0 | -0.52751 | -0.0025592 | -0.35508 | -0.17562 | -1.2679 | -0.76899 | -536.9479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Five Dock 33_11kV Tx3 | 0 | 180 | 0 | -0.53727 | -0.0026065 | -0.36166 | -0.17887 | 68.7086 | -0.78324 | -546.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  | Five Dock 33_11kV Tx4 | 0 | 75 | 160 | -0.53239 | -0.0025829 | -0.35837 | -0.17725 | -1.2796 | -0.77611 | -541.9197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  | Five Dock 33_11kV Tx5 | 0 | -355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Five Dock 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Five Dock 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Five Dock 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Five Dock 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6127. 11kV works required to retire Transformer No.5 and associated Switchgear at Five Dock Zone | Five Dock 33_11kV Tx5 | Five Dock 33_11kV Tx2 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6127. 11kV works required to retire Transformer No.5 and associated Switchgear at Five Dock Zone | Five Dock 33_11kV Tx5 | Five Dock 33_11kV Tx3 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6127. 11kV works required to retire Transformer No.5 and associated Switchgear at Five Dock Zone | Five Dock 33_11kV Tx5 | Five Dock 33_11kV Tx4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6428. Leichhardt to Five Dock load transfer of 4MVA | Leichhardt 33_11kV Tx3 | Five Dock 33_11kV Tx4 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 7090. Burwood Zone Development 2012 | Burwood 132_11kV Tx2 | Five Dock 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx1 | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx1 | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx2 | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx2 | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx3 | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.4457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx3 | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.4457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx4 | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.9598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx4 | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.9598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx5 | Croydon 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Five Dock 33_11kV Tx5 | Croydon 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Five Dock 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Five Dock 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Econometric |  | Five Dock 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Five Dock 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Energy Efficiency |  | Five Dock 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.26723 | -0.13404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Energy Efficiency |  | Five Dock 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0533 | -0.52832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Five Dock 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0728 | -0.5381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Energy Efficiency |  | Five Dock 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0631 | -0.53321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Five Dock 33_11kV Tx1 | 0 | 0 | 0 | -0.13383 | -0.00064927 | -0.090086 | -0.044556 | -0.054438 | -0.061061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Solar PV |  | Five Dock 33_11kV Tx2 | 0 | 0 | 0 | -0.52751 | -0.0025592 | -0.35508 | -0.17562 | -0.21457 | -0.24068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Five Dock 33_11kV Tx3 | 0 | 0 | 0 | -0.53727 | -0.0026065 | -0.36166 | -0.17887 | -0.21855 | -0.24513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Five Dock 33_11kV Tx4 | 0 | 0 | 0 | -0.53239 | -0.0025829 | -0.35837 | -0.17725 | -0.21656 | -0.24291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Five Dock 33_11kV Tx5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weather Correction and Public Holiday Factors | [8 empty] | 0: Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 5.803% |  | 0: 7 year ROG ok | [35 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.99208 | 0.98422 | 0.97903 | 0.97644 | 0.97644 | 0.97644 | 0.97644 | 0.97644 | 0.97644 | 0.97644 | -0.792% | -0.792% | -0.528% | -0.264% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Five Dock 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1740 | 1736 | 1788.041 | 1771.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 33.1515 |  | 34.0668 | 33.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 31.0741 | 31.0027 | 31.9167 | 31.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 11.5506 |  | 11.9108 | 11.7996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.93734 |  | 0.93689 | 0.93689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.9654 | Diversity Factor: 0.97 | Uncompensated |  | Reactive Power |  |  | MVAr | 11.5506 | 11.5241 | 11.9108 | 11.7996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.93734 |  | 0.93689 | 0.93689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Flemington 132_11kV
| Flemington 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 4360 | 4517 | 4503 | 4680 | 4123 | 4413 | 4117 |  | 4404.083 | 4215.735 | 4090.093 | 4031.536 | 4027.108 | 4043.523 | 4098.41 | 4170.555 | 4233.707 | 4299.993 | 4352.837 | 4420.311 | 4487.327 | 4565.897 | 4650.445 | 4733.435 | 4813.427 | 4894.747 | 4977.413 | 5061.44 | 5146.847 | 5233.65 | 5321.866 | 5411.515 | 5502.612 |  |  | Total | 192.6 | 131.4 | -221.7 | 231.6696 | -7.2211 | 308.949 | -4.7469 | 243.5788 | -33.6173 | -26.8997 | -10.6578 | -4.4275 | 16.4146 | 54.887 | 72.1449 | 63.1517 | 66.2868 | 52.8432 | 67.4743 | 67.0156 | 78.5702 | 84.5483 | 82.9897 | 79.9918 | 81.3204 | 82.6656 | 84.0276 | 85.4066 | 86.8029 | 88.2167 | 89.6481 | 91.0974
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 5180 |  | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 8000 |  | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 |  |  | Flemington 132_11kV Tx1 | 43.2 | 0 | 58.5 | -1.3834 | -1.5781 | -66.4972 | -101.0374 | 178.1555 | -7.3466 | -5.8785 | -2.3291 | -0.96756 | 3.5872 | 11.9948 | 15.7662 | 13.8009 | 14.486 | 11.5481 | 14.7455 | 14.6453 | 17.1704 | 18.4768 | 18.1362 | 17.4811 | 17.7714 | 18.0654 | 18.363 | 18.6644 | 18.9695 | 19.2785 | 19.5913 | 19.908
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Flemington 132_11kV Tx2 | 54 | 38.7 | 0 | -1.7704 | -2.0195 | 247.084 | -1.3275 | 35.7931 | -9.4015 | -7.5228 | -2.9806 | -1.2382 | 4.5906 | 15.3498 | 20.1763 | 17.6612 | 18.538 | 14.7783 | 18.8701 | 18.7418 | 21.9732 | 23.645 | 23.2091 | 22.3707 | 22.7423 | 23.1185 | 23.4994 | 23.8851 | 24.2756 | 24.6709 | 25.0713 | 25.4766
| Transformer Loads | [35 empty] | Flemington 132_11kV Tx3 | 95.4 | 47.7 | 28.8 | -1.6088 | -1.8351 | 130.0589 | 98.7936 | 24.6335 | -8.5434 | -6.8362 | -2.7085 | -1.1252 | 4.1716 | 13.9488 | 18.3347 | 16.0492 | 16.846 | 13.4294 | 17.1477 | 17.0312 | 19.9676 | 21.4869 | 21.0908 | 20.3289 | 20.6665 | 21.0084 | 21.3545 | 21.705 | 22.0599 | 22.4191 | 22.7829 | 23.1513
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [22 empty] | Flemington 132_11kV Tx4 | 0 | 45 | -309 | 236.4322 | -1.7884 | -1.6968 | -1.1756 | 4.9966 | -8.3258 | -6.6621 | -2.6395 | -1.0965 | 4.0653 | 13.5935 | 17.8677 | 15.6404 | 16.4169 | 13.0874 | 16.711 | 16.5974 | 19.459 | 20.9396 | 20.5536 | 19.8111 | 20.1401 | 20.4733 | 20.8106 | 21.1522 | 21.498 | 21.8481 | 22.2026 | 22.5616
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Flemington 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.99906 | -3.9181 | -4.5999 | -4.5951 | -4.1528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Flemington 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2785 | -5.014 | -5.8865 | -5.8805 | -5.3144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Flemington 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1618 | -4.5563 | -5.3493 | -5.3437 | -4.8293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Flemington 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1322 | -4.4403 | -5.213 | -5.2076 | -4.7063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 5858. Auburn Zone Development - Stage 1 | Auburn 33_11kV Tx3 | Flemington 132_11kV Tx4 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 5858. Auburn Zone Development - Stage 1 | Flemington 132_11kV Tx4 | Auburn 33_11kV Tx3 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6269. Flemington Minor Zone Development - Panels 15, 16 and 12-19-21 Feeders. RAILWAY CROSSING INVOLVED | Flemington 132_11kV Tx2 | Flemington 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6269. Flemington Minor Zone Development - Panels 15, 16 and 12-19-21 Feeders. RAILWAY CROSSING INVOLVED | Flemington 132_11kV Tx4 | Lidcombe 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6452. 11kV Feeder Transfers to new Switchgear at Auburn Zone. | Flemington 132_11kV Tx4 | Auburn 33_11kV Tx3 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6452. 11kV Feeder Transfers to new Switchgear at Auburn Zone. | Homebush Bay 132_11kV Tx2 | Flemington 132_11kV Tx4 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6639. Lidcombe to Flemington 11kV Load Transfer | Flemington 132_11kV Tx3 | Flemington 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6639. Lidcombe to Flemington 11kV Load Transfer | Lidcombe 33_11kV Tx1 | Flemington 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6639. Lidcombe to Flemington 11kV Load Transfer | Lidcombe 33_11kV Tx3 | Flemington 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6639. Lidcombe to Flemington 11kV Load Transfer | Lidcombe 33_11kV Tx3 | Flemington 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7056. Relieve PA39 of Flemington Zone | Flemington 132_11kV Tx3 | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2004293. Est Chamber S.8804 "John Hastings" for Winton Associates - Lidcombe. |  | Flemington 132_11kV Tx3 | 74.7 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2004469. Est Kiosk S.8879 "Figtree Olympic" for Grant Constructions - Homebush Bay. Re-Sent from 27/2/04. |  | Flemington 132_11kV Tx2 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2005186. Est S.8916 "Parramatta Telopia No6" & S.8917 "Parramatta Telopia No7" for Macquarie Goodman - Homebush West. Partially supersedes HV Con 2004_096. |  | Flemington 132_11kV Tx2 | 18 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2005404. Establish S.6419 Parkview Australia No.3, New load customer sub, Bovis lend lease, Flemington Zone |  | Flemington 132_11kV Tx3 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2005541. Establish S.35226 Olympic Herb Elliot, customer sub, Flemington Zone |  | Flemington 132_11kV Tx2 | 0 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2006063. Establish customer substation S.35058 Urhig Carter (2x1500kVA) |  | Flemington 132_11kV Tx1 | 43.2 | 0 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2006191. Establishment of Customer Sub, S.35345 Millenium Court No.4. 18 Millennium Court Silverwater. |  | Flemington 132_11kV Tx4 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2006234. Establishment of S.35391 Uhrig Carter No.2, S.35433 Uhrig Carter No.3 and S.35434 Uhrig Carter No.4, Uhrig Road Flemington |  | Flemington 132_11kV Tx1 | 0 | 0 | 51.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2007276. Establishment of S.35661 Shane Gould Ave No. 1, Site 31 & 32/Shane Gould Ave, Sydney Olympic Park |  | Flemington 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2008197. New load at S.6939 Figtree DSS (Fujitsu). |  | Flemington 132_11kV Tx3 | 0 | 21.6 | 28.8 | 0 | 0 | 55.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2009349. Establishment of S.46728 Figtree Australia No. 4, 4 Figtree Drive, Homebush Bay |  | Flemington 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2009349. Establishment of S.46728 Figtree Australia No. 4, 4 Figtree Drive, Homebush Bay | Flemington 132_11kV Tx1 | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2009349. Establishment of S.46728 Figtree Australia No. 4, 4 Figtree Drive, Homebush Bay | Flemington 132_11kV Tx3 | Flemington 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2011166. Establishment of 5 x Kiosks; S.49740 Centenary Park No 1; S.49741 Centenary Park No 2; S.49742 Centenary Park No 3; S.49743 Centenary Park No. 4; and S.49744 Centenary Park No 5, 78 Marlborough Rd, Homebush Bay |  | Flemington 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2011166. Establishment of 5 x Kiosks; S.49740 Centenary Park No 1; S.49741 Centenary Park No 2; S.49742 Centenary Park No 3; S.49743 Centenary Park No. 4; and S.49744 Centenary Park No 5, 78 Marlborough Rd, Homebush Bay | Flemington 132_11kV Tx1 | Flemington 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013041. Establishment of S.63390 Carter Hill No 5, 32 Carter Street, Lidcombe |  | Flemington 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013048. Establishment of 2 x Kiosks: S.63435 Herb Elliott Showground No 2 and S.63436 Herb Elliott Showground No 3, 7 Herb Elliott Ave, Sydney Olympic Park |  | Flemington 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Flemington 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9169 | 13.7724 | 20.0051 | 20.497 | 21.7957 | 21.2156 | 20.6168 | 20.8796 | 21.1457 | 21.4152 | 21.688 | 21.9643 | 22.244 | 22.5272 | 22.8139 | 23.1043 | 23.3983 | 23.6959 | 23.9973 | 24.3024 | 24.6114 | 24.9242 | 25.2409
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG | [24 empty] | Econometric |  | Flemington 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8517 | 17.6247 | 25.6008 | 26.2302 | 27.8923 | 27.1499 | 26.3836 | 26.7199 | 27.0605 | 27.4053 | 27.7545 | 28.108 | 28.4659 | 28.8283 | 29.1953 | 29.5669 | 29.9431 | 30.324 | 30.7096 | 31.1001 | 31.4955 | 31.8958 | 32.3011
[10 empty] | ROG Justification | [24 empty] | Econometric |  | Flemington 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0438 | 16.016 | 23.2641 | 23.8361 | 25.3465 | 24.6718 | 23.9755 | 24.2811 | 24.5906 | 24.9039 | 25.2212 | 25.5425 | 25.8678 | 26.1971 | 26.5306 | 26.8682 | 27.2101 | 27.5562 | 27.9067 | 28.2615 | 28.6208 | 28.9846 | 29.3529
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 4.255% |  | 7 year ROG ok | [24 empty] | Econometric |  | Flemington 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8389 | 15.6081 | 22.6715 | 23.229 | 24.7008 | 24.0434 | 23.3648 | 23.6626 | 23.9642 | 24.2696 | 24.5788 | 24.8919 | 25.2089 | 25.5298 | 25.8548 | 26.1838 | 26.517 | 26.8543 | 27.1959 | 27.5417 | 27.8918 | 28.2463 | 28.6053 | 7 year ROG ok
[35 empty] | Energy Efficiency |  | Flemington 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0571 | -2.1517 | -6.7535 | -9.9241 | -15.1264 | -15.1258 | -7.9331 | -3.6431 | -4.981 | -4.9896 | -7.9159 | -4.9879 | -5.361 | -3.1122 | -2.0854 | -2.7093 | -3.6512 | -3.6512 | -3.6512 | -3.6512 | -3.6512 | -3.6512 | -3.6512 | -3.6512 | -3.6512
[35 empty] | Energy Efficiency |  | Flemington 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.4716 | -2.7536 | -8.6426 | -12.6999 | -19.3575 | -19.3567 | -10.1521 | -4.6621 | -6.3742 | -6.3852 | -10.1301 | -6.3831 | -6.8606 | -3.9827 | -2.6688 | -3.4671 | -4.6724 | -4.6724 | -4.6724 | -4.6724 | -4.6724 | -4.6724 | -4.6724 | -4.6724 | -4.6724
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | Energy Efficiency |  | Flemington 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8809 | -2.5022 | -7.8538 | -11.5408 | -17.5906 | -17.5899 | -9.2255 | -4.2366 | -5.7924 | -5.8024 | -9.2055 | -5.8005 | -6.2344 | -3.6192 | -2.4252 | -3.1506 | -4.246 | -4.246 | -4.246 | -4.246 | -4.246 | -4.246 | -4.246 | -4.246 | -4.246
0.96487 | 0.93097 | 0.90917 | 0.89852 | 0.89852 | 0.89852 | 0.89852 | 0.89852 | 0.89852 | 0.89852 | -3.513% | -3.513% | -2.342% | -1.171% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Energy Efficiency |  | Flemington 132_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7311 | -2.4385 | -7.6537 | -11.2468 | -17.1426 | -17.1419 | -8.9905 | -4.1287 | -5.6449 | -5.6546 | -8.971 | -5.6528 | -6.0756 | -3.527 | -2.3634 | -3.0704 | -4.1378 | -4.1378 | -4.1378 | -4.1378 | -4.1378 | -4.1378 | -4.1378 | -4.1378 | -4.1378
[35 empty] | Solar PV |  | Flemington 132_11kV Tx1 | 0 | 0 | 0 | -1.3834 | -1.5781 | -1.4972 | -1.0374 | -1.1383 | -1.2768 | -1.442 | -1.5823 | -1.6934 | -1.784 | -1.8678 | -1.8062 | -1.8349 | -1.404 | -1.6817 | -1.6817 | -1.6817 | -1.6817 | -1.6817 | -1.6817 | -1.6817 | -1.6817 | -1.6817 | -1.6817 | -1.6817 | -1.6817 | -1.6817 | -1.6817 | -1.6817
2: Substation Load Detail | Solar PV |  | Flemington 132_11kV Tx2 | 0 | 0 | 0 | -1.7704 | -2.0195 | -1.916 | -1.3275 | -1.4568 | -1.634 | -1.8454 | -2.0249 | -2.1671 | -2.283 | -2.3903 | -2.3115 | -2.3482 | -1.7967 | -2.1521 | -2.1521 | -2.1521 | -2.1521 | -2.1521 | -2.1521 | -2.1521 | -2.1521 | -2.1521 | -2.1521 | -2.1521 | -2.1521 | -2.1521 | -2.1521 | -2.1521
[35 empty] | Solar PV |  | Flemington 132_11kV Tx3 | 0 | 0 | 0 | -1.6088 | -1.8351 | -1.7411 | -1.2064 | -1.3238 | -1.4848 | -1.677 | -1.8401 | -1.9693 | -2.0747 | -2.1721 | -2.1005 | -2.1339 | -1.6327 | -1.9557 | -1.9557 | -1.9557 | -1.9557 | -1.9557 | -1.9557 | -1.9557 | -1.9557 | -1.9557 | -1.9557 | -1.9557 | -1.9557 | -1.9557 | -1.9557 | -1.9557
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 | Solar PV |  | Flemington 132_11kV Tx4 | 0 | 0 | 0 | -1.5678 | -1.7884 | -1.6968 | -1.1756 | -1.2901 | -1.447 | -1.6342 | -1.7932 | -1.9192 | -2.0218 | -2.1168 | -2.047 | -2.0795 | -1.5911 | -1.9059 | -1.9059 | -1.9059 | -1.9059 | -1.9059 | -1.9059 | -1.9059 | -1.9059 | -1.9059 | -1.9059 | -1.9059 | -1.9059 | -1.9059 | -1.9059 | -1.9059
1 | Flemington 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 4117 | 4312 | 4404.083 | 4215.735 | 4090.093 | 4031.536 | 4027.108 | 4043.523 | 4098.41 | 4170.555 | 4233.707 | 4299.993 | 4352.837 | 4420.311 | 4487.327 | 4565.897 | 4650.445 | 4733.435 | 4813.427 | 4894.747 | 4977.413 | 5061.44 | 5146.847 | 5233.65 | 5321.866 | 5411.515 | 5502.612
|  |  |  | Apparent Power |  |  | MVA | 78.4394 |  | 83.909 | 80.3205 | 77.9267 | 76.8111 | 76.7267 | 77.0395 | 78.0852 | 79.4597 | 80.6629 | 81.9259 | 82.9327 | 84.2182 | 85.4951 | 86.992 | 88.6029 | 90.184 | 91.7081 | 93.2575 | 94.8324 | 96.4334 | 98.0606 | 99.7144 | 101.3951 | 103.1032 | 104.8388
|  |  |  | Real Power |  |  | MW | 72.6913 | 76.1343 | 77.7602 | 74.4346 | 72.2163 | 71.1823 | 71.1042 | 71.394 | 72.3631 | 73.6369 | 74.7519 | 75.9223 | 76.8553 | 78.0467 | 79.23 | 80.6172 | 82.11 | 83.5753 | 84.9877 | 86.4235 | 87.8831 | 89.3667 | 90.8747 | 92.4073 | 93.9649 | 95.5478 | 97.1562
|  |  |  | Reactive Power |  |  | MVAr | 29.4739 |  | 31.5291 | 30.1807 | 29.2812 | 28.862 | 28.8303 | 28.9478 | 29.3408 | 29.8573 | 30.3094 | 30.7839 | 31.1623 | 31.6453 | 32.1251 | 32.6876 | 33.2929 | 33.887 | 34.4596 | 35.0418 | 35.6336 | 36.2352 | 36.8466 | 37.468 | 38.0996 | 38.7414 | 39.3936
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.92672 |  | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672
0.94965 | Diversity Factor: 0.95 | Uncompensated |  | Reactive Power |  |  | MVAr | 29.4739 | 30.8699 | 31.5291 | 30.1807 | 29.2812 | 28.862 | 28.8303 | 28.9478 | 29.3408 | 29.8573 | 30.3094 | 30.7839 | 31.1623 | 31.6453 | 32.1251 | 32.6876 | 33.2929 | 33.887 | 34.4596 | 35.0418 | 35.6336 | 36.2352 | 36.8466 | 37.468 | 38.0996 | 38.7414 | 39.3936
|  |  |  | PF |  |  |  | 0.92672 |  | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672 | 0.92672
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Homebush Bay 132_11kV
| Homebush Bay 132_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 2799 | 2634 | 2401 | 2505 | 2253 | 2407 | 2263 |  | 2391.805 | 2224.799 | 2182.748 | 2160.445 | 2152.645 | 2163.817 | 2194.711 | 2233.681 | 2267.626 | 2303.616 | 2332.713 | 2369.103 | 2405.316 | 2447.303 | 2492.301 | 2536.581 | 2579.43 | 2622.99 | 2667.271 | 2712.281 | 2758.03 | 2804.526 | 2851.78 | 2899.799 | 2948.595 |  |  | Total | 0 | 0 | -140 | -27.696 | -108.4818 | 28.882 | -1.825 | 103.1395 | -137.0502 | -23.4757 | -13.1907 | -7.8 | 11.1718 | 30.8936 | 38.9704 | 33.9451 | 35.9896 | 29.097 | 36.3899 | 36.2138 | 41.9865 | 44.9984 | 44.2797 | 42.8486 | 43.5603 | 44.2809 | 45.0103 | 45.7488 | 46.4965 | 47.2534 | 48.0196 | 48.7954
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 2791 |  | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791 | 2791
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 5601 |  | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 | 5601 |  |  | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | -12.6601 | -3.8771 | 29.489 | -30.8342 | 64.2859 | -122.3649 | -10.7309 | -6.0296 | -3.5654 | 5.1067 | 14.1217 | 17.8137 | 15.5166 | 16.4512 | 13.3005 | 16.6341 | 16.5536 | 19.1923 | 20.5691 | 20.2406 | 19.5864 | 19.9118 | 20.2411 | 20.5746 | 20.9122 | 21.2539 | 21.5999 | 21.9502 | 22.3048
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Homebush Bay 132_11kV Tx2 | 0 | 0 | -140 | -15.0359 | -104.6047 | -0.60693 | 29.0092 | 38.8536 | -14.6853 | -12.7447 | -7.1611 | -4.2346 | 6.0651 | 16.7719 | 21.1567 | 18.4285 | 19.5385 | 15.7965 | 19.7558 | 19.6602 | 22.7941 | 24.4293 | 24.0391 | 23.2622 | 23.6486 | 24.0397 | 24.4358 | 24.8367 | 25.2426 | 25.6535 | 26.0695 | 26.4906
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0113 | -8.2132 | -9.6527 | -9.6272 | -9.0445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Homebush Bay 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3887 | -9.7545 | -11.4642 | -11.434 | -10.7419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6452. 11kV Feeder Transfers to new Switchgear at Auburn Zone. | Homebush Bay 132_11kV Tx2 | Auburn 33_11kV Tx3 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6452. 11kV Feeder Transfers to new Switchgear at Auburn Zone. | Homebush Bay 132_11kV Tx2 | Auburn 33_11kV Tx5 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6452. 11kV Feeder Transfers to new Switchgear at Auburn Zone. | Homebush Bay 132_11kV Tx2 | Flemington 132_11kV Tx4 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6531. North Concord Zone Development | Concord 33_11kV Tx3 | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6869. Newington 11kV Rearrangement (Smart Grid Smart City Energy Resource Management) | Homebush Bay 132_11kV Tx2 | Auburn 33_11kV Tx5 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 7001. Auburn North Zone Development | Homebush Bay 132_11kV Tx1 | Homebush Bay 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 7056. Relieve PA39 of Flemington Zone | Flemington 132_11kV Tx3 | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2009349. Establishment of S.46728 Figtree Australia No. 4, 4 Figtree Drive, Homebush Bay | Flemington 132_11kV Tx1 | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011752. Stage 1 - Establishment of S.61507 Day Egerton Temp No 1 and S.61508 Day Egerton Temp No 2, 8-14 Egerton Street, Silverwater |  | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.25 | -110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011752. Stage 1 - Establishment of S.61507 Day Egerton Temp No 1 and S.61508 Day Egerton Temp No 2, 8-14 Egerton Street, Silverwater |  | Homebush Bay 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2012482. Est 3 kiosk subs S.36088 Australia Figtree No.1, S.49792 Australia Figtree No.2 and S.49793 Australia Figtree No.3. decommission S.46780 |  | Homebush Bay 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2013084. Load decrease at HVC S.6648 Fariola Egerton. Dummy HVCon number created to allow for negative spot load in forecast. Discovered HVC taking no load as of Mar 2012 (25/2/13 KG) DNP7001 was issued to fix but was basically co |  | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | -135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0851 | 16.2535 | 23.6871 | 23.4494 | 25.1443 | 24.3005 | 23.4318 | 23.7266 | 24.025 | 24.3272 | 24.6331 | 24.9428 | 25.2563 | 25.5738 | 25.8951 | 26.2205 | 26.5498 | 26.8833 | 27.2208 | 27.5626 | 27.9086 | 28.2589 | 28.6135
[35 empty] | Econometric |  | Homebush Bay 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6024 | 19.3038 | 28.1324 | 27.8501 | 29.863 | 28.8609 | 27.8291 | 28.1793 | 28.5338 | 28.8926 | 29.2559 | 29.6238 | 29.9961 | 30.3731 | 30.7548 | 31.1412 | 31.5324 | 31.9284 | 32.3293 | 32.7352 | 33.1461 | 33.5621 | 33.9833
| 0 | [33 empty] | Energy Efficiency |  | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2384 | -2.2287 | -6.9915 | -10.2728 | -15.6577 | -15.6559 | -8.2095 | -3.7666 | -5.1517 | -5.1609 | -8.1918 | -5.1604 | -5.5468 | -3.2177 | -2.1545 | -2.8004 | -3.7759 | -3.7759 | -3.7759 | -3.7759 | -3.7759 | -3.7759 | -3.7759 | -3.7759 | -3.7759
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Homebush Bay 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.2215 | -2.647 | -8.3036 | -12.2007 | -18.5961 | -18.594 | -9.7502 | -4.4734 | -6.1185 | -6.1295 | -9.7292 | -6.1288 | -6.5877 | -3.8216 | -2.5588 | -3.326 | -4.4846 | -4.4846 | -4.4846 | -4.4846 | -4.4846 | -4.4846 | -4.4846 | -4.4846 | -4.4846
[35 empty] | Solar PV |  | Homebush Bay 132_11kV Tx1 | 0 | 0 | 0 | -12.6601 | -3.8771 | -0.51103 | -0.8342 | -1.7144 | -1.923 | -2.1718 | -2.383 | -2.5504 | -2.6868 | -2.813 | -2.7203 | -2.7635 | -2.1145 | -2.5327 | -2.5327 | -2.5327 | -2.5327 | -2.5327 | -2.5327 | -2.5327 | -2.5327 | -2.5327 | -2.5327 | -2.5327 | -2.5327 | -2.5327 | -2.5327 | -2.5327
[35 empty] | Solar PV |  | Homebush Bay 132_11kV Tx2 | 0 | 0 | 0 | -15.0359 | -4.6047 | -0.60693 | -0.99075 | -2.0361 | -2.2838 | -2.5793 | -2.8302 | -3.029 | -3.191 | -3.341 | -3.2308 | -3.2821 | -2.5113 | -3.0081 | -3.0081 | -3.0081 | -3.0081 | -3.0081 | -3.0081 | -3.0081 | -3.0081 | -3.0081 | -3.0081 | -3.0081 | -3.0081 | -3.0081 | -3.0081 | -3.0081
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 4.558% |  | 7 year ROG ok | [59 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.98748 | 0.97512 | 0.96698 | 0.96295 | 0.96295 | 0.96295 | 0.96295 | 0.96295 | 0.96295 | 0.96295 | -1.252% | -1.252% | -0.834% | -0.417% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Homebush Bay 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 2263 | 2318 | 2391.805 | 2224.799 | 2182.748 | 2160.445 | 2152.645 | 2163.817 | 2194.711 | 2233.681 | 2267.626 | 2303.616 | 2332.713 | 2369.103 | 2405.316 | 2447.303 | 2492.301 | 2536.581 | 2579.43 | 2622.99 | 2667.271 | 2712.281 | 2758.03 | 2804.526 | 2851.78 | 2899.799 | 2948.595
|  |  |  | Apparent Power |  |  | MVA | 43.1159 |  | 45.57 | 42.3881 | 41.5869 | 41.162 | 41.0134 | 41.2263 | 41.8149 | 42.5573 | 43.2041 | 43.8898 | 44.4442 | 45.1375 | 45.8274 | 46.6274 | 47.4847 | 48.3284 | 49.1447 | 49.9747 | 50.8183 | 51.6759 | 52.5475 | 53.4334 | 54.3337 | 55.2486 | 56.1783
|  |  |  | Real Power |  |  | MW | 41.6401 | 42.6521 | 43.9786 | 40.9078 | 40.1346 | 39.7245 | 39.5811 | 39.7865 | 40.3546 | 41.0711 | 41.6953 | 42.357 | 42.892 | 43.5612 | 44.227 | 44.999 | 45.8264 | 46.6406 | 47.4285 | 48.2294 | 49.0436 | 49.8712 | 50.7124 | 51.5674 | 52.4362 | 53.3192 | 54.2164
|  |  |  | Reactive Power |  |  | MVAr | 11.1842 |  | 11.9377 | 11.1042 | 10.8943 | 10.783 | 10.7441 | 10.7998 | 10.954 | 11.1485 | 11.3179 | 11.4976 | 11.6428 | 11.8244 | 12.0052 | 12.2147 | 12.4393 | 12.6603 | 12.8742 | 13.0916 | 13.3126 | 13.5373 | 13.7656 | 13.9977 | 14.2335 | 14.4732 | 14.7167
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.96577 |  | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508
0.86043 | Diversity Factor: 0.86 | Uncompensated |  | Reactive Power |  |  | MVAr | 11.1842 | 11.456 | 11.9377 | 11.1042 | 10.8943 | 10.783 | 10.7441 | 10.7998 | 10.954 | 11.1485 | 11.3179 | 11.4976 | 11.6428 | 11.8244 | 12.0052 | 12.2147 | 12.4393 | 12.6603 | 12.8742 | 13.0916 | 13.3126 | 13.5373 | 13.7656 | 13.9977 | 14.2335 | 14.4732 | 14.7167
|  |  |  | PF |  |  |  | 0.96577 |  | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508 | 0.96508
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Leichhardt 132_11kV
| Leichhardt 132_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone commissioned |  | 2017-04-30
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | [8 empty] | 0 | 0 | 0 | 1608.002 | 1601.229 | 1599.592 | 1613.787 | 1633.881 | 1651.05 | 1670.73 | 1686.385 | 1708.151 | 1730.087 | 1755.854 | 1783.92 | 1811.579 | 1838.716 | 1866.575 | 1895.167 | 1924.502 | 1954.592 | 1985.446 | 2017.076 | 2049.492 | 2082.707 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1607.9953 | -6.7867 | -1.6396 | 14.2215 | 20.1326 | 17.1999 | 19.7163 | 15.6819 | 21.8041 | 21.9727 | 25.8092 | 28.11 | 27.7022 | 27.1769 | 27.8993 | 28.6321 | 29.3753 | 30.1291 | 30.8937 | 31.6691 | 32.4555 | 33.253
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123 | 3123
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 | 5737 |  |  | Leichhardt 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803.9977 | -3.3934 | -0.81982 | 7.1108 | 10.0663 | 8.5999 | 9.8582 | 7.8409 | 10.9021 | 10.9863 | 12.9046 | 14.055 | 13.8511 | 13.5884 | 13.9497 | 14.3161 | 14.6877 | 15.0646 | 15.4468 | 15.8345 | 16.2277 | 16.6265
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Leichhardt 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803.9977 | -3.3934 | -0.81982 | 7.1108 | 10.0663 | 8.5999 | 9.8582 | 7.8409 | 10.9021 | 10.9863 | 12.9046 | 14.055 | 13.8511 | 13.5884 | 13.9497 | 14.3161 | 14.6877 | 15.0646 | 15.4468 | 15.8345 | 16.2277 | 16.6265
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Leichhardt 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9077 | -2.8471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Leichhardt 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9077 | -2.8471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx2 | Leichhardt 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.6511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx2 | Leichhardt 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.6511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx3 | Leichhardt 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493.7306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx3 | Leichhardt 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493.7306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx4 | Leichhardt 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx4 | Leichhardt 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Leichhardt 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.3528 | 19.0012 | 19.7258 | 20.6632 | 20.499 | 20.3167 | 20.6391 | 20.9662 | 21.2979 | 21.6344 | 21.9757 | 22.3219 | 22.673 | 23.0292 | 23.3904 | 23.7568 | 24.1284 | 24.5053 | 24.8876 | 25.2753 | 25.6685 | 26.0673
| Diversity Factor: 0 | [33 empty] | Econometric |  | Leichhardt 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.3528 | 19.0012 | 19.7258 | 20.6632 | 20.499 | 20.3167 | 20.6391 | 20.9662 | 21.2979 | 21.6344 | 21.9757 | 22.3219 | 22.673 | 23.0292 | 23.3904 | 23.7568 | 24.1284 | 24.5053 | 24.8876 | 25.2753 | 25.6685 | 26.0673
[35 empty] | Energy Efficiency |  | Leichhardt 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.7959 | -16.7092 | -17.5555 | -10.4219 | -7.4053 | -8.6413 | -8.4278 | -10.3065 | -7.5772 | -7.8294 | -6.2524 | -5.4482 | -6.0033 | -6.6221 | -6.6221 | -6.6221 | -6.6221 | -6.6221 | -6.6221 | -6.6221 | -6.6221 | -6.6221
[35 empty] | Energy Efficiency |  | Leichhardt 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.7959 | -16.7092 | -17.5555 | -10.4219 | -7.4053 | -8.6413 | -8.4278 | -10.3065 | -7.5772 | -7.8294 | -6.2524 | -5.4482 | -6.0033 | -6.6221 | -6.6221 | -6.6221 | -6.6221 | -6.6221 | -6.6221 | -6.6221 | -6.6221 | -6.6221
| 0 | [33 empty] | Solar PV |  | Leichhardt 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.652 | -2.8383 | -2.9901 | -3.1306 | -3.0274 | -3.0755 | -2.3532 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Leichhardt 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.652 | -2.8383 | -2.9901 | -3.1306 | -3.0274 | -3.0755 | -2.3532 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187 | -2.8187
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [8 empty] | Same as Leichhardt 33/11kV | [59 empty] | Same as Leichhardt 33/11kV
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.97786 | 0.95621 | 0.9421 | 0.93514 | 0.93514 | 0.93514 | 0.93514 | 0.93514 | 0.93514 | 0.93514 | -2.214% | -2.214% | -1.476% | -0.738% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Leichhardt 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 | 0 | 0 | 0 | 0 | 1608.002 | 1601.229 | 1599.592 | 1613.787 | 1633.881 | 1651.05 | 1670.73 | 1686.385 | 1708.151 | 1730.087 | 1755.854 | 1783.92 | 1811.579 | 1838.716 | 1866.575 | 1895.167 | 1924.502 | 1954.592 | 1985.446 | 2017.076 | 2049.492 | 2082.707
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 0 | 30.6366 | 30.5075 | 30.4763 | 30.7468 | 31.1296 | 31.4567 | 31.8317 | 32.13 | 32.5447 | 32.9626 | 33.4535 | 33.9882 | 34.5152 | 35.0322 | 35.563 | 36.1078 | 36.6667 | 37.24 | 37.8278 | 38.4305 | 39.0481 | 39.6809
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 0 | 28.3468 | 28.2304 | 28.2023 | 28.4461 | 28.7914 | 29.0863 | 29.4244 | 29.6933 | 30.0672 | 30.4439 | 30.8865 | 31.3685 | 31.8435 | 32.3095 | 32.7879 | 33.2789 | 33.7826 | 34.2992 | 34.829 | 35.372 | 35.9285 | 36.4987
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 11.6215 | 11.5651 | 11.5515 | 11.6696 | 11.8368 | 11.9797 | 12.1434 | 12.2736 | 12.4547 | 12.6372 | 12.8515 | 13.085 | 13.3151 | 13.5408 | 13.7725 | 14.0102 | 14.2542 | 14.5044 | 14.761 | 15.024 | 15.2935 | 15.5697
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0.92526 | 0.92536 | 0.92538 | 0.92517 | 0.92489 | 0.92464 | 0.92437 | 0.92416 | 0.92387 | 0.92359 | 0.92327 | 0.92292 | 0.92259 | 0.92228 | 0.92197 | 0.92165 | 0.92134 | 0.92103 | 0.92072 | 0.92042 | 0.92011 | 0.91981
0.98313 | Diversity Factor: 0.98 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 0 | 11.6215 | 11.5651 | 11.5515 | 11.6696 | 11.8368 | 11.9797 | 12.1434 | 12.2736 | 12.4547 | 12.6372 | 12.8515 | 13.085 | 13.3151 | 13.5408 | 13.7725 | 14.0102 | 14.2542 | 14.5044 | 14.761 | 15.024 | 15.2935 | 15.5697
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0.92526 | 0.92536 | 0.92538 | 0.92517 | 0.92489 | 0.92464 | 0.92437 | 0.92416 | 0.92387 | 0.92359 | 0.92327 | 0.92292 | 0.92259 | 0.92228 | 0.92197 | 0.92165 | 0.92134 | 0.92103 | 0.92072 | 0.92042 | 0.92011 | 0.91981
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Leichhardt 33_11kV
| Leichhardt 33_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone decommissioned |  | 2017-04-30
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 1444 | 1695 | 1513 | 1491 | 1510 | 1780 | 1530 |  | 1892.559 | 1840.097 | 1623.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | 0 | 0 | -160 | -5.2618 | 145.4959 | 218.0445 | -4.5322 | 242.9126 | -10.5571 | -188.9485 | -1612.0008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 3455 |  | 3455 | 3455 | 3455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 6000 |  | 6000 | 6000 | 6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Leichhardt 33_11kV Tx2 | 0 | 0 | 0 | -1.6951 | -3.3839 | -0.95211 | -1.46 | 178.2504 | -3.4009 | -183.8995 | -519.3023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Leichhardt 33_11kV Tx3 | 0 | 0 | -160 | -3.2232 | 149.5655 | 106.1895 | -2.7763 | 65.3208 | -6.4669 | -4.5627 | -987.4611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [35 empty] | Leichhardt 33_11kV Tx4 | 0 | 0 | 0 | -0.34351 | -0.68575 | 112.8071 | -0.29588 | -0.65854 | -0.6892 | -0.48627 | -105.2374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Leichhardt 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.24136 | -1.1962 | -1.5033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Leichhardt 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.45895 | -2.2747 | -2.8585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Leichhardt 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.048912 | -0.24242 | -0.30465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 5848. Camperdown Upgrade Stage 3 - Transferring Load from Camperdown Zone to Leichhardt Zone. | Camperdown 33_5kV Tx5 | Leichhardt 33_11kV Tx3 | 0 | 0 | 0 | 0 | 156 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 5848. Camperdown Upgrade Stage 3 - Transferring Load from Camperdown Zone to Leichhardt Zone. | Camperdown 33_5kV Tx5 | Leichhardt 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6428. Leichhardt to Five Dock load transfer of 4MVA | Leichhardt 33_11kV Tx3 | Five Dock 33_11kV Tx4 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx2 | Leichhardt 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.6511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx2 | Leichhardt 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.6511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx3 | Leichhardt 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493.7306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx3 | Leichhardt 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493.7306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx4 | Leichhardt 132_11kV Tx11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Decommission: Commissioning Transfers | Leichhardt 33_11kV Tx4 | Leichhardt 132_11kV Tx12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2013476. Negotiated offer - HV Connection Alteration - Premises at Glebe Island, 115 Sommerville Road, Rozelle, Sydney Ports Corporation - Load increase from HVC Substation S.1530 |  | Leichhardt 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2014007. Establishment of HVC CP.64632 Maritime Services No 3, 115 Sommerville Road, Glebe Island. |  | Leichhardt 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181.5 | 0 | -181.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Leichhardt 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Leichhardt 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Leichhardt 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Leichhardt 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.779 | -0.82588 | -4.4243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Energy Efficiency |  | Leichhardt 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3828 | -1.5704 | -8.4129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Energy Efficiency |  | Leichhardt 33_11kV Tx4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.36051 | -0.16737 | -0.8966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Solar PV |  | Leichhardt 33_11kV Tx2 | 0 | 0 | 0 | -1.6951 | -3.3839 | -0.95211 | -1.46 | -1.2293 | -1.3788 | -1.5572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Solar PV |  | Leichhardt 33_11kV Tx3 | 0 | 0 | 0 | -3.2232 | -6.4345 | -1.8105 | -2.7763 | -2.3375 | -2.6218 | -2.9611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Leichhardt 33_11kV Tx4 | 0 | 0 | 0 | -0.34351 | -0.68575 | -0.19295 | -0.29588 | -0.24911 | -0.27942 | -0.31557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | 0: Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 9.751% |  | 0: 7 year ROG ok | [35 empty] | 7 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.97786 | 0.95621 | 0.9421 | 0.93514 | 0.93514 | 0.93514 | 0.93514 | 0.93514 | 0.93514 | 0.93514 | -2.214% | -2.214% | -1.476% | -0.738% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Leichhardt 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 1530 | 1687 | 1892.559 | 1840.097 | 1623.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 29.1504 |  | 36.0581 | 35.0586 | 30.9411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 26.97 | 29.7375 | 33.361 | 32.4362 | 28.6267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 11.0619 |  | 13.6832 | 13.3039 | 11.7414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9252 |  | 0.9252 | 0.9252 | 0.9252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.84915 | Diversity Factor: 0.85 | Uncompensated |  | Reactive Power |  |  | MVAr | 11.0619 | 12.197 | 13.6832 | 13.3039 | 11.7414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9252 |  | 0.9252 | 0.9252 | 0.9252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Lidcombe 33_11kV
| Lidcombe 33_11kV | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | 1537 | 1494 | 1456 | 1547 | 1371 | 1138 | 990 |  | 1137.598 | 1117.203 | 1107.915 | 1112.134 | 1126.234 | 1142.696 | 1170.71 | 1200.923 | 1227.587 | 1255.408 | 1280.656 | 1309.6 | 1338.692 | 1370.446 | 1403.746 | 1436.899 | 1469.7 | 1503.033 | 1536.906 | 1571.326 | 1606.298 | 1641.832 | 1677.932 | 1714.608 | 1751.865 |  |  | Total | 0 | 0 | 76.5 | 72.6111 | 24.3067 | -427.703 | -0.99567 | 72.283 | -8.072 | -1.2197 | 8.2191 | 14.0999 | 16.4619 | 28.0145 | 30.2127 | 26.6646 | 27.8205 | 25.2481 | 28.9441 | 29.0922 | 31.7539 | 33.3001 | 33.1528 | 32.8007 | 33.3334 | 33.873 | 34.4194 | 34.9728 | 35.5332 | 36.1007 | 36.6754 | 37.2574
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 1754 |  | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754 | 1754
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 2839 |  | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 | 2839 |  |  | Lidcombe 33_11kV Tx1 | 33 | 0 | 76.5 | 37.6106 | -3.551 | -164.3344 | -0.49152 | 11.5113 | -3.9848 | -0.60211 | 4.0574 | 6.9605 | 8.1266 | 13.8296 | 14.9148 | 13.1632 | 13.7338 | 12.4639 | 14.2885 | 14.3616 | 15.6756 | 16.4389 | 16.3662 | 16.1923 | 16.4553 | 16.7217 | 16.9914 | 17.2646 | 17.5413 | 17.8214 | 18.1051 | 18.3925
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Lidcombe 33_11kV Tx2 | 0 | 0 | 0 | 110.9215 | -73.7158 | -0.26899 | -0.099081 | 42.7467 | -0.80327 | -0.12137 | 0.8179 | 1.4031 | 1.6382 | 2.7878 | 3.0065 | 2.6535 | 2.7685 | 2.5125 | 2.8803 | 2.895 | 3.1599 | 3.3138 | 3.2991 | 3.2641 | 3.3171 | 3.3708 | 3.4252 | 3.4802 | 3.536 | 3.5925 | 3.6497 | 3.7076
| Transformer Loads | [35 empty] | Lidcombe 33_11kV Tx3 | -33 | 0 | 0 | -75.9209 | 101.5736 | -263.0997 | -0.40507 | 18.0249 | -3.2839 | -0.49621 | 3.3438 | 5.7362 | 6.6972 | 11.3971 | 12.2914 | 10.8479 | 11.3182 | 10.2717 | 11.7753 | 11.8355 | 12.9184 | 13.5475 | 13.4875 | 13.3443 | 13.561 | 13.7805 | 14.0028 | 14.2279 | 14.4559 | 14.6868 | 14.9206 | 15.1574
| Historical Loads | (11kV Amps) | [7 empty] | 0: Weather Corrected Forecast Loads; 4: (11kV Amps) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Lidcombe 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.60074 | -2.2221 | -2.697 | -2.7641 | -2.5266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Lidcombe 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1211 | -0.44794 | -0.54366 | -0.5572 | -0.50932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Broad based demand management |  | Lidcombe 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.49508 | -1.8313 | -2.2226 | -2.278 | -2.0822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6111. Augmentation of the Panel 12, 18, and 26 Feeders - Lidcombe Zone | Lidcombe 33_11kV Tx3 | Lidcombe 33_11kV Tx1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6269. Flemington Minor Zone Development - Panels 15, 16 and 12-19-21 Feeders. RAILWAY CROSSING INVOLVED | Flemington 132_11kV Tx4 | Lidcombe 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 6639. Lidcombe to Flemington 11kV Load Transfer | Lidcombe 33_11kV Tx1 | Flemington 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6639. Lidcombe to Flemington 11kV Load Transfer | Lidcombe 33_11kV Tx3 | Flemington 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | DNP_ID: 6639. Lidcombe to Flemington 11kV Load Transfer | Lidcombe 33_11kV Tx3 | Flemington 132_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | DNP_ID: 6787. Relieve Tx3 at Lidcombe Zone | Lidcombe 33_11kV Tx3 | Lidcombe 33_11kV Tx2 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | DNP_ID: 7025. Rerack panel 16 from the rear busbar to the front busbar. | Lidcombe 33_11kV Tx2 | Lidcombe 33_11kV Tx3 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2007041. Establishment of S.35543 Auburn Hospital No.3, S.35584 Auburn Hospital No.4 and S.35585 Auburn Hospital No.5 (load split evenly across these subs - all located next to each other, originally a single chamber sub, now 3 KL |  | Lidcombe 33_11kV Tx1 | 0 | 0 | 76.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2007159. Establishment of S.35574 Chisholm Manchester No.2 & S.35605 Chisholm Manchester No.3, Cnr Chisholm Rd & Manchester Rd, Auburn for Lidcombe Rail Yards |  | Lidcombe 33_11kV Tx3 | 0 | 0 | 0 | 14.4 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | HVCON_ID: 2008478. Establish S.48025 Chiswick Rd to replace S.254 Chiswick Rd. Replace cubicle type switchgear with 1xRMI fuse switch. This must be done in conjunction with DNP6494 which does augmentation to this cubicles associated feeder | Sefton 132_11kV Tx4 | Lidcombe 33_11kV Tx1 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | HVCON_ID: 2008478. Establish S.48025 Chiswick Rd to replace S.254 Chiswick Rd. Replace cubicle type switchgear with 1xRMI fuse switch. This must be done in conjunction with DNP6494 which does augmentation to this cubicles associated feeder | Sefton 132_11kV Tx4 | Lidcombe 33_11kV Tx2 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2011650. Establishment of S.61188 Boorea Nyrang No 3, Unit 2, 44 Boorea Street, Lidcombe |  | Lidcombe 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HVCON_ID: 2013397. Establishment of S.64452 Park Queen, 6-14 Park Rd, Auburn |  | Lidcombe 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Econometric |  | Lidcombe 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8215 | 13.6305 | 19.4829 | 18.4244 | 20.1734 | 19.1874 | 18.1732 | 18.4109 | 18.6516 | 18.8954 | 19.1423 | 19.3923 | 19.6455 | 19.902 | 20.1617 | 20.4247 | 20.691 | 20.9608 | 21.234 | 21.5106 | 21.7908 | 22.0745 | 22.3618
| Diversity Factor: 0 | [33 empty] | Econometric |  | Lidcombe 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3751 | 2.7476 | 3.9274 | 3.714 | 4.0666 | 3.8678 | 3.6634 | 3.7113 | 3.7598 | 3.8089 | 3.8587 | 3.9091 | 3.9602 | 4.0119 | 4.0642 | 4.1172 | 4.1709 | 4.2253 | 4.2804 | 4.3361 | 4.3926 | 4.4498 | 4.5077
[35 empty] | Econometric |  | Lidcombe 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6217 | 11.233 | 16.056 | 15.1837 | 16.6251 | 15.8126 | 14.9767 | 15.1726 | 15.371 | 15.5719 | 15.7753 | 15.9814 | 16.1901 | 16.4014 | 16.6155 | 16.8322 | 17.0517 | 17.274 | 17.4991 | 17.7271 | 17.958 | 18.1918 | 18.4286
[35 empty] | Energy Efficiency |  | Lidcombe 33_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1655 | -0.95232 | -3.8114 | -5.8046 | -8.921 | -9.1656 | -5.1583 | -3.1263 | -3.8454 | -3.786 | -5.1203 | -3.5395 | -3.7133 | -2.6494 | -2.1393 | -2.4684 | -2.902 | -2.902 | -2.902 | -2.902 | -2.902 | -2.902 | -2.902 | -2.902 | -2.902
| 0 | [33 empty] | Energy Efficiency |  | Lidcombe 33_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.43652 | -0.19197 | -0.76831 | -1.1701 | -1.7983 | -1.8476 | -1.0398 | -0.63021 | -0.77516 | -0.76318 | -1.0322 | -0.7135 | -0.74854 | -0.53407 | -0.43124 | -0.49759 | -0.58499 | -0.58499 | -0.58499 | -0.58499 | -0.58499 | -0.58499 | -0.58499 | -0.58499 | -0.58499
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Lidcombe 33_11kV Tx3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7846 | -0.78482 | -3.141 | -4.7837 | -7.3519 | -7.5534 | -4.251 | -2.5764 | -3.169 | -3.1201 | -4.2197 | -2.917 | -3.0602 | -2.1834 | -1.763 | -2.0343 | -2.3916 | -2.3916 | -2.3916 | -2.3916 | -2.3916 | -2.3916 | -2.3916 | -2.3916 | -2.3916
[35 empty] | Solar PV |  | Lidcombe 33_11kV Tx1 | 0 | 0 | 0 | -0.38943 | -3.551 | -1.3344 | -0.49152 | -0.72248 | -0.81036 | -0.91522 | -1.0042 | -1.0748 | -1.1323 | -1.1855 | -1.1464 | -1.1646 | -0.89108 | -1.0673 | -1.0673 | -1.0673 | -1.0673 | -1.0673 | -1.0673 | -1.0673 | -1.0673 | -1.0673 | -1.0673 | -1.0673 | -1.0673 | -1.0673 | -1.0673 | -1.0673
[35 empty] | Solar PV |  | Lidcombe 33_11kV Tx2 | 0 | 0 | 0 | -0.078502 | -0.71582 | -0.26899 | -0.099081 | -0.14564 | -0.16335 | -0.18449 | -0.20244 | -0.21666 | -0.22824 | -0.23897 | -0.23109 | -0.23476 | -0.17963 | -0.21516 | -0.21516 | -0.21516 | -0.21516 | -0.21516 | -0.21516 | -0.21516 | -0.21516 | -0.21516 | -0.21516 | -0.21516 | -0.21516 | -0.21516 | -0.21516 | -0.21516
| 0 | [33 empty] | Solar PV |  | Lidcombe 33_11kV Tx3 | 0 | 0 | 0 | -0.32094 | -2.9264 | -1.0997 | -0.40507 | -0.5954 | -0.66783 | -0.75424 | -0.8276 | -0.88574 | -0.93312 | -0.97695 | -0.94473 | -0.95974 | -0.73435 | -0.87961 | -0.87961 | -0.87961 | -0.87961 | -0.87961 | -0.87961 | -0.87961 | -0.87961 | -0.87961 | -0.87961 | -0.87961 | -0.87961 | -0.87961 | -0.87961 | -0.87961
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | 0: Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 9.393% |  | 0: 5 year ROG ok | [35 empty] | 5 year ROG ok
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.98917 | 0.97846 | 0.97139 | 0.96789 | 0.96789 | 0.96789 | 0.96789 | 0.96789 | 0.96789 | 0.96789 | -1.083% | -1.083% | -0.722% | -0.361% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Lidcombe 33_11kV | Compensated |  | Load (LV side) |  |  | Amps | 990 | 1077 | 1137.598 | 1117.203 | 1107.915 | 1112.134 | 1126.234 | 1142.696 | 1170.71 | 1200.923 | 1227.587 | 1255.408 | 1280.656 | 1309.6 | 1338.692 | 1370.446 | 1403.746 | 1436.899 | 1469.7 | 1503.033 | 1536.906 | 1571.326 | 1606.298 | 1641.832 | 1677.932 | 1714.608 | 1751.865
|  |  |  | Apparent Power |  |  | MVA | 18.862 |  | 21.6742 | 21.2856 | 21.1086 | 21.189 | 21.4576 | 21.7713 | 22.305 | 22.8807 | 23.3887 | 23.9187 | 24.3998 | 24.9512 | 25.5055 | 26.1105 | 26.745 | 27.3766 | 28.0016 | 28.6366 | 29.282 | 29.9378 | 30.6041 | 31.2811 | 31.9689 | 32.6677 | 33.3775
|  |  |  | Real Power |  |  | MW | 17.1094 | 18.6129 | 19.6661 | 19.3135 | 19.153 | 19.2259 | 19.4697 | 19.7542 | 20.2385 | 20.7608 | 21.2218 | 21.7027 | 22.1392 | 22.6396 | 23.1425 | 23.6914 | 24.2671 | 24.8402 | 25.4073 | 25.9835 | 26.5691 | 27.1641 | 27.7687 | 28.383 | 29.0071 | 29.6411 | 30.2852
|  |  |  | Reactive Power |  |  | MVAr | 7.9402 |  | 9.1112 | 8.9478 | 8.8734 | 8.9072 | 9.0202 | 9.152 | 9.3764 | 9.6183 | 9.8319 | 10.0547 | 10.2569 | 10.4887 | 10.7218 | 10.9761 | 11.2428 | 11.5083 | 11.771 | 12.038 | 12.3093 | 12.5849 | 12.8651 | 13.1496 | 13.4388 | 13.7325 | 14.0309
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.90708 |  | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735
0.99039 | Diversity Factor: 0.99 | Uncompensated |  | Reactive Power |  |  | MVAr | 7.9402 | 8.6379 | 9.1112 | 8.9478 | 8.8734 | 8.9072 | 9.0202 | 9.152 | 9.3764 | 9.6183 | 9.8319 | 10.0547 | 10.2569 | 10.4887 | 10.7218 | 10.9761 | 11.2428 | 11.5083 | 11.771 | 12.038 | 12.3093 | 12.5849 | 12.8651 | 13.1496 | 13.4388 | 13.7325 | 14.0309
|  |  |  | PF |  |  |  | 0.90708 |  | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735 | 0.90735
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Olympic Park 132_11kV
| Olympic Park 132_11kV | [16 empty] | 2015 | SUMMER
[6 empty] | Zone commissioned |  | 2016-05-31
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [20 empty] | Spots & Transfers Summary | (11kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Firm Rating | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Olympic Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | Olympic Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (11kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (11kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | [33 empty] | Broad based demand management |  | Olympic Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Broad based demand management |  | Olympic Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Olympic Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Econometric |  | Olympic Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [33 empty] | Energy Efficiency |  | Olympic Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [33 empty] | Energy Efficiency |  | Olympic Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Olympic Park 132_11kV Tx1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Solar PV |  | Olympic Park 132_11kV Tx2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [8 empty] | No transfers committed | [59 empty] | No transfers committed
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0.97618 | 0.95293 | 0.93779 | 0.93035 | 0.93035 | 0.93035 | 0.93035 | 0.93035 | 0.93035 | 0.93035 | -2.382% | -2.382% | -1.588% | -0.794% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Olympic Park 132_11kV | Compensated |  | Load (LV side) |  |  | Amps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.87459 | Diversity Factor: 0.87 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer1
| Customer1 | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  | 3 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Customer1 | Compensated |  | Load (LV side) |  |  | Amps | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Apparent Power |  |  | MVA | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Real Power |  |  | MW | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.78333 | Diversity Factor: 0.78 | Uncompensated |  | Reactive Power |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer2
| Customer2 | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  | 316 | 421 | 289 | 514 |  | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Customer2 | Compensated |  | Load (LV side) |  |  | Amps | 514 |  | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514 | 514
|  |  |  | Apparent Power |  |  | MVA | 29.379 |  | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379 | 29.379
|  |  |  | Real Power |  |  | MW | 26.4411 |  | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411 | 26.4411
|  |  |  | Reactive Power |  |  | MVAr | 12.806 |  | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.70841 | Diversity Factor: 0.71 | Uncompensated |  | Reactive Power |  |  | MVAr | 12.806 |  | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806 | 12.806
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF

## Customer3
| Customer3 | [16 empty] | 2015 | SUMMER
| Substation Total Loads | [33 empty] | Spots & Transfers Detail
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [20 empty] | Spots & Transfers Summary | (33kV Amps) |  | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| Total |  |  |  | 304 | 273 | 238 | 279 |  | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 |  |  | Total
Firm Rating
| Total Capacity | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | -6 | -5 | -4 | -3 | -2 | -1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformer Loads | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Historical Loads | (33kV Amps) | [7 empty] | Weather Corrected Forecast Loads |  |  |  | (33kV Amps) | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diversity Factor: 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diversity Factor: 0
[38 empty] | Historical Spots & Transfers | [6 empty] | Forecast Spots & Transfers
[35 empty] | Project Name | From | To | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
0
Diversity Factor: 0
| Weather Correction and Public Holiday Factors | [8 empty] | Forecast ROG
ROG Justification
| Actual loads for season 13/14 have been weather corrected by the following: | [6 empty] | 0% |  | N/A | [59 empty] | N/A
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Substation Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
1 | Customer3 | Compensated |  | Load (LV side) |  |  | Amps | 279 |  | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279
|  |  |  | Apparent Power |  |  | MVA | 15.947 |  | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947 | 15.947
|  |  |  | Real Power |  |  | MW | 14.3523 |  | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523 | 14.3523
|  |  |  | Reactive Power |  |  | MVAr | 6.9511 |  | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511
|  |  |  | Capacitors In Service |  |  | MVAr | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
0.72552 | Diversity Factor: 0.73 | Uncompensated |  | Reactive Power |  |  | MVAr | 6.9511 |  | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511 | 6.9511
|  |  |  | PF |  |  |  | 0.9 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Transformer Load Detail
[7 empty] | Units | 13/14 |  | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | 35/36 | 36/37 | 37/38 | 38/39
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF
| 0 | Compensated |  | Load (LV side) |  |  | Amps
|  |  |  | Apparent Power |  |  | MVA
|  |  |  | Real Power |  |  | MW
|  |  |  | Reactive Power |  |  | MVAr
|  |  |  | Capacitors In Service |  |  | MVAr
PF
| Zone Div: | Uncompensated |  | Reactive Power |  |  | MVAr
PF