## Cover
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue - Headings
Yellow - Input cells
Grey - No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | Ausgrid
DNSP - Australian business number: |  | 67 505 337 385
Reporting year: |  | 2012-13
Business address | Address |  | 570 George St
| Suburb |  | Sydney
|  | State | NSW | Postcode | 2000
Postal address | Address |  | As above
Suburb
|  | State |  | Postcode
Contact name/s | John Thomson
Contact phone/s | 02 9269 2312
Contact email address/s | john.thomson@ausgrid.com.au

## Contents
Electricity DNSP Annual Reporting Template
Table of contents
Cover sheet | 3. Quality of service and customer service
1. Service Target Performance Incentive Scheme | 4. General Information
1a. STPIS - Reliability | 5. Outages
1b. STPIS - Customer service | 5a. Network data - outages
1c. STPIS - Daily performance | 5b. Network data - feeder reliability
1d. STPIS - MED threshold | 5c. Network data - outages
1e. STPIS - Exclusions | 5d. Network data - planned outages
1f. STPIS - GSL | 6. Weighted average cost of debt
2. Demand | 7. Asset installation

## 1a. STPIS Reliability
Ausgrid
STPIS Data Reporting
2012-13
Reliability
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: SAIDI
Unplanned SAIDI | CBD | Urban | Rural short | Rural long | Whole network
Total | 38.4924 | 65.7998 | 182.8115 | 640.3654 | 80.1856
Total - after removing excluded events | 38.4924 | 56.9138 | 147.8678 | 533.1495 | 68.2418
Table 2: SAIFI
Unplanned SAIFI | CBD | Urban | Rural short | Rural long | Whole network
Total | 11.6288 | 70.3343 | 155.0996 | 262.6605 | 79.6703
Total - after removing excluded events | 11.6288 | 64.941 | 141.8504 | 255.9792 | 73.4502
Table 3: Average distribution customer numbers
| CBD | Urban | Rural short | Rural long | Whole network
Customer numbers start of period | 30887 | 1401809 | 201594 | 2588 | 1636878
Customer numbers end of period | 30363 | 1417378 | 192590 | 2620 | 1642951
Average distribution customer numbers | 30625 | 1409593.5 | 197092 | 2604 | 1639914.5
Contents

## 1b. STPIS Customer Service
Ausgrid
STPIS Data Reporting
2012-13
Customer service
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Telephone answering
Telephone answering | Total - after removing excluded events | Total
Total number of calls | 212383 | 226992
Number of calls answered within 30 seconds | 184022
Percentage of calls answered within 30 seconds | 0.86646
Table 2: New connections
Note: this is for newly energised properties only
New connections
Number of new connections
Number of new connections not provided on or before the agreed date
Percentage of new connections not provided on or before the agreed date
Table 3: Streetlight repair
Streetlight repair
Total number of streetlights
Total number of streetlight faults
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neigbouring business
Faulty streetlights not repaired within 5 days of fault report or agreed date
Percentage of faulty streetlights not repaired within 5 days of fault report or agreed date
Table 4: Response to written enquiries
Note: this does not include Saturdays, Sundays and Public holidays
Response to written enquiries
Number of written enquiries
Number of written enquiries not responded to in 5 days
Percentage of written enquiries not responded to in 5 days
Contents

## 1c. STPIS Daily Performance
Ausgrid
STPIS Data Reporting |  |  |  | 2012-07-01
2012-13 |  |  |  | 2013-07-01
Daily Performance
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Daily performance data (Unplanned SAIDI, Unplanned SAIFI)
Note: the excluded events to be removed from the data refer only to events listed in clause 3.3(a) of the STPIS, with respect to reliability data, and in clause 5.4(a) of the STPIS with respect to customer service parameters.
Customer service
Date | Network SAIDI all events total | Network SAIDI all events after removing excluded events | CBD SAIDI all events total | CBD SAIDI all events after removing excluded events | Urban SAIDI all events total | Urban SAIDI all events after removing excluded events | Long rural SAIDI all events total | Long rural all events after removing excluded events | Short rural SAIDI all events total | Short rural SAIDI all events after removing excluded events | Network SAIFI all events total | Network SAIFI all events after removing excluded events | CBD SAIFI all events total | CBD SAIFI all events after removing excluded events | Urban SAIFI all events total | Urban SAIFI all events after removing excluded events | Long rural SAIFI all events total | Long rural SAIFI all events after removing excluded events | Short rural SAIFI all events total | Short Rural SAIFI all events after removing excluded events | Total number of calls (after removing excluded events) | Number of calls answered within 30 seconds (after removing excluded events) | MED
2012-07-01 | 0.0088456 | 0.0088456 | 0 | 0 | 0.0099893 | 0.0099893 | 0 | 0 | 0.0023612 | 0.0023612 | 0.0055594 | 0.0055594 | 0 | 0 | 0.0063489 | 0.0063489 | 0 | 0 | 0.00099209 | 0.00099209 | 288 | 230 | Yes
2012-07-02 | 0.10422 | 0.10422 | 0 | 0 | 0.09847 | 0.09847 | 0 | 0 | 0.16148 | 0.16148 | 0.15835 | 0.15835 | 0 | 0 | 0.16279 | 0.16279 | 0 | 0 | 0.15377 | 0.15377 | 587 | 560 | Yes
2012-07-03 | 0.016 | 0.016 | 0 | 0 | 0.014105 | 0.014105 | 0 | 0 | 0.03182 | 0.03182 | 0.010569 | 0.010569 | 0 | 0 | 0.010273 | 0.010273 | 0 | 0 | 0.014377 | 0.014377 | 493 | 467 | Yes
2012-07-04 | 0.078876 | 0.078876 | 0 | 0 | 0.071997 | 0.071997 | 0 | 0 | 0.13976 | 0.13976 | 0.46448 | 0.46448 | 0 | 0 | 0.53349 | 0.53349 | 0 | 0 | 0.061969 | 0.061969 | 521 | 510 | Yes
2012-07-05 | 0.036187 | 0.036187 | 0 | 0 | 0.041789 | 0.041789 | 0.045595 | 0.045595 | 0.0026776 | 0.0026776 | 0.026209 | 0.026209 | 0 | 0 | 0.030392 | 0.030392 | 0.03864 | 0.03864 | 0.00099151 | 0.00099151 | 549 | 517 | Yes
2012-07-06 | 0.28113 | 0.28113 | 0 | 0 | 0.309 | 0.309 | 0 | 0 | 0.13411 | 0.13411 | 1.333 | 1.333 | 0 | 0 | 1.4218 | 1.4218 | 0 | 0 | 0.93747 | 0.93747 | 606 | 463 | Yes
2012-07-07 | 0.16426 | 0.16426 | 0 | 0 | 0.18592 | 0.18592 | 0 | 0 | 0.040976 | 0.040976 | 0.072333 | 0.072333 | 0 | 0 | 0.078833 | 0.078833 | 0 | 0 | 0.039165 | 0.039165 | 379 | 298 | Yes
2012-07-08 | 0.12932 | 0.12932 | 0 | 0 | 0.14375 | 0.14375 | 0 | 0 | 0.050489 | 0.050489 | 0.17436 | 0.17436 | 0 | 0 | 0.19662 | 0.19662 | 0 | 0 | 0.048584 | 0.048584 | 439 | 296 | Yes
2012-07-09 | 0.024759 | 0.024759 | 0 | 0 | 0.028577 | 0.028577 | 0 | 0 | 0.0023324 | 0.0023324 | 0.017167 | 0.017167 | 0 | 0 | 0.019833 | 0.019833 | 0 | 0 | 0.0014873 | 0.0014873 | 506 | 490 | Yes
2012-07-10 | 0.10562 | 0.10562 | 0 | 0 | 0.11985 | 0.11985 | 0.71473 | 0.71473 | 0.015075 | 0.015075 | 0.13942 | 0.13942 | 0 | 0 | 0.1606 | 0.1606 | 0.3864 | 0.3864 | 0.010409 | 0.010409 | 483 | 479 | Yes
2012-07-11 | 0.14305 | 0.14305 | 0 | 0 | 0.10475 | 0.10475 | 1.3524 | 1.3524 | 0.41548 | 0.41548 | 0.12622 | 0.12622 | 0 | 0 | 0.085473 | 0.085473 | 0.3864 | 0.3864 | 0.42527 | 0.42527 | 452 | 437 | Yes
2012-07-12 | 0.082087 | 0.082087 | 0 | 0 | 0.095508 | 0.095508 | 0 | 0 | 0.0024386 | 0.0024386 | 0.12464 | 0.12464 | 0 | 0 | 0.1454 | 0.1454 | 0 | 0 | 0.0009913 | 0.0009913 | 492 | 444 | Yes
2012-07-13 | 0.112 | 0.112 | 0 | 0 | 0.10184 | 0.10184 | 0 | 0 | 0.20112 | 0.20112 | 0.065373 | 0.065373 | 0 | 0 | 0.043379 | 0.043379 | 0 | 0 | 0.22899 | 0.22899 | 411 | 399 | Yes
2012-07-14 | 0.24087 | 0.24087 | 0 | 0 | 0.27942 | 0.27942 | 0 | 0 | 0.012979 | 0.012979 | 0.12879 | 0.12879 | 0 | 0 | 0.14904 | 0.14904 | 0 | 0 | 0.0094173 | 0.0094173 | 377 | 302 | Yes
2012-07-15 | 0.097407 | 0.097407 | 0 | 0 | 0.11283 | 0.11283 | 0 | 0 | 0.0063565 | 0.0063565 | 0.10576 | 0.10576 | 0 | 0 | 0.12272 | 0.12272 | 0 | 0 | 0.0054521 | 0.0054521 | 288 | 246 | Yes
2012-07-16 | 0.24131 | 0.24131 | 0 | 0 | 0.25075 | 0.25075 | 0.10896 | 0.10896 | 0.21425 | 0.21425 | 0.21787 | 0.21787 | 0 | 0 | 0.23223 | 0.23223 | 0.07728 | 0.07728 | 0.15316 | 0.15316 | 624 | 588 | Yes
2012-07-17 | 0.18211 | 0.18211 | 0 | 0 | 0.20609 | 0.20609 | 0 | 0 | 0.046095 | 0.046095 | 0.16074 | 0.16074 | 0 | 0 | 0.17972 | 0.17972 | 0 | 0 | 0.055869 | 0.055869 | 603 | 515 | Yes
2012-07-18 | 0.10946 | 0.10946 | 0 | 0 | 0.086688 | 0.086688 | 0 | 0 | 0.28531 | 0.28531 | 0.073621 | 0.073621 | 0 | 0 | 0.061309 | 0.061309 | 0 | 0 | 0.17107 | 0.17107 | 563 | 528 | Yes
2012-07-19 | 0.022158 | 0.022158 | 0 | 0 | 0.0097638 | 0.0097638 | 0 | 0 | 0.11167 | 0.11167 | 0.026027 | 0.026027 | 0 | 0 | 0.010206 | 0.010206 | 0 | 0 | 0.13992 | 0.13992 | 493 | 477 | Yes
2012-07-20 | 0.032233 | 0.032233 | 0 | 0 | 0.037095 | 0.037095 | 0 | 0 | 0.0038746 | 0.0038746 | 0.020406 | 0.020406 | 0 | 0 | 0.023624 | 0.023624 | 0 | 0 | 0.0014832 | 0.0014832 | 446 | 425 | Yes
2012-07-21 | 0.23111 | 0.23111 | 0 | 0 | 0.012348 | 0.012348 | 0 | 0 | 1.7847 | 1.7847 | 0.24249 | 0.24249 | 0 | 0 | 0.01299 | 0.01299 | 0 | 0 | 1.8723 | 1.8723 | 447 | 378 | Yes
2012-07-22 | 0.4098 | 0.4098 | 0 | 0 | 0.47231 | 0.47231 | 0 | 0 | 0.044443 | 0.044443 | 0.37935 | 0.37935 | 0 | 0 | 0.44123 | 0.44123 | 0 | 0 | 0.013349 | 0.013349 | 422 | 358 | Yes
2012-07-23 | 0.082823 | 0.031751 | 0 | 0 | 0.028634 | 0.028634 | 0.055641 | 0.055641 | 0.47117 | 0.057878 | 0.059814 | 0.028288 | 0 | 0 | 0.027407 | 0.027407 | 0.07728 | 0.07728 | 0.29319 | 0.03807 | 596 | 535 | Yes
2012-07-24 | 0.21076 | 0.21076 | 0 | 0 | 0.15606 | 0.15606 | 0.65224 | 0.65224 | 0.61615 | 0.61615 | 0.28581 | 0.28581 | 0 | 0 | 0.18557 | 0.18557 | 0.15456 | 0.15456 | 1.0254 | 1.0254 | 595 | 561 | Yes
2012-07-25 | 0.062941 | 0.062941 | 0 | 0 | 0.064211 | 0.064211 | 4.4757 | 4.4757 | 0.0072632 | 0.0072632 | 0.046434 | 0.046434 | 0 | 0 | 0.051174 | 0.051174 | 1.507 | 1.507 | 0.0019777 | 0.0019777 | 544 | 462 | Yes
2012-07-26 | 0.038231 | 0.038231 | 0 | 0 | 0.042294 | 0.042294 | 0.61515 | 0.61515 | 0.0085246 | 0.0085246 | 0.011792 | 0.011792 | 0 | 0 | 0.012776 | 0.012776 | 0.3864 | 0.3864 | 0.0019777 | 0.0019777 | 419 | 409 | Yes
2012-07-27 | 0.19516 | 0.19516 | 0 | 0 | 0.22208 | 0.22208 | 0 | 0 | 0.040891 | 0.040891 | 0.17669 | 0.17669 | 0 | 0 | 0.19977 | 0.19977 | 0 | 0 | 0.045981 | 0.045981 | 596 | 573 | Yes
2012-07-28 | 0.040152 | 0.040152 | 0 | 0 | 0.046783 | 0.046783 | 0 | 0 | 0.00084307 | 0.00084307 | 0.065007 | 0.065007 | 0 | 0 | 0.075869 | 0.075869 | 0 | 0 | 0.00049442 | 0.00049442 | 316 | 260 | Yes
2012-07-29 | 0.074319 | 0.074319 | 0 | 0 | 0.082371 | 0.082371 | 0.35835 | 0.35835 | 0.026223 | 0.026223 | 0.11175 | 0.11175 | 0 | 0 | 0.12869 | 0.12869 | 0.15456 | 0.15456 | 0.010877 | 0.010877 | 317 | 283 | Yes
2012-07-30 | 0.37244 | 0.37244 | 0 | 0 | 0.43125 | 0.43125 | 0.086553 | 0.086553 | 0.025442 | 0.025442 | 0.42921 | 0.42921 | 0 | 0 | 0.4959 | 0.4959 | 0.07728 | 0.07728 | 0.037082 | 0.037082 | 802 | 644 | Yes
2012-07-31 | 0.10733 | 0.10733 | 0 | 0 | 0.12389 | 0.12389 | 0 | 0 | 0.010302 | 0.010302 | 0.13814 | 0.13814 | 0 | 0 | 0.16116 | 0.16116 | 0 | 0 | 0.0014833 | 0.0014833 | 543 | 507 | Yes
2012-08-01 | 0.030262 | 0.030262 | 0 | 0 | 0.029493 | 0.029493 | 0.072463 | 0.072463 | 0.03966 | 0.03966 | 0.015702 | 0.015702 | 0 | 0 | 0.010563 | 0.010563 | 0.03864 | 0.03864 | 0.053398 | 0.053398 | 462 | 430 | Yes
2012-08-02 | 0.28993 | 0.28993 | 0 | 0 | 0.33835 | 0.33835 | 0 | 0 | 0.0023512 | 0.0023512 | 0.31405 | 0.31405 | 0 | 0 | 0.36672 | 0.36672 | 0 | 0 | 0.00098885 | 0.00098885 | 750 | 680 | Yes
2012-08-03 | 0.029876 | 0.029876 | 0 | 0 | 0.012605 | 0.012605 | 0 | 0 | 0.15444 | 0.15444 | 0.033176 | 0.033176 | 0 | 0 | 0.017344 | 0.017344 | 0 | 0 | 0.14833 | 0.14833 | 405 | 399 | Yes
2012-08-04 | 0.039811 | 0.039811 | 0 | 0 | 0.046393 | 0.046393 | 0 | 0 | 0.00078556 | 0.00078556 | 0.0545 | 0.0545 | 0 | 0 | 0.063523 | 0.063523 | 0 | 0 | 0.00098885 | 0.00098885 | 318 | 280 | Yes
2012-08-05 | 0.011664 | 0.011664 | 0 | 0 | 0.011807 | 0.011807 | 0 | 0 | 0.012595 | 0.012595 | 0.01448 | 0.01448 | 0 | 0 | 0.015488 | 0.015488 | 0 | 0 | 0.0098885 | 0.0098885 | 292 | 258 | Yes
2012-08-06 | 0.13603 | 0.13603 | 0 | 0 | 0.15257 | 0.15257 | 0 | 0 | 0.043984 | 0.043984 | 0.21329 | 0.21329 | 0 | 0 | 0.18736 | 0.18736 | 0 | 0 | 0.42817 | 0.42817 | 562 | 521 | Yes
2012-08-07 | 0.079035 | 0.079035 | 0 | 0 | 0.042261 | 0.042261 | 0 | 0 | 0.34682 | 0.34682 | 0.064887 | 0.064887 | 0 | 0 | 0.0099211 | 0.0099211 | 0 | 0 | 0.45636 | 0.45636 | 476 | 456 | Yes
2012-08-08 | 0.010715 | 0.010715 | 0.034197 | 0.034197 | 0.011476 | 0.011476 | 0.057276 | 0.057276 | 0.0012782 | 0.0012782 | 0.0088813 | 0.0088813 | 0.0032561 | 0.0032561 | 0.010018 | 0.010018 | 0.077399 | 0.077399 | 0.00099099 | 0.00099099 | 504 | 476 | Yes
2012-08-09 | 0.18032 | 0.18032 | 0 | 0 | 0.19907 | 0.19907 | 0.087108 | 0.087108 | 0.079145 | 0.079145 | 0.211 | 0.211 | 0 | 0 | 0.23274 | 0.23274 | 0.11614 | 0.11614 | 0.093752 | 0.093752 | 543 | 526 | Yes
2012-08-10 | 6.0893 | 6.0306 | 0 | 0 | 6.4553 | 6.3867 | 8.4351 | 8.4351 | 4.4511 | 4.4511 | 3.9704 | 3.2856 | 0 | 0 | 4.1201 | 3.3201 | 1.507 | 1.507 | 3.5698 | 3.5698 |  |  | Yes
2012-08-11 | 0.69685 | 0.69685 | 0.011794 | 0.011794 | 0.64661 | 0.64661 | 0 | 0 | 1.1582 | 1.1582 | 1.1777 | 1.1777 | 0.0032464 | 0.0032464 | 1.2588 | 1.2588 | 0 | 0 | 0.80937 | 0.80937 | 1841 | 954 | Yes
2012-08-12 | 0.072705 | 0.072705 | 0 | 0 | 0.065822 | 0.065822 | 0 | 0 | 0.13238 | 0.13238 | 0.05285 | 0.05285 | 0 | 0 | 0.037971 | 0.037971 | 0 | 0 | 0.16464 | 0.16464 | 706 | 365 | Yes
2012-08-13 | 0.02204 | 0.02204 | 0 | 0 | 0.016198 | 0.016198 | 0 | 0 | 0.066148 | 0.066148 | 0.019063 | 0.019063 | 0 | 0 | 0.010849 | 0.010849 | 0 | 0 | 0.079108 | 0.079108 | 626 | 599 | Yes
2012-08-14 | 0.011746 | 0.011746 | 0 | 0 | 0.013416 | 0.013416 | 0 | 0 | 0.002117 | 0.002117 | 0.0081261 | 0.0081261 | 0 | 0 | 0.0090646 | 0.0090646 | 0 | 0 | 0.0029666 | 0.0029666 | 507 | 499 | Yes
2012-08-15 | 0.034477 | 0.034477 | 0 | 0 | 0.03981 | 0.03981 | 0 | 0 | 0.003226 | 0.003226 | 0.061832 | 0.061832 | 0 | 0 | 0.071875 | 0.071875 | 0 | 0 | 0.0024721 | 0.0024721 | 522 | 482 | Yes
2012-08-16 | 0.067152 | 0.067152 | 0 | 0 | 0.056514 | 0.056514 | 0 | 0 | 0.15193 | 0.15193 | 0.21708 | 0.21708 | 0 | 0 | 0.20328 | 0.20328 | 0 | 0 | 0.34857 | 0.34857 | 487 | 422 | Yes
2012-08-17 | 0.44418 | 0.44418 | 0 | 0 | 0.28535 | 0.28535 | 0 | 0 | 1.6178 | 1.6178 | 0.34215 | 0.34215 | 0 | 0 | 0.2643 | 0.2643 | 0 | 0 | 0.93792 | 0.93792 | 1090 | 1031 | Yes
2012-08-18 | 0.22609 | 0.22609 | 0 | 0 | 0.24345 | 0.24345 | 0 | 0 | 0.1432 | 0.1432 | 0.3036 | 0.3036 | 0 | 0 | 0.34431 | 0.34431 | 0 | 0 | 0.071692 | 0.071692 | 628 | 450 | Yes
2012-08-19 | 0.10974 | 0.10974 | 0 | 0 | 0.12694 | 0.12694 | 0.10644 | 0.10644 | 0.0073717 | 0.0073717 | 0.065803 | 0.065803 | 0 | 0 | 0.075872 | 0.075872 | 0.15456 | 0.15456 | 0.0049443 | 0.0049443 | 254 | 219 | Yes
2012-08-20 | 0.031929 | 0.031929 | 0 | 0 | 0.0021528 | 0.0021528 | 0.094281 | 0.094281 | 0.24226 | 0.24226 | 0.049184 | 0.049184 | 0 | 0 | 0.00099925 | 0.00099925 | 0.07728 | 0.07728 | 0.3901 | 0.3901 | 562 | 526 | Yes
2012-08-21 | 0.18717 | 0.18717 | 0 | 0 | 0.16201 | 0.16201 | 0.023957 | 0.023957 | 0.39204 | 0.39204 | 0.2535 | 0.2535 | 0 | 0 | 0.18322 | 0.18322 | 0.07728 | 0.07728 | 0.78119 | 0.78119 | 712 | 543 | Yes
2012-08-22 | 0.0397 | 0.0397 | 0 | 0 | 0.0079468 | 0.0079468 | 0 | 0 | 0.26622 | 0.26622 | 0.06061 | 0.06061 | 0 | 0 | 0.0042111 | 0.0042111 | 0 | 0 | 0.4613 | 0.4613 | 512 | 486 | Yes
2012-08-23 | 1.8413 | 1.8413 | 0 | 0 | 1.9146 | 1.9146 | 1.2701 | 1.2701 | 1.621 | 1.621 | 1.0506 | 1.0506 | 0 | 0 | 1.0371 | 1.0371 | 0.69552 | 0.69552 | 1.3087 | 1.3087 | 2389 | 1678 | Yes
2012-08-24 | 0.34338 | 0.34323 | 0 | 0 | 0.34573 | 0.34573 | 0 | 0 | 0.38379 | 0.38257 | 0.23584 | 0.23572 | 0 | 0 | 0.23918 | 0.23918 | 0 | 0 | 0.25166 | 0.25067 | 1003 | 850 | Yes
2012-08-25 | 0.020819 | 0.020819 | 0.060708 | 0.060708 | 0.010557 | 0.010557 | 0 | 0 | 0.086096 | 0.086096 | 0.015763 | 0.015763 | 0.11038 | 0.11038 | 0.0057814 | 0.0057814 | 0 | 0 | 0.070703 | 0.070703 | 335 | 306 | Yes
2012-08-26 | 0.02291 | 0.02291 | 0 | 0 | 0.015497 | 0.015497 | 0 | 0 | 0.078042 | 0.078042 | 0.017963 | 0.017963 | 0 | 0 | 0.0092787 | 0.0092787 | 0 | 0 | 0.081086 | 0.081086 | 272 | 234 | Yes
2012-08-27 | 0.0095476 | 0.0095476 | 0 | 0 | 0.0096267 | 0.0096267 | 0 | 0 | 0.010575 | 0.010575 | 0.021568 | 0.021568 | 0 | 0 | 0.02491 | 0.02491 | 0 | 0 | 0.0019777 | 0.0019777 | 695 | 654 | Yes
2012-08-28 | 0.071242 | 0.071242 | 0 | 0 | 0.078901 | 0.078901 | 0 | 0 | 0.029952 | 0.029952 | 0.1489 | 0.1489 | 0 | 0 | 0.1733 | 0.1733 | 0 | 0 | 0.0044498 | 0.0044498 | 751 | 610 | Yes
2012-08-29 | 0.083884 | 0.083884 | 0.041202 | 0.041202 | 0.031851 | 0.031851 | 0 | 0 | 0.4519 | 0.4519 | 0.026883 | 0.026883 | 0.0032464 | 0.0032464 | 0.018986 | 0.018986 | 0 | 0 | 0.085536 | 0.085536 | 466 | 405 | Yes
2012-08-30 | 0.2477 | 0.2477 | 0.22972 | 0.22972 | 0.28056 | 0.28056 | 0 | 0 | 0.026021 | 0.026021 | 0.25942 | 0.25942 | 0.18829 | 0.18829 | 0.29778 | 0.29778 | 0 | 0 | 0.0079108 | 0.0079108 | 588 | 544 | Yes
2012-08-31 | 0.043807 | 0.043807 | 0 | 0 | 0.047888 | 0.047888 | 0 | 0 | 0.022769 | 0.022769 | 0.045885 | 0.045885 | 0 | 0 | 0.052318 | 0.052318 | 0 | 0 | 0.0088997 | 0.0088997 | 520 | 463 | Yes
2012-09-01 | 0.09537 | 0.09537 | 0 | 0 | 0.10821 | 0.10821 | 0 | 0 | 0.022155 | 0.022155 | 0.13436 | 0.13436 | 0 | 0 | 0.15281 | 0.15281 | 0 | 0 | 0.028677 | 0.028677 | 372 | 319 | Yes
2012-09-02 | 0.22278 | 0.22278 | 0 | 0 | 0.26014 | 0.26014 | 0 | 0 | 0.00076175 | 0.00076175 | 0.31985 | 0.31985 | 0 | 0 | 0.37358 | 0.37358 | 0 | 0 | 0.00049443 | 0.00049443 | 317 | 276 | Yes
2012-09-03 | 0.1782 | 0.1782 | 0 | 0 | 0.038042 | 0.038042 | 0 | 0 | 1.1785 | 1.1785 | 0.13686 | 0.13686 | 0 | 0 | 0.026266 | 0.026266 | 0 | 0 | 0.92557 | 0.92557 | 527 | 507 | Yes
2012-09-04 | 0.06394 | 0.06394 | 0 | 0 | 0.01327 | 0.01327 | 0 | 0 | 0.4255 | 0.4255 | 0.067147 | 0.067147 | 0 | 0 | 0.018201 | 0.018201 | 0 | 0 | 0.4173 | 0.4173 | 508 | 488 | Yes
2012-09-05 | 0.25623 | 0.25623 | 0 | 0 | 0.11684 | 0.11684 | 6.022 | 6.022 | 1.187 | 1.187 | 0.31991 | 0.31991 | 0 | 0 | 0.13083 | 0.13083 | 2.5889 | 2.5889 | 1.6494 | 1.6494 | 753 | 665 | Yes
2012-09-06 | 0.30153 | 0.30153 | 0 | 0 | 0.29165 | 0.29165 | 0 | 0 | 0.41977 | 0.41977 | 0.32816 | 0.32816 | 0 | 0 | 0.3436 | 0.3436 | 0 | 0 | 0.2754 | 0.2754 | 576 | 513 | Yes
2012-09-07 | 1.063 | 1.063 | 0 | 0 | 0.58537 | 0.58537 | 0.81867 | 0.81867 | 4.537 | 4.537 | 1.5743 | 1.5743 | 0 | 0 | 1.2449 | 1.2449 | 0.07728 | 0.07728 | 4.1151 | 4.1151 | 1108 | 973 | Yes
2012-09-08 | 0.0042043 | 0.0042043 | 0 | 0 | 0.0031189 | 0.0031189 | 0 | 0 | 0.012417 | 0.012417 | 0.0065376 | 0.0065376 | 0 | 0 | 0.0034974 | 0.0034974 | 0 | 0 | 0.028677 | 0.028677 | 305 | 273 | Yes
2012-09-09 | 0.023703 | 0.023703 | 0 | 0 | 0.026441 | 0.026441 | 0 | 0 | 0.0086525 | 0.0086525 | 0.01668 | 0.01668 | 0 | 0 | 0.01763 | 0.01763 | 0 | 0 | 0.012855 | 0.012855 | 262 | 220 | Yes
2012-09-10 | 0.11024 | 0.11024 | 0 | 0 | 0.12784 | 0.12784 | 0.080841 | 0.080841 | 0.0054261 | 0.0054261 | 0.083888 | 0.083888 | 0 | 0 | 0.096856 | 0.096856 | 0.03864 | 0.03864 | 0.0074164 | 0.0074164 | 496 | 480 | Yes
2012-09-11 | 0.13925 | 0.13925 | 0 | 0 | 0.12868 | 0.12868 | 0 | 0 | 0.23542 | 0.23542 | 0.13961 | 0.13961 | 0 | 0 | 0.13197 | 0.13197 | 0 | 0 | 0.21557 | 0.21557 | 470 | 425 | Yes
2012-09-12 | 0.31204 | 0.31204 | 0 | 0 | 0.19164 | 0.19164 | 0.034776 | 0.034776 | 1.1972 | 1.1972 | 0.29071 | 0.29071 | 0 | 0 | 0.2117 | 0.2117 | 0.07728 | 0.07728 | 0.88503 | 0.88503 | 408 | 389 | Yes
2012-09-13 | 0.4763 | 0.4763 | 0 | 0 | 0.026725 | 0.026725 | 0 | 0 | 3.6994 | 3.6994 | 0.35247 | 0.35247 | 0 | 0 | 0.060736 | 0.060736 | 0 | 0 | 2.4512 | 2.4512 | 791 | 678 | Yes
2012-09-14 | 0.095158 | 0.095158 | 0 | 0 | 0.011689 | 0.011689 | 0 | 0 | 0.69477 | 0.69477 | 0.12118 | 0.12118 | 0 | 0 | 0.011812 | 0.011812 | 0 | 0 | 0.90625 | 0.90625 | 553 | 544 | Yes
2012-09-15 | 0.0087919 | 0.0087919 | 0 | 0 | 0.0094216 | 0.0094216 | 0 | 0 | 0.0058518 | 0.0058518 | 0.0096357 | 0.0096357 | 0 | 0 | 0.010745 | 0.010745 | 0 | 0 | 0.0034837 | 0.0034837 | 314 | 279 | Yes
2012-09-16 | 0.1834 | 0.1834 | 0 | 0 | 0.21399 | 0.21399 | 0 | 0 | 0 | 0 | 0.12337 | 0.12337 | 0 | 0 | 0.14395 | 0.14395 | 0 | 0 | 0 | 0 | 368 | 296 | Yes
2012-09-17 | 0.23089 | 0.23089 | 0.13751 | 0.13751 | 0.19873 | 0.19873 | 14.3484 | 14.3484 | 0.28707 | 0.28707 | 0.21491 | 0.21491 | 0.13615 | 0.13615 | 0.20358 | 0.20358 | 8.2118 | 8.2118 | 0.20255 | 0.20255 | 626 | 534 | Yes
2012-09-18 | 0.97536 | 0.97536 | 0 | 0 | 0.64999 | 0.64999 | 5.3472 | 5.3472 | 3.346 | 3.346 | 0.9604 | 0.9604 | 0 | 0 | 0.61638 | 0.61638 | 1.2279 | 1.2279 | 3.5126 | 3.5126 | 908 | 630 | Yes
2012-09-19 | 0.10803 | 0.10803 | 0 | 0 | 0.10725 | 0.10725 | 0.27522 | 0.27522 | 0.12789 | 0.12789 | 0.11655 | 0.11655 | 0 | 0 | 0.12161 | 0.12161 | 0.076746 | 0.076746 | 0.099563 | 0.099563 | 532 | 503 | Yes
2012-09-20 | 0.020996 | 0.020996 | 0 | 0 | 0.015213 | 0.015213 | 0.1729 | 0.1729 | 0.062733 | 0.062733 | 0.0079248 | 0.0079248 | 0 | 0 | 0.0058318 | 0.0058318 | 0.038373 | 0.038373 | 0.023398 | 0.023398 | 433 | 426 | Yes
2012-09-21 | 0.59535 | 0.59535 | 0 | 0 | 0.68719 | 0.68719 | 0 | 0 | 0.051659 | 0.051659 | 0.51315 | 0.51315 | 0 | 0 | 0.59284 | 0.59284 | 0 | 0 | 0.040821 | 0.040821 | 494 | 477 | Yes
2012-09-22 | 0.034469 | 0.034469 | 0 | 0 | 0.0029535 | 0.0029535 | 5.7809 | 5.7809 | 0.18582 | 0.18582 | 0.029626 | 0.029626 | 0 | 0 | 0.0056183 | 0.0056183 | 4.3361 | 4.3361 | 0.14636 | 0.14636 | 276 | 251 | Yes
2012-09-23 | 0.023884 | 0.023884 | 0 | 0 | 0.027143 | 0.027143 | 0 | 0 | 0.0050478 | 0.0050478 | 0.019933 | 0.019933 | 0 | 0 | 0.022829 | 0.022829 | 0 | 0 | 0.0029869 | 0.0029869 | 262 | 234 | Yes
2012-09-24 | 0.10167 | 0.10167 | 0.10207 | 0.10207 | 0.10338 | 0.10338 | 0.063188 | 0.063188 | 0.09009 | 0.09009 | 0.10034 | 0.10034 | 0.029163 | 0.029163 | 0.11194 | 0.11194 | 0.038373 | 0.038373 | 0.030865 | 0.030865 | 469 | 447 | Yes
2012-09-25 | 0.62971 | 0.62971 | 0 | 0 | 0.73354 | 0.73354 | 0 | 0 | 0.0096135 | 0.0096135 | 0.94233 | 0.94233 | 0 | 0 | 1.0958 | 1.0958 | 0 | 0 | 0.027803 | 0.027803 | 556 | 522 | Yes
2012-09-26 | 0.07161 | 0.07161 | 0.2707 | 0.2707 | 0.055575 | 0.055575 | 0.045344 | 0.045344 | 0.15336 | 0.15336 | 0.091845 | 0.091845 | 0.13603 | 0.13603 | 0.096805 | 0.096805 | 0.038373 | 0.038373 | 0.051138 | 0.051138 | 449 | 433 | Yes
2012-09-27 | 0.04491 | 0.04491 | 0 | 0 | 0.038983 | 0.038983 | 0.083525 | 0.083525 | 0.092666 | 0.092666 | 0.029254 | 0.029254 | 0 | 0 | 0.013657 | 0.013657 | 0.076746 | 0.076746 | 0.14199 | 0.14199 | 432 | 420 | Yes
2012-09-28 | 0.23834 | 0.23834 | 0 | 0 | 0.24558 | 0.24558 | 0.029931 | 0.029931 | 0.22703 | 0.22703 | 0.27602 | 0.27602 | 0 | 0 | 0.23551 | 0.23551 | 0.038373 | 0.038373 | 0.60422 | 0.60422 | 600 | 582 | Yes
2012-09-29 | 0.23055 | 0.23055 | 0 | 0 | 0.13055 | 0.13055 | 49.4731 | 49.4731 | 0.32685 | 0.32685 | 0.27078 | 0.27078 | 0 | 0 | 0.1939 | 0.1939 | 43.4766 | 43.4766 | 0.28995 | 0.28995 | 518 | 383 | Yes
2012-09-30 | 0.028373 | 0.028373 | 0.068636 | 0.068636 | 0.031041 | 0.031041 | 0 | 0 | 0.0039422 | 0.0039422 | 0.061799 | 0.061799 | 0.12308 | 0.12308 | 0.069137 | 0.069137 | 0 | 0 | 0.0019859 | 0.0019859 | 210 | 171 | Yes
2012-10-01 | 0.3328 | 0.3328 | 0 | 0 | 0.36665 | 0.36665 | 0 | 0 | 0.15179 | 0.15179 | 0.46635 | 0.46635 | 0 | 0 | 0.53268 | 0.53268 | 0 | 0 | 0.080927 | 0.080927 | 829 | 329 | Yes
2012-10-02 | 0.51391 | 0.51391 | 26.4647 | 26.4647 | 0.014563 | 0.014563 | 0 | 0 | 0.027106 | 0.027106 | 0.1098 | 0.1098 | 4.8041 | 4.8041 | 0.016351 | 0.016351 | 0 | 0 | 0.043773 | 0.043773 | 575 | 550 | Yes
2012-10-03 | 0.14983 | 0.14983 | 0 | 0 | 0.074998 | 0.074998 | 0 | 0 | 0.69837 | 0.69837 | 0.22051 | 0.22051 | 0 | 0 | 0.11808 | 0.11808 | 0 | 0 | 0.97396 | 0.97396 | 733 | 659 | Yes
2012-10-04 | 0.029485 | 0.029485 | 0.0044227 | 0.0044227 | 0.033961 | 0.033961 | 0 | 0 | 0.0023983 | 0.0023983 | 0.020595 | 0.020595 | 0.0032373 | 0.0032373 | 0.023673 | 0.023673 | 0 | 0 | 0.0019897 | 0.0019897 | 613 | 549 | Yes
2012-10-05 | 0.030876 | 0.030876 | 0 | 0 | 0.034355 | 0.034355 | 0 | 0 | 0.011676 | 0.011676 | 0.029477 | 0.029477 | 0 | 0 | 0.0319 | 0.0319 | 0 | 0 | 0.017436 | 0.017436 | 536 | 495 | Yes
2012-10-06 | 2.0611 | 2.0611 | 0 | 0 | 2.3979 | 2.3979 | 0 | 0 | 0.04791 | 0.04791 | 1.7917 | 1.7917 | 0 | 0 | 2.0805 | 2.0805 | 0 | 0 | 0.069744 | 0.069744 | 1347 | 543 | Yes
2012-10-07 | 0.13589 | 0.13589 | 0 | 0 | 0.14202 | 0.14202 | 1.3216 | 1.3216 | 0.09847 | 0.09847 | 0.14391 | 0.14391 | 0 | 0 | 0.15686 | 0.15686 | 0.49923 | 0.49923 | 0.070741 | 0.070741 | 245 | 219 | Yes
2012-10-08 | 0.019488 | 0.019488 | 0 | 0 | 0.021868 | 0.021868 | 0 | 0 | 0.0060797 | 0.0060797 | 0.020811 | 0.020811 | 0 | 0 | 0.023711 | 0.023711 | 0 | 0 | 0.0039854 | 0.0039854 | 641 | 593 | Yes
2012-10-09 | 0.081352 | 0.081352 | 0 | 0 | 0.093788 | 0.093788 | 0.1315 | 0.1315 | 0.0061891 | 0.0061891 | 0.11588 | 0.11588 | 0 | 0 | 0.13428 | 0.13428 | 0.23024 | 0.23024 | 0.0034818 | 0.0034818 | 743 | 664 | Yes
2012-10-10 | 0.039417 | 0.039417 | 0 | 0 | 0.043994 | 0.043994 | 0 | 0 | 0.013959 | 0.013959 | 0.037348 | 0.037348 | 0 | 0 | 0.039168 | 0.039168 | 0 | 0 | 0.030838 | 0.030838 | 808 | 724 | Yes
2012-10-11 | 0.099041 | 0.099041 | 0 | 0 | 0.087769 | 0.087769 | 0.11972 | 0.11972 | 0.19287 | 0.19287 | 0.062877 | 0.062877 | 0 | 0 | 0.052461 | 0.052461 | 0.076746 | 0.076746 | 0.14524 | 0.14524 | 730 | 678 | Yes
2012-10-12 | 0.043699 | 0.043699 | 0.58499 | 0.58499 | 0.0081175 | 0.0081175 | 0 | 0 | 0.21005 | 0.21005 | 0.037958 | 0.037958 | 0.27513 | 0.27513 | 0.014501 | 0.014501 | 0 | 0 | 0.16613 | 0.16613 | 664 | 634 | Yes
2012-10-13 | 0.032995 | 0.032995 | 1.1582 | 1.1582 | 0.01295 | 0.01295 | 0 | 0 | 0.00076093 | 0.00076093 | 0.011089 | 0.011089 | 0.13594 | 0.13594 | 0.0098809 | 0.0098809 | 0 | 0 | 0.0004974 | 0.0004974 | 327 | 281 | Yes
2012-10-14 | 0.031182 | 0.031182 | 0 | 0 | 0.032995 | 0.032995 | 0 | 0 | 0.02369 | 0.02369 | 0.085725 | 0.085725 | 0 | 0 | 0.09426 | 0.09426 | 0 | 0 | 0.040289 | 0.040289 | 189 | 170 | Yes
2012-10-15 | 0.22722 | 0.22722 | 0 | 0 | 0.26385 | 0.26385 | 0 | 0 | 0.0087485 | 0.0087485 | 0.32096 | 0.32096 | 0 | 0 | 0.37327 | 0.37327 | 0 | 0 | 0.0084557 | 0.0084557 | 637 | 594 | Yes
2012-10-16 | 0.12848 | 0.12848 | 0 | 0 | 0.10635 | 0.10635 | 0.20406 | 0.20406 | 0.30212 | 0.30212 | 0.19011 | 0.19011 | 0 | 0 | 0.16923 | 0.16923 | 0.076775 | 0.076775 | 0.36694 | 0.36694 | 640 | 590 | Yes
2012-10-17 | 0.38037 | 0.38037 | 0 | 0 | 0.34547 | 0.34547 | 19.0949 | 19.0949 | 0.44068 | 0.44068 | 0.21977 | 0.21977 | 0 | 0 | 0.18152 | 0.18152 | 5.4127 | 5.4127 | 0.45396 | 0.45396 | 699 | 672 | Yes
2012-10-18 | 0.079982 | 0.079982 | 0 | 0 | 0.08631 | 0.08631 | 0.066795 | 0.066795 | 0.048158 | 0.048158 | 0.10115 | 0.10115 | 0 | 0 | 0.11339 | 0.11339 | 0.11516 | 0.11516 | 0.030827 | 0.030827 | 546 | 527 | Yes
2012-10-19 | 0.068802 | 0.068802 | 0 | 0 | 0.069833 | 0.069833 | 0.4979 | 0.4979 | 0.066595 | 0.066595 | 0.13726 | 0.13726 | 0 | 0 | 0.14721 | 0.14721 | 0.65259 | 0.65259 | 0.08204 | 0.08204 | 610 | 570 | Yes
2012-10-20 | 0.22802 | 0.22802 | 0 | 0 | 0.26552 | 0.26552 | 0 | 0 | 0.0035799 | 0.0035799 | 0.40726 | 0.40726 | 0 | 0 | 0.47281 | 0.47281 | 0 | 0 | 0.016408 | 0.016408 | 639 | 350 | Yes
2012-10-21 | 0.11502 | 0.11502 | 0 | 0 | 0.042356 | 0.042356 | 0 | 0 | 0.64269 | 0.64269 | 0.065218 | 0.065218 | 0 | 0 | 0.052005 | 0.052005 | 0 | 0 | 0.16856 | 0.16856 | 229 | 218 | Yes
2012-10-22 | 0.91157 | 0.91157 | 0 | 0 | 0.60747 | 0.60747 | 2.4417 | 2.4417 | 3.1601 | 3.1601 | 0.75266 | 0.75266 | 0 | 0 | 0.48609 | 0.48609 | 1.5355 | 1.5355 | 2.7237 | 2.7237 | 1339 | 1177 | Yes
2012-10-23 | 0.067575 | 0.067575 | 0 | 0 | 0.01928 | 0.01928 | 0 | 0 | 0.41675 | 0.41675 | 0.064525 | 0.064525 | 0 | 0 | 0.011861 | 0.011861 | 0 | 0 | 0.44376 | 0.44376 | 786 | 732 | Yes
2012-10-24 | 0.31939 | 0.31939 | 0 | 0 | 0.13325 | 0.13325 | 0 | 0 | 1.675 | 1.675 | 0.23113 | 0.23113 | 0 | 0 | 0.16612 | 0.16612 | 0 | 0 | 0.72452 | 0.72452 | 758 | 664 | Yes
2012-10-25 | 0.14777 | 0.14777 | 0 | 0 | 0.12805 | 0.12805 | 0 | 0 | 0.31043 | 0.31043 | 0.17556 | 0.17556 | 0 | 0 | 0.20142 | 0.20142 | 0 | 0 | 0.023853 | 0.023853 | 591 | 500 | Yes
2012-10-26 | 0.10215 | 0.10215 | 0 | 0 | 0.017954 | 0.017954 | 9.7066 | 9.7066 | 0.58254 | 0.58254 | 0.10513 | 0.10513 | 0 | 0 | 0.013068 | 0.013068 | 12.3897 | 12.3897 | 0.60626 | 0.60626 | 519 | 473 | Yes
2012-10-27 | 0.11221 | 0.11221 | 0 | 0 | 0.13043 | 0.13043 | 0 | 0 | 0.0034403 | 0.0034403 | 0.10872 | 0.10872 | 0 | 0 | 0.12663 | 0.12663 | 0 | 0 | 0.0014908 | 0.0014908 | 370 | 268 | Yes
2012-10-28 | 0.17548 | 0.17548 | 0 | 0 | 0.17448 | 0.17448 | 1.1224 | 1.1224 | 0.19715 | 0.19715 | 0.42075 | 0.42075 | 0 | 0 | 0.42393 | 0.42393 | 1.4576 | 1.4576 | 0.44972 | 0.44972 | 904 | 213 | Yes
2012-10-29 | 0.055943 | 0.055943 | 0 | 0 | 0.064244 | 0.064244 | 0 | 0 | 0.0071865 | 0.0071865 | 0.051742 | 0.051742 | 0 | 0 | 0.05973 | 0.05973 | 0 | 0 | 0.0044724 | 0.0044724 | 607 | 594 | Yes
2012-10-30 | 0.072434 | 0.072434 | 0 | 0 | 0.075916 | 0.075916 | 0.087457 | 0.087457 | 0.05894 | 0.05894 | 0.65594 | 0.65594 | 0 | 0 | 0.75997 | 0.75997 | 0.076717 | 0.076717 | 0.033422 | 0.033422 | 694 | 580 | Yes
2012-10-31 | 0.2647 | 0.2647 | 0 | 0 | 0.29363 | 0.29363 | 0 | 0 | 0.1056 | 0.1056 | 0.45717 | 0.45717 | 0 | 0 | 0.40301 | 0.40301 | 0 | 0 | 0.91438 | 0.91438 | 594 | 525 | Yes
2012-11-01 | 0.30315 | 0.30315 | 0 | 0 | 0.22213 | 0.22213 | 0 | 0 | 0.9234 | 0.9234 | 0.49819 | 0.49819 | 0 | 0 | 0.35781 | 0.35781 | 0 | 0 | 1.5684 | 1.5684 | 629 | 599 | Yes
2012-11-02 | 0.059123 | 0.059123 | 0 | 0 | 0.067826 | 0.067826 | 0 | 0 | 0.0078423 | 0.0078423 | 0.063963 | 0.063963 | 0 | 0 | 0.072882 | 0.072882 | 0 | 0 | 0.011972 | 0.011972 | 578 | 547 | Yes
2012-11-03 | 0.038867 | 0.038867 | 0 | 0 | 0.036913 | 0.036913 | 0 | 0 | 0.059102 | 0.059102 | 0.042541 | 0.042541 | 0 | 0 | 0.036051 | 0.036051 | 0 | 0 | 0.095278 | 0.095278 | 415 | 315 | Yes
2012-11-04 | 0.15315 | 0.15315 | 0.064279 | 0.064279 | 0.17176 | 0.17176 | 0.75711 | 0.75711 | 0.028199 | 0.028199 | 0.094332 | 0.094332 | 0.12604 | 0.12604 | 0.1024 | 0.1024 | 0.88224 | 0.88224 | 0.022448 | 0.022448 | 261 | 231 | Yes
2012-11-05 | 0.04922 | 0.04922 | 0 | 0 | 0.042778 | 0.042778 | 0 | 0 | 0.10274 | 0.10274 | 0.051548 | 0.051548 | 0 | 0 | 0.031935 | 0.031935 | 0 | 0 | 0.19804 | 0.19804 | 675 | 651 | Yes
2012-11-06 | 0.22315 | 0.22315 | 0 | 0 | 0.24114 | 0.24114 | 0 | 0 | 0.13404 | 0.13404 | 0.30929 | 0.30929 | 0 | 0 | 0.30469 | 0.30469 | 0 | 0 | 0.39342 | 0.39342 | 787 | 598 | Yes
2012-11-07 | 0.15112 | 0.15112 | 0 | 0 | 0.1651 | 0.1651 | 0 | 0 | 0.078133 | 0.078133 | 0.15839 | 0.15839 | 0 | 0 | 0.17448 | 0.17448 | 0 | 0 | 0.071802 | 0.071802 | 654 | 591 | Yes
2012-11-08 | 0.27935 | 0.27935 | 0 | 0 | 0.19733 | 0.19733 | 0.013753 | 0.013753 | 0.90233 | 0.90233 | 0.29834 | 0.29834 | 0 | 0 | 0.22344 | 0.22344 | 0.038344 | 0.038344 | 0.8741 | 0.8741 | 890 | 825 | Yes
2012-11-09 | 0.94055 | 0.94055 | 0 | 0 | 0.86564 | 0.86564 | 0.034816 | 0.034816 | 1.6238 | 1.6238 | 0.75209 | 0.75209 | 0 | 0 | 0.61881 | 0.61881 | 0.038344 | 0.038344 | 1.814 | 1.814 | 1054 | 878 | Yes
2012-11-10 | 0.24308 | 0.24308 | 0 | 0 | 0.18696 | 0.18696 | 0.028758 | 0.028758 | 0.67777 | 0.67777 | 0.22922 | 0.22922 | 0 | 0 | 0.18825 | 0.18825 | 0.038344 | 0.038344 | 0.55498 | 0.55498 | 347 | 272 | Yes
2012-11-11 | 0.080955 | 0.080955 | 0 | 0 | 0.024103 | 0.024103 | 0 | 0 | 0.49401 | 0.49401 | 0.1161 | 0.1161 | 0 | 0 | 0.0089405 | 0.0089405 | 0 | 0 | 0.88856 | 0.88856 | 196 | 178 | Yes
2012-11-12 | 0.13501 | 0.13501 | 0 | 0 | 0.13054 | 0.13054 | 0.38804 | 0.38804 | 0.18389 | 0.18389 | 0.14312 | 0.14312 | 0 | 0 | 0.12935 | 0.12935 | 0.076687 | 0.076687 | 0.26278 | 0.26278 | 647 | 626 | Yes
2012-11-13 | 0.19453 | 0.19453 | 0 | 0 | 0.22655 | 0.22655 | 0 | 0 | 0.0020586 | 0.0020586 | 0.29161 | 0.29161 | 0 | 0 | 0.33977 | 0.33977 | 0 | 0 | 0.0019942 | 0.0019942 | 774 | 559 | Yes
2012-11-14 | 0.019132 | 0.019132 | 0 | 0 | 0.021807 | 0.021807 | 0 | 0 | 0.0035336 | 0.0035336 | 0.0040763 | 0.0040763 | 0 | 0 | 0.0044697 | 0.0044697 | 0 | 0 | 0.0019941 | 0.0019941 | 488 | 470 | Yes
2012-11-15 | 0.020158 | 0.020158 | 0 | 0 | 0.017637 | 0.017637 | 0 | 0 | 0.041247 | 0.041247 | 0.0096129 | 0.0096129 | 0 | 0 | 0.0049664 | 0.0049664 | 0 | 0 | 0.043871 | 0.043871 | 463 | 441 | Yes
2012-11-16 | 0.058343 | 0.058343 | 0 | 0 | 0.049849 | 0.049849 | 0 | 0 | 0.12779 | 0.12779 | 0.070819 | 0.070819 | 0 | 0 | 0.024477 | 0.024477 | 0 | 0 | 0.4083 | 0.4083 | 651 | 593 | Yes
2012-11-17 | 0.01586 | 0.01586 | 0 | 0 | 0.00087132 | 0.00087132 | 0.36142 | 0.36142 | 0.11914 | 0.11914 | 0.010526 | 0.010526 | 0 | 0 | 0.00028379 | 0.00028379 | 0.19172 | 0.19172 | 0.081759 | 0.081759 | 270 | 242 | Yes
2012-11-18 | 0.040913 | 0.040913 | 0 | 0 | 0.047215 | 0.047215 | 0 | 0 | 0.0034758 | 0.0034758 | 0.054879 | 0.054879 | 0 | 0 | 0.063712 | 0.063712 | 0 | 0 | 0.0019941 | 0.0019941 | 262 | 255 | Yes
2012-11-19 | 0.25287 | 0.25287 | 0 | 0 | 0.1952 | 0.1952 | 0.063586 | 0.063586 | 0.69957 | 0.69957 | 0.30919 | 0.30919 | 0 | 0 | 0.18106 | 0.18106 | 0.038344 | 0.038344 | 1.2608 | 1.2608 | 817 | 744 | Yes
2012-11-20 | 0.072904 | 0.072904 | 0 | 0 | 0.022529 | 0.022529 | 0.50345 | 0.50345 | 0.43244 | 0.43244 | 0.085837 | 0.085837 | 0 | 0 | 0.080095 | 0.080095 | 0.49847 | 0.49847 | 0.13406 | 0.13406 | 572 | 524 | Yes
2012-11-21 | 0.01583 | 0.01583 | 0 | 0 | 0.017975 | 0.017975 | 0 | 0 | 0.0034179 | 0.0034179 | 0.0071181 | 0.0071181 | 0 | 0 | 0.0080171 | 0.0080171 | 0 | 0 | 0.0019935 | 0.0019935 | 472 | 459 | Yes
2012-11-22 | 0.12706 | 0.12706 | 0 | 0 | 0.13744 | 0.13744 | 0 | 0 | 0.075377 | 0.075377 | 0.11036 | 0.11036 | 0 | 0 | 0.12124 | 0.12124 | 0 | 0 | 0.05233 | 0.05233 | 500 | 480 | Yes
2012-11-23 | 0.017624 | 0.017624 | 0 | 0 | 0.014614 | 0.014614 | 0 | 0 | 0.041716 | 0.041716 | 0.016182 | 0.016182 | 0 | 0 | 0.013196 | 0.013196 | 0 | 0 | 0.03987 | 0.03987 | 574 | 551 | Yes
2012-11-24 | 0.020864 | 0.020864 | 0 | 0 | 0.014533 | 0.014533 | 0 | 0 | 0.06883 | 0.06883 | 0.027315 | 0.027315 | 0 | 0 | 0.025469 | 0.025469 | 0 | 0 | 0.044854 | 0.044854 | 262 | 241 | Yes
2012-11-25 | 0.34797 | 0.34797 | 0 | 0 | 0.29318 | 0.29318 | 0.38729 | 0.38729 | 0.78611 | 0.78611 | 0.41344 | 0.41344 | 0 | 0 | 0.41992 | 0.41992 | 0.2684 | 0.2684 | 0.43359 | 0.43359 | 380 | 314 | Yes
2012-11-26 | 0.54705 | 0.54705 | 0 | 0 | 0.41073 | 0.41073 | 0.15759 | 0.15759 | 1.5942 | 1.5942 | 1.1179 | 1.1179 | 0 | 0 | 1.1081 | 1.1081 | 0.15337 | 0.15337 | 1.372 | 1.372 | 1024 | 786 | Yes
2012-11-27 | 0.28098 | 0.28098 | 0 | 0 | 0.28534 | 0.28534 | 0.16005 | 0.16005 | 0.29529 | 0.29529 | 0.23842 | 0.23842 | 0 | 0 | 0.25961 | 0.25961 | 0.076687 | 0.076687 | 0.1285 | 0.1285 | 810 | 727 | Yes
2012-11-28 | 0.11983 | 0.11983 | 0 | 0 | 0.024299 | 0.024299 | 0.087366 | 0.087366 | 0.80934 | 0.80934 | 0.12575 | 0.12575 | 0 | 0 | 0.03576 | 0.03576 | 0.038344 | 0.038344 | 0.77797 | 0.77797 | 635 | 587 | Yes
2012-11-29 | 0.27276 | 0.27276 | 0 | 0 | 0.17929 | 0.17929 | 0.76658 | 0.76658 | 0.96459 | 0.96459 | 0.33125 | 0.33125 | 0 | 0 | 0.25479 | 0.25479 | 0.72853 | 0.72853 | 0.91394 | 0.91394 | 628 | 514 | Yes
2012-11-30 | 0.17686 | 0.17686 | 0 | 0 | 0.14886 | 0.14886 | 2.5369 | 2.5369 | 0.37002 | 0.37002 | 0.20271 | 0.20271 | 0 | 0 | 0.13197 | 0.13197 | 2.9908 | 2.9908 | 0.6943 | 0.6943 | 833 | 718 | Yes
2012-12-01 | 0.70159 | 0.70159 | 0 | 0 | 0.15026 | 0.15026 | 0.25996 | 0.25996 | 4.6857 | 4.6857 | 0.37001 | 0.37001 | 0 | 0 | 0.23478 | 0.23478 | 0.15337 | 0.15337 | 1.3791 | 1.3791 | 803 | 477 | Yes
2012-12-02 | 0.64143 | 0.64143 | 0 | 0 | 0.19809 | 0.19809 | 71.9209 | 71.9209 | 2.9266 | 2.9266 | 0.29001 | 0.29001 | 0 | 0 | 0.20214 | 0.20214 | 16.296 | 16.296 | 0.74361 | 0.74361 | 533 | 404 | Yes
2012-12-03 | 0.099774 | 0.099774 | 0 | 0 | 0.021365 | 0.021365 | 0.13344 | 0.13344 | 0.66513 | 0.66513 | 0.11887 | 0.11887 | 0 | 0 | 0.010572 | 0.010572 | 0.11503 | 0.11503 | 0.89751 | 0.89751 | 649 | 605 | Yes
2012-12-04 | 0.2073 | 0.2073 | 0 | 0 | 0.21892 | 0.21892 | 0.06303 | 0.06303 | 0.15957 | 0.15957 | 0.16213 | 0.16213 | 0 | 0 | 0.17979 | 0.17979 | 0.038344 | 0.038344 | 0.064748 | 0.064748 | 636 | 572 | Yes
2012-12-05 | 0.14994 | 0.14994 | 0 | 0 | 0.16635 | 0.16635 | 0 | 0 | 0.059831 | 0.059831 | 0.11273 | 0.11273 | 0 | 0 | 0.11721 | 0.11721 | 0 | 0 | 0.10011 | 0.10011 | 686 | 629 | Yes
2012-12-06 | 0.039483 | 0.039483 | 0 | 0 | 0.01848 | 0.01848 | 2.4294 | 2.4294 | 0.16196 | 0.16196 | 0.025917 | 0.025917 | 0 | 0 | 0.017809 | 0.017809 | 1.2653 | 1.2653 | 0.070726 | 0.070726 | 491 | 476 | Yes
2012-12-07 | 0.063129 | 0.061001 | 0 | 0 | 0.068676 | 0.068676 | 0.25056 | 0.25056 | 0.031487 | 0.014063 | 0.19578 | 0.19572 | 0 | 0 | 0.22549 | 0.22549 | 0.11503 | 0.11503 | 0.018429 | 0.017931 | 422 | 402 | Yes
2012-12-08 | 0.15378 | 0.15378 | 0 | 0 | 0.1264 | 0.1264 | 0 | 0 | 0.3717 | 0.3717 | 0.30401 | 0.30401 | 0 | 0 | 0.23507 | 0.23507 | 0 | 0 | 0.83876 | 0.83876 | 383 | 281 | Yes
2012-12-09 | 0.56551 | 0.56551 | 0 | 0 | 0.58954 | 0.58954 | 0.50856 | 0.50856 | 0.48476 | 0.48476 | 0.58502 | 0.58502 | 0 | 0 | 0.56167 | 0.56167 | 0.69018 | 0.69018 | 0.83776 | 0.83776 | 951 | 601 | Yes
2012-12-10 | 0.33739 | 0.33739 | 0 | 0 | 0.25857 | 0.25857 | 0.10084 | 0.10084 | 0.94582 | 0.94582 | 0.4864 | 0.4864 | 0 | 0 | 0.3901 | 0.3901 | 0.038344 | 0.038344 | 1.2432 | 1.2432 | 819 | 676 | Yes
2012-12-11 | 0.060699 | 0.060699 | 0 | 0 | 0.067593 | 0.067593 | 0.60123 | 0.60123 | 0.01273 | 0.01273 | 0.11638 | 0.11638 | 0 | 0 | 0.134 | 0.134 | 0.15337 | 0.15337 | 0.0056762 | 0.0056762 | 585 | 508 | Yes
2012-12-12 | 0.11937 | 0.11937 | 0 | 0 | 0.13145 | 0.13145 | 0 | 0 | 0.051783 | 0.051783 | 0.17679 | 0.17679 | 0 | 0 | 0.19782 | 0.19782 | 0 | 0 | 0.053666 | 0.053666 | 681 | 593 | Yes
2012-12-13 | 0.18023 | 0.18023 | 0 | 0 | 0.20837 | 0.20837 | 0.027607 | 0.027607 | 0.0053694 | 0.0053694 | 0.19054 | 0.19054 | 0 | 0 | 0.22049 | 0.22049 | 0.038344 | 0.038344 | 0.0041282 | 0.0041282 | 608 | 544 | Yes
2012-12-14 | 0.056179 | 0.056179 | 0 | 0 | 0.040603 | 0.040603 | 0 | 0 | 0.17975 | 0.17975 | 0.087056 | 0.087056 | 0 | 0 | 0.084015 | 0.084015 | 0 | 0 | 0.12436 | 0.12436 | 556 | 514 | Yes
2012-12-15 | 0.054083 | 0.054083 | 0 | 0 | 0.059607 | 0.059607 | 0.31058 | 0.31058 | 0.018901 | 0.018901 | 0.076593 | 0.076593 | 0 | 0 | 0.075261 | 0.075261 | 0.23006 | 0.23006 | 0.096497 | 0.096497 | 363 | 307 | Yes
2012-12-16 | 0.055317 | 0.055317 | 0 | 0 | 0.023171 | 0.023171 | 0 | 0 | 0.29985 | 0.29985 | 0.031635 | 0.031635 | 0 | 0 | 0.013767 | 0.013767 | 0 | 0 | 0.16771 | 0.16771 | 318 | 282 | Yes
2012-12-17 | 0.10565 | 0.10565 | 0 | 0 | 0.11788 | 0.11788 | 0.6773 | 0.6773 | 0.025441 | 0.025441 | 0.18908 | 0.18908 | 0 | 0 | 0.21639 | 0.21639 | 0.8819 | 0.8819 | 0.010321 | 0.010321 | 573 | 533 | Yes
2012-12-18 | 0.090758 | 0.090758 | 0 | 0 | 0.06565 | 0.06565 | 0 | 0 | 0.28999 | 0.28999 | 0.087483 | 0.087483 | 0 | 0 | 0.071802 | 0.071802 | 0 | 0 | 0.21725 | 0.21725 | 543 | 499 | Yes
2012-12-19 | 0.088442 | 0.088442 | 0 | 0 | 0.076424 | 0.076424 | 7.2719 | 7.2719 | 0.093734 | 0.093734 | 0.049764 | 0.049764 | 0 | 0 | 0.045185 | 0.045185 | 2.9525 | 2.9525 | 0.052119 | 0.052119 | 606 | 530 | Yes
2012-12-20 | 0.13401 | 0.13401 | 0 | 0 | 0.075794 | 0.075794 | 0 | 0 | 0.58272 | 0.58272 | 0.43784 | 0.43784 | 0 | 0 | 0.22423 | 0.22423 | 0 | 0 | 2.075 | 2.075 | 662 | 474 | Yes
2012-12-21 | 0.0075574 | 0.0075574 | 0 | 0 | 0.0027777 | 0.0027777 | 0 | 0 | 0.043801 | 0.043801 | 0.11291 | 0.11291 | 0 | 0 | 0.0052246 | 0.0052246 | 0 | 0 | 0.91957 | 0.91957 | 382 | 374 | Yes
2012-12-22 | 0.010251 | 0.010251 | 0 | 0 | 0.010735 | 0.010735 | 0 | 0 | 0.0084914 | 0.0084914 | 0.0099164 | 0.0099164 | 0 | 0 | 0.010661 | 0.010661 | 0 | 0 | 0.0061924 | 0.0061924 | 353 | 281 | Yes
2012-12-23 | 0.104 | 0.104 | 0 | 0 | 0.11088 | 0.11088 | 0 | 0 | 0.071715 | 0.071715 | 0.22899 | 0.22899 | 0 | 0 | 0.24414 | 0.24414 | 0 | 0 | 0.15791 | 0.15791 | 324 | 282 | Yes
2012-12-24 | 0.57171 | 0.57171 | 0 | 0 | 0.47944 | 0.47944 | 0.17084 | 0.17084 | 1.3428 | 1.3428 | 0.3882 | 0.3882 | 0 | 0 | 0.11445 | 0.11445 | 0.038358 | 0.038358 | 2.4558 | 2.4558 | 762 | 629 | Yes
2012-12-25 | 0.52594 | 0.52594 | 0 | 0 | 0.12391 | 0.12391 | 0.97739 | 0.97739 | 3.5603 | 3.5603 | 0.68406 | 0.68406 | 0 | 0 | 0.15391 | 0.15391 | 0.84291 | 0.84291 | 4.6897 | 4.6897 | 703 | 447 | Yes
2012-12-26 | 0.2037 | 0.2037 | 0 | 0 | 0.01696 | 0.01696 | 0.2907 | 0.2907 | 1.6082 | 1.6082 | 0.099703 | 0.099703 | 0 | 0 | 0.010928 | 0.010928 | 0.19157 | 0.19157 | 0.76719 | 0.76719 | 327 | 258 | Yes
2012-12-27 | 0.084047 | 0.084047 | 0 | 0 | 0.084864 | 0.084864 | 0.23898 | 0.23898 | 0.089457 | 0.089457 | 0.12208 | 0.12208 | 0 | 0 | 0.13205 | 0.13205 | 0.11494 | 0.11494 | 0.068425 | 0.068425 | 322 | 313 | Yes
2012-12-28 | 0.23496 | 0.23496 | 0 | 0 | 0.24002 | 0.24002 | 0.045977 | 0.045977 | 0.238 | 0.238 | 0.29229 | 0.29229 | 0 | 0 | 0.30922 | 0.30922 | 0.038314 | 0.038314 | 0.21824 | 0.21824 | 665 | 607 | Yes
2012-12-29 | 0.0071775 | 0.0071775 | 0 | 0 | 0.004583 | 0.004583 | 0.045977 | 0.045977 | 0.026883 | 0.026883 | 0.012159 | 0.012159 | 0 | 0 | 0.010011 | 0.010011 | 0.076628 | 0.076628 | 0.029029 | 0.029029 | 238 | 212 | Yes
2012-12-30 | 0.14838 | 0.14838 | 0 | 0 | 0.010485 | 0.010485 | 0 | 0 | 1.1881 | 1.1881 | 0.17588 | 0.17588 | 0 | 0 | 0.012267 | 0.012267 | 0 | 0 | 1.4095 | 1.4095 | 268 | 256 | Yes
2012-12-31 | 0.045966 | 0.045966 | 0 | 0 | 0.019653 | 0.019653 | 0.035485 | 0.035485 | 0.24696 | 0.24696 | 0.03988 | 0.03988 | 0 | 0 | 0.020375 | 0.020375 | 0.038314 | 0.038314 | 0.18973 | 0.18973 | 386 | 370 | Yes
2013-01-01 | 0.12374 | 0.12374 | 0 | 0 | 0.13218 | 0.13218 | 3.5662 | 3.5662 | 0.036371 | 0.036371 | 0.1687 | 0.1687 | 0 | 0 | 0.19188 | 0.19188 | 0.91884 | 0.91884 | 0.017869 | 0.017869 | 328 | 267 | Yes
2013-01-02 | 0.14294 | 0.14289 | 0 | 0 | 0.16199 | 0.16199 | 0 | 0 | 0.029769 | 0.029355 | 0.15393 | 0.15375 | 0 | 0 | 0.17719 | 0.17719 | 0 | 0 | 0.012253 | 0.010722 | 545 | 519 | Yes
2013-01-03 | 0.0011722 | 0.0011722 | 0 | 0 | 0.00037612 | 0.00037612 | 0 | 0 | 0.0071288 | 0.0071288 | 0.0010331 | 0.0010331 | 0 | 0 | 0.00035311 | 0.00035311 | 0 | 0 | 0.0061266 | 0.0061266 | 393 | 383 | Yes
2013-01-04 | 0.055544 | 0.055544 | 0 | 0 | 0.028148 | 0.028148 | 0.074253 | 0.074253 | 0.26215 | 0.26215 | 0.077119 | 0.077119 | 0 | 0 | 0.026059 | 0.026059 | 0.038285 | 0.038285 | 0.45898 | 0.45898 | 611 | 561 | Yes
2013-01-05 | 0.042272 | 0.042272 | 0 | 0 | 0.046458 | 0.046458 | 0.91884 | 0.91884 | 0.0070178 | 0.0070178 | 0.080766 | 0.080766 | 0 | 0 | 0.091454 | 0.091454 | 1.1485 | 1.1485 | 0.0020422 | 0.0020422 | 319 | 296 | Yes
2013-01-06 | 0.14923 | 0.14923 | 0 | 0 | 0.17294 | 0.17294 | 0 | 0 | 0.0034453 | 0.0034453 | 0.16797 | 0.16797 | 0 | 0 | 0.1947 | 0.1947 | 0 | 0 | 0.0035738 | 0.0035738 | 349 | 303 | Yes
2013-01-07 | 0.077443 | 0.077443 | 0 | 0 | 0.069902 | 0.069902 | 0 | 0 | 0.14526 | 0.14526 | 0.039562 | 0.039562 | 0 | 0 | 0.026907 | 0.026907 | 0 | 0 | 0.13785 | 0.13785 | 613 | 589 | Yes
2013-01-08 | 1.8019 | 1.8019 | 0 | 0 | 1.7857 | 1.7857 | 0 | 0 | 2.2293 | 2.2293 | 1.7715 | 1.7715 | 0 | 0 | 1.8252 | 1.8252 | 0 | 0 | 1.6869 | 1.6869 | 2301 | 1359 | Yes
2013-01-09 | 0.13193 | 0.13193 | 0 | 0 | 0.059572 | 0.059572 | 0.26723 | 0.26723 | 0.67583 | 0.67583 | 0.083624 | 0.083624 | 0 | 0 | 0.030074 | 0.030074 | 0.07657 | 0.07657 | 0.48535 | 0.48535 | 737 | 674 | Yes
2013-01-10 | 0.14057 | 0.14057 | 0 | 0 | 0.14261 | 0.14261 | 0 | 0 | 0.14999 | 0.14999 | 0.1853 | 0.1853 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0.11059 | 0.11059 | 519 | 504 | Yes
2013-01-11 | 0.18265 | 0.18265 | 0 | 0 | 0.11988 | 0.11988 | 33.0425 | 33.0425 | 0.22746 | 0.22746 | 0.19794 | 0.19794 | 0 | 0 | 0.17423 | 0.17423 | 11.8683 | 11.8683 | 0.24523 | 0.24523 | 673 | 638 | Yes
2013-01-12 | 0.91514 | 0.91514 | 0 | 0 | 0.27711 | 0.27711 | 0 | 0 | 5.6998 | 5.6998 | 0.51675 | 0.51675 | 0 | 0 | 0.25083 | 0.25083 | 0 | 0 | 2.5343 | 2.5343 | 939 | 466 | Yes
2013-01-13 | 0.75603 | 0.75603 | 0 | 0 | 0.60927 | 0.60927 | 29.3087 | 29.3087 | 1.5586 | 1.5586 | 0.95705 | 0.95705 | 0 | 0 | 0.93786 | 0.93786 | 15.6585 | 15.6585 | 1.0516 | 1.0516 | 1174 | 609 | Yes
2013-01-14 | 0.16867 | 0.1673 | 0 | 0 | 0.12087 | 0.12087 | 28.4694 | 28.4694 | 0.16365 | 0.15207 | 0.17563 | 0.17448 | 0 | 0 | 0.1419 | 0.1419 | 23.3538 | 23.3538 | 0.13823 | 0.1285 | 774 | 705 | Yes
2013-01-15 | 0.077099 | 0.077099 | 0 | 0 | 0.082306 | 0.082306 | 0.035222 | 0.035222 | 0.052142 | 0.052142 | 0.11602 | 0.11602 | 0 | 0 | 0.109 | 0.109 | 0.038285 | 0.038285 | 0.18636 | 0.18636 | 584 | 523 | Yes
2013-01-16 | 0.073105 | 0.073105 | 0 | 0 | 0.083986 | 0.083986 | 0 | 0 | 0.0067811 | 0.0067811 | 0.050442 | 0.050442 | 0 | 0 | 0.055347 | 0.055347 | 0 | 0 | 0.023551 | 0.023551 | 543 | 501 | Yes
2013-01-17 | 0.069261 | 0.069261 | 0 | 0 | 0.078669 | 0.078669 | 0 | 0 | 0.012732 | 0.012732 | 0.1304 | 0.1304 | 0 | 0 | 0.14879 | 0.14879 | 0 | 0 | 0.019049 | 0.019049 | 637 | 564 | Yes
2013-01-18 | 2.1051 | 2.1051 | 0 | 0 | 1.7129 | 1.7129 | 10.066 | 10.066 | 5.1709 | 5.1709 | 1.741 | 1.741 | 0 | 0 | 1.3854 | 1.3854 | 14.8519 | 14.8519 | 4.4159 | 4.4159 | 3312 | 2165 | Yes
2013-01-19 | 0.083112 | 0.083112 | 0 | 0 | 0.041117 | 0.041117 | 1.4586 | 1.4586 | 0.38222 | 0.38222 | 0.05508 | 0.05508 | 0 | 0 | 0.022361 | 0.022361 | 0.30781 | 0.30781 | 0.29758 | 0.29758 | 825 | 637 | Yes
2013-01-20 | 0.26417 | 0.26417 | 0 | 0 | 0.031867 | 0.031867 | 0 | 0 | 1.9937 | 1.9937 | 0.2158 | 0.2158 | 0 | 0 | 0.028324 | 0.028324 | 0 | 0 | 1.612 | 1.612 | 401 | 311 | Yes
2013-01-21 | 0.36168 | 0.36168 | 0 | 0 | 0.41586 | 0.41586 | 0.06246 | 0.06246 | 0.029075 | 0.029075 | 0.34515 | 0.34515 | 0 | 0 | 0.39838 | 0.39838 | 0.038476 | 0.038476 | 0.01699 | 0.01699 | 717 | 696 | Yes
2013-01-22 | 0.44807 | 0.44807 | 0 | 0 | 0.21534 | 0.21534 | 20.089 | 20.089 | 1.943 | 1.943 | 0.35415 | 0.35415 | 0 | 0 | 0.21012 | 0.21012 | 9.0804 | 9.0804 | 1.3371 | 1.3371 | 774 | 659 | Yes
2013-01-23 | 0.093644 | 0.093644 | 0 | 0 | 0.02043 | 0.02043 | 0 | 0 | 0.64048 | 0.64048 | 0.049396 | 0.049396 | 0 | 0 | 0.02726 | 0.02726 | 0 | 0 | 0.2183 | 0.2183 | 529 | 494 | Yes
2013-01-24 | 0.12018 | 0.12018 | 0 | 0 | 0.13902 | 0.13902 | 0.094267 | 0.094267 | 0.0025993 | 0.0025993 | 0.18386 | 0.18386 | 0 | 0 | 0.21308 | 0.21308 | 0.038476 | 0.038476 | 0.0025747 | 0.0025747 | 623 | 602 | Yes
2013-01-25 | 0.091709 | 0.091709 | 0 | 0 | 0.10045 | 0.10045 | 0.19281 | 0.19281 | 0.041208 | 0.041208 | 0.11047 | 0.11047 | 0 | 0 | 0.11862 | 0.11862 | 0.15391 | 0.15391 | 0.067962 | 0.067962 | 758 | 708 | Yes
2013-01-26 | 0.15759 | 0.15759 | 0 | 0 | 0.090984 | 0.090984 | 0 | 0 | 0.66727 | 0.66727 | 0.11072 | 0.11072 | 0 | 0 | 0.05594 | 0.05594 | 0 | 0 | 0.52671 | 0.52671 | 615 | 387 | Yes
2013-01-27 | 0.58902 | 0.58902 | 0 | 0 | 0.45498 | 0.45498 | 0.52612 | 0.52612 | 1.6537 | 1.6537 | 0.66907 | 0.66907 | 0 | 0 | 0.58716 | 0.58716 | 0.50019 | 0.50019 | 1.3695 | 1.3695 | 1122 | 635 | Yes
2013-01-28 | 0.83441 | 0.83441 | 0 | 0 | 0.57331 | 0.57331 | 79.2273 | 79.2273 | 1.809 | 1.809 | 0.87246 | 0.87246 | 0 | 0 | 0.69073 | 0.69073 | 20.4309 | 20.4309 | 2.0646 | 2.0646 | 1644 | 924 | Yes
2013-01-29 | 0.4307 | 0.4307 | 0 | 0 | 0.41519 | 0.41519 | 0.8018 | 0.8018 | 0.60521 | 0.60521 | 0.62127 | 0.62127 | 0 | 0 | 0.62998 | 0.62998 | 0.57515 | 0.57515 | 0.65578 | 0.65578 | 1953 | 1727 | Yes
2013-01-30 | 0.078238 | 0.078238 | 0 | 0 | 0.087328 | 0.087328 | 0 | 0 | 0.025586 | 0.025586 | 0.10429 | 0.10429 | 0 | 0 | 0.11686 | 0.11686 | 0 | 0 | 0.030841 | 0.030841 | 704 | 648 | Yes
2013-01-31 | 0.12099 | 0.12099 | 0 | 0 | 0.01564 | 0.01564 | 0 | 0 | 0.90513 | 0.90513 | 0.089269 | 0.089269 | 0 | 0 | 0.019571 | 0.019571 | 0 | 0 | 0.60962 | 0.60962 | 645 | 601 | Yes
2013-02-01 | 0.44916 | 0.44916 | 0 | 0 | 0.41763 | 0.41763 | 4.4331 | 4.4331 | 0.69433 | 0.69433 | 0.67636 | 0.67636 | 0 | 0 | 0.70725 | 0.70725 | 2.569 | 2.569 | 0.53252 | 0.53252 | 1160 | 1055 | Yes
2013-02-02 | 0.32377 | 0.32377 | 0 | 0 | 0.26513 | 0.26513 | 0.58312 | 0.58312 | 0.79583 | 0.79583 | 0.30988 | 0.30988 | 0 | 0 | 0.26364 | 0.26364 | 0.15337 | 0.15337 | 0.69547 | 0.69547 | 713 | 493 | Yes
2013-02-03 | 0.090298 | 0.090298 | 0 | 0 | 0.093604 | 0.093604 | 0.052914 | 0.052914 | 0.080904 | 0.080904 | 0.074555 | 0.074555 | 0 | 0 | 0.079631 | 0.079631 | 0.076687 | 0.076687 | 0.049346 | 0.049346 | 385 | 331 | Yes
2013-02-04 | 0.1207 | 0.1207 | 0 | 0 | 0.096573 | 0.096573 | 0.1411 | 0.1411 | 0.31416 | 0.31416 | 0.11412 | 0.11412 | 0 | 0 | 0.078709 | 0.078709 | 0.038344 | 0.038344 | 0.38963 | 0.38963 | 702 | 671 | Yes
2013-02-05 | 0.15388 | 0.15388 | 0 | 0 | 0.16405 | 0.16405 | 0 | 0 | 0.10613 | 0.10613 | 0.039263 | 0.039263 | 0 | 0 | 0.03815 | 0.03815 | 0 | 0 | 0.053973 | 0.053973 | 505 | 489 | Yes
2013-02-06 | 0.18587 | 0.18587 | 0 | 0 | 0.15052 | 0.15052 | 0 | 0 | 0.47351 | 0.47351 | 0.17342 | 0.17342 | 0 | 0 | 0.10878 | 0.10878 | 0 | 0 | 0.67134 | 0.67134 | 609 | 592 | Yes
2013-02-07 | 0.08275 | 0.08275 | 0 | 0 | 0.079672 | 0.079672 | 1.3421 | 1.3421 | 0.10108 | 0.10108 | 0.10411 | 0.10411 | 0 | 0 | 0.1124 | 0.1124 | 1.0736 | 1.0736 | 0.047293 | 0.047293 | 498 | 470 | Yes
2013-02-08 | 0.23339 | 0.23339 | 0 | 0 | 0.12979 | 0.12979 | 0 | 0 | 1.0239 | 1.0239 | 0.15932 | 0.15932 | 0 | 0 | 0.057228 | 0.057228 | 0 | 0 | 0.92631 | 0.92631 | 666 | 499 | Yes
2013-02-09 | 0.1222 | 0.1222 | 0 | 0 | 0.068911 | 0.068911 | 0 | 0 | 0.5292 | 0.5292 | 0.17147 | 0.17147 | 0 | 0 | 0.10949 | 0.10949 | 0 | 0 | 0.64975 | 0.64975 | 355 | 288 | Yes
2013-02-10 | 0.099654 | 0.099654 | 0 | 0 | 0.023104 | 0.023104 | 16.6372 | 16.6372 | 0.44837 | 0.44837 | 0.049584 | 0.049584 | 0 | 0 | 0.019998 | 0.019998 | 3.4509 | 3.4509 | 0.22618 | 0.22618 | 413 | 371 | Yes
2013-02-11 | 0.092993 | 0.092993 | 0 | 0 | 0.0041834 | 0.0041834 | 3.0217 | 3.0217 | 0.71199 | 0.71199 | 0.073094 | 0.073094 | 0 | 0 | 0.0012055 | 0.0012055 | 1.342 | 1.342 | 0.58858 | 0.58858 | 687 | 632 | Yes
2013-02-12 | 0.10493 | 0.10493 | 0 | 0 | 0.0091132 | 0.0091132 | 4.8618 | 4.8618 | 0.75205 | 0.75205 | 0.10253 | 0.10253 | 0 | 0 | 0.0088645 | 0.0088645 | 1.1887 | 1.1887 | 0.78291 | 0.78291 | 674 | 658 | Yes
2013-02-13 | 0.23844 | 0.23844 | 0 | 0 | 0.22199 | 0.22199 | 6.2021 | 6.2021 | 0.3149 | 0.3149 | 0.28384 | 0.28384 | 0 | 0 | 0.29253 | 0.29253 | 1.5337 | 1.5337 | 0.24829 | 0.24829 | 639 | 586 | Yes
2013-02-14 | 0.10145 | 0.10145 | 0 | 0 | 0.077075 | 0.077075 | 0 | 0 | 0.29529 | 0.29529 | 0.067417 | 0.067417 | 0 | 0 | 0.012907 | 0.012907 | 0 | 0 | 0.47397 | 0.47397 | 520 | 483 | Yes
2013-02-15 | 0.060452 | 0.060452 | 0 | 0 | 0.069922 | 0.069922 | 0 | 0 | 0.0020357 | 0.0020357 | 0.080791 | 0.080791 | 0 | 0 | 0.093539 | 0.093539 | 0 | 0 | 0.0020563 | 0.0020563 | 568 | 551 | Yes
2013-02-16 | 0.066912 | 0.066912 | 0 | 0 | 0.077372 | 0.077372 | 0 | 0 | 0.0024111 | 0.0024111 | 0.089096 | 0.089096 | 0 | 0 | 0.10333 | 0.10333 | 0 | 0 | 0.0010281 | 0.0010281 | 340 | 288 | Yes
2013-02-17 | 0.046952 | 0.046952 | 0 | 0 | 0.024878 | 0.024878 | 0 | 0 | 0.21491 | 0.21491 | 0.048059 | 0.048059 | 0 | 0 | 0.016027 | 0.016027 | 0 | 0 | 0.28839 | 0.28839 | 281 | 234 | Yes
2013-02-18 | 0.22676 | 0.22676 | 0 | 0 | 0.023613 | 0.023613 | 0 | 0 | 1.7377 | 1.7377 | 0.20805 | 0.20805 | 0 | 0 | 0.017162 | 0.017162 | 0 | 0 | 1.627 | 1.627 | 582 | 579 | Yes
2013-02-19 | 0.20961 | 0.20961 | 0 | 0 | 0.22683 | 0.22683 | 0 | 0 | 0.1202 | 0.1202 | 0.4184 | 0.4184 | 0 | 0 | 0.43703 | 0.43703 | 0 | 0 | 0.3541 | 0.3541 | 741 | 702 | Yes
2013-02-20 | 0.087267 | 0.087267 | 0 | 0 | 0.042099 | 0.042099 | 0 | 0 | 0.43188 | 0.43188 | 0.044887 | 0.044887 | 0 | 0 | 0.028698 | 0.028698 | 0 | 0 | 0.17072 | 0.17072 | 588 | 572 | Yes
2013-02-21 | 0.17708 | 0.17708 | 0 | 0 | 0.2035 | 0.2035 | 0.115 | 0.115 | 0.012722 | 0.012722 | 0.47349 | 0.47349 | 0 | 0 | 0.54747 | 0.54747 | 0.11499 | 0.11499 | 0.012416 | 0.012416 | 713 | 603 | Yes
2013-02-22 | 0.26847 | 0.26847 | 0 | 0 | 0.13356 | 0.13356 | 0.27918 | 0.27918 | 1.2953 | 1.2953 | 0.18303 | 0.18303 | 0 | 0 | 0.12061 | 0.12061 | 0.15332 | 0.15332 | 0.66786 | 0.66786 | 760 | 686 | Yes
2013-02-23 | 5.7997 | 5.7997 | 0 | 0 | 2.4307 | 2.4307 | 98.7808 | 98.7808 | 30.0486 | 30.0486 | 2.2166 | 2.2166 | 0 | 0 | 1.2732 | 1.2732 | 5.1744 | 5.1744 | 9.4116 | 9.4116 |  |  | Yes
2013-02-24 | 1.1761 | 1.1761 | 0 | 0 | 1.1914 | 1.1914 | 33.0782 | 33.0782 | 0.81803 | 0.81803 | 0.39373 | 0.39373 | 0 | 0 | 0.32015 | 0.32015 | 12.2652 | 12.2652 | 0.83237 | 0.83237 | 4139 | 2121 | Yes
2013-02-25 | 0.36583 | 0.36583 | 2.3587 | 2.3587 | 0.33841 | 0.33841 | 0 | 0 | 0.25862 | 0.25862 | 0.57835 | 0.57835 | 4.625 | 4.625 | 0.44834 | 0.44834 | 0 | 0 | 0.90118 | 0.90118 | 1453 | 1310 | Yes
2013-02-26 | 0.11088 | 0.11088 | 0 | 0 | 0.1015 | 0.1015 | 0.057493 | 0.057493 | 0.19744 | 0.19744 | 0.12453 | 0.12453 | 0 | 0 | 0.098357 | 0.098357 | 0.038329 | 0.038329 | 0.33627 | 0.33627 | 776 | 697 | Yes
2013-02-27 | 0.25982 | 0.25982 | 0 | 0 | 0.30026 | 0.30026 | 0.097253 | 0.097253 | 0.0074827 | 0.0074827 | 0.19776 | 0.19776 | 0 | 0 | 0.22889 | 0.22889 | 0.038329 | 0.038329 | 0.0036214 | 0.0036214 | 836 | 726 | Yes
2013-02-28 | 0.2005 | 0.2005 | 0 | 0 | 0.22817 | 0.22817 | 0 | 0 | 0.03258 | 0.03258 | 0.22994 | 0.22994 | 0 | 0 | 0.26361 | 0.26361 | 0 | 0 | 0.023281 | 0.023281 | 690 | 647 | Yes
2013-03-01 | 0.71965 | 0.71965 | 0 | 0 | 0.38877 | 0.38877 | 0.62024 | 0.62024 | 3.2494 | 3.2494 | 0.85462 | 0.85462 | 0 | 0 | 0.41002 | 0.41002 | 0.42162 | 0.42162 | 4.2402 | 4.2402 | 1540 | 1221 | Yes
2013-03-02 | 0.59434 | 0.59434 | 0 | 0 | 0.41071 | 0.41071 | 0 | 0 | 2.0361 | 2.0361 | 0.45476 | 0.45476 | 0 | 0 | 0.37409 | 0.37409 | 0 | 0 | 1.1211 | 1.1211 | 1094 | 644 | Yes
2013-03-03 | 0.25615 | 0.25615 | 0 | 0 | 0.14676 | 0.14676 | 0 | 0 | 1.0983 | 1.0983 | 0.35173 | 0.35173 | 0 | 0 | 0.20012 | 0.20012 | 0 | 0 | 1.5184 | 1.5184 | 637 | 470 | Yes
2013-03-04 | 0.32626 | 0.32626 | 4.1719 | 4.1719 | 0.23151 | 0.23151 | 0 | 0 | 0.41971 | 0.41971 | 0.2854 | 0.2854 | 0.12545 | 0.12545 | 0.2841 | 0.2841 | 0 | 0 | 0.32386 | 0.32386 | 890 | 844 | Yes
2013-03-05 | 0.073463 | 0.073463 | 0.0082226 | 0.0082226 | 0.026668 | 0.026668 | 10.3102 | 10.3102 | 0.27299 | 0.27299 | 0.052496 | 0.052496 | 0.0032985 | 0.0032985 | 0.021462 | 0.021462 | 1.076 | 1.076 | 0.27172 | 0.27172 | 637 | 594 | Yes
2013-03-06 | 0.10462 | 0.10462 | 0 | 0 | 0.1164 | 0.1164 | 0 | 0 | 0.036526 | 0.036526 | 0.068551 | 0.068551 | 0 | 0 | 0.077277 | 0.077277 | 0 | 0 | 0.016563 | 0.016563 | 610 | 597 | Yes
2013-03-07 | 0.090061 | 0.090061 | 0.0096819 | 0.0096819 | 0.064386 | 0.064386 | 0 | 0 | 0.29163 | 0.29163 | 0.10921 | 0.10921 | 0.0032986 | 0.0032986 | 0.089531 | 0.089531 | 0 | 0 | 0.27122 | 0.27122 | 585 | 547 | Yes
2013-03-08 | 0.085744 | 0.085744 | 0 | 0 | 0.094015 | 0.094015 | 0 | 0 | 0.040029 | 0.040029 | 0.10255 | 0.10255 | 0 | 0 | 0.11631 | 0.11631 | 0 | 0 | 0.019671 | 0.019671 | 577 | 556 | Yes
2013-03-09 | 0.018014 | 0.018014 | 0 | 0 | 0.017577 | 0.017577 | 0 | 0 | 0.024304 | 0.024304 | 0.014345 | 0.014345 | 0 | 0 | 0.013529 | 0.013529 | 0 | 0 | 0.022777 | 0.022777 | 507 | 456 | Yes
2013-03-10 | 0.19985 | 0.19985 | 0 | 0 | 0.23104 | 0.23104 | 0.20826 | 0.20826 | 0.0031132 | 0.0031132 | 0.46515 | 0.46515 | 0 | 0 | 0.5391 | 0.5391 | 0.17355 | 0.17355 | 0.0020706 | 0.0020706 | 322 | 234 | Yes
2013-03-11 | 0.033364 | 0.033364 | 0 | 0 | 0.037518 | 0.037518 | 0 | 0 | 0.0087399 | 0.0087399 | 0.046271 | 0.046271 | 0 | 0 | 0.051849 | 0.051849 | 0 | 0 | 0.013459 | 0.013459 | 541 | 529 | Yes
2013-03-12 | 0.44212 | 0.44212 | 0 | 0 | 0.42815 | 0.42815 | 1.9424 | 1.9424 | 0.59148 | 0.59148 | 0.39993 | 0.39993 | 0 | 0 | 0.3526 | 0.3526 | 1.9424 | 1.9424 | 0.78619 | 0.78619 | 841 | 769 | Yes
2013-03-13 | 0.01013 | 0.01013 | 0 | 0 | 0.011373 | 0.011373 | 0.04489 | 0.04489 | 0.0021057 | 0.0021057 | 0.0073237 | 0.0073237 | 0 | 0 | 0.0081424 | 0.0081424 | 0.034686 | 0.034686 | 0.002073 | 0.002073 | 696 | 658 | Yes
2013-03-14 | 0.098173 | 0.098173 | 0 | 0 | 0.10047 | 0.10047 | 0 | 0 | 0.098232 | 0.098232 | 0.026671 | 0.026671 | 0 | 0 | 0.027614 | 0.027614 | 0 | 0 | 0.024358 | 0.024358 | 595 | 532 | Yes
2013-03-15 | 0.21376 | 0.21376 | 0 | 0 | 0.11276 | 0.11276 | 0 | 0 | 0.98989 | 0.98989 | 0.22997 | 0.22997 | 0 | 0 | 0.13771 | 0.13771 | 0 | 0 | 0.94479 | 0.94479 | 764 | 673 | Yes
2013-03-16 | 0.11634 | 0.11634 | 0 | 0 | 0.077406 | 0.077406 | 0 | 0 | 0.42133 | 0.42133 | 0.10381 | 0.10381 | 0 | 0 | 0.098064 | 0.098064 | 0 | 0 | 0.16377 | 0.16377 | 288 | 264 | Yes
2013-03-17 | 0.067043 | 0.067043 | 0.19026 | 0.19026 | 0.049315 | 0.049315 | 0 | 0 | 0.17845 | 0.17845 | 0.14147 | 0.14147 | 0.09236 | 0.09236 | 0.10606 | 0.10606 | 0 | 0 | 0.41046 | 0.41046 | 267 | 240 | Yes
2013-03-18 | 0.15335 | 0.15335 | 0 | 0 | 0.17394 | 0.17394 | 0 | 0 | 0.029033 | 0.029033 | 0.16369 | 0.16369 | 0 | 0 | 0.18671 | 0.18671 | 0 | 0 | 0.023322 | 0.023322 | 515 | 469 | Yes
2013-03-19 | 0.2387 | 0.2387 | 0 | 0 | 0.21271 | 0.21271 | 0.11554 | 0.11554 | 0.46822 | 0.46822 | 0.20525 | 0.20525 | 0 | 0 | 0.13857 | 0.13857 | 0.034698 | 0.034698 | 0.72819 | 0.72819 | 517 | 461 | Yes
2013-03-20 | 0.20286 | 0.20286 | 0 | 0 | 0.025746 | 0.025746 | 0.062457 | 0.062457 | 1.5333 | 1.5333 | 0.14447 | 0.14447 | 0 | 0 | 0.015011 | 0.015011 | 0.20819 | 0.20819 | 1.1138 | 1.1138 | 554 | 518 | Yes
2013-03-21 | 0.092886 | 0.092886 | 0 | 0 | 0.052882 | 0.052882 | 0.06248 | 0.06248 | 0.40076 | 0.40076 | 0.13006 | 0.13006 | 0 | 0 | 0.074842 | 0.074842 | 0.034698 | 0.034698 | 0.55613 | 0.55613 | 566 | 473 | Yes
2013-03-22 | 0.17353 | 0.17353 | 0 | 0 | 0.19935 | 0.19935 | 0.041638 | 0.041638 | 0.013793 | 0.013793 | 0.21362 | 0.21362 | 0 | 0 | 0.24641 | 0.24641 | 0.034698 | 0.034698 | 0.0098477 | 0.0098477 | 582 | 568 | Yes
2013-03-23 | 0.11059 | 0.11059 | 0 | 0 | 0.081256 | 0.081256 | 0 | 0 | 0.34438 | 0.34438 | 0.12366 | 0.12366 | 0 | 0 | 0.10833 | 0.10833 | 0 | 0 | 0.25708 | 0.25708 | 328 | 280 | Yes
2013-03-24 | 0.03443 | 0.03443 | 0.11991 | 0.11991 | 0.025844 | 0.025844 | 0 | 0 | 0.08436 | 0.08436 | 0.032958 | 0.032958 | 0.016493 | 0.016493 | 0.013666 | 0.013666 | 0 | 0 | 0.17726 | 0.17726 | 223 | 206 | Yes
2013-03-25 | 0.29124 | 0.29124 | 0 | 0 | 0.33623 | 0.33623 | 0 | 0 | 0.012002 | 0.012002 | 0.22198 | 0.22198 | 0 | 0 | 0.25391 | 0.25391 | 0 | 0 | 0.026433 | 0.026433 | 625 | 527 | Yes
2013-03-26 | 0.31173 | 0.31173 | 0 | 0 | 0.1121 | 0.1121 | 0 | 0 | 1.8274 | 1.8274 | 0.18745 | 0.18745 | 0 | 0 | 0.03333 | 0.03333 | 0 | 0 | 1.3484 | 1.3484 | 758 | 698 | Yes
2013-03-27 | 0.084999 | 0.084999 | 0 | 0 | 0.095035 | 0.095035 | 0 | 0 | 0.026129 | 0.026129 | 0.061977 | 0.061977 | 0 | 0 | 0.066872 | 0.066872 | 0 | 0 | 0.036794 | 0.036794 | 678 | 630 | Yes
2013-03-28 | 0.21512 | 0.21512 | 0.09733 | 0.09733 | 0.21483 | 0.21483 | 0 | 0 | 0.23889 | 0.23889 | 0.50418 | 0.50418 | 0.069266 | 0.069266 | 0.51383 | 0.51383 | 0 | 0 | 0.50935 | 0.50935 | 796 | 714 | Yes
2013-03-29 | 0.097879 | 0.097879 | 0.11597 | 0.11597 | 0.080169 | 0.080169 | 0.062062 | 0.062062 | 0.22495 | 0.22495 | 0.058989 | 0.058989 | 0.013193 | 0.013193 | 0.047639 | 0.047639 | 0.034662 | 0.034662 | 0.14945 | 0.14945 | 248 | 221 | Yes
2013-03-30 | 0.1684 | 0.1684 | 0 | 0 | 0.097303 | 0.097303 | 0 | 0 | 0.7167 | 0.7167 | 0.15305 | 0.15305 | 0 | 0 | 0.14915 | 0.14915 | 0 | 0 | 0.20788 | 0.20788 | 338 | 287 | Yes
2013-03-31 | 0.018962 | 0.018962 | 0 | 0 | 0.012708 | 0.012708 | 0 | 0 | 0.067902 | 0.067902 | 0.095346 | 0.095346 | 0 | 0 | 0.094712 | 0.094712 | 0 | 0 | 0.11635 | 0.11635 | 155 | 151 | Yes
2013-04-01 | 0.0056569 | 0.0056569 | 0 | 0 | 0.0035968 | 0.0035968 | 0 | 0 | 0.021677 | 0.021677 | 0.0058562 | 0.0058562 | 0 | 0 | 0.0023359 | 0.0023359 | 0 | 0 | 0.032578 | 0.032578 | 181 | 166 | Yes
2013-04-02 | 0.085056 | 0.085056 | 0 | 0 | 0.094962 | 0.094962 | 0.062392 | 0.062392 | 0.026183 | 0.026183 | 0.09115 | 0.09115 | 0 | 0 | 0.1041 | 0.1041 | 0.069324 | 0.069324 | 0.010891 | 0.010891 | 497 | 483 | Yes
2013-04-03 | 0.018592 | 0.018592 | 0 | 0 | 0.017953 | 0.017953 | 0 | 0 | 0.026484 | 0.026484 | 0.039413 | 0.039413 | 0 | 0 | 0.042675 | 0.042675 | 0 | 0 | 0.022301 | 0.022301 | 577 | 479 | Yes
2013-04-04 | 0.26446 | 0.26446 | 0 | 0 | 0.21731 | 0.21731 | 0 | 0 | 0.65551 | 0.65551 | 0.26687 | 0.26687 | 0 | 0 | 0.21536 | 0.21536 | 0 | 0 | 0.6903 | 0.6903 | 838 | 734 | Yes
2013-04-05 | 0.088597 | 0.088597 | 0.2918 | 0.2918 | 0.096326 | 0.096326 | 0 | 0 | 0.0013201 | 0.0013201 | 0.03014 | 0.03014 | 0.18468 | 0.18468 | 0.030361 | 0.030361 | 0 | 0 | 0.0046678 | 0.0046678 | 544 | 503 | Yes
2013-04-06 | 0.004152 | 0.004152 | 0 | 0 | 0.0021767 | 0.0021767 | 0 | 0 | 0.019342 | 0.019342 | 0.0058572 | 0.0058572 | 0 | 0 | 0.0034678 | 0.0034678 | 0 | 0 | 0.024376 | 0.024376 | 233 | 217 | Yes
2013-04-07 | 0.0077984 | 0.0077984 | 0 | 0 | 0.0088978 | 0.0088978 | 0.072449 | 0.072449 | 0 | 0 | 0.0076876 | 0.0076876 | 0 | 0 | 0.0088465 | 0.0088465 | 0.034662 | 0.034662 | 0 | 0 | 168 | 162 | Yes
2013-04-08 | 0.039038 | 0.039038 | 0 | 0 | 0.013122 | 0.013122 | 0.11161 | 0.11161 | 0.23401 | 0.23401 | 0.037889 | 0.037889 | 0 | 0 | 0.0027601 | 0.0027601 | 0.069324 | 0.069324 | 0.30082 | 0.30082 | 503 | 449 | Yes
2013-04-09 | 0.099277 | 0.099277 | 0.0023748 | 0.0023748 | 0.11289 | 0.11289 | 0.013865 | 0.013865 | 0.016301 | 0.016301 | 0.11972 | 0.11972 | 0.0065967 | 0.0065967 | 0.11451 | 0.11451 | 0.034662 | 0.034662 | 0.17674 | 0.17674 | 660 | 377 | Yes
2013-04-10 | 0.11276 | 0.11276 | 0 | 0 | 0.082308 | 0.082308 | 0 | 0 | 0.35445 | 0.35445 | 0.32988 | 0.32988 | 0 | 0 | 0.12604 | 0.12604 | 0 | 0 | 1.8749 | 1.8749 | 701 | 369 | Yes
2013-04-11 | 0.040421 | 0.040421 | 0 | 0 | 0.042876 | 0.042876 | 0.14766 | 0.14766 | 0.02723 | 0.02723 | 0.069403 | 0.069403 | 0 | 0 | 0.077495 | 0.077495 | 0.069324 | 0.069324 | 0.021188 | 0.021188 | 497 | 362 | Yes
2013-04-12 | 0.13087 | 0.13087 | 0 | 0 | 0.14409 | 0.14409 | 0.071404 | 0.071404 | 0.05569 | 0.05569 | 0.12075 | 0.12075 | 0 | 0 | 0.13213 | 0.13213 | 0.034662 | 0.034662 | 0.05788 | 0.05788 | 459 | 306 | Yes
2013-04-13 | 0.038409 | 0.038409 | 0 | 0 | 0.039904 | 0.039904 | 0 | 0 | 0.034086 | 0.034086 | 0.014637 | 0.014637 | 0 | 0 | 0.014438 | 0.014438 | 0 | 0 | 0.018604 | 0.018604 | 324 | 268 | Yes
2013-04-14 | 0.23125 | 0.23125 | 0 | 0 | 0.26836 | 0.26836 | 0 | 0 | 0 | 0 | 0.33305 | 0.33305 | 0 | 0 | 0.38649 | 0.38649 | 0 | 0 | 0 | 0 | 314 | 250 | Yes
2013-04-15 | 0.13137 | 0.13137 | 0 | 0 | 0.084647 | 0.084647 | 0 | 0 | 0.49508 | 0.49508 | 0.21608 | 0.21608 | 0 | 0 | 0.14282 | 0.14282 | 0 | 0 | 0.7881 | 0.7881 | 688 | 420 | Yes
2013-04-16 | 0.027232 | 0.027232 | 0.0029099 | 0.0029099 | 0.020254 | 0.020254 | 1.1823 | 1.1823 | 0.06496 | 0.06496 | 0.021772 | 0.021772 | 0.0032986 | 0.0032986 | 0.01259 | 0.01259 | 0.7279 | 0.7279 | 0.081462 | 0.081462 | 583 | 348 | Yes
2013-04-17 | 0.017247 | 0.017247 | 0 | 0 | 0.013176 | 0.013176 | 0 | 0 | 0.050081 | 0.050081 | 0.01549 | 0.01549 | 0 | 0 | 0.0089121 | 0.0089121 | 0 | 0 | 0.066415 | 0.066415 | 535 | 321 | Yes
2013-04-18 | 0.14998 | 0.14998 | 0 | 0 | 0.05604 | 0.05604 | 0.44194 | 0.44194 | 0.85827 | 0.85827 | 0.14423 | 0.14423 | 0 | 0 | 0.08021 | 0.08021 | 0.17331 | 0.17331 | 0.63614 | 0.63614 | 518 | 413 | Yes
2013-04-19 | 0.06151 | 0.06151 | 0 | 0 | 0.046029 | 0.046029 | 0 | 0 | 0.18567 | 0.18567 | 0.042569 | 0.042569 | 0 | 0 | 0.036215 | 0.036215 | 0 | 0 | 0.096511 | 0.096511 | 632 | 615 | Yes
2013-04-20 | 0.3118 | 0.3118 | 0 | 0 | 0.32719 | 0.32719 | 0 | 0 | 0.25261 | 0.25261 | 0.41855 | 0.41855 | 0 | 0 | 0.41881 | 0.41881 | 0 | 0 | 0.48878 | 0.48878 | 698 | 499 | Yes
2013-04-21 | 0.059827 | 0.059827 | 0 | 0 | 0.060199 | 0.060199 | 0.22451 | 0.22451 | 0.064043 | 0.064043 | 0.020857 | 0.020857 | 0 | 0 | 0.020017 | 0.020017 | 0.10399 | 0.10399 | 0.029057 | 0.029057 | 368 | 307 | Yes
2013-04-22 | 0.092712 | 0.092712 | 0.099231 | 0.099231 | 0.10219 | 0.10219 | 1.4461 | 1.4461 | 0.0019038 | 0.0019038 | 0.1657 | 0.1657 | 0.052783 | 0.052783 | 0.18306 | 0.18306 | 3.8821 | 3.8821 | 0.00051887 | 0.00051887 | 765 | 645 | Yes
2013-04-23 | 0.31852 | 0.31852 | 0 | 0 | 0.1339 | 0.1339 | 1.0268 | 1.0268 | 1.711 | 1.711 | 0.22173 | 0.22173 | 0 | 0 | 0.12298 | 0.12298 | 0.41739 | 0.41739 | 0.97739 | 0.97739 | 605 | 587 | Yes
2013-04-24 | 0.044515 | 0.044515 | 0 | 0 | 0.02709 | 0.02709 | 0 | 0 | 0.17823 | 0.17823 | 0.062475 | 0.062475 | 0 | 0 | 0.06286 | 0.06286 | 0 | 0 | 0.07024 | 0.07024 | 622 | 565 | Yes
2013-04-25 | 0.013705 | 0.013705 | 0 | 0 | 0.015766 | 0.015766 | 0 | 0 | 0.0010879 | 0.0010879 | 0.0090209 | 0.0090209 | 0 | 0 | 0.010406 | 0.010406 | 0 | 0 | 0.00051271 | 0.00051271 | 230 | 217 | Yes
2013-04-26 | 0.18778 | 0.18778 | 0 | 0 | 0.13038 | 0.13038 | 0 | 0 | 0.63527 | 0.63527 | 0.37339 | 0.37339 | 0 | 0 | 0.36945 | 0.36945 | 0 | 0 | 0.46502 | 0.46502 | 541 | 507 | Yes
2013-04-27 | 0.10002 | 0.10002 | 0 | 0 | 0.046193 | 0.046193 | 0 | 0 | 0.50675 | 0.50675 | 0.1102 | 0.1102 | 0 | 0 | 0.039217 | 0.039217 | 0 | 0 | 0.64293 | 0.64293 | 387 | 304 | Yes
2013-04-28 | 0.10276 | 0.10276 | 0 | 0 | 0.099147 | 0.099147 | 0 | 0 | 0.14627 | 0.14627 | 0.15622 | 0.15622 | 0 | 0 | 0.14158 | 0.14158 | 0 | 0 | 0.28865 | 0.28865 | 269 | 254 | Yes
2013-04-29 | 0.03877 | 0.03877 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0.055309 | 0.055309 | 0.058453 | 0.058453 | 0 | 0 | 0.06548 | 0.06548 | 0 | 0 | 0.017432 | 0.017432 | 552 | 513 | Yes
2013-04-30 | 0.10462 | 0.10462 | 0 | 0 | 0.010259 | 0.010259 | 0 | 0 | 0.80572 | 0.80572 | 0.12772 | 0.12772 | 0 | 0 | 0.0040339 | 0.0040339 | 0 | 0 | 1.0452 | 1.0452 | 528 | 495 | Yes
2013-05-01 | 0.028721 | 0.028721 | 0 | 0 | 0.014266 | 0.014266 | 0.0015724 | 0.0015724 | 0.13825 | 0.13825 | 0.022485 | 0.022485 | 0 | 0 | 0.01564 | 0.01564 | 0.038197 | 0.038197 | 0.075353 | 0.075353 | 542 | 518 | Yes
2013-05-02 | 0.16149 | 0.16149 | 0 | 0 | 0.1867 | 0.1867 | 0 | 0 | 0.0061298 | 0.0061298 | 0.018768 | 0.018768 | 0 | 0 | 0.021443 | 0.021443 | 0 | 0 | 0.0025631 | 0.0025631 | 472 | 448 | Yes
2013-05-03 | 0.12881 | 0.12881 | 0 | 0 | 0.13845 | 0.13845 | 0.14897 | 0.14897 | 0.078795 | 0.078795 | 0.10554 | 0.10554 | 0 | 0 | 0.11776 | 0.11776 | 0.076394 | 0.076394 | 0.033832 | 0.033832 | 481 | 469 | Yes
2013-05-04 | 0.00079237 | 0.00079237 | 0 | 0 | 0.0002402 | 0.0002402 | 0.12452 | 0.12452 | 0.0032546 | 0.0032546 | 0.00048749 | 0.00048749 | 0 | 0 | 0.00021231 | 0.00021231 | 0.076394 | 0.076394 | 0.0015378 | 0.0015378 | 207 | 202 | Yes
2013-05-05 | 0.04495 | 0.04495 | 0 | 0 | 0.047028 | 0.047028 | 0 | 0 | 0.037489 | 0.037489 | 0.065263 | 0.065263 | 0 | 0 | 0.074876 | 0.074876 | 0 | 0 | 0.0066639 | 0.0066639 | 269 | 237 | Yes
2013-05-06 | 0.1547 | 0.1547 | 0.054382 | 0.054382 | 0.16952 | 0.16952 | 0 | 0 | 0.065106 | 0.065106 | 0.20517 | 0.20517 | 0.049438 | 0.049438 | 0.23326 | 0.23326 | 0 | 0 | 0.028706 | 0.028706 | 771 | 708 | Yes
2013-05-07 | 0.031474 | 0.031474 | 0 | 0 | 0.036029 | 0.036029 | 0.12743 | 0.12743 | 0.0021496 | 0.0021496 | 0.049955 | 0.049955 | 0 | 0 | 0.05782 | 0.05782 | 0.038183 | 0.038183 | 0.0010233 | 0.0010233 | 709 | 631 | Yes
2013-05-08 | 0.15424 | 0.15424 | 0 | 0 | 0.13408 | 0.13408 | 0.34377 | 0.34377 | 0.32144 | 0.32144 | 0.12008 | 0.12008 | 0 | 0 | 0.12937 | 0.12937 | 0.68755 | 0.68755 | 0.063954 | 0.063954 | 662 | 610 | Yes
2013-05-09 | 0.14541 | 0.14541 | 0 | 0 | 0.092467 | 0.092467 | 0 | 0 | 0.55273 | 0.55273 | 0.2203 | 0.2203 | 0 | 0 | 0.13263 | 0.13263 | 0 | 0 | 0.89127 | 0.89127 | 602 | 548 | Yes
2013-05-10 | 0.029569 | 0.029569 | 0 | 0 | 0.03103 | 0.03103 | 0 | 0 | 0.024002 | 0.024002 | 0.021506 | 0.021506 | 0 | 0 | 0.023001 | 0.023001 | 0 | 0 | 0.014326 | 0.014326 | 574 | 499 | Yes
2013-05-11 | 0.10995 | 0.10995 | 0 | 0 | 0.12714 | 0.12714 | 0 | 0 | 0.0042434 | 0.0042434 | 0.13519 | 0.13519 | 0 | 0 | 0.15676 | 0.15676 | 0 | 0 | 0.0020465 | 0.0020465 | 308 | 249 | Yes
2013-05-12 | 0.14878 | 0.14878 | 0 | 0 | 0.16972 | 0.16972 | 0 | 0 | 0.022539 | 0.022539 | 0.089679 | 0.089679 | 0 | 0 | 0.099649 | 0.099649 | 0 | 0 | 0.032745 | 0.032745 | 266 | 237 | Yes
2013-05-13 | 0.049752 | 0.049752 | 0 | 0 | 0.056382 | 0.056382 | 0.041915 | 0.041915 | 0.009655 | 0.009655 | 0.10716 | 0.10716 | 0 | 0 | 0.12392 | 0.12392 | 0.038197 | 0.038197 | 0.0035814 | 0.0035814 | 543 | 532 | Yes
2013-05-14 | 0.095609 | 0.095609 | 0 | 0 | 0.035983 | 0.035983 | 0.10287 | 0.10287 | 0.54154 | 0.54154 | 0.11453 | 0.11453 | 0 | 0 | 0.0095532 | 0.0095532 | 0.038197 | 0.038197 | 0.89243 | 0.89243 | 626 | 537 | Yes
2013-05-15 | 0.15678 | 0.15678 | 0 | 0 | 0.17888 | 0.17888 | 0 | 0 | 0.023437 | 0.023437 | 0.11989 | 0.11989 | 0 | 0 | 0.13814 | 0.13814 | 0 | 0 | 0.0081875 | 0.0081875 | 541 | 521 | Yes
2013-05-16 | 0.0076507 | 0.0076507 | 0 | 0 | 0.0051873 | 0.0051873 | 0 | 0 | 0.026755 | 0.026755 | 0.0073713 | 0.0073713 | 0 | 0 | 0.0050952 | 0.0050952 | 0 | 0 | 0.025074 | 0.025074 | 445 | 419 | Yes
2013-05-17 | 0.21848 | 0.21848 | 0 | 0 | 0.216 | 0.216 | 0 | 0 | 0.27323 | 0.27323 | 0.21785 | 0.21785 | 0 | 0 | 0.20799 | 0.20799 | 0 | 0 | 0.32597 | 0.32597 | 521 | 482 | Yes
2013-05-18 | 0.012935 | 0.012935 | 0 | 0 | 0.013339 | 0.013339 | 0 | 0 | 0.012194 | 0.012194 | 0.012245 | 0.012245 | 0 | 0 | 0.011818 | 0.011818 | 0 | 0 | 0.017399 | 0.017399 | 321 | 249 | Yes
2013-05-19 | 0.034744 | 0.034744 | 0 | 0 | 0.033604 | 0.033604 | 0 | 0 | 0.048852 | 0.048852 | 0.041731 | 0.041731 | 0 | 0 | 0.024698 | 0.024698 | 0 | 0 | 0.17194 | 0.17194 | 211 | 199 | Yes
2013-05-20 | 0.022265 | 0.022265 | 0 | 0 | 0.025447 | 0.025447 | 0 | 0 | 0.003009 | 0.003009 | 0.05026 | 0.05026 | 0 | 0 | 0.058171 | 0.058171 | 0 | 0 | 0.0015352 | 0.0015352 | 558 | 512 | Yes
2013-05-21 | 0.17869 | 0.17869 | 0 | 0 | 0.2004 | 0.2004 | 0 | 0 | 0.051559 | 0.051559 | 0.21627 | 0.21627 | 0 | 0 | 0.24245 | 0.24245 | 0 | 0 | 0.06309 | 0.06309 | 549 | 512 | Yes
2013-05-22 | 0.3062 | 0.3062 | 0 | 0 | 0.32322 | 0.32322 | 0 | 0 | 0.23455 | 0.23455 | 0.36913 | 0.36913 | 0 | 0 | 0.4027 | 0.4027 | 0 | 0 | 0.18825 | 0.18825 | 728 | 627 | Yes
2013-05-23 | 0.27113 | 0.27113 | 0 | 0 | 0.12451 | 0.12451 | 13.3923 | 13.3923 | 1.2002 | 1.2002 | 0.23626 | 0.23626 | 0 | 0 | 0.1548 | 0.1548 | 3.5523 | 3.5523 | 0.81915 | 0.81915 | 707 | 630 | Yes
2013-05-24 | 0.1152 | 0.1152 | 0 | 0 | 0.12964 | 0.12964 | 0 | 0 | 0.030039 | 0.030039 | 0.12642 | 0.12642 | 0 | 0 | 0.14426 | 0.14426 | 0 | 0 | 0.018466 | 0.018466 | 600 | 544 | Yes
2013-05-25 | 0.16488 | 0.16488 | 0 | 0 | 0.17576 | 0.17576 | 0 | 0 | 0.11385 | 0.11385 | 0.1584 | 0.1584 | 0 | 0 | 0.17829 | 0.17829 | 0 | 0 | 0.041035 | 0.041035 | 422 | 358 | Yes
2013-05-26 | 0.35102 | 0.35102 | 0 | 0 | 0.081276 | 0.081276 | 0.046683 | 0.046683 | 2.3654 | 2.3654 | 0.31949 | 0.31949 | 0 | 0 | 0.069617 | 0.069617 | 0.038197 | 0.038197 | 2.1846 | 2.1846 | 293 | 280 | Yes
2013-05-27 | 0.44055 | 0.44055 | 0 | 0 | 0.51124 | 0.51124 | 0 | 0 | 0.0025197 | 0.0025197 | 0.56867 | 0.56867 | 0 | 0 | 0.66016 | 0.66016 | 0 | 0 | 0.0015388 | 0.0015388 | 733 | 565 | Yes
2013-05-28 | 0.018365 | 0.018365 | 0 | 0 | 0.017041 | 0.017041 | 0 | 0 | 0.031254 | 0.031254 | 0.020766 | 0.020766 | 0 | 0 | 0.021319 | 0.021319 | 0 | 0 | 0.020254 | 0.020254 | 501 | 490 | Yes
2013-05-29 | 0.015429 | 0.015429 | 0 | 0 | 0.016355 | 0.016355 | 0 | 0 | 0.011262 | 0.011262 | 0.049692 | 0.049692 | 0 | 0 | 0.054993 | 0.054993 | 0 | 0 | 0.019215 | 0.019215 | 579 | 541 | Yes
2013-05-30 | 0.27864 | 0.27864 | 0 | 0 | 0.31847 | 0.31847 | 0.19656 | 0.19656 | 0.030614 | 0.030614 | 0.16662 | 0.16662 | 0 | 0 | 0.18926 | 0.18926 | 0.15267 | 0.15267 | 0.026486 | 0.026486 | 586 | 538 | Yes
2013-05-31 | 0.017924 | 0.017924 | 0 | 0 | 0.012809 | 0.012809 | 0.12023 | 0.12023 | 0.056984 | 0.056984 | 0.037332 | 0.037332 | 0 | 0 | 0.010025 | 0.010025 | 0.1145 | 0.1145 | 0.24304 | 0.24304 | 489 | 471 | Yes
2013-06-01 | 0.02448 | 0.02448 | 0 | 0 | 0.0246 | 0.0246 | 0.09313 | 0.09313 | 0.026519 | 0.026519 | 0.019366 | 0.019366 | 0 | 0 | 0.017437 | 0.017437 | 0.076336 | 0.076336 | 0.035833 | 0.035833 | 289 | 270 | Yes
2013-06-02 | 0.51677 | 0.51677 | 1.1622 | 1.1622 | 0.49183 | 0.49183 | 0 | 0 | 0.60561 | 0.60561 | 0.53068 | 0.53068 | 0.069222 | 0.069222 | 0.54104 | 0.54104 | 0 | 0 | 0.53438 | 0.53438 | 850 | 486 | Yes
2013-06-03 | 0.12578 | 0.12578 | 0 | 0 | 0.14431 | 0.14431 | 0 | 0 | 0.010996 | 0.010996 | 0.11559 | 0.11559 | 0 | 0 | 0.13307 | 0.13307 | 0 | 0 | 0.0067512 | 0.0067512 | 680 | 625 | Yes
2013-06-04 | 0.25496 | 0.25496 | 0 | 0 | 0.27842 | 0.27842 | 0.11449 | 0.11449 | 0.12436 | 0.12436 | 0.28205 | 0.28205 | 0 | 0 | 0.30125 | 0.30125 | 0.076336 | 0.076336 | 0.18795 | 0.18795 | 669 | 632 | Yes
2013-06-05 | 0.028111 | 0.028111 | 0 | 0 | 0.029089 | 0.029089 | 0 | 0 | 0.025729 | 0.025729 | 0.027328 | 0.027328 | 0 | 0 | 0.027797 | 0.027797 | 0 | 0 | 0.028557 | 0.028557 | 537 | 508 | Yes
2013-06-06 | 0.086178 | 0.086178 | 0 | 0 | 0.04229 | 0.04229 | 0 | 0 | 0.42393 | 0.42393 | 0.08089 | 0.08089 | 0 | 0 | 0.013899 | 0.013899 | 0 | 0 | 0.58777 | 0.58777 | 493 | 455 | Yes
2013-06-07 | 0.07265 | 0.07265 | 0 | 0 | 0.071923 | 0.071923 | 0 | 0 | 0.090443 | 0.090443 | 0.073039 | 0.073039 | 0 | 0 | 0.072599 | 0.072599 | 0 | 0 | 0.08879 | 0.08879 | 489 | 461 | Yes
2013-06-08 | 0.037631 | 0.037631 | 0 | 0 | 0.042304 | 0.042304 | 0.46183 | 0.46183 | 0.003401 | 0.003401 | 0.027572 | 0.027572 | 0 | 0 | 0.031184 | 0.031184 | 0.22901 | 0.22901 | 0.0025962 | 0.0025962 | 345 | 301 | Yes
2013-06-09 | 0.046659 | 0.046659 | 0 | 0 | 0.053325 | 0.053325 | 0 | 0 | 0.0055977 | 0.0055977 | 0.017773 | 0.017773 | 0 | 0 | 0.020319 | 0.020319 | 0 | 0 | 0.002077 | 0.002077 | 216 | 210 | Yes
2013-06-10 | 0.14208 | 0.14208 | 0 | 0 | 0.03698 | 0.03698 | 0 | 0 | 0.93994 | 0.93994 | 0.32095 | 0.32095 | 0 | 0 | 0.22316 | 0.22316 | 0 | 0 | 1.0956 | 1.0956 | 380 | 278 | Yes
2013-06-11 | 0.029646 | 0.029646 | 0 | 0 | 0.029825 | 0.029825 | 0 | 0 | 0.033411 | 0.033411 | 0.010286 | 0.010286 | 0 | 0 | 0.0089602 | 0.0089602 | 0 | 0 | 0.021808 | 0.021808 | 586 | 570 | Yes
2013-06-12 | 0.19431 | 0.19431 | 0 | 0 | 0.079013 | 0.079013 | 0 | 0 | 1.0762 | 1.0762 | 0.21437 | 0.21437 | 0 | 0 | 0.1162 | 0.1162 | 0 | 0 | 0.97357 | 0.97357 | 584 | 545 | Yes
2013-06-13 | 0.14007 | 0.14007 | 0 | 0 | 0.15046 | 0.15046 | 0 | 0 | 0.087576 | 0.087576 | 0.12958 | 0.12958 | 0 | 0 | 0.14294 | 0.14294 | 0 | 0 | 0.053481 | 0.053481 | 647 | 569 | Yes
2013-06-14 | 0.023641 | 0.023641 | 0 | 0 | 0.018627 | 0.018627 | 0 | 0 | 0.064595 | 0.064595 | 0.037859 | 0.037859 | 0 | 0 | 0.017003 | 0.017003 | 0 | 0 | 0.19783 | 0.19783 | 525 | 515 | Yes
2013-06-15 | 0.08828 | 0.08828 | 0 | 0 | 0.0083055 | 0.0083055 | 0 | 0 | 0.69198 | 0.69198 | 0.12386 | 0.12386 | 0 | 0 | 0.0091719 | 0.0091719 | 0 | 0 | 0.98915 | 0.98915 | 284 | 271 | Yes
2013-06-16 | 0.039198 | 0.039198 | 0 | 0 | 0.044507 | 0.044507 | 0 | 0 | 0.0068347 | 0.0068347 | 0.026477 | 0.026477 | 0 | 0 | 0.030479 | 0.030479 | 0 | 0 | 0.0015577 | 0.0015577 | 261 | 230 | Yes
2013-06-17 | 0.024347 | 0.024347 | 0.052134 | 0.052134 | 0.020945 | 0.020945 | 0 | 0 | 0.04534 | 0.04534 | 0.031163 | 0.031163 | 0.092218 | 0.092218 | 0.026387 | 0.026387 | 0 | 0 | 0.057116 | 0.057116 | 582 | 554 | Yes
2013-06-18 | 0.11522 | 0.11522 | 0 | 0 | 0.12011 | 0.12011 | 0 | 0 | 0.098919 | 0.098919 | 0.29234 | 0.29234 | 0 | 0 | 0.32624 | 0.32624 | 0 | 0 | 0.092944 | 0.092944 | 528 | 471 | Yes
2013-06-19 | 0.19842 | 0.19842 | 0 | 0 | 0.19913 | 0.19913 | 0 | 0 | 0.22721 | 0.22721 | 0.42217 | 0.42217 | 0 | 0 | 0.42501 | 0.42501 | 0 | 0 | 0.47354 | 0.47354 | 597 | 548 | Yes
2013-06-20 | 0.0073831 | 0.0073831 | 0 | 0 | 0.0027834 | 0.0027834 | 0 | 0 | 0.0425 | 0.0425 | 0.0044432 | 0.0044432 | 0 | 0 | 0.0028221 | 0.0028221 | 0 | 0 | 0.017135 | 0.017135 | 480 | 485 | Yes
2013-06-21 | 0.06664 | 0.06664 | 0 | 0 | 0.076434 | 0.076434 | 0 | 0 | 0.0059718 | 0.0059718 | 0.048571 | 0.048571 | 0 | 0 | 0.055455 | 0.055455 | 0 | 0 | 0.0062309 | 0.0062309 | 484 | 464 | Yes
2013-06-22 | 0.41274 | 0.41274 | 0 | 0 | 0.47535 | 0.47535 | 0 | 0 | 0.02264 | 0.02264 | 0.029764 | 0.029764 | 0 | 0 | 0.031819 | 0.031819 | 0 | 0 | 0.019731 | 0.019731 | 383 | 308 | Yes
2013-06-23 | 0.47413 | 0.47413 | 0 | 0 | 0.53508 | 0.53508 | 0.084733 | 0.084733 | 0.10559 | 0.10559 | 0.5509 | 0.5509 | 0 | 0 | 0.63201 | 0.63201 | 0.076336 | 0.076336 | 0.047251 | 0.047251 | 728 | 343 | Yes
2013-06-24 | 0.41488 | 0.41488 | 0 | 0 | 0.47906 | 0.47906 | 0 | 0 | 0.013609 | 0.013609 | 0.73575 | 0.73575 | 0 | 0 | 0.85178 | 0.85178 | 0 | 0 | 0.0077886 | 0.0077886 | 1111 | 939 | Yes
2013-06-25 | 0.55428 | 0.55428 | 0 | 0 | 0.63823 | 0.63823 | 0.066908 | 0.066908 | 0.030444 | 0.030444 | 0.47609 | 0.47609 | 0 | 0 | 0.54798 | 0.54798 | 0.038168 | 0.038168 | 0.028039 | 0.028039 | 848 | 725 | Yes
2013-06-26 | 0.30367 | 0.30367 | 0 | 0 | 0.34665 | 0.34665 | 0 | 0 | 0.039361 | 0.039361 | 0.26288 | 0.26288 | 0 | 0 | 0.30154 | 0.30154 | 0 | 0 | 0.023366 | 0.023366 | 786 | 728 | Yes
2013-06-27 | 0.020938 | 0.020938 | 0 | 0 | 0.022591 | 0.022591 | 0 | 0 | 0.012352 | 0.012352 | 0.01479 | 0.01479 | 0 | 0 | 0.01658 | 0.01658 | 0 | 0 | 0.0041539 | 0.0041539 | 546 | 508 | Yes
2013-06-28 | 0.29433 | 0.29433 | 0 | 0 | 0.17948 | 0.17948 | 0.040076 | 0.040076 | 1.1894 | 1.1894 | 0.2893 | 0.2893 | 0 | 0 | 0.1665 | 0.1665 | 0.1145 | 0.1145 | 1.241 | 1.241 | 711 | 642 | Yes
2013-06-29 | 0.1331 | 0.1331 | 0.024042 | 0.024042 | 0.012032 | 0.012032 | 0 | 0 | 1.0431 | 1.0431 | 0.1434 | 0.1434 | 0.032935 | 0.032935 | 0.013828 | 0.013828 | 0 | 0 | 1.1164 | 1.1164 | 518 | 368 | Yes
2013-06-30 | 0.10965 | 0.10965 | 0.49797 | 0.49797 | 0.11501 | 0.11501 | 0.11238 | 0.11238 | 0.0089245 | 0.0089245 | 0.15241 | 0.15241 | 0.11198 | 0.11198 | 0.17257 | 0.17257 | 0.076336 | 0.076336 | 0.011423 | 0.011423 | 591 | 385 | Yes
Contents

## 1d. STPIS MED Threshold
Ausgrid
STPIS Data Reporting
2012-13 |  |  |  | 2007-07-01
MED Threshold |  |  |  | 2008-07-01
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: MED threshold
MED threshold (t-med) year ending 30 June
Alpha - average of Ln(SAIDI)
Beta-standard deviation of Ln(SAIDI)
X Beta from the mean
Table 2: MED calculation
Date | Unplanned SAIDI - total (after removing exluded events allowed under clause 3.3(a) of the STPIS) | Total unplanned customer minutes off supply (after removing exluded events allowed under clause 3.3(a) of the STPIS) | Ln (SAIDI)
2007-07-01 | 0.086034 | 114823.7333 | -2.453
2007-07-02 | 0.23226 | 343949.9167 | -1.4599
2007-07-03 | 0.21247 | 312276.2167 | -1.5489
2007-07-04 | 0.71252 | 1040949.6 | -0.33895
2007-07-05 | 1.9206 | 2792079.1 | 0.65264
2007-07-06 | 0.34572 | 500183.5667 | -1.0621
2007-07-07 | 0.29532 | 425421.75 | -1.2197
2007-07-08 | 0.76591 | 1103328.05 | -0.2667
2007-07-09 | 0.16284 | 240636.2 | -1.815
2007-07-10 | 0.15585 | 228141.5333 | -1.8588
2007-07-11 | 0.25006 | 363679.0833 | -1.386
2007-07-12 | 0.85732 | 1239889.2167 | -0.15394
2007-07-13 | 0.32514 | 465096.25 | -1.1235
2007-07-14 | 0.048036 | 70646.15 | -3.0358
2007-07-15 | 0.56203 | 826572.75 | -0.57621
2007-07-16 | 1.7665 | 2611129.7167 | 0.56898
2007-07-17 | 0.77906 | 1153010.9333 | -0.24967
2007-07-18 | 0.43919 | 643047.45 | -0.82283
2007-07-19 | 0.1199 | 177691.6 | -2.1211
2007-07-20 | 0.19432 | 284686.3 | -1.6383
2007-07-21 | 0.1269 | 187265.3667 | -2.0644
2007-07-22 | 1.6153 | 2383675.0333 | 0.47949
2007-07-23 | 0.10969 | 162784.95 | -2.2101
2007-07-24 | 0.096414 | 142564.4833 | -2.3391
2007-07-25 | 0.21226 | 311858.7167 | -1.55
2007-07-26 | 0.03718 | 54716.8833 | -3.292
2007-07-27 | 0.029683 | 43986.0667 | -3.5172
2007-07-28 | 0.14113 | 208158.6667 | -1.958
2007-07-29 | 0.37482 | 552819.5167 | -0.98131
2007-07-30 | 0.23239 | 345640.2 | -1.4593
2007-07-31 | 0.027116 | 40143.9333 | -3.6076
2007-08-01 | 0.074924 | 110494.7833 | -2.5913
2007-08-02 | 0.27554 | 408675.5667 | -1.289
2007-08-03 | 0.23522 | 348171.25 | -1.4472
2007-08-04 | 0.078576 | 116579.7 | -2.5437
2007-08-05 | 0.46958 | 696691.1667 | -0.75592
2007-08-06 | 0.085026 | 125300.3167 | -2.4648
2007-08-07 | 0.014745 | 21780.0667 | -4.2168
2007-08-08 | 2.1196 | 3148058.7667 | 0.75124
2007-08-09 | 0.15539 | 230939.6667 | -1.8618
2007-08-10 | 0.018728 | 27822.2333 | -3.9778
2007-08-11 | 0.22163 | 328642.9 | -1.5068
2007-08-12 | 0.19294 | 286104.95 | -1.6454
2007-08-13 | 0.050649 | 74340.5833 | -2.9828
2007-08-14 | 0.17088 | 254357.25 | -1.7668
2007-08-15 | 0.048751 | 72245.85 | -3.021
2007-08-16 | 0.087747 | 130548.55 | -2.4333
2007-08-17 | 0.085263 | 126982.35 | -2.462
2007-08-18 | 0.30441 | 454220.2 | -1.1894
2007-08-19 | 0.36704 | 547662.85 | -1.0023
2007-08-20 | 1.1794 | 1756786.2333 | 0.16497
2007-08-21 | 0.57628 | 864014.0167 | -0.55116
2007-08-22 | 0.19765 | 297126.4167 | -1.6212
2007-08-23 | 0.045268 | 68074.15 | -3.0952
2007-08-24 | 0.062219 | 93592.1167 | -2.7771
2007-08-25 | 0.50025 | 752209.45 | -0.69265
2007-08-26 | 0.084515 | 127082.7 | -2.4708
2007-08-27 | 0.050494 | 75398.55 | -2.9859
2007-08-28 | 0.48596 | 730966.0833 | -0.72164
2007-08-29 | 0.23745 | 357071.1 | -1.4378
2007-08-30 | 0.11464 | 172500.1333 | -2.166
2007-08-31 | 0.1582 | 238019.4833 | -1.8439
2007-09-01 | 0.15492 | 232992.3 | -1.8648
2007-09-02 | 0.056379 | 84790 | -2.8757
2007-09-03 | 0.19169 | 286147.5833 | -1.6519
2007-09-04 | 0.10831 | 162549.0333 | -2.2227
2007-09-05 | 0.096924 | 145760.3167 | -2.3338
2007-09-06 | 0.18736 | 281060.3167 | -1.6747
2007-09-07 | 0.16633 | 249703.7167 | -1.7938
2007-09-08 | 0.20835 | 313129.3 | -1.5685
2007-09-09 | 0.088208 | 132565.8667 | -2.4281
2007-09-10 | 0.035073 | 52336.8167 | -3.3503
2007-09-11 | 0.17668 | 265596.55 | -1.7334
2007-09-12 | 0.16836 | 250249.9833 | -1.7816
2007-09-13 | 0.033229 | 49979.9333 | -3.4043
2007-09-14 | 0.24278 | 365208.45 | -1.4156
2007-09-15 | 0.016149 | 23958.7667 | -4.1259
2007-09-16 | 0.1005 | 149109.75 | -2.2976
2007-09-17 | 0.056159 | 83084.8333 | -2.8796
2007-09-18 | 0.31071 | 468867.75 | -1.1689
2007-09-19 | 0.12715 | 191869.0833 | -2.0624
2007-09-20 | 0.23113 | 348778.95 | -1.4648
2007-09-21 | 0.15346 | 231548.6833 | -1.8743
2007-09-22 | 0.16252 | 245145.2 | -1.817
2007-09-23 | 0.042434 | 64007.75 | -3.1598
2007-09-24 | 0.13673 | 205686.7333 | -1.9898
2007-09-25 | 0.086685 | 130918.45 | -2.4455
2007-09-26 | 0.085765 | 129528.9333 | -2.4561
2007-09-27 | 0.17959 | 271236.1167 | -1.7171
2007-09-28 | 0.21958 | 331279.65 | -1.516
2007-09-29 | 0.10675 | 160803.1333 | -2.2373
2007-09-30 | 0.12645 | 190477.7667 | -2.0679
2007-10-01 | 1.1615 | 1740142.9 | 0.14967
2007-10-02 | 0.44298 | 664045.2167 | -0.81424
2007-10-03 | 0.7822 | 1180871.3833 | -0.24565
2007-10-04 | 0.1412 | 213173.2833 | -1.9576
2007-10-05 | 0.082265 | 124121.1667 | -2.4978
2007-10-06 | 0.22862 | 344568.6833 | -1.4757
2007-10-07 | 0.24395 | 367670.15 | -1.4108
2007-10-08 | 0.14899 | 223482.5833 | -1.9039
2007-10-09 | 0.025778 | 38652.8333 | -3.6582
2007-10-10 | 0.081346 | 122760.7667 | -2.509
2007-10-11 | 0.52676 | 794957.1833 | -0.64102
2007-10-12 | 0.53388 | 805610.3833 | -0.62758
2007-10-13 | 0.040809 | 61515.5833 | -3.1989
2007-10-14 | 0.18181 | 274056.3833 | -1.7048
2007-10-15 | 0.11621 | 174293.2 | -2.1523
2007-10-16 | 0.22057 | 330664.6667 | -1.5115
2007-10-17 | 0.033953 | 51329.85 | -3.3828
2007-10-18 | 0.092944 | 131081.05 | -2.3758
2007-10-19 | 0.098762 | 146253.8 | -2.315
2007-10-20 | 0.16349 | 240928.9833 | -1.811
2007-10-21 | 0.054987 | 81034.0333 | -2.9007
2007-10-22 | 0.055104 | 80786.9 | -2.8985
2007-10-23 | 0.067937 | 99321.85 | -2.6892
2007-10-24 | 0.35403 | 532840.5833 | -1.0384
2007-10-25 | 1.4327 | 2157293.4667 | 0.35957
2007-10-26 | 0.95207 | 1433536.1 | -0.04912
2007-10-27 | 0.19785 | 295220.75 | -1.6202
2007-10-28 | 0.24344 | 363241.4333 | -1.4129
2007-10-29 | 0.050917 | 75859.5 | -2.9776
2007-10-30 | 0.13895 | 206366.1167 | -1.9736
2007-10-31 | 0.014526 | 21894.5833 | -4.2318
2007-11-01 | 0.037216 | 56090.8833 | -3.291
2007-11-02 | 0.35434 | 533717.4833 | -1.0375
2007-11-03 | 0.19438 | 293113.9333 | -1.6379
2007-11-04 | 0.29398 | 443301.2333 | -1.2243
2007-11-05 | 0.5163 | 777430.4833 | -0.66106
2007-11-06 | 0.11108 | 166291.4 | -2.1975
2007-11-07 | 0.15018 | 226309.5167 | -1.8959
2007-11-08 | 0.015561 | 23434.65 | -4.163
2007-11-09 | 0.096979 | 145987.3 | -2.3333
2007-11-10 | 0.12323 | 185586.2833 | -2.0937
2007-11-11 | 0.25318 | 381294.6 | -1.3736
2007-11-12 | 0.075764 | 113998.25 | -2.5801
2007-11-13 | 0.071854 | 107532.9667 | -2.6331
2007-11-14 | 0.21177 | 316868.4667 | -1.5522
2007-11-15 | 0.25775 | 385974.7 | -1.3557
2007-11-16 | 0.093715 | 141005.4667 | -2.3675
2007-11-17 | 0.15712 | 236792.6167 | -1.8508
2007-11-18 | 0.19942 | 300553.35 | -1.6123
2007-11-19 | 0.20435 | 305262 | -1.5879
2007-11-20 | 0.15724 | 233754.45 | -1.85
2007-11-21 | 0.87344 | 1313471.8 | -0.13531
2007-11-22 | 0.28796 | 433224.5333 | -1.2449
2007-11-23 | 0.28284 | 425301.4 | -1.2629
2007-11-24 | 0.036384 | 54757.5667 | -3.3136
2007-11-25 | 0.03746 | 56376.5833 | -3.2845
2007-11-26 | 0.19433 | 290802.2667 | -1.6382
2007-11-27 | 0.86879 | 1293341.35 | -0.14065
2007-11-28 | 0.23851 | 353398.0833 | -1.4334
2007-11-29 | 0.12645 | 190456.1333 | -2.0679
2007-11-30 | 0.35652 | 533463.1833 | -1.0314
2007-12-01 | 0.32228 | 485607.2833 | -1.1323
2007-12-02 | 0.038596 | 58155.3333 | -3.2546
2007-12-03 | 1.3354 | 2009897.85 | 0.28925
2007-12-04 | 0.29341 | 439900.5 | -1.2262
2007-12-05 | 0.2203 | 328688.1 | -1.5128
2007-12-06 | 0.2603 | 386691.5167 | -1.3459
2007-12-07 | 3.2358 | 4872817.6333 | 1.1743
2007-12-08 | 0.28837 | 434670.6333 | -1.2435
2007-12-09 | 3.4857 | 5254226.9 | 1.2487
2007-12-10 | 0.47012 | 708331.6667 | -0.75478
2007-12-11 | 0.31022 | 465428.25 | -1.1705
2007-12-12 | 0.4163 | 627272.0333 | -0.87635
2007-12-13 | 0.21333 | 321579.4167 | -1.5449
2007-12-14 | 0.052311 | 78869.2833 | -2.9505
2007-12-15 | 0.050221 | 75568.6667 | -2.9913
2007-12-16 | 0.61579 | 926604.5333 | -0.48484
2007-12-17 | 0.16723 | 251617.7167 | -1.7884
2007-12-18 | 0.047824 | 71636.6333 | -3.0402
2007-12-19 | 0.66113 | 985323.8333 | -0.4138
2007-12-20 | 0.97216 | 1443787.3167 | -0.02824
2007-12-21 | 0.11761 | 177443.4 | -2.1404
2007-12-22 | 0.29395 | 443596.3833 | -1.2244
2007-12-23 | 0.14255 | 215121.2833 | -1.9481
2007-12-24 | 0.0061577 | 9272.6667 | -5.0901
2007-12-25 | 0.4242 | 637163.5167 | -0.85756
2007-12-26 | 0.020578 | 31192.2167 | -3.8835
2007-12-27 | 0.095034 | 144068.25 | -2.3535
2007-12-28 | 0.12011 | 181625.8833 | -2.1193
2007-12-29 | 0.17175 | 259764.2667 | -1.7617
2007-12-30 | 0.28686 | 433874.65 | -1.2488
2007-12-31 | 0.1622 | 244990.1167 | -1.8189
2008-01-01 | 0.11294 | 170180.6333 | -2.1809
2008-01-02 | 0.11135 | 168768.3833 | -2.1951
2008-01-03 | 0.1582 | 239128.1333 | -1.8439
2008-01-04 | 0.12294 | 185836.1333 | -2.096
2008-01-05 | 0.17586 | 265824.6333 | -1.738
2008-01-06 | 0.13765 | 208065.8 | -1.983
2008-01-07 | 0.043999 | 66458.8 | -3.1236
2008-01-08 | 0.11819 | 177863.6833 | -2.1355
2008-01-09 | 0.066926 | 101187.3333 | -2.7042
2008-01-10 | 0.086399 | 130684.0667 | -2.4488
2008-01-11 | 0.027538 | 41638.5333 | -3.5922
2008-01-12 | 0.15208 | 230111.85 | -1.8833
2008-01-13 | 0.79109 | 1196955.6333 | -0.23435
2008-01-14 | 0.081834 | 123540.0333 | -2.5031
2008-01-15 | 0.2871 | 431622.8667 | -1.2479
2008-01-16 | 0.73368 | 1107414.95 | -0.30968
2008-01-17 | 0.22383 | 338092.2333 | -1.4969
2008-01-18 | 0.26106 | 394333.1 | -1.343
2008-01-19 | 0.80123 | 1209985.7167 | -0.22161
2008-01-20 | 0.6118 | 923913.9667 | -0.49135
2008-01-21 | 0.55478 | 836882.1 | -0.58918
2008-01-22 | 0.093297 | 140196.8833 | -2.372
2008-01-23 | 0.099689 | 150621.4333 | -2.3057
2008-01-24 | 0.21933 | 331357.6333 | -1.5172
2008-01-25 | 0.15322 | 231465.9333 | -1.8759
2008-01-26 | 0.23405 | 353785.3 | -1.4522
2008-01-27 | 0.12888 | 194808.0667 | -2.0489
2008-01-28 | 0.051313 | 77495.8833 | -2.9698
2008-01-29 | 0.052465 | 79157.2833 | -2.9476
2008-01-30 | 0.14595 | 219388.55 | -1.9245
2008-01-31 | 4.6265 | 6929958.75 | 1.5318
2008-02-01 | 0.85696 | 1278088.3833 | -0.15436
2008-02-02 | 0.12384 | 183846.8167 | -2.0888
2008-02-03 | 0.37071 | 550324.5833 | -0.99235
2008-02-04 | 0.58064 | 859113.8667 | -0.54363
2008-02-05 | 1.2127 | 1790153.6167 | 0.19286
2008-02-06 | 0.37822 | 556240.0833 | -0.97228
2008-02-07 | 3.1514 | 4620144.3167 | 1.1478
2008-02-08 | 0.15838 | 231447.8 | -1.8427
2008-02-09 | 1.0098 | 1471948.7333 | 0.0097829
2008-02-10 | 0.29642 | 432073.7333 | -1.216
2008-02-11 | 0.070995 | 103370.4167 | -2.6451
2008-02-12 | 0.10761 | 156075.8667 | -2.2293
2008-02-13 | 0.23127 | 349442.1667 | -1.4642
2008-02-14 | 0.13402 | 202552.7 | -2.0097
2008-02-15 | 0.12027 | 181635.5167 | -2.118
2008-02-16 | 0.026158 | 39471.9 | -3.6436
2008-02-17 | 0.0081665 | 12323.1 | -4.8077
2008-02-18 | 0.26889 | 406064.1333 | -1.3135
2008-02-19 | 0.21122 | 318206.55 | -1.5549
2008-02-20 | 0.20246 | 303876.8167 | -1.5972
2008-02-21 | 0.17 | 257500.3667 | -1.772
2008-02-22 | 0.20393 | 308457.45 | -1.59
2008-02-23 | 0.22135 | 340521.1167 | -1.508
2008-02-24 | 0.22038 | 339025 | -1.5124
2008-02-25 | 0.18268 | 280431.0333 | -1.7
2008-02-26 | 0.44703 | 683002.4667 | -0.80512
2008-02-27 | 0.40539 | 624100.6667 | -0.90292
2008-02-28 | 0.21886 | 336575.1 | -1.5193
2008-02-29 | 0.13478 | 207260.1667 | -2.0041
2008-03-01 | 0.20824 | 320624.3167 | -1.5691
2008-03-02 | 0.40939 | 630324.2333 | -0.89309
2008-03-03 | 0.35133 | 539968.6167 | -1.046
2008-03-04 | 0.15229 | 233002.75 | -1.882
2008-03-05 | 0.15786 | 242641.0167 | -1.846
2008-03-06 | 0.10659 | 163894.8333 | -2.2388
2008-03-07 | 2.2135 | 3405883.1 | 0.79459
2008-03-08 | 1.096 | 1685212.9667 | 0.091683
2008-03-09 | 0.3165 | 486647.8 | -1.1504
2008-03-10 | 0.071388 | 109620.75 | -2.6396
2008-03-11 | 0.24049 | 367742.3833 | -1.4251
2008-03-12 | 0.08 | 123024.6333 | -2.5257
2008-03-13 | 0.13421 | 206465.85 | -2.0084
2008-03-14 | 0.37825 | 581485.2667 | -0.9722
2008-03-15 | 0.28858 | 444370.1333 | -1.2428
2008-03-16 | 0.024535 | 37779.1333 | -3.7077
2008-03-17 | 0.14129 | 217564.3 | -1.9569
2008-03-18 | 0.20666 | 316565.6167 | -1.5767
2008-03-19 | 0.24117 | 367613.0333 | -1.4222
2008-03-20 | 0.11474 | 174405.0833 | -2.1651
2008-03-21 | 0.46384 | 717041.7667 | -0.76821
2008-03-22 | 0.37396 | 573708.3333 | -0.9836
2008-03-23 | 0.015738 | 24144.1833 | -4.1517
2008-03-24 | 0.02153 | 33028.4167 | -3.8383
2008-03-25 | 0.63877 | 979186.8833 | -0.44822
2008-03-26 | 0.19659 | 299982.3667 | -1.6266
2008-03-27 | 0.13308 | 201897.5 | -2.0168
2008-03-28 | 0.27276 | 419860.3667 | -1.2992
2008-03-29 | 0.010875 | 16793.6333 | -4.5213
2008-03-30 | 0.49063 | 757654.1 | -0.71206
2008-03-31 | 0.040205 | 62086.65 | -3.2138
2008-04-01 | 0.039032 | 60275.2333 | -3.2434
2008-04-02 | 0.48932 | 755872.85 | -0.71474
2008-04-03 | 0.42739 | 660212.0833 | -0.85005
2008-04-04 | 0.13139 | 202287.5833 | -2.0296
2008-04-05 | 0.27612 | 425322.75 | -1.2869
2008-04-06 | 0.081904 | 126163.1333 | -2.5022
2008-04-07 | 0.26746 | 410562.3833 | -1.3188
2008-04-08 | 0.49905 | 763378.5833 | -0.69504
2008-04-09 | 0.070626 | 108844.6 | -2.6504
2008-04-10 | 0.15781 | 243279.0167 | -1.8464
2008-04-11 | 0.064037 | 98640.85 | -2.7483
2008-04-12 | 0.78034 | 1203392.1333 | -0.24802
2008-04-13 | 0.68737 | 1060024.35 | -0.37488
2008-04-14 | 0.1415 | 219052.0667 | -1.9555
2008-04-15 | 0.1994 | 307412.7167 | -1.6124
2008-04-16 | 0.11552 | 178211.2833 | -2.1583
2008-04-17 | 0.24656 | 380502.75 | -1.4001
2008-04-18 | 0.032451 | 50076.95 | -3.428
2008-04-19 | 0.13735 | 211232 | -1.9852
2008-04-20 | 0.43036 | 661866.8167 | -0.84314
2008-04-21 | 0.47523 | 724160.7667 | -0.74396
2008-04-22 | 0.0052656 | 7992.6 | -5.2466
2008-04-23 | 0.23325 | 356971.3 | -1.4556
2008-04-24 | 0.16911 | 258945.4833 | -1.7772
2008-04-25 | 0.22276 | 340976.5 | -1.5016
2008-04-26 | 0.26941 | 412372.6667 | -1.3115
2008-04-27 | 0.39734 | 608193.3833 | -0.92297
2008-04-28 | 0.36892 | 565974.5 | -0.99716
2008-04-29 | 0.26484 | 406347.0333 | -1.3286
2008-04-30 | 0.1117 | 170641.8667 | -2.1919
2008-05-01 | 0.19959 | 304919.6 | -1.6115
2008-05-02 | 0.77269 | 1180397.9333 | -0.25787
2008-05-03 | 0.22624 | 347248.5 | -1.4861
2008-05-04 | 0.25187 | 386584.8167 | -1.3788
2008-05-05 | 0.063121 | 96288.5333 | -2.7627
2008-05-06 | 0.11872 | 180488.9667 | -2.131
2008-05-07 | 0.19613 | 300156.5167 | -1.629
2008-05-08 | 0.35309 | 540818.8167 | -1.041
2008-05-09 | 0.095857 | 146893.8667 | -2.3449
2008-05-10 | 0.017947 | 27512.0333 | -4.0203
2008-05-11 | 0.010654 | 16331.25 | -4.5419
2008-05-12 | 0.037961 | 58098.7333 | -3.2712
2008-05-13 | 0.14045 | 213898.3333 | -1.9629
2008-05-14 | 0.17875 | 273627.4333 | -1.7218
2008-05-15 | 0.15536 | 236975.1667 | -1.862
2008-05-16 | 0.013766 | 21096.1667 | -4.2855
2008-05-17 | 0.056246 | 86066.0167 | -2.878
2008-05-18 | 0.018938 | 28978.8667 | -3.9666
2008-05-19 | 0.22271 | 339536.0167 | -1.5019
2008-05-20 | 0.33318 | 506264.05 | -1.0991
2008-05-21 | 0.025483 | 38941.6333 | -3.6698
2008-05-22 | 0.13491 | 206631.65 | -2.0032
2008-05-23 | 0.026638 | 40764.95 | -3.6254
2008-05-24 | 0.44667 | 683398.9167 | -0.80595
2008-05-25 | 0.08161 | 124863.9 | -2.5058
2008-05-26 | 0.042675 | 65203.3833 | -3.1541
2008-05-27 | 0.076099 | 115847.1833 | -2.5757
2008-05-28 | 2.5123 | 3846303.15 | 0.92119
2008-05-29 | 0.12219 | 187088.7167 | -2.1022
2008-05-30 | 0.14153 | 216736.6333 | -1.9553
2008-05-31 | 0.014347 | 21970.7667 | -4.2442
2008-06-01 | 0.56283 | 861910.1333 | -0.57478
2008-06-02 | 0.36794 | 562959.35 | -0.99983
2008-06-03 | 0.071113 | 108202 | -2.6435
2008-06-04 | 0.3254 | 498813.6667 | -1.1227
2008-06-05 | 1.379 | 2115160.5167 | 0.32139
2008-06-06 | 0.22104 | 339025 | -1.5094
2008-06-07 | 0.33706 | 516595.35 | -1.0875
2008-06-08 | 0.014823 | 22718.1 | -4.2116
2008-06-09 | 0.063818 | 97722.5667 | -2.7517
2008-06-10 | 0.27143 | 415056.8833 | -1.3041
2008-06-11 | 0.074064 | 113643.3167 | -2.6028
2008-06-12 | 0.32674 | 501204.6833 | -1.1186
2008-06-13 | 0.21977 | 337289.6833 | -1.5152
2008-06-14 | 0.099757 | 153018.5 | -2.305
2008-06-15 | 0.15943 | 244546.3667 | -1.8362
2008-06-16 | 0.13216 | 202334.55 | -2.0237
2008-06-17 | 0.11387 | 173679.3667 | -2.1727
2008-06-18 | 0.23727 | 363344.95 | -1.4385
2008-06-19 | 0.1924 | 294965.0667 | -1.6482
2008-06-20 | 0.066868 | 102489.7667 | -2.705
2008-06-21 | 0.11818 | 181155.35 | -2.1356
2008-06-22 | 0.94743 | 1452347.6333 | -0.054003
2008-06-23 | 0.24503 | 375153.95 | -1.4064
2008-06-24 | 0.12347 | 188189.8667 | -2.0918
2008-06-25 | 0.064444 | 98740.2333 | -2.742
2008-06-26 | 0.22598 | 346488.65 | -1.4873
2008-06-27 | 0.033612 | 51555.7667 | -3.3929
2008-06-28 | 0.22549 | 345388.45 | -1.4895
2008-06-29 | 0.68493 | 1049138.7333 | -0.37843
2008-06-30 | 0.26134 | 400308.6833 | -1.3419
2008-07-01 | 1.9028 | 2890316.2 | 0.64333
2008-07-02 | 0.8387 | 1273965.0167 | -0.17591
2008-07-03 | 0.20093 | 305204.7333 | -1.6048
2008-07-04 | 0.16721 | 253988.5333 | -1.7885
2008-07-05 | 0.087418 | 133262.8833 | -2.4371
2008-07-06 | 0.067943 | 103575.0167 | -2.6891
2008-07-07 | 0.029055 | 44295.05 | -3.5386
2008-07-08 | 0.094379 | 143389.9 | -2.3604
2008-07-09 | 0.17508 | 268125.1833 | -1.7425
2008-07-10 | 0.35733 | 547305.7 | -1.0291
2008-07-11 | 0.077961 | 119448.8667 | -2.5516
2008-07-12 | 0.16906 | 258944.3667 | -1.7775
2008-07-13 | 0.12316 | 188644.5667 | -2.0942
2008-07-14 | 0.13901 | 214032.5833 | -1.9732
2008-07-15 | 0.55402 | 849021.5667 | -0.59055
2008-07-16 | 0.027421 | 42223.75 | -3.5964
2008-07-17 | 0.037423 | 57696.7833 | -3.2855
2008-07-18 | 0.089348 | 137867.7833 | -2.4152
2008-07-19 | 0.1297 | 200211.9833 | -2.0426
2008-07-20 | 0.10687 | 164972.1667 | -2.2362
2008-07-21 | 0.33082 | 510853.1333 | -1.1062
2008-07-22 | 0.90617 | 1399320.2333 | -0.098528
2008-07-23 | 0.082599 | 127550.9833 | -2.4938
2008-07-24 | 0.10955 | 169174.2333 | -2.2113
2008-07-25 | 0.22662 | 349957.1 | -1.4845
2008-07-26 | 0.37354 | 576820.2 | -0.98474
2008-07-27 | 0.030566 | 47200.2667 | -3.4879
2008-07-28 | 0.38646 | 596779.15 | -0.95072
2008-07-29 | 0.061558 | 95058.4 | -2.7878
2008-07-30 | 0.35107 | 542127.1833 | -1.0468
2008-07-31 | 0.59225 | 917880.1333 | -0.52382
2008-08-01 | 0.71307 | 1096665.6333 | -0.33818
2008-08-02 | 0.046544 | 71025.9 | -3.0674
2008-08-03 | 0.20269 | 309303.2333 | -1.5961
2008-08-04 | 0.043614 | 66471.95 | -3.1324
2008-08-05 | 0.60172 | 914505.2667 | -0.50797
2008-08-06 | 0.046383 | 70116.3 | -3.0708
2008-08-07 | 0.067301 | 101313.4 | -2.6986
2008-08-08 | 0.15811 | 243317.3167 | -1.8444
2008-08-09 | 0.033831 | 52222.1 | -3.3864
2008-08-10 | 0.72198 | 1114463.3 | -0.32575
2008-08-11 | 0.95882 | 1481870.8333 | -0.042047
2008-08-12 | 0.12668 | 195103.5833 | -2.0661
2008-08-13 | 0.1332 | 204754.4167 | -2.0159
2008-08-14 | 0.14538 | 225270.1667 | -1.9284
2008-08-15 | 0.048131 | 74624.4333 | -3.0338
2008-08-16 | 0.037276 | 57745.0667 | -3.2894
2008-08-17 | 0.19832 | 307218.6833 | -1.6179
2008-08-18 | 0.28157 | 436153.95 | -1.2674
2008-08-19 | 0.060174 | 92889.9 | -2.8105
2008-08-20 | 0.10747 | 166802.0667 | -2.2305
2008-08-21 | 0.39108 | 607033.9167 | -0.93883
2008-08-22 | 0.35671 | 553833.8333 | -1.0308
2008-08-23 | 0.7619 | 1183294.5333 | -0.27194
2008-08-24 | 0.098113 | 152376.8 | -2.3216
2008-08-25 | 0.059798 | 92448.4833 | -2.8168
2008-08-26 | 0.040808 | 63080.15 | -3.1989
2008-08-27 | 0.027063 | 42078.1 | -3.6096
2008-08-28 | 0.031765 | 49434.3833 | -3.4494
2008-08-29 | 0.19575 | 304470.8667 | -1.6309
2008-08-30 | 0.048855 | 76027.8167 | -3.0189
2008-08-31 | 0.052264 | 81332.2667 | -2.9514
2008-09-01 | 0.30389 | 472416.8167 | -1.1911
2008-09-02 | 0.057205 | 88631.9167 | -2.8611
2008-09-03 | 0.15808 | 245946.6833 | -1.8446
2008-09-04 | 0.071597 | 111461.1167 | -2.6367
2008-09-05 | 0.32606 | 507477.2833 | -1.1207
2008-09-06 | 2.1365 | 3325768.0833 | 0.75919
2008-09-07 | 0.15067 | 234531.35 | -1.8927
2008-09-08 | 0.044758 | 69188.8833 | -3.1065
2008-09-09 | 0.35775 | 550315.4167 | -1.0279
2008-09-10 | 0.30947 | 480030.6833 | -1.1729
2008-09-11 | 0.14747 | 228814.6333 | -1.9141
2008-09-12 | 0.098048 | 152141.95 | -2.3223
2008-09-13 | 0.07746 | 119746.65 | -2.558
2008-09-14 | 0.035076 | 54224.0333 | -3.3502
2008-09-15 | 0.21019 | 323332.2833 | -1.5597
2008-09-16 | 0.090072 | 137937 | -2.4071
2008-09-17 | 0.0067808 | 10474.65 | -4.9937
2008-09-18 | 0.021616 | 33401.5833 | -3.8343
2008-09-19 | 0.0053848 | 8327.4667 | -5.2242
2008-09-20 | 0.055923 | 85147.55 | -2.8838
2008-09-21 | 0.01722 | 26218.2667 | -4.0617
2008-09-22 | 0.10521 | 162977.7167 | -2.2518
2008-09-23 | 0.25433 | 392405.85 | -1.3691
2008-09-24 | 0.094359 | 146241.8667 | -2.3606
2008-09-25 | 0.082189 | 127322.3 | -2.4987
2008-09-26 | 0.22215 | 345199.8333 | -1.5044
2008-09-27 | 0.053352 | 82886.9333 | -2.9308
2008-09-28 | 0.19737 | 306635.9833 | -1.6227
2008-09-29 | 2.7184 | 4212387.6167 | 1.0001
2008-09-30 | 0.090354 | 139502.9333 | -2.404
2008-10-01 | 0.059801 | 93152.6667 | -2.8167
2008-10-02 | 0.13743 | 213797.6333 | -1.9846
2008-10-03 | 0.66168 | 1029202.4333 | -0.41297
2008-10-04 | 0.096208 | 149917.8667 | -2.3412
2008-10-05 | 0.29558 | 460600.1167 | -1.2188
2008-10-06 | 0.80881 | 1256086.5333 | -0.21219
2008-10-07 | 0.018858 | 29322.0333 | -3.9708
2008-10-08 | 0.043136 | 67284.4667 | -3.1434
2008-10-09 | 0.0060615 | 9444.8 | -5.1058
2008-10-10 | 0.043873 | 68388.7667 | -3.1265
2008-10-11 | 0.22555 | 351861.35 | -1.4892
2008-10-12 | 0.031502 | 49144.7 | -3.4577
2008-10-13 | 0.30037 | 468580.4 | -1.2028
2008-10-14 | 0.1127 | 165455.4 | -2.183
2008-10-15 | 0.18803 | 292499.5333 | -1.6712
2008-10-16 | 0.12472 | 194598.7 | -2.0817
2008-10-17 | 0.17596 | 274555.6 | -1.7375
2008-10-18 | 0.054825 | 85605.2167 | -2.9036
2008-10-19 | 0.51516 | 804384.3333 | -0.66329
2008-10-20 | 0.58853 | 917893.5833 | -0.53013
2008-10-21 | 0.27987 | 434703.4167 | -1.2734
2008-10-22 | 0.61268 | 948015.5 | -0.48991
2008-10-23 | 0.31584 | 493419.5667 | -1.1525
2008-10-24 | 0.085282 | 133253.6833 | -2.4618
2008-10-25 | 0.005311 | 8300.85 | -5.238
2008-10-26 | 0.065573 | 102488.45 | -2.7246
2008-10-27 | 0.5033 | 785389.0167 | -0.68657
2008-10-28 | 0.32169 | 500383.1333 | -1.1342
2008-10-29 | 0.2966 | 463351.2167 | -1.2154
2008-10-30 | 0.343 | 535741.45 | -1.07
2008-10-31 | 0.12662 | 197882.3667 | -2.0666
2008-11-01 | 0.095458 | 149276.8833 | -2.3491
2008-11-02 | 0.010175 | 15911.9333 | -4.5878
2008-11-03 | 0.24283 | 379065.95 | -1.4154
2008-11-04 | 0.1572 | 244629.6333 | -1.8502
2008-11-05 | 0.012346 | 19299.5167 | -4.3944
2008-11-06 | 0.026797 | 41856.8667 | -3.6195
2008-11-07 | 0.064946 | 101469.4833 | -2.7342
2008-11-08 | 0.0033318 | 5205.6 | -5.7043
2008-11-09 | 0.0020904 | 3266.0833 | -6.1704
2008-11-10 | 0.070176 | 109521.0167 | -2.6567
2008-11-11 | 0.19242 | 298983.7333 | -1.6481
2008-11-12 | 0.10644 | 166187.2333 | -2.2402
2008-11-13 | 0.49656 | 776081.4167 | -0.70006
2008-11-14 | 0.75266 | 1176978.05 | -0.28414
2008-11-15 | 0.32949 | 514538.75 | -1.1102
2008-11-16 | 0.085674 | 133792.3833 | -2.4572
2008-11-17 | 0.00527 | 8216.5333 | -5.2457
2008-11-18 | 0.12824 | 199131.7167 | -2.0538
2008-11-19 | 0.37323 | 583545.6333 | -0.98555
2008-11-20 | 0.54607 | 853687.1833 | -0.605
2008-11-21 | 0.15763 | 246363.05 | -1.8475
2008-11-22 | 0.40311 | 630980.9667 | -0.90854
2008-11-23 | 0.42497 | 665199.0333 | -0.85573
2008-11-24 | 0.27272 | 426145.2333 | -1.2993
2008-11-25 | 0.040817 | 63486.4167 | -3.1987
2008-11-26 | 0.24898 | 389197.7667 | -1.3904
2008-11-27 | 0.4471 | 699115.3667 | -0.80498
2008-11-28 | 0.3363 | 525910.8667 | -1.0898
2008-11-29 | 0.15735 | 246047.2833 | -1.8493
2008-11-30 | 0.16964 | 265275.7833 | -1.774
2008-12-01 | 0.1624 | 253583.85 | -1.8177
2008-12-02 | 0.56677 | 881063.7833 | -0.56781
2008-12-03 | 0.9968 | 1557318.7 | -0.0032025
2008-12-04 | 0.40321 | 629975.4667 | -0.90831
2008-12-05 | 0.018573 | 29015.8333 | -3.9861
2008-12-06 | 0.23402 | 364121.6333 | -1.4523
2008-12-07 | 0.46249 | 719595.5833 | -0.77114
2008-12-08 | 0.45717 | 709190.0333 | -0.78269
2008-12-09 | 0.40616 | 627627.9667 | -0.90101
2008-12-10 | 0.15745 | 241609.2667 | -1.8486
2008-12-11 | 1.4164 | 2171735.5833 | 0.34813
2008-12-12 | 0.49533 | 748921.9667 | -0.70252
2008-12-13 | 0.59961 | 888608.8333 | -0.51148
2008-12-14 | 0.11363 | 168400.9667 | -2.1748
2008-12-15 | 0.17564 | 259878.5 | -1.7393
2008-12-16 | 0.24924 | 362985.1833 | -1.3894
2008-12-17 | 0.024332 | 38040.0833 | -3.716
2008-12-18 | 0.14725 | 229425.6333 | -1.9156
2008-12-19 | 0.047395 | 74156.0167 | -3.0492
2008-12-20 | 0.03638 | 56918.5667 | -3.3137
2008-12-21 | 0.16085 | 251658.8667 | -1.8273
2008-12-22 | 0.73844 | 1151283.2 | -0.30322
2008-12-23 | 0.35452 | 552406.95 | -1.037
2008-12-24 | 0.083888 | 130853.6167 | -2.4783
2008-12-25 | 0.12539 | 195018.25 | -2.0763
2008-12-26 | 0.0152 | 23796.8 | -4.1865
2008-12-27 | 0.025744 | 40305.0833 | -3.6596
2008-12-28 | 0.10875 | 170269.5333 | -2.2187
2008-12-29 | 1.2839 | 2011139.6 | 0.24993
2008-12-30 | 0.15343 | 240001.0167 | -1.8745
2008-12-31 | 0.16854 | 264045.9833 | -1.7806
2009-01-01 | 0.28113 | 440450.5167 | -1.2689
2009-01-02 | 0.041795 | 65446.95 | -3.175
2009-01-03 | 0.0043774 | 6854.5667 | -5.4313
2009-01-04 | 0.22142 | 346727.2167 | -1.5077
2009-01-05 | 0.37942 | 594133.75 | -0.96911
2009-01-06 | 0.24491 | 381886.5167 | -1.4069
2009-01-07 | 0.56713 | 885998.0167 | -0.56717
2009-01-08 | 0.36198 | 566419.0167 | -1.0162
2009-01-09 | 0.28742 | 449791.2167 | -1.2468
2009-01-10 | 0.16851 | 263717.2333 | -1.7808
2009-01-11 | 0.20779 | 325187.25 | -1.5712
2009-01-12 | 2.5194 | 3936248.6 | 0.92403
2009-01-13 | 0.40441 | 631124.0667 | -0.90533
2009-01-14 | 0.53723 | 836806.55 | -0.62133
2009-01-15 | 1.0619 | 1654085.95 | 0.060082
2009-01-16 | 0.24638 | 383762.5833 | -1.4009
2009-01-17 | 0.030261 | 47336.1333 | -3.4979
2009-01-18 | 0.11626 | 181853.35 | -2.152
2009-01-19 | 0.074989 | 117040.6833 | -2.5904
2009-01-20 | 0.33288 | 519544.4167 | -1.1
2009-01-21 | 1.7504 | 2731979.9667 | 0.55985
2009-01-22 | 0.8927 | 1393295.0667 | -0.1135
2009-01-23 | 0.26893 | 420947.6667 | -1.3133
2009-01-24 | 2.108 | 3298349.2667 | 0.74573
2009-01-25 | 0.39269 | 614447.0167 | -0.93472
2009-01-26 | 0.94705 | 1481852.05 | -0.054399
2009-01-27 | 0.78125 | 1220764.2833 | -0.24687
2009-01-28 | 0.15179 | 237584.8 | -1.8853
2009-01-29 | 0.14226 | 222676.3 | -1.9501
2009-01-30 | 0.1887 | 295366.4333 | -1.6676
2009-01-31 | 0.12122 | 189865.05 | -2.1101
2009-02-01 | 0.33351 | 522362.2667 | -1.0981
2009-02-02 | 0.2759 | 430804.1167 | -1.2877
2009-02-03 | 0.27944 | 434677.5833 | -1.275
2009-02-04 | 0.070492 | 109654.05 | -2.6523
2009-02-05 | 0.08499 | 132206.1833 | -2.4652
2009-02-06 | 0.71931 | 1126088.7833 | -0.32947
2009-02-07 | 0.27354 | 428240.1333 | -1.2963
2009-02-08 | 1.1533 | 1805555.7833 | 0.14265
2009-02-09 | 0.37866 | 592801.65 | -0.97111
2009-02-10 | 0.82051 | 1281658.7167 | -0.19783
2009-02-11 | 0.42472 | 663416.7167 | -0.85633
2009-02-12 | 0.13636 | 212993.5667 | -1.9925
2009-02-13 | 0.37312 | 585503.7667 | -0.98584
2009-02-14 | 0.33185 | 520731.4 | -1.1031
2009-02-15 | 0.18937 | 297162.7167 | -1.664
2009-02-16 | 0.13254 | 207733.1333 | -2.0209
2009-02-17 | 0.12805 | 199773.1 | -2.0554
2009-02-18 | 0.33028 | 517456.2167 | -1.1078
2009-02-19 | 0.80742 | 1267062.2 | -0.21391
2009-02-20 | 0.33631 | 528553.5667 | -1.0897
2009-02-21 | 0.47428 | 745398.8 | -0.74596
2009-02-22 | 0.18518 | 291031.7667 | -1.6864
2009-02-23 | 0.030304 | 47626.2833 | -3.4965
2009-02-24 | 0.53084 | 819108.8167 | -0.63329
2009-02-25 | 0.073708 | 113733.1667 | -2.6076
2009-02-26 | 0.2652 | 408859.2167 | -1.3273
2009-02-27 | 0.071175 | 110576.8167 | -2.6426
2009-02-28 | 0.047284 | 73453.7 | -3.0516
2009-03-01 | 0.1234 | 191700.1167 | -2.0923
2009-03-02 | 0.15259 | 236151.2667 | -1.88
2009-03-03 | 0.55836 | 869764.9 | -0.58275
2009-03-04 | 0.14131 | 219677.6333 | -1.9568
2009-03-05 | 0.4732 | 735644.85 | -0.74824
2009-03-06 | 0.0094904 | 14743.75 | -4.6575
2009-03-07 | 0.081019 | 125888.25 | -2.5131
2009-03-08 | 0.38561 | 599156.5333 | -0.95294
2009-03-09 | 0.34499 | 535646.3667 | -1.0642
2009-03-10 | 0.12761 | 197980.4 | -2.0588
2009-03-11 | 0.21992 | 341933.95 | -1.5145
2009-03-12 | 0.091144 | 141708.9667 | -2.3953
2009-03-13 | 0.33738 | 524892.65 | -1.0865
2009-03-14 | 1.198 | 1862446.8667 | 0.18067
2009-03-15 | 0.32192 | 500453.5167 | -1.1335
2009-03-16 | 0.14818 | 231073.1667 | -1.9094
2009-03-17 | 0.11203 | 174256.7833 | -2.189
2009-03-18 | 0.028638 | 44446.9833 | -3.553
2009-03-19 | 0.14358 | 223212.1 | -1.9408
2009-03-20 | 0.073098 | 113594.3167 | -2.616
2009-03-21 | 0.019839 | 30861.5833 | -3.9201
2009-03-22 | 0.019213 | 29887.2167 | -3.9522
2009-03-23 | 0.13816 | 217362.2167 | -1.9794
2009-03-24 | 0.45424 | 712169.55 | -0.78912
2009-03-25 | 0.3143 | 492845.2 | -1.1574
2009-03-26 | 0.34042 | 534136.3667 | -1.0776
2009-03-27 | 1.9471 | 3049206.05 | 0.66632
2009-03-28 | 0.083483 | 129779.25 | -2.4831
2009-03-29 | 0.15107 | 234840.3 | -1.89
2009-03-30 | 5.6086 | 8841998.7333 | 1.7243
2009-03-31 | 0.65751 | 1034744.8667 | -0.4193
2009-04-01 | 1.1548 | 1813711.85 | 0.14392
2009-04-02 | 0.1645 | 258361.3833 | -1.8049
2009-04-03 | 0.20678 | 325101.2833 | -1.5761
2009-04-04 | 1.2095 | 1901535.5 | 0.19017
2009-04-05 | 0.18402 | 289313.9833 | -1.6927
2009-04-06 | 0.069139 | 108988 | -2.6716
2009-04-07 | 0.078842 | 124504.3833 | -2.5403
2009-04-08 | 0.10207 | 161186.3167 | -2.2821
2009-04-09 | 0.29464 | 465288.6167 | -1.222
2009-04-10 | 0.040018 | 63196.2 | -3.2184
2009-04-11 | 0.22026 | 347832.3167 | -1.5129
2009-04-12 | 0.16851 | 266104.3333 | -1.7808
2009-04-13 | 1.8075 | 2854988 | 0.59195
2009-04-14 | 0.11374 | 179652.1833 | -2.1739
2009-04-15 | 0.26498 | 418541.0167 | -1.3281
2009-04-16 | 0.14207 | 224404.5167 | -1.9514
2009-04-17 | 0.77595 | 1225614.1667 | -0.25366
2009-04-18 | 0.010469 | 16535.3833 | -4.5594
2009-04-19 | 0.34747 | 548823.35 | -1.0571
2009-04-20 | 0.22432 | 354317.2667 | -1.4947
2009-04-21 | 0.046284 | 73095.2833 | -3.073
2009-04-22 | 0.064572 | 101991.5333 | -2.74
2009-04-23 | 0.042842 | 67669.4833 | -3.1502
2009-04-24 | 0.33331 | 526467.5667 | -1.0987
2009-04-25 | 0.09279 | 146564.05 | -2.3774
2009-04-26 | 0.79816 | 1260701.6 | -0.22545
2009-04-27 | 0.17419 | 275138.55 | -1.7476
2009-04-28 | 0.25647 | 401421.2167 | -1.3608
2009-04-29 | 0.086358 | 136404.75 | -2.4492
2009-04-30 | 0.021791 | 34419.4667 | -3.8262
2009-05-01 | 0.06858 | 108323.8333 | -2.6798
2009-05-02 | 0.1058 | 167114.85 | -2.2462
2009-05-03 | 0.26707 | 421842.4 | -1.3202
2009-05-04 | 0.045337 | 71610.6333 | -3.0936
2009-05-05 | 0.010319 | 16300.7833 | -4.5737
2009-05-06 | 0.14145 | 223463.2833 | -1.9558
2009-05-07 | 0.089681 | 141678.55 | -2.4115
2009-05-08 | 0.49917 | 789851.1167 | -0.6948
2009-05-09 | 0.10294 | 162886.6333 | -2.2736
2009-05-10 | 0.48456 | 766729.35 | -0.72451
2009-05-11 | 0.072407 | 114571.0833 | -2.6255
2009-05-12 | 0.050723 | 80259.2833 | -2.9814
2009-05-13 | 0.42707 | 661579.9167 | -0.8508
2009-05-14 | 0.04643 | 70847.9333 | -3.0698
2009-05-15 | 0.10099 | 157041.4 | -2.2927
2009-05-16 | 0.82234 | 1278750.0333 | -0.1956
2009-05-17 | 0.044878 | 69785.5 | -3.1038
2009-05-18 | 0.036061 | 56074.8 | -3.3226
2009-05-19 | 0.49477 | 767066.45 | -0.70367
2009-05-20 | 0.6123 | 955639.8167 | -0.49054
2009-05-21 | 0.20831 | 329473.3333 | -1.5688
2009-05-22 | 1.3067 | 2066817.1167 | 0.26752
2009-05-23 | 0.27734 | 438656.1833 | -1.2825
2009-05-24 | 0.070475 | 111468.4167 | -2.6525
2009-05-25 | 0.71788 | 1135464.5167 | -0.33145
2009-05-26 | 0.078229 | 122886.5667 | -2.5481
2009-05-27 | 0.1509 | 237314.6333 | -1.8911
2009-05-28 | 0.20351 | 321903.65 | -1.592
2009-05-29 | 0.059863 | 94877.8833 | -2.8157
2009-05-30 | 0.1352 | 214279.3333 | -2.001
2009-05-31 | 0.17419 | 276068.7167 | -1.7476
2009-06-01 | 0.14526 | 230228.2833 | -1.9292
2009-06-02 | 0.20041 | 317607.5167 | -1.6074
2009-06-03 | 0.11184 | 177259.6333 | -2.1907
2009-06-04 | 0.02505 | 39700.5833 | -3.6869
2009-06-05 | 0.38933 | 617049.8667 | -0.94332
2009-06-06 | 0.016544 | 26220.55 | -4.1017
2009-06-07 | 0.0069111 | 10953.2667 | -4.9746
2009-06-08 | 0.1285 | 203664.8167 | -2.0518
2009-06-09 | 0.35174 | 555982.45 | -1.0449
2009-06-10 | 0.41841 | 662055.3167 | -0.8713
2009-06-11 | 0.339 | 536741.2167 | -1.0818
2009-06-12 | 0.1696 | 268557.4333 | -1.7743
2009-06-13 | 0.2053 | 324097.0667 | -1.5833
2009-06-14 | 0.10108 | 159563.6 | -2.2919
2009-06-15 | 0.2145 | 338616.3667 | -1.5394
2009-06-16 | 0.32226 | 510108.5 | -1.1324
2009-06-17 | 0.23803 | 377697.7167 | -1.4354
2009-06-18 | 0.19071 | 302618.8833 | -1.657
2009-06-19 | 0.18708 | 296408.25 | -1.6762
2009-06-20 | 0.16342 | 258931.6667 | -1.8114
2009-06-21 | 0.077478 | 122757.85 | -2.5578
2009-06-22 | 0.10241 | 162258.4333 | -2.2788
2009-06-23 | 2.2144 | 3500022.6333 | 0.79498
2009-06-24 | 1.1415 | 1811340.4167 | 0.13237
2009-06-25 | 0.092642 | 147000.1833 | -2.379
2009-06-26 | 0.082174 | 130390.3 | -2.4989
2009-06-27 | 0.27352 | 434007.5 | -1.2964
2009-06-28 | 0.060312 | 95700.5 | -2.8082
2009-06-29 | 0.1419 | 225167.4 | -1.9526
2009-06-30 | 0.13427 | 212952.4833 | -2.0079
2009-07-01 | 0.11437 | 181335.7333 | -2.1683
2009-07-02 | 0.13857 | 219715.1667 | -1.9764
2009-07-03 | 0.38231 | 606170 | -0.96153
2009-07-04 | 0.19089 | 302663.4 | -1.6561
2009-07-05 | 0.086238 | 136734.3833 | -2.4506
2009-07-06 | 0.27521 | 436360.25 | -1.2902
2009-07-07 | 0.080578 | 127760.45 | -2.5185
2009-07-08 | 0.20352 | 317537.2333 | -1.592
2009-07-09 | 0.029246 | 45695.95 | -3.532
2009-07-10 | 0.090018 | 140650.6167 | -2.4077
2009-07-11 | 0.18916 | 295563.8167 | -1.6651
2009-07-12 | 0.024765 | 38694.1167 | -3.6983
2009-07-13 | 0.14731 | 230171.7833 | -1.9152
2009-07-14 | 0.018701 | 29555.7833 | -3.9792
2009-07-15 | 0.05105 | 80772.1 | -2.975
2009-07-16 | 0.016963 | 26838.4 | -4.0767
2009-07-17 | 0.33252 | 526109.6833 | -1.1011
2009-07-18 | 0.53077 | 839790.9667 | -0.63343
2009-07-19 | 0.17354 | 274570.9167 | -1.7514
2009-07-20 | 0.069957 | 110686.5833 | -2.6599
2009-07-21 | 0.25771 | 408155.9167 | -1.3559
2009-07-22 | 0.39051 | 619115.3833 | -0.94029
2009-07-23 | 0.016315 | 25864.85 | -4.1157
2009-07-24 | 0.14295 | 226637.1333 | -1.9452
2009-07-25 | 0.13696 | 217141.3667 | -1.988
2009-07-26 | 0.34227 | 542589.5333 | -1.0721
2009-07-27 | 0.081082 | 128535.9333 | -2.5123
2009-07-28 | 1.0721 | 1699394.1167 | 0.069639
2009-07-29 | 0.19374 | 307089.9167 | -1.6412
2009-07-30 | 0.045088 | 71698.8 | -3.0991
2009-07-31 | 0.047987 | 76307.8667 | -3.0368
2009-08-01 | 0.037778 | 60074.8833 | -3.276
2009-08-02 | 0.15272 | 242853.8667 | -1.8791
2009-08-03 | 0.01358 | 21595.3667 | -4.2991
2009-08-04 | 0.23149 | 367339.9667 | -1.4632
2009-08-05 | 0.014789 | 23523.4167 | -4.2139
2009-08-06 | 0.23149 | 368213.4833 | -1.4632
2009-08-07 | 0.25576 | 406821.2167 | -1.3635
2009-08-08 | 0.13639 | 216945.6167 | -1.9922
2009-08-09 | 0.10881 | 173068.55 | -2.2182
2009-08-10 | 0.064256 | 102206.6833 | -2.7449
2009-08-11 | 0.16497 | 262152.1 | -1.802
2009-08-12 | 0.065087 | 103505.0833 | -2.732
2009-08-13 | 0.090989 | 144696.6833 | -2.397
2009-08-14 | 0.037234 | 59211.6667 | -3.2905
2009-08-15 | 0.31399 | 499333.35 | -1.1584
2009-08-16 | 0.27666 | 439965.6333 | -1.285
2009-08-17 | 0.065273 | 103800.65 | -2.7292
2009-08-18 | 0.17421 | 276733.9 | -1.7475
2009-08-19 | 0.17741 | 278919.1833 | -1.7293
2009-08-20 | 0.15769 | 248177.0167 | -1.8471
2009-08-21 | 0.042552 | 66963.5667 | -3.157
2009-08-22 | 0.078789 | 123990.0833 | -2.541
2009-08-23 | 0.059676 | 93912.55 | -2.8188
2009-08-24 | 0.26441 | 416094.5 | -1.3303
2009-08-25 | 1.3766 | 2185239.5333 | 0.31959
2009-08-26 | 0.10903 | 173315.1333 | -2.2162
2009-08-27 | 0.058497 | 93038.85 | -2.8388
2009-08-28 | 0.37697 | 599576.5833 | -0.97559
2009-08-29 | 0.57329 | 911830.3167 | -0.55636
2009-08-30 | 0.35798 | 569367.9667 | -1.0273
2009-08-31 | 0.15504 | 246600.7833 | -1.864
2009-09-01 | 0.0012346 | 1959.45 | -6.697
2009-09-02 | 0.029348 | 46679.3667 | -3.5285
2009-09-03 | 0.19592 | 311652.1333 | -1.63
2009-09-04 | 0.4571 | 727005.1333 | -0.78285
2009-09-05 | 0.044348 | 70533.3 | -3.1157
2009-09-06 | 0.29177 | 464048.5667 | -1.2318
2009-09-07 | 0.20459 | 325393.65 | -1.5867
2009-09-08 | 0.21488 | 341576.5167 | -1.5377
2009-09-09 | 0.052566 | 83641.0333 | -2.9457
2009-09-10 | 0.093564 | 148866.1833 | -2.3691
2009-09-11 | 0.065817 | 104719.2667 | -2.7209
2009-09-12 | 0.16935 | 269450.1333 | -1.7758
2009-09-13 | 0.10895 | 173352.0667 | -2.2168
2009-09-14 | 0.10907 | 173540.7333 | -2.2158
2009-09-15 | 0.015043 | 23908.8833 | -4.1968
2009-09-16 | 0.11462 | 182257.3333 | -2.1661
2009-09-17 | 0.27403 | 435968.7167 | -1.2945
2009-09-18 | 0.2352 | 374194.9333 | -1.4473
2009-09-19 | 0.36338 | 578137.2 | -1.0123
2009-09-20 | 0.17095 | 271982.6 | -1.7664
2009-09-21 | 0.063189 | 100531.9 | -2.7616
2009-09-22 | 0.24764 | 393377.45 | -1.3958
2009-09-23 | 1.2799 | 2037398.5167 | 0.24679
2009-09-24 | 0.025374 | 40075.7 | -3.674
2009-09-25 | 0.048414 | 77066.85 | -3.028
2009-09-26 | 0.68432 | 1089317.2167 | -0.37933
2009-09-27 | 0.44632 | 710464.7 | -0.80672
2009-09-28 | 0.067334 | 107183.1333 | -2.6981
2009-09-29 | 0.099718 | 158482.8167 | -2.3054
2009-09-30 | 0.25116 | 399676.5667 | -1.3817
2009-10-01 | 0.24331 | 387395.7833 | -1.4134
2009-10-02 | 0.23492 | 374052.7833 | -1.4485
2009-10-03 | 0.3274 | 521302.3167 | -1.1166
2009-10-04 | 0.060543 | 96398.5167 | -2.8044
2009-10-05 | 4.4399 | 7069413.1333 | 1.4906
2009-10-06 | 0.090355 | 143482.1833 | -2.404
2009-10-07 | 0.17982 | 286065.3167 | -1.7158
2009-10-08 | 0.37392 | 595498.3167 | -0.9837
2009-10-09 | 0.027074 | 43124.5 | -3.6092
2009-10-10 | 0.20473 | 326103.75 | -1.586
2009-10-11 | 0.017089 | 27220.3833 | -4.0693
2009-10-12 | 0.23629 | 376367.5333 | -1.4427
2009-10-13 | 0.33786 | 536379.7833 | -1.0851
2009-10-14 | 0.22534 | 358527.6167 | -1.4901
2009-10-15 | 0.15451 | 246083.1667 | -1.8675
2009-10-16 | 0.12126 | 193170.3333 | -2.1098
2009-10-17 | 0.046786 | 74528.9333 | -3.0622
2009-10-18 | 0.0020672 | 3293 | -6.1816
2009-10-19 | 0.08766 | 139642.15 | -2.4343
2009-10-20 | 0.08239 | 131026.3333 | -2.4963
2009-10-21 | 0.25035 | 398744.7 | -1.3849
2009-10-22 | 0.029011 | 46208.15 | -3.5401
2009-10-23 | 0.39893 | 635523.8667 | -0.91896
2009-10-24 | 0.18658 | 297231.1667 | -1.6789
2009-10-25 | 1.9075 | 3038744.6333 | 0.64579
2009-10-26 | 0.4616 | 735358.35 | -0.77305
2009-10-27 | 0.056658 | 89792.1167 | -2.8707
2009-10-28 | 0.1295 | 205763.2333 | -2.0441
2009-10-29 | 0.058072 | 92273.1667 | -2.8461
2009-10-30 | 0.2266 | 360031.5167 | -1.4846
2009-10-31 | 0.046708 | 74212.6 | -3.0638
2009-11-01 | 0.18946 | 301031.6667 | -1.6636
2009-11-02 | 0.1575 | 250253.3833 | -1.8483
2009-11-03 | 0.28322 | 450354.1833 | -1.2615
2009-11-04 | 0.11808 | 187976.8833 | -2.1364
2009-11-05 | 0.068485 | 109019.8333 | -2.6811
2009-11-06 | 0.024892 | 39623.8 | -3.6932
2009-11-07 | 0.015028 | 23921.4667 | -4.1978
2009-11-08 | 0.24177 | 384850.2667 | -1.4198
2009-11-09 | 0.046422 | 73894.4 | -3.07
2009-11-10 | 0.19785 | 314521.8333 | -1.6203
2009-11-11 | 0.05669 | 90249.4167 | -2.8702
2009-11-12 | 0.30055 | 478460.2667 | -1.2021
2009-11-13 | 0.090975 | 144829.8833 | -2.3972
2009-11-14 | 0.10487 | 166945.9 | -2.2551
2009-11-15 | 0.21599 | 343844.1667 | -1.5325
2009-11-16 | 0.63806 | 1015782.1833 | -0.44932
2009-11-17 | 0.19493 | 309752.1 | -1.6351
2009-11-18 | 0.080833 | 128597.9667 | -2.5154
2009-11-19 | 0.14657 | 233451.1 | -1.9202
2009-11-20 | 4.1559 | 6618581.3 | 1.4245
2009-11-21 | 0.46036 | 733160.1833 | -0.77575
2009-11-22 | 0.62154 | 989850.7667 | -0.47556
2009-11-23 | 0.39061 | 622082.4833 | -0.94004
2009-11-24 | 0.18291 | 291006.1 | -1.6988
2009-11-25 | 0.15907 | 253440.8833 | -1.8384
2009-11-26 | 0.025172 | 40113.2667 | -3.682
2009-11-27 | 0.096764 | 154197.9667 | -2.3355
2009-11-28 | 1.1722 | 1867939.3333 | 0.15887
2009-11-29 | 0.16276 | 259363.8 | -1.8155
2009-11-30 | 0.32956 | 525173.2167 | -1.11
2009-12-01 | 0.23383 | 372161.2333 | -1.4532
2009-12-02 | 0.041413 | 65996.7833 | -3.1842
2009-12-03 | 0.094524 | 150648.5333 | -2.3589
2009-12-04 | 0.24101 | 384097.25 | -1.4229
2009-12-05 | 0.05367 | 85533.5333 | -2.9249
2009-12-06 | 0.059886 | 95440.0333 | -2.8153
2009-12-07 | 0.21812 | 347622.65 | -1.5227
2009-12-08 | 0.55694 | 886174.8333 | -0.58529
2009-12-09 | 0.21994 | 350559 | -1.5144
2009-12-10 | 0.18285 | 291412.4167 | -1.6991
2009-12-11 | 0.075405 | 120168.9667 | -2.5849
2009-12-12 | 0.21265 | 338887.4 | -1.5481
2009-12-13 | 0.35122 | 559721.9833 | -1.0463
2009-12-14 | 0.17806 | 283763.15 | -1.7256
2009-12-15 | 0.086095 | 137095.2833 | -2.4523
2009-12-16 | 0.15917 | 253645.2 | -1.8378
2009-12-17 | 1.1276 | 1796992.5667 | 0.12007
2009-12-18 | 0.58286 | 928874.4833 | -0.53981
2009-12-19 | 0.22353 | 356222.4833 | -1.4982
2009-12-20 | 0.21558 | 343560.3667 | -1.5344
2009-12-21 | 0.12983 | 206907.1667 | -2.0415
2009-12-22 | 0.109 | 170410.7667 | -2.2164
2009-12-23 | 0.06928 | 108670.7167 | -2.6696
2009-12-24 | 0.28206 | 447973.7167 | -1.2656
2009-12-25 | 0.083891 | 133338.0167 | -2.4782
2009-12-26 | 0.68695 | 1091851.1333 | -0.37549
2009-12-27 | 0.0799 | 127181.1167 | -2.527
2009-12-28 | 0.25457 | 405215.7 | -1.3682
2009-12-29 | 0.12343 | 197152.2333 | -2.0921
2009-12-30 | 0.24989 | 399436.3167 | -1.3867
2009-12-31 | 0.12524 | 200202.7833 | -2.0775
2010-01-01 | 0.067143 | 107341.7167 | -2.7009
2010-01-02 | 0.62907 | 1004550.3833 | -0.46351
2010-01-03 | 0.1614 | 257730.6333 | -1.8239
2010-01-04 | 0.015444 | 24662.1167 | -4.1705
2010-01-05 | 0.14484 | 231230.2167 | -1.9321
2010-01-06 | 0.23767 | 379987.7167 | -1.4369
2010-01-07 | 0.12813 | 204840.5667 | -2.0547
2010-01-08 | 0.1058 | 169142.5 | -2.2462
2010-01-09 | 0.12726 | 203448.7 | -2.0615
2010-01-10 | 0.25998 | 415607.15 | -1.3472
2010-01-11 | 0.20032 | 320230.8 | -1.6079
2010-01-12 | 0.86507 | 1381696.8833 | -0.14494
2010-01-13 | 0.80772 | 1291495.8667 | -0.21354
2010-01-14 | 0.14972 | 239392.3667 | -1.899
2010-01-15 | 0.055679 | 89028.8 | -2.8882
2010-01-16 | 0.12764 | 204092.7667 | -2.0585
2010-01-17 | 0.34518 | 551932.2833 | -1.0637
2010-01-18 | 0.037659 | 60234.8333 | -3.2792
2010-01-19 | 0.29206 | 466384.65 | -1.2308
2010-01-20 | 0.31567 | 504926.3 | -1.153
2010-01-21 | 0.16425 | 262718.1 | -1.8064
2010-01-22 | 0.85997 | 1375503.8667 | -0.15086
2010-01-23 | 0.77325 | 1236805.7667 | -0.25715
2010-01-24 | 0.29842 | 477321.6667 | -1.2092
2010-01-25 | 0.37226 | 595424.3667 | -0.98816
2010-01-26 | 0.096392 | 154177.9 | -2.3393
2010-01-27 | 0.5995 | 958731.1 | -0.51166
2010-01-28 | 1.4212 | 2272828.3167 | 0.35151
2010-01-29 | 0.16359 | 259786.35 | -1.8104
2010-01-30 | 0.18295 | 290537.85 | -1.6985
2010-01-31 | 0.32491 | 515964.25 | -1.1242
2010-02-01 | 0.40453 | 642404.2833 | -0.90504
2010-02-02 | 0.053478 | 85481.4833 | -2.9285
2010-02-03 | 0.23585 | 377384.9833 | -1.4446
2010-02-04 | 0.11012 | 176218.6667 | -2.2062
2010-02-05 | 1.0358 | 1657541.8167 | 0.035129
2010-02-06 | 0.4412 | 704295.5333 | -0.81827
2010-02-07 | 0.67276 | 1073939.7833 | -0.39637
2010-02-08 | 0.095461 | 152387.15 | -2.349
2010-02-09 | 0.053469 | 85335.55 | -2.9287
2010-02-10 | 0.056088 | 89779.3833 | -2.8808
2010-02-11 | 0.25385 | 406308.65 | -1.371
2010-02-12 | 1.6356 | 2617987.5833 | 0.49204
2010-02-13 | 0.15746 | 252026.1333 | -1.8486
2010-02-14 | 0.12761 | 204253.3833 | -2.0588
2010-02-15 | 0.62576 | 1000786.9333 | -0.46879
2010-02-16 | 0.24404 | 388414.5167 | -1.4104
2010-02-17 | 0.20473 | 326617.5667 | -1.5861
2010-02-18 | 0.60744 | 969142.35 | -0.4985
2010-02-19 | 0.44205 | 705256.5833 | -0.81633
2010-02-20 | 0.27335 | 436107.7167 | -1.297
2010-02-21 | 0.26631 | 424867.6167 | -1.3231
2010-02-22 | 0.43947 | 701138.2 | -0.82218
2010-02-23 | 0.33667 | 537120.15 | -1.0887
2010-02-24 | 0.055967 | 89203.05 | -2.883
2010-02-25 | 0.014507 | 23164.85 | -4.2331
2010-02-26 | 0.35253 | 562903.05 | -1.0426
2010-02-27 | 0.19378 | 309416.85 | -1.641
2010-02-28 | 0.42803 | 683448.8667 | -0.84857
2010-03-01 | 0.089331 | 142639.3667 | -2.4154
2010-03-02 | 0.0065309 | 10405.5 | -5.0312
2010-03-03 | 0.027554 | 43992.55 | -3.5916
2010-03-04 | 0.074448 | 118861.6167 | -2.5977
2010-03-05 | 0.60164 | 960526.25 | -0.5081
2010-03-06 | 0.24069 | 384272.2333 | -1.4242
2010-03-07 | 0.23169 | 369772.55 | -1.4623
2010-03-08 | 0.34119 | 544517.7333 | -1.0753
2010-03-09 | 0.21387 | 341341.3333 | -1.5424
2010-03-10 | 0.10154 | 162382.1167 | -2.2873
2010-03-11 | 0.12181 | 194780.3 | -2.1053
2010-03-12 | 0.24964 | 399188.75 | -1.3877
2010-03-13 | 0.053568 | 85658.1667 | -2.9268
2010-03-14 | 0.015274 | 24424.8667 | -4.1816
2010-03-15 | 0.005251 | 8396.75 | -5.2493
2010-03-16 | 0.27183 | 433996.1833 | -1.3026
2010-03-17 | 0.075139 | 120193.3167 | -2.5884
2010-03-18 | 0.0081923 | 13103.7167 | -4.8046
2010-03-19 | 0.06707 | 107283.95 | -2.702
2010-03-20 | 0.35425 | 566646.05 | -1.0378
2010-03-21 | 0.31066 | 496923.1333 | -1.1691
2010-03-22 | 0.2342 | 374622.7333 | -1.4516
2010-03-23 | 0.14401 | 230039.4 | -1.9379
2010-03-24 | 0.076327 | 122180.3 | -2.5727
2010-03-25 | 0.076251 | 122060.6667 | -2.5737
2010-03-26 | 0.12074 | 193275.1833 | -2.1141
2010-03-27 | 0.070507 | 112863.5 | -2.652
2010-03-28 | 0.1611 | 257879.6667 | -1.8257
2010-03-29 | 0.10937 | 175070.6833 | -2.213
2010-03-30 | 0.49425 | 790287.75 | -0.70471
2010-03-31 | 0.42811 | 685705.9167 | -0.84838
2010-04-01 | 0.0036806 | 5894.9167 | -5.6047
2010-04-02 | 0.065705 | 105230.8 | -2.7226
2010-04-03 | 0.20134 | 322452.4167 | -1.6028
2010-04-04 | 0.0148 | 23702.9 | -4.2131
2010-04-05 | 0.0072605 | 11628.1167 | -4.9253
2010-04-06 | 0.10546 | 168901.3833 | -2.2494
2010-04-07 | 0.13031 | 208169.5667 | -2.0378
2010-04-08 | 0.089083 | 142666.7167 | -2.4182
2010-04-09 | 0.072685 | 116404.1167 | -2.6216
2010-04-10 | 0.060554 | 96976.8667 | -2.8042
2010-04-11 | 0.062413 | 99953.7833 | -2.774
2010-04-12 | 0.37371 | 598502.9 | -0.98426
2010-04-13 | 0.19194 | 306430.3667 | -1.6506
2010-04-14 | 0.19574 | 313427.1333 | -1.631
2010-04-15 | 0.036461 | 58384.0833 | -3.3115
2010-04-16 | 0.21809 | 349225.3333 | -1.5229
2010-04-17 | 0.025874 | 41432.85 | -3.6545
2010-04-18 | 0.057185 | 91571.9 | -2.8615
2010-04-19 | 0.18877 | 302275.8167 | -1.6672
2010-04-20 | 0.1223 | 195506.6167 | -2.1013
2010-04-21 | 0.01904 | 30498.8167 | -3.9612
2010-04-22 | 0.054219 | 86864.6 | -2.9147
2010-04-23 | 0.47359 | 758731.3167 | -0.74741
2010-04-24 | 0.038651 | 61921.0833 | -3.2532
2010-04-25 | 0.019652 | 31483.8333 | -3.9296
2010-04-26 | 0.072469 | 116100.0833 | -2.6246
2010-04-27 | 0.017802 | 28491.7333 | -4.0284
2010-04-28 | 0.1819 | 291267.1833 | -1.7043
2010-04-29 | 0.11874 | 190158.1833 | -2.1308
2010-04-30 | 0.094231 | 150893.75 | -2.362
2010-05-01 | 0.10116 | 161988.3167 | -2.2911
2010-05-02 | 0.027373 | 43832.5167 | -3.5982
2010-05-03 | 0.040877 | 65457.4167 | -3.1972
2010-05-04 | 0.066778 | 106696.15 | -2.7064
2010-05-05 | 0.24114 | 386368.0167 | -1.4224
2010-05-06 | 0.072564 | 116266.6333 | -2.6233
2010-05-07 | 0.026368 | 42249.2667 | -3.6356
2010-05-08 | 0.03119 | 49975.4333 | -3.4677
2010-05-09 | 0.03332 | 53388.3667 | -3.4016
2010-05-10 | 0.081459 | 130521.8333 | -2.5077
2010-05-11 | 0.16579 | 265522.6333 | -1.797
2010-05-12 | 0.55036 | 882065.8 | -0.59717
2010-05-13 | 0.024052 | 38549.3167 | -3.7276
2010-05-14 | 0.17817 | 285545.1333 | -1.725
2010-05-15 | 0.032212 | 51624.5167 | -3.4354
2010-05-16 | 0.011527 | 18473.75 | -4.4631
2010-05-17 | 0.22996 | 368546.0667 | -1.4699
2010-05-18 | 0.22905 | 366159.8 | -1.4738
2010-05-19 | 0.088575 | 141953.4 | -2.4239
2010-05-20 | 0.11163 | 178903.3667 | -2.1926
2010-05-21 | 0.19364 | 310335.3167 | -1.6417
2010-05-22 | 1.0066 | 1613209.8 | 0.006578
2010-05-23 | 0.26313 | 421702.5833 | -1.3351
2010-05-24 | 0.46228 | 740861.35 | -0.77159
2010-05-25 | 0.77835 | 1245199.0667 | -0.25057
2010-05-26 | 0.32219 | 516406.7667 | -1.1326
2010-05-27 | 0.058966 | 94546.7833 | -2.8308
2010-05-28 | 0.25156 | 403371.5 | -1.3801
2010-05-29 | 0.114 | 182798.8 | -2.1715
2010-05-30 | 0.20023 | 321065.6 | -1.6083
2010-05-31 | 0.16702 | 267810.85 | -1.7896
2010-06-01 | 0.053004 | 84367.7333 | -2.9374
2010-06-02 | 0.072769 | 116705.4333 | -2.6205
2010-06-03 | 0.17255 | 276741.3833 | -1.7571
2010-06-04 | 0.50414 | 808524.1833 | -0.6849
2010-06-05 | 0.10634 | 170545.1667 | -2.2411
2010-06-06 | 0.04923 | 78952.9333 | -3.0113
2010-06-07 | 0.17869 | 286572.1167 | -1.7221
2010-06-08 | 0.14876 | 238155.2833 | -1.9054
2010-06-09 | 0.14475 | 232238.1167 | -1.9328
2010-06-10 | 0.20604 | 330590.6 | -1.5797
2010-06-11 | 0.057244 | 91845.6 | -2.8604
2010-06-12 | 0.089449 | 143517.4833 | -2.4141
2010-06-13 | 0.067306 | 107990.4 | -2.6985
2010-06-14 | 0.073539 | 117991.25 | -2.6099
2010-06-15 | 0.1454 | 233159.6833 | -1.9283
2010-06-16 | 0.026654 | 42752.1667 | -3.6248
2010-06-17 | 0.13309 | 213467.45 | -2.0167
2010-06-18 | 0.036394 | 58378.1 | -3.3134
2010-06-19 | 0.048255 | 77405.2333 | -3.0312
2010-06-20 | 0.464 | 744290.35 | -0.76787
2010-06-21 | 0.27364 | 438933 | -1.296
2010-06-22 | 0.16549 | 264810.5333 | -1.7989
2010-06-23 | 0.20419 | 327409.3333 | -1.5887
2010-06-24 | 0.17803 | 285450.8333 | -1.7258
2010-06-25 | 0.18976 | 304271.8167 | -1.662
2010-06-26 | 0.0078408 | 12572.6833 | -4.8484
2010-06-27 | 0.06943 | 111329.3167 | -2.6674
2010-06-28 | 0.37245 | 597219.05 | -0.98765
2010-06-29 | 0.20246 | 324124.3 | -1.5972
2010-06-30 | 0.25716 | 412358.4833 | -1.3581
2010-07-01 | 0.34674 | 556269.5833 | -1.0592
2010-07-02 | 0.028995 | 46513.8333 | -3.5406
2010-07-03 | 0.041746 | 66969.9 | -3.1761
2010-07-04 | 0.12755 | 204620.6167 | -2.0592
2010-07-05 | 0.78945 | 1266440.25 | -0.23642
2010-07-06 | 0.16477 | 263692.7833 | -1.8032
2010-07-07 | 0.10749 | 172525.8 | -2.2303
2010-07-08 | 0.11996 | 192522.1333 | -2.1206
2010-07-09 | 0.066927 | 107419.75 | -2.7042
2010-07-10 | 0.46545 | 746186.0833 | -0.76475
2010-07-11 | 0.13428 | 215274.5 | -2.0078
2010-07-12 | 0.18948 | 303757.2833 | -1.6635
2010-07-13 | 0.067446 | 107991.9833 | -2.6964
2010-07-14 | 0.34075 | 547033.4167 | -1.0766
2010-07-15 | 0.032602 | 52339.0333 | -3.4234
2010-07-16 | 0.030764 | 49392.3167 | -3.4814
2010-07-17 | 0.763 | 1224918.8167 | -0.2705
2010-07-18 | 0.15703 | 252096.1833 | -1.8513
2010-07-19 | 0.13127 | 210747.9833 | -2.0305
2010-07-20 | 0.16481 | 264312.6167 | -1.8029
2010-07-21 | 0.29037 | 466230.2 | -1.2366
2010-07-22 | 0.12167 | 195357.4167 | -2.1064
2010-07-23 | 0.076896 | 123468.2667 | -2.5653
2010-07-24 | 0.32094 | 515324.6667 | -1.1365
2010-07-25 | 0.022569 | 36238.1333 | -3.7912
2010-07-26 | 0.32881 | 527961.35 | -1.1123
2010-07-27 | 0.068472 | 109646.75 | -2.6813
2010-07-28 | 0.95515 | 1531656.5 | -0.045884
2010-07-29 | 0.1223 | 196117.9667 | -2.1013
2010-07-30 | 0.04707 | 75483.35 | -3.0561
2010-07-31 | 1.8824 | 3018633.05 | 0.63252
2010-08-01 | 0.14531 | 233032.9833 | -1.9289
2010-08-02 | 0.63584 | 1019666.4333 | -0.4528
2010-08-03 | 4.2727 | 6842251.8833 | 1.4523
2010-08-04 | 0.19136 | 306851.3333 | -1.6536
2010-08-05 | 0.23617 | 378716.2 | -1.4432
2010-08-06 | 0.021367 | 34265.0333 | -3.8459
2010-08-07 | 0.088393 | 141747.4667 | -2.426
2010-08-08 | 0.081968 | 131445.4 | -2.5014
2010-08-09 | 0.0058413 | 9367.1 | -5.1428
2010-08-10 | 0.3848 | 615777.6667 | -0.95503
2010-08-11 | 0.19461 | 311964.4333 | -1.6368
2010-08-12 | 0.27786 | 445413.8167 | -1.2806
2010-08-13 | 0.011306 | 18123.2 | -4.4824
2010-08-14 | 0.0056768 | 9099.7333 | -5.1714
2010-08-15 | 0.25999 | 416750.1667 | -1.3471
2010-08-16 | 0.10208 | 163637.0167 | -2.282
2010-08-17 | 0.011776 | 18863.6333 | -4.4417
2010-08-18 | 0.036563 | 58659.5 | -3.3087
2010-08-19 | 0.20612 | 330674.5 | -1.5793
2010-08-20 | 0.28253 | 453280.85 | -1.264
2010-08-21 | 0.24893 | 399377.9833 | -1.3906
2010-08-22 | 0.33663 | 540072.6333 | -1.0888
2010-08-23 | 0.11314 | 181514.85 | -2.1791
2010-08-24 | 0.19186 | 307933.5667 | -1.651
2010-08-25 | 0.059699 | 95933.5667 | -2.8184
2010-08-26 | 0.028564 | 45900.15 | -3.5556
2010-08-27 | 0.07565 | 121562.2 | -2.5816
2010-08-28 | 0.11599 | 186381.6333 | -2.1543
2010-08-29 | 0.0098216 | 15782.3833 | -4.6232
2010-08-30 | 1.406 | 2259373.7167 | 0.34078
2010-08-31 | 0.091626 | 147000.7833 | -2.39
2010-09-01 | 0.19943 | 320524.05 | -1.6123
2010-09-02 | 0.20806 | 334431.3167 | -1.5699
2010-09-03 | 1.2285 | 1973110.8167 | 0.20579
2010-09-04 | 0.20172 | 323993.55 | -1.6009
2010-09-05 | 3.1103 | 4995560.2333 | 1.1347
2010-09-06 | 0.010571 | 16978.8833 | -4.5496
2010-09-07 | 0.087283 | 139024.2167 | -2.4386
2010-09-08 | 0.29073 | 464040.7667 | -1.2353
2010-09-09 | 0.19453 | 310485.0333 | -1.6372
2010-09-10 | 0.26629 | 425058.2 | -1.3232
2010-09-11 | 0.025319 | 40415.5 | -3.6762
2010-09-12 | 0.33791 | 539379.0667 | -1.085
2010-09-13 | 0.045866 | 73212.3 | -3.082
2010-09-14 | 0.58898 | 940201.75 | -0.52936
2010-09-15 | 0.1537 | 245670.6167 | -1.8728
2010-09-16 | 0.092445 | 147754.4333 | -2.3811
2010-09-17 | 0.20086 | 321054.3833 | -1.6051
2010-09-18 | 0.013576 | 21699.2167 | -4.2995
2010-09-19 | 0.094208 | 150578.7333 | -2.3623
2010-09-20 | 0.19487 | 311472.05 | -1.6354
2010-09-21 | 0.11665 | 186161.7 | -2.1485
2010-09-22 | 0.31405 | 502411.1 | -1.1582
2010-09-23 | 0.023547 | 37671.15 | -3.7487
2010-09-24 | 0.15408 | 246511.8 | -1.8703
2010-09-25 | 0.3031 | 484913.0167 | -1.1937
2010-09-26 | 0.12673 | 202755.5 | -2.0657
2010-09-27 | 0.1524 | 243825.0667 | -1.8812
2010-09-28 | 0.078533 | 125521.5833 | -2.5442
2010-09-29 | 0.078561 | 125709.3 | -2.5439
2010-09-30 | 0.12242 | 196273.8667 | -2.1003
2010-10-01 | 0.20913 | 335292.9333 | -1.5648
2010-10-02 | 0.099532 | 159580.6667 | -2.3073
2010-10-03 | 0.17363 | 278381.7667 | -1.7508
2010-10-04 | 0.025142 | 40310.1333 | -3.6832
2010-10-05 | 0.21122 | 338513.1833 | -1.5549
2010-10-06 | 0.058486 | 93607.7333 | -2.839
2010-10-07 | 0.06817 | 109336.5333 | -2.6858
2010-10-08 | 0.15991 | 256485.8 | -1.8331
2010-10-09 | 0.097307 | 156073.7333 | -2.3299
2010-10-10 | 0.010585 | 16978.2167 | -4.5483
2010-10-11 | 0.090771 | 145589.9833 | -2.3994
2010-10-12 | 0.37901 | 607234.7833 | -0.9702
2010-10-13 | 0.088816 | 142473.5 | -2.4212
2010-10-14 | 0.069949 | 112215.6667 | -2.66
2010-10-15 | 0.69735 | 1118732.4333 | -0.36046
2010-10-16 | 2.3474 | 3765752.9 | 0.85329
2010-10-17 | 0.011687 | 18749.3667 | -4.4493
2010-10-18 | 0.065502 | 105081.1667 | -2.7257
2010-10-19 | 0.099286 | 158949.3 | -2.3098
2010-10-20 | 0.1068 | 171418.85 | -2.2368
2010-10-21 | 0.18379 | 295002.4333 | -1.694
2010-10-22 | 0.050745 | 81457.5167 | -2.9809
2010-10-23 | 0.31503 | 505693.4833 | -1.1551
2010-10-24 | 0.26324 | 422565.4167 | -1.3347
2010-10-25 | 0.069888 | 112186.1 | -2.6609
2010-10-26 | 0.48233 | 774158.2333 | -0.72913
2010-10-27 | 0.046332 | 74570.2667 | -3.0719
2010-10-28 | 0.24826 | 399578.95 | -1.3933
2010-10-29 | 0.23539 | 378862.6667 | -1.4465
2010-10-30 | 0.13517 | 217558.2333 | -2.0012
2010-10-31 | 0.14429 | 232233.6333 | -1.936
2010-11-01 | 0.24723 | 397927.7 | -1.3974
2010-11-02 | 0.20586 | 330717.9333 | -1.5806
2010-11-03 | 0.063255 | 101818.8333 | -2.7606
2010-11-04 | 0.027938 | 44970.3167 | -3.5778
2010-11-05 | 0.4728 | 761093.4 | -0.74908
2010-11-06 | 0.15125 | 243481.1 | -1.8888
2010-11-07 | 0.046228 | 74415.8833 | -3.0742
2010-11-08 | 0.66082 | 1063761.2333 | -0.41427
2010-11-09 | 0.041599 | 66901.2333 | -3.1797
2010-11-10 | 0.46685 | 751525.6667 | -0.76175
2010-11-11 | 0.19881 | 320049.1333 | -1.6154
2010-11-12 | 0.066619 | 107252.1 | -2.7088
2010-11-13 | 0.10371 | 166963.1 | -2.2662
2010-11-14 | 0.071763 | 115532.5667 | -2.6344
2010-11-15 | 0.16893 | 271968.3833 | -1.7783
2010-11-16 | 0.11594 | 186088.2667 | -2.1547
2010-11-17 | 0.25906 | 416560.35 | -1.3507
2010-11-18 | 0.10929 | 175760.3833 | -2.2137
2010-11-19 | 0.35274 | 566827.6 | -1.042
2010-11-20 | 0.0044741 | 7189.5167 | -5.4095
2010-11-21 | 0.078781 | 126594.8333 | -2.5411
2010-11-22 | 0.14885 | 239188.0833 | -1.9048
2010-11-23 | 0.58495 | 938914.55 | -0.53623
2010-11-24 | 0.26794 | 431129.7833 | -1.317
2010-11-25 | 0.16938 | 272536.8 | -1.7756
2010-11-26 | 0.18638 | 299925.45 | -1.68
2010-11-27 | 0.48949 | 787693.2333 | -0.71439
2010-11-28 | 0.16523 | 265882.6833 | -1.8004
2010-11-29 | 0.094042 | 151334.0167 | -2.364
2010-11-30 | 0.11238 | 177892.0667 | -2.1859
2010-12-01 | 0.24299 | 390987.35 | -1.4147
2010-12-02 | 0.37421 | 601772.0833 | -0.98295
2010-12-03 | 0.092282 | 147720.6333 | -2.3829
2010-12-04 | 0.33401 | 534659.9667 | -1.0966
2010-12-05 | 0.038495 | 61620.2833 | -3.2572
2010-12-06 | 0.23003 | 368218.05 | -1.4696
2010-12-07 | 0.0792 | 127215.2667 | -2.5358
2010-12-08 | 0.13192 | 212377.85 | -2.0256
2010-12-09 | 0.39016 | 628165.7833 | -0.9412
2010-12-10 | 0.063728 | 102600.2667 | -2.7531
2010-12-11 | 0.10691 | 172120.4833 | -2.2358
2010-12-12 | 0.17562 | 282735.9333 | -1.7395
2010-12-13 | 0.35215 | 566955.1333 | -1.0437
2010-12-14 | 0.57636 | 925808.1833 | -0.55102
2010-12-15 | 0.1561 | 251394.7833 | -1.8573
2010-12-16 | 1.0545 | 1697983.9833 | 0.053026
2010-12-17 | 0.30552 | 491993.75 | -1.1858
2010-12-18 | 0.077539 | 124866.4833 | -2.557
2010-12-19 | 0.23044 | 371096.5 | -1.4678
2010-12-20 | 1.5141 | 2438185.25 | 0.41479
2010-12-21 | 0.13704 | 220495.1833 | -1.9875
2010-12-22 | 0.40048 | 645457.4333 | -0.9151
2010-12-23 | 0.091732 | 147842.05 | -2.3889
2010-12-24 | 0.13438 | 216601.25 | -2.0071
2010-12-25 | 0.06683 | 107720.6833 | -2.7056
2010-12-26 | 0.30053 | 484416.95 | -1.2022
2010-12-27 | 0.14341 | 231152.8667 | -1.9421
2010-12-28 | 0.0048534 | 7762.0833 | -5.3281
2010-12-29 | 0.056456 | 90268.6167 | -2.8743
2010-12-30 | 0.19548 | 314995.5 | -1.6323
2010-12-31 | 0.079647 | 128491.8 | -2.5302
2011-01-01 | 0.25253 | 407393.3 | -1.3762
2011-01-02 | 0.47592 | 767787.4 | -0.74251
2011-01-03 | 2.0617 | 3326016.8 | 0.72351
2011-01-04 | 0.063414 | 102304.3333 | -2.7581
2011-01-05 | 0.076505 | 123408.05 | -2.5704
2011-01-06 | 0.21207 | 342126.6 | -1.5508
2011-01-07 | 0.0098123 | 15829.75 | -4.6241
2011-01-08 | 0.081357 | 131249.4833 | -2.5089
2011-01-09 | 0.11262 | 181676.2833 | -2.1838
2011-01-10 | 0.19644 | 316907.65 | -1.6274
2011-01-11 | 0.24253 | 390654.5 | -1.4166
2011-01-12 | 0.26988 | 435380.9333 | -1.3098
2011-01-13 | 0.098693 | 159220.1667 | -2.3157
2011-01-14 | 0.13867 | 223667.0167 | -1.9757
2011-01-15 | 0.10145 | 163642.7833 | -2.2882
2011-01-16 | 0.1413 | 227908.9333 | -1.9569
2011-01-17 | 0.23128 | 373060.4 | -1.4641
2011-01-18 | 0.081875 | 131967.1833 | -2.5026
2011-01-19 | 0.13596 | 219309.9167 | -1.9954
2011-01-20 | 0.099176 | 159993.4333 | -2.3109
2011-01-21 | 0.12678 | 204523.65 | -2.0653
2011-01-22 | 0.20806 | 335643.0667 | -1.5699
2011-01-23 | 0.058859 | 94951.8 | -2.8326
2011-01-24 | 0.36222 | 584336.3833 | -1.0155
2011-01-25 | 0.10167 | 164021.6833 | -2.286
2011-01-26 | 0.35813 | 577777.4333 | -1.0268
2011-01-27 | 0.23002 | 371094.7833 | -1.4696
2011-01-28 | 0.11612 | 187331.8833 | -2.1532
2011-01-29 | 0.044441 | 71697.35 | -3.1136
2011-01-30 | 0.039185 | 63216.3667 | -3.2395
2011-01-31 | 2.9741 | 4798080.8333 | 1.0899
2011-02-01 | 2.7917 | 4500610.15 | 1.0266
2011-02-02 | 3.9823 | 6419974.05 | 1.3818
2011-02-03 | 0.60804 | 980244.15 | -0.49752
2011-02-04 | 0.74796 | 1205816.8833 | -0.29041
2011-02-05 | 1.6732 | 2697363.6 | 0.51471
2011-02-06 | 1.3155 | 2120837.5333 | 0.27425
2011-02-07 | 0.037123 | 59847.2 | -3.2935
2011-02-08 | 0.13112 | 211379.4167 | -2.0317
2011-02-09 | 0.76186 | 1225919.5167 | -0.27199
2011-02-10 | 0.15412 | 248631.2 | -1.87
2011-02-11 | 0.6169 | 995209.0833 | -0.48304
2011-02-12 | 0.4578 | 738539.6 | -0.78132
2011-02-13 | 0.44009 | 709961.2833 | -0.82078
2011-02-14 | 0.14092 | 227336.2 | -1.9596
2011-02-15 | 0.16319 | 263561.5667 | -1.8128
2011-02-16 | 0.25407 | 410347.45 | -1.3702
2011-02-17 | 1.2655 | 2043975.7833 | 0.2355
2011-02-18 | 0.49464 | 798893.65 | -0.70393
2011-02-19 | 0.20481 | 330795.1833 | -1.5857
2011-02-20 | 0.9014 | 1455847 | -0.10381
2011-02-21 | 0.44487 | 718517.1833 | -0.80997
2011-02-22 | 0.15637 | 252616.7 | -1.8555
2011-02-23 | 0.083036 | 134146.5833 | -2.4885
2011-02-24 | 0.041485 | 67018.7667 | -3.1824
2011-02-25 | 0.28367 | 458271.2167 | -1.2599
2011-02-26 | 0.020463 | 33057.7333 | -3.8891
2011-02-27 | 0.035139 | 56766.4167 | -3.3485
2011-02-28 | 0.080908 | 130707.25 | -2.5144
2011-03-01 | 2.5634 | 4142040.2667 | 0.94135
2011-03-02 | 0.10952 | 176962.3667 | -2.2117
2011-03-03 | 0.0635 | 102603.8333 | -2.7567
2011-03-04 | 0.039974 | 64590.2333 | -3.2195
2011-03-05 | 0.017484 | 28250.4667 | -4.0465
2011-03-06 | 0.066398 | 107286.5333 | -2.7121
2011-03-07 | 0.33319 | 538374.75 | -1.099
2011-03-08 | 0.049401 | 79440.1167 | -3.0078
2011-03-09 | 0.043749 | 70671.5667 | -3.1293
2011-03-10 | 0.039469 | 63758.2333 | -3.2322
2011-03-11 | 0.1845 | 298044.5 | -1.6901
2011-03-12 | 0.35697 | 576643 | -1.0301
2011-03-13 | 0.07561 | 122139.8833 | -2.5822
2011-03-14 | 0.10266 | 165839.4167 | -2.2763
2011-03-15 | 0.1476 | 238516.15 | -1.9133
2011-03-16 | 0.12371 | 199924.3667 | -2.0898
2011-03-17 | 0.14209 | 229617.4333 | -1.9513
2011-03-18 | 0.087055 | 140681.9667 | -2.4412
2011-03-19 | 0.53596 | 866121.0667 | -0.62369
2011-03-20 | 0.69532 | 1123634.3667 | -0.36339
2011-03-21 | 0.47191 | 762603.3833 | -0.75097
2011-03-22 | 0.066668 | 107736.55 | -2.708
2011-03-23 | 0.040037 | 64714.0333 | -3.218
2011-03-24 | 0.26878 | 434440.7667 | -1.3139
2011-03-25 | 0.090279 | 145922.0667 | -2.4049
2011-03-26 | 0.027702 | 44776.2167 | -3.5862
2011-03-27 | 0.03193 | 51610.6667 | -3.4442
2011-03-28 | 0.10282 | 166198.5833 | -2.2747
2011-03-29 | 0.0099328 | 16054.8167 | -4.6119
2011-03-30 | 0.5878 | 950084.45 | -0.53137
2011-03-31 | 0.68271 | 1103487.6667 | -0.38169
2011-04-01 | 0.024216 | 39141.2333 | -3.7207
2011-04-02 | 0.074098 | 119767.4167 | -2.6024
2011-04-03 | 0.0052426 | 8473.7333 | -5.2509
2011-04-04 | 0.1075 | 173751.5 | -2.2303
2011-04-05 | 0.21605 | 349305.45 | -1.5322
2011-04-06 | 0.10817 | 174888.6167 | -2.224
2011-04-07 | 0.13908 | 224865.7333 | -1.9727
2011-04-08 | 0.11384 | 184055.0167 | -2.1729
2011-04-09 | 0.05564 | 89955.6667 | -2.8889
2011-04-10 | 0.66713 | 1078576.6333 | -0.40477
2011-04-11 | 0.19144 | 309504.0833 | -1.6532
2011-04-12 | 0.12536 | 202560.6167 | -2.0765
2011-04-13 | 0.03078 | 49733.8833 | -3.4809
2011-04-14 | 0.36209 | 585051.1 | -1.0159
2011-04-15 | 0.12548 | 202742.4167 | -2.0756
2011-04-16 | 0.28524 | 461311.6833 | -1.2544
2011-04-17 | 0.020001 | 32347.8333 | -3.912
2011-04-18 | 0.29266 | 473304.0167 | -1.2288
2011-04-19 | 0.10569 | 170977.0333 | -2.2472
2011-04-20 | 0.099116 | 160339.3 | -2.3115
2011-04-21 | 0.069026 | 111662.5667 | -2.6733
2011-04-22 | 0.062848 | 101665.9833 | -2.767
2011-04-23 | 0.17178 | 277887.3 | -1.7615
2011-04-24 | 0.014575 | 23579.8333 | -4.2284
2011-04-25 | 0.14412 | 233163.3167 | -1.9371
2011-04-26 | 0.28994 | 469076.5333 | -1.2381
2011-04-27 | 0.11763 | 190302.9833 | -2.1402
2011-04-28 | 0.21202 | 343007.9 | -1.5511
2011-04-29 | 0.99856 | 1615475.85 | -0.0014438
2011-04-30 | 0.2431 | 393297.3667 | -1.4143
2011-05-01 | 0.0028778 | 4655.7167 | -5.8507
2011-05-02 | 0.028026 | 45340.4333 | -3.5746
2011-05-03 | 0.030374 | 49129.4333 | -3.4942
2011-05-04 | 0.093937 | 151950.1833 | -2.3651
2011-05-05 | 0.082636 | 133670.2333 | -2.4933
2011-05-06 | 0.032617 | 52759.8667 | -3.4229
2011-05-07 | 0.010674 | 17266.7167 | -4.5399
2011-05-08 | 0.12764 | 206469.0833 | -2.0585
2011-05-09 | 0.069624 | 112621.8667 | -2.6646
2011-05-10 | 0.15006 | 242852.8167 | -1.8967
2011-05-11 | 0.18086 | 292684.3 | -1.7101
2011-05-12 | 0.21061 | 340836.6 | -1.5577
2011-05-13 | 0.20837 | 337210.75 | -1.5684
2011-05-14 | 0.16386 | 265179.1 | -1.8087
2011-05-15 | 0.36185 | 585591.4 | -1.0165
2011-05-16 | 0.11877 | 192204.2333 | -2.1306
2011-05-17 | 0.14142 | 228902.9333 | -1.956
2011-05-18 | 0.016249 | 26299.4167 | -4.1198
2011-05-19 | 0.10913 | 176630.3 | -2.2152
2011-05-20 | 0.18758 | 303613.9167 | -1.6735
2011-05-21 | 0.055558 | 89924.0667 | -2.8903
2011-05-22 | 0.03478 | 56294.0333 | -3.3587
2011-05-23 | 0.077369 | 125226.7667 | -2.5592
2011-05-24 | 0.16885 | 273333.9167 | -1.7788
2011-05-25 | 0.53058 | 858903.8833 | -0.63379
2011-05-26 | 0.092191 | 149238.95 | -2.3839
2011-05-27 | 0.066895 | 108289.7667 | -2.7046
2011-05-28 | 0.18598 | 301060.7333 | -1.6821
2011-05-29 | 0.074169 | 120064.4167 | -2.6014
2011-05-30 | 0.84969 | 1375485.7667 | -0.16288
2011-05-31 | 0.58628 | 949074.2833 | -0.53396
2011-06-01 | 0.080465 | 130256.8667 | -2.5199
2011-06-02 | 0.32148 | 520416.1167 | -1.1348
2011-06-03 | 0.15011 | 243001.9 | -1.8964
2011-06-04 | 0.034049 | 55118.2667 | -3.38
2011-06-05 | 0.31237 | 505663.85 | -1.1636
2011-06-06 | 0.15013 | 243036.3833 | -1.8962
2011-06-07 | 0.36381 | 589195.7 | -1.0111
2011-06-08 | 0.90711 | 1469045.1833 | -0.097487
2011-06-09 | 0.60353 | 977395.6 | -0.50496
2011-06-10 | 0.10535 | 170055.6667 | -2.2505
2011-06-11 | 0.25884 | 417828.5333 | -1.3515
2011-06-12 | 0.54423 | 878508.7 | -0.60838
2011-06-13 | 0.18565 | 299675.2833 | -1.6839
2011-06-14 | 0.88002 | 1425147.1167 | -0.12781
2011-06-15 | 0.61606 | 997685.6667 | -0.4844
2011-06-16 | 0.093832 | 151955.4 | -2.3663
2011-06-17 | 0.39645 | 642021.4667 | -0.92522
2011-06-18 | 0.97521 | 1579299.6333 | -0.025101
2011-06-19 | 0.085648 | 138702.7833 | -2.4575
2011-06-20 | 0.4653 | 753520.15 | -0.76508
2011-06-21 | 0.45943 | 744021.05 | -0.77776
2011-06-22 | 0.038666 | 62616.6833 | -3.2528
2011-06-23 | 0.10725 | 173686.4833 | -2.2326
2011-06-24 | 1.4513 | 2350268.1167 | 0.37246
2011-06-25 | 0.11464 | 185653.2333 | -2.1659
2011-06-26 | 0.17282 | 279860.6167 | -1.7555
2011-06-27 | 0.12476 | 202031.5 | -2.0814
2011-06-28 | 0.016512 | 26519.85 | -4.1037
2011-06-29 | 0.58771 | 951971.2167 | -0.53153
2011-06-30 | 0.13661 | 221279.2 | -1.9906
2011-07-01 | 0.19437 | 315024.0833 | -1.638
2011-07-02 | 0.16385 | 265570.1333 | -1.8088
2011-07-03 | 0.043252 | 70101.3167 | -3.1407
2011-07-04 | 0.15238 | 246976.7167 | -1.8814
2011-07-05 | 0.17478 | 283299.4 | -1.7442
2011-07-06 | 0.26668 | 432266.6667 | -1.3217
2011-07-07 | 0.18627 | 301924.75 | -1.6806
2011-07-08 | 0.18293 | 296001.3833 | -1.6986
2011-07-09 | 0.02291 | 37069.8667 | -3.7762
2011-07-10 | 0.30105 | 487117.1 | -1.2005
2011-07-11 | 0.067634 | 109437.1833 | -2.6936
2011-07-12 | 0.16592 | 268640 | -1.7962
2011-07-13 | 0.054206 | 87762.8333 | -2.915
2011-07-14 | 0.07192 | 116442.0333 | -2.6322
2011-07-15 | 0.17102 | 276886.6667 | -1.766
2011-07-16 | 0.10279 | 166426.45 | -2.275
2011-07-17 | 0.012348 | 19991.95 | -4.3943
2011-07-18 | 0.09833 | 159201.0833 | -2.3194
2011-07-19 | 0.53589 | 869354.5333 | -0.62382
2011-07-20 | 0.74641 | 1210859.2167 | -0.29248
2011-07-21 | 0.52729 | 855365.5167 | -0.64001
2011-07-22 | 0.93873 | 1522852.6333 | -0.063223
2011-07-23 | 0.31084 | 504258.2167 | -1.1685
2011-07-24 | 0.18333 | 297404.0333 | -1.6965
2011-07-25 | 0.3868 | 627483.9 | -0.94985
2011-07-26 | 0.039315 | 63828.9667 | -3.2362
2011-07-27 | 0.11374 | 184663.2333 | -2.1738
2011-07-28 | 0.13949 | 226462.7333 | -1.9698
2011-07-29 | 0.0367 | 59583.0333 | -3.305
2011-07-30 | 0.060138 | 97635.4833 | -2.8111
2011-07-31 | 0.16238 | 263628.7333 | -1.8178
2011-08-01 | 0.067486 | 109565.5 | -2.6958
2011-08-02 | 0.06684 | 108538.3833 | -2.7055
2011-08-03 | 0.11179 | 181534.2333 | -2.1911
2011-08-04 | 0.10344 | 167970.4333 | -2.2688
2011-08-05 | 0.13647 | 221608.65 | -1.9916
2011-08-06 | 0.071541 | 116170.0167 | -2.6375
2011-08-07 | 0.19928 | 323593.1833 | -1.6131
2011-08-08 | 0.23562 | 382604.5833 | -1.4455
2011-08-09 | 0.20014 | 325031.1333 | -1.6087
2011-08-10 | 0.07235 | 117495.5 | -2.6262
2011-08-11 | 0.10934 | 177566.8167 | -2.2133
2011-08-12 | 0.44366 | 720486.7667 | -0.8127
2011-08-13 | 0.087824 | 142622.55 | -2.4324
2011-08-14 | 0.053393 | 86708.5833 | -2.9301
2011-08-15 | 0.36256 | 588779.7 | -1.0146
2011-08-16 | 0.034907 | 56686.35 | -3.3551
2011-08-17 | 0.13821 | 224445.6167 | -1.979
2011-08-18 | 0.048427 | 78641.3667 | -3.0277
2011-08-19 | 0.77882 | 1264753.0333 | -0.24997
2011-08-20 | 0.25601 | 415736.2667 | -1.3626
2011-08-21 | 0.14752 | 238145.9 | -1.9138
2011-08-22 | 0.24509 | 395650.6333 | -1.4061
2011-08-23 | 0.23455 | 380771.5833 | -1.4501
2011-08-24 | 0.068222 | 110752.9833 | -2.685
2011-08-25 | 0.34572 | 561241.7833 | -1.0621
2011-08-26 | 0.097485 | 158257.3333 | -2.3281
2011-08-27 | 0.081985 | 133151.1 | -2.5012
2011-08-28 | 0.12448 | 202160.5833 | -2.0836
2011-08-29 | 0.073912 | 120039.1 | -2.6049
2011-08-30 | 0.088476 | 143558.8333 | -2.425
2011-08-31 | 0.15792 | 256249.8167 | -1.8456
2011-09-01 | 0.29864 | 484635.1 | -1.2085
2011-09-02 | 0.099919 | 162150.7333 | -2.3034
2011-09-03 | 0.18716 | 303734.5833 | -1.6758
2011-09-04 | 0.037723 | 61217.2833 | -3.2775
2011-09-05 | 0.083911 | 136173.0167 | -2.478
2011-09-06 | 0.044129 | 71617.7 | -3.1206
2011-09-07 | 0.21607 | 350670.95 | -1.5321
2011-09-08 | 0.077302 | 125457.4333 | -2.56
2011-09-09 | 0.032172 | 52214.3333 | -3.4367
2011-09-10 | 0.19127 | 310421.4833 | -1.6541
2011-09-11 | 0.20936 | 339793.6833 | -1.5637
2011-09-12 | 0.10504 | 170476.6 | -2.2534
2011-09-13 | 0.35927 | 583071.6 | -1.0237
2011-09-14 | 0.16068 | 260794.4 | -1.8283
2011-09-15 | 0.090056 | 146168 | -2.4073
2011-09-16 | 0.046138 | 74886.7333 | -3.0761
2011-09-17 | 0.175 | 284037.95 | -1.743
2011-09-18 | 0.024872 | 40370.0167 | -3.694
2011-09-19 | 0.01273 | 20662.5 | -4.3638
2011-09-20 | 0.70507 | 1144451.7 | -0.34946
2011-09-21 | 0.17803 | 288992.1 | -1.7258
2011-09-22 | 0.027203 | 44157.1833 | -3.6044
2011-09-23 | 0.17417 | 282735.15 | -1.7477
2011-09-24 | 0.72488 | 1176700.05 | -0.32174
2011-09-25 | 1.0763 | 1747127.75 | 0.073515
2011-09-26 | 0.033184 | 53867.2333 | -3.4057
2011-09-27 | 0.0040733 | 6556.7333 | -5.5033
2011-09-28 | 0.010759 | 17422.05 | -4.532
2011-09-29 | 0.38184 | 617784.6667 | -0.96275
2011-09-30 | 0.092797 | 150270.05 | -2.3773
2011-10-01 | 0.23165 | 375198.7333 | -1.4625
2011-10-02 | 0.076402 | 123746.3167 | -2.5718
2011-10-03 | 0.96244 | 1558841.9333 | -0.038287
2011-10-04 | 0.41884 | 677995.2333 | -0.87027
2011-10-05 | 0.085746 | 139420.7333 | -2.4564
2011-10-06 | 0.04971 | 80826.35 | -3.0016
2011-10-07 | 0.64307 | 1045590.6333 | -0.4415
2011-10-08 | 0.63177 | 1027209.5333 | -0.45924
2011-10-09 | 0.031384 | 51027.7333 | -3.4615
2011-10-10 | 0.45178 | 734556.5333 | -0.79457
2011-10-11 | 0.090005 | 146337.4333 | -2.4079
2011-10-12 | 0.017289 | 28110.4333 | -4.0577
2011-10-13 | 0.12103 | 196776.1667 | -2.1117
2011-10-14 | 0.10675 | 173553.8833 | -2.2373
2011-10-15 | 0.085048 | 138275.9 | -2.4645
2011-10-16 | 0.18418 | 299458.4667 | -1.6918
2011-10-17 | 0.25819 | 419784.4333 | -1.3541
2011-10-18 | 0.16137 | 262408.1833 | -1.8241
2011-10-19 | 0.24911 | 405091.1333 | -1.3899
2011-10-20 | 0.25943 | 421869.8333 | -1.3493
2011-10-21 | 0.65354 | 1062760.8667 | -0.42535
2011-10-22 | 0.098681 | 160471.4833 | -2.3159
2011-10-23 | 0.0098465 | 16012.0167 | -4.6206
2011-10-24 | 0.11739 | 190896.7 | -2.1422
2011-10-25 | 0.16451 | 267514.1667 | -1.8048
2011-10-26 | 0.072419 | 117764.0333 | -2.6253
2011-10-27 | 0.0092388 | 15023.7167 | -4.6843
2011-10-28 | 0.028881 | 46964.7333 | -3.5446
2011-10-29 | 0.015349 | 24958.95 | -4.1767
2011-10-30 | 0.38859 | 631902.55 | -0.94523
2011-10-31 | 0.04611 | 74981.9167 | -3.0767
2011-11-01 | 0.22687 | 368980.9333 | -1.4834
2011-11-02 | 0.037179 | 60469.8833 | -3.292
2011-11-03 | 0.17151 | 278940.7333 | -1.7631
2011-11-04 | 0.0012768 | 2076.55 | -6.6634
2011-11-05 | 0.049965 | 81264.5333 | -2.9964
2011-11-06 | 0.037581 | 61123.1833 | -3.2812
2011-11-07 | 0.36817 | 598799.5667 | -0.99921
2011-11-08 | 2.6909 | 4378003.6333 | 0.98989
2011-11-09 | 1.3067 | 2125899.6833 | 0.26749
2011-11-10 | 0.3274 | 532667.0833 | -1.1166
2011-11-11 | 0.0085825 | 13963.1 | -4.758
2011-11-12 | 0.087206 | 141878.5667 | -2.4395
2011-11-13 | 0.17803 | 289836.5 | -1.7258
2011-11-14 | 0.3772 | 614084.1667 | -0.97497
2011-11-15 | 0.20619 | 335666.4833 | -1.579
2011-11-16 | 0.39485 | 642797.65 | -0.92926
2011-11-17 | 1.7115 | 2786320.8167 | 0.53738
2011-11-18 | 0.27443 | 446767.0833 | -1.2931
2011-11-19 | 0.16686 | 271640.5 | -1.7906
2011-11-20 | 0.24019 | 391020.2333 | -1.4263
2011-11-21 | 0.062784 | 102210.1167 | -2.7681
2011-11-22 | 0.22232 | 360426.3 | -1.5036
2011-11-23 | 0.18839 | 305419.35 | -1.6692
2011-11-24 | 0.222 | 359905.8 | -1.5051
2011-11-25 | 0.23932 | 387984.45 | -1.4299
2011-11-26 | 0.11587 | 188697.2 | -2.1553
2011-11-27 | 0.32113 | 522972.6167 | -1.1359
2011-11-28 | 0.46494 | 757158.8333 | -0.76585
2011-11-29 | 0.080453 | 130951.4167 | -2.5201
2011-11-30 | 0.14178 | 230777.1833 | -1.9535
2011-12-01 | 0.20389 | 331864.3167 | -1.5902
2011-12-02 | 0.087125 | 141809.8333 | -2.4404
2011-12-03 | 0.15207 | 247517.35 | -1.8834
2011-12-04 | 0.057136 | 92998.1833 | -2.8623
2011-12-05 | 0.099934 | 162658.7667 | -2.3032
2011-12-06 | 0.12382 | 201579.3167 | -2.0889
2011-12-07 | 4.6007 | 7489942.9833 | 1.5262
2011-12-08 | 0.075798 | 123398.9667 | -2.5797
2011-12-09 | 0.015714 | 25583.0833 | -4.1532
2011-12-10 | 0.10556 | 171852.1667 | -2.2485
2011-12-11 | 0.16576 | 269851.45 | -1.7972
2011-12-12 | 0.055848 | 90980.3167 | -2.8851
2011-12-13 | 0.1056 | 172042.65 | -2.2481
2011-12-14 | 0.098812 | 160975.2167 | -2.3145
2011-12-15 | 0.0072747 | 11851.3167 | -4.9233
2011-12-16 | 0.052016 | 84738.7333 | -2.9562
2011-12-17 | 0.47515 | 774070.9833 | -0.74412
2011-12-18 | 0.023463 | 38223.3167 | -3.7523
2011-12-19 | 0.26607 | 433451.2667 | -1.324
2011-12-20 | 0.05893 | 95742.65 | -2.8314
2011-12-21 | 0.26145 | 424770.8833 | -1.3415
2011-12-22 | 0.39063 | 634648.4667 | -0.93999
2011-12-23 | 0.098393 | 159857.1833 | -2.3188
2011-12-24 | 0.17126 | 278247.95 | -1.7645
2011-12-25 | 0.14335 | 232900.55 | -1.9425
2011-12-26 | 0.1389 | 225976.9667 | -1.974
2011-12-27 | 0.35074 | 570114.0667 | -1.0477
2011-12-28 | 0.054893 | 89227.05 | -2.9024
2011-12-29 | 0.058391 | 94912.75 | -2.8406
2011-12-30 | 0.073231 | 119221.2833 | -2.6141
2011-12-31 | 0.098912 | 161030.7833 | -2.3135
2012-01-01 | 0.13907 | 226407.1833 | -1.9728
2012-01-02 | 0.052999 | 86283.8667 | -2.9375
2012-01-03 | 0.21973 | 358128.3667 | -1.5154
2012-01-04 | 0.95907 | 1563181.45 | -0.041789
2012-01-05 | 0.9993 | 1628751.9833 | -0.00069785
2012-01-06 | 0.23497 | 382976.1667 | -1.4483
2012-01-07 | 0.18118 | 295299.5167 | -1.7083
2012-01-08 | 0.55327 | 901819.1333 | -0.5919
2012-01-09 | 0.1471 | 239768.0667 | -1.9166
2012-01-10 | 0.091663 | 149415.8333 | -2.3896
2012-01-11 | 0.55869 | 910693.4833 | -0.58216
2012-01-12 | 0.19918 | 324673.6167 | -1.6135
2012-01-13 | 0.29388 | 479036.0333 | -1.2246
2012-01-14 | 0.41988 | 684417.5833 | -0.86779
2012-01-15 | 0.28601 | 466208.4333 | -1.2517
2012-01-16 | 0.072717 | 118532.0333 | -2.6212
2012-01-17 | 0.21588 | 351970.65 | -1.533
2012-01-18 | 0.11626 | 189559.0167 | -2.1519
2012-01-19 | 0.1638 | 267057.9167 | -1.8091
2012-01-20 | 0.15362 | 250451.5167 | -1.8732
2012-01-21 | 0.096701 | 157650.9 | -2.3361
2012-01-22 | 0.14605 | 238098.6167 | -1.9238
2012-01-23 | 0.12309 | 200676.35 | -2.0948
2012-01-24 | 0.11897 | 193975.7167 | -2.1289
2012-01-25 | 0.62661 | 1021633.5833 | -0.46743
2012-01-26 | 0.011492 | 18736.8833 | -4.4661
2012-01-27 | 0.35834 | 584241.6667 | -1.0263
2012-01-28 | 0.24611 | 401257.6833 | -1.402
2012-01-29 | 0.19207 | 313153.3833 | -1.6499
2012-01-30 | 0.45033 | 734212.7167 | -0.79778
2012-01-31 | 0.0084174 | 13727.5667 | -4.7775
2012-02-01 | 0.054707 | 89218.2833 | -2.9058
2012-02-02 | 0.033566 | 54739.8667 | -3.3942
2012-02-03 | 0.1563 | 254892.55 | -1.856
2012-02-04 | 0.096111 | 156740.4333 | -2.3422
2012-02-05 | 0.064664 | 105455.4833 | -2.7386
2012-02-06 | 0.35253 | 574919.8833 | -1.0426
2012-02-07 | 0.033621 | 54834.75 | -3.3926
2012-02-08 | 0.066532 | 108512.1833 | -2.7101
2012-02-09 | 1.6134 | 2631351.25 | 0.47832
2012-02-10 | 0.25268 | 412102.2333 | -1.3756
2012-02-11 | 1.0473 | 1708034.7667 | 0.04618
2012-02-12 | 0.23244 | 379101.9667 | -1.4591
2012-02-13 | 0.25217 | 411273.45 | -1.3777
2012-02-14 | 0.13234 | 215872.1 | -2.0224
2012-02-15 | 0.19753 | 322199.2667 | -1.6219
2012-02-16 | 0.068157 | 111174.7333 | -2.6859
2012-02-17 | 0.23363 | 381085.95 | -1.454
2012-02-18 | 0.018446 | 30088.1167 | -3.9929
2012-02-19 | 1.9373 | 3159961.5 | 0.66127
2012-02-20 | 0.74343 | 1212643.15 | -0.29648
2012-02-21 | 0.61525 | 1003436.35 | -0.48573
2012-02-22 | 0.13661 | 222816.2333 | -1.9907
2012-02-23 | 0.049874 | 81348.1833 | -2.9983
2012-02-24 | 0.044166 | 72039.0833 | -3.1198
2012-02-25 | 0.029862 | 48706.9833 | -3.5112
2012-02-26 | 0.15106 | 246388.9333 | -1.8901
2012-02-27 | 0.1504 | 245318.7667 | -1.8945
2012-02-28 | 0.42974 | 701030.6167 | -0.84458
2012-02-29 | 0.30566 | 498621.7833 | -1.1853
2012-03-01 | 0.3296 | 537676.2667 | -1.1099
2012-03-02 | 0.29587 | 482653.1333 | -1.2178
2012-03-03 | 0.029433 | 48014.0167 | -3.5256
2012-03-04 | 0.20254 | 330404.7167 | -1.5968
2012-03-05 | 0.10937 | 178410 | -2.213
2012-03-06 | 0.049974 | 81543.9333 | -2.9962
2012-03-07 | 0.18578 | 303143.2667 | -1.6832
2012-03-08 | 0.73813 | 1204401.4333 | -0.30363
2012-03-09 | 0.31051 | 506661.2667 | -1.1695
2012-03-10 | 0.081044 | 132238.2833 | -2.5128
2012-03-11 | 0.03868 | 63114.5333 | -3.2524
2012-03-12 | 0.1515 | 247196.2 | -1.8872
2012-03-13 | 0.12118 | 197749.6 | -2.1105
2012-03-14 | 0.29791 | 486147.0833 | -1.211
2012-03-15 | 0.10032 | 163704.1 | -2.2994
2012-03-16 | 0.40453 | 660137.85 | -0.90502
2012-03-17 | 0.19473 | 317768.7 | -1.6361
2012-03-18 | 0.0772 | 125979.65 | -2.5614
2012-03-19 | 0.14117 | 230400.1167 | -1.9578
2012-03-20 | 0.13393 | 218539.3833 | -2.0104
2012-03-21 | 0.12611 | 205770.2 | -2.0706
2012-03-22 | 0.23972 | 391148.5 | -1.4283
2012-03-23 | 0.052693 | 85978.5 | -2.9433
2012-03-24 | 0.015405 | 25135.6833 | -4.1731
2012-03-25 | 0.0075457 | 12312.2333 | -4.8868
2012-03-26 | 0.35058 | 572034.3167 | -1.0482
2012-03-27 | 0.15232 | 248562.3833 | -1.8817
2012-03-28 | 0.43419 | 708514.7833 | -0.83427
2012-03-29 | 0.072829 | 118841.7833 | -2.6196
2012-03-30 | 0.04531 | 73930.6 | -3.0942
2012-03-31 | 0.052304 | 85342.5667 | -2.9507
2012-04-01 | 0.086794 | 141618.3667 | -2.4442
2012-04-02 | 0.070525 | 115073.3833 | -2.6518
2012-04-03 | 0.11756 | 191931.8167 | -2.1408
2012-04-04 | 0.035255 | 57558.9667 | -3.3451
2012-04-05 | 0.16087 | 262639.1167 | -1.8272
2012-04-06 | 0.01566 | 25566.9167 | -4.1566
2012-04-07 | 0.29342 | 479038.0167 | -1.2262
2012-04-08 | 1.9517 | 3186336.4333 | 0.66869
2012-04-09 | 0.044671 | 72930.65 | -3.1084
2012-04-10 | 0.10933 | 178554.45 | -2.2134
2012-04-11 | 0.17905 | 292420.5667 | -1.7201
2012-04-12 | 0.34132 | 557429.1 | -1.0749
2012-04-13 | 0.072326 | 118119.65 | -2.6266
2012-04-14 | 0.066248 | 108193.5167 | -2.7143
2012-04-15 | 0.0036959 | 6036.0333 | -5.6005
2012-04-16 | 0.032136 | 52482.8333 | -3.4378
2012-04-17 | 0.132 | 215607.9667 | -2.0249
2012-04-18 | 0.53963 | 881394.3333 | -0.61688
2012-04-19 | 0.14942 | 244048.2667 | -1.901
2012-04-20 | 0.14109 | 230452.8333 | -1.9583
2012-04-21 | 0.32486 | 530608.2 | -1.1244
2012-04-22 | 0.064658 | 105607.9 | -2.7386
2012-04-23 | 0.025476 | 41610.9167 | -3.67
2012-04-24 | 0.13703 | 223911.75 | -1.9876
2012-04-25 | 0.32701 | 534343.4167 | -1.1178
2012-04-26 | 0.02179 | 35606.45 | -3.8263
2012-04-27 | 0.05155 | 84234.65 | -2.9652
2012-04-28 | 0.11658 | 190498.3833 | -2.1492
2012-04-29 | 0.036122 | 59024.35 | -3.3209
2012-04-30 | 0.35984 | 587986.5833 | -1.0221
2012-05-01 | 0.1526 | 249392.3833 | -1.8799
2012-05-02 | 0.63881 | 1044013.7833 | -0.44814
2012-05-03 | 0.2649 | 432925.75 | -1.3284
2012-05-04 | 0.011708 | 19133.9 | -4.4475
2012-05-05 | 0.13628 | 222713.8833 | -1.9931
2012-05-06 | 0.038018 | 62132.4667 | -3.2697
2012-05-07 | 0.09627 | 157332.9833 | -2.3406
2012-05-08 | 0.018457 | 30174.4667 | -3.9923
2012-05-09 | 0.23574 | 385399.3833 | -1.445
2012-05-10 | 0.10585 | 173055.05 | -2.2457
2012-05-11 | 0.015364 | 25117.6 | -4.1757
2012-05-12 | 0.10435 | 170592.7667 | -2.26
2012-05-13 | 0.13295 | 217357.7167 | -2.0178
2012-05-14 | 0.050119 | 81936.2 | -2.9934
2012-05-15 | 0.035588 | 58194.6667 | -3.3358
2012-05-16 | 0.046523 | 76075.9833 | -3.0678
2012-05-17 | 0.45885 | 750332.7667 | -0.77903
2012-05-18 | 0.23041 | 376770.6667 | -1.4679
2012-05-19 | 0.14938 | 244270.2833 | -1.9013
2012-05-20 | 0.054164 | 88571 | -2.9157
2012-05-21 | 0.010908 | 17836.6667 | -4.5183
2012-05-22 | 0.053813 | 87997.8833 | -2.9222
2012-05-23 | 0.025904 | 42358.45 | -3.6534
2012-05-24 | 0.2709 | 442988.4667 | -1.306
2012-05-25 | 0.65967 | 1078649.5833 | -0.41601
2012-05-26 | 0.24291 | 397195.15 | -1.415
2012-05-27 | 0.025863 | 42289 | -3.6549
2012-05-28 | 0.098424 | 160936.5333 | -2.3185
2012-05-29 | 0.14413 | 235709.35 | -1.9371
2012-05-30 | 0.044364 | 72554.2333 | -3.1153
2012-05-31 | 0.08196 | 134038.9 | -2.5015
2012-06-01 | 0.0088081 | 14404.8833 | -4.7321
2012-06-02 | 0.057668 | 94311.55 | -2.853
2012-06-03 | 0.095953 | 156921.9667 | -2.3439
2012-06-04 | 0.58402 | 955106.1667 | -0.53783
2012-06-05 | 2.9183 | 4773818.95 | 1.071
2012-06-06 | 0.68088 | 1113897.4667 | -0.38437
2012-06-07 | 0.094092 | 153932.1167 | -2.3635
2012-06-08 | 0.18883 | 308921.15 | -1.6669
2012-06-09 | 0.16821 | 275181.8167 | -1.7826
2012-06-10 | 0.2039 | 333580.25 | -1.5901
2012-06-11 | 0.33261 | 544140.1667 | -1.1008
2012-06-12 | 0.34827 | 569833.5667 | -1.0548
2012-06-13 | 0.074202 | 121408.8167 | -2.601
2012-06-14 | 0.022292 | 36474.4333 | -3.8035
2012-06-15 | 0.088956 | 145549.7 | -2.4196
2012-06-16 | 0.079532 | 130129.1167 | -2.5316
2012-06-17 | 0.089648 | 146681.4833 | -2.4119
2012-06-18 | 0.14689 | 240344.0667 | -1.9181
2012-06-19 | 0.080059 | 131043.7833 | -2.525
2012-06-20 | 0.070008 | 114590.8833 | -2.6592
2012-06-21 | 0.10259 | 167920.6333 | -2.277
2012-06-22 | 0.20267 | 331725.6833 | -1.5962
2012-06-23 | 0.17838 | 291970.4167 | -1.7239
2012-06-24 | 0.081939 | 134119.35 | -2.5018
2012-06-25 | 0.079631 | 130340.4333 | -2.5304
2012-06-26 | 0.27401 | 448527.4667 | -1.2946
2012-06-27 | 0.33649 | 550804.45 | -1.0892
2012-06-28 | 0.57578 | 942482.8667 | -0.55204
2012-06-29 | 0.20384 | 333664.45 | -1.5904
2012-06-30 | 0.064767 | 106016.2333 | -2.737
Contents

## 1e. STPIS Exclusions
Ausgrid
STPIS Data Reporting
2012-13
Exclusions
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Exclusions
Date of event (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Cause of event | Number of customers interrupted | Duration of interruption (mins) | Total unplanned customer minutes off supply | Event category (Use Exclusion categories listed in section 3.3 (a) of the AER's STPIS) | Unplanned SAIDI impact | Unplanned SAIFI impact | Further information (Please provide separate explanation to confirm the outage was not due to inadequate transmission connection planning)
2012-07-23 | 851263 | 806:74076 | SHORT RURAL | Transmission failure | 40 | 162 | 6480 | 6 | 0.0039591 | 0.0024439
2012-07-23 | 851263 | 806:74080 | SHORT RURAL | Transmission failure | 231 | 162 | 37422 | 6 | 0.022864 | 0.014113
2012-07-23 | 851263 | 811:74234 | SHORT RURAL | Transmission failure | 245 | 162 | 39690 | 6 | 0.024249 | 0.014969
2012-08-10 | 859180 | ZN195:PA30 | URBAN | Load Shedding | 1 | 206.8667 | 206.8667 | 7 | 0.00012639 | 6.1099e-05
2012-08-10 | 859646 | ZN15009:PA1 | URBAN | Transmission failure | 2013 | 11 | 16104 | 6 | 0.0098393 | 0.12299
2012-08-10 | 859646 | ZN15009:PA11 | URBAN | Transmission failure | 2186 | 11 | 17488 | 6 | 0.010685 | 0.13356
2012-08-10 | 859646 | ZN15009:PA12 | URBAN | Transmission failure | 54 | 11 | 432 | 6 | 0.00026395 | 0.0032993
2012-08-10 | 859646 | ZN15009:PA3 | URBAN | Transmission failure | 849 | 11 | 6792 | 6 | 0.0041498 | 0.051873
2012-08-10 | 859646 | ZN15009:PA5 | URBAN | Transmission failure | 1849 | 11 | 14792 | 6 | 0.0090377 | 0.11297
2012-08-10 | 859646 | ZN15009:PA7 | URBAN | Transmission failure | 1578 | 11 | 12624 | 6 | 0.0077131 | 0.096414
2012-08-10 | 859646 | ZN15009:PA9 | URBAN | Transmission failure | 592 | 11 | 4736 | 6 | 0.0028936 | 0.03617
2012-08-10 | 859646 | ZN15015:PA15 | URBAN | Transmission failure | 444 | 11 | 4884 | 6 | 0.0029841 | 0.027128
2012-08-10 | 859646 | ZN15015:PA5 | URBAN | Transmission failure | 1642 | 11 | 18062 | 6 | 0.011036 | 0.10032
2012-08-24 | 868484 | ZN340:PA19 | SHORT RURAL | Load Shedding | 2 | 124 | 248 | 7 | 0.00015152 | 0.0001222
2012-12-07 | 909162 | ZN35500:PA19 | SHORT RURAL | Load Shedding | 1 | 3498.2833 | 3498.2833 | 7 | 0.0021283 | 6.0838e-05
2013-01-02 | 918141 | 507:80923 | SHORT RURAL | Load Shedding | 3 | 27 | 81 | 7 | 4.9225e-05 | 0.00018231
2013-01-14 | 922033 | 813:89062 | SHORT RURAL | Load Shedding | 19 | 119 | 2261 | 7 | 0.0013741 | 0.0011547
Weather
Equipment failure
Operational error
Vegetation
Animals
Third party impacts
Transmission failure
Load shedding
Inter-distributor connection failure
Other
Contents

## 1f. STPIS GSL
Ausgrid
STPIS Data Reporting - AER Definitions |  | Yes
2012-13 |  | No
Guaranteed Service Level
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Did the AER's GSL Scheme apply at any time during the regulatory year? | No
If the AER's GSL scheme applied at any time during the regulatory year, table 1 must be completed. Do not complete table 1 if the AER's GSL scheme did not apply during the regulatory year.
Table 1: Guaranteed service levels - AER GSL scheme
Reliability of supply
Frequency of interruptions CBD feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Urban feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Rural (short and long) feeders – 15 interruptions
Low reliability payments - 15 interruptions - ($)
Duration of interruptions CBD feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions urban feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions Rural (short and long) feeders – 18 hours
Low reliability payments - 18 hours - ($)
Total duration of interruptions Level 1 – 20 hours
Low reliability payments - 20 hours - ($)
Total duration of interruptions Level 2 – 30 hours
Low reliability payments - 30 hours - ($)
Total duration of interruptions Level 3 – 60 hours
Low reliability payments - 60 hours - ($)
Street lights
Streetlight repair 5 days - GSL payments - number
Street lights - GSL payments - ($)
New connections
Connections made
Connection not made on or before the day agreed - number
Connection not made on or before the day agreed - ($)
Connections - GSL payments - 1-6 day delay - number
Connections - GSL payments - 1-6 day delay - ($)
Connections - GSL payments - 7+ day delay - number
Connections - GSL payments - 7+ day delay - ($)
Planned interruptions
Notice of planned interruptions - 4 days not given - number
Notice of planned interruptions - 4 days not given - ($)
Total GSL payments payable under the AER's GSL scheme ($) | 0
Contents

## 2. Demand
Ausgrid
Demand
2012-13
The information is required to assess forecasts against outturn demand, and will inform the AER’s review of demand forecasts in future regulatory proposals. The information may be used in performance reports.
Note: a) Forecasts should be the demand forecasts for the relevant regulatory year that were made at the time of the regulatory proposal
b) t+1 forecasts should be the latest updates to the demand forecasts for the regulatory year t+1
c) The PoE level only applies to the forecasts.
Table 1: Maximum coincident demand at the network level
Network coincident maximum demand | Forecast | Actual - raw | Actual - weather normalised | Variation % | t+1 forecast
90% PoE level
Network coincident maximum demand (MW) |  | 5659 | 5028.5617 | #DIV/0! | 5211.3972
Network coincident maximum demand (MVA) |  |  |  | #DIV/0!
50% PoE level
Network coincident maximum demand (MW) | 6467 | 5659 | 5391.2428 | -12.49% | 5542.5646
Network coincident maximum demand (MVA) | N/A | N/A | 5823.848 | #VALUE! | 5990.7946
10% PoE level
Network coincident maximum demand (MW) |  | 5659 | 5762.4452 | #DIV/0! | 5986.4739
Network coincident maximum demand (MVA) |  |  |  | #DIV/0!
Table 2: Summer and winter non-coincident maximum demand by zone substation
Summer and winter maximum demand - ZS | [12 empty] | t+1 forecast |  |  |  | Nameplate rating (MVA)
POE level = 50% | Forecast |  |  |  | Actual - raw |  |  |  | Actual - weather normalised
Location | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF
Aberdeen 33_11kV - summer peak demand | 7.6492 | 7.9679 | 2.231 | 0.96 | 2.808 | 2.845 | 0.4572 | 0.98699 | 2.8922 | 2.9303 | 0.471 | 0.987 | 0 | 0 | 0 | #DIV/0! | 8
Aberdeen 33_11kV - winter peak demand | 6.9886 | 7.2798 | 2.0383 | 0.96 | 2.2893 | 2.438 | 0.8385 | 0.93901 | 2.2246 | 2.3691 | 0.8148 | 0.93901 | 2.5335 | 2.6396 | 0.7408 | 0.9598 | 8.48
Aberdeen 66_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0.927 | 1.03 | 0.449 | 0.9 | 1.0062 | 1.118 | 0.4873 | 0.9 | 3.4566 | 3.7312 | 1.405 | 0.9264 | 19
Aberdeen 66_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0.6453 | 0.7621 | 0.4055 | 0.84674 | 0
Adamstown 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 30.9744 | 32.401 | 9.5084 | 0.95597 | 28.3962 | 29.704 | 8.7169 | 0.95597 | 24.9125 | 24.9207 | 0.64 | 0.99967 | 63.03
Adamstown 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 23.708 | 24.368 | 5.633 | 0.97292 | 24.5951 | 25.2798 | 5.8437 | 0.97292 | 22.0771 | 22.2066 | 2.3945 | 0.99417 | 65.01
Adamstown 33_11kV - summer peak demand | 32.3625 | 33.3634 | 8.1108 | 0.97 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Adamstown 33_11kV - winter peak demand | 20.7601 | 21.4022 | 5.203 | 0.97 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Alexandria 33_5kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Alexandria 33_5kV - winter peak demand | 0.0033048 | 0.0034641 | 0.0010386 | 0.954 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Argenton 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 33.5813 | 35.836 | 12.5107 | 0.93708 | 33.5231 | 35.7739 | 12.489 | 0.93708 | 35.9616 | 38.3388 | 13.2902 | 0.93799 | 60.8
Argenton 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 26.591 | 27.706 | 7.7808 | 0.95976 | 27.1441 | 28.2823 | 7.9427 | 0.95976 | 29.487 | 30.6993 | 8.5421 | 0.96051 | 64.19
Arncliffe 33_11kV - summer peak demand | 33.5796 | 35.3469 | 11.0371 | 0.95 | 19.5532 | 21.4913 | 8.919 | 0.90982 | 19.8845 | 21.8554 | 9.0702 | 0.90982 | 19.2264 | 21.1321 | 8.77 | 0.90982 | 39.06
Arncliffe 33_11kV - winter peak demand | 43.9098 | 44.1305 | 4.4075 | 0.995 | 17.6309 | 18.862 | 6.7029 | 0.93473 | 18.4932 | 19.7846 | 7.0307 | 0.93473 | 18.9486 | 20.2717 | 7.2038 | 0.93473 | 42.9
Auburn 33_11kV - summer peak demand | 31.3941 | 31.3941 | 0 | 1 | 25.0975 | 27.8358 | 12.0393 | 0.90163 | 25.179 | 27.9262 | 12.0784 | 0.90163 | 26.9333 | 29.8718 | 12.9199 | 0.90163 | 41.01
Auburn 33_11kV - winter peak demand | 14.1711 | 14.9326 | 4.7079 | 0.949 | 23.5809 | 25.5114 | 9.735 | 0.92433 | 24.1264 | 26.1015 | 9.9602 | 0.92433 | 24.4368 | 26.4373 | 10.0884 | 0.92433 | 41.01
Avoca 66_11kV - summer peak demand | 38.0176 | 42.2418 | 18.4128 | 0.9 | 40.0144 | 41.8718 | 12.3328 | 0.95564 | 30.5056 | 31.9217 | 9.4021 | 0.95564 | 32.2059 | 33.7009 | 9.9261 | 0.95564 | 55.65
Avoca 66_11kV - winter peak demand | 56.0048 | 56.8577 | 9.811 | 0.985 | 43.7435 | 43.8971 | 3.669 | 0.9965 | 46.0207 | 46.1823 | 3.86 | 0.9965 | 39.5198 | 39.6889 | 3.6602 | 0.99574 | 57.01
Avondale 33_11kV - summer peak demand | 18.5837 | 20.6486 | 9.0005 | 0.9 | 14.3337 | 15.104 | 4.7619 | 0.949 | 12.3714 | 13.0362 | 4.11 | 0.949 | 9.2143 | 9.7095 | 3.0612 | 0.949 | 22.86
Avondale 33_11kV - winter peak demand | 20.1525 | 22.3916 | 9.7603 | 0.9 | 11.5122 | 11.856 | 2.8345 | 0.971 | 11.8174 | 12.1703 | 2.9097 | 0.971 | 8.391 | 8.6416 | 2.066 | 0.971 | 22.86
Baerami 33_11kV - summer peak demand | 1.0966 | 1.2184 | 0.5311 | 0.9 | 0.9678 | 1.022 | 0.3283 | 0.94697 | 1.0011 | 1.0571 | 0.3396 | 0.94702 | 0.9944 | 1.0001 | 0.1073 | 0.9943 | 0
Baerami 33_11kV - winter peak demand | 1.1028 | 1.2254 | 0.53413 | 0.9 | 0.6628 | 0.684 | 0.169 | 0.96901 | 0.6589 | 0.68 | 0.168 | 0.96897 | 0.6299 | 0.6328 | 0.0606 | 0.99542 | 0
Balgowlah 33_11kV - summer peak demand | 33.9282 | 34.2709 | 4.8345 | 0.99 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Balgowlah 33_11kV - winter peak demand | 47.9746 | 48.4592 | 6.836 | 0.99 | 0 | 0 | 0 | #DIV/0! | 0 | 0.2725 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
Balgowlah North 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 26.7344 | 29.7048 | 12.948 | 0.9 | 25.0381 | 27.8201 | 12.1265 | 0.9 | 25.2103 | 28.0115 | 12.2099 | 0.9 | 37.9
Balgowlah North 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 31.5458 | 32.0597 | 5.7174 | 0.98397 | 34.0778 | 34.633 | 6.1763 | 0.98397 | 33.6392 | 34.1873 | 6.0968 | 0.98397 | 37.9
Bankstown 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 17.5967 | 22.844 | 14.5672 | 0.7703 | 18.248 | 23.6895 | 15.1064 | 0.7703 | 33.4697 | 40.401 | 22.6279 | 0.82844 | 65.01
Bankstown 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 17.6536 | 22.2153 | 13.4859 | 0.79466 | 18.0384 | 22.6995 | 13.7799 | 0.79466 | 34.671 | 39.3767 | 18.6668 | 0.8805 | 65.01
Bass Hill 33_11kV - summer peak demand | 30.0662 | 30.3699 | 4.2842 | 0.99 | 22.4734 | 25.4923 | 12.0335 | 0.88158 | 21.1619 | 24.0046 | 11.3312 | 0.88158 | 24.7342 | 28.0568 | 13.244 | 0.88158 | 29.19
Bass Hill 33_11kV - winter peak demand | 24.7969 | 24.8217 | 1.1098 | 0.999 | 20.2853 | 22.5392 | 9.8246 | 0.9 | 19.5696 | 21.744 | 9.478 | 0.9 | 19.7266 | 21.9184 | 9.554 | 0.9 | 29.19
Beacon Hill 33_11kV - summer peak demand | 28.1968 | 28.4817 | 4.0178 | 0.99 | 21.3993 | 24.5969 | 12.1275 | 0.87 | 19.6581 | 22.5956 | 11.1408 | 0.87 | 20.6502 | 21.3754 | 5.5207 | 0.96607 | 26.67
Beacon Hill 33_11kV - winter peak demand | 27.0483 | 27.3216 | 3.8542 | 0.99 | 20.1109 | 21.6247 | 7.9483 | 0.93 | 21.4135 | 23.0253 | 8.4632 | 0.93 | 19.981 | 20.0399 | 1.5364 | 0.99706 | 26.67
Belmore Park 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Belmore Park 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Belrose 33_11kV - summer peak demand | 40.6801 | 41.091 | 5.7966 | 0.99 | 24.7237 | 27.1689 | 11.2645 | 0.91 | 24.138 | 26.5253 | 10.9976 | 0.91 | 24.3712 | 26.7815 | 11.1038 | 0.91 | 43.04
Belrose 33_11kV - winter peak demand | 32.4429 | 32.7707 | 4.6229 | 0.99 | 22.1539 | 23.568 | 8.0408 | 0.94 | 23.187 | 24.667 | 8.4157 | 0.94 | 26.8622 | 28.5611 | 9.7037 | 0.94052 | 44.75
Berkeley Vale 132_11kV - summer peak demand | 64.8542 | 69.7357 | 25.632 | 0.93 | 42.4186 | 46.1072 | 18.0703 | 0.92 | 38.7993 | 42.1731 | 16.5284 | 0.92 | 37.9152 | 41.2122 | 16.1518 | 0.92 | 59.9
Berkeley Vale 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 30.5908 | 33.9898 | 14.8158 | 0.9 | 32.0589 | 35.621 | 15.5268 | 0.9 | 31.7894 | 35.3215 | 15.3963 | 0.9 | 63.25
Berkeley Vale 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Berkeley Vale 33_11kV - winter peak demand | 54.8112 | 55.987 | 11.4135 | 0.979 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Berowra 132_11kV - summer peak demand | 29.8136 | 32.4061 | 12.7005 | 0.92 | 22.6205 | 24.292 | 8.8553 | 0.93119 | 19.8375 | 21.3034 | 7.7658 | 0.93119 | 20.9072 | 22.4521 | 8.1846 | 0.93119 | 42.3348
Berowra 132_11kV - winter peak demand | 27.4077 | 28.8502 | 9.0085 | 0.95 | 20.5324 | 21.1674 | 5.1459 | 0.97 | 21.9818 | 22.6616 | 5.5092 | 0.97 | 22.4877 | 23.1832 | 5.6359 | 0.97 | 44.5639
Blackwattle Bay 33_5kV - summer peak demand | 25.1723 | 26.4972 | 8.2737 | 0.95 | 19.3373 | 21.9711 | 10.4306 | 0.88012 | 19.4871 | 22.1413 | 10.5114 | 0.88012 | 19.6666 | 22.3452 | 10.6082 | 0.88013 | 41.67
Blackwattle Bay 33_5kV - winter peak demand | 23.0549 | 25.335 | 10.5041 | 0.91 | 20.849 | 22.6552 | 8.8644 | 0.92027 | 21.5028 | 23.3656 | 9.1423 | 0.92028 | 19.7295 | 21.4387 | 8.3884 | 0.92028 | 44.78
Blakehurst 33_11kV - summer peak demand | 34.4185 | 36.23 | 11.3128 | 0.95 | 19.1311 | 20.653 | 7.7811 | 0.92631 | 19.353 | 20.8925 | 7.8714 | 0.92631 | 20.3978 | 22.0204 | 8.2963 | 0.92631 | 31.59
Blakehurst 33_11kV - winter peak demand | 29.566 | 29.7146 | 2.9677 | 0.995 | 17.3759 | 18.0999 | 5.068 | 0.96 | 18.368 | 19.1333 | 5.3573 | 0.96 | 18.2486 | 19.009 | 5.3225 | 0.96 | 31.59
Boolaroo 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Boolaroo 33_11kV - winter peak demand | 0.00064555 | 0.00068675 | 0.0002343 | 0.94 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Botany 33_11kV - summer peak demand | 42.9425 | 45.5866 | 15.2994 | 0.942 | 26.7592 | 29.379 | 12.1273 | 0.91083 | 26.7232 | 29.3395 | 12.111 | 0.91083 | 24.9044 | 27.3427 | 11.2867 | 0.91082 | 53.11
Botany 33_11kV - winter peak demand | 36.0693 | 37.8084 | 11.3352 | 0.954 | 25.3695 | 26.7307 | 8.4216 | 0.94908 | 25.9567 | 27.3495 | 8.6165 | 0.94907 | 25.2039 | 26.5563 | 8.3666 | 0.94907 | 53.11
Brandy Hill 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0.8807 | 0.9295 | 0.2972 | 0.9475 | 0
Brandy Hill 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 1.4921 | 1.539 | 0.3771 | 0.96953 | 0
Branxton 66_11kV - summer peak demand | 12.3595 | 13.1484 | 4.4859 | 0.94 | 12.7838 | 13.485 | 4.2919 | 0.948 | 12.9233 | 13.6322 | 4.3387 | 0.948 | 10.3135 | 10.8792 | 3.4625 | 0.948 | 15.07
Branxton 66_11kV - winter peak demand | 9.11 | 9.6915 | 3.3065 | 0.94 | 9.1233 | 9.3 | 1.8043 | 0.981 | 8.7084 | 8.8771 | 1.7222 | 0.981 | 5.9198 | 6.0345 | 1.1707 | 0.98099 | 15.24
Broadmeadow 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 31.5503 | 33.9238 | 12.466 | 0.93003 | 0
Broadmeadow 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Broadmeadow 33_11kV - summer peak demand | 33.0508 | 34.073 | 8.2833 | 0.97 | 21.5025 | 23.121 | 8.4983 | 0.93 | 21.2483 | 22.8476 | 8.3979 | 0.93 | 0 | 0 | 0 | #DIV/0! | 18.9
Broadmeadow 33_11kV - winter peak demand | 21.7616 | 22.4346 | 5.454 | 0.97 | 18.8688 | 19.967 | 6.5306 | 0.945 | 19.7752 | 20.9261 | 6.8443 | 0.945 | 0.4295 | 0.4545 | 0.1487 | 0.94499 | 21.42
Brookvale 33_11kV - summer peak demand | 50.6719 | 51.1837 | 7.2204 | 0.99 | 38.4228 | 43.9184 | 21.2723 | 0.87487 | 37.7406 | 43.1385 | 20.8946 | 0.87487 | 40.0057 | 45.6871 | 22.0647 | 0.87565 | 54.33
Brookvale 33_11kV - winter peak demand | 46.9791 | 47.4536 | 6.6942 | 0.99 | 36.1991 | 36.7905 | 6.5698 | 0.98393 | 36.4139 | 37.0088 | 6.6088 | 0.98393 | 37.9012 | 38.5076 | 6.8067 | 0.98425 | 54.33
Burwood 132_11kV - summer peak demand | 96.911 | 106.4956 | 44.1539 | 0.91 | 70.7992 | 78.0202 | 32.7816 | 0.90745 | 67.5194 | 74.4059 | 31.263 | 0.90745 | 71.023 | 74.0301 | 20.8852 | 0.95938 | 83.6
Burwood 132_11kV - winter peak demand | 80.3339 | 86.3805 | 31.75 | 0.93 | 58.8067 | 61.9018 | 19.3288 | 0.95 | 60.2099 | 63.3788 | 19.79 | 0.95 | 59.4256 | 59.901 | 7.5322 | 0.99206 | 90.31
Campbell St 132_11kV - summer peak demand | 55.8272 | 64.1692 | 31.6387 | 0.87 | 40.6096 | 43.6494 | 16.0042 | 0.93036 | 41.202 | 44.2862 | 16.2376 | 0.93036 | 41.4169 | 44.5171 | 16.3223 | 0.93036 | 62.8
Campbell St 132_11kV - winter peak demand | 46.0099 | 50.0107 | 19.6001 | 0.92 | 31.503 | 33.0943 | 10.1387 | 0.95192 | 32.2286 | 33.8566 | 10.3723 | 0.95191 | 33.371 | 35.0567 | 10.7399 | 0.95192 | 65.01
Camperdown 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 16.9784 | 19.7179 | 10.0265 | 0.86107 | 0
Camperdown 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Camperdown 33_5kV - summer peak demand | 30.6271 | 32.5129 | 10.9117 | 0.942 | 20.2127 | 23.5299 | 12.0459 | 0.85902 | 20.6508 | 24.0399 | 12.307 | 0.85902 | 0 | 0 | 0 | #DIV/0! | 56.23
Camperdown 33_5kV - winter peak demand | 27.1052 | 28.4122 | 8.5182 | 0.954 | 22.5095 | 23.9456 | 8.1679 | 0.94003 | 22.5807 | 24.0213 | 8.1937 | 0.94003 | 21.533 | 22.9433 | 7.9198 | 0.93853 | 59.31
Campsie 33_11kV - summer peak demand | 61.0478 | 61.0478 | 0 | 1 | 57.2292 | 63.5974 | 27.739 | 0.89987 | 52.4238 | 58.2573 | 25.4098 | 0.89987 | 56.1454 | 62.4104 | 27.2535 | 0.89962 | 87.01
Campsie 33_11kV - winter peak demand | 57.4569 | 57.5145 | 2.5715 | 0.999 | 50.2959 | 59.5202 | 31.8273 | 0.84502 | 52.3714 | 61.9763 | 33.1407 | 0.84502 | 52.864 | 62.5593 | 33.4524 | 0.84502 | 87.01
Cardiff 33_11kV - summer peak demand | 23.7332 | 24.7221 | 6.9222 | 0.96 | 22.2135 | 22.69 | 4.6256 | 0.979 | 21.5994 | 22.0627 | 4.4977 | 0.979 | 20.257 | 21.5607 | 7.3836 | 0.93953 | 22.86
Cardiff 33_11kV - winter peak demand | 14.2152 | 14.8075 | 4.1461 | 0.96 | 16.2889 | 16.81 | 4.1531 | 0.969 | 16.6642 | 17.1973 | 4.2488 | 0.969 | 13.5186 | 13.9532 | 3.4554 | 0.96885 | 22.86
Careel Bay 33_11kV - summer peak demand | 14.0413 | 14.6264 | 4.0954 | 0.96 | 11.7539 | 12.1174 | 2.9458 | 0.97 | 10.4043 | 10.726 | 2.6076 | 0.97001 | 9.696 | 9.9959 | 2.4301 | 0.97 | 15.24
Careel Bay 33_11kV - winter peak demand | 15.554 | 16.0848 | 4.098 | 0.967 | 11.6945 | 12.9938 | 5.6639 | 0.90001 | 12.1518 | 13.502 | 5.8854 | 0.9 | 11.6242 | 12.9158 | 5.6299 | 0.9 | 15.26
Caringbah 33_11kV - summer peak demand | 37.3941 | 39.7809 | 13.5722 | 0.94 | 19.1272 | 21.4913 | 9.7992 | 0.89 | 18.9012 | 21.2373 | 9.6834 | 0.89 | 20.6465 | 23.1984 | 10.5775 | 0.89 | 38.11
Caringbah 33_11kV - winter peak demand | 30.0987 | 30.8705 | 6.8596 | 0.975 | 17.0987 | 18.3857 | 6.7578 | 0.93 | 17.6381 | 18.9657 | 6.971 | 0.93 | 19.4536 | 20.9178 | 7.6885 | 0.93 | 38.11
Carlton 33_11kV - summer peak demand | 49.7886 | 52.409 | 16.3647 | 0.95 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Carlton 33_11kV - winter peak demand | 44.6823 | 44.9069 | 4.4851 | 0.995 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Carrington 33_11kV - summer peak demand | 25.6087 | 26.4007 | 6.4181 | 0.97 | 24.4222 | 26.431 | 10.107 | 0.924 | 24.8288 | 26.871 | 10.2753 | 0.924 | 23.9522 | 25.9223 | 9.9125 | 0.924 | 30.48
Carrington 33_11kV - winter peak demand | 24.6349 | 25.3968 | 6.1741 | 0.97 | 21.406 | 22.724 | 7.6265 | 0.942 | 22.4812 | 23.8654 | 8.0095 | 0.942 | 20.3752 | 21.6297 | 7.2592 | 0.942 | 30.48
Castle Cove 132_11kV - summer peak demand | 76.2925 | 88.7122 | 45.2693 | 0.86 | 66.0385 | 69.9038 | 22.923 | 0.94471 | 64.0232 | 67.7706 | 22.2235 | 0.9447 | 66.6947 | 68.171 | 14.1104 | 0.97834 | 90.65
Castle Cove 132_11kV - winter peak demand | 74.5559 | 84.7226 | 40.241 | 0.88 | 51.4438 | 59.0629 | 29.0166 | 0.871 | 52.9003 | 60.7351 | 29.8381 | 0.871 | 52.4918 | 55.3663 | 17.6077 | 0.94808 | 96.25
Cessnock 33_11kV - summer peak demand | 25.7756 | 26.5727 | 6.46 | 0.97 | 22.5504 | 22.573 | 1.0092 | 0.999 | 23.5973 | 23.6209 | 1.0561 | 0.999 | 21.3466 | 21.3549 | 0.5945 | 0.99961 | 22.86
Cessnock 33_11kV - winter peak demand | 15.4217 | 15.8986 | 3.865 | 0.97 | 15.8954 | 16.303 | 3.6226 | 0.975 | 16.328 | 16.7467 | 3.7212 | 0.975 | 14.5372 | 14.5964 | 1.3131 | 0.99594 | 22.86
Charlestown 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 35.118 | 39.02 | 17.0084 | 0.9 | 32.5708 | 36.1897 | 15.7747 | 0.9 | 30.3566 | 33.7224 | 14.686 | 0.90019 | 60
Charlestown 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 30.5389 | 33.7375 | 14.3386 | 0.90519 | 0
Charlestown 33_11kV - summer peak demand | 36.8894 | 38.0303 | 9.2454 | 0.97 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Charlestown 33_11kV - winter peak demand | 39.1385 | 40.349 | 9.809 | 0.97 | 18.4092 | 18.539 | 2.1897 | 0.993 | 18.2362 | 18.3648 | 2.1691 | 0.993 | 0 | 0 | 0 | #DIV/0! | 30.48
Charmhaven 132_11kV - summer peak demand | 77.0649 | 87.5738 | 41.5952 | 0.88 | 45.1463 | 47.8219 | 15.7717 | 0.94405 | 37.8612 | 40.105 | 13.2267 | 0.94405 | 38.7946 | 41.0891 | 13.5385 | 0.94416 | 63.25
Charmhaven 132_11kV - winter peak demand | 61.2849 | 63.8385 | 17.8748 | 0.96 | 33.7021 | 34.3899 | 6.8436 | 0.98 | 35.1317 | 35.8487 | 7.1339 | 0.98 | 33.412 | 34.1044 | 6.8374 | 0.9797 | 65.01
Chatswood 33_11kV - summer peak demand | 43.4689 | 47.2488 | 18.5177 | 0.92 | 39.7029 | 43.3827 | 17.4854 | 0.91518 | 37.8149 | 41.3197 | 16.6539 | 0.91518 | 42.2622 | 46.1792 | 18.6125 | 0.91518 | 67.14
Chatswood 33_11kV - winter peak demand | 46.8574 | 48.4064 | 12.1476 | 0.968 | 37.7584 | 41.9537 | 18.2872 | 0.9 | 39.9513 | 44.3903 | 19.3493 | 0.9 | 39.5451 | 43.939 | 19.1526 | 0.9 | 70.51
City Central 132_11kV - summer peak demand | 183.765 | 187.5153 | 37.3151 | 0.98 | 131.36 | 136.84 | 38.31 | 0.95995 | 132.0571 | 137.5595 | 38.5167 | 0.96 | 140.72 | 140.73 | 1.61 | 0.99993 | 191.9926
City Central 132_11kV - winter peak demand | 124.2699 | 138.0777 | 60.1867 | 0.9 | 104.4 | 108.75 | 30.45 | 0.96 | 101.951 | 106.199 | 29.7357 | 0.96 | 112.01 | 112.02 | 1.25 | 0.99991 | 195.022
City East 33_11kV - summer peak demand | 59.8784 | 61.7303 | 15.0069 | 0.97 | 40.88 | 42.6 | 11.92 | 0.95962 | 41.0987 | 42.8111 | 11.9871 | 0.96 | 42.64 | 44.41 | 12.44 | 0.96014 | 71.6376
City East 33_11kV - winter peak demand | 42.3363 | 47.2503 | 20.9817 | 0.896 | 33.97 | 36.14 | 12.33 | 0.93996 | 33.1861 | 35.3044 | 12.045 | 0.94 | 33.4 | 35.53 | 12.12 | 0.94005 | 75.5243
City North 132_11kV - summer peak demand | 60.3589 | 62.2257 | 15.1274 | 0.97 | 54.22 | 55.9 | 13.59 | 0.96995 | 54.5189 | 56.205 | 13.6637 | 0.97 | 59.3 | 59.37 | 2.86 | 0.99882 | 167.9293
City North 132_11kV - winter peak demand | 46.1112 | 47.0522 | 9.3633 | 0.98 | 35.81 | 36.54 | 7.27 | 0.98002 | 34.9717 | 35.6854 | 7.1013 | 0.98 | 47.93 | 47.96 | 1.73 | 0.99937 | 167.9293
City North 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
City North 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
City South 132_11kV - summer peak demand | 185.4454 | 189.23 | 37.6563 | 0.98 | 129.16 | 135.96 | 42.45 | 0.94999 | 129.8489 | 136.6831 | 42.6793 | 0.95 | 153.26 | 154.36 | 18.4 | 0.99287 | 195.022
City South 132_11kV - winter peak demand | 141.767 | 143.199 | 20.2007 | 0.99 | 108.46 | 109.55 | 15.45 | 0.99005 | 105.9103 | 106.9801 | 15.0914 | 0.99 | 130.78 | 130.78 | 0.74 | 1 | 195.022
Clovelly 132_11kV - summer peak demand | 62.7945 | 67.521 | 24.818 | 0.93 | 57.0534 | 59.101 | 15.4223 | 0.96535 | 58.2423 | 60.3326 | 15.7437 | 0.96535 | 58.2104 | 60.2996 | 15.7351 | 0.96535 | 87.64
Clovelly 132_11kV - winter peak demand | 92.2777 | 95.1316 | 23.127 | 0.97 | 79.0114 | 79.8302 | 11.4044 | 0.98974 | 82.0535 | 82.9038 | 11.8435 | 0.98974 | 79.8787 | 80.7064 | 11.5296 | 0.98974 | 92.98
Concord 33_11kV - summer peak demand | 59.3031 | 59.3031 | 0 | 1 | 40.265 | 43.0397 | 15.2036 | 0.93553 | 41.4157 | 44.2697 | 15.6381 | 0.93553 | 43.4547 | 46.4492 | 16.408 | 0.93553 | 54.41
Concord 33_11kV - winter peak demand | 34.0344 | 35.8635 | 11.3069 | 0.949 | 28.0785 | 30.1221 | 10.906 | 0.93216 | 29.3267 | 31.4612 | 11.3908 | 0.93215 | 28.442 | 30.5121 | 11.0472 | 0.93215 | 54.41
Cronulla 132_11kV - summer peak demand | 49.7177 | 52.8912 | 18.0451 | 0.94 | 49.8332 | 51.6324 | 13.5116 | 0.96515 | 48.6071 | 50.3621 | 13.1792 | 0.96515 | 50.7065 | 52.5374 | 13.7484 | 0.96515 | 53.46
Cronulla 132_11kV - winter peak demand | 64.2999 | 66.2886 | 16.1151 | 0.97 | 55.343 | 56.1479 | 9.4733 | 0.98566 | 57.769 | 58.6093 | 9.8886 | 0.98566 | 55.4951 | 56.3022 | 9.4993 | 0.98566 | 64.17
Croudace Bay 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 26.2035 | 26.9403 | 6.2576 | 0.97265 | 25.0846 | 25.79 | 5.9904 | 0.97265 | 23.5554 | 23.7552 | 3.0745 | 0.99159 | 38.11
Croudace Bay 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 17.298 | 18.0683 | 5.2193 | 0.95737 | 17.7334 | 18.523 | 5.3507 | 0.95737 | 17.5342 | 18.2921 | 5.2106 | 0.95857 | 38.11
Crows Nest 33_11kV - summer peak demand | 37.0242 | 40.2437 | 15.7723 | 0.92 | 33.9491 | 39.3816 | 19.9593 | 0.86205 | 34.0998 | 39.5564 | 20.0479 | 0.86206 | 37.028 | 42.9157 | 21.6952 | 0.86281 | 60.02
Crows Nest 33_11kV - winter peak demand | 36.7607 | 37.9759 | 9.5301 | 0.968 | 31.5602 | 36.2761 | 17.886 | 0.87 | 32.6013 | 37.4727 | 18.476 | 0.87 | 32.5604 | 37.4257 | 18.4528 | 0.87 | 60.04
Dalley St 132_11kV - summer peak demand | 170.3962 | 173.8737 | 34.6004 | 0.98 | 113.82 | 118.56 | 33.2 | 0.96002 | 114.4251 | 119.1928 | 33.374 | 0.96 | 125.74 | 125.75 | 0.58 | 0.99992 | 185.4195
Dalley St 132_11kV - winter peak demand | 136.4514 | 139.2361 | 27.7076 | 0.98 | 110.16 | 112.41 | 22.37 | 0.97998 | 107.5852 | 109.7808 | 21.8461 | 0.98 | 104.41 | 104.46 | 3.44 | 0.99952 | 195.022
Darling Harbour 132_11kV - summer peak demand | 73.6475 | 80.0517 | 31.3737 | 0.92 | 54.086 | 57.0586 | 18.1766 | 0.9479 | 56.0114 | 59.0898 | 18.8236 | 0.9479 | 61.1914 | 64.8686 | 21.53 | 0.94331 | 70.3
Darling Harbour 132_11kV - winter peak demand | 42.6899 | 44.0102 | 10.6991 | 0.97 | 41.6675 | 43.2493 | 11.5898 | 0.96343 | 41.6675 | 43.2493 | 11.5898 | 0.96343 | 44.4581 | 46.1662 | 12.4419 | 0.963 | 70.3
Darlinghurst 33_11kV - summer peak demand | 48.6222 | 50.126 | 12.1859 | 0.97 | 47.4637 | 48.7364 | 11.065 | 0.97389 | 47.4997 | 48.7733 | 11.0733 | 0.97389 | 47.3628 | 48.6328 | 11.0414 | 0.97389 | 85.16
Darlinghurst 33_11kV - winter peak demand | 45.7786 | 51.0922 | 22.6877 | 0.896 | 38.2157 | 39.0006 | 7.7848 | 0.97987 | 38.0014 | 38.7818 | 7.7411 | 0.97988 | 37.7936 | 38.5698 | 7.6988 | 0.97988 | 90.08
Dee Why West 33_11kV - summer peak demand | 40.3988 | 40.8069 | 5.7565 | 0.99 | 35.0302 | 37.6669 | 13.8448 | 0.93 | 33.6165 | 36.1468 | 13.2861 | 0.93 | 33.8848 | 36.4353 | 13.3921 | 0.93 | 53.45
Dee Why West 33_11kV - winter peak demand | 51.0229 | 51.5383 | 7.2704 | 0.99 | 40.5632 | 41.5346 | 8.9302 | 0.97661 | 42.9673 | 43.9963 | 9.4595 | 0.97661 | 43.7028 | 44.7494 | 9.6214 | 0.97661 | 58.78
Denman 66_11kV - summer peak demand | 9.9331 | 11.0367 | 4.8108 | 0.9 | 6.3479 | 6.833 | 2.5288 | 0.92901 | 6.394 | 6.8827 | 2.5472 | 0.929 | 5.9921 | 6.0045 | 0.387 | 0.99793 | 16.8806
Denman 66_11kV - winter peak demand | 5.5825 | 6.2028 | 2.7037 | 0.9 | 4.1002 | 4.214 | 0.9726 | 0.97299 | 4.2112 | 4.3281 | 0.9989 | 0.97299 | 3.9601 | 4.07 | 0.9394 | 0.973 | 18.2333
Double Bay 132_11kV - summer peak demand | 76.9816 | 88.4846 | 43.6275 | 0.87 | 56.9402 | 59.9965 | 18.9048 | 0.94906 | 56.4136 | 59.4417 | 18.73 | 0.94906 | 57.7022 | 60.7566 | 19.0216 | 0.94973 | 81.28
Double Bay 132_11kV - winter peak demand | 88.7996 | 96.5213 | 37.8285 | 0.92 | 62.0843 | 63.2735 | 12.2098 | 0.98121 | 62.8397 | 64.0434 | 12.3583 | 0.9812 | 61.1103 | 62.2809 | 12.0182 | 0.9812 | 87.79
Drummoyne 132_11kV - summer peak demand | 59.5804 | 65.473 | 27.1456 | 0.91 | 47.2105 | 50.737 | 18.5852 | 0.93049 | 47.6447 | 51.2036 | 18.7561 | 0.9305 | 50.5638 | 54.3408 | 19.9053 | 0.93049 | 56.15
Drummoyne 132_11kV - winter peak demand | 66.4874 | 69.9867 | 21.8533 | 0.95 | 53.6441 | 56.548 | 17.888 | 0.94865 | 57.2608 | 60.3604 | 19.094 | 0.94865 | 55.6815 | 58.6956 | 18.5674 | 0.94865 | 61.77
Dudley 33_11kV - summer peak demand | 14.8335 | 15.2922 | 3.7176 | 0.97 | 4.7238 | 5.036 | 1.7457 | 0.93801 | 3.9039 | 4.162 | 1.4427 | 0.93799 | 0 | 0 | 0 | #DIV/0! | 16.65
Dudley 33_11kV - winter peak demand | 13.2903 | 13.7013 | 3.3309 | 0.97 | 8.3275 | 8.541 | 1.8979 | 0.975 | 8.5566 | 8.776 | 1.9501 | 0.975 | 0 | 0 | 0 | #DIV/0! | 18.31
Dulwich Hill 33_11kV - summer peak demand | 47.9793 | 47.9793 | 0 | 1 | 36.216 | 38.1623 | 12.0317 | 0.949 | 37.3496 | 39.3568 | 12.4083 | 0.949 | 38.8985 | 40.9889 | 12.9228 | 0.949 | 61.89
Dulwich Hill 33_11kV - winter peak demand | 53.3543 | 53.4077 | 2.3879 | 0.999 | 41.5408 | 42.6206 | 9.5327 | 0.97466 | 43.9011 | 45.0422 | 10.0744 | 0.97467 | 42.5102 | 43.6151 | 9.7552 | 0.97467 | 61.89
East Maitland 33_11kV - summer peak demand | 31.9757 | 35.1381 | 14.5686 | 0.91 | 30.7782 | 30.964 | 3.3868 | 0.994 | 31.4021 | 31.5916 | 3.4555 | 0.994 | 32.1617 | 32.1633 | 0.32 | 0.99995 | 30.48
East Maitland 33_11kV - winter peak demand | 27.7951 | 30.544 | 12.6638 | 0.91 | 19.6779 | 20.059 | 3.8916 | 0.981 | 20.6987 | 21.0996 | 4.0935 | 0.981 | 21.4863 | 21.5099 | 1.0072 | 0.9989 | 30.48
Edgeworth 33_11kV - summer peak demand | 26.4223 | 27.5233 | 7.7065 | 0.96 | 20.9931 | 22.168 | 7.1211 | 0.947 | 21.5082 | 22.712 | 7.2958 | 0.947 | 21.836 | 23.058 | 7.407 | 0.947 | 22.86
Edgeworth 33_11kV - winter peak demand | 16.1851 | 16.8594 | 4.7206 | 0.96 | 13.261 | 13.601 | 3.0222 | 0.975 | 13.7353 | 14.0874 | 3.1303 | 0.97501 | 12.4886 | 12.8088 | 2.8462 | 0.975 | 22.86
Empire Bay 66_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 8.9524 | 9.6903 | 3.7088 | 0.92385 | 0
Empire Bay 66_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 11.2859 | 11.4553 | 1.9624 | 0.98521 | 0
Enfield 33_11kV - summer peak demand | 42.2718 | 42.2718 | 0 | 1 | 19.212 | 21.5865 | 9.8426 | 0.89 | 17.9196 | 20.1344 | 9.1805 | 0.89 | 19.5457 | 21.9615 | 10.0136 | 0.89 | 44.75
Enfield 33_11kV - winter peak demand | 38.6629 | 38.7016 | 1.7304 | 0.999 | 19.2764 | 20.291 | 6.3359 | 0.95 | 19.9235 | 20.9721 | 6.5485 | 0.95 | 19.5204 | 20.5478 | 6.416 | 0.95 | 44.75
Engadine 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Engadine 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Engadine 33_11kV - summer peak demand | 37.4387 | 38.5966 | 9.383 | 0.97 | 27.3024 | 28.1787 | 6.9727 | 0.9689 | 25.5312 | 26.3507 | 6.5204 | 0.9689 | 25.7867 | 26.6143 | 6.5856 | 0.9689 | 29.02
Engadine 33_11kV - winter peak demand | 37.2675 | 37.7201 | 5.826 | 0.988 | 28.0819 | 28.655 | 5.7023 | 0.98 | 29.0708 | 29.664 | 5.9031 | 0.98 | 28.4348 | 29.0151 | 5.7739 | 0.98 | 30.85
Epping 66_11kV - summer peak demand | 68.9025 | 72.529 | 22.6472 | 0.95 | 58.609 | 61.1016 | 17.274 | 0.95921 | 56.7582 | 59.1721 | 16.7285 | 0.95921 | 65.4492 | 65.8539 | 7.2896 | 0.99385 | 74.91
Epping 66_11kV - winter peak demand | 54.9969 | 57.8915 | 18.0766 | 0.95 | 47.8308 | 48.5269 | 8.1899 | 0.98566 | 49.7197 | 50.4433 | 8.5134 | 0.98566 | 49.255 | 49.3151 | 2.4338 | 0.99878 | 74.91
Erina 66_11kV - summer peak demand | 40.7239 | 45.2488 | 19.7235 | 0.9 | 32.2928 | 34.2184 | 11.3169 | 0.94373 | 29.4576 | 31.2142 | 10.3233 | 0.94372 | 30.38 | 30.7332 | 4.6466 | 0.98851 | 49.26
Erina 66_11kV - winter peak demand | 46.5363 | 47.245 | 8.1523 | 0.985 | 24.3514 | 25.0541 | 5.8923 | 0.97195 | 25.5239 | 26.2605 | 6.176 | 0.97195 | 22.8554 | 22.995 | 2.5303 | 0.99393 | 49.26
Five Dock 33_11kV - summer peak demand | 32.634 | 32.634 | 0 | 1 | 30.1568 | 32.7323 | 12.7268 | 0.92132 | 29.9544 | 32.5126 | 12.6414 | 0.92132 | 32.8604 | 35.6668 | 13.8678 | 0.92132 | 41.26
Five Dock 33_11kV - winter peak demand | 37.4754 | 39.4893 | 12.45 | 0.949 | 30.4966 | 31.5701 | 8.1625 | 0.966 | 31.9599 | 33.0849 | 8.5542 | 0.966 | 33.063 | 34.2268 | 8.8494 | 0.966 | 44.17
Flemington 132_11kV - summer peak demand | 80.6703 | 91.6708 | 43.5412 | 0.88 | 77.9148 | 84.0789 | 31.5998 | 0.92669 | 77.7789 | 83.9322 | 31.5447 | 0.92669 | 86.3058 | 93.1338 | 35.0029 | 0.92669 | 98.69
Flemington 132_11kV - winter peak demand | 72.5547 | 74.7987 | 18.1839 | 0.97 | 59.556 | 64.7596 | 25.4341 | 0.91965 | 60.7229 | 66.0286 | 25.9325 | 0.91965 | 61.2582 | 66.4599 | 25.7752 | 0.92173 | 106.62
Galston 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 8.7193 | 9.4882 | 3.7416 | 0.91896 | 8.7745 | 9.5483 | 3.7653 | 0.91896 | 8.6026 | 9.3613 | 3.6916 | 0.91895 | 38.11
Galston 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 8.319 | 8.688 | 2.505 | 0.95753 | 8.0118 | 8.3671 | 2.4125 | 0.95754 | 7.8157 | 8.1624 | 2.3534 | 0.95752 | 38.11
Gateshead 33_11kV - summer peak demand | 19.1153 | 19.7064 | 4.7907 | 0.97 | 11.8026 | 12.556 | 4.2838 | 0.94 | 11.4842 | 12.2173 | 4.1682 | 0.93999 | 14.4148 | 15.3417 | 5.2518 | 0.93958 | 24.08
Gateshead 33_11kV - winter peak demand | 17.8719 | 18.4246 | 4.4791 | 0.97 | 11.2878 | 11.613 | 2.7288 | 0.972 | 11.5011 | 11.8324 | 2.7804 | 0.972 | 13.1789 | 13.5461 | 3.1328 | 0.97289 | 24.41
Gore Hill 33_11kV - summer peak demand | 74.7089 | 81.2053 | 31.8259 | 0.92 | 61.3673 | 66.1267 | 24.6331 | 0.92803 | 62.2277 | 67.0538 | 24.9785 | 0.92803 | 59.969 | 64.6199 | 24.0718 | 0.92803 | 96.89
Gore Hill 33_11kV - winter peak demand | 78.3746 | 80.9655 | 20.3183 | 0.968 | 54.7978 | 61.0444 | 26.9002 | 0.89767 | 54.7239 | 60.9621 | 26.8639 | 0.89767 | 49.6721 | 55.3343 | 24.3839 | 0.89767 | 96.89
Graving Dock No 1 33_11kV - summer peak demand | 13.5059 | 13.9236 | 3.3849 | 0.97 | 7.2705 | 8.0783 | 3.5212 | 0.9 | 7.2705 | 8.0783 | 3.5212 | 0.9 | 7.2705 | 8.0783 | 3.5212 | 0.9 | 0
Graving Dock No 1 33_11kV - winter peak demand | 10.0175 | 11.1305 | 4.8517 | 0.9 | 6.5503 | 7.2781 | 3.1724 | 0.9 | 6.5503 | 7.2781 | 3.1724 | 0.9 | 7.0475 | 7.8306 | 3.4133 | 0.89999 | 0
Graving Dock No 2 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 6.6703 | 7.4114 | 3.2306 | 0.90001 | 6.6703 | 7.4114 | 3.2306 | 0.90001 | 6.6703 | 7.4114 | 3.2306 | 0.90001 | 0
Graving Dock No 2 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 7.8192 | 8.688 | 3.787 | 0.9 | 7.8192 | 8.688 | 3.787 | 0.9 | 7.3048 | 8.1164 | 3.5379 | 0.9 | 0
Green Square 132_11kV - summer peak demand | 41.2763 | 42.5529 | 10.3448 | 0.97 | 27.1064 | 34.4661 | 21.2874 | 0.78647 | 26.865 | 34.1591 | 21.0979 | 0.78647 | 38.1904 | 48.5596 | 29.9921 | 0.78646 | 114.32
Green Square 132_11kV - winter peak demand | 14.2461 | 14.6867 | 3.5704 | 0.97 | 27.0425 | 28.4264 | 8.7614 | 0.95132 | 26.8848 | 28.2606 | 8.7103 | 0.95132 | 30.3594 | 31.913 | 9.8361 | 0.95132 | 114.32
Greenacre Park 132_11kV - summer peak demand | 95.8464 | 103.0607 | 37.8809 | 0.93 | 76.2722 | 78.8585 | 20.0304 | 0.9672 | 75.5976 | 78.161 | 19.8532 | 0.9672 | 42.2648 | 42.2728 | 0.8248 | 0.99981 | 86.16
Greenacre Park 132_11kV - winter peak demand | 99.3091 | 103.447 | 28.9652 | 0.96 | 56.9822 | 57.5578 | 8.1195 | 0.99 | 57.7158 | 58.2988 | 8.2241 | 0.99 | 56.2267 | 56.2652 | 2.0828 | 0.99932 | 91.95
Gwawley Bay 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 28.0701 | 31.189 | 13.595 | 0.9 | 28.4789 | 31.6433 | 13.793 | 0.9 | 28.5671 | 31.7412 | 13.8357 | 0.9 | 40.2
Gwawley Bay 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 25.1157 | 26.0212 | 6.8047 | 0.9652 | 0
Gwawley Bay 33_11kV - summer peak demand | 39.7009 | 40.9287 | 9.95 | 0.97 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Gwawley Bay 33_11kV - winter peak demand | 43.047 | 43.5699 | 6.7295 | 0.988 | 24.973 | 25.8734 | 6.766 | 0.9652 | 25.4084 | 26.3245 | 6.884 | 0.9652 | 0 | 0 | 0 | #DIV/0! | 38.11
Harbord 33_11kV - summer peak demand | 18.0604 | 18.2428 | 2.5735 | 0.99 | 16.8097 | 18.2714 | 7.1609 | 0.92 | 15.506 | 16.8544 | 6.6055 | 0.92 | 17.3434 | 18.8515 | 7.3883 | 0.92 | 37.27
Harbord 33_11kV - winter peak demand | 27.1462 | 27.4204 | 3.8681 | 0.99 | 21.1986 | 22.0819 | 6.1829 | 0.96 | 22.5376 | 23.4767 | 6.5735 | 0.96 | 22.8159 | 23.7665 | 6.6546 | 0.96 | 37.49
Homebush Bay 132_11kV - summer peak demand | 66.3318 | 72.0998 | 28.2572 | 0.92 | 44.1891 | 45.8595 | 12.2644 | 0.96358 | 43.5515 | 45.1978 | 12.0874 | 0.96358 | 51.021 | 52.9496 | 14.1605 | 0.96358 | 53.18
Homebush Bay 132_11kV - winter peak demand | 43.3056 | 44.6449 | 10.8534 | 0.97 | 33.8575 | 34.5232 | 6.7472 | 0.98072 | 34.1349 | 34.8061 | 6.8025 | 0.98072 | 35.9005 | 36.6702 | 7.4736 | 0.97901 | 57.44
Hornsby 132_11kV - summer peak demand | 81.887 | 92.0078 | 41.9519 | 0.89 | 68.4433 | 70.342 | 16.2334 | 0.97301 | 66.6519 | 68.501 | 15.8086 | 0.97301 | 72.0985 | 73.5295 | 14.4357 | 0.98054 | 114.32
Hornsby 132_11kV - winter peak demand | 82.5303 | 85.9691 | 24.0713 | 0.96 | 56.3975 | 62.6639 | 27.3145 | 0.9 | 60.5321 | 67.2579 | 29.3171 | 0.9 | 64.0624 | 67.767 | 22.0991 | 0.94533 | 114.32
Hunters Hill 66_11kV - summer peak demand | 66.9085 | 70.43 | 21.9918 | 0.95 | 42.054 | 48.3935 | 23.9457 | 0.869 | 42.6902 | 49.1256 | 24.3079 | 0.869 | 46.3352 | 53.3201 | 26.3834 | 0.869 | 69.83
Hunters Hill 66_11kV - winter peak demand | 60.9495 | 64.1573 | 20.0331 | 0.95 | 44.9798 | 46.6026 | 12.1909 | 0.96518 | 44.8803 | 46.4995 | 12.1639 | 0.96518 | 44.4194 | 46.022 | 12.039 | 0.96518 | 72.32
Hurstville North 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 11.1674 | 11.3195 | 1.8495 | 0.98656 | 0
Hurstville North 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Hurstville North 33_11kV - summer peak demand | 40.3234 | 42.4457 | 13.2537 | 0.95 | 18.6852 | 20.31 | 7.9599 | 0.92 | 19.0087 | 20.6617 | 8.0977 | 0.92 | 9.5864 | 10.42 | 4.0838 | 0.92 | 41.74
Hurstville North 33_11kV - winter peak demand | 34.9645 | 35.1402 | 3.5096 | 0.995 | 15.2944 | 16.0994 | 5.027 | 0.95 | 15.3873 | 16.1972 | 5.0576 | 0.95 | 15.4976 | 16.3133 | 5.0938 | 0.95 | 42.02
Jannali 33_11kV - summer peak demand | 44.9303 | 46.3199 | 11.2606 | 0.97 | 27.8916 | 29.741 | 10.3241 | 0.93782 | 27.3344 | 29.1469 | 10.1179 | 0.93781 | 28.2759 | 30.1508 | 10.4663 | 0.93782 | 40.91
Jannali 33_11kV - winter peak demand | 40.4882 | 40.98 | 6.3295 | 0.988 | 31.5362 | 32.1798 | 6.4037 | 0.98 | 31.063 | 31.697 | 6.3076 | 0.98 | 30.6728 | 31.2988 | 6.2284 | 0.98 | 44.75
Jesmond 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 43.3276 | 45.832 | 14.9428 | 0.94536 | 42.7778 | 45.2503 | 14.7532 | 0.94536 | 42.651 | 45.1195 | 14.7194 | 0.94529 | 57.48
Jesmond 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 33.141 | 34.095 | 8.0089 | 0.97202 | 33.8225 | 34.7961 | 8.1736 | 0.97202 | 33.3277 | 35.811 | 13.103 | 0.93066 | 57.48
Jewells 33_11kV - summer peak demand | 22.4796 | 23.1749 | 5.6339 | 0.97 | 16.3892 | 17.27 | 5.4448 | 0.949 | 14.3746 | 15.1471 | 4.7755 | 0.949 | 15.0796 | 15.89 | 5.0097 | 0.949 | 16.92
Jewells 33_11kV - winter peak demand | 22.1298 | 22.8143 | 5.5463 | 0.97 | 12.8725 | 13.298 | 3.3371 | 0.968 | 13.3385 | 13.7795 | 3.458 | 0.968 | 12.6196 | 13.0368 | 3.2716 | 0.968 | 18.14
Killarney 33_11kV - summer peak demand | 24.3122 | 24.5577 | 3.4643 | 0.99 | 12.8948 | 14.3275 | 6.2452 | 0.9 | 11.8932 | 13.2147 | 5.7602 | 0.9 | 11.5166 | 12.7962 | 5.5777 | 0.9 | 21.09
Killarney 33_11kV - winter peak demand | 20.9203 | 21.1316 | 2.981 | 0.99 | 14.1934 | 14.7848 | 4.1397 | 0.96 | 15.0133 | 15.6389 | 4.3789 | 0.96 | 12.8485 | 13.3839 | 3.7475 | 0.96 | 21.09
Kingsford 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 33.7287 | 37.4764 | 16.3356 | 0.9 | 33.369 | 37.0766 | 16.1613 | 0.9 | 36.9983 | 41.1092 | 17.9191 | 0.9 | 62.24
Kingsford 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 42.1652 | 46.8502 | 20.4215 | 0.9 | 43.4651 | 48.2946 | 21.0511 | 0.9 | 46.0381 | 51.1535 | 22.2973 | 0.9 | 65.01
Kirrawee 132_11kV - summer peak demand | 33.258 | 39.5928 | 21.4825 | 0.84 | 31.9283 | 35.4759 | 15.4636 | 0.9 | 32.315 | 35.9056 | 15.6509 | 0.9 | 33.7156 | 37.4618 | 16.3292 | 0.9 | 44.56
Kirrawee 132_11kV - winter peak demand | 38.8948 | 42.277 | 16.5691 | 0.92 | 32.9017 | 36.8095 | 16.5052 | 0.89384 | 34.8164 | 38.9517 | 17.4657 | 0.89384 | 34.3841 | 38.4681 | 17.2489 | 0.89383 | 44.56
Kogarah 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 67.4575 | 74.9528 | 32.6712 | 0.9 | 67.8552 | 75.3946 | 32.8638 | 0.9 | 68.7573 | 76.397 | 33.3007 | 0.9 | 114.32
Kogarah 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 58.5383 | 65.3122 | 28.9645 | 0.89628 | 60.6237 | 67.6389 | 29.9964 | 0.89628 | 61.9912 | 69.1584 | 30.6592 | 0.89637 | 114.32
Kotara 33_11kV - summer peak demand | 30.497 | 31.4402 | 7.6433 | 0.97 | 23.3994 | 24.709 | 7.9374 | 0.947 | 23.2534 | 24.5548 | 7.8878 | 0.947 | 23.2554 | 24.5569 | 7.8885 | 0.947 | 30.48
Kotara 33_11kV - winter peak demand | 22.4771 | 23.1722 | 5.6333 | 0.97 | 16.2743 | 16.7776 | 4.0787 | 0.97 | 16.8034 | 17.3231 | 4.2113 | 0.97 | 14.8737 | 15.3337 | 3.7277 | 0.97 | 30.48
Kurnell 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 17.0056 | 17.2235 | 2.7313 | 0.98735 | 17.0056 | 17.2235 | 2.7313 | 0.98735 | 8.2477 | 8.3534 | 1.3247 | 0.98735 | 28.67
Kurnell 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 15.2867 | 16.6138 | 6.5066 | 0.92012 | 15.9604 | 17.346 | 6.7934 | 0.92012 | 18.6712 | 20.2921 | 7.9472 | 0.92012 | 29.63
Kurnell 33_6.3kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 8.1962 | 9.5916 | 4.9821 | 0.85452 | 8.1962 | 9.5916 | 4.9821 | 0.85452 | 4.0981 | 4.7958 | 2.491 | 0.85452 | 9.71
Kurnell 33_6.3kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 7.3329 | 8.5986 | 4.4904 | 0.8528 | 7.3329 | 8.5986 | 4.4904 | 0.8528 | 7.0258 | 8.2385 | 4.3024 | 0.8528 | 9.71
Kurnell South 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 12.3458 | 12.922 | 3.8157 | 0.95541 | 0
Kurnell South 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Kurri 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 27.3273 | 28.342 | 7.5158 | 0.9642 | 26.9739 | 27.9755 | 7.4186 | 0.9642 | 27.3215 | 27.3573 | 1.3984 | 0.99869 | 60
Kurri 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 20.136 | 20.988 | 5.9193 | 0.95941 | 20.5491 | 21.4186 | 6.0407 | 0.9594 | 18.6724 | 18.7734 | 1.9442 | 0.99462 | 60
Kurri 33_11kV - summer peak demand | 38.7264 | 39.9242 | 9.7058 | 0.97 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Kurri 33_11kV - winter peak demand | 24.3791 | 25.133 | 6.11 | 0.97 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Lake Munmorah 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 19.2221 | 20.2338 | 6.318 | 0.95 | 15.7532 | 16.5823 | 5.1778 | 0.95 | 15.6997 | 16.526 | 5.1602 | 0.95 | 38.11
Lake Munmorah 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 23.1737 | 24.2069 | 6.9968 | 0.95732 | 0
Lake Munmorah 33_11kV - summer peak demand | 26.4864 | 27.59 | 7.7252 | 0.96 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Lake Munmorah 33_11kV - winter peak demand | 26.2357 | 27.0471 | 6.5753 | 0.97 | 15.1747 | 15.8898 | 4.7132 | 0.955 | 15.7962 | 16.5405 | 4.9062 | 0.955 | 0 | 0 | 0 | #DIV/0! | 30.48
Leichhardt 33_11kV - summer peak demand | 45.2133 | 48.6165 | 17.8694 | 0.93 | 31.425 | 33.9136 | 12.7514 | 0.92662 | 31.0008 | 33.4557 | 12.5792 | 0.92662 | 31.0305 | 33.4878 | 12.5913 | 0.92662 | 65.83
Leichhardt 33_11kV - winter peak demand | 51.285 | 53.6454 | 15.7378 | 0.956 | 34.5523 | 37.0572 | 13.3931 | 0.9324 | 36.7908 | 39.4579 | 14.2607 | 0.93241 | 34.7451 | 37.2639 | 13.4678 | 0.93241 | 69.07
Leightonfield 33_11kV - summer peak demand | 29.3464 | 30.8909 | 9.6457 | 0.95 | 20.7212 | 22.0438 | 7.5208 | 0.94 | 20.6752 | 21.9949 | 7.5041 | 0.94 | 22.2363 | 23.6557 | 8.0707 | 0.94 | 30.51
Leightonfield 33_11kV - winter peak demand | 22.7299 | 23.9262 | 7.471 | 0.95 | 18.8234 | 19.4056 | 4.7176 | 0.97 | 19.5134 | 20.1169 | 4.8905 | 0.97 | 19.8268 | 20.44 | 4.9691 | 0.97 | 30.51
Lemington 66_11kV - summer peak demand | 4.5101 | 4.798 | 1.637 | 0.94 | 2.6877 | 2.931 | 1.1691 | 0.91699 | 2.6909 | 2.9344 | 1.1705 | 0.91702 | 2.6593 | 2.9 | 1.1568 | 0.917 | 13.36
Lemington 66_11kV - winter peak demand | 2.8863 | 3.0705 | 1.0476 | 0.94 | 1.8435 | 1.957 | 0.6568 | 0.942 | 1.8463 | 1.96 | 0.6578 | 0.94199 | 1.6673 | 1.77 | 0.594 | 0.94198 | 14.69
Lidcombe 33_11kV - summer peak demand | 27.8927 | 27.8927 | 0 | 1 | 19.6565 | 21.6818 | 9.1501 | 0.90659 | 19.3756 | 21.372 | 9.0193 | 0.90659 | 20.4903 | 22.5948 | 9.5223 | 0.90686 | 33.41
Lidcombe 33_11kV - winter peak demand | 23.6633 | 24.935 | 7.8614 | 0.949 | 18.8175 | 20.0814 | 7.0118 | 0.93706 | 18.6684 | 19.9223 | 6.9562 | 0.93706 | 15.1181 | 16.1366 | 5.6419 | 0.93688 | 33.41
Lindfield 33_11kV - summer peak demand | 37.7678 | 42.6755 | 19.8693 | 0.885 | 28.6565 | 30.808 | 11.3109 | 0.93016 | 27.4318 | 29.4913 | 10.8275 | 0.93017 | 27.128 | 29.1647 | 10.7076 | 0.93017 | 35.18
Lindfield 33_11kV - winter peak demand | 39.5754 | 42.5085 | 15.5164 | 0.931 | 30.8632 | 31.8178 | 7.7351 | 0.97 | 31.9397 | 32.9275 | 8.0048 | 0.97 | 31.8269 | 32.8214 | 8.0182 | 0.9697 | 37.13
Lisarow 33_11kV - summer peak demand | 33.4946 | 35.7466 | 12.4874 | 0.937 | 26.6894 | 27.188 | 5.1829 | 0.98166 | 22.7752 | 23.2006 | 4.4228 | 0.98166 | 23.1106 | 23.1168 | 0.5359 | 0.99973 | 30.48
Lisarow 33_11kV - winter peak demand | 31.0571 | 31.7233 | 6.4671 | 0.979 | 20.3704 | 20.9007 | 4.6781 | 0.97463 | 21.1325 | 21.6826 | 4.8531 | 0.97463 | 21.4549 | 21.4749 | 0.9272 | 0.99907 | 30.54
Long Jetty 33_11kV - summer peak demand | 50.8654 | 54.2854 | 18.9635 | 0.937 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Long Jetty 33_11kV - winter peak demand | 59.5114 | 60.7879 | 12.3922 | 0.979 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Long Jetty 66_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 40.7763 | 45.307 | 19.7489 | 0.9 | 31.8701 | 35.4112 | 15.4354 | 0.9 | 31.7812 | 35.3125 | 15.3923 | 0.9 | 71.69
Long Jetty 66_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 34.6718 | 38.5243 | 16.7923 | 0.9 | 37.6204 | 41.8004 | 18.2204 | 0.9 | 37.2826 | 41.4251 | 18.0568 | 0.9 | 76.21
Lucas Heights 33_11kV - summer peak demand | 9.5953 | 9.8921 | 2.4048 | 0.97 | 6.4559 | 7.1066 | 2.9708 | 0.90844 | 6.3901 | 7.0342 | 2.9405 | 0.90843 | 6.8713 | 7.5639 | 3.162 | 0.90843 | 19.22
Lucas Heights 33_11kV - winter peak demand | 7.1983 | 7.2857 | 1.1253 | 0.988 | 5.7664 | 6.2683 | 2.4577 | 0.91993 | 5.7195 | 6.2173 | 2.4377 | 0.91993 | 5.9592 | 6.4779 | 2.5399 | 0.91993 | 22.02
Macquarie Park 132_11kV - summer peak demand | 80.4437 | 89.3819 | 38.9607 | 0.9 | 65.5048 | 68.2844 | 19.2842 | 0.95929 | 67.2665 | 70.1208 | 19.8028 | 0.95929 | 100.8615 | 105.1414 | 29.693 | 0.95929 | 114.32
Macquarie Park 132_11kV - winter peak demand | 55.8684 | 58.8088 | 18.3631 | 0.95 | 52.7594 | 55.2524 | 16.4097 | 0.95488 | 52.7594 | 55.2524 | 16.4097 | 0.95488 | 73.8567 | 77.3466 | 22.9715 | 0.95488 | 114.32
Maitland 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 24.2273 | 26.0348 | 9.5314 | 0.93057 | 0
Maitland 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Maitland Central 33_11kV - summer peak demand | 29.313 | 30.2196 | 7.3465 | 0.97 | 19.3131 | 20.834 | 7.814 | 0.927 | 20.1102 | 21.6939 | 8.1365 | 0.927 | 0 | 0 | 0 | #DIV/0! | 23.82
Maitland Central 33_11kV - winter peak demand | 16.931 | 17.4546 | 4.2433 | 0.97 | 11.4965 | 11.988 | 3.3975 | 0.959 | 12.3158 | 12.8424 | 3.6396 | 0.959 | 12.1228 | 12.6216 | 3.5131 | 0.96048 | 23.82
Manly 33_11kV - summer peak demand | 22.2413 | 22.466 | 3.1692 | 0.99 | 16.0636 | 17.5855 | 7.1561 | 0.91346 | 16.2959 | 17.8398 | 7.2596 | 0.91346 | 16.2188 | 17.7554 | 7.2253 | 0.91346 | 23.24
Manly 33_11kV - winter peak demand | 25.1343 | 25.3881 | 3.5814 | 0.99 | 19.871 | 20.8435 | 6.2925 | 0.95334 | 20.6161 | 21.6251 | 6.5285 | 0.95334 | 20.0707 | 21.053 | 6.3558 | 0.95334 | 25.44
Maroubra 132_11kV - summer peak demand | 55.4464 | 63.7315 | 31.4229 | 0.87 | 41.9915 | 44.5639 | 14.9218 | 0.94228 | 42.8748 | 45.5014 | 15.2357 | 0.94227 | 45.0662 | 47.8497 | 16.0819 | 0.94183 | 102.77
Maroubra 132_11kV - winter peak demand | 52.3964 | 58.2182 | 25.3767 | 0.9 | 46.1177 | 49.5367 | 18.0843 | 0.93098 | 46.7395 | 50.2046 | 18.3282 | 0.93098 | 47.8961 | 51.447 | 18.7817 | 0.93098 | 102.77
Marrickville 132_11kV - summer peak demand | 57.9275 | 67.3575 | 34.3722 | 0.86 | 45.0994 | 49.289 | 19.8858 | 0.915 | 45.6824 | 49.9261 | 20.1429 | 0.915 | 45.8433 | 50.1019 | 20.2138 | 0.915 | 74.8
Marrickville 132_11kV - winter peak demand | 60.7716 | 64.6507 | 22.0572 | 0.94 | 50.6185 | 51.7658 | 10.8383 | 0.97784 | 53.6953 | 54.9124 | 11.4971 | 0.97784 | 50.6721 | 51.8207 | 10.8497 | 0.97784 | 74.8
Maryland 132_11kV - summer peak demand | 38.1335 | 41.905 | 17.3741 | 0.91 | 22.7794 | 24.329 | 8.5439 | 0.93631 | 23.541 | 25.1424 | 8.8296 | 0.93631 | 21.7172 | 23.1946 | 8.1456 | 0.9363 | 38.11
Maryland 132_11kV - winter peak demand | 20.8767 | 22.9415 | 9.5117 | 0.91 | 13.044 | 13.61 | 3.8841 | 0.95841 | 13.6164 | 14.2072 | 4.0545 | 0.95842 | 12.2609 | 12.7929 | 3.6509 | 0.95841 | 38.11
Mascot 33_11kV - summer peak demand | 46.6983 | 49.5736 | 16.6375 | 0.942 | 45.5747 | 50.5655 | 21.9048 | 0.9013 | 45.2906 | 50.2503 | 21.7683 | 0.9013 | 45.4567 | 50.4346 | 21.8481 | 0.9013 | 76.49
Mascot 33_11kV - winter peak demand | 39.7839 | 41.7022 | 12.5026 | 0.954 | 35.2763 | 39.7627 | 18.3481 | 0.88717 | 36.2992 | 40.9157 | 18.8801 | 0.88717 | 35.6637 | 40.1055 | 18.3454 | 0.88925 | 78.84
Matraville 33_11kV - summer peak demand | 51.9795 | 55.1799 | 18.5191 | 0.942 | 39.233 | 42.3919 | 16.0577 | 0.92548 | 38.6926 | 41.808 | 15.8365 | 0.92548 | 24.6294 | 26.6125 | 10.0806 | 0.92548 | 68.09
Matraville 33_11kV - winter peak demand | 50.2534 | 52.6765 | 15.7928 | 0.954 | 40.8139 | 43.1731 | 14.0763 | 0.94535 | 41.6834 | 44.0928 | 14.3761 | 0.94536 | 41.3661 | 43.7572 | 14.2667 | 0.94536 | 72.67
Mayfield 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0.3399 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
Mayfield 33_11kV - winter peak demand | 22.0271 | 22.7083 | 5.5205 | 0.97 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Mayfield West 132_11kV - summer peak demand | 39.02 | 41.0737 | 12.8252 | 0.95 | 23.4752 | 25.458 | 9.8502 | 0.92211 | 24.4516 | 26.5169 | 10.26 | 0.92211 | 31.0509 | 33.6736 | 13.029 | 0.92211 | 31.68
Mayfield West 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 19.472 | 20.982 | 7.8157 | 0.92803 | 19.9292 | 21.4747 | 7.9993 | 0.92803 | 25.4648 | 27.4396 | 10.2211 | 0.92803 | 33.72
Meadowbank 132_11kV - summer peak demand | 96.2802 | 118.8644 | 69.7057 | 0.81 | 63.0469 | 66.3029 | 20.5222 | 0.95089 | 66.4573 | 69.8894 | 21.6323 | 0.95089 | 70.9536 | 74.618 | 23.0959 | 0.95089 | 103.84
Meadowbank 132_11kV - winter peak demand | 85.345 | 92.7663 | 36.3568 | 0.92 | 54.6938 | 57.996 | 19.2906 | 0.94306 | 55.4266 | 58.7731 | 19.549 | 0.94306 | 53.6357 | 56.874 | 18.9174 | 0.94306 | 108.66
Medowie 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 13.8386 | 14.7848 | 5.2042 | 0.936 | 0
Medowie 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Menai 132_11kV - summer peak demand | 69.1753 | 70.5871 | 14.0467 | 0.98 | 42.2537 | 44.0495 | 12.4495 | 0.95923 | 38.7647 | 40.4123 | 11.4215 | 0.95923 | 41.3951 | 43.1545 | 12.1965 | 0.95923 | 60.72
Menai 132_11kV - winter peak demand | 52.6066 | 53.6802 | 10.6822 | 0.98 | 36.3401 | 37.6288 | 9.7633 | 0.96575 | 37.7857 | 39.1257 | 10.1517 | 0.96575 | 34.9593 | 36.199 | 9.3923 | 0.96575 | 65.01
Merriwa 33_11kV - summer peak demand | 4.5958 | 5.1064 | 2.2258 | 0.9 | 3.5379 | 3.67 | 0.9759 | 0.96401 | 3.5705 | 3.7039 | 0.9849 | 0.96398 | 3.6141 | 3.6212 | 0.2264 | 0.99804 | 0
Merriwa 33_11kV - winter peak demand | 2.6764 | 2.9738 | 1.2963 | 0.9 | 3.0697 | 3.082 | 0.2754 | 0.99601 | 2.9782 | 2.9901 | 0.2672 | 0.99602 | 2.947 | 2.9616 | 0.2939 | 0.99507 | 0
Milperra 132_11kV - summer peak demand | 47.316 | 51.4305 | 20.1565 | 0.92 | 42.3969 | 47.4409 | 21.287 | 0.89368 | 43.92 | 49.1451 | 22.0517 | 0.89368 | 45.6835 | 51.1184 | 22.9371 | 0.89368 | 61.18
Milperra 132_11kV - winter peak demand | 44.1581 | 45.0593 | 8.9667 | 0.98 | 42.2186 | 46.6407 | 19.8228 | 0.90519 | 42.2546 | 46.6805 | 19.8397 | 0.90519 | 40.5505 | 44.7979 | 19.0396 | 0.90519 | 64.61
Miranda 33_11kV - summer peak demand | 40.7736 | 42.0347 | 10.2188 | 0.97 | 30.148 | 31.8368 | 10.2315 | 0.94695 | 31.0458 | 32.7849 | 10.5362 | 0.94695 | 30.7442 | 32.4665 | 10.4338 | 0.94695 | 41.98
Miranda 33_11kV - winter peak demand | 53.318 | 53.9656 | 8.3352 | 0.988 | 27.7322 | 28.2359 | 5.3097 | 0.98216 | 28.2117 | 28.7242 | 5.4015 | 0.98216 | 27.59 | 28.0911 | 5.2824 | 0.98216 | 41.98
Mitchell Line 66_11kV - summer peak demand | 9.9752 | 11.0836 | 4.8312 | 0.9 | 12.1 | 12.955 | 4.6285 | 0.934 | 12.6978 | 13.5951 | 4.8572 | 0.934 | 13.7376 | 14.7084 | 5.2549 | 0.934 | 0
Mitchell Line 66_11kV - winter peak demand | 9.5734 | 10.6371 | 4.6366 | 0.9 | 8.992 | 9.232 | 2.0915 | 0.974 | 9.1465 | 9.3906 | 2.1274 | 0.97401 | 9.6122 | 9.8688 | 2.2358 | 0.974 | 0
Mitchells Flat 66_11kV - summer peak demand | 2.0648 | 2.1966 | 0.74941 | 0.94 | 1.2861 | 1.311 | 0.2543 | 0.98101 | 1.3249 | 1.3506 | 0.262 | 0.98097 | 1.4196 | 1.4471 | 0.2807 | 0.981 | 0
Mitchells Flat 66_11kV - winter peak demand | 1.0812 | 1.1502 | 0.39241 | 0.94 | 0.931 | 0.931 | 0 | 1 | 0.8948 | 0.8948 | 0 | 1 | 0.8942 | 0.8942 | 0 | 1 | 0
Mona Vale 33_11kV - summer peak demand | 38.9693 | 40.593 | 11.366 | 0.96 | 33.8816 | 36.6952 | 14.0918 | 0.92333 | 33.2202 | 35.9789 | 13.8167 | 0.92332 | 33.5479 | 36.3339 | 13.953 | 0.92332 | 53.52
Mona Vale 33_11kV - winter peak demand | 40.4325 | 41.8123 | 10.6528 | 0.967 | 29.461 | 31.3415 | 10.6929 | 0.94 | 30.7997 | 32.7657 | 11.1788 | 0.94 | 31.747 | 33.7734 | 11.5226 | 0.94 | 55.68
Moonan 33_11kV - summer peak demand | 1.3474 | 1.4035 | 0.39298 | 0.96 | 0.9367 | 1.004 | 0.3613 | 0.93297 | 0.9976 | 1.0693 | 0.3848 | 0.93295 | 0.9674 | 1.0369 | 0.3731 | 0.93297 | 2.86
Moonan 33_11kV - winter peak demand | 1.2502 | 1.3023 | 0.36465 | 0.96 | 1.0117 | 1.025 | 0.1647 | 0.98702 | 1.0556 | 1.0695 | 0.1719 | 0.987 | 0.9957 | 1.0088 | 0.1621 | 0.98701 | 3.14
Morisset 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 20.1927 | 21.469 | 7.2921 | 0.94055 | 18.2259 | 19.3779 | 6.5818 | 0.94055 | 21.375 | 22.6959 | 7.6297 | 0.9418 | 38.11
Morisset 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 15.858 | 16.431 | 4.3013 | 0.96513 | 16.9459 | 17.5582 | 4.5964 | 0.96513 | 19.2999 | 19.9808 | 5.1715 | 0.96592 | 38.11
Morisset 33_11kV - summer peak demand | 28.9989 | 32.221 | 14.0448 | 0.9 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Morisset 33_11kV - winter peak demand | 10.0306 | 11.1452 | 4.8581 | 0.9 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Mortdale 33_11kV - summer peak demand | 62.0566 | 65.3228 | 20.397 | 0.95 | 44.3715 | 46.3168 | 13.2822 | 0.958 | 45.7802 | 47.7873 | 13.7039 | 0.958 | 46.2244 | 48.2697 | 13.9024 | 0.95763 | 64.25
Mortdale 33_11kV - winter peak demand | 54.2562 | 54.5288 | 5.4461 | 0.995 | 40.4936 | 41.4203 | 8.7125 | 0.97763 | 42.9792 | 43.9628 | 9.2473 | 0.97763 | 41.212 | 42.1551 | 8.8671 | 0.97763 | 70.68
Mosman 132_11kV - summer peak demand | 70.3992 | 78.2213 | 34.0959 | 0.9 | 63.0816 | 63.807 | 9.5939 | 0.98863 | 63.2069 | 63.9337 | 9.6129 | 0.98863 | 67.0878 | 67.0999 | 1.2768 | 0.99982 | 82.46
Mosman 132_11kV - winter peak demand | 91.8744 | 98.7897 | 36.3111 | 0.93 | 73.9797 | 79.4741 | 29.0367 | 0.93087 | 77.5924 | 83.355 | 30.4546 | 0.93087 | 77.3942 | 79.5486 | 18.3884 | 0.97292 | 89.05
Mt Hutton 33_11kV - summer peak demand | 20.7446 | 21.609 | 6.0505 | 0.96 | 19.1809 | 20.05 | 5.8392 | 0.95665 | 17.9358 | 18.7484 | 5.4601 | 0.95666 | 17.9911 | 20.3401 | 9.4889 | 0.88451 | 32.68
Mt Hutton 33_11kV - winter peak demand | 17.5885 | 18.3213 | 5.13 | 0.96 | 13.9849 | 14.34 | 3.1713 | 0.97524 | 14.6508 | 15.0227 | 3.3223 | 0.97524 | 12.7643 | 14.3607 | 6.5805 | 0.88884 | 34.33
Mt Thorley 66_11kV - summer peak demand | 9.9935 | 10.6314 | 3.6272 | 0.94 | 8.6653 | 9.27 | 3.2933 | 0.93477 | 9.0305 | 9.6607 | 3.4321 | 0.93477 | 8.9685 | 9.5944 | 3.4085 | 0.93476 | 20.25
Mt Thorley 66_11kV - winter peak demand | 8.5133 | 9.0567 | 3.0899 | 0.94 | 6.833 | 7.253 | 2.4323 | 0.94209 | 7.0007 | 7.431 | 2.492 | 0.94209 | 6.6689 | 7.0788 | 2.3739 | 0.94209 | 20.25
Muswellbrook 33_11kV - summer peak demand | 2.0448 | 2.13 | 0.5964 | 0.96 | 14.1023 | 14.2881 | 2.2964 | 0.987 | 14.5851 | 14.7772 | 2.375 | 0.987 | 14.5236 | 14.6789 | 2.1295 | 0.98942 | 23.82
Muswellbrook 33_11kV - winter peak demand | 2.3712 | 2.47 | 0.6916 | 0.96 | 11.524 | 11.856 | 2.7859 | 0.972 | 11.9619 | 12.3065 | 2.8918 | 0.972 | 10.5315 | 10.794 | 2.366 | 0.97568 | 23.82
Narrabeen 33_11kV - summer peak demand | 14.7599 | 15.3749 | 4.305 | 0.96 | 10.0826 | 11.2029 | 4.8832 | 0.9 | 9.9305 | 11.0339 | 4.8096 | 0.9 | 10.2787 | 11.3849 | 4.8952 | 0.90284 | 19.62
Narrabeen 33_11kV - winter peak demand | 22.3624 | 23.1256 | 5.8918 | 0.967 | 10.8794 | 11.6983 | 4.2998 | 0.93 | 11.2782 | 12.1271 | 4.4574 | 0.93 | 10.3468 | 11.1256 | 4.0893 | 0.93 | 20.25
Nelson Bay 33_11kV - summer peak demand | 52.2602 | 55.0107 | 17.1771 | 0.95 | 27.7904 | 28.503 | 6.3335 | 0.975 | 27.3772 | 28.0792 | 6.2393 | 0.975 | 24.9122 | 25.478 | 5.3394 | 0.97779 | 45.73
Nelson Bay 33_11kV - winter peak demand | 45.8589 | 48.2725 | 15.0731 | 0.95 | 35.7962 | 36.564 | 7.4539 | 0.979 | 36.2182 | 36.9951 | 7.5418 | 0.979 | 20.4544 | 20.4561 | 0.2593 | 0.99992 | 45.73
New Lambton 33_11kV - summer peak demand | 37.6864 | 38.8519 | 9.4451 | 0.97 | 20.8559 | 21.793 | 6.3219 | 0.957 | 20.7625 | 21.6954 | 6.2936 | 0.957 | 17.5189 | 18.3061 | 5.3104 | 0.957 | 22.86
New Lambton 33_11kV - winter peak demand | 27.2954 | 28.1396 | 6.8409 | 0.97 | 14.8295 | 15.241 | 3.5177 | 0.973 | 15.5763 | 16.0086 | 3.6949 | 0.973 | 10.5133 | 10.805 | 2.4939 | 0.973 | 22.86
Newcastle CBD 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 49.6194 | 50.162 | 7.3583 | 0.98918 | 46.4674 | 46.9755 | 6.8909 | 0.98918 | 51.5471 | 51.6866 | 3.7947 | 0.9973 | 45.73
Newcastle CBD 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 32.546 | 32.94 | 5.0795 | 0.98804 | 32.5685 | 32.9628 | 5.083 | 0.98804 | 35.7442 | 35.8021 | 2.0363 | 0.99838 | 45.73
Newcastle City Main 33_11kV - summer peak demand | 89.5369 | 92.3061 | 22.4401 | 0.97 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Newcastle City Main 33_11kV - winter peak demand | 57.1064 | 58.8726 | 14.3122 | 0.97 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Newdell 66_11kV - summer peak demand | 9.8121 | 10.4384 | 3.5613 | 0.94 | 8.9296 | 9.802 | 4.0424 | 0.911 | 8.9707 | 9.847 | 4.061 | 0.91101 | 4.3879 | 4.8166 | 1.9864 | 0.911 | 26.83
Newdell 66_11kV - winter peak demand | 8.656 | 9.2085 | 3.1417 | 0.94 | 8.175 | 8.734 | 3.0744 | 0.936 | 8.1713 | 8.73 | 3.073 | 0.936 | 8.424 | 9 | 3.168 | 0.936 | 28.98
Newport 33_11kV - summer peak demand | 21.1252 | 22.0055 | 6.1615 | 0.96 | 12.0031 | 13.3368 | 5.8134 | 0.9 | 11.6215 | 12.9128 | 5.6285 | 0.9 | 11.6082 | 12.898 | 5.6221 | 0.9 | 22.38
Newport 33_11kV - winter peak demand | 19.2744 | 19.9321 | 5.0782 | 0.967 | 14.7467 | 16.3852 | 7.1421 | 0.9 | 13.9817 | 15.5352 | 6.7716 | 0.9 | 14.4264 | 16.0293 | 6.987 | 0.9 | 22.38
Noraville 33_11kV - summer peak demand | 30.187 | 31.4448 | 8.8045 | 0.96 | 22.9419 | 24.4063 | 8.3268 | 0.94 | 18.9684 | 20.1792 | 6.8846 | 0.94 | 19.7097 | 20.9677 | 7.1537 | 0.94 | 34.37
Noraville 33_11kV - winter peak demand | 25.7256 | 26.5212 | 6.4474 | 0.97 | 23.2647 | 23.7395 | 4.7241 | 0.98 | 25.0823 | 25.5942 | 5.0932 | 0.98 | 24.2785 | 24.774 | 4.93 | 0.98 | 37.5
North Head 33_11kV - summer peak demand | 21.1934 | 21.4075 | 3.0199 | 0.99 | 18.6018 | 20.3291 | 8.2003 | 0.91503 | 18.6018 | 20.3291 | 8.2003 | 0.91503 | 19.1422 | 20.9197 | 8.4386 | 0.91503 | 23.38
North Head 33_11kV - winter peak demand | 28.2504 | 28.5358 | 4.0255 | 0.99 | 18.3464 | 21.2055 | 10.634 | 0.86517 | 18.3464 | 21.2055 | 10.634 | 0.86517 | 18.7585 | 21.6818 | 10.8729 | 0.86517 | 23.64
North Ryde 66_11kV - summer peak demand | 43.509 | 45.799 | 14.3007 | 0.95 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
North Ryde 66_11kV - winter peak demand | 32.602 | 34.3179 | 10.7158 | 0.95 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
North Sydney 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 35.4968 | 38.8627 | 15.8206 | 0.91339 | 0
North Sydney 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
North Sydney 33_11kV - summer peak demand | 92.1029 | 100.1119 | 39.2357 | 0.92 | 71.8719 | 78.6871 | 32.0326 | 0.91339 | 72.1004 | 78.9373 | 32.1345 | 0.91339 | 35.4968 | 38.8627 | 15.8206 | 0.91339 | 112.98
North Sydney 33_11kV - winter peak demand | 76.217 | 78.7366 | 19.759 | 0.968 | 60.4729 | 63.1973 | 18.3557 | 0.95689 | 60.6085 | 63.3391 | 18.3969 | 0.95689 | 58.8356 | 61.4862 | 17.8587 | 0.95689 | 119.69
Nulkaba 33_11kV - summer peak demand | 24.9894 | 25.7623 | 6.2629 | 0.97 | 19.5287 | 19.727 | 2.79 | 0.98995 | 19.74 | 19.9405 | 2.8202 | 0.98995 | 21.117 | 21.1421 | 1.0288 | 0.99881 | 38.11
Nulkaba 33_11kV - winter peak demand | 17.4921 | 18.0331 | 4.3839 | 0.97 | 11.946 | 12.273 | 2.8142 | 0.97336 | 12.5893 | 12.9339 | 2.9657 | 0.97336 | 13.4718 | 13.8223 | 3.0932 | 0.97464 | 38.11
Paddington 33_11kV - summer peak demand | 41.3281 | 42.6063 | 10.3578 | 0.97 | 27.9709 | 29.5505 | 9.5323 | 0.94655 | 27.2912 | 28.8324 | 9.3006 | 0.94655 | 27.0124 | 28.5379 | 9.2056 | 0.94654 | 66.47
Paddington 33_11kV - winter peak demand | 33.5981 | 37.4979 | 16.6511 | 0.896 | 30.5037 | 31.4177 | 7.5229 | 0.97091 | 31.4644 | 32.4071 | 7.7598 | 0.97091 | 30.7203 | 31.6408 | 7.5763 | 0.97091 | 69.83
Padstow 33_11kV - summer peak demand | 46.1615 | 46.6278 | 6.5777 | 0.99 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Padstow 33_11kV - winter peak demand | 30.4601 | 30.4906 | 1.3632 | 0.999 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Paxton 33_11kV - summer peak demand | 7.1908 | 7.4132 | 1.8022 | 0.97 | 5.2691 | 5.529 | 1.6751 | 0.95299 | 5.043 | 5.2917 | 1.6032 | 0.953 | 5.092 | 5.3432 | 1.6188 | 0.95299 | 0
Paxton 33_11kV - winter peak demand | 5.0389 | 5.1947 | 1.2629 | 0.97 | 3.8166 | 3.8905 | 0.7548 | 0.98101 | 3.9534 | 4.03 | 0.7818 | 0.98099 | 4.0151 | 4.0928 | 0.794 | 0.98102 | 0
Peats Ridge 33_11kV - summer peak demand | 14.423 | 15.3927 | 5.3771 | 0.937 | 10.205 | 10.5551 | 2.696 | 0.96683 | 10.2824 | 10.6352 | 2.7165 | 0.96683 | 12.2379 | 12.6578 | 3.2331 | 0.96683 | 15.24
Peats Ridge 33_11kV - winter peak demand | 12.552 | 12.8212 | 2.6137 | 0.979 | 8.4738 | 9.2595 | 3.7327 | 0.91515 | 8.8625 | 9.6843 | 3.9039 | 0.91514 | 9.5471 | 10.4323 | 4.2054 | 0.91515 | 15.24
Pelican 33_11kV - summer peak demand | 13.0297 | 13.4326 | 3.2655 | 0.97 | 11.2349 | 11.952 | 4.0777 | 0.94 | 9.5374 | 10.1462 | 3.4616 | 0.94 | 11.2454 | 12.0105 | 4.2181 | 0.9363 | 22.86
Pelican 33_11kV - winter peak demand | 14.5038 | 14.9524 | 3.635 | 0.97 | 9.72 | 10.083 | 2.6811 | 0.964 | 9.8803 | 10.2492 | 2.7253 | 0.96401 | 9.3134 | 10.8055 | 5.4789 | 0.86191 | 22.86
Pennant Hills 132_11kV - summer peak demand | 115.9393 | 128.8214 | 56.1519 | 0.9 | 76.2338 | 80.4209 | 25.6109 | 0.94794 | 70.274 | 74.1337 | 23.6087 | 0.94794 | 77.3767 | 81.6265 | 25.9948 | 0.94794 | 106.92
Pennant Hills 132_11kV - winter peak demand | 101.6072 | 106.9549 | 33.3967 | 0.95 | 62.399 | 69.3323 | 30.2212 | 0.9 | 65.2023 | 72.4469 | 31.5789 | 0.9 | 60.6269 | 67.3632 | 29.3629 | 0.9 | 114.32
Port Botany 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 2.3757 | 2.8198 | 1.519 | 0.84251 | 2.3757 | 2.8198 | 1.519 | 0.84251 | 25.1415 | 27.9334 | 12.1728 | 0.90005 | 59.16
Port Botany 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 2.1028 | 2.4959 | 1.3445 | 0.8425 | 2.1028 | 2.4959 | 1.3445 | 0.8425 | 2.1028 | 2.4959 | 1.3445 | 0.8425 | 59.16
Potts Hill 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 60.9673 | 65.7558 | 24.6336 | 0.92718 | 0
Potts Hill 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Punchbowl 33_11kV - summer peak demand | 73.9179 | 74.6646 | 10.5327 | 0.99 | 49.5847 | 55.3286 | 24.5482 | 0.89619 | 46.5074 | 51.8949 | 23.0247 | 0.89618 | 34.7957 | 38.8264 | 17.2265 | 0.89619 | 75.66
Punchbowl 33_11kV - winter peak demand | 62.0446 | 62.1067 | 2.7768 | 0.999 | 45.9669 | 47.9934 | 13.7988 | 0.95778 | 47.9636 | 50.078 | 14.3981 | 0.95778 | 30.8774 | 32.2386 | 9.2691 | 0.95778 | 77.52
Pymble 33_11kV - summer peak demand | 36.2134 | 40.9191 | 19.0516 | 0.885 | 30.9439 | 33.8183 | 13.6438 | 0.915 | 29.5836 | 32.3316 | 13.0441 | 0.91501 | 31.8638 | 34.8237 | 14.0495 | 0.915 | 38.9
Pymble 33_11kV - winter peak demand | 29.0505 | 31.2035 | 11.3899 | 0.931 | 30.006 | 32.7513 | 13.126 | 0.91618 | 31.7047 | 34.6055 | 13.8691 | 0.91618 | 31.2365 | 34.0945 | 13.6643 | 0.91617 | 40.89
Randwick 33_11kV - summer peak demand | 43.2112 | 45.8718 | 15.3952 | 0.942 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Randwick 33_11kV - winter peak demand | 45.8427 | 48.0531 | 14.4066 | 0.954 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Rathmines 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 13.6157 | 14.5151 | 5.0301 | 0.93804 | 0
Rathmines 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 12.407 | 13.0594 | 4.076 | 0.95004 | 0
Rathmines 132_11kV Temp - summer peak demand | 0 | 0 | 0 | #DIV/0! | 15.5896 | 16.62 | 5.7611 | 0.938 | 13.5535 | 14.4494 | 5.0087 | 0.938 | 0 | 0 | 0 | #DIV/0! | 0
Rathmines 132_11kV Temp - winter peak demand | 0 | 0 | 0 | #DIV/0! | 11.6499 | 12.263 | 3.8291 | 0.95 | 12.4083 | 13.0614 | 4.0784 | 0.95 | 0 | 0 | 0 | #DIV/0! | 0
Raymond Terr NEW 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 20.0026 | 21.096 | 6.7036 | 0.94817 | 20.7482 | 21.8824 | 6.9535 | 0.94817 | 21.8605 | 22.7571 | 6.3251 | 0.9606 | 38.11
Raymond Terr NEW 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 15.977 | 16.471 | 4.0037 | 0.97001 | 16.5095 | 17.02 | 4.1371 | 0.97001 | 9.8857 | 10.1704 | 2.3896 | 0.97201 | 38.11
Raymond Terrace 33_11kV - summer peak demand | 45.1135 | 47.4878 | 14.8281 | 0.95 | 14.5961 | 15.032 | 3.5938 | 0.971 | 16.6242 | 17.1207 | 4.0932 | 0.971 | 0 | 0 | 0 | #DIV/0! | 35.44
Raymond Terrace 33_11kV - winter peak demand | 35.9099 | 37.7999 | 11.803 | 0.95 | 12.9175 | 13.276 | 3.0642 | 0.973 | 12.9409 | 13.3 | 3.0697 | 0.973 | 0 | 0 | 0 | #DIV/0! | 35.44
Revesby 132_11kV - summer peak demand | 54.2242 | 62.3267 | 30.7303 | 0.87 | 40.921 | 43.4398 | 14.577 | 0.94202 | 36.6422 | 38.8976 | 13.0528 | 0.94202 | 41.0342 | 43.56 | 14.6173 | 0.94202 | 44.93
Revesby 132_11kV - winter peak demand | 50.3717 | 54.1632 | 19.9082 | 0.93 | 34.6376 | 38.4862 | 16.7757 | 0.9 | 35.7772 | 39.7525 | 17.3277 | 0.9 | 35.4917 | 39.4352 | 17.1894 | 0.9 | 47.8
Riverwood 33_11kV - summer peak demand | 33.7464 | 35.5225 | 11.0919 | 0.95 | 24.8265 | 28.4836 | 13.9627 | 0.87161 | 23.0583 | 26.4549 | 12.9683 | 0.87161 | 24.8768 | 28.5413 | 13.991 | 0.87161 | 42.81
Riverwood 33_11kV - winter peak demand | 28.0814 | 28.2225 | 2.8187 | 0.995 | 22.2194 | 23.187 | 6.6282 | 0.95827 | 24.1604 | 25.2125 | 7.2073 | 0.95827 | 23.6249 | 24.6536 | 7.0475 | 0.95827 | 42.81
RNS Hospital 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 12.3077 | 12.3842 | 1.3738 | 0.99382 | 12.2226 | 12.2985 | 1.3643 | 0.99383 | 17.8064 | 17.917 | 1.9876 | 0.99383 | 53.54
RNS Hospital 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 6.5674 | 7.2971 | 3.1807 | 0.9 | 6.6709 | 7.4121 | 3.2309 | 0.9 | 7.1916 | 7.9906 | 3.483 | 0.90001 | 53.54
Rockdale 33_11kV - summer peak demand | 23.7534 | 25.0036 | 7.8074 | 0.95 | 13.9998 | 15.604 | 6.8915 | 0.89719 | 14.0277 | 15.6351 | 6.9052 | 0.89719 | 17.6659 | 19.6279 | 8.554 | 0.90004 | 27.09
Rockdale 33_11kV - winter peak demand | 25.3112 | 25.4384 | 2.5407 | 0.995 | 11.899 | 12.8414 | 4.8287 | 0.92661 | 12.3677 | 13.3473 | 5.0189 | 0.92661 | 15.5482 | 16.7477 | 6.2242 | 0.92838 | 27.09
Rose Bay 33_11kV - summer peak demand | 43.4191 | 44.762 | 10.8819 | 0.97 | 31.2479 | 33.9517 | 13.2773 | 0.92036 | 30.4552 | 33.0904 | 12.9405 | 0.92036 | 31.5179 | 34.245 | 13.392 | 0.92037 | 48.54
Rose Bay 33_11kV - winter peak demand | 39.751 | 44.365 | 19.7005 | 0.896 | 41.3094 | 42.7349 | 10.9455 | 0.96664 | 42.3813 | 43.8437 | 11.2295 | 0.96665 | 41.8387 | 43.2825 | 11.0857 | 0.96664 | 50.36
Rothbury 132_11kV - summer peak demand | 19.0785 | 20.0827 | 6.2708 | 0.95 | 10.0633 | 10.396 | 2.6089 | 0.968 | 10.099 | 10.4329 | 2.6181 | 0.968 | 14.7529 | 15.3122 | 4.1009 | 0.96347 | 38.11
Rothbury 132_11kV - winter peak demand | 10.9816 | 11.5596 | 3.6095 | 0.95 | 6.122 | 6.122 | 0 | 1 | 5.9326 | 5.9326 | 0 | 1 | 8.425 | 8.4409 | 0.5175 | 0.99812 | 38.11
Rouchel 33_11kV - summer peak demand | 2.197 | 2.2885 | 0.64079 | 0.96 | 0.8684 | 0.947 | 0.3777 | 0.917 | 0.9695 | 1.0572 | 0.4217 | 0.91705 | 1.0637 | 1.16 | 0.4627 | 0.91698 | 0
Rouchel 33_11kV - winter peak demand | 1.5393 | 1.6034 | 0.44896 | 0.96 | 0.8244 | 0.913 | 0.3923 | 0.90296 | 0.8217 | 0.91 | 0.391 | 0.90297 | 0.7585 | 0.84 | 0.3609 | 0.90298 | 0
Rutherford 33_11kV - summer peak demand | 30.4785 | 31.4211 | 7.6386 | 0.97 | 28.1591 | 29.9848 | 10.3032 | 0.93911 | 27.3668 | 29.1412 | 10.0133 | 0.93911 | 28.6311 | 28.6792 | 1.6601 | 0.99832 | 38.11
Rutherford 33_11kV - winter peak demand | 24.117 | 24.8629 | 6.0443 | 0.97 | 20.88 | 21.154 | 3.3937 | 0.98705 | 21.1148 | 21.3919 | 3.4319 | 0.98705 | 23.2173 | 23.2484 | 1.2019 | 0.99866 | 38.11
Salt Ash 33_11kV - summer peak demand | 2.8295 | 2.9784 | 0.93001 | 0.95 | 2.2763 | 2.653 | 1.3627 | 0.85801 | 2.077 | 2.4207 | 1.2434 | 0.85802 | 0 | 0 | 0 | #DIV/0! | 0
Salt Ash 33_11kV - winter peak demand | 2.2342 | 2.3517 | 0.73433 | 0.95 | 5.4967 | 5.655 | 1.3288 | 0.97201 | 1.8518 | 1.9051 | 0.4477 | 0.97202 | 0 | 0 | 0 | #DIV/0! | 0
Sans Souci 33_11kV - summer peak demand | 31.4838 | 33.1409 | 10.3482 | 0.95 | 14.3256 | 15.5278 | 5.9908 | 0.92258 | 14.0591 | 15.2389 | 5.8793 | 0.92258 | 14.4228 | 15.6332 | 6.0314 | 0.92258 | 26.85
Sans Souci 33_11kV - winter peak demand | 26.1214 | 26.2527 | 2.622 | 0.995 | 14.4256 | 15.1849 | 4.7415 | 0.95 | 15.2424 | 16.0446 | 5.0099 | 0.95 | 14.9566 | 15.7438 | 4.916 | 0.95 | 26.85
Scone 33_11kV - summer peak demand | 19.9202 | 20.7502 | 5.8101 | 0.96 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Scone 33_11kV - winter peak demand | 13.7978 | 14.3727 | 4.0243 | 0.96 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Scone 66_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 15.9105 | 16.167 | 2.8684 | 0.98413 | 16.3714 | 16.6354 | 2.9515 | 0.98413 | 16.0916 | 16.2193 | 2.0315 | 0.99213 | 38
Scone 66_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 12.172 | 12.443 | 2.5828 | 0.97822 | 12.6083 | 12.8891 | 2.6753 | 0.97821 | 12.4676 | 12.4754 | 0.4415 | 0.99937 | 38
Sefton 132_11kV - summer peak demand | 77.5284 | 91.2099 | 48.0478 | 0.85 | 62.8249 | 69.3513 | 29.3707 | 0.90589 | 61.0207 | 67.3596 | 28.5272 | 0.90589 | 41.1065 | 45.3768 | 19.2173 | 0.90589 | 94.58
Sefton 132_11kV - winter peak demand | 64.9566 | 65.6127 | 9.2558 | 0.99 | 56.0974 | 59.2344 | 19.0209 | 0.94704 | 57.6049 | 60.8262 | 19.5321 | 0.94704 | 56.4691 | 59.6269 | 19.147 | 0.94704 | 99.68
Shortland 33_11kV - summer peak demand | 30.3581 | 31.623 | 8.8544 | 0.96 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Shortland 33_11kV - winter peak demand | 28.7191 | 29.9157 | 8.3764 | 0.96 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Singleton 66_11kV - summer peak demand | 27.4563 | 29.2088 | 9.9653 | 0.94 | 18.4694 | 20.296 | 8.4149 | 0.91 | 18.6886 | 20.5369 | 8.5148 | 0.91 | 19.9137 | 21.8832 | 9.073 | 0.91 | 22.86
Singleton 66_11kV - winter peak demand | 23.6642 | 25.1747 | 8.589 | 0.94 | 12.7703 | 13.485 | 4.3318 | 0.947 | 12.7887 | 13.5044 | 4.3381 | 0.947 | 11.74 | 12.3971 | 3.9824 | 0.947 | 22.86
Singleton North 66_11kV - summer peak demand | 22.0899 | 23.4999 | 8.0176 | 0.94 | 16.4179 | 17.6 | 6.3413 | 0.93284 | 17.0436 | 18.2707 | 6.583 | 0.93284 | 17.9906 | 19.286 | 6.9488 | 0.93283 | 38.11
Singleton North 66_11kV - winter peak demand | 14.819 | 15.7649 | 5.3786 | 0.94 | 11.9001 | 12.4 | 3.4852 | 0.95969 | 12.538 | 13.0647 | 3.6721 | 0.95969 | 13.7943 | 14.3837 | 4.0751 | 0.95902 | 38.11
Somersby 132_11kV - summer peak demand | 21.439 | 26.1451 | 14.9645 | 0.82 | 16.0001 | 17.2045 | 6.3237 | 0.93 | 15.5258 | 16.6944 | 6.1362 | 0.93 | 17.3633 | 18.6702 | 6.8624 | 0.93 | 51.9
Somersby 132_11kV - winter peak demand | 19.1832 | 21.3147 | 9.2909 | 0.9 | 15.0873 | 16.309 | 6.1932 | 0.92509 | 15.5989 | 16.862 | 6.4032 | 0.92509 | 18.1177 | 19.5848 | 7.4372 | 0.92509 | 56.07
St Ives 33_11kV - summer peak demand | 61.1354 | 69.0795 | 32.1628 | 0.885 | 42.4356 | 47.4218 | 21.1671 | 0.89485 | 40.715 | 45.499 | 20.3088 | 0.89485 | 42.0063 | 46.9258 | 20.9166 | 0.89516 | 58.38
St Ives 33_11kV - winter peak demand | 69.8664 | 75.0445 | 27.3927 | 0.931 | 43.4124 | 46.1834 | 15.7566 | 0.94 | 46.3776 | 49.3378 | 16.8328 | 0.94 | 45.5313 | 48.4615 | 16.5959 | 0.93954 | 61.08
St Peters 132_11kV - summer peak demand | 69.1122 | 77.6541 | 35.4072 | 0.89 | 61.6328 | 66.0552 | 23.7632 | 0.93305 | 62.9129 | 67.4272 | 24.2567 | 0.93305 | 67.4054 | 72.3946 | 26.4102 | 0.93108 | 87.45
St Peters 132_11kV - winter peak demand | 59.4475 | 63.922 | 23.4951 | 0.93 | 51.9411 | 53.9187 | 14.4692 | 0.96332 | 52.5638 | 54.5651 | 14.6426 | 0.96332 | 54.207 | 56.2872 | 15.1608 | 0.96304 | 87.45
Stockton 33_11kV - summer peak demand | 8.6613 | 9.1171 | 2.8468 | 0.95 | 7.8269 | 8.17 | 2.3429 | 0.958 | 6.9816 | 7.2877 | 2.0899 | 0.958 | 7.3441 | 7.6661 | 2.1984 | 0.958 | 20.01
Stockton 33_11kV - winter peak demand | 6.1085 | 6.43 | 2.0078 | 0.95 | 5.4583 | 5.604 | 1.2696 | 0.974 | 5.5817 | 5.7307 | 1.2983 | 0.974 | 5.3569 | 5.4999 | 1.246 | 0.974 | 20.01
Surry Hills 33_11kV - summer peak demand | 55.2753 | 56.9849 | 13.8533 | 0.97 | 40.5996 | 43.6113 | 15.9254 | 0.93094 | 40.9193 | 43.9547 | 16.0508 | 0.93094 | 52.3244 | 56.3206 | 20.8367 | 0.92905 | 77.75
Surry Hills 33_11kV - winter peak demand | 55.8225 | 62.3019 | 27.6654 | 0.896 | 34.0662 | 35.8591 | 11.197 | 0.95 | 34.302 | 36.1073 | 11.2745 | 0.95 | 34.5421 | 36.3601 | 11.3534 | 0.95 | 77.75
Swansea 33_11kV - summer peak demand | 15.9375 | 16.4304 | 3.9943 | 0.97 | 13.3371 | 13.554 | 2.4149 | 0.984 | 11.5852 | 11.7736 | 2.0977 | 0.984 | 11.316 | 12.7017 | 5.7689 | 0.8909 | 16.42
Swansea 33_11kV - winter peak demand | 19.222 | 19.8165 | 4.8175 | 0.97 | 11.5463 | 11.794 | 2.4043 | 0.979 | 11.6464 | 11.8962 | 2.4252 | 0.979 | 10.6833 | 10.9245 | 2.2828 | 0.97792 | 16.42
Tanilba Bay 33_11kV - summer peak demand | 11.4706 | 12.0744 | 3.7702 | 0.95 | 7.7334 | 8.5927 | 3.7455 | 0.9 | 6.3696 | 7.0774 | 3.085 | 0.89999 | 8.7541 | 9.8867 | 4.5948 | 0.88544 | 18.73
Tanilba Bay 33_11kV - winter peak demand | 9.4747 | 9.9734 | 3.1142 | 0.95 | 6.372 | 7.08 | 3.0861 | 0.9 | 6.5265 | 7.2516 | 3.1609 | 0.90001 | 7.9168 | 8.5171 | 3.1407 | 0.92952 | 18.75
Tarro 33_11kV - summer peak demand | 38.7661 | 42.6001 | 17.6623 | 0.91 | 22.4999 | 24.617 | 9.9875 | 0.914 | 23.4875 | 25.6974 | 10.4258 | 0.914 | 22.0515 | 24.1264 | 9.7884 | 0.914 | 22.86
Tarro 33_11kV - winter peak demand | 16.7241 | 18.3781 | 7.6197 | 0.91 | 17.4977 | 18.978 | 7.3481 | 0.922 | 17.8425 | 19.3519 | 7.4929 | 0.922 | 18.312 | 19.8612 | 7.69 | 0.922 | 22.86
Telarah 33_11kV - summer peak demand | 18.3519 | 18.9195 | 4.5994 | 0.97 | 17.2234 | 18.149 | 5.7219 | 0.949 | 18.1404 | 19.1153 | 6.0266 | 0.949 | 15.2857 | 16.0894 | 5.0216 | 0.95005 | 15.24
Telarah 33_11kV - winter peak demand | 9.2138 | 9.4988 | 2.3092 | 0.97 | 9.9565 | 10.139 | 1.9151 | 0.982 | 10.5785 | 10.7724 | 2.0347 | 0.982 | 10.3411 | 10.7123 | 2.7957 | 0.96535 | 15.24
Terrey Hills 33_11kV - summer peak demand | 19.1851 | 19.9844 | 5.5956 | 0.96 | 15.7054 | 16.7091 | 5.704 | 0.93993 | 15.0492 | 16.011 | 5.4657 | 0.93993 | 15.6956 | 16.6987 | 5.7004 | 0.93993 | 30.48
Terrey Hills 33_11kV - winter peak demand | 16.3276 | 16.8848 | 4.3019 | 0.967 | 12.5252 | 13.1844 | 4.1168 | 0.95 | 12.893 | 13.5716 | 4.2377 | 0.95 | 12.9244 | 13.6046 | 4.248 | 0.95 | 30.54
Thornton 33_11kV - summer peak demand | 41.3837 | 45.4766 | 18.855 | 0.91 | 31.9288 | 32.1988 | 4.1613 | 0.99161 | 34.0243 | 34.3121 | 4.4344 | 0.99161 | 36.4652 | 37.0446 | 6.5266 | 0.98436 | 72.59
Thornton 33_11kV - winter peak demand | 33.2963 | 36.5893 | 15.1702 | 0.91 | 20.3244 | 21.2055 | 6.0493 | 0.95845 | 21.1537 | 22.0708 | 6.2961 | 0.95845 | 19.9261 | 19.9465 | 0.9008 | 0.99898 | 72.59
Tomago 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 3.8002 | 4.1 | 1.5391 | 0.92688 | 3.8002 | 4.1 | 1.5391 | 0.92688 | 19.773 | 20.8295 | 6.5495 | 0.94928 | 38
Tomago 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 2.2785 | 2.61 | 1.2729 | 0.87299 | 2.4047 | 2.7545 | 1.3434 | 0.87301 | 18.4519 | 19.2581 | 5.5138 | 0.95814 | 38
Tomalpin 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 1.8078 | 1.8261 | 0.2576 | 0.98998 | 1.8117 | 1.83 | 0.2582 | 0.99 | 1.782 | 1.8 | 0.2539 | 0.99 | 0
Tomalpin 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 1.5149 | 1.615 | 0.5598 | 0.93802 | 1.5196 | 1.62 | 0.5615 | 0.93802 | 1.5008 | 1.6 | 0.5546 | 0.938 | 0
Tomaree 33_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 15.3015 | 0 | 0 | 16.2206 | 16.2973 | 1.5788 | 0.99529 | 0
Tomaree 33_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 14.1013 | 14.4037 | 2.9363 | 0.97901 | 0
Top Ryde 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 52.8763 | 55.3477 | 16.3542 | 0.95535 | 51.0398 | 53.4253 | 15.7862 | 0.95535 | 53.7366 | 56.2482 | 16.6203 | 0.95535 | 61.25
Top Ryde 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 42.4991 | 43.3255 | 8.4217 | 0.98093 | 43.219 | 44.0594 | 8.5644 | 0.98093 | 42.3896 | 43.2139 | 8.4 | 0.98093 | 61.25
Toronto 33_11kV - summer peak demand | 44.8015 | 47.6612 | 16.2608 | 0.94 | 17.5909 | 18.595 | 6.0279 | 0.946 | 16.0116 | 16.9256 | 5.4867 | 0.946 | 17.2289 | 18.2124 | 5.9039 | 0.946 | 30.48
Toronto 33_11kV - winter peak demand | 36.5392 | 38.8715 | 13.262 | 0.94 | 12.7017 | 13.108 | 3.2385 | 0.969 | 13.0753 | 13.4936 | 3.3337 | 0.969 | 13.6871 | 14.125 | 3.4897 | 0.969 | 30.54
Turramurra 33_11kV - summer peak demand | 34.6554 | 39.1587 | 18.2319 | 0.885 | 33.3319 | 34.1231 | 7.3058 | 0.97681 | 30.1228 | 30.8379 | 6.6024 | 0.97681 | 33.8442 | 34.6476 | 7.4181 | 0.97681 | 43.31
Turramurra 33_11kV - winter peak demand | 38.7381 | 41.6091 | 15.1881 | 0.931 | 30.7732 | 31.6272 | 7.3 | 0.973 | 33.017 | 33.9333 | 7.8323 | 0.973 | 34.5352 | 35.533 | 8.3613 | 0.97192 | 44.75
Umina 66_11kV - summer peak demand | 38.3045 | 42.5606 | 18.5517 | 0.9 | 30.7665 | 34.8471 | 16.3629 | 0.8829 | 24.4266 | 27.6663 | 12.9911 | 0.8829 | 24.5223 | 27.7748 | 13.042 | 0.8829 | 58.82
Umina 66_11kV - winter peak demand | 40.405 | 41.0203 | 7.0782 | 0.985 | 24.2166 | 26.083 | 9.689 | 0.92844 | 25.4475 | 27.4087 | 10.1815 | 0.92845 | 25.5491 | 27.5182 | 10.2222 | 0.92844 | 61.03
Vales Point 33_11kV - summer peak demand | 6.6724 | 6.9504 | 1.9461 | 0.96 | 7.7487 | 9.2786 | 5.1039 | 0.83512 | 7.7487 | 9.2786 | 5.1039 | 0.83512 | 8.0351 | 9.6215 | 5.2925 | 0.83512 | 15.24
Vales Point 33_11kV - winter peak demand | 7.4774 | 7.7087 | 1.874 | 0.97 | 8.3 | 10.3265 | 6.2 | 0.80376 | 8.3 | 10.3265 | 6.1959 | 0.80376 | 8.2 | 10.1931 | 6.1159 | 0.80447 | 15.24
Wallalong 33_11kV - summer peak demand | 5.0229 | 5.5197 | 2.2885 | 0.91 | 4.0408 | 4.4897 | 1.957 | 0.90002 | 4.1382 | 4.598 | 2.0042 | 0.9 | 4.149 | 4.61 | 2.0095 | 0.9 | 0
Wallalong 33_11kV - winter peak demand | 2.3277 | 2.558 | 1.0605 | 0.91 | 2.5332 | 2.8147 | 1.2269 | 0.89999 | 2.735 | 3.0389 | 1.3246 | 0.9 | 2.6784 | 2.976 | 1.2972 | 0.9 | 0
Wallsend 33_11kV - summer peak demand | 21.7683 | 22.6754 | 6.3491 | 0.96 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Wallsend 33_11kV - winter peak demand | 15.4374 | 16.0807 | 4.5026 | 0.96 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Wamberal 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 13.0405 | 14.4895 | 6.3158 | 0.9 | 10.3739 | 11.5265 | 5.0243 | 0.9 | 10.4199 | 11.5777 | 5.0466 | 0.9 | 34.4
Wamberal 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 12.7062 | 14.1179 | 6.1539 | 0.90001 | 13.6167 | 15.1297 | 6.5949 | 0.9 | 13.528 | 15.0311 | 6.5519 | 0.9 | 36.9
Wamberal 66_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 6.8246 | 7.5829 | 3.3053 | 0.9 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 34.39
Wamberal 66_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Waverley 132_11kV - summer peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 10.4823 | 11.1212 | 3.7151 | 0.94255 | 0
Waverley 132_11kV - winter peak demand | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0
Waverley 33_11kV - summer peak demand | 32.6643 | 33.6745 | 8.1864 | 0.97 | 21.406 | 22.7107 | 7.5865 | 0.94255 | 21.4289 | 22.7349 | 7.5946 | 0.94256 | 10.4823 | 11.1212 | 3.7151 | 0.94255 | 51.73
Waverley 33_11kV - winter peak demand | 37.0613 | 41.363 | 18.3674 | 0.896 | 27.6435 | 28.3693 | 6.3757 | 0.97442 | 29.142 | 29.907 | 6.7213 | 0.97442 | 28.507 | 29.2554 | 6.5748 | 0.97442 | 55.44
West Gosford 132_11kV - summer peak demand | 62.5037 | 63.135 | 8.9063 | 0.99 | 46.1091 | 51.2323 | 22.3317 | 0.9 | 40.7649 | 45.2944 | 19.7434 | 0.9 | 47.1134 | 53.7688 | 25.9115 | 0.87622 | 65.01
West Gosford 132_11kV - winter peak demand | 45.7447 | 46.6783 | 9.2889 | 0.98 | 37.5164 | 38.6767 | 9.4025 | 0.97 | 39.8879 | 41.1216 | 9.9969 | 0.97 | 41.6131 | 41.6376 | 1.4293 | 0.99941 | 65.01
Williamtown 33_11kV - summer peak demand | 22.7241 | 23.9201 | 7.469 | 0.95 | 15.1379 | 16.173 | 5.6929 | 0.936 | 14.7871 | 15.7982 | 5.561 | 0.936 | 2.8699 | 3.0661 | 1.0793 | 0.93601 | 24.75
Williamtown 33_11kV - winter peak demand | 9.7988 | 10.3145 | 3.2207 | 0.95 | 11.3436 | 11.755 | 3.0827 | 0.965 | 12.0679 | 12.5056 | 3.2796 | 0.965 | 11.6534 | 12.0761 | 3.167 | 0.965 | 25.64
Woy Woy 66_11kV - summer peak demand | 35.97 | 39.9667 | 17.4211 | 0.9 | 28.5267 | 31.0938 | 12.3713 | 0.91744 | 23.8178 | 25.9611 | 10.3291 | 0.91744 | 17.6813 | 19.2724 | 7.6679 | 0.91744 | 30.75
Woy Woy 66_11kV - winter peak demand | 34.7645 | 35.2939 | 6.0901 | 0.985 | 26.1208 | 26.6545 | 5.3073 | 0.97998 | 27.3104 | 27.8684 | 5.549 | 0.97998 | 17.8111 | 18.1665 | 3.5759 | 0.98044 | 32.66
Wyong 132_11kV - summer peak demand | 39.8265 | 45.7776 | 22.5707 | 0.87 | 34.0279 | 35.8188 | 11.1844 | 0.95 | 29.152 | 30.6863 | 9.5818 | 0.95 | 33.8983 | 35.6824 | 11.1418 | 0.95 | 54.01
Wyong 132_11kV - winter peak demand | 33.5745 | 35.7175 | 12.1859 | 0.94 | 29.8653 | 30.7889 | 7.485 | 0.97 | 31.1189 | 32.0814 | 7.7992 | 0.97 | 33.0401 | 34.062 | 8.2807 | 0.97 | 58.82
Zetland 132_11kV - summer peak demand | 90.4226 | 102.753 | 48.805 | 0.88 | 69.2405 | 70.7231 | 14.4052 | 0.97904 | 68.8986 | 70.3739 | 14.3341 | 0.97904 | 59.9391 | 60.6215 | 9.0704 | 0.98874 | 83.6
Zetland 132_11kV - winter peak demand | 80.3588 | 87.3465 | 34.2327 | 0.92 | 55.8032 | 56.5289 | 9.029 | 0.98716 | 55.9728 | 56.7008 | 9.0564 | 0.98716 | 53.8834 | 54.371 | 7.265 | 0.99103 | 90.31
Contents

## 3. Outcomes customer service
Ausgrid
Customer Service
2012-13
This information is used to monitor the service performance of the DNSP, and assist the AER understand service outcomes for customers. The information will inform the AER’s assessment of future service improvement expenditure proposals by the DNSP. The information may be used in performance reports.
Table 1: Quality of supply
2012-13
Over voltage events - due to high voltage injection
Customers receiving over-voltage - due to high voltage injection
Over voltage events - due to lightning
Customers receiving over-voltage - due to lightning
Over voltage events - due to voltage regulation or other cause
Customers receiving over-voltage - due to voltage regulation or other cause
Voltage variations - steady state (zone sub)
Voltage variations - one minute (zone sub)
Voltage variations - 10 seconds (zone sub) Min<0.7
Voltage variations - 10 seconds (zone sub) Min<0.8
Voltage variations - 10 seconds (zone sub) Min<0.9
Voltage variations - steady state (feeder)
Voltage variations - % zone subs monitored
Voltage variations - % feeders monitored
Customers - quality of supply improvement
Table 2: Complaints - technical quality of supply
2012-13
Complaints - technical quality of supply - number | 225
Complaints by category (%)
Low voltage supply
Voltage dips
Voltage swell
Voltage spike (impulsive transient)
Waveform distortion
TV or radio interference
Noise from appliances
Other
Complaints by Likely Cause (%)
Network equipment faulty
Network interference by NSP equipment
Network interference by another customer
Network limitation
Customer internal problem
No problem identified
Environmental
Other
Table 3: Customer service
2012-13
Timely provision of services
Connections made | 11476
Connections not made on agreed date | 0
Timely repair of faulty streetlights
Streetlights - average monthly number "out" | 1875.2
Streetlights - not repaired by "fix by" date | 4940
Streetlights - average number of days to repair | 5.8
Total streetlights | 248449
Call Centre Performance (number, unless stated)
Calls to call centre fault line | 464893
Calls to fault line not answered within 30 seconds | 123445
Calls to fault line - average waiting time before call answered | 28
Calls abandoned - percentage | 6.4
Call centre - number of overload events | 0
Customer complaints (number)
Complaint - reliability of supply
Complaint - technical quality of supply
Complaint - administrative process or customer service
Complaint - connection or augmentation
Complaint - other
Total complaints
Contents

## 4. General information
Ausgrid
General information
2012-13
The information will enable the AER to better understand the network and service performance outcomes reported by the DNSP. Network characteristics will be used to normalise other information, to assist in any benchmarking or other comparisons between DNSP financial and service performance outcomes.
Table 1: Metered supply points
| Total no. | By type of customer |  | By supply voltage
Number of metered supply points |  | Domestic | Non-domestic | Subtransmission | HV | LV
CBD | 30247 | 12359 | 17888 | 0 | 33 | 30214
Urban | 1378599 | 1228935 | 149664 | 37 | 226 | 1378336
Rural Short | 222511 | 203260 | 19262 | 18 | 32 | 222461
Rural Long | 2611 | 2130 | 470 | 0 | 0 | 2611
Total | 1633968 | 1446684 | 187284 | 55 | 291 | 1633622
Table 2: Energy delivered
| Total GWh | By type of customer |  | By supply voltage
Energy delivered (GWh) |  | Domestic | Non-domestic | Subtransmission | HV | LV
CBD | 0
Urban | 0
Rural Short | 0
Rural Long | 0
Total | 26316 | 0 | 0 | 0 | 0 | 0
Table 3: Line length
Note: where a line supplies more than one feeder type, the line length should be proportionately allocated according to the number of feeders in each category. For example if a line supplied one each of a CBD and Urban feeder, 50% of the line length would be allocated to CBD and 50% to urban.
| Total km | Underground lines |  |  | Overhead lines
Line Length (km) |  | Subtransmission | HV | LV | Subtransmission | HV | LV
CBD | 287.87 | NA | 0 | NA | NA | 287.87 | NA
Urban | 8714.83 | NA | 2293.67 | NA | NA | 6421.16 | NA
Rural Short | 7780.99 | NA | 6672.09 | NA | NA | 1108.9 | NA
Rural Long | 1156.94 | NA | 1151.98 | NA | NA | 4.96 | NA
Total | 40962.2142 | 2894.0147 | 10117.74 | 13060.4733 | 1428.4084 | 7822.89 | 5638.6879
Table 4: Customer numbers
| Total no. | By supply voltage
Customer numbers |  | Subtransmission | HV | LV - residential | LV - non-residential
Total customer numbers beginning of period | 1627948 | 114 | 259 | 1442154.5435 | 185420.4565
Total customer numbers end of period | 1642353 | 117 | 264 | 1454329.8647 | 187642.1353
Controlled load customers | 510847 |  |  | 504866 | 5981
Total new customer connections | 24149
Customer disconnections | 77583
Table 5: Number and capacity of transformers
Number & total capacity of transformers | Total no. | Capacity (MVA)
Distribution | 32579 | 14235
Zone substation | 496 | 14296
Table 6: Unmetered supply points
Number of unmetered supply points
CBD | 4
Urban | 96
Rural Short | 17
Rural Long | 0
Total | 117
Table 7: Poles and substations
Number of poles and substations
Subtransmission poles | 29042
Distribution poles | 420182
Subtransmission and zone substations | 221
Distribution substations | 30765
Table 8: Other information
Other information
Distribution losses (% of purchases) | 3.983%
Network Service area (sq.km) | 22275 | From Ausgrid's 2012/13 Electricity Network Performance Report
Network Coincident Maximum Demand (MW) | 5659
FTE employees | 5713 | From Ausgrid's 2012/13 Electricity Network Performance Report
Contents

## 5a. Network data outage
Ausgrid
Nework data - outages
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Unplanned Outages
Date (DD/MM/YYYY) | Feeder ID / name | Feeder classification | Cause of event | Event ID | Number of customers interrupted | Duration of interruption (Mins) | Total unplanned customer minutes off supply (Mins) | Unplanned SAIDI impact | Unplanned SAIFI impact
2012-07-01 | ZN9037:PA2 | URBAN | Equipment Failure | 842782 | 38 | 227 | 8626 | 0.0052698 | 0.0023215
2012-07-01 | ZN901:PA32 | URBAN | Other | 842813 | 45 | 96 | 4320 | 0.0026392 | 0.0027491
2012-07-01 | ZN12610:PA18 | URBAN | Equipment Failure | 842822 | 1 | 194.55 | 194.55 | 0.00011885 | 6.1092e-05
2012-07-01 | ZN15008:PA10 | URBAN | Other | 842848 | 1 | 38.9333 | 38.9333 | 2.3785e-05 | 6.1092e-05
2012-07-01 | ZN2196:PA21 | URBAN | Other | 842855 | 1 | 216.9333 | 216.9333 | 0.00013253 | 6.1092e-05
2012-07-01 | ZN12600:PA13 | SHORT RURAL | Equipment Failure | 842869 | 2 | 238 | 476 | 0.0002908 | 0.00012218
2012-07-01 | ZN36300:PA11 | URBAN | Other | 842875 | 1 | 3.65 | 3.65 | 2.2299e-06 | 6.1092e-05
2012-07-01 | 238:34144 | URBAN | Other | 842902 | 1 | 101.3 | 101.3 | 6.1886e-05 | 6.1092e-05
2012-07-01 | ZN12640:PA10 | URBAN | Other | 842916 | 1 | 501.75 | 501.75 | 0.00030653 | 6.1092e-05
2012-07-02 | 502:48004 | URBAN | Equipment Failure | 842951 | 1 | 206.7167 | 206.7167 | 0.00012629 | 6.1092e-05
2012-07-02 | ZN12610:PA18 | URBAN | Equipment Failure | 842974 | 90 | 145.4667 | 13092 | 0.0079982 | 0.0054983
2012-07-02 | 806:74080 | SHORT RURAL | Other | 843066 | 1 | 236 | 236 | 0.00014418 | 6.1092e-05
2012-07-02 | 504:48034 | URBAN | Equipment Failure | 843106 | 1 | 161.2833 | 161.2833 | 9.8531e-05 | 6.1092e-05
2012-07-02 | ZN1193:PA1 | URBAN | Other | 843133 | 602 | 118 | 55598 | 0.033966 | 0.036777
2012-07-02 | 225:33670 | SHORT RURAL | Vegetation | 843195 | 188 | 541 | 23345 | 0.014262 | 0.011485
2012-07-02 | ZN129:PA18 | URBAN | Equipment Failure | 843226 | 20 | 125.9833 | 2519.6667 | 0.0015393 | 0.0012218
2012-07-02 | 224:80346 | URBAN | Third Party Impacts | 843248 | 1518 | 34 | 51612 | 0.031531 | 0.092738
2012-07-02 | ZN14892:PA3 | SHORT RURAL | Animals | 843375 | 77 | 51.3833 | 3956.5167 | 0.0024171 | 0.0047041
2012-07-02 | ZN35600:PA9 | URBAN | Equipment Failure | 843402 | 50 | 296.9167 | 14845.8333 | 0.0090696 | 0.0030546
2012-07-02 | 238:34141 | SHORT RURAL | Other | 843451 | 44 | 114 | 5016 | 0.0030644 | 0.002688
2012-07-03 | ZN10999:PA38 | URBAN | Equipment Failure | 843460 | 1 | 192.7833 | 192.7833 | 0.00011778 | 6.1092e-05
2012-07-03 | ZN15001:PA18 | URBAN | Third Party Impacts | 843461 | 39 | 57 | 2223 | 0.0013581 | 0.0023826
2012-07-03 | 220:8688 | URBAN | Other | 843464 | 1 | 31.9167 | 31.9167 | 1.9499e-05 | 6.1092e-05
2012-07-03 | ZN15004:PA5 | URBAN | Equipment Failure | 843481 | 1 | 327.4667 | 327.4667 | 0.00020006 | 6.1092e-05
2012-07-03 | ZN80:PA24 | URBAN | Equipment Failure | 843489 | 8 | 57 | 456 | 0.00027858 | 0.00048874
2012-07-03 | 225:33679 | URBAN | Vegetation | 843599 | 1 | 140.65 | 140.65 | 8.5926e-05 | 6.1092e-05
2012-07-03 | 513:48056 | SHORT RURAL | Other | 843623 | 1 | 52.0833 | 52.0833 | 3.1819e-05 | 6.1092e-05
2012-07-03 | 202:34253 | URBAN | Equipment Failure | 843637 | 55 | 76 | 4180 | 0.0025536 | 0.0033601
2012-07-03 | 225:33670 | SHORT RURAL | Vegetation | 843673 | 25 | 530 | 6050 | 0.0036961 | 0.0015273
2012-07-03 | ZN2466:PA27 | URBAN | Equipment Failure | 843741 | 2 | 280 | 560 | 0.00034211 | 0.00012218
2012-07-03 | 216:10728 | URBAN | Other | 843906 | 1 | 161.3333 | 161.3333 | 9.8562e-05 | 6.1092e-05
2012-07-03 | 216:10728 | URBAN | Other | 843912 | 1 | 153.6667 | 153.6667 | 9.3878e-05 | 6.1092e-05
2012-07-03 | ZN1850:PA10 | URBAN | Equipment Failure | 843948 | 33 | 333.8667 | 11017.6 | 0.0067309 | 0.002016
2012-07-03 | ZN1850:PA10 | URBAN | Equipment Failure | 843953 | 1 | 326.7333 | 326.7333 | 0.00019961 | 6.1092e-05
2012-07-03 | 264:81240 | SHORT RURAL | Equipment Failure | 843957 | 3 | 105.4667 | 316.4 | 0.00019329 | 0.00018328
2012-07-04 | ZN269:PA18 | URBAN | Equipment Failure | 843979 | 1079 | 7 | 7553 | 0.0046143 | 0.065918
2012-07-04 | ZN269:PA19 | URBAN | Equipment Failure | 843979 | 1367 | 7 | 9569 | 0.0058459 | 0.083513
2012-07-04 | ZN269:PA24 | URBAN | Equipment Failure | 843979 | 222 | 7 | 1554 | 0.00094937 | 0.013562
2012-07-04 | ZN269:PA25 | URBAN | Equipment Failure | 843979 | 54 | 7 | 378 | 0.00023093 | 0.003299
2012-07-04 | ZN269:PA26 | URBAN | Equipment Failure | 843979 | 1468 | 7 | 10276 | 0.0062778 | 0.089683
2012-07-04 | ZN187:PA30 | URBAN | Equipment Failure | 843986 | 88 | 51.0333 | 4490.9333 | 0.0027436 | 0.0053761
2012-07-04 | ZN9037:PA8 | URBAN | Third Party Impacts | 844002 | 1 | 51.2333 | 51.2333 | 3.1299e-05 | 6.1092e-05
2012-07-04 | ZN847:PA39 | URBAN | Equipment Failure | 844039 | 1 | 300.3833 | 300.3833 | 0.00018351 | 6.1092e-05
2012-07-04 | 220:8689 | URBAN | Other | 844041 | 1 | 249.3833 | 249.3833 | 0.00015235 | 6.1092e-05
2012-07-04 | ZN2400:PA18 | SHORT RURAL | Equipment Failure | 844073 | 108 | 125 | 13500 | 0.0082474 | 0.0065979
2012-07-04 | 504:48033 | SHORT RURAL | Equipment Failure | 844142 | 6 | 249.7333 | 1498.4 | 0.0009154 | 0.00036655
2012-07-04 | ZN35500:PA22 | URBAN | Third Party Impacts | 844231 | 33 | 390 | 10890 | 0.0066529 | 0.002016
2012-07-04 | ZN35500:PA28 | URBAN | Third Party Impacts | 844231 | 3034 | 390 | 42575 | 0.02601 | 0.18535
2012-07-04 | ZN3472:PA30 | URBAN | Third Party Impacts | 844348 | 1 | 269.2167 | 269.2167 | 0.00016447 | 6.1092e-05
2012-07-04 | ZN14892:PA12 | SHORT RURAL | Equipment Failure | 844359 | 1 | 9827.05 | 9827.05 | 0.0060035 | 6.1092e-05
2012-07-04 | ZN12640:PA8 | SHORT RURAL | Equipment Failure | 844406 | 1 | 1507.55 | 1507.55 | 0.00092099 | 6.1092e-05
2012-07-04 | ZN14143:PA17 | SHORT RURAL | Equipment Failure | 844434 | 3 | 331 | 993 | 0.00060664 | 0.00018328
2012-07-04 | ZN901:PA18 | URBAN | Equipment Failure | 844456 | 86 | 106.75 | 9180.5 | 0.0056085 | 0.0052539
2012-07-04 | ZN269:PA3 | URBAN | Other | 844457 | 43 | 83.3 | 3581.9 | 0.0021883 | 0.002627
2012-07-04 | 807:74184 | SHORT RURAL | Equipment Failure | 844468 | 4 | 144 | 576 | 0.00035189 | 0.00024437
2012-07-05 | ZN690:PA12 | URBAN | Other | 844481 | 1 | 292 | 292 | 0.00017839 | 6.1092e-05
2012-07-05 | ZN1850:PA10 | URBAN | Other | 844489 | 1 | 118.1333 | 118.1333 | 7.217e-05 | 6.1092e-05
2012-07-05 | ZN129:PA2 | URBAN | Other | 844500 | 135 | 100 | 13500 | 0.0082474 | 0.0082474
2012-07-05 | ZN35500:PA24 | URBAN | Other | 844500 | 29 | 100 | 2900 | 0.0017717 | 0.0017717
2012-07-05 | 509:48039 | LONG RURAL | Other | 844522 | 1 | 118 | 118 | 7.2089e-05 | 6.1092e-05
2012-07-05 | ZN2635:PA1 | URBAN | Other | 844529 | 58 | 288 | 16704 | 0.010205 | 0.0035433
2012-07-05 | ZN15014:PA19 | URBAN | Equipment Failure | 844560 | 1 | 340.4333 | 340.4333 | 0.00020798 | 6.1092e-05
2012-07-05 | 224:80346 | URBAN | Other | 844578 | 25 | 121.3667 | 3034.1667 | 0.0018536 | 0.0015273
2012-07-05 | ZN3472:PA8 | URBAN | Equipment Failure | 844659 | 1 | 151.2667 | 151.2667 | 9.2412e-05 | 6.1092e-05
2012-07-05 | ZN12620:PA1 | SHORT RURAL | Other | 844715 | 1 | 352.1167 | 352.1167 | 0.00021512 | 6.1092e-05
2012-07-05 | 202:34231 37 42 | URBAN | Other | 844770 | 38 | 2725 | 2850 | 0.0017411 | 0.0023215
2012-07-05 | 202:34259 | URBAN | Other | 844770 | 7 | 2725 | 5825 | 0.0035586 | 0.00042764
2012-07-05 | ZN15005:PA12 | URBAN | Third Party Impacts | 844771 | 1 | 109.7833 | 109.7833 | 6.7069e-05 | 6.1092e-05
2012-07-05 | ZN10999:PA17 | URBAN | Equipment Failure | 844879 | 71 | 98.0667 | 6962.7333 | 0.0042537 | 0.0043375
2012-07-05 | 223:14393 | URBAN | Other | 844908 | 1 | 92.2667 | 92.2667 | 5.6368e-05 | 6.1092e-05
2012-07-05 | ZN2196:PA2 | URBAN | Other | 844934 | 1 | 279.0833 | 279.0833 | 0.0001705 | 6.1092e-05
2012-07-05 | 513:48051 | URBAN | Other | 844946 | 55 | 95 | 5225 | 0.0031921 | 0.0033601
2012-07-05 | ZN4545:PA32 | URBAN | Equipment Failure | 844949 | 1 | 191.6667 | 191.6667 | 0.00011709 | 6.1092e-05
2012-07-05 | ZN12660:PA5 | SHORT RURAL | Vegetation | 844952 | 1 | 188 | 188 | 0.00011485 | 6.1092e-05
2012-07-06 | ZN2466:PA5 | URBAN | Equipment Failure | 844955 | 108 | 404.35 | 43669.8 | 0.026679 | 0.006598
2012-07-06 | 513:48059 | SHORT RURAL | Other | 844958 | 1 | 169.1 | 169.1 | 0.00010331 | 6.1092e-05
2012-07-06 | ZN12570:PA6 | SHORT RURAL | Other | 844965 | 6 | 111.7167 | 670.3 | 0.0004095 | 0.00036655
2012-07-04 | 235:2857 | SHORT RURAL | Equipment Failure | 844980 | 2 | 145 | 290 | 0.00017717 | 0.00012218
2012-07-06 | ZN2466:PA5 | URBAN | Equipment Failure | 845045 | 108 | 490.2167 | 52943.4 | 0.032344 | 0.006598
2012-07-06 | ZN72:PA22 | URBAN | Equipment Failure | 845048 | 1 | 388.2833 | 388.2833 | 0.00023721 | 6.1092e-05
2012-07-06 | 232:11457 | URBAN | Equipment Failure | 845074 | 101 | 173 | 17473 | 0.010675 | 0.0061703
2012-07-06 | 512:48049 | SHORT RURAL | Other | 845088 | 3 | 62 | 186 | 0.00011363 | 0.00018328
2012-07-06 | 806:74080 | SHORT RURAL | Other | 845144 | 1 | 142 | 142 | 8.6751e-05 | 6.1092e-05
2012-07-06 | ZN1788:PA11 | URBAN | Equipment Failure | 845159 | 1 | 634.4167 | 634.4167 | 0.00038758 | 6.1092e-05
2012-07-06 | ZN1285:PA27 | URBAN | Equipment Failure | 845191 | 1 | 252.4167 | 252.4167 | 0.00015421 | 6.1092e-05
2012-07-06 | 504:48029 | URBAN | Other | 845293 | 1 | 146.0167 | 146.0167 | 8.9205e-05 | 6.1092e-05
2012-07-06 | 812:19066 | SHORT RURAL | Equipment Failure | 845319 | 1 | 200.8667 | 200.8667 | 0.00012271 | 6.1092e-05
2012-07-06 | ZN1193:PA2 | URBAN | Equipment Failure | 845320 | 45 | 186 | 8370 | 0.0051134 | 0.0027491
2012-07-06 | ZN1193:PA8 | URBAN | Equipment Failure | 845320 | 77 | 186 | 14322 | 0.0087496 | 0.0047041
2012-07-06 | ZN1193:PA9 | URBAN | Equipment Failure | 845320 | 49 | 186 | 9114 | 0.0055679 | 0.0029935
2012-07-06 | 232:11453 | SHORT RURAL | Equipment Failure | 845335 | 27 | 346 | 9342 | 0.0057072 | 0.0016495
2012-07-06 | 232:11454 | SHORT RURAL | Other | 845341 | 1 | 354.4167 | 354.4167 | 0.00021652 | 6.1092e-05
2012-07-06 | 220:8687 | URBAN | Equipment Failure | 845358 | 1522 | 56 | 12176 | 0.0074386 | 0.092982
2012-07-06 | 220:8688 | URBAN | Equipment Failure | 845358 | 448 | 56 | 3584 | 0.0021895 | 0.027369
2012-07-06 | 220:8689 | URBAN | Equipment Failure | 845358 | 1465 | 56 | 11720 | 0.00716 | 0.0895
2012-07-06 | 220:8691 | URBAN | Equipment Failure | 845358 | 1148 | 56 | 9184 | 0.0056107 | 0.070134
2012-07-06 | 220:8692 | URBAN | Equipment Failure | 845358 | 897 | 56 | 7176 | 0.004384 | 0.0548
2012-07-06 | 221:11893 | URBAN | Equipment Failure | 845358 | 709 | 56 | 5672 | 0.0034651 | 0.043314
2012-07-06 | 221:11894 | URBAN | Equipment Failure | 845358 | 927 | 56 | 7416 | 0.0045306 | 0.056632
2012-07-06 | 221:11895 | URBAN | Equipment Failure | 845358 | 377 | 56 | 3016 | 0.0018425 | 0.023032
2012-07-06 | 221:11897 | URBAN | Equipment Failure | 845358 | 649 | 56 | 5192 | 0.0031719 | 0.039649
2012-07-06 | 221:11898 | URBAN | Equipment Failure | 845358 | 262 | 56 | 2096 | 0.0012805 | 0.016006
2012-07-06 | 221:11899 | URBAN | Equipment Failure | 845358 | 33 | 56 | 264 | 0.00016128 | 0.002016
2012-07-06 | 221:11900 | URBAN | Equipment Failure | 845358 | 2094 | 56 | 16752 | 0.010234 | 0.12793
2012-07-06 | 222:2014 | URBAN | Equipment Failure | 845358 | 1175 | 56 | 9400 | 0.0057427 | 0.071783
2012-07-06 | 222:2015 | SHORT RURAL | Equipment Failure | 845358 | 782 | 56 | 6256 | 0.0038219 | 0.047774
2012-07-06 | 222:2017 | URBAN | Equipment Failure | 845358 | 1249 | 56 | 9992 | 0.0061043 | 0.076304
2012-07-06 | 222:2018 | URBAN | Equipment Failure | 845358 | 1039 | 56 | 8312 | 0.005078 | 0.063475
2012-07-06 | 223:14393 | URBAN | Equipment Failure | 845358 | 1042 | 56 | 3126 | 0.0019097 | 0.063658
2012-07-06 | 223:14394 | URBAN | Equipment Failure | 845358 | 1507 | 56 | 33154 | 0.020255 | 0.092066
2012-07-06 | 223:14395 | SHORT RURAL | Equipment Failure | 845358 | 924 | 56 | 2772 | 0.0016935 | 0.056449
2012-07-06 | 223:14397 | URBAN | Equipment Failure | 845358 | 1132 | 56 | 49808 | 0.030429 | 0.069156
2012-07-06 | 223:14398 | URBAN | Equipment Failure | 845358 | 848 | 56 | 40704 | 0.024867 | 0.051806
2012-07-06 | 223:14399 | SHORT RURAL | Equipment Failure | 845358 | 145 | 56 | 6960 | 0.004252 | 0.0088584
2012-07-06 | 221:11897 | URBAN | Other | 845367 | 1 | 126.3333 | 126.3333 | 7.718e-05 | 6.1092e-05
2012-07-06 | 206:34440 | URBAN | Other | 845383 | 1 | 182.8167 | 182.8167 | 0.00011169 | 6.1092e-05
2012-07-06 | ZN129:PA5 | URBAN | Equipment Failure | 845402 | 912 | 53 | 46762 | 0.028568 | 0.055716
2012-07-07 | ZN2635:PA17 | URBAN | Equipment Failure | 845407 | 505 | 409 | 206545 | 0.12618 | 0.030852
2012-07-07 | ZN10991:PA13 | URBAN | Third Party Impacts | 845415 | 1 | 266.8833 | 266.8833 | 0.00016304 | 6.1092e-05
2012-07-07 | 806:74080 | SHORT RURAL | Other | 845427 | 1 | 159 | 159 | 9.7137e-05 | 6.1092e-05
2012-07-07 | ZN2635:PA17 | URBAN | Equipment Failure | 845464 | 1 | 300.7 | 300.7 | 0.0001837 | 6.1092e-05
2012-07-07 | ZN12690:PA12 | SHORT RURAL | Equipment Failure | 845486 | 50 | 123.8167 | 6190.8333 | 0.0037821 | 0.0030546
2012-07-07 | ZN12640:PA15 | URBAN | Other | 845511 | 1 | 225.1667 | 225.1667 | 0.00013756 | 6.1092e-05
2012-07-07 | ZN342:PA24 | URBAN | Equipment Failure | 845515 | 1 | 146.2167 | 146.2167 | 8.9327e-05 | 6.1092e-05
2012-07-07 | ZN342:PA18 | URBAN | Vegetation | 845516 | 111 | 77 | 8547 | 0.0052216 | 0.0067812
2012-07-07 | ZN3472:PA8 | URBAN | Other | 845568 | 1 | 234.8167 | 234.8167 | 0.00014345 | 6.1092e-05
2012-07-07 | ZN12600:PA2 | SHORT RURAL | Equipment Failure | 845584 | 1 | 1375.5167 | 1375.5167 | 0.00084033 | 6.1092e-05
2012-07-07 | ZN262:PA16 | URBAN | Equipment Failure | 845596 | 79 | 152 | 10823 | 0.006612 | 0.0048263
2012-07-07 | ZN262:PA29 | URBAN | Equipment Failure | 845596 | 405 | 152 | 33510 | 0.020472 | 0.024742
2012-07-08 | ZN12570:PA12 | SHORT RURAL | Third Party Impacts | 845630 | 1 | 345.1 | 345.1 | 0.00021083 | 6.1092e-05
2012-07-08 | ZN12590:PA7 | SHORT RURAL | Equipment Failure | 845631 | 8 | 220 | 1760 | 0.0010752 | 0.00048874
2012-07-08 | ZN12640:PA19 | URBAN | Equipment Failure | 845699 | 1225 | 65 | 79625 | 0.048645 | 0.074838
2012-07-08 | ZN12640:PA8 | SHORT RURAL | Equipment Failure | 845699 | 4 | 65 | 260 | 0.00015884 | 0.00024437
2012-07-08 | ZN3472:PA12 | URBAN | Equipment Failure | 845722 | 26 | 91 | 2028 | 0.0012389 | 0.0015884
2012-07-08 | ZN3472:PA33 | URBAN | Equipment Failure | 845722 | 1400 | 91 | 111969 | 0.068404 | 0.085529
2012-07-08 | 235:2120 | SHORT RURAL | Equipment Failure | 845729 | 2 | 174.5667 | 349.1333 | 0.00021329 | 0.00012218
2012-07-08 | ZN9900:PA8 | URBAN | Third Party Impacts | 845738 | 37 | 104 | 3848 | 0.0023508 | 0.0022604
2012-07-08 | 219:1785 | URBAN | Operational Error | 845740 | 28 | 43.8167 | 1226.8667 | 0.00074952 | 0.0017106
2012-07-08 | ZN3922:PA29 | URBAN | Other | 845747 | 1 | 531.1 | 531.1 | 0.00032446 | 6.1092e-05
2012-07-08 | ZN2602:PA27 | URBAN | Other | 845762 | 39 | 58 | 2262 | 0.0013819 | 0.0023826
2012-07-09 | 526:34636 | SHORT RURAL | Other | 845810 | 2 | 110 | 220 | 0.0001344 | 0.00012218
2012-07-07 | 232:11453 | SHORT RURAL | Equipment Failure | 845882 | 27 | 20 | 540 | 0.0003299 | 0.0016495
2012-07-08 | 507:80922 | SHORT RURAL | Other | 845896 | 83 | 90 | 7470 | 0.0045636 | 0.0050707
2012-07-09 | ZN35600:PA4 | URBAN | Third Party Impacts | 845907 | 2 | 155 | 310 | 0.00018939 | 0.00012218
2012-07-09 | ZN9700:PA23 | URBAN | Operational Error | 845950 | 46 | 81.8167 | 3763.5667 | 0.0022992 | 0.0028102
2012-07-09 | ZN15005:PA6 | URBAN | Equipment Failure | 845975 | 1 | 176.45 | 176.45 | 0.0001078 | 6.1092e-05
2012-07-09 | ZN15014:PA5 | URBAN | Equipment Failure | 845984 | 34 | 297.7167 | 10122.3667 | 0.006184 | 0.0020771
2012-07-09 | ZN9252:PA2 | URBAN | Equipment Failure | 846019 | 1 | 41.5333 | 41.5333 | 2.5374e-05 | 6.1092e-05
2012-07-09 | ZN9252:PA2 | URBAN | Third Party Impacts | 846036 | 22 | 153 | 3366 | 0.0020564 | 0.001344
2012-07-09 | ZN35600:PA22 | URBAN | Other | 846127 | 1 | 680.5667 | 680.5667 | 0.00041577 | 6.1092e-05
2012-07-09 | 504:48031 | SHORT RURAL | Other | 846181 | 1 | 250.4667 | 250.4667 | 0.00015302 | 6.1092e-05
2012-07-09 | ZN9700:PA16 | URBAN | Other | 846198 | 1 | 220.7833 | 220.7833 | 0.00013488 | 6.1092e-05
2012-07-09 | ZN180:PA23 | URBAN | Third Party Impacts | 846248 | 1 | 570.1667 | 570.1667 | 0.00034833 | 6.1092e-05
2012-07-09 | ZN3155:PA19 | URBAN | Equipment Failure | 846269 | 127 | 127 | 15989 | 0.009768 | 0.0077587
2012-07-09 | ZN180:PA23 | URBAN | Other | 846273 | 1 | 100.7833 | 100.7833 | 6.1571e-05 | 6.1092e-05
2012-07-10 | ZN2568:PA14 | URBAN | Equipment Failure | 846318 | 1 | 311.6667 | 311.6667 | 0.00019041 | 6.1094e-05
2012-07-10 | ZN14144:PA10 | SHORT RURAL | Vegetation | 846324 | 15 | 156 | 2340 | 0.0014296 | 0.00091641
2012-07-09 | ZN2568:PA40 | URBAN | Other | 846365 | 41 | 115 | 4715 | 0.0028805 | 0.0025048
2012-07-10 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 846418 | 1 | 65.55 | 65.55 | 4.0047e-05 | 6.1094e-05
2012-07-10 | ZN10993:PA2 | URBAN | Equipment Failure | 846463 | 116 | 221 | 25581.8667 | 0.015629 | 0.0070869
2012-07-10 | ZN10999:PA10 | URBAN | Equipment Failure | 846463 | 67 | 221 | 14807 | 0.0090462 | 0.0040933
2012-07-10 | ZN3472:PA11 | URBAN | Equipment Failure | 846529 | 2 | 273 | 546 | 0.00033357 | 0.00012219
2012-07-10 | ZN12580:PA12 | SHORT RURAL | Equipment Failure | 846666 | 1 | 226.05 | 226.05 | 0.0001381 | 6.1094e-05
2012-07-10 | ZN15008:PA5 | URBAN | Equipment Failure | 846671 | 1 | 421.6167 | 421.6167 | 0.00025758 | 6.1094e-05
2012-07-10 | 813:89061 | LONG RURAL | Other | 846672 | 10 | 301.7167 | 1849.7167 | 0.0011301 | 0.00061094
2012-07-10 | 512:48047 | SHORT RURAL | Equipment Failure | 846747 | 1 | 85.9167 | 85.9167 | 5.249e-05 | 6.1094e-05
2012-07-10 | ZN8100:PA20 | URBAN | Other | 846758 | 1 | 442.35 | 442.35 | 0.00027025 | 6.1094e-05
2012-07-10 | ZN129:PA5 | URBAN | Equipment Failure | 846759 | 44 | 471 | 3481 | 0.0021267 | 0.0026881
2012-07-10 | ZN9037:PA16 | URBAN | Equipment Failure | 846766 | 31 | 271 | 8401 | 0.0051325 | 0.0018939
2012-07-10 | 803:74010 | SHORT RURAL | Equipment Failure | 846828 | 3 | 108 | 324 | 0.00019794 | 0.00018328
2012-07-10 | ZN2635:PA17 | URBAN | Equipment Failure | 846831 | 90 | 178 | 7003.75 | 0.0042789 | 0.0054984
2012-07-10 | ZN9037:PA8 | URBAN | Equipment Failure | 846836 | 1 | 104.9833 | 104.9833 | 6.4138e-05 | 6.1094e-05
2012-07-10 | ZN874:PA17 | URBAN | Equipment Failure | 846865 | 361 | 59 | 21299 | 0.013012 | 0.022055
2012-07-10 | ZN874:PA22 | URBAN | Equipment Failure | 846865 | 1464 | 59 | 80544 | 0.049207 | 0.089441
2012-07-11 | ZN874:PA17 | URBAN | Other | 846868 | 54 | 523 | 28242 | 0.017254 | 0.0032991
2012-07-11 | ZN874:PA18 | SHORT RURAL | Other | 846868 | 19 | 523 | 9937 | 0.0060709 | 0.0011608
2012-07-11 | 813:89061 | LONG RURAL | Equipment Failure | 846873 | 9 | 375 | 3375 | 0.0020619 | 0.00054985
2012-07-11 | 813:89062 | SHORT RURAL | Equipment Failure | 846880 | 823 | 323 | 70854 | 0.043288 | 0.050281
2012-07-11 | 213:33774 | URBAN | Equipment Failure | 846929 | 77 | 150.6167 | 10934.3667 | 0.0066803 | 0.0047043
2012-07-11 | ZN2310:PA31 | URBAN | Third Party Impacts | 846932 | 1 | 130.4 | 130.4 | 7.9667e-05 | 6.1094e-05
2012-07-10 | ZN180:PA21 | URBAN | Equipment Failure | 846934 | 72 | 70 | 5040 | 0.0030791 | 0.0043988
2012-07-11 | ZN4545:PA17 | URBAN | Other | 846965 | 120 | 347 | 41640 | 0.02544 | 0.0073313
2012-07-11 | ZN2835:PA19 | URBAN | Other | 847044 | 6 | 188 | 1128 | 0.00068914 | 0.00036657
2012-07-11 | 228:7490 | SHORT RURAL | Equipment Failure | 847099 | 1 | 71 | 71 | 4.3377e-05 | 6.1094e-05
2012-07-11 | ZN847:PA47 | SHORT RURAL | Equipment Failure | 847192 | 1 | 1199.7333 | 1199.7333 | 0.00073297 | 6.1094e-05
2012-07-11 | ZN14892:PA16 | URBAN | Vegetation | 847241 | 1 | 1034.5333 | 1034.5333 | 0.00063204 | 6.1094e-05
2012-07-11 | 203:8088 | URBAN | Other | 847251 | 1 | 100.9 | 100.9 | 6.1644e-05 | 6.1094e-05
2012-07-11 | 203:8089 | URBAN | Vegetation | 847255 | 1 | 54.4833 | 54.4833 | 3.3286e-05 | 6.1094e-05
2012-07-11 | 507:80932 | SHORT RURAL | Equipment Failure | 847322 | 14 | 126 | 1763.45 | 0.0010774 | 0.00085532
2012-07-11 | ZN35500:PA34 | URBAN | Equipment Failure | 847355 | 937 | 72 | 63552 | 0.038827 | 0.057245
2012-07-12 | 503:48016 | URBAN | Equipment Failure | 847381 | 748 | 54 | 40392 | 0.024678 | 0.0457
2012-07-12 | 503:48078 | URBAN | Equipment Failure | 847381 | 1155 | 54 | 62370 | 0.038106 | 0.070566
2012-07-12 | 238:34151 | URBAN | Equipment Failure | 847391 | 1 | 122 | 122 | 7.4538e-05 | 6.1097e-05
2012-07-11 | 813:89061 | LONG RURAL | Equipment Failure | 847407 | 1 | 125 | 125 | 7.6368e-05 | 6.1094e-05
2012-07-12 | ZN10995:PA2 | URBAN | Other | 847706 | 1 | 125.75 | 125.75 | 7.6829e-05 | 6.1097e-05
2012-07-12 | ZN4545:PA24 | URBAN | Third Party Impacts | 847735 | 88 | 58.1167 | 5114.2667 | 0.0031246 | 0.0053765
2012-07-12 | ZN14891:PA17 | SHORT RURAL | Equipment Failure | 847792 | 2 | 246 | 492 | 0.00030059 | 0.00012219
2012-07-12 | ZN80:PA37 | URBAN | Other | 847812 | 45 | 572 | 25740 | 0.015726 | 0.0027493
2012-07-13 | ZN12690:PA6 | URBAN | Equipment Failure | 847818 | 492 | 14 | 6888 | 0.0042083 | 0.03006
2012-07-13 | ZN9118:PA21 | URBAN | Vegetation | 847827 | 1 | 30.5833 | 30.5833 | 1.8685e-05 | 6.1097e-05
2012-07-13 | ZN5868:PA27 | URBAN | Equipment Failure | 847828 | 8 | 296 | 2368 | 0.0014468 | 0.00048877
2012-07-13 | ZN384:PA23 | URBAN | Vegetation | 847860 | 1 | 143.0333 | 143.0333 | 8.7388e-05 | 6.1097e-05
2012-07-13 | ZN12570:PA5 | URBAN | Equipment Failure | 847935 | 1 | 244.7 | 244.7 | 0.0001495 | 6.1097e-05
2012-07-13 | ZN15013:PA10 | SHORT RURAL | Other | 847965 | 38 | 86.9167 | 3302.8333 | 0.0020179 | 0.0023217
2012-07-13 | ZN931:PA12 | URBAN | Equipment Failure | 847966 | 1 | 120.9667 | 120.9667 | 7.3906e-05 | 6.1097e-05
2012-07-13 | ZN1193:PA17 | URBAN | Other | 848020 | 1 | 195.5833 | 195.5833 | 0.00011949 | 6.1097e-05
2012-07-13 | ZN340:PA14 | SHORT RURAL | Operational Error | 848039 | 35 | 132 | 4610.8167 | 0.0028171 | 0.0021384
2012-07-13 | ZN340:PA24 | URBAN | Operational Error | 848039 | 1 | 132 | 132 | 8.0647e-05 | 6.1097e-05
2012-07-13 | ZN901:PA19 | URBAN | Third Party Impacts | 848067 | 1 | 134.9 | 134.9 | 8.2419e-05 | 6.1097e-05
2012-07-13 | 813:89062 | SHORT RURAL | Equipment Failure | 848071 | 1 | 72.4167 | 72.4167 | 4.4244e-05 | 6.1097e-05
2012-07-13 | ZN3472:PA33 | URBAN | Third Party Impacts | 848090 | 1 | 41.7667 | 41.7667 | 2.5518e-05 | 6.1097e-05
2012-07-13 | ZN4545:PA25 | URBAN | Equipment Failure | 848203 | 1 | 96.0333 | 96.0333 | 5.8673e-05 | 6.1097e-05
2012-07-13 | 520:48172 | SHORT RURAL | Vegetation | 848223 | 388 | 84 | 32592 | 0.019913 | 0.023705
2012-07-13 | 221:11893 | URBAN | Other | 848232 | 1 | 49.65 | 49.65 | 3.0334e-05 | 6.1097e-05
2012-07-13 | 264:81236 | URBAN | Other | 848242 | 1 | 426.05 | 426.05 | 0.0002603 | 6.1097e-05
2012-07-13 | ZN2473:PA31 | URBAN | Equipment Failure | 848243 | 97 | 1359.5 | 131871.5 | 0.080569 | 0.0059264
2012-07-14 | ZN195:PA11 | URBAN | Other | 848251 | 21 | 143 | 3003 | 0.0018347 | 0.001283
2012-07-14 | ZN1285:PA29 | URBAN | Third Party Impacts | 848276 | 1 | 79 | 29.2333 | 1.7861e-05 | 6.1097e-05
2012-07-14 | ZN35800:PA1 | URBAN | Third Party Impacts | 848276 | 1307 | 79 | 103253 | 0.063084 | 0.079853
2012-07-14 | 523:33501 | SHORT RURAL | Equipment Failure | 848282 | 1 | 92.4833 | 92.4833 | 5.6504e-05 | 6.1097e-05
2012-07-14 | 503:48011 | SHORT RURAL | Other | 848288 | 1 | 151.0167 | 151.0167 | 9.2266e-05 | 6.1097e-05
2012-07-14 | ZN847:PA10 | URBAN | Equipment Failure | 848325 | 33 | 179 | 5907 | 0.003609 | 0.0020162
2012-07-14 | ZN847:PA19 | URBAN | Equipment Failure | 848325 | 32 | 179 | 5720.5333 | 0.003495 | 0.0019551
2012-07-14 | ZN7900:PA12 | URBAN | Equipment Failure | 848344 | 5 | 1788 | 8940 | 0.005462 | 0.00030548
2012-07-14 | ZN901:PA23 | URBAN | Equipment Failure | 848344 | 73 | 1788 | 365 | 0.000223 | 0.00446
2012-07-14 | ZN901:PA8 | URBAN | Equipment Failure | 848344 | 105 | 1788 | 187685.75 | 0.11467 | 0.0064151
2012-07-14 | ZN9245:PA13 | URBAN | Other | 848348 | 52 | 186 | 9412 | 0.0057504 | 0.003177
2012-07-14 | ZN9245:PA14 | URBAN | Other | 848348 | 47 | 186 | 8742 | 0.0053411 | 0.0028715
2012-07-14 | ZN2635:PA21 | URBAN | Vegetation | 848361 | 1 | 19.1667 | 19.1667 | 1.171e-05 | 6.1097e-05
2012-07-14 | ZN2635:PA21 | URBAN | Vegetation | 848364 | 1 | 39.25 | 39.25 | 2.398e-05 | 6.1097e-05
2012-07-14 | 264:81240 | SHORT RURAL | Other | 848375 | 17 | 139.7167 | 2375.1833 | 0.0014512 | 0.0010386
2012-07-14 | ZN2568:PA26 | URBAN | Equipment Failure | 848385 | 8 | 230.3333 | 1485.55 | 0.00090762 | 0.00048877
2012-07-14 | ZN2568:PA27 | URBAN | Equipment Failure | 848385 | 101 | 230.3333 | 18254.0667 | 0.011153 | 0.0061708
2012-07-14 | ZN342:PA22 | URBAN | Other | 848400 | 302 | 128.4 | 38776.8 | 0.023691 | 0.018451
2012-07-15 | ZN2196:PA5 | URBAN | Vegetation | 848412 | 1544 | 179 | 127354 | 0.077809 | 0.094333
2012-07-15 | ZN9118:PA21 | URBAN | Third Party Impacts | 848415 | 12 | 59 | 708 | 0.00043256 | 0.00073316
2012-07-15 | ZN2835:PA16 | URBAN | Other | 848416 | 7 | 205 | 1435 | 0.00087674 | 0.00042768
2012-07-15 | 240:34846 | URBAN | Equipment Failure | 848441 | 1 | 151.2 | 151.2 | 9.2378e-05 | 6.1097e-05
2012-07-15 | ZN14891:PA20 | SHORT RURAL | Equipment Failure | 848457 | 1 | 283.0667 | 283.0667 | 0.00017294 | 6.1097e-05
2012-07-15 | ZN690:PA28 | URBAN | Equipment Failure | 848460 | 72 | 246.1167 | 17720.4 | 0.010827 | 0.004399
2012-07-15 | ZN12660:PA6 | SHORT RURAL | Vegetation | 848496 | 1 | 269.3667 | 269.3667 | 0.00016457 | 6.1097e-05
2012-07-15 | 507:80923 | SHORT RURAL | Other | 848517 | 6 | 86.4833 | 518.9 | 0.00031703 | 0.00036658
2012-07-15 | ZN9118:PA21 | URBAN | Equipment Failure | 848518 | 50 | 172.5167 | 8625.8333 | 0.0052701 | 0.0030548
2012-07-15 | 512:48049 | SHORT RURAL | Other | 848534 | 2 | 78 | 156 | 9.5311e-05 | 0.00012219
2012-07-15 | 512:48049 | SHORT RURAL | Other | 848540 | 1 | 55.1333 | 55.1333 | 3.3685e-05 | 6.1097e-05
2012-07-15 | ZN9900:PA5 | URBAN | Equipment Failure | 848562 | 34 | 63.3667 | 2154.4667 | 0.0013163 | 0.0020773
2012-07-16 | ZN4545:PA25 | URBAN | Equipment Failure | 848568 | 1557 | 117 | 160794 | 0.09824 | 0.095127
2012-07-16 | 232:33411 | SHORT RURAL | Vegetation | 848585 | 1 | 77.25 | 77.25 | 4.7197e-05 | 6.1097e-05
2012-07-16 | ZN1164:PA21 | URBAN | Other | 848626 | 54 | 93 | 5022 | 0.0030683 | 0.0032992
2012-07-16 | ZN1164:PA22 | URBAN | Other | 848626 | 2 | 93 | 186 | 0.00011364 | 0.00012219
2012-07-16 | ZN10999:PA38 | URBAN | Equipment Failure | 848648 | 132 | 66.6167 | 8793.4 | 0.0053725 | 0.0080647
2012-07-16 | 807:74184 | SHORT RURAL | Equipment Failure | 848702 | 1 | 107.9 | 107.9 | 6.5923e-05 | 6.1097e-05
2012-07-16 | ZN195:PA11 | URBAN | Equipment Failure | 848724 | 1 | 557.0333 | 557.0333 | 0.00034033 | 6.1097e-05
2012-07-16 | ZN10994:PA9 | URBAN | Other | 848751 | 1 | 80.9167 | 80.9167 | 4.9437e-05 | 6.1097e-05
2012-07-16 | ZN9252:PA12 | URBAN | Equipment Failure | 848755 | 323 | 322 | 104006 | 0.063544 | 0.019734
2012-07-16 | 523:33508 | SHORT RURAL | Equipment Failure | 848813 | 1 | 46.95 | 46.95 | 2.8685e-05 | 6.1097e-05
2012-07-16 | ZN2835:PA31 | URBAN | Equipment Failure | 848885 | 1 | 336.8333 | 336.8333 | 0.00020579 | 6.1097e-05
2012-07-16 | 523:33501 | SHORT RURAL | Equipment Failure | 848939 | 189 | 79.6 | 15044.4 | 0.0091916 | 0.011547
2012-07-16 | ZN3425:PA32 | URBAN | Equipment Failure | 848956 | 28 | 113.95 | 3190.6 | 0.0019493 | 0.0017107
2012-07-16 | ZN3425:PA21 | URBAN | Equipment Failure | 848963 | 2 | 164.2833 | 328.5667 | 0.00020074 | 0.00012219
2012-07-16 | 509:48039 | LONG RURAL | Other | 849015 | 2 | 141 | 282 | 0.00017229 | 0.00012219
2012-07-16 | ZN262:PA20 | URBAN | Third Party Impacts | 849016 | 34 | 160 | 5440 | 0.0033237 | 0.0020773
2012-07-16 | 512:48047 | SHORT RURAL | Other | 849024 | 1 | 231.3167 | 231.3167 | 0.00014133 | 6.1097e-05
2012-07-16 | ZN3154:PA5 | URBAN | Other | 849030 | 1120 | 56 | 62720 | 0.03832 | 0.068428
2012-07-16 | 514:18137 | SHORT RURAL | Equipment Failure | 849044 | 51 | 269 | 4689 | 0.0028648 | 0.0031159
2012-07-16 | 243:80084 | SHORT RURAL | Other | 849047 | 60 | 141.5667 | 8494 | 0.0051895 | 0.0036658
2012-07-17 | ZN12650:PA6 | URBAN | Equipment Failure | 849058 | 4 | 187 | 748 | 0.000457 | 0.00024439
2012-07-16 | 243:80083 | SHORT RURAL | Equipment Failure | 849082 | 2 | 48 | 96 | 5.8653e-05 | 0.00012219
2012-07-17 | 216:10723 | URBAN | Other | 849095 | 1 | 75 | 75 | 4.5822e-05 | 6.1096e-05
2012-07-16 | 511:29878 | SHORT RURAL | Third Party Impacts | 849097 | 1 | 40 | 40 | 2.4439e-05 | 6.1097e-05
2012-07-16 | 807:74184 | SHORT RURAL | Other | 849174 | 1 | 80 | 80 | 4.8877e-05 | 6.1097e-05
2012-07-17 | 812:19072 | SHORT RURAL | Equipment Failure | 849178 | 1 | 70.1333 | 70.1333 | 4.2849e-05 | 6.1096e-05
2012-07-17 | 216:10726 | URBAN | Other | 849285 | 1 | 214.3333 | 214.3333 | 0.00013095 | 6.1096e-05
2012-07-17 | 511:29877 | SHORT RURAL | Third Party Impacts | 849311 | 107 | 394 | 8804 | 0.0053789 | 0.0065373
2012-07-17 | ZN10994:PA20 | URBAN | Equipment Failure | 849324 | 82 | 86.9167 | 7127.1667 | 0.0043544 | 0.0050099
2012-07-17 | ZN4545:PA25 | URBAN | Equipment Failure | 849340 | 1 | 261.6333 | 261.6333 | 0.00015985 | 6.1096e-05
2012-07-17 | ZN14891:PA10 | SHORT RURAL | Equipment Failure | 849353 | 1 | 30.1333 | 30.1333 | 1.841e-05 | 6.1096e-05
2012-07-17 | ZN14891:PA16 | SHORT RURAL | Other | 849415 | 1 | 189 | 189 | 0.00011547 | 6.1096e-05
2012-07-17 | ZN9252:PA8 | URBAN | Equipment Failure | 849487 | 144 | 30 | 4320 | 0.0026394 | 0.0087979
2012-07-17 | ZN2310:PA34 | URBAN | Equipment Failure | 849511 | 2221 | 164 | 268645 | 0.16413 | 0.13569
2012-07-17 | ZN2310:PA40 | URBAN | Equipment Failure | 849511 | 64 | 164 | 7360 | 0.0044967 | 0.0039102
2012-07-18 | 511:29878 | SHORT RURAL | Equipment Failure | 849522 | 126 | 572 | 37746 | 0.023061 | 0.0076981
2012-07-18 | ZN15011:PA8 | URBAN | Equipment Failure | 849523 | 413 | 90 | 37170 | 0.02271 | 0.025233
2012-07-18 | ZN262:PA16 | URBAN | Other | 849534 | 1 | 250.9833 | 250.9833 | 0.00015334 | 6.1096e-05
2012-07-17 | ZN14891:PA10 | SHORT RURAL | Equipment Failure | 849537 | 2 | 60 | 120 | 7.3316e-05 | 0.00012219
2012-07-18 | 524:33572 | SHORT RURAL | Other | 849552 | 1 | 493.4333 | 493.4333 | 0.00030147 | 6.1096e-05
2012-07-18 | 218:7476 | URBAN | Other | 849560 | 102 | 60 | 6120 | 0.0037391 | 0.0062318
2012-07-17 | 807:74184 | SHORT RURAL | Other | 849593 | 1 | 110 | 110 | 6.7206e-05 | 6.1096e-05
2012-07-18 | 210:8679 | URBAN | Other | 849659 | 1 | 60.45 | 60.45 | 3.6933e-05 | 6.1096e-05
2012-07-18 | 232:33409 | URBAN | Animals | 849666 | 1 | 15 | 15 | 9.1645e-06 | 6.1096e-05
2012-07-18 | 807:74181 | SHORT RURAL | Third Party Impacts | 849676 | 1 | 348.5333 | 348.5333 | 0.00021294 | 6.1096e-05
2012-07-18 | ZN2835:PA36 | URBAN | Equipment Failure | 849701 | 21 | 667 | 14007 | 0.0085578 | 0.001283
2012-07-18 | ZN12600:PA2 | SHORT RURAL | Equipment Failure | 849777 | 1 | 375.3167 | 375.3167 | 0.0002293 | 6.1096e-05
2012-07-18 | ZN901:PA11 | URBAN | Equipment Failure | 849800 | 130 | 366.8667 | 47692.6667 | 0.029138 | 0.0079425
2012-07-18 | 807:74181 | SHORT RURAL | Third Party Impacts | 849809 | 1 | 167.4 | 167.4 | 0.00010228 | 6.1096e-05
2012-07-18 | 210:8682 | URBAN | Vegetation | 849895 | 1 | 76.6 | 76.6 | 4.68e-05 | 6.1096e-05
2012-07-18 | ZN1164:PA27 | URBAN | Equipment Failure | 849962 | 32 | 266 | 7430.75 | 0.0045399 | 0.0019551
2012-07-19 | ZN12690:PA12 | SHORT RURAL | Third Party Impacts | 849969 | 93 | 48 | 4464 | 0.0027273 | 0.005682
2012-07-18 | 512:48049 | SHORT RURAL | Other | 849975 | 63 | 86 | 5418 | 0.0033102 | 0.0038491
2012-07-18 | 526:34637 | SHORT RURAL | Other | 849975 | 153 | 86 | 13158 | 0.0080391 | 0.0093477
2012-07-18 | 214:8669 | URBAN | Other | 849978 | 157 | 55 | 8635 | 0.0052757 | 0.0095921
2012-07-19 | ZN965:PA28 | SHORT RURAL | Equipment Failure | 850000 | 49 | 90 | 4410 | 0.0026944 | 0.0029937
2012-07-19 | 502:48010 | SHORT RURAL | Equipment Failure | 850005 | 1 | 158.2667 | 158.2667 | 9.6695e-05 | 6.1096e-05
2012-07-19 | ZN14892:PA8 | URBAN | Other | 850062 | 1 | 307.0833 | 307.0833 | 0.00018762 | 6.1096e-05
2012-07-19 | 504:48028 | URBAN | Equipment Failure | 850130 | 1 | 101 | 101 | 6.1707e-05 | 6.1096e-05
2012-07-19 | ZN10994:PA19 | URBAN | Third Party Impacts | 850132 | 1 | 195.45 | 195.45 | 0.00011941 | 6.1096e-05
2012-07-19 | ZN847:PA39 | URBAN | Third Party Impacts | 850142 | 39 | 597.65 | 5475.3 | 0.0033452 | 0.0023828
2012-07-19 | ZN4545:PA25 | URBAN | Equipment Failure | 850161 | 1 | 720.6 | 720.6 | 0.00044026 | 6.1096e-05
2012-07-19 | ZN630:PA38 | URBAN | Equipment Failure | 850245 | 1 | 210.5 | 210.5 | 0.00012861 | 6.1096e-05
2012-07-19 | 223:14393 | URBAN | Equipment Failure | 850253 | 90 | 35.45 | 3190.5 | 0.0019493 | 0.0054987
2012-07-19 | 812:19065 | SHORT RURAL | Equipment Failure | 850282 | 14 | 237 | 3318 | 0.0020272 | 0.00085535
2012-07-19 | 515:35193 | SHORT RURAL | Animals | 850320 | 2 | 118.6667 | 198.55 | 0.00012131 | 0.00012219
2012-07-19 | 224:80346 | URBAN | Other | 850325 | 1 | 174.5167 | 174.5167 | 0.00010662 | 6.1096e-05
2012-07-19 | ZN1164:PA21 | URBAN | Equipment Failure | 850416 | 7 | 448 | 3136 | 0.001916 | 0.00042767
2012-07-19 | 232:11459 | SHORT RURAL | Other | 850431 | 113 | 85 | 9597.6 | 0.0058638 | 0.0069039
2012-07-19 | 504:48034 | URBAN | Third Party Impacts | 850445 | 1 | 169.1 | 169.1 | 0.00010331 | 6.1096e-05
2012-07-20 | ZN1164:PA27 | URBAN | Third Party Impacts | 850472 | 205 | 278 | 39200 | 0.02395 | 0.012525
2012-07-20 | ZN15009:PA3 | URBAN | Equipment Failure | 850521 | 21 | 145 | 1725 | 0.0010539 | 0.001283
2012-07-20 | ZN15009:PA5 | URBAN | Equipment Failure | 850521 | 26 | 145 | 3770 | 0.0023033 | 0.0015885
2012-07-20 | ZN12610:PA2 | URBAN | Other | 850539 | 1 | 331.9333 | 331.9333 | 0.0002028 | 6.1097e-05
2012-07-20 | ZN1164:PA23 | URBAN | Third Party Impacts | 850577 | 6 | 311 | 1866 | 0.0011401 | 0.00036658
2012-07-20 | 220:8688 | URBAN | Other | 850612 | 1 | 40.2 | 40.2 | 2.4561e-05 | 6.1097e-05
2012-07-20 | ZN269:PA6 | URBAN | Equipment Failure | 850647 | 2 | 83.95 | 167.9 | 0.00010258 | 0.00012219
2012-07-20 | 523:33509 | URBAN | Vegetation | 850723 | 29 | 114.35 | 3316.15 | 0.0020261 | 0.0017718
2012-07-20 | ZN116:PA50 | URBAN | Other | 850757 | 1 | 21.85 | 21.85 | 1.335e-05 | 6.1097e-05
2012-07-20 | 806:74080 | SHORT RURAL | Animals | 850767 | 1 | 177.6667 | 177.6667 | 0.00010855 | 6.1097e-05
2012-07-20 | ZN35500:PA31 | URBAN | Equipment Failure | 850806 | 39 | 39.3333 | 1534 | 0.00093722 | 0.0023828
2012-07-20 | 512:48049 | SHORT RURAL | Equipment Failure | 850808 | 2 | 303 | 606 | 0.00037025 | 0.00012219
2012-07-21 | ZN14144:PA2 | SHORT RURAL | Third Party Impacts | 850812 | 39 | 174 | 6786 | 0.004146 | 0.0023828
2012-07-21 | ZN15008:PA7 | URBAN | Equipment Failure | 850824 | 1 | 122.2333 | 122.2333 | 7.468e-05 | 6.1097e-05
2012-07-21 | ZN195:PA28 | URBAN | Other | 850828 | 1 | 182.4 | 182.4 | 0.00011144 | 6.1097e-05
2012-07-21 | ZN180:PA17 | URBAN | Equipment Failure | 850832 | 26 | 119.2 | 3099.2 | 0.0018935 | 0.0015885
2012-07-21 | ZN2310:PA26 | URBAN | Vegetation | 850857 | 1 | 197.0833 | 197.0833 | 0.00012041 | 6.1097e-05
2012-07-21 | ZN9700:PA23 | URBAN | Equipment Failure | 850886 | 31 | 206.7833 | 6410.2833 | 0.0039165 | 0.001894
2012-07-21 | ZN15012:PA6 | URBAN | Vegetation | 850893 | 1 | 247.3667 | 247.3667 | 0.00015113 | 6.1097e-05
2012-07-21 | ZN12570:PA11 | URBAN | Other | 850904 | 10 | 135 | 1090 | 0.00066595 | 0.00061097
2012-07-21 | ZN12570:PA6 | SHORT RURAL | Other | 850904 | 2137 | 135 | 275957 | 0.1686 | 0.13056
2012-07-21 | ZN195:PA29 | URBAN | Third Party Impacts | 850945 | 34 | 15 | 510 | 0.00031159 | 0.0020773
2012-07-21 | 219:1740 | SHORT RURAL | Equipment Failure | 850957 | 16 | 124 | 1984 | 0.0012122 | 0.00097755
2012-07-21 | 515:35193 | SHORT RURAL | Equipment Failure | 850964 | 1 | 215 | 215 | 0.00013136 | 6.1097e-05
2012-07-21 | ZN9118:PA6 | URBAN | Equipment Failure | 850971 | 1 | 557 | 557 | 0.00034031 | 6.1097e-05
2012-07-21 | 229:34983 | SHORT RURAL | Equipment Failure | 850993 | 1592 | 54 | 74068 | 0.045253 | 0.097266
2012-07-21 | 504:48031 | SHORT RURAL | Equipment Failure | 851021 | 2 | 977 | 1954 | 0.0011938 | 0.00012219
2012-07-21 | ZN15005:PA8 | URBAN | Equipment Failure | 851026 | 64 | 75.9667 | 4861.8667 | 0.0029704 | 0.0039102
2012-07-22 | ZN8000:PA38 | URBAN | Equipment Failure | 851031 | 616 | 160 | 68945 | 0.042123 | 0.037636
2012-07-22 | ZN269:PA18 | URBAN | Equipment Failure | 851032 | 1076 | 89 | 90508 | 0.055297 | 0.06574
2012-07-22 | 205:12203 | URBAN | Other | 851033 | 1 | 225.6 | 225.6 | 0.00013783 | 6.1097e-05
2012-07-22 | ZN9118:PA8 | URBAN | Equipment Failure | 851057 | 1 | 152.9667 | 152.9667 | 9.3458e-05 | 6.1097e-05
2012-07-22 | ZN35600:PA1 | URBAN | Equipment Failure | 851070 | 39 | 135.8667 | 5298.8 | 0.0032374 | 0.0023828
2012-07-22 | 526:34640 | SHORT RURAL | Other | 851092 | 4 | 55 | 220 | 0.00013441 | 0.00024439
2012-07-22 | 503:48017 | URBAN | Other | 851099 | 1 | 56.8667 | 56.8667 | 3.4744e-05 | 6.1097e-05
2012-07-22 | 507:80922 | SHORT RURAL | Other | 851119 | 2 | 106 | 212 | 0.00012952 | 0.00012219
2012-07-22 | 807:74183 | SHORT RURAL | Other | 851120 | 1 | 134.15 | 134.15 | 8.1961e-05 | 6.1097e-05
2012-07-22 | ZN195:PA9 | URBAN | Equipment Failure | 851135 | 1253 | 62 | 72286 | 0.044164 | 0.076554
2012-07-22 | 501:48123 | SHORT RURAL | Equipment Failure | 851149 | 19 | 1049 | 8230 | 0.0050283 | 0.0011608
2012-07-22 | 511:29878 | SHORT RURAL | Other | 851182 | 1 | 192.8333 | 192.8333 | 0.00011781 | 6.1097e-05
2012-07-22 | ZN3472:PA27 | URBAN | Other | 851189 | 1 | 485.75 | 485.75 | 0.00029678 | 6.1097e-05
2012-07-22 | 234:2001 | URBAN | Other | 851193 | 1 | 142.7 | 142.7 | 8.7185e-05 | 6.1097e-05
2012-07-22 | 223:14393 | URBAN | Other | 851209 | 1 | 170.6167 | 170.6167 | 0.00010424 | 6.1097e-05
2012-07-22 | ZN269:PA9 | URBAN | Equipment Failure | 851215 | 1440 | 104 | 148156 | 0.090518 | 0.087979
2012-07-22 | ZN72:PA16 | URBAN | Third Party Impacts | 851235 | 3 | 362 | 1086 | 0.00066351 | 0.00018329
2012-07-23 | 208:58 | URBAN | Other | 851238 | 1 | 416.2833 | 416.2833 | 0.00025434 | 6.1097e-05
2012-07-23 | ZN1287:PA11 | URBAN | Vegetation | 851240 | 38 | 147 | 5586 | 0.0034129 | 0.0023217
2012-07-23 | 523:33509 | URBAN | Other | 851243 | 1 | 430.0667 | 430.0667 | 0.00026276 | 6.1097e-05
2012-07-23 | 264:81240 | SHORT RURAL | Equipment Failure | 851270 | 4 | 434.45 | 1737.8 | 0.0010617 | 0.00024439
2012-07-23 | 512:48049 | SHORT RURAL | Equipment Failure | 851291 | 2 | 542 | 1084 | 0.00066229 | 0.00012219
2012-07-23 | ZN12660:PA14 | SHORT RURAL | Equipment Failure | 851314 | 1 | 306.3333 | 306.3333 | 0.00018716 | 6.1097e-05
2012-07-21 | ZN2635:PA14 | URBAN | Operational Error | 851323 | 12 | 2 | 24 | 1.4663e-05 | 0.00073316
2012-07-23 | 807:74184 | SHORT RURAL | Equipment Failure | 851408 | 1 | 229.2667 | 229.2667 | 0.00014007 | 6.1097e-05
2012-07-23 | ZN2400:PA22 | URBAN | Equipment Failure | 851428 | 97 | 77 | 7469 | 0.0045633 | 0.0059264
2012-07-19 | 812:19065 | SHORT RURAL | Equipment Failure | 851453 | 11 | 40 | 440 | 0.00026882 | 0.00067206
2012-07-23 | ZN3154:PA12 | URBAN | Other | 851507 | 1 | 225.45 | 225.45 | 0.00013774 | 6.1097e-05
2012-07-23 | ZN15011:PA2 | URBAN | Other | 851560 | 1 | 368.2333 | 368.2333 | 0.00022498 | 6.1097e-05
2012-07-23 | 504:48032 | URBAN | Other | 851561 | 1 | 303.0167 | 303.0167 | 0.00018513 | 6.1097e-05
2012-07-23 | ZN180:PA19 | URBAN | Other | 851635 | 1 | 169.5833 | 169.5833 | 0.00010361 | 6.1097e-05
2012-07-23 | ZN36300:PA5 | URBAN | Equipment Failure | 851648 | 1 | 318.6833 | 318.6833 | 0.0001947 | 6.1097e-05
2012-07-23 | ZN262:PA32 | URBAN | Other | 851801 | 90 | 63.8167 | 5743.5 | 0.0035091 | 0.0054987
2012-07-23 | 509:48039 | LONG RURAL | Other | 851812 | 2 | 72 | 144 | 8.7979e-05 | 0.00012219
2012-07-23 | ZN342:PA23 | URBAN | Equipment Failure | 851818 | 150 | 232.4 | 18911.2 | 0.011554 | 0.0091645
2012-07-23 | ZN1648:PA2 | URBAN | Equipment Failure | 851820 | 1 | 136 | 136 | 8.3091e-05 | 6.1097e-05
2012-07-23 | ZN342:PA23 | URBAN | Equipment Failure | 851825 | 1 | 41.6667 | 41.6667 | 2.5457e-05 | 6.1097e-05
2012-07-24 | ZN2466:PA32 | URBAN | Equipment Failure | 851828 | 22 | 59 | 1298 | 0.00079304 | 0.0013441
2012-07-24 | ZN9245:PA10 | URBAN | Other | 851833 | 1 | 149 | 149 | 9.1034e-05 | 6.1097e-05
2012-07-24 | ZN2466:PA29 | URBAN | Other | 851834 | 1 | 116.9 | 75.45 | 4.6098e-05 | 6.1097e-05
2012-07-24 | ZN2466:PA32 | URBAN | Other | 851834 | 1 | 116.9 | 84.9 | 5.1871e-05 | 6.1097e-05
2012-07-24 | ZN2466:PA5 | URBAN | Other | 851834 | 1 | 116.9 | 62.1167 | 3.7951e-05 | 6.1097e-05
2012-07-24 | ZN36300:PA3 | URBAN | Vegetation | 851949 | 1 | 171.9 | 171.9 | 0.00010503 | 6.1097e-05
2012-07-24 | 812:19071 | SHORT RURAL | Equipment Failure | 851977 | 1 | 1428.55 | 1428.55 | 0.0008728 | 6.1097e-05
2012-07-24 | ZN12570:PA12 | SHORT RURAL | Other | 851987 | 2042 | 60 | 119879 | 0.073242 | 0.12476
2012-07-24 | ZN1068:PA12 | URBAN | Third Party Impacts | 851999 | 921 | 137 | 121655 | 0.074327 | 0.05627
2012-07-24 | ZN1068:PA16 | URBAN | Third Party Impacts | 851999 | 104 | 137 | 9961.6833 | 0.0060863 | 0.0063541
2012-07-24 | ZN1068:PA21 | SHORT RURAL | Third Party Impacts | 851999 | 17 | 137 | 2329 | 0.0014229 | 0.0010386
2012-07-24 | ZN2466:PA27 | URBAN | Third Party Impacts | 851999 | 84 | 137 | 10920 | 0.0066718 | 0.0051321
2012-07-22 | ZN8000:PA19 | URBAN | Other | 852027 | 42 | 160 | 6720 | 0.0041057 | 0.0025661
2012-07-24 | 509:48039 | LONG RURAL | Other | 852103 | 4 | 422 | 1688 | 0.0010313 | 0.00024439
2012-07-24 | ZN35600:PA9 | URBAN | Other | 852134 | 1 | 328.4167 | 328.4167 | 0.00020065 | 6.1097e-05
2012-07-24 | ZN15009:PA5 | URBAN | Other | 852160 | 1 | 92.25 | 92.25 | 5.6362e-05 | 6.1097e-05
2012-07-24 | ZN12610:PA18 | URBAN | Other | 852231 | 62 | 65 | 3989.7 | 0.0024376 | 0.003788
2012-07-24 | ZN12610:PA2 | URBAN | Other | 852231 | 1 | 65 | 65 | 3.9713e-05 | 6.1097e-05
2012-07-24 | ZN12660:PA14 | SHORT RURAL | Equipment Failure | 852247 | 2 | 286.1833 | 572.3667 | 0.0003497 | 0.00012219
2012-07-24 | ZN180:PA17 | URBAN | Equipment Failure | 852252 | 26 | 61.6333 | 1602.4667 | 0.00097906 | 0.0015885
2012-07-24 | ZN15001:PA15 | URBAN | Equipment Failure | 852256 | 1 | 833.7 | 833.7 | 0.00050936 | 6.1097e-05
2012-07-24 | ZN12690:PA7 | SHORT RURAL | Other | 852260 | 1 | 391 | 391 | 0.00023889 | 6.1097e-05
2012-07-24 | ZN340:PA8 | URBAN | Other | 852268 | 79 | 121.6 | 9606.4 | 0.0058692 | 0.0048266
2012-07-24 | ZN15001:PA2 | URBAN | Equipment Failure | 852277 | 1 | 56.8833 | 56.8833 | 3.4754e-05 | 6.1097e-05
2012-07-24 | ZN15008:PA7 | URBAN | Equipment Failure | 852277 | 1143 | 56.8833 | 48006 | 0.02933 | 0.069834
2012-07-24 | 256:80650 | URBAN | Equipment Failure | 852296 | 149 | 65.1 | 9699.9 | 0.0059263 | 0.0091034
2012-07-25 | ZN10994:PA19 | URBAN | Vegetation | 852308 | 33 | 239 | 7887 | 0.0048187 | 0.0020162
2012-07-25 | 218:7478 | URBAN | Animals | 852317 | 100 | 40 | 4000 | 0.0024439 | 0.0061097
2012-07-25 | ZN2568:PA21 | URBAN | Equipment Failure | 852332 | 1 | 48.4667 | 48.4667 | 2.9612e-05 | 6.1097e-05
2012-07-25 | ZN690:PA30 | URBAN | Other | 852339 | 1 | 156.95 | 156.95 | 9.5891e-05 | 6.1097e-05
2012-07-25 | ZN15006:PA12 | URBAN | Equipment Failure | 852361 | 1 | 288.4167 | 288.4167 | 0.00017621 | 6.1097e-05
2012-07-24 | 812:19072 | SHORT RURAL | Operational Error | 852377 | 11 | 2 | 22 | 1.3441e-05 | 0.00067206
2012-07-25 | ZN874:PA7 | URBAN | Other | 852378 | 1 | 15 | 15 | 9.1645e-06 | 6.1097e-05
2012-07-23 | ZN14891:PA5 | SHORT RURAL | Vegetation | 852452 | 69 | 121 | 8349 | 0.005101 | 0.0042157
2012-07-25 | ZN9037:PA10 | URBAN | Equipment Failure | 852466 | 1 | 172.1167 | 172.1167 | 0.00010516 | 6.1097e-05
2012-07-25 | ZN188:PA16 | URBAN | Third Party Impacts | 852486 | 102 | 61 | 6222 | 0.0038014 | 0.0062319
2012-07-25 | ZN188:PA4 | URBAN | Third Party Impacts | 852486 | 8 | 61 | 481.7333 | 0.00029432 | 0.00048877
2012-07-25 | ZN2568:PA6 | SHORT RURAL | Equipment Failure | 852522 | 1 | 182.4 | 182.4 | 0.00011144 | 6.1097e-05
2012-07-25 | 258:80791 | URBAN | Other | 852541 | 1 | 49.8667 | 49.8667 | 3.0467e-05 | 6.1097e-05
2012-07-25 | ZN14144:PA2 | SHORT RURAL | Other | 852671 | 1 | 260.3667 | 260.3667 | 0.00015908 | 6.1097e-05
2012-07-25 | 509:48039 | LONG RURAL | Vegetation | 852685 | 39 | 1143 | 11583 | 0.0070768 | 0.0023828
2012-07-25 | ZN9550:PA35 | URBAN | Other | 852737 | 65 | 87 | 5655 | 0.003455 | 0.0039713
2012-07-25 | ZN14144:PA10 | SHORT RURAL | Other | 852754 | 1 | 306.2667 | 306.2667 | 0.00018712 | 6.1097e-05
2012-07-25 | 220:8689 | URBAN | Equipment Failure | 852758 | 13 | 784 | 10192 | 0.006227 | 0.00079426
2012-07-25 | ZN269:PA16 | URBAN | Other | 852760 | 78 | 158 | 12286.3 | 0.0075065 | 0.0047656
2012-07-25 | ZN269:PA26 | URBAN | Other | 852760 | 35 | 158 | 5530 | 0.0033787 | 0.0021384
2012-07-25 | ZN269:PA6 | URBAN | Other | 852760 | 72 | 158 | 11376 | 0.0069504 | 0.004399
2012-07-25 | ZN269:PA7 | URBAN | Other | 852760 | 86 | 158 | 13588 | 0.0083018 | 0.0052543
2012-07-25 | ZN10999:PA22 | URBAN | Equipment Failure | 852776 | 13 | 308.25 | 4007.25 | 0.0024483 | 0.00079426
2012-07-25 | 512:48046 | SHORT RURAL | Other | 852780 | 1 | 720 | 720 | 0.0004399 | 6.1097e-05
2012-07-25 | ZN180:PA27 | URBAN | Equipment Failure | 852787 | 106 | 75.5667 | 8010.0667 | 0.0048939 | 0.0064763
2012-07-26 | ZN15001:PA18 | URBAN | Equipment Failure | 853008 | 1 | 403.2167 | 403.2167 | 0.00024635 | 6.1097e-05
2012-07-26 | ZN129:PA18 | URBAN | Equipment Failure | 853010 | 26 | 925 | 6136 | 0.0037489 | 0.0015885
2012-07-26 | ZN129:PA5 | URBAN | Equipment Failure | 853010 | 44 | 925 | 25480 | 0.015568 | 0.0026883
2012-07-26 | ZN5868:PA14 | URBAN | Equipment Failure | 853011 | 69 | 144 | 9936 | 0.0060706 | 0.0042157
2012-07-26 | ZN15001:PA18 | URBAN | Other | 853013 | 1 | 78.2333 | 78.2333 | 4.7798e-05 | 6.1097e-05
2012-07-26 | ZN965:PA42 | URBAN | Third Party Impacts | 853016 | 1 | 685.1333 | 685.1333 | 0.0004186 | 6.1097e-05
2012-07-26 | ZN195:PA30 | URBAN | Equipment Failure | 853020 | 1 | 1118.35 | 1118.35 | 0.00068328 | 6.1097e-05
2012-07-26 | ZN965:PA42 | URBAN | Third Party Impacts | 853042 | 1 | 360.8833 | 360.8833 | 0.00022049 | 6.1097e-05
2012-07-26 | ZN12650:PA1 | SHORT RURAL | Other | 853108 | 1 | 198.1167 | 198.1167 | 0.00012104 | 6.1097e-05
2012-07-26 | 238:34140 | URBAN | Third Party Impacts | 853130 | 1 | 298.8833 | 298.8833 | 0.00018261 | 6.1097e-05
2012-07-26 | 507:80931 | URBAN | Third Party Impacts | 853152 | 1 | 131.1167 | 131.1167 | 8.0108e-05 | 6.1097e-05
2012-07-26 | ZN35600:PA25 | URBAN | Equipment Failure | 853158 | 1 | 97.1167 | 97.1167 | 5.9335e-05 | 6.1097e-05
2012-07-26 | ZN35600:PA25 | URBAN | Equipment Failure | 853166 | 1 | 86.35 | 86.35 | 5.2757e-05 | 6.1097e-05
2012-07-26 | 243:80081 | URBAN | Third Party Impacts | 853173 | 1 | 234.0333 | 234.0333 | 0.00014299 | 6.1097e-05
2012-07-26 | ZN3472:PA23 | URBAN | Other | 853183 | 1 | 159.3667 | 159.3667 | 9.7368e-05 | 6.1097e-05
2012-07-26 | ZN5868:PA14 | URBAN | Other | 853201 | 1 | 203.4333 | 203.4333 | 0.00012429 | 6.1097e-05
2012-07-26 | 235:8684 | SHORT RURAL | Other | 853218 | 1 | 191 | 191 | 0.0001167 | 6.1097e-05
2012-07-16 | 807:74184 | SHORT RURAL | Equipment Failure | 853347 | 1 | 14320 | 14320 | 0.008749 | 6.1097e-05
2012-07-26 | ZN3472:PA23 | URBAN | Other | 853366 | 1 | 353.25 | 353.25 | 0.00021583 | 6.1097e-05
2012-07-26 | 806:74080 | SHORT RURAL | Other | 853377 | 1 | 227.9833 | 227.9833 | 0.00013929 | 6.1097e-05
2012-07-26 | ZN12630:PA4 | SHORT RURAL | Equipment Failure | 853390 | 1 | 1107.0833 | 1107.0833 | 0.00067639 | 6.1097e-05
2012-07-26 | ZN965:PA46 | URBAN | Equipment Failure | 853437 | 7 | 1068 | 7476 | 0.0045676 | 0.00042768
2012-07-27 | ZN80:PA24 | URBAN | Other | 853450 | 8 | 102 | 816 | 0.00049855 | 0.00048878
2012-07-27 | 507:80922 | SHORT RURAL | Other | 853465 | 14 | 237.55 | 3325.7 | 0.0020319 | 0.00085536
2012-07-27 | ZN1287:PA4 | URBAN | Other | 853471 | 1 | 929.8833 | 929.8833 | 0.00056813 | 6.1097e-05
2012-07-27 | ZN15014:PA18 | URBAN | Equipment Failure | 853477 | 1 | 736.5333 | 736.5333 | 0.00045 | 6.1097e-05
2012-07-26 | 509:48039 | LONG RURAL | Vegetation | 853502 | 8 | 180 | 1440 | 0.0008798 | 0.00048878
2012-07-26 | 810:74054 | LONG RURAL | Other | 853522 | 1 | 66 | 66 | 4.0324e-05 | 6.1097e-05
2012-07-26 | 810:74054 | LONG RURAL | Other | 853532 | 1 | 86 | 86 | 5.2543e-05 | 6.1097e-05
2012-07-27 | ZN188:PA41 | URBAN | Equipment Failure | 853598 | 1 | 124 | 80.5333 | 4.9203e-05 | 6.1097e-05
2012-07-27 | ZN2602:PA32 | URBAN | Equipment Failure | 853598 | 12 | 124 | 1488 | 0.00090912 | 0.00073316
2012-07-27 | ZN2602:PA42 | URBAN | Equipment Failure | 853598 | 495 | 124 | 61066.5 | 0.03731 | 0.030243
2012-07-27 | ZN187:PA17 | URBAN | Operational Error | 853625 | 1180 | 140 | 115910 | 0.070818 | 0.072094
2012-07-27 | ZN187:PA19 | URBAN | Operational Error | 853625 | 1 | 140 | 87 | 5.3154e-05 | 6.1097e-05
2012-07-27 | ZN187:PA13 | URBAN | Other | 853644 | 1 | 69.7833 | 69.7833 | 4.2636e-05 | 6.1097e-05
2012-07-27 | ZN187:PA13 | URBAN | Other | 853650 | 1 | 58.75 | 58.75 | 3.5895e-05 | 6.1097e-05
2012-07-27 | 218:7476 | URBAN | Other | 853671 | 1 | 61.05 | 61.05 | 3.73e-05 | 6.1097e-05
2012-07-27 | 509:48040 | SHORT RURAL | Equipment Failure | 853678 | 22 | 102.8333 | 2262.3333 | 0.0013822 | 0.0013441
2012-07-27 | ZN9550:PA32 | URBAN | Equipment Failure | 853729 | 31 | 406 | 12586 | 0.0076897 | 0.001894
2012-07-27 | ZN187:PA17 | URBAN | Other | 853731 | 359 | 131 | 37249 | 0.022758 | 0.021934
2012-07-27 | ZN180:PA18 | URBAN | Third Party Impacts | 853795 | 1 | 197.3667 | 197.3667 | 0.00012059 | 6.1097e-05
2012-07-27 | 504:48034 | URBAN | Other | 853809 | 1 | 105.3833 | 105.3833 | 6.4386e-05 | 6.1097e-05
2012-07-27 | 260:33344 | URBAN | Other | 853831 | 1 | 164.8667 | 164.8667 | 0.00010073 | 6.1097e-05
2012-07-27 | 507:80922 | SHORT RURAL | Equipment Failure | 853847 | 56 | 58.9167 | 2571.55 | 0.0015711 | 0.0034214
2012-07-27 | 523:33501 | SHORT RURAL | Equipment Failure | 853852 | 1 | 111 | 111 | 6.7818e-05 | 6.1097e-05
2012-07-27 | ZN187:PA17 | URBAN | Other | 853857 | 313 | 148 | 46324 | 0.028303 | 0.019123
2012-07-27 | ZN15005:PA12 | URBAN | Equipment Failure | 853876 | 247 | 88 | 21316 | 0.013023 | 0.015091
2012-07-27 | ZN116:PA47 | URBAN | Equipment Failure | 853882 | 1 | 270.3333 | 270.3333 | 0.00016517 | 6.1097e-05
2012-07-27 | ZN10993:PA7 | URBAN | Equipment Failure | 853884 | 143 | 81.4167 | 11642.5833 | 0.0071133 | 0.0087369
2012-07-28 | ZN965:PA33 | URBAN | Equipment Failure | 853894 | 1 | 83 | 83 | 5.0711e-05 | 6.1097e-05
2012-07-28 | ZN965:PA43 | URBAN | Equipment Failure | 853894 | 1059 | 83 | 63844 | 0.039007 | 0.064702
2012-07-28 | 235:2123 | URBAN | Other | 853977 | 1 | 79.2333 | 79.2333 | 4.8409e-05 | 6.1097e-05
2012-07-28 | ZN14891:PA21 | SHORT RURAL | Other | 853983 | 1 | 170.5167 | 170.5167 | 0.00010418 | 6.1097e-05
2012-07-28 | ZN1193:PA1 | URBAN | Equipment Failure | 854001 | 1 | 294.35 | 294.35 | 0.00017984 | 6.1097e-05
2012-07-28 | ZN9900:PA21 | URBAN | Equipment Failure | 854055 | 1 | 1247.35 | 1247.35 | 0.00076209 | 6.1097e-05
2012-07-29 | ZN4545:PA41 | URBAN | Equipment Failure | 854066 | 104 | 112 | 11648 | 0.0071166 | 0.0063541
2012-07-29 | 524:33570 | SHORT RURAL | Third Party Impacts | 854072 | 8 | 180 | 1440 | 0.0008798 | 0.00048878
2012-07-29 | 509:48040 | SHORT RURAL | Other | 854076 | 1 | 222.15 | 222.15 | 0.00013573 | 6.1097e-05
2012-07-29 | 238:34141 | SHORT RURAL | Equipment Failure | 854085 | 9 | 336.2833 | 3026.55 | 0.0018491 | 0.00054987
2012-07-29 | 813:89055 | SHORT RURAL | Other | 854093 | 1 | 264.4167 | 264.4167 | 0.00016155 | 6.1097e-05
2012-07-29 | 260:33353 | URBAN | Vegetation | 854122 | 1 | 84.9833 | 84.9833 | 5.1922e-05 | 6.1097e-05
2012-07-29 | ZN14143:PA6 | URBAN | Animals | 854144 | 1 | 516.2667 | 516.2667 | 0.00031542 | 6.1097e-05
2012-07-29 | 509:48039 | LONG RURAL | Vegetation | 854146 | 4 | 231.85 | 927.4 | 0.00056661 | 0.00024439
2012-07-29 | 264:81241 | SHORT RURAL | Equipment Failure | 854181 | 1 | 120.6833 | 120.6833 | 7.3734e-05 | 6.1097e-05
2012-07-29 | ZN3672:PA13 | URBAN | Equipment Failure | 854195 | 1 | 340.9167 | 340.9167 | 0.00020829 | 6.1097e-05
2012-07-29 | ZN9900:PA1 | URBAN | Third Party Impacts | 854197 | 1 | 61.7167 | 61.7167 | 3.7707e-05 | 6.1097e-05
2012-07-29 | ZN2473:PA15 | URBAN | Other | 854198 | 76 | 117 | 8832.4667 | 0.0053964 | 0.0046434
2012-07-29 | ZN2473:PA4 | URBAN | Other | 854198 | 122 | 117 | 14274 | 0.008721 | 0.0074538
2012-07-29 | 526:34636 | SHORT RURAL | Equipment Failure | 854206 | 2 | 115 | 230 | 0.00014052 | 0.00012219
2012-07-29 | 217:33610 | URBAN | Other | 854212 | 1 | 146.5833 | 146.5833 | 8.9558e-05 | 6.1097e-05
2012-07-29 | ZN262:PA19 | URBAN | Equipment Failure | 854213 | 1 | 94.2167 | 94.2167 | 5.7564e-05 | 6.1097e-05
2012-07-29 | ZN262:PA19 | URBAN | Equipment Failure | 854219 | 1 | 66.7833 | 66.7833 | 4.0803e-05 | 6.1097e-05
2012-07-30 | ZN1673:PA21 | URBAN | Third Party Impacts | 854232 | 54 | 90.8833 | 4907.7 | 0.0029985 | 0.0032992
2012-07-30 | 509:48039 | LONG RURAL | Equipment Failure | 854238 | 2 | 112 | 224 | 0.00013686 | 0.00012219
2012-07-30 | ZN12610:PA22 | URBAN | Equipment Failure | 854239 | 12 | 106 | 1272 | 0.00077715 | 0.00073316
2012-07-30 | ZN1788:PA17 | URBAN | Other | 854254 | 1 | 158.3333 | 158.3333 | 9.6737e-05 | 6.1097e-05
2012-07-30 | 513:48051 | URBAN | Other | 854257 | 1 | 121.3167 | 121.3167 | 7.4121e-05 | 6.1097e-05
2012-07-30 | 220:8687 | URBAN | Equipment Failure | 854332 | 2 | 133.8167 | 241.85 | 0.00014776 | 0.00012219
2012-07-30 | 208:72 | URBAN | Animals | 854371 | 10 | 79 | 790 | 0.00048267 | 0.00061097
2012-07-29 | ZN1788:PA17 | URBAN | Equipment Failure | 854392 | 1386 | 50 | 69300 | 0.04234 | 0.08468
2012-07-30 | 260:33347 | SHORT RURAL | Equipment Failure | 854401 | 1 | 181 | 181 | 0.00011059 | 6.1097e-05
2012-07-30 | ZN10999:PA25 | URBAN | Other | 854455 | 1 | 121.7667 | 121.7667 | 7.4396e-05 | 6.1097e-05
2012-07-30 | ZN12580:PA1 | URBAN | Other | 854468 | 1 | 250.7167 | 250.7167 | 0.00015318 | 6.1097e-05
2012-07-30 | ZN9700:PA20 | URBAN | Third Party Impacts | 854477 | 32 | 169.4333 | 5421.8667 | 0.0033126 | 0.0019551
2012-07-30 | ZN167:PA13 | URBAN | Equipment Failure | 854513 | 1 | 1262.1833 | 1262.1833 | 0.00077116 | 6.1097e-05
2012-07-30 | ZN4545:PA2 | URBAN | Equipment Failure | 854561 | 1 | 257.3167 | 257.3167 | 0.00015721 | 6.1097e-05
2012-07-30 | 223:14394 | URBAN | Vegetation | 854581 | 117 | 24.35 | 2848.95 | 0.0017406 | 0.0071484
2012-07-30 | 243:80084 | SHORT RURAL | Other | 854636 | 1 | 143.25 | 143.25 | 8.7521e-05 | 6.1097e-05
2012-07-30 | 227:13020 | SHORT RURAL | Vegetation | 854657 | 1 | 128.1833 | 128.1833 | 7.8316e-05 | 6.1097e-05
2012-07-30 | ZN965:PA38 | URBAN | Equipment Failure | 854671 | 31 | 252.2333 | 7819.2333 | 0.0047773 | 0.001894
2012-07-30 | ZN35600:PA1 | URBAN | Equipment Failure | 854689 | 66 | 164.4 | 3366 | 0.0020565 | 0.0040324
2012-07-30 | ZN965:PA28 | SHORT RURAL | Equipment Failure | 854689 | 1 | 164.4 | 164.4 | 0.00010044 | 6.1097e-05
2012-07-30 | 513:48050 | SHORT RURAL | Other | 854692 | 70 | 62.2333 | 4356.3333 | 0.0026616 | 0.0042768
2012-07-30 | 202:34260 | URBAN | Equipment Failure | 854693 | 2598 | 77 | 200046 | 0.12222 | 0.15873
2012-07-30 | 256:80650 | URBAN | Equipment Failure | 854693 | 620 | 77 | 47740 | 0.029168 | 0.03788
2012-07-30 | 202:34231 37 42 | URBAN | Third Party Impacts | 854706 | 56 | 403 | 7584.05 | 0.0046336 | 0.0034214
2012-07-30 | ZN2473:PA21 | URBAN | Other | 854719 | 116 | 185 | 21460 | 0.013111 | 0.0070873
2012-07-30 | ZN2473:PA26 | URBAN | Other | 854719 | 235 | 185 | 43475 | 0.026562 | 0.014358
2012-07-30 | 217:33610 | URBAN | Other | 854724 | 170 | 45 | 7650 | 0.0046739 | 0.010386
2012-07-30 | ZN15008:PA7 | URBAN | Equipment Failure | 854735 | 2717 | 204 | 239175 | 0.14613 | 0.166
2012-07-30 | ZN1164:PA11 | URBAN | Vegetation | 854747 | 1 | 503.1167 | 503.1167 | 0.00030739 | 6.1097e-05
2012-07-30 | ZN3472:PA30 | URBAN | Other | 854761 | 57 | 83.6833 | 4769.95 | 0.0029143 | 0.0034825
2012-07-30 | ZN1673:PA7 | URBAN | Equipment Failure | 854764 | 48 | 62 | 2976 | 0.0018182 | 0.0029327
2012-07-30 | ZN12640:PA18 | SHORT RURAL | Equipment Failure | 854766 | 1 | 172.7167 | 172.7167 | 0.00010552 | 6.1097e-05
2012-07-31 | 221:11894 | URBAN | Animals | 854767 | 61 | 52 | 3172 | 0.001938 | 0.003727
2012-07-31 | ZN2310:PA21 | URBAN | Equipment Failure | 854770 | 150 | 71 | 8250 | 0.0050406 | 0.0091646
2012-07-31 | ZN2310:PA33 | URBAN | Equipment Failure | 854770 | 1821 | 71 | 102571 | 0.062668 | 0.11126
2012-07-31 | ZN1285:PA27 | URBAN | Other | 854774 | 1 | 79.9333 | 79.9333 | 4.8837e-05 | 6.1098e-05
2012-07-31 | ZN188:PA2 | URBAN | Other | 854776 | 48 | 202.4667 | 9718.4 | 0.0059377 | 0.0029327
2012-07-31 | 256:80650 | URBAN | Equipment Failure | 854796 | 1 | 122.25 | 122.25 | 7.4692e-05 | 6.1098e-05
2012-07-31 | ZN12570:PA1 | SHORT RURAL | Other | 854818 | 1 | 575.4 | 575.4 | 0.00035156 | 6.1098e-05
2012-07-31 | ZN1673:PA19 | URBAN | Other | 854853 | 1 | 72.1667 | 72.1667 | 4.4092e-05 | 6.1098e-05
2012-07-26 | ZN129:PA5 | URBAN | Other | 854894 | 20 | 301 | 6020 | 0.003678 | 0.0012219
2012-07-31 | 802:82225 | SHORT RURAL | Equipment Failure | 854929 | 1 | 83.1667 | 83.1667 | 5.0813e-05 | 6.1098e-05
2012-07-31 | ZN12580:PA16 | URBAN | Third Party Impacts | 854970 | 1 | 590.9333 | 590.9333 | 0.00036105 | 6.1098e-05
2012-07-31 | ZN180:PA17 | URBAN | Equipment Failure | 855178 | 13 | 1475 | 19175 | 0.011715 | 0.00079427
2012-07-31 | ZN262:PA6 | URBAN | Equipment Failure | 855187 | 1 | 403.0333 | 403.0333 | 0.00024624 | 6.1098e-05
2012-07-31 | ZN15011:PA10 | URBAN | Vegetation | 855192 | 82 | 47 | 3854 | 0.0023547 | 0.00501
2012-07-31 | ZN14892:PA8 | URBAN | Equipment Failure | 855203 | 1 | 1114.15 | 1114.15 | 0.00068072 | 6.1098e-05
2012-07-31 | 210:8681 | URBAN | Other | 855205 | 1 | 88.1 | 88.1 | 5.3827e-05 | 6.1098e-05
2012-07-31 | ZN1285:PA24 | URBAN | Equipment Failure | 855255 | 36 | 588.15 | 21173.4 | 0.012936 | 0.0021995
2012-08-01 | 812:19072 | SHORT RURAL | Other | 855258 | 2 | 198 | 396 | 0.00024195 | 0.0001222
2012-08-01 | 264:81244 | URBAN | Other | 855264 | 66 | 212.1 | 13998.6 | 0.0085529 | 0.0040325
2012-08-01 | ZN711:PA21 | URBAN | Equipment Failure | 855266 | 77 | 808 | 25508 | 0.015585 | 0.0047045
2012-08-01 | ZN12570:PA5 | URBAN | Equipment Failure | 855291 | 1 | 287.35 | 287.35 | 0.00017557 | 6.1098e-05
2012-07-31 | ZN9900:PA21 | URBAN | Operational Error | 855299 | 40 | 80 | 3200 | 0.0019551 | 0.0024439
2012-08-01 | 243:80080 | SHORT RURAL | Equipment Failure | 855311 | 3 | 125 | 336.5833 | 0.00020565 | 0.00018329
2012-08-01 | ZN1164:PA21 | URBAN | Equipment Failure | 855313 | 2 | 528.4167 | 1056.8333 | 0.0006457 | 0.0001222
2012-08-01 | 803:74010 | SHORT RURAL | Other | 855327 | 1 | 134.7333 | 134.7333 | 8.2319e-05 | 6.1098e-05
2012-07-31 | 232:11459 | SHORT RURAL | Equipment Failure | 855332 | 1 | 1425 | 1425 | 0.00087064 | 6.1098e-05
2012-08-01 | ZN14891:PA16 | SHORT RURAL | Third Party Impacts | 855498 | 1 | 460.8833 | 460.8833 | 0.00028159 | 6.1098e-05
2012-08-01 | ZN15004:PA3 | URBAN | Other | 855533 | 1 | 364.95 | 364.95 | 0.00022298 | 6.1098e-05
2012-08-01 | ZN35370:PA8 | SHORT RURAL | Third Party Impacts | 855538 | 8 | 236 | 1888 | 0.0011535 | 0.00048878
2012-08-01 | ZN15002:PA6 | URBAN | Other | 855542 | 1 | 105.3667 | 105.3667 | 6.4377e-05 | 6.1098e-05
2012-08-01 | 813:89061 | LONG RURAL | Other | 855600 | 1 | 187.5333 | 187.5333 | 0.00011458 | 6.1098e-05
2012-08-01 | ZN12660:PA14 | SHORT RURAL | Vegetation | 855623 | 1 | 365.0333 | 365.0333 | 0.00022303 | 6.1098e-05
2012-08-01 | 264:81240 | SHORT RURAL | Other | 855693 | 37 | 62.0333 | 2295.2333 | 0.0014023 | 0.0022606
2012-08-01 | ZN12620:PA11 | SHORT RURAL | Other | 855729 | 18 | 39 | 702 | 0.00042891 | 0.0010998
2012-08-02 | ZN12580:PA1 | URBAN | Equipment Failure | 855746 | 1896 | 122 | 154286 | 0.094266 | 0.11584
2012-08-02 | ZN9037:PA16 | URBAN | Vegetation | 855823 | 1 | 102.05 | 102.05 | 6.2351e-05 | 6.1098e-05
2012-08-02 | ZN15008:PA5 | URBAN | Third Party Impacts | 855927 | 19 | 216.8167 | 4119.5167 | 0.002517 | 0.0011609
2012-08-02 | ZN847:PA2 | URBAN | Third Party Impacts | 855990 | 54 | 137.4 | 7419.6 | 0.0045333 | 0.0032993
2012-08-02 | ZN269:PA19 | URBAN | Equipment Failure | 856063 | 1334 | 103 | 110762 | 0.067674 | 0.081505
2012-08-02 | ZN269:PA26 | URBAN | Equipment Failure | 856063 | 1462 | 103 | 121168 | 0.074032 | 0.089326
2012-08-02 | ZN847:PA10 | URBAN | Vegetation | 856079 | 39 | 116 | 4524 | 0.0027641 | 0.0023828
2012-08-02 | ZN2602:PA10 | URBAN | Third Party Impacts | 856100 | 1 | 382.8333 | 382.8333 | 0.00023391 | 6.1098e-05
2012-08-02 | ZN15015:PA5 | URBAN | Third Party Impacts | 856117 | 184 | 85 | 13617 | 0.0083198 | 0.011242
2012-08-02 | ZN269:PA6 | URBAN | Equipment Failure | 856119 | 1 | 32.0333 | 32.0333 | 1.9572e-05 | 6.1098e-05
2012-08-02 | ZN398:PA20 | URBAN | Other | 856132 | 1 | 129.0333 | 129.0333 | 7.8837e-05 | 6.1098e-05
2012-08-02 | ZN965:PA33 | URBAN | Equipment Failure | 856137 | 82 | 193.75 | 15887.5 | 0.009707 | 0.0050101
2012-08-02 | ZN12640:PA13 | SHORT RURAL | Other | 856139 | 1 | 240.7833 | 240.7833 | 0.00014711 | 6.1098e-05
2012-08-02 | 812:19071 | SHORT RURAL | Other | 856161 | 1 | 234.7667 | 234.7667 | 0.00014344 | 6.1098e-05
2012-08-02 | ZN398:PA8 | URBAN | Equipment Failure | 856193 | 1 | 670.8833 | 670.8833 | 0.0004099 | 6.1098e-05
2012-08-02 | ZN965:PA46 | URBAN | Equipment Failure | 856194 | 63 | 650.0167 | 40951.05 | 0.02502 | 0.0038492
2012-08-03 | ZN7900:PA17 | URBAN | Equipment Failure | 856197 | 135 | 62 | 8356 | 0.0051054 | 0.0082483
2012-08-03 | 801:74121 | SHORT RURAL | Other | 856208 | 1 | 168 | 168 | 0.00010265 | 6.1098e-05
2012-08-03 | ZN80:PA40 | URBAN | Third Party Impacts | 856216 | 19 | 55 | 1045 | 0.00063848 | 0.0011609
2012-08-03 | ZN12690:PA3 | SHORT RURAL | Vegetation | 856363 | 29 | 59 | 1711 | 0.0010454 | 0.0017719
2012-08-03 | ZN195:PA11 | URBAN | Other | 856436 | 1 | 100.55 | 100.55 | 6.1434e-05 | 6.1098e-05
2012-08-03 | ZN15012:PA6 | URBAN | Equipment Failure | 856506 | 54 | 85.5 | 4617 | 0.0028209 | 0.0032993
2012-08-03 | 206:34440 | URBAN | Equipment Failure | 856540 | 31 | 32 | 992 | 0.0006061 | 0.0018941
2012-08-04 | ZN1788:PA14 | URBAN | Other | 856610 | 1 | 279.0833 | 279.0833 | 0.00017052 | 6.1098e-05
2012-08-04 | 523:33501 | SHORT RURAL | Other | 856638 | 1 | 47.8833 | 47.8833 | 2.9256e-05 | 6.1098e-05
2012-08-04 | ZN10993:PA7 | URBAN | Equipment Failure | 856665 | 713 | 160 | 46440 | 0.028374 | 0.043563
2012-08-04 | ZN12610:PA7 | URBAN | Equipment Failure | 856686 | 36 | 91.1833 | 3282.6 | 0.0020056 | 0.0021995
2012-08-04 | ZN195:PA11 | URBAN | Other | 856711 | 21 | 88.2 | 1852.2 | 0.0011317 | 0.0012831
2012-08-04 | ZN1788:PA7 | SHORT RURAL | Third Party Impacts | 856721 | 1 | 111 | 111 | 6.7819e-05 | 6.1098e-05
2012-08-04 | ZN1788:PA8 | URBAN | Third Party Impacts | 856721 | 119 | 111 | 13145.5333 | 0.0080317 | 0.0072707
2012-08-05 | ZN15004:PA5 | URBAN | Other | 856740 | 32 | 79.5167 | 2544.5333 | 0.0015547 | 0.0019551
2012-08-05 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 856763 | 1 | 376.1 | 376.1 | 0.00022979 | 6.1098e-05
2012-08-05 | 512:48049 | SHORT RURAL | Animals | 856774 | 3 | 51.3333 | 154 | 9.4092e-05 | 0.0001833
2012-08-05 | ZN180:PA34 | URBAN | Other | 856786 | 1 | 398.2333 | 398.2333 | 0.00024331 | 6.1098e-05
2012-08-05 | ZN14891:PA1 | SHORT RURAL | Vegetation | 856797 | 13 | 94 | 1222 | 0.00074662 | 0.00079428
2012-08-05 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 856815 | 2 | 103 | 206 | 0.00012586 | 0.0001222
2012-08-05 | ZN262:PA5 | URBAN | Other | 856831 | 104 | 88.0833 | 9160.6667 | 0.005597 | 0.0063542
2012-08-05 | ZN262:PA5 | URBAN | Equipment Failure | 856854 | 1 | 278.35 | 278.35 | 0.00017007 | 6.1098e-05
2012-08-05 | ZN1610:PA11 | URBAN | Equipment Failure | 856860 | 79 | 52.6667 | 4160.6667 | 0.0025421 | 0.0048268
2012-08-05 | 513:48059 | SHORT RURAL | Other | 856875 | 1 | 589.4 | 589.4 | 0.00036011 | 6.1098e-05
2012-08-06 | ZN398:PA8 | URBAN | Equipment Failure | 856879 | 2463 | 83 | 198239 | 0.12112 | 0.15049
2012-08-06 | 264:81240 | SHORT RURAL | Operational Error | 856917 | 828 | 7 | 5796 | 0.0035413 | 0.050589
2012-08-06 | ZN10990:PA6 | URBAN | Third Party Impacts | 856948 | 61 | 39 | 2379 | 0.0014535 | 0.003727
2012-07-22 | ZN9252:PA2 | URBAN | Equipment Failure | 857038 | 1707 | 215 | 267524 | 0.16345 | 0.10429
2012-08-06 | ZN269:PA6 | URBAN | Equipment Failure | 857054 | 1 | 668.3667 | 668.3667 | 0.00040836 | 6.1098e-05
2012-08-06 | 813:89062 | SHORT RURAL | Other | 857062 | 1 | 126.3833 | 126.3833 | 7.7218e-05 | 6.1098e-05
2012-08-03 | ZN80:PA40 | URBAN | Third Party Impacts | 857138 | 3 | 850 | 2550 | 0.001558 | 0.0001833
2012-08-06 | ZN1287:PA4 | URBAN | Equipment Failure | 857149 | 1 | 182.8667 | 182.8667 | 0.00011173 | 6.1098e-05
2012-08-06 | 206:34432 | URBAN | Third Party Impacts | 857213 | 1 | 102.5833 | 102.5833 | 6.2677e-05 | 6.1098e-05
2012-08-06 | ZN874:PA18 | SHORT RURAL | Other | 857256 | 1 | 109.15 | 109.15 | 6.6689e-05 | 6.1098e-05
2012-08-06 | ZN14143:PA12 | SHORT RURAL | Other | 857286 | 36 | 79.5667 | 2864.4 | 0.0017501 | 0.0021995
2012-08-06 | ZN3425:PA28 | URBAN | Other | 857291 | 1 | 175.9167 | 175.9167 | 0.00010748 | 6.1098e-05
2012-08-06 | ZN12640:PA6 | URBAN | Equipment Failure | 857323 | 82 | 125.8333 | 10318.3333 | 0.0063043 | 0.0050101
2012-08-06 | ZN12640:PA6 | URBAN | Equipment Failure | 857332 | 15 | 112.45 | 1686.75 | 0.0010306 | 0.00091648
2012-08-07 | ZN167:PA21 | URBAN | Third Party Impacts | 857384 | 1 | 251.5833 | 251.5833 | 0.00015371 | 6.1099e-05
2012-08-07 | ZN167:PA21 | URBAN | Third Party Impacts | 857386 | 1 | 249.1 | 249.1 | 0.0001522 | 6.1099e-05
2012-08-07 | 501:48115 | SHORT RURAL | Equipment Failure | 857432 | 1 | 83.2 | 83.2 | 5.0834e-05 | 6.1099e-05
2012-08-07 | ZN3155:PA19 | URBAN | Other | 857454 | 46 | 113 | 5198 | 0.0031759 | 0.0028105
2012-08-07 | ZN3155:PA34 | SHORT RURAL | Other | 857454 | 19 | 113 | 2129.5833 | 0.0013011 | 0.0011609
2012-08-07 | ZN12650:PA12 | URBAN | Equipment Failure | 857455 | 1 | 5.0833 | 5.0833 | 3.1058e-06 | 6.1099e-05
2012-08-07 | 232:11457 | URBAN | Equipment Failure | 857494 | 1 | 162.35 | 162.35 | 9.9193e-05 | 6.1099e-05
2012-08-07 | 807:74183 | SHORT RURAL | Equipment Failure | 857506 | 1 | 220.5667 | 220.5667 | 0.00013476 | 6.1099e-05
2012-08-07 | ZN195:PA23 | URBAN | Third Party Impacts | 857612 | 50 | 10 | 500 | 0.00030549 | 0.0030549
2012-08-07 | 813:89059 | URBAN | Other | 857675 | 1 | 282.85 | 282.85 | 0.00017282 | 6.1099e-05
2012-08-07 | 258:80791 | URBAN | Equipment Failure | 857764 | 1 | 125.1 | 125.1 | 7.6434e-05 | 6.1099e-05
2012-08-07 | ZN901:PA14 | URBAN | Equipment Failure | 857773 | 1 | 1096.25 | 1096.25 | 0.00066979 | 6.1099e-05
2012-08-07 | 812:19066 | SHORT RURAL | Equipment Failure | 857791 | 1 | 95.3167 | 95.3167 | 5.8237e-05 | 6.1099e-05
2012-08-07 | ZN14891:PA21 | SHORT RURAL | Equipment Failure | 857793 | 1 | 90 | 72 | 4.3991e-05 | 6.1099e-05
2012-08-07 | ZN14892:PA1 | SHORT RURAL | Equipment Failure | 857793 | 900 | 90 | 67545 | 0.041269 | 0.054989
2012-08-07 | ZN3155:PA23 | URBAN | Equipment Failure | 857802 | 35 | 1448.1167 | 49910 | 0.030494 | 0.0021384
2012-08-07 | ZN342:PA17 | URBAN | Equipment Failure | 857802 | 1 | 1448.1167 | 1429.95 | 0.00087368 | 6.1099e-05
2012-08-08 | ZN15006:PA12 | URBAN | Equipment Failure | 857815 | 46 | 133.9 | 6159.4 | 0.0037727 | 0.0028175
2012-08-08 | 515:35200 | URBAN | Equipment Failure | 857832 | 7 | 92 | 644 | 0.00039445 | 0.00042875
2012-08-08 | ZN2466:PA6 | URBAN | Other | 857933 | 1 | 95.5167 | 95.5167 | 5.8504e-05 | 6.1251e-05
2012-08-08 | ZN2466:PA44 | URBAN | Other | 857958 | 1 | 80.8667 | 80.8667 | 4.9531e-05 | 6.1251e-05
2012-08-08 | 203:8090 | URBAN | Equipment Failure | 858005 | 3 | 93.8167 | 278.7667 | 0.00017075 | 0.00018375
2012-08-08 | 516:48065 | SHORT RURAL | Other | 858059 | 1 | 97.4667 | 97.4667 | 5.9699e-05 | 6.1251e-05
2012-08-08 | ZN1788:PA8 | URBAN | Third Party Impacts | 858115 | 1 | 262.3833 | 262.3833 | 0.00016071 | 6.1251e-05
2012-08-08 | ZN15008:PA10 | URBAN | Other | 858206 | 1 | 74.7333 | 74.7333 | 4.5775e-05 | 6.1251e-05
2012-08-08 | ZN3288:PA43 44GHJ | CBD | Equipment Failure | 858246 | 1 | 1050.25 | 1050.25 | 0.00064328 | 6.1251e-05
2012-08-08 | ZN15006:PA13 | URBAN | Equipment Failure | 858272 | 43 | 142.7667 | 6138.9667 | 0.0037602 | 0.0026338
2012-08-08 | 217:33611 | URBAN | Equipment Failure | 858288 | 1 | 214.9333 | 214.9333 | 0.00013165 | 6.1251e-05
2012-08-08 | 509:48039 | LONG RURAL | Equipment Failure | 858295 | 2 | 74 | 148 | 9.0651e-05 | 0.0001225
2012-08-08 | 206:34441 | URBAN | Vegetation | 858296 | 36 | 58 | 2088 | 0.0012789 | 0.002205
2012-08-08 | 504:48033 | SHORT RURAL | Other | 858298 | 1 | 160.5 | 160.5 | 9.8307e-05 | 6.1251e-05
2012-08-09 | ZN2310:PA17 | URBAN | Equipment Failure | 858302 | 8 | 549 | 4392 | 0.0026939 | 0.00049069
2012-08-09 | ZN15004:PA5 | URBAN | Other | 858304 | 32 | 139.45 | 4462.4 | 0.0027371 | 0.0019627
2012-08-09 | ZN2602:PA22 | URBAN | Equipment Failure | 858328 | 1 | 299.7167 | 299.7167 | 0.00018383 | 6.1336e-05
2012-08-09 | ZN12610:PA22 | URBAN | Other | 858335 | 1 | 235.25 | 235.25 | 0.00014429 | 6.1336e-05
2012-08-09 | ZN3425:PA28 | URBAN | Equipment Failure | 858336 | 1 | 352.9167 | 352.9167 | 0.00021646 | 6.1336e-05
2012-08-09 | ZN80:PA24 | URBAN | Third Party Impacts | 858370 | 16 | 152 | 2432 | 0.0014917 | 0.00098137
2012-08-09 | 810:74050 | SHORT RURAL | Equipment Failure | 858489 | 79 | 108.9667 | 8608.3667 | 0.00528 | 0.0048455
2012-08-03 | ZN12630:PA5 | SHORT RURAL | Equipment Failure | 858491 | 6 | 361 | 2166 | 0.0013234 | 0.00036659
2012-08-09 | ZN1068:PA18 | URBAN | Other | 858565 | 14 | 210.5 | 2947 | 0.0018076 | 0.0008587
2012-08-09 | 238:34144 | URBAN | Third Party Impacts | 858575 | 829 | 64 | 53056 | 0.032542 | 0.050847
2012-08-09 | 240:34835 | URBAN | Other | 858581 | 1 | 80.4 | 80.4 | 4.9314e-05 | 6.1336e-05
2012-08-09 | ZN12610:PA22 | URBAN | Other | 858633 | 1 | 117.55 | 117.55 | 7.21e-05 | 6.1336e-05
2012-08-09 | 225:13444 | URBAN | Other | 858674 | 1 | 37.8667 | 37.8667 | 2.3226e-05 | 6.1336e-05
2012-08-09 | ZN2835:PA28 | URBAN | Other | 858726 | 84 | 163 | 13639.3 | 0.0083658 | 0.0051522
2012-08-09 | ZN2400:PA18 | SHORT RURAL | Weather | 858742 | 1 | 43.95 | 43.95 | 2.6957e-05 | 6.1336e-05
2012-08-09 | ZN2466:PA30 | URBAN | Equipment Failure | 858754 | 157 | 255.4 | 40097.8 | 0.024594 | 0.0096297
2012-08-09 | 813:89061 | LONG RURAL | Other | 858802 | 3 | 75 | 225 | 0.00013801 | 0.00018401
2012-08-09 | ZN1068:PA18 | URBAN | Equipment Failure | 858812 | 14 | 122.6667 | 1717.3333 | 0.0010533 | 0.0008587
2012-08-09 | ZN2835:PA28 | URBAN | Other | 858825 | 84 | 102 | 8554.5667 | 0.005247 | 0.0051522
2012-08-09 | ZN15009:PA1 | URBAN | Animals | 858846 | 2004 | 86 | 145382 | 0.089171 | 0.12292
2012-08-10 | 203:8089 | URBAN | Third Party Impacts | 858873 | 233 | 365 | 72195 | 0.04411 | 0.014236
2012-08-10 | 260:33353 | URBAN | Vegetation | 858965 | 1 | 86.1833 | 86.1833 | 5.2657e-05 | 6.1099e-05
2012-08-10 | ZN9700:PA17 | URBAN | Other | 858971 | 2134 | 95 | 147060 | 0.089852 | 0.13038
2012-08-10 | ZN15005:PA12 | URBAN | Vegetation | 859000 | 74 | 65 | 4810 | 0.0029388 | 0.0045213
2012-08-10 | ZN690:PA12 | URBAN | Vegetation | 859024 | 1 | 648.4333 | 648.4333 | 0.00039618 | 6.1099e-05
2012-08-10 | ZN12580:PA16 | URBAN | Other | 859027 | 1 | 235.9 | 235.9 | 0.00014413 | 6.1099e-05
2012-08-10 | ZN15005:PA4 | URBAN | Vegetation | 859053 | 50 | 85.5 | 4275 | 0.002612 | 0.0030549
2012-08-10 | ZN847:PA44 | URBAN | Vegetation | 859058 | 1035 | 50 | 51750 | 0.031619 | 0.063237
2012-08-10 | ZN9550:PA36 | URBAN | Vegetation | 859066 | 38 | 119 | 4522 | 0.0027629 | 0.0023217
2012-08-10 | ZN398:PA11 | URBAN | Other | 859071 | 93 | 137 | 12660.4 | 0.0077353 | 0.0056822
2012-08-10 | ZN398:PA22 | URBAN | Other | 859071 | 1 | 137 | 137 | 8.3705e-05 | 6.1099e-05
2012-08-10 | ZN3672:PA13 | URBAN | Vegetation | 859073 | 54 | 100.2167 | 5411.7 | 0.0033065 | 0.0032993
2012-08-10 | ZN15008:PA7 | URBAN | Vegetation | 859080 | 229 | 314 | 71906 | 0.043934 | 0.013992
2012-08-10 | ZN262:PA34 | URBAN | Other | 859081 | 3 | 288 | 864 | 0.00052789 | 0.0001833
2012-08-10 | ZN4545:PA41 | URBAN | Vegetation | 859085 | 156 | 97.1333 | 15152.8 | 0.0092582 | 0.0095314
2012-08-10 | ZN9037:PA8 | URBAN | Vegetation | 859090 | 84 | 440 | 36960 | 0.022582 | 0.0051323
2012-08-10 | ZN10995:PA7 | URBAN | Vegetation | 859099 | 2110 | 90 | 189900 | 0.11603 | 0.12892
2012-08-10 | ZN1193:PA9 | URBAN | Vegetation | 859100 | 44 | 123 | 5412 | 0.0033067 | 0.0026883
2012-08-10 | ZN5868:PA14 | URBAN | Vegetation | 859102 | 1 | 250.5 | 250.5 | 0.00015305 | 6.1099e-05
2012-08-10 | ZN1287:PA3 | URBAN | Equipment Failure | 859107 | 1 | 279.55 | 279.55 | 0.0001708 | 6.1099e-05
2012-08-10 | ZN340:PA20 | URBAN | Other | 859113 | 3 | 233 | 699 | 0.00042708 | 0.0001833
2012-08-10 | ZN36300:PA17 | URBAN | Vegetation | 859114 | 73 | 300 | 21900 | 0.013381 | 0.0044602
2012-08-10 | ZN9700:PA23 | URBAN | Other | 859119 | 27 | 381.05 | 10288.35 | 0.006286 | 0.0016497
2012-08-10 | ZN10991:PA12 | URBAN | Equipment Failure | 859126 | 1 | 34.5667 | 34.5667 | 2.112e-05 | 6.1099e-05
2012-08-10 | ZN80:PA32 | URBAN | Vegetation | 859129 | 75 | 154.2667 | 11570 | 0.0070691 | 0.0045824
2012-08-10 | ZN15002:PA4 | URBAN | Vegetation | 859137 | 699 | 185 | 78243 | 0.047805 | 0.042708
2012-08-10 | ZN10991:PA12 | URBAN | Equipment Failure | 859147 | 1 | 343.9 | 343.9 | 0.00021012 | 6.1099e-05
2012-08-10 | ZN1164:PA9 | URBAN | Weather | 859152 | 1 | 239.1667 | 239.1667 | 0.00014613 | 6.1099e-05
2012-08-10 | ZN847:PA15 | URBAN | Other | 859154 | 33 | 1375 | 45375 | 0.027724 | 0.0020163
2012-08-10 | ZN690:PA35 | URBAN | Other | 859168 | 11 | 899.8833 | 9898.7167 | 0.006048 | 0.00067208
2012-08-10 | ZN10994:PA13 | URBAN | Vegetation | 859174 | 1 | 232.15 | 232.15 | 0.00014184 | 6.1099e-05
2012-08-10 | ZN9035:PA7 | URBAN | Vegetation | 859192 | 1 | 486.1333 | 486.1333 | 0.00029702 | 6.1099e-05
2012-08-10 | ZN10997:PA12 | URBAN | Other | 859199 | 10 | 227 | 2270 | 0.0013869 | 0.00061099
2012-08-10 | ZN10997:PA5 | URBAN | Other | 859199 | 79 | 227 | 17931.6833 | 0.010956 | 0.0048268
2012-08-10 | ZN15014:PA19 | URBAN | Equipment Failure | 859201 | 91 | 527 | 47957 | 0.029301 | 0.00556
2012-08-10 | ZN2835:PA35 | URBAN | Vegetation | 859205 | 1 | 91.4833 | 91.4833 | 5.5895e-05 | 6.1099e-05
2012-08-10 | ZN15004:PA5 | URBAN | Vegetation | 859213 | 61 | 404.7333 | 24688.7333 | 0.015084 | 0.003727
2012-08-10 | ZN2835:PA35 | URBAN | Vegetation | 859220 | 1 | 88.1667 | 88.1667 | 5.3869e-05 | 6.1099e-05
2012-08-10 | ZN116:PA42 | URBAN | Vegetation | 859221 | 78 | 267.6833 | 20879.3 | 0.012757 | 0.0047657
2012-08-10 | ZN3154:PA10 | URBAN | Vegetation | 859226 | 1 | 70.3833 | 70.3833 | 4.3003e-05 | 6.1099e-05
2012-08-10 | ZN10994:PA21 | URBAN | Vegetation | 859244 | 1050 | 159 | 149193 | 0.091155 | 0.064154
2012-08-10 | ZN847:PA2 | URBAN | Vegetation | 859249 | 42 | 45.6167 | 1915.9 | 0.0011706 | 0.0025661
2012-08-10 | ZN9118:PA12 | URBAN | Vegetation | 859252 | 1 | 1151 | 1151 | 0.00070325 | 6.1099e-05
2012-08-10 | ZN35370:PA2 | SHORT RURAL | Equipment Failure | 859255 | 31 | 618 | 18918 | 0.011559 | 0.0018941
2012-08-10 | ZN12570:PA1 | SHORT RURAL | Other | 859257 | 1733 | 72 | 115398 | 0.070507 | 0.10588
2012-08-10 | ZN1193:PA9 | URBAN | Other | 859263 | 1 | 31.0667 | 31.0667 | 1.8981e-05 | 6.1099e-05
2012-08-10 | ZN1850:PA9 | URBAN | Vegetation | 859271 | 2 | 389 | 777.2 | 0.00047486 | 0.0001222
2012-08-10 | ZN10995:PA2 | URBAN | Equipment Failure | 859276 | 1 | 250.1667 | 250.1667 | 0.00015285 | 6.1099e-05
2012-08-10 | ZN15005:PA8 | URBAN | Other | 859283 | 78 | 252 | 6396 | 0.0039079 | 0.0047657
2012-08-10 | ZN15012:PA8 | URBAN | Other | 859283 | 355 | 252 | 59364 | 0.036271 | 0.02169
2012-08-10 | ZN2835:PA35 | URBAN | Vegetation | 859288 | 1 | 68.45 | 68.45 | 4.1822e-05 | 6.1099e-05
2012-08-10 | ZN129:PA28 | URBAN | Vegetation | 859291 | 1 | 262.4 | 262.4 | 0.00016032 | 6.1099e-05
2012-08-10 | ZN9252:PA9 | URBAN | Operational Error | 859302 | 46 | 623.05 | 28660.3 | 0.017511 | 0.0028105
2012-08-10 | ZN10995:PA8 | URBAN | Other | 859306 | 1 | 15.4167 | 15.4167 | 9.4194e-06 | 6.1099e-05
2012-08-10 | ZN195:PA28 | URBAN | Vegetation | 859323 | 135 | 247 | 33345 | 0.020373 | 0.0082483
2012-08-10 | ZN10994:PA4 | URBAN | Other | 859327 | 1 | 267.45 | 267.45 | 0.00016341 | 6.1099e-05
2012-08-10 | ZN9118:PA11 | URBAN | Weather | 859332 | 781 | 297 | 182507 | 0.11151 | 0.047718
2012-08-10 | ZN15004:PA3 | URBAN | Vegetation | 859353 | 78 | 756.3667 | 58942.0667 | 0.036013 | 0.0047657
2012-08-10 | 260:33353 | URBAN | Equipment Failure | 859361 | 1601 | 418 | 118395 | 0.072338 | 0.097819
2012-08-10 | ZN10994:PA7 | URBAN | Equipment Failure | 859372 | 1 | 237.3667 | 237.3667 | 0.00014503 | 6.1099e-05
2012-08-10 | ZN15014:PA11 | URBAN | Equipment Failure | 859379 | 39 | 154 | 5996.25 | 0.0036636 | 0.0023828
2012-08-10 | ZN15014:PA18 | URBAN | Equipment Failure | 859379 | 1 | 154 | 154 | 9.4092e-05 | 6.1099e-05
2012-08-10 | ZN15008:PA10 | URBAN | Other | 859391 | 64 | 33 | 2112 | 0.0012904 | 0.0039103
2012-08-10 | ZN15008:PA7 | URBAN | Other | 859391 | 229 | 33 | 7557 | 0.0046172 | 0.013992
2012-08-10 | ZN15006:PA1 | URBAN | Equipment Failure | 859392 | 50 | 903.35 | 45167.5 | 0.027597 | 0.0030549
2012-08-10 | 232:33413 | SHORT RURAL | Vegetation | 859395 | 1897 | 140 | 235653 | 0.14398 | 0.1159
2012-08-10 | ZN12580:PA1 | URBAN | Equipment Failure | 859411 | 1 | 139.45 | 139.45 | 8.5202e-05 | 6.1099e-05
2012-08-10 | ZN9550:PA33 | URBAN | Other | 859412 | 45 | 195.1333 | 8781 | 0.0053651 | 0.0027494
2012-08-10 | ZN2568:PA32 | URBAN | Vegetation | 859430 | 95 | 210 | 19915.1167 | 0.012168 | 0.0058044
2012-08-10 | ZN195:PA28 | URBAN | Vegetation | 859452 | 53 | 62 | 3286 | 0.0020077 | 0.0032382
2012-08-10 | ZN9252:PA10 | URBAN | Other | 859455 | 46 | 362.7167 | 16684.9667 | 0.010194 | 0.0028105
2012-08-10 | 232:11455 | URBAN | Vegetation | 859456 | 1 | 400.6833 | 400.6833 | 0.00024481 | 6.1099e-05
2012-08-10 | 227:13016 | SHORT RURAL | Vegetation | 859457 | 1 | 219.9833 | 219.9833 | 0.00013441 | 6.1099e-05
2012-08-10 | ZN9900:PA1 | URBAN | Other | 859488 | 38 | 776.0167 | 29488.6333 | 0.018017 | 0.0023217
2012-08-10 | ZN2602:PA21 | URBAN | Other | 859492 | 1 | 510.2667 | 510.2667 | 0.00031177 | 6.1099e-05
2012-08-10 | ZN12600:PA2 | SHORT RURAL | Vegetation | 859494 | 4 | 1327 | 5308 | 0.0032431 | 0.00024439
2012-08-10 | 227:13020 | SHORT RURAL | Other | 859496 | 92 | 90 | 8280 | 0.005059 | 0.0056211
2012-08-10 | ZN35600:PA10 | URBAN | Vegetation | 859515 | 1 | 326.7667 | 326.7667 | 0.00019965 | 6.1099e-05
2012-08-10 | ZN1788:PA1 | URBAN | Other | 859523 | 1 | 2899.7 | 2899.7 | 0.0017717 | 6.1099e-05
2012-08-10 | ZN2835:PA28 | URBAN | Vegetation | 859529 | 84 | 103 | 8650.9667 | 0.0052856 | 0.0051323
2012-08-10 | 230:81440 | URBAN | Equipment Failure | 859530 | 1 | 92.9 | 92.9 | 5.6761e-05 | 6.1099e-05
2012-08-10 | ZN2635:PA17 | URBAN | Vegetation | 859534 | 1 | 467.2833 | 467.2833 | 0.0002855 | 6.1099e-05
2012-08-10 | ZN2835:PA22 | URBAN | Vegetation | 859546 | 25 | 120 | 3000 | 0.001833 | 0.0015275
2012-08-10 | ZN2835:PA28 | URBAN | Vegetation | 859546 | 3 | 120 | 360 | 0.00021996 | 0.0001833
2012-08-10 | ZN9118:PA22 | URBAN | Third Party Impacts | 859548 | 1 | 299.1333 | 299.1333 | 0.00018277 | 6.1099e-05
2012-08-10 | ZN10995:PA1 | URBAN | Vegetation | 859562 | 168 | 569 | 95572.5167 | 0.058393 | 0.010265
2012-08-10 | 258:80775 | URBAN | Equipment Failure | 859567 | 1 | 177.8167 | 177.8167 | 0.00010864 | 6.1099e-05
2012-08-10 | 228:7487 | URBAN | Equipment Failure | 859571 | 1 | 261.15 | 261.15 | 0.00015956 | 6.1099e-05
2012-08-10 | ZN10999:PA12 | URBAN | Vegetation | 859575 | 1 | 1205.3833 | 1205.3833 | 0.00073647 | 6.1099e-05
2012-08-10 | ZN12650:PA1 | SHORT RURAL | Vegetation | 859580 | 17 | 116 | 1972 | 0.0012049 | 0.0010387
2012-08-10 | ZN1164:PA15 | URBAN | Weather | 859581 | 1 | 92.1 | 92.1 | 5.6272e-05 | 6.1099e-05
2012-08-10 | 230:81440 | URBAN | Vegetation | 859585 | 1 | 275.0167 | 275.0167 | 0.00016803 | 6.1099e-05
2012-08-10 | 256:80641 | URBAN | Equipment Failure | 859590 | 1 | 659.85 | 659.85 | 0.00040316 | 6.1099e-05
2012-08-10 | ZN35600:PA20 | URBAN | Other | 859592 | 54 | 169.4333 | 9149.4 | 0.0055902 | 0.0032993
2012-08-10 | 232:11455 | URBAN | Vegetation | 859594 | 1 | 479.2333 | 479.2333 | 0.0002928 | 6.1099e-05
2012-08-10 | ZN4545:PA24 | URBAN | Vegetation | 859595 | 1 | 179.1 | 179.1 | 0.00010943 | 6.1099e-05
2012-08-10 | 224:80332 | URBAN | Vegetation | 859596 | 1798 | 91 | 163618 | 0.099968 | 0.10986
2012-08-10 | 202:34250 | URBAN | Equipment Failure | 859600 | 1 | 73.8667 | 73.8667 | 4.5132e-05 | 6.1099e-05
2012-08-10 | 229:34995 | SHORT RURAL | Vegetation | 859605 | 1 | 264.8833 | 264.8833 | 0.00016184 | 6.1099e-05
2012-08-10 | ZN9252:PA11 | URBAN | Other | 859607 | 32 | 492.45 | 15758.4 | 0.0096282 | 0.0019552
2012-08-10 | ZN15006:PA13 | URBAN | Equipment Failure | 859608 | 1306 | 264 | 181220 | 0.11072 | 0.079795
2012-08-10 | 260:33347 | SHORT RURAL | Other | 859609 | 1 | 477.2333 | 477.2333 | 0.00029158 | 6.1099e-05
2012-08-10 | ZN2466:PA30 | URBAN | Vegetation | 859611 | 25 | 337 | 8425 | 0.0051476 | 0.0015275
2012-08-10 | ZN2466:PA45 | URBAN | Vegetation | 859611 | 87 | 337 | 29311.75 | 0.017909 | 0.0053156
2012-08-10 | ZN262:PA34 | URBAN | Other | 859639 | 1 | 291.9333 | 291.9333 | 0.00017837 | 6.1099e-05
2012-08-10 | 222:2018 | URBAN | Vegetation | 859641 | 1 | 146.65 | 146.65 | 8.9601e-05 | 6.1099e-05
2012-08-10 | ZN80:PA25 | URBAN | Vegetation | 859642 | 860 | 75 | 64500 | 0.039409 | 0.052545
2012-08-10 | 232:11457 | URBAN | Equipment Failure | 859643 | 1 | 1956.5167 | 1956.5167 | 0.0011954 | 6.1099e-05
2012-08-10 | 232:11453 | SHORT RURAL | Vegetation | 859650 | 1 | 1670.7 | 1670.7 | 0.0010208 | 6.1099e-05
2012-08-10 | 256:80641 | URBAN | Equipment Failure | 859655 | 1 | 649.9167 | 649.9167 | 0.00039709 | 6.1099e-05
2012-08-10 | 206:34434 | URBAN | Other | 859657 | 44 | 155 | 6820 | 0.0041669 | 0.0026883
2012-08-10 | ZN9118:PA2 | URBAN | Vegetation | 859658 | 1 | 263.0833 | 263.0833 | 0.00016074 | 6.1099e-05
2012-08-10 | ZN12640:PA19 | URBAN | Vegetation | 859698 | 107 | 282.1667 | 30191.8333 | 0.018447 | 0.0065376
2012-08-10 | ZN1287:PA3 | URBAN | Other | 859699 | 1 | 65.8333 | 65.8333 | 4.0223e-05 | 6.1099e-05
2012-08-10 | ZN9118:PA3 | SHORT RURAL | Vegetation | 859702 | 1 | 1540.0667 | 1540.0667 | 0.00094096 | 6.1099e-05
2012-08-10 | ZN15011:PA6 | URBAN | Vegetation | 859714 | 38 | 460 | 17480 | 0.01068 | 0.0023217
2012-08-10 | ZN12570:PA16 | SHORT RURAL | Vegetation | 859719 | 757 | 341 | 65713 | 0.04015 | 0.046252
2012-08-10 | 230:81440 | URBAN | Other | 859722 | 51 | 268 | 13668 | 0.008351 | 0.003116
2012-08-10 | ZN1648:PA16 | URBAN | Other | 859723 | 72 | 732.65 | 52750.8 | 0.03223 | 0.0043991
2012-08-10 | ZN9118:PA2 | URBAN | Vegetation | 859726 | 1 | 1266.3 | 1266.3 | 0.00077369 | 6.1099e-05
2012-08-10 | ZN9700:PA17 | URBAN | Vegetation | 859727 | 42 | 1292.4667 | 54283.6 | 0.033167 | 0.0025661
2012-08-10 | ZN10999:PA15 | URBAN | Weather | 859742 | 65 | 406.7333 | 26437.6667 | 0.016153 | 0.0039714
2012-08-10 | ZN10999:PA16 | URBAN | Weather | 859742 | 95 | 406.7333 | 29910 | 0.018275 | 0.0058044
2012-08-10 | ZN2835:PA35 | URBAN | Vegetation | 859746 | 22 | 60 | 1320 | 0.0008065 | 0.0013442
2012-08-10 | ZN3154:PA10 | URBAN | Equipment Failure | 859757 | 48 | 677.15 | 32503.2 | 0.019859 | 0.0029327
2012-08-10 | ZN1193:PA7 | URBAN | Vegetation | 859759 | 48 | 101.7833 | 4885.6 | 0.002985 | 0.0029327
2012-08-10 | 223:14393 | URBAN | Vegetation | 859764 | 1 | 13.45 | 13.45 | 8.2178e-06 | 6.1099e-05
2012-08-10 | 228:7491 | URBAN | Equipment Failure | 859765 | 1 | 220.3333 | 220.3333 | 0.00013462 | 6.1099e-05
2012-08-10 | ZN1673:PA13 | URBAN | Other | 859776 | 27 | 243.1833 | 6565.95 | 0.0040117 | 0.0016497
2012-08-10 | ZN10994:PA3 | URBAN | Other | 859780 | 1 | 222.65 | 222.65 | 0.00013604 | 6.1099e-05
2012-08-10 | ZN9700:PA23 | URBAN | Other | 859781 | 31 | 217.3167 | 6736.8167 | 0.0041161 | 0.0018941
2012-08-10 | ZN5868:PA30 | URBAN | Other | 859782 | 1 | 1168.9167 | 1168.9167 | 0.00071419 | 6.1099e-05
2012-08-10 | ZN2310:PA25 | URBAN | Other | 859785 | 43 | 366.1167 | 15743.0167 | 0.0096188 | 0.0026272
2012-08-10 | 243:80080 | SHORT RURAL | Equipment Failure | 859799 | 1 | 212.35 | 212.35 | 0.00012974 | 6.1099e-05
2012-08-10 | ZN2473:PA11 | URBAN | Other | 859801 | 6 | 437 | 2622 | 0.001602 | 0.00036659
2012-08-10 | ZN965:PA11 | URBAN | Vegetation | 859803 | 1 | 315.45 | 315.45 | 0.00019274 | 6.1099e-05
2012-08-10 | ZN9252:PA11 | URBAN | Vegetation | 859805 | 1 | 584.3167 | 584.3167 | 0.00035701 | 6.1099e-05
2012-08-10 | ZN9700:PA17 | URBAN | Vegetation | 859823 | 1 | 221.9167 | 221.9167 | 0.00013559 | 6.1099e-05
2012-08-10 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 859855 | 1 | 35.5833 | 35.5833 | 2.1741e-05 | 6.1099e-05
2012-08-10 | ZN9252:PA10 | URBAN | Vegetation | 859857 | 1 | 785.0833 | 785.0833 | 0.00047968 | 6.1099e-05
2012-08-10 | 260:33353 | URBAN | Vegetation | 859861 | 1 | 394.15 | 394.15 | 0.00024082 | 6.1099e-05
2012-08-10 | 224:80340 | SHORT RURAL | Vegetation | 859862 | 84 | 1375 | 35358 | 0.021603 | 0.0051323
2012-08-10 | ZN1285:PA31 | URBAN | Other | 859868 | 79 | 362.6667 | 28650.6667 | 0.017505 | 0.0048268
2012-08-10 | ZN1285:PA33 | URBAN | Other | 859869 | 78 | 317.2 | 24741.6 | 0.015117 | 0.0047657
2012-08-10 | ZN10994:PA19 | URBAN | Vegetation | 859874 | 1 | 1051.45 | 1051.45 | 0.00064242 | 6.1099e-05
2012-08-10 | 260:33344 | URBAN | Other | 859880 | 1808 | 133 | 240464 | 0.14692 | 0.11047
2012-08-10 | 224:80340 | SHORT RURAL | Vegetation | 859883 | 58 | 255 | 14790 | 0.0090365 | 0.0035437
2012-08-10 | ZN3155:PA12 | URBAN | Equipment Failure | 859887 | 53 | 378 | 4159.6167 | 0.0025415 | 0.0032382
2012-08-10 | ZN3155:PA23 | URBAN | Equipment Failure | 859887 | 35 | 378 | 3777.6667 | 0.0023081 | 0.0021385
2012-08-10 | ZN342:PA17 | URBAN | Equipment Failure | 859887 | 251 | 378 | 44673 | 0.027295 | 0.015336
2012-08-10 | ZN12630:PA1 | SHORT RURAL | Other | 859890 | 233 | 238 | 42045 | 0.025689 | 0.014236
2012-08-10 | 260:33353 | URBAN | Vegetation | 859892 | 1 | 387.0667 | 387.0667 | 0.00023649 | 6.1099e-05
2012-08-10 | ZN9550:PA35 | URBAN | Vegetation | 859900 | 1 | 1091.25 | 1091.25 | 0.00066674 | 6.1099e-05
2012-08-10 | ZN2835:PA18 | URBAN | Weather | 859901 | 101 | 811.35 | 81946.35 | 0.050068 | 0.006171
2012-08-10 | 202:34250 | URBAN | Equipment Failure | 859906 | 1 | 9.25 | 9.25 | 5.6516e-06 | 6.1099e-05
2012-08-10 | ZN342:PA17 | URBAN | Other | 859909 | 1 | 534.1 | 534.1 | 0.00032633 | 6.1099e-05
2012-08-10 | 260:33353 | URBAN | Vegetation | 859913 | 1 | 383.1167 | 383.1167 | 0.00023408 | 6.1099e-05
2012-08-10 | 258:80785 | URBAN | Vegetation | 859919 | 1 | 262.4333 | 262.4333 | 0.00016034 | 6.1099e-05
2012-08-10 | ZN12580:PA12 | SHORT RURAL | Equipment Failure | 859923 | 1 | 201.4667 | 201.4667 | 0.00012309 | 6.1099e-05
2012-08-10 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 859932 | 8 | 305 | 2440 | 0.0014908 | 0.00048879
2012-08-10 | ZN847:PA44 | URBAN | Weather | 859936 | 29 | 205 | 5945 | 0.0036323 | 0.0017719
2012-08-10 | 230:81434 | URBAN | Equipment Failure | 859939 | 1 | 287.75 | 287.75 | 0.00017581 | 6.1099e-05
2012-08-10 | ZN2835:PA10 | URBAN | Other | 859947 | 20 | 405 | 8100 | 0.004949 | 0.001222
2012-08-10 | ZN2835:PA23 | URBAN | Other | 859947 | 34 | 405 | 13757.9 | 0.0084059 | 0.0020774
2012-08-10 | 210:8681 | URBAN | Equipment Failure | 859953 | 1 | 523.35 | 523.35 | 0.00031976 | 6.1099e-05
2012-08-10 | ZN9118:PA3 | SHORT RURAL | Other | 859955 | 1 | 117.15 | 117.15 | 7.1577e-05 | 6.1099e-05
2012-08-10 | ZN195:PA30 | URBAN | Equipment Failure | 859961 | 1 | 1931.6833 | 1931.6833 | 0.0011802 | 6.1099e-05
2012-08-10 | ZN80:PA25 | URBAN | Other | 859963 | 1 | 93.0667 | 93.0667 | 5.6862e-05 | 6.1099e-05
2012-08-10 | 507:80923 | SHORT RURAL | Other | 859967 | 1 | 531.3 | 531.3 | 0.00032462 | 6.1099e-05
2012-08-10 | ZN2602:PA41 | URBAN | Other | 859972 | 1 | 639.7833 | 639.7833 | 0.0003909 | 6.1099e-05
2012-08-10 | ZN847:PA18 | URBAN | Vegetation | 859974 | 1572 | 376 | 120972 | 0.073912 | 0.096047
2012-08-10 | 235:2120 | SHORT RURAL | Equipment Failure | 859991 | 1 | 155.45 | 155.45 | 9.4978e-05 | 6.1099e-05
2012-08-10 | ZN10996:PA11 | URBAN | Other | 859994 | 55 | 58.6667 | 3226.6667 | 0.0019714 | 0.0033604
2012-08-10 | ZN2602:PA15 | URBAN | Other | 860001 | 1 | 212.6167 | 212.6167 | 0.00012991 | 6.1099e-05
2012-08-10 | 235:2120 | SHORT RURAL | Equipment Failure | 860007 | 1 | 150.0667 | 150.0667 | 9.1689e-05 | 6.1099e-05
2012-08-10 | ZN1285:PA33 | URBAN | Vegetation | 860023 | 74 | 269.4333 | 19938.0667 | 0.012182 | 0.0045213
2012-08-10 | ZN9035:PA11 | URBAN | Vegetation | 860024 | 1 | 274.3 | 274.3 | 0.00016759 | 6.1099e-05
2012-08-10 | ZN187:PA30 | URBAN | Other | 860025 | 33 | 354.25 | 11690.25 | 0.0071426 | 0.0020163
2012-08-10 | 258:80785 | URBAN | Vegetation | 860040 | 1 | 236.3333 | 236.3333 | 0.0001444 | 6.1099e-05
2012-08-10 | 260:33347 | SHORT RURAL | Other | 860057 | 1 | 382.9833 | 382.9833 | 0.000234 | 6.1099e-05
2012-08-10 | 232:33413 | SHORT RURAL | Equipment Failure | 860058 | 1 | 1252.8833 | 1252.8833 | 0.00076549 | 6.1099e-05
2012-08-10 | ZN4545:PA25 | URBAN | Equipment Failure | 860089 | 92 | 434.5333 | 39977.0667 | 0.024425 | 0.0056211
2012-08-10 | ZN9035:PA11 | URBAN | Other | 860092 | 117 | 174.75 | 20445.75 | 0.012492 | 0.0071485
2012-08-10 | ZN4545:PA36 | URBAN | Equipment Failure | 860108 | 54 | 603.8 | 32605.2 | 0.019921 | 0.0032993
2012-08-10 | ZN35600:PA4 | URBAN | Weather | 860110 | 1 | 461.45 | 461.45 | 0.00028194 | 6.1099e-05
2012-08-10 | 205:12203 | URBAN | Equipment Failure | 860115 | 1 | 145.9333 | 145.9333 | 8.9163e-05 | 6.1099e-05
2012-08-10 | ZN15005:PA12 | URBAN | Equipment Failure | 860124 | 58 | 1255 | 72790 | 0.044474 | 0.0035437
2012-08-10 | 232:11457 | URBAN | Other | 860127 | 1 | 428.5167 | 428.5167 | 0.00026182 | 6.1099e-05
2012-08-10 | 220:8687 | URBAN | Equipment Failure | 860134 | 1 | 92.3667 | 92.3667 | 5.6435e-05 | 6.1099e-05
2012-08-10 | ZN2196:PA5 | URBAN | Other | 860140 | 31 | 454.7 | 14095.7 | 0.0086123 | 0.0018941
2012-08-10 | ZN2602:PA15 | URBAN | Other | 860148 | 1 | 185.4333 | 185.4333 | 0.0001133 | 6.1099e-05
2012-08-10 | ZN10990:PA5 | URBAN | Vegetation | 860152 | 473 | 136 | 60260 | 0.036818 | 0.0289
2012-08-10 | ZN10990:PA8 | URBAN | Vegetation | 860152 | 2 | 136 | 254 | 0.00015519 | 0.0001222
2012-08-10 | ZN1673:PA11 | URBAN | Vegetation | 860153 | 25 | 229.7833 | 5744.5833 | 0.0035099 | 0.0015275
2012-08-10 | 232:33409 | URBAN | Vegetation | 860157 | 2 | 1744.4333 | 3479.2667 | 0.0021258 | 0.0001222
2012-08-10 | 208:62 | URBAN | Other | 860192 | 1 | 332.5167 | 332.5167 | 0.00020316 | 6.1099e-05
2012-08-10 | ZN2835:PA32 | SHORT RURAL | Vegetation | 860193 | 35 | 497 | 17395 | 0.010628 | 0.0021385
2012-08-10 | ZN9700:PA24 | URBAN | Vegetation | 860196 | 31 | 1226.4833 | 38020.9833 | 0.02323 | 0.0018941
2012-08-10 | ZN12630:PA2 | SHORT RURAL | Vegetation | 860205 | 53 | 566 | 19468 | 0.011895 | 0.0032382
2012-08-10 | ZN9035:PA11 | URBAN | Equipment Failure | 860207 | 1 | 431.8833 | 431.8833 | 0.00026387 | 6.1099e-05
2012-08-10 | ZN965:PA21 | URBAN | Vegetation | 860209 | 47 | 498.75 | 23441.25 | 0.014322 | 0.0028716
2012-08-10 | ZN35600:PA16 | URBAN | Other | 860219 | 1 | 355.3 | 355.3 | 0.00021708 | 6.1099e-05
2012-08-10 | ZN2466:PA45 | URBAN | Vegetation | 860222 | 1 | 111.4667 | 111.4667 | 6.8105e-05 | 6.1099e-05
2012-08-10 | ZN15006:PA2 | URBAN | Vegetation | 860228 | 55 | 300.7667 | 16542.1667 | 0.010107 | 0.0033604
2012-08-10 | ZN116:PA42 | URBAN | Other | 860232 | 71 | 135.2833 | 9605.1167 | 0.0058686 | 0.004338
2012-08-10 | ZN2602:PA15 | URBAN | Other | 860241 | 1 | 168 | 168 | 0.00010265 | 6.1099e-05
2012-08-10 | 203:8085 | URBAN | Other | 860250 | 1 | 526.4833 | 526.4833 | 0.00032167 | 6.1099e-05
2012-08-10 | ZN35500:PA22 | URBAN | Vegetation | 860262 | 44 | 1063.7167 | 46803.5333 | 0.028596 | 0.0026883
2012-08-10 | 256:80646 | URBAN | Equipment Failure | 860265 | 1 | 26.3 | 26.3 | 1.6069e-05 | 6.1099e-05
2012-08-10 | ZN2196:PA18 | URBAN | Other | 860267 | 13 | 357.1167 | 4642.5167 | 0.0028365 | 0.00079428
2012-08-10 | ZN1673:PA18 | URBAN | Vegetation | 860279 | 47 | 1223.25 | 57492.75 | 0.035127 | 0.0028716
2012-08-10 | ZN35600:PA16 | URBAN | Other | 860284 | 1 | 98.7167 | 98.7167 | 6.0315e-05 | 6.1099e-05
2012-08-10 | ZN3922:PA11 | URBAN | Vegetation | 860285 | 1 | 998.6333 | 998.6333 | 0.00061015 | 6.1099e-05
2012-08-10 | ZN3425:PA34 | URBAN | Other | 860288 | 1 | 128.2333 | 128.2333 | 7.8349e-05 | 6.1099e-05
2012-08-10 | ZN10990:PA12 | URBAN | Equipment Failure | 860290 | 9 | 77 | 693 | 0.00042341 | 0.00054989
2012-08-10 | ZN9252:PA9 | URBAN | Other | 860296 | 44 | 493.0333 | 21693.4667 | 0.013254 | 0.0026883
2012-08-10 | ZN10995:PA13 | URBAN | Other | 860301 | 42 | 366.2 | 15380.4 | 0.0093972 | 0.0025661
2012-08-10 | ZN2602:PA9 | URBAN | Vegetation | 860328 | 1 | 119.5667 | 119.5667 | 7.3054e-05 | 6.1099e-05
2012-08-10 | ZN80:PA40 | URBAN | Vegetation | 860331 | 16 | 676.4667 | 10823.4667 | 0.006613 | 0.00097758
2012-08-10 | ZN195:PA30 | URBAN | Other | 860337 | 1 | 208.55 | 208.55 | 0.00012742 | 6.1099e-05
2012-08-10 | ZN2310:PA34 | URBAN | Vegetation | 860357 | 1 | 153 | 153 | 9.3481e-05 | 6.1099e-05
2012-08-10 | ZN2310:PA40 | URBAN | Vegetation | 860357 | 29 | 153 | 4415.25 | 0.0026977 | 0.0017719
2012-08-10 | 229:34995 | SHORT RURAL | Other | 860365 | 1 | 200.5333 | 200.5333 | 0.00012252 | 6.1099e-05
2012-08-10 | 202:34250 | URBAN | Equipment Failure | 860368 | 1 | 2.1333 | 2.1333 | 1.3034e-06 | 6.1099e-05
2012-08-10 | ZN2602:PA22 | URBAN | Other | 860384 | 6 | 615.6667 | 3694 | 0.002257 | 0.00036659
2012-08-10 | ZN10993:PA5 | URBAN | Other | 860388 | 75 | 535.6333 | 40172.5 | 0.024545 | 0.0045824
2012-08-10 | ZN2602:PA8 | URBAN | Vegetation | 860393 | 86 | 1633.6 | 25249.6 | 0.015427 | 0.0052545
2012-08-10 | ZN269:PA14 | URBAN | Vegetation | 860393 | 1 | 1633.6 | 1573.9333 | 0.00096165 | 6.1099e-05
2012-08-10 | ZN340:PA11 | URBAN | Other | 860398 | 1 | 792.8167 | 792.8167 | 0.0004844 | 6.1099e-05
2012-08-10 | ZN2835:PA41 | URBAN | Vegetation | 860408 | 119 | 116.3333 | 13843.6667 | 0.0084583 | 0.0072707
2012-08-10 | ZN129:PA11 | URBAN | Other | 860409 | 108 | 262 | 28296 | 0.017288 | 0.0065987
2012-08-10 | ZN129:PA12 | URBAN | Other | 860409 | 1293 | 262 | 338766 | 0.20698 | 0.079001
2012-08-10 | ZN129:PA16 | URBAN | Other | 860409 | 1248 | 262 | 326976 | 0.19978 | 0.076251
2012-08-10 | ZN129:PA18 | URBAN | Other | 860409 | 861 | 262 | 225582 | 0.13783 | 0.052606
2012-08-10 | ZN129:PA19 | URBAN | Other | 860409 | 1716 | 262 | 449592 | 0.27469 | 0.10485
2012-08-10 | ZN129:PA2 | URBAN | Other | 860409 | 853 | 262 | 223486 | 0.13655 | 0.052117
2012-08-10 | ZN129:PA21 | URBAN | Other | 860409 | 675 | 262 | 176850 | 0.10805 | 0.041242
2012-08-10 | ZN129:PA24 | URBAN | Other | 860409 | 1521 | 262 | 398502 | 0.24348 | 0.092931
2012-08-10 | ZN129:PA25 | URBAN | Other | 860409 | 95 | 262 | 24890 | 0.015207 | 0.0058044
2012-08-10 | ZN129:PA27 | URBAN | Other | 860409 | 194 | 262 | 50828 | 0.031055 | 0.011853
2012-08-10 | ZN129:PA28 | URBAN | Other | 860409 | 978 | 262 | 256236 | 0.15656 | 0.059754
2012-08-10 | ZN129:PA3 | URBAN | Other | 860409 | 1406 | 262 | 368372 | 0.22507 | 0.085905
2012-08-10 | ZN129:PA4 | URBAN | Other | 860409 | 406 | 262 | 106372 | 0.064992 | 0.024806
2012-08-10 | ZN129:PA5 | URBAN | Other | 860409 | 912 | 262 | 238944 | 0.14599 | 0.055722
2012-08-10 | ZN129:PA8 | URBAN | Other | 860409 | 1102 | 262 | 288724 | 0.17641 | 0.067331
2012-08-10 | ZN129:PA9 | URBAN | Other | 860409 | 1095 | 262 | 286890 | 0.17529 | 0.066903
2012-08-10 | ZN35500:PA34 | URBAN | Other | 860409 | 4 | 262 | 1048 | 0.00064031 | 0.00024439
2012-08-10 | ZN9035:PA11 | URBAN | Equipment Failure | 860431 | 1 | 250.1 | 250.1 | 0.00015281 | 6.1099e-05
2012-08-10 | ZN15009:PA7 | URBAN | Operational Error | 860432 | 1575 | 59 | 92925 | 0.056776 | 0.09623
2012-08-10 | ZN9037:PA9 | URBAN | Other | 860435 | 1 | 313.6 | 313.6 | 0.00019161 | 6.1099e-05
2012-08-10 | ZN1850:PA9 | URBAN | Vegetation | 860437 | 1 | 125.5 | 125.5 | 7.6679e-05 | 6.1099e-05
2012-08-10 | ZN9037:PA16 | URBAN | Other | 860440 | 1 | 387.1333 | 387.1333 | 0.00023653 | 6.1099e-05
2012-08-10 | ZN3154:PA4 | URBAN | Vegetation | 860442 | 1 | 1144.8 | 1144.8 | 0.00069946 | 6.1099e-05
2012-08-10 | ZN9037:PA16 | URBAN | Equipment Failure | 860444 | 1 | 385.3167 | 385.3167 | 0.00023542 | 6.1099e-05
2012-08-10 | ZN965:PA35 | URBAN | Vegetation | 860445 | 27 | 534.2167 | 14423.85 | 0.0088128 | 0.0016497
2012-08-10 | ZN10991:PA7 | URBAN | Vegetation | 860455 | 53 | 331.3167 | 17559.7833 | 0.010729 | 0.0032382
2012-08-10 | 235:2120 | SHORT RURAL | Equipment Failure | 860464 | 1 | 120.3167 | 120.3167 | 7.3512e-05 | 6.1099e-05
2012-08-10 | ZN2310:PA17 | URBAN | Other | 860465 | 82 | 100.2333 | 8219.1333 | 0.0050218 | 0.0050101
2012-08-10 | ZN9037:PA16 | URBAN | Equipment Failure | 860466 | 1 | 381.2333 | 381.2333 | 0.00023293 | 6.1099e-05
2012-08-10 | ZN2473:PA21 | URBAN | Other | 860475 | 1 | 1351.5833 | 1351.5833 | 0.0008258 | 6.1099e-05
2012-08-10 | ZN12570:PA11 | URBAN | Other | 860478 | 1 | 106.2167 | 106.2167 | 6.4897e-05 | 6.1099e-05
2012-08-10 | ZN690:PA11 | URBAN | Other | 860479 | 22 | 357.1167 | 7856.5667 | 0.0048003 | 0.0013442
2012-08-10 | ZN10997:PA12 | URBAN | Other | 860481 | 44 | 120 | 5280 | 0.003226 | 0.0026883
2012-08-10 | ZN9035:PA11 | URBAN | Equipment Failure | 860484 | 1 | 373.45 | 373.45 | 0.00022817 | 6.1099e-05
2012-08-10 | ZN35500:PA22 | URBAN | Vegetation | 860486 | 1 | 179.65 | 179.65 | 0.00010976 | 6.1099e-05
2012-08-10 | ZN10990:PA12 | URBAN | Vegetation | 860488 | 1 | 1074.9167 | 1074.9167 | 0.00065676 | 6.1099e-05
2012-08-10 | ZN35500:PA24 | URBAN | Other | 860498 | 1944 | 189 | 367416 | 0.22449 | 0.11878
2012-08-10 | ZN35500:PA31 | URBAN | Other | 860498 | 50 | 189 | 9450 | 0.0057738 | 0.0030549
2012-08-10 | ZN262:PA42 | URBAN | Equipment Failure | 860501 | 1 | 413.4167 | 413.4167 | 0.00025259 | 6.1099e-05
2012-08-10 | ZN9550:PA31 | URBAN | Other | 860537 | 83 | 468.35 | 38873.05 | 0.023751 | 0.0050712
2012-08-10 | ZN35600:PA3 | URBAN | Other | 860539 | 2 | 1188.3167 | 2376.6333 | 0.0014521 | 0.0001222
2012-08-10 | ZN9035:PA7 | URBAN | Vegetation | 860542 | 64 | 235 | 15040 | 0.0091892 | 0.0039103
2012-08-10 | 258:80785 | URBAN | Equipment Failure | 860543 | 1 | 497.55 | 497.55 | 0.000304 | 6.1099e-05
2012-08-10 | ZN9252:PA9 | URBAN | Equipment Failure | 860544 | 1 | 470 | 470 | 0.00028716 | 6.1099e-05
2012-08-10 | ZN1788:PA8 | URBAN | Vegetation | 860561 | 2 | 2646 | 5210.2 | 0.0031834 | 0.0001222
2012-08-10 | ZN3672:PA13 | URBAN | Other | 860568 | 1 | 943.0167 | 943.0167 | 0.00057617 | 6.1099e-05
2012-08-10 | ZN9118:PA22 | URBAN | Equipment Failure | 860577 | 1 | 1540.75 | 1540.75 | 0.00094138 | 6.1099e-05
2012-08-10 | ZN269:PA18 | URBAN | Equipment Failure | 860579 | 1 | 1600.4167 | 1600.4167 | 0.00097783 | 6.1099e-05
2012-08-10 | ZN116:PA34 | URBAN | Other | 860596 | 1 | 365.3833 | 365.3833 | 0.00022324 | 6.1099e-05
2012-08-10 | ZN10994:PA21 | URBAN | Other | 860600 | 25 | 150.05 | 3751.25 | 0.002292 | 0.0015275
2012-08-10 | 260:33347 | SHORT RURAL | Other | 860605 | 1 | 274.1667 | 274.1667 | 0.00016751 | 6.1099e-05
2012-08-10 | ZN9118:PA21 | URBAN | Vegetation | 860617 | 24 | 877 | 21048 | 0.01286 | 0.0014664
2012-08-10 | ZN1193:PA10 | URBAN | Vegetation | 860618 | 20 | 192.7333 | 3854.6667 | 0.0023551 | 0.001222
2012-08-10 | ZN15005:PA8 | URBAN | Weather | 860621 | 25 | 132 | 3300 | 0.0020163 | 0.0015275
2012-08-10 | ZN3672:PA35 | URBAN | Vegetation | 860624 | 1 | 1106.2833 | 1106.2833 | 0.00067592 | 6.1099e-05
2012-08-10 | ZN690:PA6 | URBAN | Vegetation | 860634 | 1 | 53.4333 | 53.4333 | 3.2647e-05 | 6.1099e-05
2012-08-10 | ZN9035:PA11 | URBAN | Equipment Failure | 860640 | 1 | 338.2833 | 338.2833 | 0.00020669 | 6.1099e-05
2012-08-10 | ZN847:PA22 | SHORT RURAL | Other | 860664 | 70 | 1105 | 77350 | 0.04726 | 0.0042769
2012-08-10 | ZN9035:PA7 | URBAN | Third Party Impacts | 860670 | 1 | 279.7667 | 279.7667 | 0.00017093 | 6.1099e-05
2012-08-10 | ZN3154:PA17 | URBAN | Vegetation | 860706 | 1 | 952.4167 | 952.4167 | 0.00058191 | 6.1099e-05
2012-08-11 | 232:33413 | SHORT RURAL | Other | 860712 | 18 | 201 | 3618 | 0.0022105 | 0.0010998
2012-08-10 | ZN35500:PA32 | URBAN | Vegetation | 860724 | 1 | 1061.6833 | 1061.6833 | 0.00064867 | 6.1099e-05
2012-08-10 | ZN965:PA21 | URBAN | Vegetation | 860732 | 1 | 1263.6833 | 1263.6833 | 0.00077209 | 6.1099e-05
2012-08-10 | ZN9700:PA23 | URBAN | Vegetation | 860741 | 1 | 1026.1333 | 1026.1333 | 0.00062695 | 6.1099e-05
2012-08-10 | ZN9700:PA23 | URBAN | Vegetation | 860743 | 1 | 1024.8833 | 1024.8833 | 0.00062619 | 6.1099e-05
2012-08-10 | ZN10991:PA1 | URBAN | Other | 860751 | 28 | 472.4833 | 13229.5333 | 0.0080831 | 0.0017108
2012-08-10 | 232:33411 | SHORT RURAL | Equipment Failure | 860765 | 120 | 1190 | 142800 | 0.087249 | 0.0073318
2012-08-10 | ZN15014:PA11 | URBAN | Equipment Failure | 860767 | 52 | 576 | 29146 | 0.017808 | 0.0031771
2012-08-10 | ZN15014:PA19 | URBAN | Equipment Failure | 860767 | 139 | 576 | 80064 | 0.048918 | 0.0084927
2012-08-10 | ZN12620:PA11 | SHORT RURAL | Other | 860780 | 1 | 238.4833 | 238.4833 | 0.00014571 | 6.1099e-05
2012-08-10 | ZN12610:PA11 | URBAN | Vegetation | 860792 | 1 | 1203.3167 | 1203.3167 | 0.00073521 | 6.1099e-05
2012-08-10 | ZN15014:PA11 | URBAN | Equipment Failure | 860797 | 1 | 182.25 | 182.25 | 0.00011135 | 6.1099e-05
2012-08-10 | 232:33413 | SHORT RURAL | Other | 860799 | 1 | 240.8 | 240.8 | 0.00014713 | 6.1099e-05
2012-08-10 | ZN3672:PA37 | URBAN | Other | 860800 | 1 | 959.3667 | 959.3667 | 0.00058616 | 6.1099e-05
2012-08-10 | ZN35500:PA22 | URBAN | Vegetation | 860803 | 1 | 1016.1833 | 1016.1833 | 0.00062087 | 6.1099e-05
2012-08-10 | ZN14144:PA2 | SHORT RURAL | Vegetation | 860805 | 76 | 465 | 10824 | 0.0066133 | 0.0046435
2012-08-10 | ZN10997:PA12 | URBAN | Other | 860806 | 42 | 489.4667 | 20557.6 | 0.01256 | 0.0025661
2012-08-10 | 224:80337 | URBAN | Equipment Failure | 860810 | 266 | 150 | 39900 | 0.024378 | 0.016252
2012-08-10 | 507:80923 | SHORT RURAL | Equipment Failure | 860824 | 1 | 44.5333 | 44.5333 | 2.7209e-05 | 6.1099e-05
2012-08-10 | ZN12610:PA11 | URBAN | Other | 860831 | 1 | 157 | 157 | 9.5925e-05 | 6.1099e-05
2012-08-10 | ZN15014:PA11 | URBAN | Vegetation | 860841 | 39 | 812.7167 | 31695.95 | 0.019366 | 0.0023828
2012-08-10 | ZN1648:PA20 | URBAN | Equipment Failure | 860842 | 1 | 87.5 | 87.5 | 5.3461e-05 | 6.1099e-05
2012-08-10 | 202:34239 | SHORT RURAL | Other | 860872 | 1 | 206.2 | 206.2 | 0.00012599 | 6.1099e-05
2012-08-10 | ZN2602:PA21 | URBAN | Equipment Failure | 860874 | 1 | 1195.7667 | 1195.7667 | 0.0007306 | 6.1099e-05
2012-08-11 | 232:33413 | SHORT RURAL | Equipment Failure | 860875 | 15 | 557 | 8355 | 0.0051048 | 0.00091648
2012-08-10 | ZN3425:PA30 | URBAN | Other | 860878 | 1 | 1132.4667 | 1132.4667 | 0.00069192 | 6.1099e-05
2012-08-10 | ZN12640:PA19 | URBAN | Vegetation | 860889 | 80 | 112.85 | 9028 | 0.005516 | 0.0048879
2012-08-10 | ZN3472:PA28 | URBAN | Vegetation | 860905 | 1 | 210.95 | 210.95 | 0.00012889 | 6.1099e-05
2012-08-10 | 232:33413 | SHORT RURAL | Equipment Failure | 860908 | 1 | 940.6667 | 940.6667 | 0.00057473 | 6.1099e-05
2012-08-10 | ZN2310:PA25 | URBAN | Vegetation | 860912 | 1 | 815.9 | 815.9 | 0.0004985 | 6.1099e-05
2012-08-10 | ZN10991:PA12 | URBAN | Other | 860923 | 1 | 840.85 | 840.85 | 0.00051375 | 6.1099e-05
2012-08-10 | 512:48047 | SHORT RURAL | Other | 860931 | 25 | 49.8 | 1245 | 0.00076068 | 0.0015275
2012-08-10 | 230:81434 | URBAN | Vegetation | 860936 | 1 | 1059.6167 | 1059.6167 | 0.00064741 | 6.1099e-05
2012-08-10 | ZN35600:PA16 | URBAN | Other | 860941 | 1 | 1028.3667 | 1028.3667 | 0.00062832 | 6.1099e-05
2012-08-10 | ZN1788:PA14 | URBAN | Other | 860943 | 1 | 817.4833 | 817.4833 | 0.00049947 | 6.1099e-05
2012-08-10 | ZN1164:PA23 | URBAN | Other | 860946 | 1 | 615.0667 | 615.0667 | 0.0003758 | 6.1099e-05
2012-08-10 | ZN15002:PA4 | URBAN | Equipment Failure | 860956 | 1 | 881.35 | 881.35 | 0.00053849 | 6.1099e-05
2012-08-10 | ZN129:PA2 | URBAN | Other | 860961 | 114 | 174 | 12619.8 | 0.0077105 | 0.0069652
2012-08-10 | ZN129:PA28 | URBAN | Other | 860961 | 91 | 174 | 15834 | 0.0096744 | 0.00556
2012-08-10 | ZN129:PA9 | URBAN | Other | 860961 | 58 | 174 | 1624 | 0.00099224 | 0.0035437
2012-08-10 | ZN35500:PA24 | URBAN | Other | 860964 | 107 | 193 | 20651 | 0.012617 | 0.0065376
2012-08-10 | ZN2310:PA25 | URBAN | Vegetation | 860970 | 1 | 717.4833 | 717.4833 | 0.00043837 | 6.1099e-05
2012-08-10 | 230:81438 | SHORT RURAL | Equipment Failure | 860975 | 1 | 1101.1 | 1101.1 | 0.00067276 | 6.1099e-05
2012-08-10 | ZN14891:PA20 | SHORT RURAL | Vegetation | 860986 | 1 | 689.95 | 689.95 | 0.00042155 | 6.1099e-05
2012-08-10 | ZN847:PA10 | URBAN | Vegetation | 860992 | 55 | 665.7833 | 36618.0833 | 0.022373 | 0.0033604
2012-08-11 | 232:33413 | SHORT RURAL | Equipment Failure | 861006 | 1 | 540.4333 | 540.4333 | 0.0003302 | 6.1099e-05
2012-08-11 | 229:34995 | SHORT RURAL | Equipment Failure | 861009 | 1 | 798.7 | 798.7 | 0.00048799 | 6.1099e-05
2012-08-11 | ZN1164:PA23 | URBAN | Equipment Failure | 861015 | 1 | 99.4 | 99.4 | 6.0732e-05 | 6.1099e-05
2012-08-11 | ZN15014:PA12 | SHORT RURAL | Equipment Failure | 861017 | 16 | 141.0667 | 2257.0667 | 0.001379 | 0.00097758
2012-08-11 | ZN129:PA28 | URBAN | Other | 861021 | 23 | 193 | 4439 | 0.0027122 | 0.0014053
2012-08-11 | 232:11457 | URBAN | Animals | 861027 | 1 | 195.5167 | 195.5167 | 0.00011946 | 6.1099e-05
2012-08-11 | 230:81440 | URBAN | Equipment Failure | 861030 | 1 | 252.3833 | 252.3833 | 0.0001542 | 6.1099e-05
2012-08-11 | ZN80:PA40 | URBAN | Other | 861033 | 1 | 234.2 | 234.2 | 0.00014309 | 6.1099e-05
2012-08-11 | ZN12570:PA16 | SHORT RURAL | Equipment Failure | 861045 | 1 | 148.5 | 148.5 | 9.0731e-05 | 6.1099e-05
2012-08-11 | ZN116:PA32 | URBAN | Vegetation | 861051 | 1 | 90.2 | 90.2 | 5.5111e-05 | 6.1099e-05
2012-08-11 | 230:81440 | URBAN | Vegetation | 861052 | 1 | 126.4167 | 126.4167 | 7.7239e-05 | 6.1099e-05
2012-08-11 | 224:80337 | URBAN | Other | 861053 | 1 | 524.8667 | 524.8667 | 0.00032069 | 6.1099e-05
2012-08-11 | ZN9118:PA17 | URBAN | Vegetation | 861055 | 43 | 202 | 8652.5167 | 0.0052866 | 0.0026272
2012-08-11 | ZN15014:PA12 | SHORT RURAL | Equipment Failure | 861061 | 1 | 211.95 | 211.95 | 0.0001295 | 6.1099e-05
2012-08-11 | ZN12570:PA16 | SHORT RURAL | Vegetation | 861071 | 69 | 129 | 8461 | 0.0051696 | 0.0042158
2012-08-11 | 202:34245 | URBAN | Other | 861073 | 1 | 272.4167 | 272.4167 | 0.00016644 | 6.1099e-05
2012-08-11 | ZN2568:PA14 | URBAN | Equipment Failure | 861087 | 61 | 154.2 | 9406.2 | 0.0057471 | 0.003727
2012-08-11 | ZN116:PA50 | URBAN | Vegetation | 861098 | 1 | 267.5833 | 267.5833 | 0.00016349 | 6.1099e-05
2012-08-11 | 232:11457 | URBAN | Other | 861115 | 1 | 376.4667 | 376.4667 | 0.00023002 | 6.1099e-05
2012-08-11 | 232:33413 | SHORT RURAL | Other | 861161 | 1 | 523.9 | 523.9 | 0.0003201 | 6.1099e-05
2012-08-11 | ZN15014:PA19 | URBAN | Equipment Failure | 861177 | 1 | 192.4333 | 192.4333 | 0.00011757 | 6.1099e-05
2012-08-11 | ZN1673:PA11 | URBAN | Vegetation | 861179 | 32 | 20 | 640 | 0.00039103 | 0.0019552
2012-08-11 | 234:2001 | URBAN | Vegetation | 861181 | 940 | 42 | 39480 | 0.024122 | 0.057433
2012-08-11 | ZN12610:PA22 | URBAN | Other | 861182 | 1 | 522.8 | 522.8 | 0.00031942 | 6.1099e-05
2012-08-11 | ZN4545:PA40 | URBAN | Vegetation | 861194 | 1 | 101.55 | 101.55 | 6.2046e-05 | 6.1099e-05
2012-08-11 | ZN9037:PA16 | URBAN | Vegetation | 861200 | 1 | 513.5167 | 513.5167 | 0.00031375 | 6.1099e-05
2012-08-11 | ZN12570:PA16 | SHORT RURAL | Equipment Failure | 861220 | 1 | 772.3667 | 772.3667 | 0.00047191 | 6.1099e-05
2012-08-11 | ZN1285:PA23 | URBAN | Other | 861276 | 19 | 267 | 5073 | 0.0030995 | 0.0011609
2012-08-11 | 513:48056 | SHORT RURAL | Equipment Failure | 861277 | 3 | 115 | 345 | 0.00021079 | 0.0001833
2012-08-11 | ZN10990:PA7 | URBAN | Other | 861294 | 1 | 65.25 | 65.25 | 3.9867e-05 | 6.1099e-05
2012-08-11 | ZN2835:PA15 | URBAN | Equipment Failure | 861321 | 49 | 1612.1333 | 78994.5333 | 0.048265 | 0.0029938
2012-08-11 | ZN10997:PA12 | URBAN | Vegetation | 861334 | 1 | 275.9667 | 275.9667 | 0.00016861 | 6.1099e-05
2012-08-11 | 232:11457 | URBAN | Vegetation | 861339 | 1 | 137.05 | 137.05 | 8.3736e-05 | 6.1099e-05
2012-08-11 | ZN2466:PA5 | URBAN | Other | 861345 | 1 | 231.1167 | 231.1167 | 0.00014121 | 6.1099e-05
2012-08-11 | ZN2602:PA21 | URBAN | Equipment Failure | 861347 | 1 | 219.1833 | 219.1833 | 0.00013392 | 6.1099e-05
2012-08-11 | 232:33409 | URBAN | Equipment Failure | 861373 | 1 | 212.45 | 212.45 | 0.0001298 | 6.1099e-05
2012-08-11 | 232:33409 | URBAN | Equipment Failure | 861374 | 1 | 210.9167 | 210.9167 | 0.00012887 | 6.1099e-05
2012-08-11 | ZN195:PA9 | URBAN | Equipment Failure | 861375 | 1 | 230.6167 | 230.6167 | 0.0001409 | 6.1099e-05
2012-08-11 | ZN10994:PA21 | URBAN | Vegetation | 861385 | 1 | 66.3167 | 66.3167 | 4.0519e-05 | 6.1099e-05
2012-08-11 | 230:81440 | URBAN | Vegetation | 861386 | 128 | 35 | 4480 | 0.0027372 | 0.0078206
2012-08-11 | ZN10994:PA21 | URBAN | Vegetation | 861396 | 1 | 291.45 | 291.45 | 0.00017807 | 6.1099e-05
2012-08-10 | ZN1287:PA3 | URBAN | Vegetation | 861405 | 46 | 167 | 7682 | 0.0046936 | 0.0028105
2012-08-10 | ZN1610:PA23 | URBAN | Other | 861408 | 4 | 457 | 1828 | 0.0011169 | 0.00024439
2012-08-11 | ZN2466:PA30 | URBAN | Vegetation | 861433 | 25 | 174 | 4350 | 0.0026578 | 0.0015275
2012-08-11 | ZN2466:PA45 | URBAN | Vegetation | 861433 | 86 | 174 | 14928.1667 | 0.0091209 | 0.0052545
2012-08-11 | ZN342:PA17 | URBAN | Other | 861439 | 1 | 62 | 62 | 3.7881e-05 | 6.1099e-05
2012-08-11 | ZN342:PA18 | URBAN | Other | 861439 | 1 | 62 | 62 | 3.7881e-05 | 6.1099e-05
2012-08-11 | ZN342:PA23 | URBAN | Other | 861439 | 67 | 62 | 4097.05 | 0.0025032 | 0.0040936
2012-08-11 | 230:81440 | URBAN | Other | 861480 | 1 | 178.7167 | 178.7167 | 0.00010919 | 6.1099e-05
2012-08-11 | ZN10993:PA7 | URBAN | Vegetation | 861503 | 65 | 125.75 | 8173.75 | 0.004994 | 0.0039714
2012-08-11 | ZN15004:PA3 | URBAN | Vegetation | 861522 | 1 | 675.7 | 675.7 | 0.00041284 | 6.1099e-05
2012-08-11 | 504:48031 | SHORT RURAL | Other | 861524 | 1 | 132.7333 | 132.7333 | 8.1098e-05 | 6.1099e-05
2012-08-11 | 229:34995 | SHORT RURAL | Equipment Failure | 861531 | 4 | 85 | 340 | 0.00020774 | 0.00024439
2012-08-11 | 232:11454 | SHORT RURAL | Other | 861545 | 1 | 170.65 | 170.65 | 0.00010426 | 6.1099e-05
2012-08-11 | ZN2400:PA11 | SHORT RURAL | Vegetation | 861576 | 58 | 2754 | 139332 | 0.08513 | 0.0035437
2012-08-11 | ZN15009:PA1 | URBAN | Equipment Failure | 861587 | 2012 | 330 | 20120 | 0.012293 | 0.12293
2012-08-11 | ZN15009:PA11 | URBAN | Equipment Failure | 861587 | 2186 | 330 | 21860 | 0.013356 | 0.13356
2012-08-11 | ZN15009:PA12 | URBAN | Equipment Failure | 861587 | 54 | 330 | 540 | 0.00032993 | 0.0032993
2012-08-11 | ZN15009:PA3 | URBAN | Equipment Failure | 861587 | 845 | 330 | 8450 | 0.0051628 | 0.051628
2012-08-11 | ZN15009:PA5 | URBAN | Equipment Failure | 861587 | 1847 | 330 | 18470 | 0.011285 | 0.11285
2012-08-11 | ZN15009:PA7 | URBAN | Equipment Failure | 861587 | 1575 | 330 | 15750 | 0.009623 | 0.09623
2012-08-11 | ZN15009:PA9 | URBAN | Equipment Failure | 861587 | 591 | 330 | 5910 | 0.0036109 | 0.036109
2012-08-11 | ZN15015:PA15 | URBAN | Equipment Failure | 861587 | 444 | 330 | 29304 | 0.017904 | 0.027128
2012-08-11 | ZN15015:PA5 | URBAN | Equipment Failure | 861587 | 1642 | 330 | 55828 | 0.03411 | 0.10032
2012-08-11 | ZN180:PA21 | URBAN | Equipment Failure | 861603 | 72 | 109.3167 | 7870.8 | 0.004809 | 0.0043991
2012-08-11 | 218:7478 | URBAN | Other | 861606 | 1 | 71.9333 | 71.9333 | 4.395e-05 | 6.1099e-05
2012-08-11 | ZN9550:PA35 | URBAN | Other | 861624 | 64 | 179 | 11456 | 0.0069995 | 0.0039103
2012-08-11 | ZN12620:PA13 | SHORT RURAL | Equipment Failure | 861641 | 1 | 1057.4667 | 1057.4667 | 0.0006461 | 6.1099e-05
2012-08-11 | ZN9037:PA2 | URBAN | Vegetation | 861643 | 69 | 56.5 | 3898.5 | 0.0023819 | 0.0042158
2012-08-11 | ZN2568:PA9 | URBAN | Other | 861654 | 1 | 234.7333 | 234.7333 | 0.00014342 | 6.1099e-05
2012-08-11 | ZN2602:PA31 | URBAN | Other | 861655 | 1 | 770.5667 | 770.5667 | 0.00047081 | 6.1099e-05
2012-08-11 | 218:7482 | URBAN | Vegetation | 861658 | 1630 | 58 | 94540 | 0.057763 | 0.099591
2012-08-11 | ZN2568:PA26 | URBAN | Other | 861674 | 1 | 789.4167 | 789.4167 | 0.00048232 | 6.1099e-05
2012-08-11 | ZN3425:PA28 | URBAN | Other | 861679 | 1 | 180.8833 | 180.8833 | 0.00011052 | 6.1099e-05
2012-08-11 | ZN2602:PA41 | URBAN | Other | 861680 | 1 | 240.3833 | 240.3833 | 0.00014687 | 6.1099e-05
2012-08-11 | ZN15008:PA9 | URBAN | Other | 861682 | 1 | 426.4 | 426.4 | 0.00026052 | 6.1099e-05
2012-08-11 | ZN2568:PA9 | URBAN | Other | 861692 | 1 | 176.65 | 176.65 | 0.00010793 | 6.1099e-05
2012-08-11 | ZN3922:PA18 | URBAN | Other | 861696 | 1 | 260.9 | 260.9 | 0.00015941 | 6.1099e-05
2012-08-11 | ZN9252:PA9 | URBAN | Equipment Failure | 861700 | 1 | 216 | 216 | 0.00013197 | 6.1099e-05
2012-08-11 | ZN80:PA40 | URBAN | Other | 861701 | 1 | 206.3 | 206.3 | 0.00012605 | 6.1099e-05
2012-08-11 | ZN15008:PA10 | URBAN | Other | 861703 | 64 | 956 | 61184 | 0.037383 | 0.0039103
2012-08-11 | ZN15008:PA7 | URBAN | Other | 861703 | 67 | 956 | 64052 | 0.039135 | 0.0040936
2012-08-11 | ZN3672:PA35 | URBAN | Other | 861704 | 1 | 573.3667 | 573.3667 | 0.00035032 | 6.1099e-05
2012-08-11 | ZN263:PA33 34DEF | CBD | Equipment Failure | 861705 | 1 | 363.2833 | 363.2833 | 0.00022196 | 6.1099e-05
2012-08-11 | ZN2568:PA9 | URBAN | Other | 861707 | 1 | 148.9667 | 148.9667 | 9.1017e-05 | 6.1099e-05
2012-08-11 | ZN116:PA30 | URBAN | Other | 861719 | 1 | 337.5 | 337.5 | 0.00020621 | 6.1099e-05
2012-08-11 | ZN3922:PA22 | URBAN | Other | 861721 | 1 | 46.7167 | 46.7167 | 2.8543e-05 | 6.1099e-05
2012-08-11 | ZN2568:PA9 | URBAN | Other | 861722 | 1 | 96.6833 | 96.6833 | 5.9072e-05 | 6.1099e-05
2012-08-11 | ZN14143:PA17 | SHORT RURAL | Equipment Failure | 861723 | 746 | 76 | 56696 | 0.03464 | 0.04558
2012-08-11 | ZN15005:PA6 | URBAN | Equipment Failure | 861726 | 1 | 1345.8167 | 1345.8167 | 0.00082228 | 6.1099e-05
2012-08-11 | ZN3922:PA22 | URBAN | Other | 861731 | 1 | 11.8 | 11.8 | 7.2096e-06 | 6.1099e-05
2012-08-11 | ZN9037:PA8 | URBAN | Other | 861733 | 1 | 307.7833 | 307.7833 | 0.00018805 | 6.1099e-05
2012-08-11 | ZN15011:PA10 | URBAN | Other | 861736 | 1 | 272.4333 | 272.4333 | 0.00016645 | 6.1099e-05
2012-08-11 | ZN2568:PA9 | URBAN | Other | 861745 | 1 | 15.5667 | 15.5667 | 9.511e-06 | 6.1099e-05
2012-08-11 | ZN1164:PA4 | URBAN | Vegetation | 861747 | 1 | 1069.6 | 1069.6 | 0.00065351 | 6.1099e-05
2012-08-11 | ZN1285:PA31 | URBAN | Equipment Failure | 861749 | 78 | 42.4167 | 3308.5 | 0.0020214 | 0.0047657
2012-08-11 | ZN36300:PA11 | URBAN | Equipment Failure | 861751 | 176 | 315.2667 | 32340.2667 | 0.019759 | 0.010753
2012-08-11 | ZN36300:PA3 | URBAN | Equipment Failure | 861751 | 2483 | 315.2667 | 237039 | 0.14483 | 0.15171
2012-08-12 | ZN1193:PA7 | URBAN | Other | 861756 | 2 | 917.0667 | 1834.0667 | 0.0011206 | 0.0001222
2012-08-12 | ZN187:PA17 | URBAN | Equipment Failure | 861757 | 1 | 1193 | 1193 | 0.00072891 | 6.1099e-05
2012-08-12 | ZN9118:PA21 | URBAN | Other | 861758 | 1 | 770.1667 | 770.1667 | 0.00047056 | 6.1099e-05
2012-08-12 | ZN72:PA18 | URBAN | Other | 861764 | 1 | 459.7 | 459.7 | 0.00028087 | 6.1099e-05
2012-08-12 | ZN398:PA16 | URBAN | Third Party Impacts | 861773 | 24 | 540 | 12960 | 0.0079184 | 0.0014664
2012-08-12 | ZN15004:PA9 | URBAN | Other | 861775 | 1 | 681.3167 | 681.3167 | 0.00041628 | 6.1099e-05
2012-08-12 | ZN36300:PA3 | URBAN | Other | 861777 | 69 | 90 | 6210 | 0.0037942 | 0.0042158
2012-08-12 | ZN36300:PA11 | URBAN | Other | 861780 | 81 | 114.8167 | 9300.15 | 0.0056823 | 0.004949
2012-08-12 | ZN15004:PA5 | URBAN | Vegetation | 861781 | 35 | 222.2167 | 7777.5833 | 0.004752 | 0.0021385
2012-08-12 | ZN9245:PA13 | URBAN | Equipment Failure | 861784 | 1 | 265.6 | 265.6 | 0.00016228 | 6.1099e-05
2012-08-12 | ZN1788:PA8 | URBAN | Other | 861791 | 1 | 364.0333 | 364.0333 | 0.00022242 | 6.1099e-05
2012-08-12 | ZN15006:PA9 | URBAN | Other | 861792 | 1 | 630.9833 | 630.9833 | 0.00038552 | 6.1099e-05
2012-08-12 | ZN9118:PA21 | URBAN | Equipment Failure | 861802 | 1 | 378.9167 | 378.9167 | 0.00023151 | 6.1099e-05
2012-08-12 | ZN36300:PA11 | URBAN | Other | 861805 | 42 | 65 | 2730 | 0.001668 | 0.0025661
2012-08-12 | 260:33347 | SHORT RURAL | Other | 861863 | 1 | 267.3833 | 267.3833 | 0.00016337 | 6.1099e-05
2012-08-12 | ZN9118:PA11 | URBAN | Third Party Impacts | 861867 | 1 | 594.8667 | 594.8667 | 0.00036346 | 6.1099e-05
2012-08-12 | ZN12620:PA11 | SHORT RURAL | Vegetation | 861875 | 1 | 250.0833 | 250.0833 | 0.0001528 | 6.1099e-05
2012-08-12 | 807:74181 | SHORT RURAL | Equipment Failure | 861886 | 1 | 105 | 105 | 6.4154e-05 | 6.1099e-05
2012-08-12 | ZN12610:PA22 | URBAN | Other | 861899 | 1 | 96.7333 | 96.7333 | 5.9103e-05 | 6.1099e-05
2012-08-12 | ZN12610:PA18 | URBAN | Equipment Failure | 861921 | 1 | 313.9333 | 313.9333 | 0.00019181 | 6.1099e-05
2012-08-12 | ZN129:PA16 | URBAN | Equipment Failure | 861935 | 1 | 277.1833 | 277.1833 | 0.00016936 | 6.1099e-05
2012-08-12 | ZN2568:PA25 | URBAN | Equipment Failure | 861937 | 1 | 521.3667 | 521.3667 | 0.00031855 | 6.1099e-05
2012-08-12 | ZN15006:PA16 | URBAN | Equipment Failure | 861945 | 1 | 315.4667 | 315.4667 | 0.00019275 | 6.1099e-05
2012-08-12 | 232:33413 | SHORT RURAL | Other | 861982 | 1 | 120.4 | 120.4 | 7.3563e-05 | 6.1099e-05
2012-08-12 | ZN36300:PA11 | URBAN | Other | 861988 | 1 | 290.5333 | 290.5333 | 0.00017751 | 6.1099e-05
2012-08-12 | 208:53 | URBAN | Other | 862000 | 1 | 1108.05 | 1108.05 | 0.000677 | 6.1099e-05
2012-08-12 | ZN12580:PA16 | URBAN | Vegetation | 862013 | 118 | 13 | 1534 | 0.00093725 | 0.0072096
2012-08-12 | 264:81244 | URBAN | Other | 862019 | 15 | 125 | 1875 | 0.0011456 | 0.00091648
2012-08-12 | 220:8689 | URBAN | Other | 862020 | 1 | 98.0333 | 98.0333 | 5.9897e-05 | 6.1099e-05
2012-08-12 | ZN12610:PA6 | URBAN | Other | 862024 | 1 | 69.0333 | 69.0333 | 4.2178e-05 | 6.1099e-05
2012-08-12 | 520:48172 | SHORT RURAL | Equipment Failure | 862047 | 1 | 120 | 120 | 7.3318e-05 | 6.1099e-05
2012-08-12 | 213:33771 | URBAN | Other | 862062 | 1 | 83.1667 | 83.1667 | 5.0814e-05 | 6.1099e-05
2012-08-12 | ZN12620:PA7 | URBAN | Equipment Failure | 862067 | 1 | 193.8333 | 193.8333 | 0.00011843 | 6.1099e-05
2012-08-12 | ZN116:PA48 | URBAN | Equipment Failure | 862093 | 1 | 954.7 | 954.7 | 0.00058331 | 6.1099e-05
2012-08-12 | ZN262:PA16 | URBAN | Other | 862101 | 1 | 306.4 | 306.4 | 0.00018721 | 6.1099e-05
2012-08-12 | ZN690:PA30 | URBAN | Other | 862102 | 1 | 696.4 | 696.4 | 0.00042549 | 6.1099e-05
2012-08-12 | ZN3922:PA12 | URBAN | Other | 862105 | 1 | 387.8333 | 387.8333 | 0.00023696 | 6.1099e-05
2012-08-12 | ZN9700:PA15 | URBAN | Other | 862106 | 1 | 392.2 | 392.2 | 0.00023963 | 6.1099e-05
2012-08-12 | ZN10999:PA24 | URBAN | Other | 862111 | 1 | 368.25 | 368.25 | 0.000225 | 6.1099e-05
2012-08-13 | 513:48051 | URBAN | Other | 862114 | 1 | 344.1833 | 344.1833 | 0.00021029 | 6.1099e-05
2012-08-13 | ZN8000:PA20 | URBAN | Equipment Failure | 862117 | 74 | 81 | 5844 | 0.0035706 | 0.0045213
2012-08-13 | 801:74122 | URBAN | Other | 862118 | 1 | 42.9667 | 42.9667 | 2.6252e-05 | 6.1099e-05
2012-08-09 | 227:13015 | SHORT RURAL | Animals | 862126 | 109 | 67 | 7303 | 0.0044794 | 0.0066856
2012-08-13 | ZN3154:PA13 | URBAN | Equipment Failure | 862137 | 1 | 366.0167 | 366.0167 | 0.00022363 | 6.1099e-05
2012-08-13 | 224:80332 | URBAN | Other | 862200 | 1 | 99.4667 | 99.4667 | 6.0773e-05 | 6.1099e-05
2012-08-13 | ZN12610:PA6 | URBAN | Other | 862226 | 1 | 201.5667 | 201.5667 | 0.00012315 | 6.1099e-05
2012-08-13 | ZN12570:PA12 | SHORT RURAL | Vegetation | 862283 | 1 | 454.8167 | 454.8167 | 0.00027789 | 6.1099e-05
2012-08-10 | ZN1788:PA17 | URBAN | Other | 862306 | 121 | 178 | 21538 | 0.013159 | 0.0073929
2012-08-10 | ZN2602:PA18 | URBAN | Equipment Failure | 862318 | 57 | 4411 | 5177.5 | 0.0031634 | 0.0034826
2012-08-10 | ZN2602:PA35 | URBAN | Equipment Failure | 862318 | 71 | 4411 | 6461 | 0.0039476 | 0.004338
2012-08-10 | 227:13014 | SHORT RURAL | Vegetation | 862376 | 6 | 165 | 990 | 0.00060488 | 0.00036659
2012-08-13 | ZN9118:PA26 | URBAN | Other | 862384 | 1 | 1503.5667 | 1503.5667 | 0.00091866 | 6.1099e-05
2012-08-10 | 264:81244 | URBAN | Other | 862387 | 1234 | 79 | 97486 | 0.059563 | 0.075396
2012-08-13 | ZN9037:PA8 | URBAN | Equipment Failure | 862468 | 1 | 29.5833 | 29.5833 | 1.8075e-05 | 6.1099e-05
2012-08-10 | 222:2017 | URBAN | Equipment Failure | 862482 | 24 | 59 | 1416 | 0.00086516 | 0.0014664
2012-08-13 | 238:34144 | URBAN | Other | 862487 | 1 | 426.8667 | 426.8667 | 0.00026081 | 6.1099e-05
2012-08-13 | ZN9118:PA11 | URBAN | Equipment Failure | 862498 | 1 | 419.7833 | 419.7833 | 0.00025648 | 6.1099e-05
2012-08-13 | ZN15002:PA6 | URBAN | Equipment Failure | 862534 | 1 | 423.4 | 423.4 | 0.00025869 | 6.1099e-05
2012-08-10 | 238:34141 | SHORT RURAL | Other | 862538 | 8 | 118 | 944 | 0.00057677 | 0.00048879
2012-08-13 | ZN14144:PA7 | SHORT RURAL | Equipment Failure | 862541 | 1 | 388.1 | 388.1 | 0.00023712 | 6.1099e-05
2012-08-13 | ZN10997:PA5 | URBAN | Equipment Failure | 862546 | 1 | 186.0833 | 186.0833 | 0.00011369 | 6.1099e-05
2012-08-13 | ZN9037:PA9 | URBAN | Equipment Failure | 862554 | 1 | 244.1167 | 244.1167 | 0.00014915 | 6.1099e-05
2012-08-13 | ZN9252:PA2 | URBAN | Equipment Failure | 862578 | 1 | 985.7833 | 985.7833 | 0.0006023 | 6.1099e-05
2012-08-13 | ZN398:PA8 | URBAN | Other | 862591 | 1 | 1043.75 | 1043.75 | 0.00063772 | 6.1099e-05
2012-08-13 | 807:74179 | SHORT RURAL | Equipment Failure | 862603 | 149 | 72 | 10728 | 0.0065547 | 0.0091037
2012-08-13 | 812:19072 | SHORT RURAL | Equipment Failure | 862603 | 1 | 72 | 72 | 4.3991e-05 | 6.1099e-05
2012-08-13 | 221:11900 | URBAN | Other | 862611 | 1 | 98.5 | 98.5 | 6.0182e-05 | 6.1099e-05
2012-08-13 | 229:34995 | SHORT RURAL | Other | 862626 | 1 | 23.2333 | 23.2333 | 1.4195e-05 | 6.1099e-05
2012-08-13 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 862644 | 1 | 1074.45 | 1074.45 | 0.00065647 | 6.1099e-05
2012-08-13 | 227:13020 | SHORT RURAL | Other | 862654 | 1 | 125.5167 | 125.5167 | 7.6689e-05 | 6.1099e-05
2012-08-13 | 502:48010 | SHORT RURAL | Other | 862668 | 4 | 101 | 404 | 0.00024684 | 0.00024439
2012-08-13 | ZN180:PA28 | URBAN | Equipment Failure | 862678 | 47 | 144.9333 | 6811.8667 | 0.004162 | 0.0028716
2012-08-13 | ZN2602:PA41 | URBAN | Equipment Failure | 862719 | 1 | 359.4333 | 359.4333 | 0.00021961 | 6.1099e-05
2012-08-13 | ZN9245:PA4 | URBAN | Equipment Failure | 862732 | 1 | 742.75 | 742.75 | 0.00045381 | 6.1099e-05
2012-08-13 | 512:48047 | SHORT RURAL | Other | 862736 | 1 | 108.5833 | 108.5833 | 6.6343e-05 | 6.1099e-05
2012-08-14 | ZN3922:PA12 | URBAN | Other | 862738 | 1 | 355.6667 | 355.6667 | 0.00021731 | 6.1099e-05
2012-08-14 | 216:10726 | URBAN | Equipment Failure | 862740 | 1 | 237.7 | 237.7 | 0.00014523 | 6.1099e-05
2012-08-11 | ZN15005:PA8 | URBAN | Equipment Failure | 862747 | 16 | 75 | 1200 | 0.00073318 | 0.00097758
2012-08-14 | ZN847:PA48 | URBAN | Other | 862750 | 1 | 205.4167 | 205.4167 | 0.00012551 | 6.1099e-05
2012-08-12 | ZN15014:PA14 | SHORT RURAL | Vegetation | 862800 | 328 | 79 | 25912 | 0.015832 | 0.02004
2012-08-14 | ZN12690:PA10 | URBAN | Other | 862807 | 1 | 251.7333 | 251.7333 | 0.00015381 | 6.1099e-05
2012-08-12 | ZN36300:PA3 | URBAN | Other | 862811 | 26 | 65 | 1690 | 0.0010326 | 0.0015886
2012-08-10 | 509:48039 | LONG RURAL | Vegetation | 862820 | 39 | 985 | 21830 | 0.013338 | 0.0023828
2012-08-10 | 501:48123 | SHORT RURAL | Equipment Failure | 862831 | 21 | 1019 | 4706 | 0.0028753 | 0.0012831
2012-08-14 | ZN10994:PA13 | URBAN | Other | 862860 | 51 | 263.8167 | 13454.65 | 0.0082206 | 0.003116
2012-08-14 | 813:89059 | URBAN | Other | 862864 | 1 | 249.0833 | 249.0833 | 0.00015219 | 6.1099e-05
2012-08-14 | ZN630:PA38 | URBAN | Other | 862871 | 1 | 296.0833 | 296.0833 | 0.0001809 | 6.1099e-05
2012-08-14 | ZN12580:PA16 | URBAN | Other | 862902 | 1 | 153.7667 | 153.7667 | 9.3949e-05 | 6.1099e-05
2012-08-14 | ZN3154:PA14 | URBAN | Vegetation | 862929 | 1 | 160.4 | 160.4 | 9.8002e-05 | 6.1099e-05
2012-08-10 | ZN195:PA30 | URBAN | Vegetation | 862954 | 26 | 250 | 6500 | 0.0039714 | 0.0015886
2012-08-10 | ZN15005:PA12 | URBAN | Vegetation | 862963 | 129 | 42 | 5418 | 0.0033103 | 0.0078817
2012-08-10 | ZN15005:PA12 | URBAN | Equipment Failure | 862965 | 1 | 105 | 105 | 6.4154e-05 | 6.1099e-05
2012-08-14 | ZN1164:PA26 | URBAN | Equipment Failure | 862988 | 61 | 17 | 1037 | 0.00063359 | 0.003727
2012-08-14 | ZN9118:PA12 | URBAN | Vegetation | 863009 | 1 | 294.5167 | 294.5167 | 0.00017995 | 6.1099e-05
2012-08-14 | ZN12660:PA5 | SHORT RURAL | Other | 863040 | 1 | 152.3 | 152.3 | 9.3053e-05 | 6.1099e-05
2012-08-14 | ZN12610:PA9 | SHORT RURAL | Equipment Failure | 863095 | 1 | 151 | 151 | 9.2259e-05 | 6.1099e-05
2012-08-14 | ZN10997:PA8 | URBAN | Other | 863134 | 1 | 162.95 | 162.95 | 9.956e-05 | 6.1099e-05
2012-08-14 | ZN12640:PA8 | SHORT RURAL | Equipment Failure | 863157 | 1 | 94.8667 | 94.8667 | 5.7962e-05 | 6.1099e-05
2012-08-11 | ZN2602:PA8 | URBAN | Weather | 863165 | 86 | 102 | 8772 | 0.0053596 | 0.0052545
2012-08-14 | ZN262:PA34 | URBAN | Other | 863179 | 1 | 403.3833 | 403.3833 | 0.00024646 | 6.1099e-05
2012-08-14 | 202:34260 | URBAN | Other | 863238 | 1 | 675.9167 | 675.9167 | 0.00041298 | 6.1099e-05
2012-08-14 | ZN2835:PA18 | URBAN | Other | 863242 | 1 | 430.6667 | 430.6667 | 0.00026313 | 6.1099e-05
2012-08-14 | ZN3472:PA8 | URBAN | Other | 863247 | 1 | 203.2667 | 203.2667 | 0.00012419 | 6.1099e-05
2012-08-14 | ZN3472:PA21 | URBAN | Other | 863256 | 1 | 223.6167 | 223.6167 | 0.00013663 | 6.1099e-05
2012-08-15 | ZN2568:PA29 | URBAN | Equipment Failure | 863265 | 1 | 78.6667 | 78.6667 | 4.8064e-05 | 6.1099e-05
2012-08-15 | ZN3425:PA44 | URBAN | Animals | 863266 | 57 | 95 | 5415 | 0.0033085 | 0.0034826
2012-08-15 | ZN12630:PA2 | SHORT RURAL | Equipment Failure | 863354 | 1 | 237.8833 | 237.8833 | 0.00014534 | 6.1099e-05
2012-08-14 | 501:48123 | SHORT RURAL | Equipment Failure | 863366 | 3 | 10 | 30 | 1.833e-05 | 0.0001833
2012-08-13 | ZN116:PA48 | URBAN | Equipment Failure | 863410 | 14 | 180 | 2520 | 0.0015397 | 0.00085538
2012-08-15 | ZN1788:PA17 | URBAN | Third Party Impacts | 863418 | 50 | 81.5833 | 4079.1667 | 0.0024923 | 0.0030549
2012-08-15 | ZN3472:PA7 | SHORT RURAL | Equipment Failure | 863457 | 1 | 121.0167 | 121.0167 | 7.394e-05 | 6.1099e-05
2012-08-15 | 520:48172 | SHORT RURAL | Animals | 863485 | 1 | 128.5667 | 128.5667 | 7.8552e-05 | 6.1099e-05
2012-08-15 | ZN14892:PA16 | URBAN | Other | 863489 | 1 | 252.5167 | 252.5167 | 0.00015428 | 6.1099e-05
2012-08-15 | ZN10994:PA21 | URBAN | Equipment Failure | 863508 | 1 | 956.15 | 956.15 | 0.00058419 | 6.1099e-05
2012-08-10 | ZN15001:PA10 | URBAN | Equipment Failure | 863511 | 24 | 60 | 1440 | 0.00087982 | 0.0014664
2012-08-15 | 203:8084 | URBAN | Equipment Failure | 863514 | 1 | 172.3167 | 172.3167 | 0.00010528 | 6.1099e-05
2012-08-15 | 801:74121 | SHORT RURAL | Animals | 863568 | 1 | 65 | 65 | 3.9714e-05 | 6.1099e-05
2012-08-11 | ZN2635:PA9 | URBAN | Vegetation | 863655 | 1 | 20 | 20 | 1.222e-05 | 6.1099e-05
2012-08-15 | ZN10999:PA17 | URBAN | Third Party Impacts | 863679 | 37 | 152 | 5624 | 0.0034362 | 0.0022606
2012-08-15 | ZN35800:PA21 | URBAN | Other | 863715 | 1 | 297.6667 | 297.6667 | 0.00018187 | 6.1099e-05
2012-08-15 | ZN10990:PA11 | URBAN | Other | 863753 | 1 | 307.7667 | 307.7667 | 0.00018804 | 6.1099e-05
2012-08-15 | ZN35800:PA21 | URBAN | Other | 863787 | 1 | 72.55 | 72.55 | 4.4327e-05 | 6.1099e-05
2012-08-15 | ZN15014:PA22 | URBAN | Animals | 863794 | 856 | 45 | 38520 | 0.023535 | 0.0523
2012-08-16 | ZN1850:PA14 | URBAN | Equipment Failure | 863802 | 26 | 283.2167 | 7363.6333 | 0.0044991 | 0.0015886
2012-08-16 | ZN10999:PA12 | URBAN | Other | 863808 | 2641 | 23 | 60743 | 0.037113 | 0.16136
2012-08-16 | ZN10999:PA32 | URBAN | Other | 863808 | 47 | 23 | 1081 | 0.00066048 | 0.0028716
2012-08-15 | 520:48172 | SHORT RURAL | Animals | 863830 | 1 | 100 | 100 | 6.1099e-05 | 6.1099e-05
2012-08-11 | ZN9118:PA24 | URBAN | Operational Error | 863846 | 47 | 145 | 6815 | 0.0041639 | 0.0028716
2012-08-10 | ZN15014:PA11 | URBAN | Vegetation | 863852 | 926 | 203 | 182434 | 0.11146 | 0.056577
2012-08-10 | ZN15014:PA20 | URBAN | Vegetation | 863852 | 1 | 203 | 179 | 0.00010937 | 6.1099e-05
2012-08-12 | ZN690:PA35 | URBAN | Equipment Failure | 863908 | 94 | 367 | 34498 | 0.021078 | 0.0057433
2012-08-16 | 512:48049 | SHORT RURAL | Other | 863934 | 8 | 95 | 760 | 0.00046435 | 0.00048879
2012-08-16 | ZN9301:PA13 | SHORT RURAL | Third Party Impacts | 863990 | 1 | 255.1 | 255.1 | 0.00015586 | 6.1099e-05
2012-08-16 | ZN9301:PA13 | SHORT RURAL | Third Party Impacts | 863992 | 1 | 254.1667 | 254.1667 | 0.00015529 | 6.1099e-05
2012-08-16 | ZN12650:PA13 | SHORT RURAL | Vegetation | 864054 | 1 | 92.0667 | 92.0667 | 5.6251e-05 | 6.1099e-05
2012-08-16 | 225:33679 | URBAN | Vegetation | 864086 | 1 | 111.2833 | 111.2833 | 6.7993e-05 | 6.1099e-05
2012-08-16 | ZN14144:PA2 | SHORT RURAL | Equipment Failure | 864092 | 3 | 285 | 855 | 0.00052239 | 0.0001833
2012-08-16 | ZN15001:PA13 | URBAN | Equipment Failure | 864199 | 1 | 49 | 37 | 2.2606e-05 | 6.1099e-05
2012-08-16 | ZN15001:PA17 | URBAN | Equipment Failure | 864199 | 12 | 49 | 480 | 0.00029327 | 0.00073318
2012-08-16 | ZN2400:PA18 | SHORT RURAL | Equipment Failure | 864210 | 1 | 293.85 | 293.85 | 0.00017954 | 6.1099e-05
2012-08-16 | ZN180:PA32 | URBAN | Other | 864215 | 1 | 53.8333 | 53.8333 | 3.2891e-05 | 6.1099e-05
2012-08-16 | ZN9900:PA1 | URBAN | Other | 864221 | 1 | 894.7667 | 894.7667 | 0.00054669 | 6.1099e-05
2012-08-16 | 264:81240 | SHORT RURAL | Third Party Impacts | 864247 | 311 | 142 | 27082 | 0.016547 | 0.019002
2012-08-16 | ZN15015:PA15 | URBAN | Other | 864276 | 1 | 62 | 62 | 3.7881e-05 | 6.1099e-05
2012-08-16 | ZN15015:PA5 | URBAN | Other | 864276 | 62 | 62 | 3787.1667 | 0.0023139 | 0.0037881
2012-08-17 | ZN167:PA20 | URBAN | Equipment Failure | 864296 | 1 | 136 | 136 | 8.3094e-05 | 6.1099e-05
2012-08-17 | ZN12610:PA11 | URBAN | Other | 864312 | 1 | 237.6 | 237.6 | 0.00014517 | 6.1099e-05
2012-08-17 | ZN1788:PA11 | URBAN | Equipment Failure | 864314 | 1 | 349.3667 | 349.3667 | 0.00021346 | 6.1099e-05
2012-08-17 | 813:89055 | SHORT RURAL | Equipment Failure | 864334 | 1 | 168 | 168 | 0.00010265 | 6.1099e-05
2012-08-17 | 807:74184 | SHORT RURAL | Other | 864335 | 1 | 249.1833 | 249.1833 | 0.00015225 | 6.1099e-05
2012-08-16 | ZN35370:PA10 | SHORT RURAL | Other | 864372 | 379 | 3 | 1137 | 0.00069469 | 0.023156
2012-08-17 | ZN1788:PA30 | URBAN | Other | 864394 | 1 | 37.1333 | 37.1333 | 2.2688e-05 | 6.1099e-05
2012-08-01 | ZN12620:PA11 | SHORT RURAL | Other | 864447 | 37 | 39 | 1443 | 0.00088164 | 0.0022606
2012-08-17 | ZN10994:PA13 | URBAN | Vegetation | 864461 | 49 | 83.8167 | 4107.0167 | 0.0025093 | 0.0029938
2012-08-17 | ZN12630:PA2 | SHORT RURAL | Equipment Failure | 864469 | 526 | 714 | 85888 | 0.052476 | 0.032138
2012-08-10 | ZN12570:PA1 | SHORT RURAL | Equipment Failure | 864489 | 1733 | 93 | 52011 | 0.031778 | 0.10588
2012-08-17 | ZN9118:PA22 | URBAN | Vegetation | 864493 | 16 | 107 | 1712 | 0.001046 | 0.00097758
2012-08-17 | 238:34144 | URBAN | Equipment Failure | 864497 | 19 | 32 | 608 | 0.00037148 | 0.0011609
2012-08-17 | ZN1290:PA12 | URBAN | Equipment Failure | 864508 | 954 | 54 | 51516 | 0.031476 | 0.058288
2012-08-17 | 520:48172 | SHORT RURAL | Other | 864513 | 13 | 157 | 2041 | 0.001247 | 0.00079428
2012-08-17 | 526:34636 | SHORT RURAL | Vegetation | 864535 | 4 | 235 | 940 | 0.00057433 | 0.00024439
2012-08-17 | ZN3425:PA28 | URBAN | Other | 864549 | 1 | 141.2667 | 141.2667 | 8.6312e-05 | 6.1099e-05
2012-08-17 | 516:48065 | SHORT RURAL | Equipment Failure | 864555 | 6 | 188 | 1128 | 0.00068919 | 0.00036659
2012-08-17 | ZN10990:PA1 | URBAN | Equipment Failure | 864565 | 2 | 107 | 214 | 0.00013075 | 0.0001222
2012-08-17 | ZN10990:PA11 | URBAN | Equipment Failure | 864565 | 1146 | 107 | 122622 | 0.07492 | 0.070019
2012-08-17 | ZN10990:PA2 | URBAN | Equipment Failure | 864565 | 2 | 107 | 214 | 0.00013075 | 0.0001222
2012-08-17 | ZN2835:PA31 | URBAN | Vegetation | 864578 | 1 | 625.5167 | 625.5167 | 0.00038218 | 6.1099e-05
2012-08-17 | ZN35370:PA8 | SHORT RURAL | Vegetation | 864582 | 623 | 1423 | 65423 | 0.039973 | 0.038064
2012-08-17 | 526:34636 | SHORT RURAL | Vegetation | 864586 | 238 | 449 | 75404 | 0.046071 | 0.014541
2012-08-17 | 224:80332 | URBAN | Other | 864589 | 1 | 15.6333 | 15.6333 | 9.5518e-06 | 6.1099e-05
2012-08-17 | 224:80332 | URBAN | Other | 864590 | 1 | 13.5167 | 13.5167 | 8.2585e-06 | 6.1099e-05
2012-08-17 | ZN3154:PA12 | URBAN | Other | 864593 | 769 | 143 | 76170 | 0.046539 | 0.046985
2012-08-17 | 813:89063 | SHORT RURAL | Equipment Failure | 864595 | 33 | 346.65 | 11439.45 | 0.0069893 | 0.0020163
2012-08-17 | ZN2568:PA27 | URBAN | Vegetation | 864616 | 45 | 164.7333 | 7413 | 0.0045292 | 0.0027494
2012-08-17 | 225:33670 | SHORT RURAL | Vegetation | 864654 | 33 | 173.95 | 5150.5333 | 0.0031469 | 0.0020163
2012-08-17 | ZN9118:PA17 | URBAN | Vegetation | 864655 | 33 | 62.5667 | 2064.7 | 0.0012615 | 0.0020163
2012-08-17 | ZN384:PA33 | URBAN | Equipment Failure | 864657 | 1 | 97.4167 | 97.4167 | 5.952e-05 | 6.1099e-05
2012-08-17 | ZN10994:PA21 | URBAN | Vegetation | 864664 | 32 | 202.7167 | 6486.9333 | 0.0039634 | 0.0019552
2012-08-17 | ZN2466:PA5 | URBAN | Equipment Failure | 864665 | 108 | 226.65 | 24478.2 | 0.014956 | 0.0065987
2012-08-17 | ZN129:PA19 | URBAN | Equipment Failure | 864667 | 1 | 151.35 | 151.35 | 9.2473e-05 | 6.1099e-05
2012-08-17 | ZN1068:PA26 | URBAN | Other | 864671 | 1 | 509.3833 | 509.3833 | 0.00031123 | 6.1099e-05
2012-08-17 | ZN2835:PA31 | URBAN | Vegetation | 864691 | 70 | 169.95 | 11896.5 | 0.0072686 | 0.0042769
2012-08-17 | ZN901:PA14 | URBAN | Vegetation | 864715 | 3 | 509 | 1527 | 0.00093298 | 0.0001833
2012-08-17 | ZN2602:PA21 | URBAN | Other | 864722 | 116 | 125 | 14500 | 0.0088593 | 0.0070874
2012-08-17 | ZN1193:PA8 | URBAN | Other | 864730 | 1 | 34.3833 | 34.3833 | 2.1008e-05 | 6.1099e-05
2012-08-17 | ZN35370:PA8 | SHORT RURAL | Vegetation | 864745 | 22 | 15 | 330 | 0.00020163 | 0.0013442
2012-08-17 | ZN847:PA7 | URBAN | Equipment Failure | 864747 | 61 | 266.7833 | 16273.7833 | 0.0099431 | 0.003727
2012-08-17 | ZN3154:PA4 | URBAN | Vegetation | 864749 | 31 | 140 | 4340 | 0.0026517 | 0.0018941
2012-08-17 | ZN1287:PA17 | URBAN | Other | 864753 | 1 | 185.4667 | 185.4667 | 0.00011332 | 6.1099e-05
2012-08-17 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 864763 | 1 | 1621.0833 | 1621.0833 | 0.00099046 | 6.1099e-05
2012-08-17 | ZN262:PA31 | URBAN | Vegetation | 864797 | 1 | 93.2667 | 93.2667 | 5.6985e-05 | 6.1099e-05
2012-08-17 | ZN12640:PA13 | SHORT RURAL | Vegetation | 864807 | 1 | 367.0833 | 367.0833 | 0.00022428 | 6.1099e-05
2012-08-17 | 238:34140 | URBAN | Other | 864811 | 1 | 175.2 | 175.2 | 0.00010704 | 6.1099e-05
2012-08-17 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 864817 | 3 | 146 | 378 | 0.00023095 | 0.0001833
2012-08-17 | ZN4545:PA17 | URBAN | Other | 864823 | 1 | 83.0667 | 83.0667 | 5.0753e-05 | 6.1099e-05
2012-08-17 | ZN195:PA9 | URBAN | Vegetation | 864839 | 70 | 235.6 | 16492 | 0.010076 | 0.0042769
2012-08-17 | ZN15010:PA11 | URBAN | Vegetation | 864842 | 58 | 253.05 | 14676.9 | 0.0089674 | 0.0035437
2012-08-17 | 501:48123 | SHORT RURAL | Vegetation | 864847 | 368 | 209 | 74259 | 0.045371 | 0.022484
2012-08-17 | ZN15008:PA5 | URBAN | Equipment Failure | 864848 | 1 | 1217.75 | 1217.75 | 0.00074403 | 6.1099e-05
2012-08-17 | 512:48046 | SHORT RURAL | Vegetation | 864851 | 7 | 141.0667 | 987.4667 | 0.00060333 | 0.00042769
2012-08-17 | ZN129:PA12 | URBAN | Weather | 864854 | 56 | 176.3167 | 9873.7333 | 0.0060327 | 0.0034215
2012-08-17 | ZN1193:PA10 | URBAN | Other | 864889 | 1 | 985.7667 | 985.7667 | 0.00060229 | 6.1099e-05
2012-08-18 | ZN14144:PA1 | URBAN | Other | 864952 | 1 | 639.6667 | 639.6667 | 0.00039083 | 6.1099e-05
2012-08-18 | 238:34147 | URBAN | Other | 864953 | 1 | 127.8667 | 127.8667 | 7.8125e-05 | 6.1099e-05
2012-08-18 | 231:8415 | SHORT RURAL | Vegetation | 864963 | 1 | 111.6333 | 83.3833 | 5.0946e-05 | 6.1099e-05
2012-08-18 | 264:81244 | URBAN | Vegetation | 864963 | 85 | 111.6333 | 9350 | 0.0057127 | 0.0051934
2012-08-18 | ZN2400:PA22 | URBAN | Vegetation | 864975 | 1 | 194.3 | 194.3 | 0.00011871 | 6.1099e-05
2012-08-18 | 232:11454 | SHORT RURAL | Other | 864979 | 1 | 186.1667 | 186.1667 | 0.00011375 | 6.1099e-05
2012-08-18 | 258:80784 | URBAN | Vegetation | 864990 | 1 | 550.2 | 550.2 | 0.00033616 | 6.1099e-05
2012-08-18 | 224:80346 | URBAN | Other | 865000 | 1 | 84.9333 | 84.9333 | 5.1893e-05 | 6.1099e-05
2012-08-18 | 526:34637 | SHORT RURAL | Equipment Failure | 865006 | 2 | 379 | 484.0667 | 0.00029576 | 0.0001222
2012-08-18 | 511:29878 | SHORT RURAL | Equipment Failure | 865013 | 6 | 279 | 1674 | 0.0010228 | 0.00036659
2012-08-18 | 256:80635 | URBAN | Other | 865032 | 1 | 120.95 | 120.95 | 7.3899e-05 | 6.1099e-05
2012-08-18 | 507:80922 | SHORT RURAL | Other | 865038 | 1 | 88.0667 | 88.0667 | 5.3808e-05 | 6.1099e-05
2012-08-18 | ZN15008:PA1 | URBAN | Equipment Failure | 865039 | 1 | 713.1333 | 713.1333 | 0.00043571 | 6.1099e-05
2012-08-18 | 507:80922 | SHORT RURAL | Other | 865041 | 1 | 87.3667 | 87.3667 | 5.338e-05 | 6.1099e-05
2012-08-18 | ZN9118:PA13 | URBAN | Equipment Failure | 865042 | 47 | 50 | 2350 | 0.0014358 | 0.0028716
2012-08-18 | 256:80635 | URBAN | Other | 865043 | 1 | 101.9333 | 101.9333 | 6.228e-05 | 6.1099e-05
2012-08-18 | 258:80785 | URBAN | Vegetation | 865046 | 1 | 381.8667 | 381.8667 | 0.00023332 | 6.1099e-05
2012-08-18 | 227:13020 | SHORT RURAL | Vegetation | 865049 | 20 | 94 | 1880 | 0.0011487 | 0.001222
2012-08-18 | ZN12610:PA7 | URBAN | Equipment Failure | 865055 | 1 | 434.4333 | 434.4333 | 0.00026543 | 6.1099e-05
2012-08-18 | ZN847:PA5 | URBAN | Vegetation | 865075 | 1 | 1380.95 | 1380.95 | 0.00084374 | 6.1099e-05
2012-08-18 | 229:34986 | SHORT RURAL | Other | 865080 | 1 | 851.75 | 851.75 | 0.00052041 | 6.1099e-05
2012-08-18 | 232:11457 | URBAN | Other | 865083 | 1 | 647.75 | 647.75 | 0.00039577 | 6.1099e-05
2012-08-18 | 501:48122 | SHORT RURAL | Vegetation | 865084 | 1 | 194.3167 | 194.3167 | 0.00011872 | 6.1099e-05
2012-08-18 | 238:34144 | URBAN | Other | 865085 | 1 | 119.75 | 119.75 | 7.3166e-05 | 6.1099e-05
2012-08-18 | ZN2473:PA21 | URBAN | Equipment Failure | 865101 | 1906 | 133 | 218240 | 0.13334 | 0.11645
2012-08-18 | 230:81440 | URBAN | Vegetation | 865109 | 1 | 479.9167 | 479.9167 | 0.00029322 | 6.1099e-05
2012-08-18 | 264:81240 | SHORT RURAL | Equipment Failure | 865114 | 22 | 464.3 | 10214.6 | 0.006241 | 0.0013442
2012-08-18 | 203:8086 | URBAN | Other | 865125 | 1 | 117.5333 | 117.5333 | 7.1811e-05 | 6.1099e-05
2012-08-18 | ZN1673:PA7 | URBAN | Other | 865127 | 1 | 42.35 | 42.35 | 2.5875e-05 | 6.1099e-05
2012-08-18 | 203:8086 | URBAN | Other | 865128 | 1 | 113.3333 | 113.3333 | 6.9245e-05 | 6.1099e-05
2012-08-18 | ZN10996:PA20 | URBAN | Equipment Failure | 865140 | 136 | 57 | 7752 | 0.0047364 | 0.0083094
2012-08-18 | 512:48047 | SHORT RURAL | Other | 865144 | 1 | 336.95 | 336.95 | 0.00020587 | 6.1099e-05
2012-08-18 | ZN116:PA33 | URBAN | Other | 865158 | 1 | 345.8 | 345.8 | 0.00021128 | 6.1099e-05
2012-08-18 | 227:13015 | SHORT RURAL | Other | 865161 | 1 | 95.4667 | 95.4667 | 5.8329e-05 | 6.1099e-05
2012-08-18 | 801:74117 | SHORT RURAL | Vegetation | 865173 | 1 | 44.0667 | 44.0667 | 2.6924e-05 | 6.1099e-05
2012-08-18 | 258:80785 | URBAN | Equipment Failure | 865203 | 1173 | 10 | 11730 | 0.0071669 | 0.071669
2012-08-18 | 258:80793 | SHORT RURAL | Equipment Failure | 865203 | 1 | 10 | 10 | 6.1099e-06 | 6.1099e-05
2012-08-18 | 510:48164 | SHORT RURAL | Vegetation | 865213 | 84 | 296 | 12533 | 0.0076575 | 0.0051323
2012-08-18 | 512:48047 | SHORT RURAL | Other | 865223 | 1 | 198.8 | 198.8 | 0.00012146 | 6.1099e-05
2012-08-18 | ZN14892:PA13 | URBAN | Animals | 865225 | 57 | 58 | 3306 | 0.0020199 | 0.0034826
2012-08-18 | ZN14892:PA19 | URBAN | Animals | 865225 | 1 | 58 | 58 | 3.5437e-05 | 6.1099e-05
2012-08-30 | ZN14892:PA19 | URBAN | Equipment Failure | 865227 | 132 | 13 | 1716 | 0.0010485 | 0.008065
2012-08-18 | ZN1193:PA16 | URBAN | Other | 865253 | 2 | 84.5 | 167.75 | 0.00010249 | 0.0001222
2012-08-19 | ZN3425:PA28 | URBAN | Equipment Failure | 865257 | 744 | 217 | 125900 | 0.076923 | 0.045457
2012-08-19 | ZN1287:PA6 | URBAN | Equipment Failure | 865264 | 54 | 346 | 18684 | 0.011416 | 0.0032993
2012-08-19 | 510:48164 | SHORT RURAL | Equipment Failure | 865265 | 1 | 375 | 375 | 0.00022912 | 6.1099e-05
2012-08-19 | 224:80341 | URBAN | Other | 865267 | 1 | 39.95 | 39.95 | 2.4409e-05 | 6.1099e-05
2012-08-19 | 203:8089 | URBAN | Other | 865305 | 1 | 50.2833 | 50.2833 | 3.0722e-05 | 6.1099e-05
2012-08-19 | 232:11454 | SHORT RURAL | Other | 865318 | 1 | 217.95 | 217.95 | 0.00013316 | 6.1099e-05
2012-08-19 | 235:2120 | SHORT RURAL | Vegetation | 865326 | 1 | 80.3167 | 80.3167 | 4.9072e-05 | 6.1099e-05
2012-08-19 | 235:2124 | URBAN | Vegetation | 865331 | 1 | 88.15 | 88.15 | 5.3858e-05 | 6.1099e-05
2012-08-19 | 512:48049 | SHORT RURAL | Other | 865337 | 1 | 94.2833 | 94.2833 | 5.7606e-05 | 6.1099e-05
2012-08-19 | ZN10999:PA15 | URBAN | Vegetation | 865351 | 51 | 137 | 6987 | 0.004269 | 0.003116
2012-08-19 | 504:48033 | SHORT RURAL | Other | 865361 | 1 | 88.4167 | 88.4167 | 5.4021e-05 | 6.1099e-05
2012-08-19 | ZN9118:PA12 | URBAN | Animals | 865368 | 32 | 116.05 | 3713.6 | 0.002269 | 0.0019552
2012-08-19 | ZN2602:PA4 | URBAN | Equipment Failure | 865374 | 75 | 30 | 2250 | 0.0013747 | 0.0045824
2012-08-19 | 509:48039 | LONG RURAL | Animals | 865379 | 4 | 68.8667 | 275.4667 | 0.00016831 | 0.00024439
2012-08-19 | ZN187:PA14 | URBAN | Other | 865381 | 95 | 189 | 17955 | 0.01097 | 0.0058044
2012-08-19 | ZN15014:PA7 | URBAN | Equipment Failure | 865383 | 9 | 242 | 2178 | 0.0013307 | 0.00054989
2012-08-19 | 511:29873 | SHORT RURAL | Equipment Failure | 865395 | 5 | 127 | 635 | 0.00038798 | 0.00030549
2012-08-20 | 810:74054 | LONG RURAL | Other | 865408 | 2 | 122 | 244 | 0.00014908 | 0.0001222
2012-08-20 | ZN15001:PA11 | URBAN | Other | 865426 | 1 | 63.9833 | 63.9833 | 3.9093e-05 | 6.1099e-05
2012-08-20 | 512:48046 | SHORT RURAL | Equipment Failure | 865468 | 1 | 507.2333 | 507.2333 | 0.00030991 | 6.1099e-05
2012-08-16 | ZN690:PA36 | URBAN | Third Party Impacts | 865565 | 55 | 83 | 4565 | 0.0027892 | 0.0033604
2012-08-20 | ZN36300:PA11 | URBAN | Equipment Failure | 865572 | 2 | 279.45 | 558.9 | 0.00034148 | 0.0001222
2012-08-20 | 206:34441 | URBAN | Vegetation | 865636 | 1 | 78.8167 | 78.8167 | 4.8156e-05 | 6.1099e-05
2012-08-20 | ZN9700:PA22 | URBAN | Other | 865659 | 1 | 96.1333 | 96.1333 | 5.8736e-05 | 6.1099e-05
2012-08-20 | 513:48056 | SHORT RURAL | Animals | 865691 | 10 | 42 | 420 | 0.00025661 | 0.00061099
2012-08-17 | 515:35193 | SHORT RURAL | Other | 865744 | 17 | 84 | 1428 | 0.00087249 | 0.0010387
2012-08-20 | 512:48047 | SHORT RURAL | Other | 865798 | 1 | 159.45 | 159.45 | 9.7422e-05 | 6.1099e-05
2012-08-20 | ZN690:PA12 | URBAN | Third Party Impacts | 865826 | 1 | 277.8333 | 277.8333 | 0.00016975 | 6.1099e-05
2012-08-20 | ZN12570:PA15 | SHORT RURAL | Equipment Failure | 865829 | 777 | 79 | 47912 | 0.029274 | 0.047474
2012-08-20 | ZN12570:PA5 | URBAN | Equipment Failure | 865829 | 1 | 79 | 60 | 3.6659e-05 | 6.1099e-05
2012-08-20 | ZN10996:PA8 | URBAN | Other | 865879 | 1 | 419.9667 | 419.9667 | 0.00025659 | 6.1099e-05
2012-08-20 | ZN9700:PA23 | URBAN | Equipment Failure | 865916 | 1 | 983.2 | 983.2 | 0.00060072 | 6.1099e-05
2012-08-20 | 504:48028 | URBAN | Other | 865928 | 1 | 101.6167 | 101.6167 | 6.2086e-05 | 6.1099e-05
2012-08-20 | ZN9252:PA4 | URBAN | Vegetation | 865944 | 1 | 183.7667 | 183.7667 | 0.00011228 | 6.1099e-05
2012-08-21 | 217:33612 | URBAN | Equipment Failure | 865970 | 1854 | 568 | 114336 | 0.069858 | 0.11328
2012-08-21 | ZN12570:PA11 | URBAN | Other | 865971 | 1 | 187.1 | 187.1 | 0.00011432 | 6.1099e-05
2012-08-21 | ZN901:PA8 | URBAN | Equipment Failure | 865993 | 102 | 606.2 | 61832.4 | 0.037779 | 0.0062321
2012-08-21 | ZN7900:PA12 | URBAN | Other | 866005 | 78 | 189 | 14732.2667 | 0.0090012 | 0.0047657
2012-08-21 | ZN2466:PA5 | URBAN | Animals | 866024 | 77 | 54 | 4158 | 0.0025405 | 0.0047046
2012-08-21 | 218:7476 | URBAN | Other | 866148 | 1 | 103.6333 | 103.6333 | 6.3319e-05 | 6.1099e-05
2012-08-21 | 232:11455 | URBAN | Other | 866163 | 1 | 390.6833 | 390.6833 | 0.0002387 | 6.1099e-05
2012-08-21 | ZN10995:PA6 | URBAN | Other | 866192 | 1 | 256.6 | 256.6 | 0.00015678 | 6.1099e-05
2012-08-21 | 229:34983 | SHORT RURAL | Third Party Impacts | 866257 | 1 | 50 | 50 | 3.0549e-05 | 6.1099e-05
2012-08-21 | 256:80653 | URBAN | Other | 866265 | 1 | 77.4833 | 77.4833 | 4.7341e-05 | 6.1099e-05
2012-08-21 | ZN12660:PA14 | SHORT RURAL | Other | 866269 | 1 | 227.6833 | 227.6833 | 0.00013911 | 6.1099e-05
2012-08-21 | ZN15012:PA2 | URBAN | Vegetation | 866345 | 23 | 20 | 460 | 0.00028105 | 0.0014053
2012-08-21 | 210:8682 | URBAN | Other | 866347 | 1 | 117.1 | 117.1 | 7.1546e-05 | 6.1099e-05
2012-08-21 | 205:12205 | URBAN | Other | 866362 | 1 | 88.3333 | 88.3333 | 5.397e-05 | 6.1099e-05
2012-08-21 | 813:89063 | SHORT RURAL | Other | 866393 | 1 | 117.1833 | 117.1833 | 7.1597e-05 | 6.1099e-05
2012-08-21 | ZN35370:PA10 | SHORT RURAL | Equipment Failure | 866411 | 521 | 76 | 20146 | 0.012309 | 0.031832
2012-08-21 | ZN35370:PA2 | SHORT RURAL | Equipment Failure | 866411 | 370 | 76 | 8510 | 0.0051995 | 0.022606
2012-08-21 | ZN35370:PA4 | URBAN | Equipment Failure | 866411 | 372 | 76 | 25668 | 0.015683 | 0.022729
2012-08-21 | ZN35370:PA8 | SHORT RURAL | Equipment Failure | 866411 | 682 | 76 | 49723 | 0.03038 | 0.041669
2012-08-21 | ZN2400:PA18 | SHORT RURAL | Other | 866421 | 1 | 136.2333 | 136.2333 | 8.3237e-05 | 6.1099e-05
2012-08-21 | 813:89061 | LONG RURAL | Other | 866440 | 2 | 31 | 62 | 3.7881e-05 | 0.0001222
2012-08-21 | ZN4545:PA36 | URBAN | Other | 866477 | 1 | 67.5 | 67.5 | 4.1242e-05 | 6.1099e-05
2012-08-21 | 525:34586 | SHORT RURAL | Third Party Impacts | 866483 | 3 | 127 | 381 | 0.00023279 | 0.0001833
2012-08-22 | 523:33509 | URBAN | Third Party Impacts | 866493 | 11 | 347 | 3817 | 0.0023321 | 0.00067208
2012-08-22 | ZN9118:PA21 | URBAN | Equipment Failure | 866497 | 26 | 156.7667 | 4075.9333 | 0.0024903 | 0.0015886
2012-08-22 | 256:80653 | URBAN | Other | 866522 | 1 | 150.5833 | 150.5833 | 9.2004e-05 | 6.1099e-05
2012-08-22 | ZN15014:PA18 | URBAN | Other | 866526 | 1 | 353.85 | 353.85 | 0.0002162 | 6.1099e-05
2012-08-22 | ZN15001:PA3 | URBAN | Equipment Failure | 866635 | 1 | 1275.1333 | 1275.1333 | 0.00077909 | 6.1099e-05
2012-08-22 | 218:7481 | URBAN | Vegetation | 866723 | 1 | 273.4167 | 273.4167 | 0.00016705 | 6.1099e-05
2012-08-10 | ZN15011:PA8 | URBAN | Equipment Failure | 866744 | 90 | 38 | 3420 | 0.0020896 | 0.0054989
2012-08-10 | ZN15011:PA8 | URBAN | Other | 866750 | 323 | 38 | 12274 | 0.0074992 | 0.019735
2012-08-10 | ZN15012:PA8 | URBAN | Other | 866750 | 208 | 38 | 7904 | 0.0048292 | 0.012709
2012-08-17 | ZN1673:PA11 | URBAN | Vegetation | 866829 | 45 | 167 | 7515 | 0.0045916 | 0.0027494
2012-08-22 | ZN14891:PA21 | SHORT RURAL | Equipment Failure | 866859 | 1 | 61 | 61 | 3.727e-05 | 6.1099e-05
2012-08-22 | ZN14892:PA1 | SHORT RURAL | Equipment Failure | 866859 | 904 | 61 | 50617 | 0.030926 | 0.055233
2012-08-22 | 511:29878 | SHORT RURAL | Third Party Impacts | 866875 | 6 | 188 | 1128 | 0.00068919 | 0.00036659
2012-08-22 | 520:48172 | SHORT RURAL | Other | 866910 | 4 | 170 | 680 | 0.00041547 | 0.00024439
2012-08-22 | 243:80081 | URBAN | Equipment Failure | 866934 | 18 | 66 | 1188 | 0.00072585 | 0.0010998
2012-08-22 | 229:34995 | SHORT RURAL | Other | 866938 | 18 | 75.4167 | 1357.5 | 0.00082941 | 0.0010998
2012-08-23 | ZN12610:PA11 | URBAN | Other | 866947 | 1 | 227.4833 | 227.4833 | 0.00013899 | 6.1099e-05
2012-08-23 | ZN2196:PA6 | URBAN | Third Party Impacts | 866959 | 12 | 76 | 867 | 0.00052973 | 0.00073318
2012-08-11 | ZN12570:PA16 | SHORT RURAL | Vegetation | 866962 | 699 | 15 | 10485 | 0.0064062 | 0.042708
2012-08-23 | ZN1287:PA24 | URBAN | Vegetation | 866996 | 39 | 38.3833 | 1496.95 | 0.00091462 | 0.0023828
2012-08-23 | 803:74013 | SHORT RURAL | Other | 867043 | 1 | 297.35 | 297.35 | 0.00018168 | 6.1099e-05
2012-08-21 | ZN7900:PA12 | URBAN | Other | 867096 | 53 | 85 | 4505 | 0.0027525 | 0.0032382
2012-08-20 | ZN8100:PA2 | URBAN | Third Party Impacts | 867143 | 3 | 64 | 192 | 0.00011731 | 0.0001833
2012-08-23 | 218:7482 | URBAN | Other | 867168 | 1 | 728.5 | 728.5 | 0.0004451 | 6.1099e-05
2012-08-23 | ZN2400:PA18 | SHORT RURAL | Other | 867180 | 106 | 100 | 10600 | 0.0064765 | 0.0064765
2012-08-23 | ZN12630:PA2 | SHORT RURAL | Vegetation | 867199 | 192 | 540 | 32166 | 0.019653 | 0.011731
2012-08-23 | 513:48056 | SHORT RURAL | Equipment Failure | 867200 | 252 | 185 | 10450 | 0.0063848 | 0.015397
2012-08-23 | 513:48059 | SHORT RURAL | Other | 867203 | 1 | 61.0667 | 61.0667 | 3.7311e-05 | 6.1099e-05
2012-08-18 | ZN187:PA14 | URBAN | Equipment Failure | 867207 | 95 | 68 | 6460 | 0.003947 | 0.0058044
2012-08-18 | ZN187:PA7 | URBAN | Equipment Failure | 867207 | 1304 | 68 | 75076 | 0.04587 | 0.079673
2012-08-23 | 811:74234 | SHORT RURAL | Other | 867208 | 5 | 150 | 750 | 0.00045824 | 0.00030549
2012-08-23 | ZN1673:PA18 | URBAN | Other | 867221 | 1131 | 172 | 172848 | 0.10561 | 0.069103
2012-08-23 | ZN1673:PA11 | URBAN | Vegetation | 867229 | 1609 | 229 | 326493 | 0.19948 | 0.098308
2012-08-23 | ZN1193:PA1 | URBAN | Other | 867232 | 602 | 66 | 39732 | 0.024276 | 0.036781
2012-08-23 | 807:74184 | SHORT RURAL | Other | 867234 | 4 | 26 | 104 | 6.3543e-05 | 0.00024439
2012-08-23 | ZN1193:PA6 | URBAN | Other | 867235 | 43 | 550.4 | 23667.2 | 0.01446 | 0.0026272
2012-08-23 | ZN14143:PA10 | SHORT RURAL | Vegetation | 867236 | 311 | 694 | 40014 | 0.024448 | 0.019002
2012-08-23 | ZN1287:PA22 | URBAN | Other | 867238 | 99 | 241 | 23859 | 0.014578 | 0.0060488
2012-08-23 | ZN195:PA28 | URBAN | Other | 867240 | 1 | 630.3167 | 630.3167 | 0.00038511 | 6.1099e-05
2012-08-23 | ZN9252:PA2 | URBAN | Vegetation | 867243 | 1707 | 66 | 112662 | 0.068835 | 0.1043
2012-08-23 | ZN1673:PA7 | URBAN | Other | 867248 | 2 | 1598.6167 | 3135.2833 | 0.0019156 | 0.0001222
2012-08-23 | ZN965:PA22 | URBAN | Equipment Failure | 867249 | 44 | 483 | 21252 | 0.012985 | 0.0026883
2012-08-23 | ZN15010:PA9 | SHORT RURAL | Vegetation | 867260 | 1 | 111 | 111 | 6.7819e-05 | 6.1099e-05
2012-08-23 | ZN3472:PA27 | URBAN | Other | 867262 | 1 | 170.55 | 170.55 | 0.0001042 | 6.1099e-05
2012-08-23 | ZN1788:PA32 | URBAN | Other | 867265 | 1 | 109.85 | 109.85 | 6.7117e-05 | 6.1099e-05
2012-08-23 | ZN9118:PA7 | URBAN | Vegetation | 867277 | 54 | 319.4167 | 17248.5 | 0.010539 | 0.0032993
2012-08-23 | ZN1164:PA26 | URBAN | Weather | 867279 | 1 | 165.3167 | 165.3167 | 0.00010101 | 6.1099e-05
2012-08-23 | ZN10994:PA11 | URBAN | Vegetation | 867280 | 1 | 521.8167 | 521.8167 | 0.00031882 | 6.1099e-05
2012-08-24 | ZN2400:PA18 | SHORT RURAL | Vegetation | 867281 | 13 | 1308 | 17004 | 0.010389 | 0.00079428
2012-08-23 | ZN10994:PA21 | URBAN | Vegetation | 867286 | 1051 | 92 | 96692 | 0.059077 | 0.064215
2012-08-23 | ZN2635:PA17 | URBAN | Vegetation | 867289 | 128 | 710 | 9728 | 0.0059437 | 0.0078206
2012-08-23 | ZN2635:PA21 | URBAN | Vegetation | 867289 | 1323 | 710 | 150352 | 0.091863 | 0.080833
2012-08-23 | ZN2635:PA4 | URBAN | Vegetation | 867289 | 1 | 710 | 74 | 4.5213e-05 | 6.1099e-05
2012-08-23 | ZN965:PA43 | URBAN | Vegetation | 867291 | 1 | 1291.4667 | 1291.4667 | 0.00078907 | 6.1099e-05
2012-08-23 | ZN10994:PA11 | URBAN | Vegetation | 867292 | 1 | 506.2667 | 506.2667 | 0.00030932 | 6.1099e-05
2012-08-23 | ZN965:PA22 | URBAN | Vegetation | 867294 | 41 | 502 | 20582 | 0.012575 | 0.002505
2012-08-23 | ZN35370:PA8 | SHORT RURAL | Vegetation | 867298 | 237 | 1558 | 37319 | 0.022801 | 0.01448
2012-08-23 | ZN398:PA3 | URBAN | Vegetation | 867300 | 1 | 341.2 | 341.2 | 0.00020847 | 6.1099e-05
2012-08-23 | ZN4545:PA27 | URBAN | Other | 867309 | 79 | 479.8 | 37904.2 | 0.023159 | 0.0048268
2012-08-23 | ZN1287:PA24 | URBAN | Third Party Impacts | 867313 | 3 | 255 | 765 | 0.0004674 | 0.0001833
2012-08-23 | ZN1673:PA2 | URBAN | Vegetation | 867326 | 44 | 280 | 12320 | 0.0075274 | 0.0026883
2012-08-23 | ZN195:PA30 | URBAN | Vegetation | 867332 | 745 | 475 | 353875 | 0.21621 | 0.045518
2012-08-23 | ZN9245:PA13 | URBAN | Vegetation | 867333 | 1 | 87.4 | 87.4 | 5.34e-05 | 6.1099e-05
2012-08-23 | ZN3154:PA17 | URBAN | Vegetation | 867340 | 95 | 213 | 20235 | 0.012363 | 0.0058044
2012-08-23 | ZN3154:PA23 | URBAN | Vegetation | 867340 | 246 | 213 | 16482 | 0.01007 | 0.01503
2012-08-23 | ZN188:PA44 | URBAN | Vegetation | 867349 | 1 | 241.9667 | 241.9667 | 0.00014784 | 6.1099e-05
2012-08-23 | ZN35800:PA7 | URBAN | Other | 867352 | 97 | 102 | 9894 | 0.0060451 | 0.0059266
2012-08-23 | ZN874:PA25 | URBAN | Other | 867355 | 23 | 230.55 | 5302.65 | 0.0032398 | 0.0014053
2012-08-23 | ZN847:PA44 | URBAN | Other | 867358 | 1 | 1543.7833 | 1543.7833 | 0.00094323 | 6.1099e-05
2012-08-23 | ZN1164:PA11 | URBAN | Other | 867360 | 1 | 29.7667 | 29.7667 | 1.8187e-05 | 6.1099e-05
2012-08-23 | ZN5868:PA13 | URBAN | Other | 867368 | 1 | 131.4667 | 131.4667 | 8.0324e-05 | 6.1099e-05
2012-08-23 | ZN2400:PA15 | URBAN | Vegetation | 867369 | 1 | 87 | 87 | 5.3156e-05 | 6.1099e-05
2012-08-23 | ZN965:PA2 | URBAN | Vegetation | 867370 | 32 | 1483.5167 | 47472.5333 | 0.029005 | 0.0019552
2012-08-23 | ZN3155:PA22 | URBAN | Vegetation | 867371 | 27 | 131.2833 | 3544.65 | 0.0021657 | 0.0016497
2012-08-23 | ZN10994:PA11 | URBAN | Vegetation | 867373 | 1 | 17.4 | 17.4 | 1.0631e-05 | 6.1099e-05
2012-08-23 | ZN35500:PA27 | URBAN | Vegetation | 867378 | 1 | 295.1833 | 295.1833 | 0.00018035 | 6.1099e-05
2012-08-23 | ZN3425:PA28 | URBAN | Other | 867382 | 1 | 1434.1833 | 1434.1833 | 0.00087627 | 6.1099e-05
2012-08-23 | ZN9550:PA42 | URBAN | Vegetation | 867384 | 1 | 452.6 | 452.6 | 0.00027653 | 6.1099e-05
2012-08-23 | ZN1287:PA12 | URBAN | Other | 867389 | 1 | 262.3667 | 262.3667 | 0.0001603 | 6.1099e-05
2012-08-23 | ZN2310:PA25 | URBAN | Vegetation | 867394 | 1 | 217.5 | 217.5 | 0.00013289 | 6.1099e-05
2012-08-23 | ZN874:PA22 | URBAN | Other | 867399 | 45 | 185.5167 | 8348.25 | 0.0051007 | 0.0027494
2012-08-23 | 234:2001 | URBAN | Equipment Failure | 867400 | 7 | 560.4833 | 3923.3833 | 0.0023971 | 0.00042769
2012-08-23 | ZN1285:PA33 | URBAN | Equipment Failure | 867405 | 1 | 260 | 260 | 0.00015886 | 6.1099e-05
2012-08-23 | ZN10995:PA2 | URBAN | Vegetation | 867419 | 2319 | 176 | 309323 | 0.18899 | 0.14169
2012-08-23 | 512:48047 | SHORT RURAL | Equipment Failure | 867429 | 1 | 135.6167 | 135.6167 | 8.286e-05 | 6.1099e-05
2012-08-23 | ZN10993:PA2 | URBAN | Vegetation | 867430 | 1 | 146 | 146 | 8.9204e-05 | 6.1099e-05
2012-08-23 | ZN10993:PA5 | URBAN | Vegetation | 867430 | 75 | 146 | 10888.75 | 0.0066529 | 0.0045824
2012-08-23 | ZN2635:PA1 | URBAN | Equipment Failure | 867435 | 62 | 132 | 8184 | 0.0050003 | 0.0037881
2012-08-23 | ZN965:PA22 | URBAN | Vegetation | 867437 | 83 | 314 | 26062 | 0.015924 | 0.0050712
2012-08-23 | 264:81244 | URBAN | Vegetation | 867442 | 1 | 1454.0167 | 1454.0167 | 0.00088838 | 6.1099e-05
2012-08-23 | ZN2310:PA25 | URBAN | Vegetation | 867443 | 1 | 332.8667 | 332.8667 | 0.00020338 | 6.1099e-05
2012-08-23 | ZN195:PA28 | URBAN | Other | 867466 | 1 | 579.2167 | 579.2167 | 0.00035389 | 6.1099e-05
2012-08-23 | ZN15013:PA6 | SHORT RURAL | Equipment Failure | 867469 | 1 | 68.6333 | 68.6333 | 4.1934e-05 | 6.1099e-05
2012-08-23 | ZN10999:PA17 | URBAN | Vegetation | 867472 | 1 | 145.9667 | 145.9667 | 8.9184e-05 | 6.1099e-05
2012-08-23 | ZN965:PA47 | URBAN | Vegetation | 867481 | 17 | 520.2833 | 8844.8167 | 0.0054041 | 0.0010387
2012-08-23 | ZN847:PA15 | URBAN | Vegetation | 867487 | 1234 | 314 | 282628 | 0.17268 | 0.075396
2012-08-23 | ZN2400:PA22 | URBAN | Vegetation | 867493 | 1 | 1293.2333 | 1293.2333 | 0.00079015 | 6.1099e-05
2012-08-23 | ZN2466:PA16 | URBAN | Other | 867497 | 58 | 103 | 5974 | 0.00365 | 0.0035437
2012-08-23 | ZN15006:PA15 | URBAN | Vegetation | 867499 | 1 | 152.05 | 152.05 | 9.29e-05 | 6.1099e-05
2012-08-23 | ZN398:PA20 | URBAN | Third Party Impacts | 867504 | 1 | 194.7833 | 194.7833 | 0.00011901 | 6.1099e-05
2012-08-23 | ZN262:PA5 | URBAN | Other | 867505 | 59 | 300.5833 | 17734.4167 | 0.010835 | 0.0036048
2012-08-23 | ZN1287:PA6 | URBAN | Other | 867508 | 57 | 160.6833 | 9158.95 | 0.005596 | 0.0034826
2012-08-23 | ZN195:PA11 | URBAN | Other | 867509 | 70 | 654.7 | 45829 | 0.028001 | 0.0042769
2012-08-23 | ZN1193:PA10 | URBAN | Vegetation | 867510 | 29 | 535.5333 | 15530.4667 | 0.0094889 | 0.0017719
2012-08-23 | ZN10996:PA8 | URBAN | Third Party Impacts | 867520 | 1 | 79.7667 | 79.7667 | 4.8736e-05 | 6.1099e-05
2012-08-23 | ZN80:PA25 | URBAN | Equipment Failure | 867523 | 100 | 561 | 56100 | 0.034276 | 0.0061099
2012-08-23 | ZN36300:PA11 | URBAN | Vegetation | 867530 | 1 | 443.6167 | 443.6167 | 0.00027104 | 6.1099e-05
2012-08-23 | ZN80:PA25 | URBAN | Other | 867547 | 43 | 595.9 | 25623.7 | 0.015656 | 0.0026272
2012-08-23 | ZN2400:PA18 | SHORT RURAL | Vegetation | 867549 | 1 | 2774.1333 | 2774.1333 | 0.001695 | 6.1099e-05
2012-08-23 | ZN9037:PA8 | URBAN | Weather | 867552 | 1 | 60.9833 | 60.9833 | 3.726e-05 | 6.1099e-05
2012-08-23 | 509:48039 | LONG RURAL | Equipment Failure | 867575 | 1 | 157.25 | 157.25 | 9.6078e-05 | 6.1099e-05
2012-08-23 | ZN2310:PA20 | URBAN | Vegetation | 867585 | 2 | 228.0333 | 456.0667 | 0.00027865 | 0.0001222
2012-08-23 | 243:80075 | SHORT RURAL | Vegetation | 867589 | 143 | 226 | 20668 | 0.012628 | 0.0087371
2012-08-23 | ZN10995:PA13 | URBAN | Vegetation | 867597 | 1 | 177.05 | 177.05 | 0.00010818 | 6.1099e-05
2012-08-23 | ZN3922:PA7 | URBAN | Other | 867605 | 23 | 207.7833 | 4779.0167 | 0.0029199 | 0.0014053
2012-08-23 | 501:48115 | SHORT RURAL | Equipment Failure | 867610 | 1 | 217.5167 | 217.5167 | 0.0001329 | 6.1099e-05
2012-08-23 | ZN1193:PA10 | URBAN | Other | 867613 | 1 | 171.4667 | 171.4667 | 0.00010476 | 6.1099e-05
2012-08-23 | 807:74184 | SHORT RURAL | Other | 867618 | 1 | 119.3667 | 119.3667 | 7.2931e-05 | 6.1099e-05
2012-08-23 | ZN129:PA28 | URBAN | Other | 867619 | 2 | 2630.2667 | 5260.5333 | 0.0032141 | 0.0001222
2012-08-23 | ZN15010:PA7 | URBAN | Vegetation | 867621 | 1 | 30 | 30 | 1.833e-05 | 6.1099e-05
2012-08-23 | ZN15010:PA9 | SHORT RURAL | Vegetation | 867621 | 46 | 30 | 1380 | 0.00084316 | 0.0028105
2012-08-23 | ZN1164:PA11 | URBAN | Other | 867622 | 1 | 51.8833 | 51.8833 | 3.17e-05 | 6.1099e-05
2012-08-23 | ZN2635:PA1 | URBAN | Vegetation | 867623 | 1 | 351.7333 | 351.7333 | 0.0002149 | 6.1099e-05
2012-08-23 | ZN1285:PA24 | URBAN | Other | 867631 | 1 | 318.6333 | 318.6333 | 0.00019468 | 6.1099e-05
2012-08-23 | ZN965:PA33 | URBAN | Vegetation | 867633 | 59 | 72 | 4205.7167 | 0.0025696 | 0.0036048
2012-08-23 | ZN965:PA43 | URBAN | Vegetation | 867633 | 1 | 72 | 72 | 4.3991e-05 | 6.1099e-05
2012-08-23 | ZN1164:PA13 | URBAN | Other | 867638 | 101 | 188.25 | 19013.25 | 0.011617 | 0.006171
2012-08-23 | ZN180:PA30 | URBAN | Vegetation | 867653 | 35 | 57.25 | 2003.75 | 0.0012243 | 0.0021385
2012-08-23 | ZN3155:PA34 | SHORT RURAL | Vegetation | 867668 | 1 | 247.35 | 247.35 | 0.00015113 | 6.1099e-05
2012-08-23 | ZN12630:PA1 | SHORT RURAL | Vegetation | 867671 | 233 | 317 | 25497 | 0.015578 | 0.014236
2012-08-23 | ZN12600:PA13 | SHORT RURAL | Third Party Impacts | 867680 | 1 | 154.7833 | 154.7833 | 9.457e-05 | 6.1099e-05
2012-08-23 | ZN3154:PA10 | URBAN | Other | 867683 | 1 | 513.2667 | 513.2667 | 0.0003136 | 6.1099e-05
2012-08-23 | ZN15005:PA12 | URBAN | Equipment Failure | 867693 | 1 | 20.3167 | 20.3167 | 1.2413e-05 | 6.1099e-05
2012-08-23 | 238:34147 | URBAN | Other | 867697 | 1 | 338.55 | 338.55 | 0.00020685 | 6.1099e-05
2012-08-23 | ZN15005:PA6 | URBAN | Vegetation | 867708 | 1 | 67.7167 | 67.7167 | 4.1374e-05 | 6.1099e-05
2012-08-23 | ZN15004:PA3 | URBAN | Vegetation | 867711 | 1 | 238.8167 | 238.8167 | 0.00014591 | 6.1099e-05
2012-08-23 | ZN874:PA25 | URBAN | Other | 867716 | 1 | 171.9 | 171.9 | 0.00010503 | 6.1099e-05
2012-08-23 | ZN3155:PA19 | URBAN | Other | 867722 | 1 | 224.9333 | 224.9333 | 0.00013743 | 6.1099e-05
2012-08-23 | ZN2635:PA16 | URBAN | Vegetation | 867728 | 1 | 1121.2333 | 1121.2333 | 0.00068506 | 6.1099e-05
2012-08-23 | ZN1287:PA15 | URBAN | Other | 867752 | 43 | 103.3833 | 4445.4833 | 0.0027161 | 0.0026272
2012-08-23 | ZN15001:PA18 | URBAN | Vegetation | 867758 | 1 | 295.1667 | 295.1667 | 0.00018034 | 6.1099e-05
2012-08-23 | ZN15005:PA12 | URBAN | Weather | 867761 | 40 | 154.3167 | 6172.6667 | 0.0037714 | 0.0024439
2012-08-23 | ZN2310:PA27 | URBAN | Vegetation | 867763 | 1 | 293.35 | 293.35 | 0.00017923 | 6.1099e-05
2012-08-23 | ZN15006:PA8 | URBAN | Vegetation | 867765 | 1 | 82.2 | 82.2 | 5.0223e-05 | 6.1099e-05
2012-08-23 | ZN690:PA4 | URBAN | Other | 867766 | 1 | 147.7 | 147.7 | 9.0243e-05 | 6.1099e-05
2012-08-23 | ZN12690:PA16 | SHORT RURAL | Vegetation | 867767 | 1 | 350.65 | 350.65 | 0.00021424 | 6.1099e-05
2012-08-23 | ZN965:PA2 | URBAN | Vegetation | 867789 | 1 | 1237.1833 | 1237.1833 | 0.0007559 | 6.1099e-05
2012-08-23 | ZN12690:PA24 | SHORT RURAL | Vegetation | 867790 | 1 | 338.45 | 338.45 | 0.00020679 | 6.1099e-05
2012-08-23 | ZN1287:PA12 | URBAN | Other | 867808 | 1 | 91.4333 | 91.4333 | 5.5865e-05 | 6.1099e-05
2012-08-23 | ZN1673:PA13 | URBAN | Other | 867814 | 1 | 102.75 | 102.75 | 6.2779e-05 | 6.1099e-05
2012-08-23 | ZN1193:PA16 | URBAN | Other | 867830 | 37 | 370.7167 | 13716.5167 | 0.0083806 | 0.0022606
2012-08-23 | ZN1287:PA23 | URBAN | Other | 867832 | 1 | 280.5667 | 280.5667 | 0.00017142 | 6.1099e-05
2012-08-23 | 243:80083 | SHORT RURAL | Vegetation | 867836 | 15 | 18 | 270 | 0.00016497 | 0.00091648
2012-08-23 | ZN10994:PA21 | URBAN | Vegetation | 867839 | 1 | 9.2167 | 9.2167 | 5.6313e-06 | 6.1099e-05
2012-08-23 | ZN15008:PA7 | URBAN | Equipment Failure | 867840 | 1 | 306.5167 | 306.5167 | 0.00018728 | 6.1099e-05
2012-08-23 | ZN12690:PA24 | SHORT RURAL | Vegetation | 867847 | 1 | 363.7833 | 363.7833 | 0.00022227 | 6.1099e-05
2012-08-23 | ZN15008:PA9 | URBAN | Equipment Failure | 867864 | 1 | 174.9667 | 174.9667 | 0.0001069 | 6.1099e-05
2012-08-23 | ZN2635:PA19 | URBAN | Other | 867870 | 54 | 1191.4167 | 64336.5 | 0.039309 | 0.0032993
2012-08-23 | ZN3472:PA28 | URBAN | Other | 867875 | 1 | 110.2833 | 110.2833 | 6.7382e-05 | 6.1099e-05
2012-08-23 | ZN3922:PA22 | URBAN | Other | 867880 | 1 | 198.5333 | 198.5333 | 0.0001213 | 6.1099e-05
2012-08-23 | ZN690:PA33 | URBAN | Equipment Failure | 867881 | 1 | 1218.1333 | 1218.1333 | 0.00074426 | 6.1099e-05
2012-08-23 | ZN1287:PA23 | URBAN | Other | 867888 | 1 | 251.5833 | 251.5833 | 0.00015371 | 6.1099e-05
2012-08-23 | ZN2400:PA21 | URBAN | Other | 867892 | 1 | 1352.5 | 1352.5 | 0.00082636 | 6.1099e-05
2012-08-23 | ZN15008:PA7 | URBAN | Other | 867893 | 1 | 335.55 | 335.55 | 0.00020502 | 6.1099e-05
2012-08-23 | ZN711:PA21 | URBAN | Other | 867902 | 1 | 273.2 | 273.2 | 0.00016692 | 6.1099e-05
2012-08-23 | ZN80:PA39 | URBAN | Other | 867911 | 1 | 1223.3667 | 1223.3667 | 0.00074746 | 6.1099e-05
2012-08-23 | 810:74058 | SHORT RURAL | Equipment Failure | 867919 | 64 | 323 | 12004 | 0.0073343 | 0.0039103
2012-08-23 | 513:48059 | SHORT RURAL | Other | 867929 | 5 | 135 | 675 | 0.00041242 | 0.00030549
2012-08-23 | 243:80081 | URBAN | Other | 867931 | 13 | 199 | 2587 | 0.0015806 | 0.00079428
2012-08-23 | ZN3425:PA33 | URBAN | Weather | 867932 | 1 | 1207.3667 | 1207.3667 | 0.00073768 | 6.1099e-05
2012-08-23 | ZN398:PA24 | URBAN | Other | 867945 | 1 | 927.4167 | 927.4167 | 0.00056664 | 6.1099e-05
2012-08-23 | 515:35197 | LONG RURAL | Other | 867946 | 10 | 202 | 2020 | 0.0012342 | 0.00061099
2012-08-23 | ZN847:PA10 | URBAN | Vegetation | 867955 | 46 | 133.95 | 6161.7 | 0.0037647 | 0.0028105
2012-08-23 | 515:35197 | LONG RURAL | Other | 867958 | 7 | 158.55 | 1109.85 | 0.0006781 | 0.00042769
2012-08-23 | 524:33576 | SHORT RURAL | Other | 867959 | 47 | 286 | 13442 | 0.0082129 | 0.0028716
2012-08-23 | ZN12570:PA2 | SHORT RURAL | Other | 867960 | 769 | 123 | 80258 | 0.049037 | 0.046985
2012-08-23 | 221:11900 | URBAN | Other | 867962 | 1 | 310.1167 | 310.1167 | 0.00018948 | 6.1099e-05
2012-08-23 | ZN1673:PA13 | URBAN | Other | 867971 | 1 | 1230.45 | 1230.45 | 0.00075179 | 6.1099e-05
2012-08-23 | ZN965:PA11 | URBAN | Vegetation | 867978 | 1 | 1076.3 | 1076.3 | 0.0006576 | 6.1099e-05
2012-08-23 | 513:48059 | SHORT RURAL | Other | 867981 | 10 | 143.4 | 1434 | 0.00087615 | 0.00061099
2012-08-23 | 227:13015 | SHORT RURAL | Vegetation | 867989 | 58 | 158 | 9164 | 0.0055991 | 0.0035437
2012-08-23 | ZN1673:PA11 | URBAN | Other | 868003 | 36 | 349.9 | 12596.4 | 0.0076962 | 0.0021996
2012-08-23 | ZN340:PA19 | SHORT RURAL | Other | 868017 | 1 | 452.9333 | 452.9333 | 0.00027674 | 6.1099e-05
2012-08-23 | ZN12580:PA12 | SHORT RURAL | Other | 868021 | 1 | 832.7667 | 832.7667 | 0.00050881 | 6.1099e-05
2012-08-23 | ZN36300:PA11 | URBAN | Other | 868033 | 1 | 99.8667 | 99.8667 | 6.1017e-05 | 6.1099e-05
2012-08-23 | ZN2473:PA4 | URBAN | Vegetation | 868048 | 65 | 45.5833 | 2962.9167 | 0.0018103 | 0.0039714
2012-08-23 | 256:80652 | URBAN | Other | 868050 | 1 | 88.7333 | 88.7333 | 5.4215e-05 | 6.1099e-05
2012-08-23 | ZN2635:PA21 | URBAN | Equipment Failure | 868051 | 89 | 347.4333 | 30921.5667 | 0.018893 | 0.0054378
2012-08-23 | ZN690:PA33 | URBAN | Vegetation | 868052 | 1 | 96.55 | 96.55 | 5.8991e-05 | 6.1099e-05
2012-08-23 | ZN847:PA15 | URBAN | Vegetation | 868056 | 37 | 1137.0167 | 42069.6167 | 0.025704 | 0.0022606
2012-08-23 | 801:74121 | SHORT RURAL | Other | 868057 | 1 | 40.1167 | 40.1167 | 2.4511e-05 | 6.1099e-05
2012-08-23 | ZN9118:PA13 | URBAN | Vegetation | 868061 | 1 | 887.1333 | 887.1333 | 0.00054203 | 6.1099e-05
2012-08-23 | ZN2602:PA42 | URBAN | Other | 868069 | 1 | 329.4833 | 329.4833 | 0.00020131 | 6.1099e-05
2012-08-23 | 258:80775 | URBAN | Other | 868071 | 1 | 46.8833 | 46.8833 | 2.8645e-05 | 6.1099e-05
2012-08-24 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 868095 | 44 | 575 | 25300 | 0.015458 | 0.0026883
2012-08-24 | ZN14891:PA12 | SHORT RURAL | Vegetation | 868096 | 373 | 79 | 29467 | 0.018004 | 0.02279
2012-08-24 | ZN1673:PA11 | URBAN | Equipment Failure | 868102 | 35 | 377 | 3080 | 0.0018818 | 0.0021385
2012-08-24 | ZN195:PA11 | URBAN | Equipment Failure | 868102 | 1223 | 377 | 98746 | 0.060332 | 0.074724
2012-08-24 | ZN14891:PA20 | SHORT RURAL | Equipment Failure | 868111 | 8 | 172 | 1376 | 0.00084072 | 0.00048879
2012-08-24 | ZN1287:PA23 | URBAN | Other | 868121 | 1 | 107.6667 | 107.6667 | 6.5783e-05 | 6.1099e-05
2012-08-24 | 243:80080 | SHORT RURAL | Vegetation | 868132 | 1 | 109.0833 | 109.0833 | 6.6648e-05 | 6.1099e-05
2012-08-23 | ZN1673:PA7 | URBAN | Other | 868135 | 1 | 1437.4833 | 1437.4833 | 0.00087828 | 6.1099e-05
2012-08-24 | ZN2196:PA20 | URBAN | Other | 868164 | 1 | 324.1333 | 324.1333 | 0.00019804 | 6.1099e-05
2012-08-24 | 801:74123 | SHORT RURAL | Other | 868182 | 2 | 55 | 110 | 6.7208e-05 | 0.0001222
2012-08-24 | ZN12580:PA16 | URBAN | Equipment Failure | 868198 | 1 | 421.4 | 421.4 | 0.00025747 | 6.1099e-05
2012-08-24 | 208:58 | URBAN | Other | 868209 | 1 | 150.8 | 150.8 | 9.2137e-05 | 6.1099e-05
2012-08-24 | ZN14892:PA1 | SHORT RURAL | Equipment Failure | 868233 | 1 | 324.0333 | 324.0333 | 0.00019798 | 6.1099e-05
2012-08-24 | ZN15009:PA11 | URBAN | Other | 868250 | 1 | 98.8167 | 98.8167 | 6.0376e-05 | 6.1099e-05
2012-08-24 | ZN9118:PA13 | URBAN | Vegetation | 868253 | 1 | 19.7667 | 19.7667 | 1.2077e-05 | 6.1099e-05
2012-08-24 | ZN9118:PA13 | URBAN | Vegetation | 868260 | 1 | 6.3167 | 6.3167 | 3.8594e-06 | 6.1099e-05
2012-08-24 | ZN2602:PA31 | URBAN | Vegetation | 868281 | 1 | 166.7 | 166.7 | 0.00010185 | 6.1099e-05
2012-08-24 | 202:34245 | URBAN | Vegetation | 868282 | 1 | 135.7167 | 135.7167 | 8.2921e-05 | 6.1099e-05
2012-08-24 | 810:74058 | SHORT RURAL | Equipment Failure | 868305 | 20 | 77.1 | 1542 | 0.00094214 | 0.001222
2012-08-24 | ZN690:PA4 | URBAN | Third Party Impacts | 868332 | 41 | 67 | 2709.6667 | 0.0016556 | 0.002505
2012-08-23 | 513:48059 | SHORT RURAL | Other | 868341 | 2 | 60 | 120 | 7.3318e-05 | 0.0001222
2012-08-24 | ZN4545:PA2 | URBAN | Vegetation | 868343 | 1 | 390.3833 | 390.3833 | 0.00023852 | 6.1099e-05
2012-08-23 | 807:74184 | SHORT RURAL | Other | 868347 | 63 | 62 | 3906 | 0.0023865 | 0.0038492
2012-08-24 | ZN2635:PA16 | URBAN | Vegetation | 868367 | 1 | 670.3833 | 670.3833 | 0.0004096 | 6.1099e-05
2012-08-24 | ZN12650:PA17 | URBAN | Equipment Failure | 868376 | 1 | 252.7167 | 252.7167 | 0.00015441 | 6.1099e-05
2012-08-23 | ZN965:PA22 | URBAN | Vegetation | 868469 | 29 | 314 | 9106 | 0.0055636 | 0.0017719
2012-08-24 | 217:33612 | URBAN | Equipment Failure | 868474 | 1 | 103.4667 | 103.4667 | 6.3217e-05 | 6.1099e-05
2012-08-24 | ZN3425:PA28 | URBAN | Equipment Failure | 868518 | 364 | 786 | 166563 | 0.10177 | 0.02224
2012-08-24 | ZN3425:PA33 | URBAN | Equipment Failure | 868518 | 1 | 786 | 199 | 0.00012159 | 6.1099e-05
2012-08-24 | ZN12630:PA1 | SHORT RURAL | Other | 868553 | 1 | 232.7333 | 232.7333 | 0.0001422 | 6.1099e-05
2012-08-24 | ZN116:PA42 | URBAN | Equipment Failure | 868571 | 1 | 167.65 | 167.65 | 0.00010243 | 6.1099e-05
2012-08-23 | ZN15008:PA7 | URBAN | Other | 868579 | 1 | 353.7833 | 353.7833 | 0.00021616 | 6.1099e-05
2012-08-23 | ZN14891:PA5 | SHORT RURAL | Vegetation | 868595 | 69 | 542 | 21070 | 0.012873 | 0.0042158
2012-08-24 | 229:34995 | SHORT RURAL | Other | 868605 | 1 | 178.0333 | 178.0333 | 0.00010878 | 6.1099e-05
2012-08-24 | 256:80650 | URBAN | Other | 868621 | 1 | 136.0167 | 136.0167 | 8.3104e-05 | 6.1099e-05
2012-08-24 | ZN12580:PA16 | URBAN | Equipment Failure | 868630 | 24 | 65.0667 | 1561.6 | 0.00095412 | 0.0014664
2012-08-24 | 222:2014 | URBAN | Equipment Failure | 868633 | 1175 | 263 | 167328 | 0.10224 | 0.071791
2012-08-24 | ZN12630:PA1 | SHORT RURAL | Vegetation | 868668 | 16 | 83 | 1328 | 0.00081139 | 0.00097758
2012-08-24 | 222:2017 | URBAN | Other | 868700 | 337 | 68 | 22850.45 | 0.013961 | 0.02059
2012-08-24 | ZN1673:PA13 | URBAN | Other | 868708 | 1 | 194.6333 | 194.6333 | 0.00011892 | 6.1099e-05
2012-08-24 | ZN847:PA39 | URBAN | Vegetation | 868725 | 37 | 164 | 5801.1667 | 0.0035444 | 0.0022606
2012-08-24 | 238:34140 | URBAN | Equipment Failure | 868741 | 1 | 961.65 | 545.3833 | 0.00033322 | 6.1099e-05
2012-08-24 | 503:48078 | URBAN | Equipment Failure | 868741 | 41 | 961.65 | 8314.8 | 0.0050802 | 0.002505
2012-08-24 | ZN10999:PA24 | URBAN | Other | 868749 | 1 | 865.6 | 865.6 | 0.00052887 | 6.1099e-05
2012-08-25 | ZN15006:PA9 | URBAN | Equipment Failure | 868761 | 30 | 439.4333 | 13183 | 0.0080546 | 0.001833
2012-08-25 | ZN1673:PA11 | URBAN | Weather | 868789 | 47 | 15 | 705 | 0.00043075 | 0.0028716
2012-08-25 | 807:74184 | SHORT RURAL | Other | 868803 | 1 | 233.1167 | 233.1167 | 0.00014243 | 6.1099e-05
2012-08-25 | ZN1287:PA12 | URBAN | Other | 868807 | 1 | 375.0333 | 375.0333 | 0.00022914 | 6.1099e-05
2012-08-25 | ZN8700:PA61 62GHJ | CBD | Third Party Impacts | 868840 | 34 | 55 | 1870 | 0.0011425 | 0.0020774
2012-08-25 | ZN1673:PA11 | URBAN | Vegetation | 868845 | 1 | 256.95 | 256.95 | 0.00015699 | 6.1099e-05
2012-08-25 | ZN14892:PA3 | SHORT RURAL | Other | 868847 | 1 | 39.45 | 39.45 | 2.4103e-05 | 6.1099e-05
2012-08-25 | 210:8681 | URBAN | Other | 868849 | 1 | 64.3333 | 64.3333 | 3.9307e-05 | 6.1099e-05
2012-08-25 | ZN15014:PA12 | SHORT RURAL | Other | 868855 | 1 | 339.7 | 339.7 | 0.00020755 | 6.1099e-05
2012-08-25 | 232:11455 | URBAN | Equipment Failure | 868874 | 1 | 206.3 | 206.3 | 0.00012605 | 6.1099e-05
2012-08-25 | ZN12620:PA13 | SHORT RURAL | Third Party Impacts | 868919 | 99 | 85 | 8415 | 0.0051414 | 0.0060488
2012-08-25 | ZN12610:PA10 | SHORT RURAL | Equipment Failure | 868927 | 34 | 59 | 2006 | 0.0012256 | 0.0020774
2012-08-26 | 260:33347 | SHORT RURAL | Equipment Failure | 868957 | 101 | 89.8167 | 9071.4833 | 0.0055426 | 0.006171
2012-08-26 | 232:11457 | URBAN | Other | 868967 | 1 | 148.7 | 148.7 | 9.0854e-05 | 6.1099e-05
2012-08-26 | ZN15006:PA8 | URBAN | Equipment Failure | 868983 | 1 | 303.8167 | 303.8167 | 0.00018563 | 6.1099e-05
2012-08-26 | 503:48076 | URBAN | Equipment Failure | 868990 | 1 | 110.5833 | 110.5833 | 6.7565e-05 | 6.1099e-05
2012-08-26 | ZN12620:PA1 | SHORT RURAL | Other | 868993 | 1 | 56.4167 | 56.4167 | 3.447e-05 | 6.1099e-05
2012-08-26 | 514:18137 | SHORT RURAL | Other | 869010 | 8 | 49 | 392 | 0.00023951 | 0.00048879
2012-08-26 | 509:48040 | SHORT RURAL | Equipment Failure | 869018 | 52 | 115.8 | 6021.6 | 0.0036791 | 0.0031771
2012-08-26 | 214:8665 | URBAN | Operational Error | 869028 | 77 | 121.4167 | 9349.0833 | 0.0057122 | 0.0047046
2012-08-26 | 258:80793 | SHORT RURAL | Operational Error | 869028 | 2 | 121.4167 | 242.8333 | 0.00014837 | 0.0001222
2012-08-26 | ZN9118:PA21 | URBAN | Equipment Failure | 869066 | 50 | 236 | 11800 | 0.0072096 | 0.0030549
2012-08-27 | ZN14892:PA8 | URBAN | Other | 869109 | 2 | 83 | 166 | 0.00010142 | 0.0001222
2012-08-25 | 807:74184 | SHORT RURAL | Operational Error | 869185 | 4 | 10 | 40 | 2.4439e-05 | 0.00024439
2012-08-25 | 807:74184 | SHORT RURAL | Equipment Failure | 869190 | 1 | 90 | 90 | 5.4989e-05 | 6.1099e-05
2012-08-23 | ZN9037:PA8 | URBAN | Vegetation | 869195 | 46 | 82 | 3772 | 0.0023046 | 0.0028105
2012-08-27 | ZN35800:PA13 | URBAN | Vegetation | 869205 | 2 | 205.5333 | 411.0667 | 0.00025116 | 0.0001222
2012-08-27 | 511:29878 | SHORT RURAL | Equipment Failure | 869232 | 1 | 63.6333 | 63.6333 | 3.8879e-05 | 6.1099e-05
2012-08-27 | ZN398:PA11 | URBAN | Third Party Impacts | 869291 | 1 | 86.8167 | 86.8167 | 5.3044e-05 | 6.1099e-05
2012-08-27 | 205:12205 | URBAN | Vegetation | 869346 | 1 | 101.6667 | 101.6667 | 6.2117e-05 | 6.1099e-05
2012-08-27 | ZN116:PA35 | URBAN | Other | 869355 | 1 | 340.9333 | 340.9333 | 0.00020831 | 6.1099e-05
2012-08-27 | ZN1164:PA15 | URBAN | Other | 869380 | 1 | 265.1667 | 265.1667 | 0.00016201 | 6.1099e-05
2012-08-27 | 210:8682 | URBAN | Other | 869407 | 1 | 160.6 | 160.6 | 9.8124e-05 | 6.1099e-05
2012-08-27 | 504:48033 | SHORT RURAL | Other | 869451 | 1 | 1273.6333 | 1273.6333 | 0.00077817 | 6.1099e-05
2012-08-27 | ZN15014:PA12 | SHORT RURAL | Vegetation | 869453 | 1 | 219.8667 | 219.8667 | 0.00013434 | 6.1099e-05
2012-08-27 | ZN9245:PA10 | URBAN | Equipment Failure | 869472 | 23 | 201.7167 | 4639.4833 | 0.0028347 | 0.0014053
2012-08-27 | ZN1673:PA11 | URBAN | Vegetation | 869547 | 1 | 357.4833 | 357.4833 | 0.00021842 | 6.1099e-05
2012-08-27 | ZN1673:PA11 | URBAN | Equipment Failure | 869612 | 52 | 57.0833 | 2968.3333 | 0.0018136 | 0.0031771
2012-08-27 | 803:74010 | SHORT RURAL | Equipment Failure | 869630 | 1 | 581.8 | 581.8 | 0.00035547 | 6.1099e-05
2012-08-28 | ZN9118:PA12 | URBAN | Equipment Failure | 869636 | 32 | 94.8167 | 3034.1333 | 0.0018538 | 0.0019552
2012-08-28 | 203:8088 | URBAN | Equipment Failure | 869647 | 57 | 107 | 6099 | 0.0037264 | 0.0034826
2012-08-28 | ZN15008:PA7 | URBAN | Equipment Failure | 869649 | 53 | 274 | 14499.9 | 0.0088592 | 0.0032382
2012-08-28 | ZN10990:PA2 | URBAN | Third Party Impacts | 869881 | 1 | 90.3 | 90.3 | 5.5172e-05 | 6.1099e-05
2012-08-28 | ZN4545:PA27 | URBAN | Other | 869922 | 65 | 52.0667 | 3384.3333 | 0.0020678 | 0.0039714
2012-08-28 | ZN12630:PA5 | SHORT RURAL | Other | 869967 | 1 | 204.1833 | 204.1833 | 0.00012475 | 6.1099e-05
2012-08-28 | ZN12690:PA6 | URBAN | Animals | 870113 | 46 | 70.3333 | 3235.3333 | 0.0019767 | 0.0028105
2012-08-28 | 520:48172 | SHORT RURAL | Equipment Failure | 870127 | 1 | 66.2333 | 66.2333 | 4.0468e-05 | 6.1099e-05
2012-08-28 | ZN2466:PA30 | URBAN | Equipment Failure | 870143 | 19 | 38.3333 | 728.3333 | 0.000445 | 0.0011609
2012-08-28 | ZN9037:PA2 | URBAN | Equipment Failure | 870150 | 934 | 53 | 49502 | 0.030245 | 0.057066
2012-08-28 | ZN9037:PA9 | URBAN | Equipment Failure | 870150 | 23 | 53 | 1219 | 0.00074479 | 0.0014053
2012-08-28 | 205:12205 | URBAN | Animals | 870186 | 1198 | 24 | 28752 | 0.017567 | 0.073196
2012-08-29 | ZN9118:PA12 | URBAN | Other | 870206 | 32 | 216.9167 | 6941.3333 | 0.0042411 | 0.0019552
2012-08-29 | ZN8000:PA25 | URBAN | Third Party Impacts | 870209 | 47 | 305 | 14335 | 0.0087585 | 0.0028716
2012-08-28 | ZN12630:PA3 | SHORT RURAL | Equipment Failure | 870215 | 7 | 826.8 | 5787.6 | 0.0035361 | 0.00042769
2012-08-29 | ZN3288:PA43 44KLM | CBD | Equipment Failure | 870274 | 1 | 1269.1333 | 1269.1333 | 0.00077542 | 6.1099e-05
2012-08-25 | 812:19072 | SHORT RURAL | Equipment Failure | 870310 | 2 | 3125 | 6250 | 0.0038187 | 0.0001222
2012-08-29 | 218:7478 | URBAN | Other | 870445 | 1 | 108.0833 | 108.0833 | 6.6037e-05 | 6.1099e-05
2012-08-29 | ZN12610:PA22 | URBAN | Equipment Failure | 870487 | 1 | 236.5 | 236.5 | 0.0001445 | 6.1099e-05
2012-08-29 | ZN14143:PA17 | SHORT RURAL | Other | 870488 | 1 | 1217.1167 | 1217.1167 | 0.00074364 | 6.1099e-05
2012-08-29 | ZN9245:PA8 | SHORT RURAL | Third Party Impacts | 870520 | 2 | 347 | 694 | 0.00042402 | 0.0001222
2012-08-29 | 216:10728 | URBAN | Other | 870529 | 1 | 49.75 | 49.75 | 3.0397e-05 | 6.1099e-05
2012-08-29 | ZN2196:PA5 | URBAN | Third Party Impacts | 870581 | 184 | 125 | 22954.25 | 0.014025 | 0.011242
2012-08-29 | 511:29878 | SHORT RURAL | Equipment Failure | 870592 | 93 | 978 | 80964 | 0.049468 | 0.0056822
2012-08-29 | ZN12660:PA5 | SHORT RURAL | Other | 870596 | 77 | 119 | 8523 | 0.0052074 | 0.0047046
2012-08-30 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 870603 | 13 | 375 | 4875 | 0.0029786 | 0.00079428
2012-08-30 | ZN10993:PA1 | URBAN | Equipment Failure | 870604 | 218 | 105 | 22454 | 0.013719 | 0.01332
2012-08-30 | ZN10993:PA2 | URBAN | Equipment Failure | 870604 | 999 | 105 | 87912 | 0.053713 | 0.061038
2012-08-30 | ZN10993:PA5 | URBAN | Equipment Failure | 870604 | 1950 | 105 | 198646 | 0.12137 | 0.11914
2012-08-30 | ZN10993:PA6 | URBAN | Equipment Failure | 870604 | 595 | 105 | 55335 | 0.033809 | 0.036354
2012-08-30 | ZN10993:PA5 | URBAN | Other | 870607 | 1 | 48.3833 | 48.3833 | 2.9562e-05 | 6.1099e-05
2012-08-23 | ZN15006:PA16 | URBAN | Vegetation | 870616 | 31 | 28 | 868 | 0.00053034 | 0.0018941
2012-08-30 | 502:48008 | URBAN | Other | 870625 | 1 | 48.45 | 48.45 | 2.9602e-05 | 6.1099e-05
2012-08-23 | ZN180:PA34 | URBAN | Vegetation | 870632 | 27 | 10 | 270 | 0.00016497 | 0.0016497
2012-08-30 | 243:80077 | URBAN | Other | 870633 | 1 | 1358.6333 | 1358.6333 | 0.00083011 | 6.1099e-05
2012-08-24 | ZN15013:PA10 | SHORT RURAL | Other | 870634 | 27 | 15 | 405 | 0.00024745 | 0.0016497
2012-08-30 | ZN10993:PA8 | URBAN | Weather | 870660 | 33 | 191 | 6303 | 0.003851 | 0.0020163
2012-08-30 | ZN10993:PA5 | URBAN | Other | 870677 | 1 | 87.75 | 87.75 | 5.3614e-05 | 6.1099e-05
2012-08-30 | ZN180:PA22 | URBAN | Third Party Impacts | 870697 | 2 | 131 | 262 | 0.00016008 | 0.0001222
2012-08-30 | 504:48034 | URBAN | Equipment Failure | 870713 | 1 | 62.6167 | 62.6167 | 3.8258e-05 | 6.1099e-05
2012-08-30 | 503:48011 | SHORT RURAL | Other | 870800 | 1 | 147.4 | 147.4 | 9.0059e-05 | 6.1099e-05
2012-08-30 | 503:48011 | SHORT RURAL | Other | 870814 | 1 | 131.7667 | 131.7667 | 8.0508e-05 | 6.1099e-05
2012-08-30 | ZN690:PA36 | URBAN | Equipment Failure | 870824 | 1 | 296 | 296 | 0.00018085 | 6.1099e-05
2012-08-30 | 213:33775 | URBAN | Third Party Impacts | 870841 | 19 | 125 | 2375 | 0.0014511 | 0.0011609
2012-08-30 | 258:80791 | URBAN | Other | 870876 | 1 | 86.2333 | 86.2333 | 5.2687e-05 | 6.1099e-05
2012-08-10 | ZN10994:PA21 | URBAN | Vegetation | 870880 | 9 | 115 | 1035 | 0.00063237 | 0.00054989
2012-08-30 | ZN3288:PA43 44KLM | CBD | Equipment Failure | 870911 | 58 | 122 | 7076 | 0.0043233 | 0.0035437
2012-08-30 | ZN35500:PA28 | URBAN | Other | 870923 | 165 | 74.9833 | 12372.25 | 0.0075593 | 0.010081
2012-08-30 | 222:2015 | SHORT RURAL | Other | 870935 | 1 | 108.6333 | 108.6333 | 6.6373e-05 | 6.1099e-05
2012-08-30 | ZN2602:PA4 | URBAN | Equipment Failure | 871007 | 50 | 70.15 | 3507.5 | 0.002143 | 0.0030549
2012-08-31 | ZN3922:PA13 | URBAN | Vegetation | 871011 | 72 | 150 | 10800 | 0.0065987 | 0.0043991
2012-08-30 | 230:81434 | URBAN | Other | 871012 | 1 | 156.4167 | 156.4167 | 9.5568e-05 | 6.1099e-05
2012-08-30 | 256:80652 | URBAN | Other | 871018 | 1 | 48.1333 | 48.1333 | 2.9409e-05 | 6.1099e-05
2012-08-31 | 221:11897 | URBAN | Other | 871081 | 1 | 342.7833 | 342.7833 | 0.00020944 | 6.1099e-05
2012-08-31 | ZN12620:PA13 | SHORT RURAL | Other | 871120 | 1 | 471.95 | 471.95 | 0.00028836 | 6.1099e-05
2012-08-24 | ZN1673:PA7 | URBAN | Vegetation | 871197 | 55 | 45 | 2475 | 0.0015122 | 0.0033604
2012-08-31 | ZN35600:PA19 | URBAN | Other | 871245 | 1 | 77.7833 | 77.7833 | 4.7525e-05 | 6.1099e-05
2012-08-31 | 260:33344 | URBAN | Other | 871290 | 1 | 137.1 | 137.1 | 8.3766e-05 | 6.1099e-05
2012-08-31 | ZN12630:PA2 | SHORT RURAL | Other | 871417 | 1 | 2497.15 | 2497.15 | 0.0015257 | 6.1099e-05
2012-08-31 | 264:81240 | SHORT RURAL | Operational Error | 871424 | 15 | 100 | 1500 | 0.00091648 | 0.00091648
2012-08-31 | 504:48034 | URBAN | Equipment Failure | 871426 | 571 | 75 | 42825 | 0.026166 | 0.034887
2012-08-31 | ZN1788:PA7 | SHORT RURAL | Equipment Failure | 871473 | 1 | 136 | 136 | 8.3094e-05 | 6.1099e-05
2012-08-31 | ZN1788:PA8 | URBAN | Equipment Failure | 871473 | 85 | 136 | 11480.6667 | 0.0070145 | 0.0051934
2012-08-31 | ZN2196:PA5 | URBAN | Other | 871501 | 1 | 1085.9833 | 1085.9833 | 0.00066352 | 6.1099e-05
2012-08-31 | ZN847:PA26 | URBAN | Vegetation | 871506 | 1 | 343.6 | 343.6 | 0.00020994 | 6.1099e-05
2012-09-01 | 524:33580 | SHORT RURAL | Other | 871514 | 49 | 55 | 2695 | 0.0016466 | 0.0029938
2012-09-01 | 512:48047 | SHORT RURAL | Other | 871520 | 1 | 143.1 | 143.1 | 8.7432e-05 | 6.1099e-05
2012-09-01 | ZN1788:PA8 | URBAN | Equipment Failure | 871531 | 1 | 387.3833 | 387.3833 | 0.00023669 | 6.1099e-05
2012-09-01 | ZN15002:PA6 | URBAN | Equipment Failure | 871538 | 38 | 247 | 9386 | 0.0057347 | 0.0023217
2012-09-01 | 238:34144 | URBAN | Other | 871600 | 1 | 56.9167 | 56.9167 | 3.4775e-05 | 6.1099e-05
2012-09-01 | 208:62 | URBAN | Other | 871601 | 1 | 66.8167 | 66.8167 | 4.0824e-05 | 6.1099e-05
2012-09-01 | ZN12650:PA1 | SHORT RURAL | Vegetation | 871616 | 6 | 206 | 1236 | 0.00075518 | 0.00036659
2012-09-01 | 243:80074 | URBAN | Other | 871618 | 1 | 160.65 | 160.65 | 9.8155e-05 | 6.1099e-05
2012-09-01 | ZN1673:PA13 | URBAN | Equipment Failure | 871626 | 18 | 148 | 2664 | 0.0016277 | 0.0010998
2012-09-01 | ZN1673:PA7 | URBAN | Equipment Failure | 871626 | 28 | 148 | 4144 | 0.0025319 | 0.0017108
2012-09-01 | ZN1648:PA20 | URBAN | Equipment Failure | 871633 | 1 | 2565.5167 | 2565.5167 | 0.0015675 | 6.1099e-05
2012-09-01 | ZN9118:PA12 | URBAN | Third Party Impacts | 871634 | 18 | 163.7833 | 2948.1 | 0.0018012 | 0.0010998
2012-09-01 | ZN9118:PA12 | URBAN | Third Party Impacts | 871637 | 1 | 243.0667 | 243.0667 | 0.00014851 | 6.1099e-05
2012-09-01 | ZN342:PA18 | URBAN | Equipment Failure | 871639 | 1 | 957.15 | 957.15 | 0.00058481 | 6.1099e-05
2012-09-01 | 258:80784 | URBAN | Other | 871650 | 1 | 69.9 | 69.9 | 4.2708e-05 | 6.1099e-05
2012-09-01 | ZN12610:PA22 | URBAN | Other | 871667 | 1327 | 53 | 65083 | 0.039765 | 0.081078
2012-09-01 | ZN3155:PA16 | URBAN | Equipment Failure | 871668 | 681 | 82 | 49974 | 0.030533 | 0.041608
2012-09-01 | 511:29878 | SHORT RURAL | Other | 871669 | 1 | 119.8833 | 119.8833 | 7.3247e-05 | 6.1099e-05
2012-09-01 | 507:80923 | SHORT RURAL | Animals | 871675 | 1 | 287 | 287 | 0.00017535 | 6.1099e-05
2012-09-01 | ZN36300:PA3 | URBAN | Other | 871677 | 1 | 55.65 | 55.65 | 3.4001e-05 | 6.1099e-05
2012-09-01 | ZN690:PA18 | URBAN | Third Party Impacts | 871697 | 22 | 584 | 12848 | 0.00785 | 0.0013442
2012-09-02 | ZN72:PA10 | URBAN | Third Party Impacts | 871713 | 59 | 366 | 21594 | 0.013194 | 0.0036048
2012-09-02 | ZN72:PA18 | URBAN | Third Party Impacts | 871713 | 100 | 366 | 36600 | 0.022362 | 0.0061099
2012-09-02 | ZN10990:PA11 | URBAN | Third Party Impacts | 871714 | 59 | 200 | 11800 | 0.0072096 | 0.0036048
2012-09-02 | ZN398:PA22 | URBAN | Other | 871736 | 1 | 74.7167 | 74.7167 | 4.5651e-05 | 6.1099e-05
2012-09-02 | ZN72:PA18 | URBAN | Third Party Impacts | 871766 | 100 | 129.5333 | 12953.3333 | 0.0079143 | 0.0061099
2012-09-02 | ZN5868:PA28 | URBAN | Operational Error | 871775 | 43 | 34 | 1462 | 0.00089326 | 0.0026272
2012-09-02 | ZN15005:PA12 | URBAN | Other | 871780 | 1 | 62.2167 | 62.2167 | 3.8014e-05 | 6.1099e-05
2012-09-02 | ZN342:PA22 | URBAN | Equipment Failure | 871784 | 2 | 97.15 | 172.2 | 0.00010521 | 0.0001222
2012-09-02 | ZN342:PA26 | URBAN | Equipment Failure | 871784 | 2827 | 97.15 | 147004 | 0.089817 | 0.17273
2012-09-02 | ZN342:PA27 | URBAN | Equipment Failure | 871784 | 166 | 97.15 | 8964 | 0.0054769 | 0.010142
2012-09-02 | ZN342:PA28 | URBAN | Equipment Failure | 871784 | 989 | 97.15 | 54395 | 0.033235 | 0.060427
2012-09-02 | ZN342:PA35 | URBAN | Equipment Failure | 871784 | 782 | 97.15 | 50830 | 0.031056 | 0.047779
2012-09-02 | ZN931:PA11 | URBAN | Equipment Failure | 871784 | 1 | 97.15 | 46 | 2.8105e-05 | 6.1099e-05
2012-09-02 | ZN2602:PA20 | URBAN | Other | 871788 | 1 | 291.6667 | 291.6667 | 0.0001782 | 6.1099e-05
2012-09-02 | ZN847:PA1 | URBAN | Vegetation | 871789 | 1 | 203.1 | 203.1 | 0.00012409 | 6.1099e-05
2012-09-02 | 210:8681 | URBAN | Other | 871799 | 1 | 54.5167 | 54.5167 | 3.3309e-05 | 6.1099e-05
2012-09-02 | ZN2602:PA20 | URBAN | Other | 871802 | 1 | 167.05 | 167.05 | 0.00010207 | 6.1099e-05
2012-09-02 | ZN965:PA6 | URBAN | Other | 871814 | 100 | 178 | 17800 | 0.010876 | 0.0061099
2012-09-02 | 203:8083 | SHORT RURAL | Other | 871825 | 1 | 154.0667 | 154.0667 | 9.4133e-05 | 6.1099e-05
2012-09-03 | ZN4545:PA41 | URBAN | Equipment Failure | 871836 | 112 | 177 | 19824 | 0.012112 | 0.0068431
2012-09-03 | ZN3154:PA19 | URBAN | Vegetation | 871839 | 43 | 54.65 | 2349.95 | 0.0014358 | 0.0026272
2012-09-03 | 507:80922 | SHORT RURAL | Equipment Failure | 871917 | 88 | 99.8333 | 8785.3333 | 0.0053677 | 0.0053767
2012-09-03 | ZN12570:PA12 | SHORT RURAL | Other | 871924 | 1 | 70.6667 | 70.6667 | 4.3176e-05 | 6.1099e-05
2012-09-03 | 220:8689 | URBAN | Other | 871928 | 1 | 128.6333 | 128.6333 | 7.8593e-05 | 6.1099e-05
2012-09-03 | 232:11459 | SHORT RURAL | Other | 872123 | 1 | 293.1 | 293.1 | 0.00017908 | 6.1099e-05
2012-09-03 | ZN12610:PA25 | SHORT RURAL | Other | 872154 | 1 | 101.3167 | 101.3167 | 6.1903e-05 | 6.1099e-05
2012-09-03 | ZN129:PA24 | URBAN | Other | 872230 | 39 | 328 | 12792 | 0.0078157 | 0.0023828
2012-09-03 | 227:13020 | SHORT RURAL | Third Party Impacts | 872240 | 1722 | 444 | 218694 | 0.13362 | 0.10521
2012-09-03 | ZN874:PA18 | SHORT RURAL | Equipment Failure | 872274 | 57 | 176.7833 | 10076.65 | 0.0061567 | 0.0034826
2012-09-03 | ZN15014:PA5 | URBAN | Equipment Failure | 872277 | 29 | 120 | 3480 | 0.0021262 | 0.0017719
2012-09-03 | ZN5868:PA14 | URBAN | Equipment Failure | 872287 | 8 | 38 | 304 | 0.00018574 | 0.00048879
2012-09-03 | ZN5868:PA5 | URBAN | Equipment Failure | 872287 | 103 | 38 | 3914 | 0.0023914 | 0.0062932
2012-09-03 | 504:48031 | SHORT RURAL | Equipment Failure | 872299 | 2 | 166 | 332 | 0.00020285 | 0.0001222
2012-09-04 | ZN630:PA31 | URBAN | Third Party Impacts | 872330 | 8 | 145 | 1160 | 0.00070874 | 0.00048879
2012-08-27 | ZN1193:PA1 | URBAN | Equipment Failure | 872348 | 237 | 10 | 2370 | 0.001448 | 0.01448
2012-08-27 | ZN965:PA33 | URBAN | Vegetation | 872355 | 27 | 60 | 1620 | 0.0009898 | 0.0016497
2012-09-04 | ZN1287:PA3 | URBAN | Other | 872387 | 113 | 28.6 | 3231.8 | 0.0019746 | 0.0069041
2012-09-03 | 511:29872 | URBAN | Other | 872410 | 1 | 10 | 10 | 6.1099e-06 | 6.1099e-05
2012-09-04 | ZN10999:PA16 | URBAN | Vegetation | 872481 | 1 | 91.2 | 91.2 | 5.5722e-05 | 6.1099e-05
2012-09-04 | 801:74121 | SHORT RURAL | Equipment Failure | 872503 | 1 | 164 | 164 | 0.0001002 | 6.1099e-05
2012-09-04 | ZN2635:PA17 | URBAN | Other | 872681 | 1 | 58.1833 | 58.1833 | 3.5549e-05 | 6.1099e-05
2012-09-04 | 524:33570 | SHORT RURAL | Third Party Impacts | 872694 | 827 | 221 | 85088 | 0.051988 | 0.050529
2012-09-04 | 501:48122 | SHORT RURAL | Other | 872700 | 1 | 56.4333 | 56.4333 | 3.448e-05 | 6.1099e-05
2012-09-04 | 503:48016 | URBAN | Other | 872770 | 106 | 84.55 | 8082 | 0.004938 | 0.0064765
2012-09-04 | 503:48078 | URBAN | Other | 872770 | 1 | 84.55 | 43.2833 | 2.6446e-05 | 6.1099e-05
2012-09-04 | ZN10994:PA20 | URBAN | Third Party Impacts | 872792 | 25 | 237 | 5925 | 0.0036201 | 0.0015275
2012-09-05 | ZN80:PA32 | URBAN | Animals | 872810 | 57 | 36 | 2052 | 0.0012537 | 0.0034826
2012-09-05 | 516:48066 | SHORT RURAL | Other | 872812 | 1 | 361.3333 | 361.3333 | 0.00022077 | 6.1099e-05
2012-09-04 | 264:81240 | SHORT RURAL | Operational Error | 872838 | 15 | 50 | 750 | 0.00045824 | 0.00091648
2012-09-05 | 208:62 | URBAN | Other | 872852 | 1 | 65.2833 | 65.2833 | 3.9887e-05 | 6.1099e-05
2012-09-05 | ZN9118:PA26 | URBAN | Other | 872882 | 33 | 125 | 4125 | 0.0025203 | 0.0020163
2012-09-05 | 220:8688 | URBAN | Other | 872884 | 1 | 257.0833 | 257.0833 | 0.00015707 | 6.1099e-05
2012-09-05 | 227:13015 | SHORT RURAL | Vegetation | 872991 | 1509 | 69 | 104121 | 0.063617 | 0.092198
2012-09-05 | ZN10995:PA6 | URBAN | Equipment Failure | 873019 | 1 | 360.1333 | 360.1333 | 0.00022004 | 6.1099e-05
2012-09-05 | 515:35200 | URBAN | Equipment Failure | 873035 | 4 | 263 | 1052 | 0.00064276 | 0.00024439
2012-09-05 | ZN12620:PA10 | SHORT RURAL | Vegetation | 873103 | 1074 | 81 | 63627 | 0.038875 | 0.06562
2012-09-05 | 509:48039 | LONG RURAL | Other | 873110 | 67 | 262 | 15585 | 0.0095222 | 0.0040936
2012-09-05 | 232:11460 | URBAN | Equipment Failure | 873114 | 1 | 199.4333 | 199.4333 | 0.00012185 | 6.1099e-05
2012-08-10 | ZN129:PA24 | URBAN | Other | 873125 | 109 | 266 | 28994 | 0.017715 | 0.0066598
2012-09-05 | 502:48008 | URBAN | Operational Error | 873127 | 104 | 30.6833 | 3191.0667 | 0.0019497 | 0.0063543
2012-09-05 | 203:8089 | URBAN | Equipment Failure | 873147 | 233 | 732 | 43636 | 0.026661 | 0.014236
2012-09-05 | ZN2835:PA23 | URBAN | Equipment Failure | 873159 | 51 | 115.7333 | 5902.4 | 0.0036063 | 0.003116
2012-09-05 | 227:13020 | SHORT RURAL | Vegetation | 873171 | 16 | 84.25 | 1348 | 0.00082361 | 0.00097758
2012-09-05 | ZN2635:PA17 | URBAN | Equipment Failure | 873255 | 1 | 245.8167 | 245.8167 | 0.00015019 | 6.1099e-05
2012-09-05 | ZN1287:PA17 | URBAN | Third Party Impacts | 873259 | 1 | 321.65 | 321.65 | 0.00019652 | 6.1099e-05
2012-09-05 | ZN2635:PA1 | URBAN | Third Party Impacts | 873261 | 1 | 119.1167 | 119.1167 | 7.2779e-05 | 6.1099e-05
2012-09-05 | ZN9700:PA23 | URBAN | Equipment Failure | 873264 | 1 | 303.35 | 303.35 | 0.00018534 | 6.1099e-05
2012-09-05 | 523:33501 | SHORT RURAL | Animals | 873278 | 663 | 99 | 60124 | 0.036735 | 0.040508
2012-09-05 | ZN12630:PA1 | SHORT RURAL | Vegetation | 873290 | 71 | 267 | 10417 | 0.0063646 | 0.004338
2012-09-05 | 205:12203 | URBAN | Vegetation | 873293 | 42 | 73 | 3066 | 0.0018733 | 0.0025661
2012-09-05 | ZN3154:PA16 | URBAN | Equipment Failure | 873301 | 950 | 107 | 97756 | 0.059728 | 0.058044
2012-09-06 | 813:89055 | SHORT RURAL | Operational Error | 873303 | 133 | 748 | 25731 | 0.015721 | 0.0081261
2012-09-06 | ZN1290:PA4 | URBAN | Weather | 873306 | 68 | 229.3833 | 15598.0667 | 0.0095302 | 0.0041547
2012-09-06 | ZN129:PA12 | URBAN | Animals | 873307 | 1291 | 205 | 90294 | 0.055168 | 0.078878
2012-09-06 | 243:80080 | SHORT RURAL | Other | 873309 | 1 | 273.55 | 273.55 | 0.00016714 | 6.1099e-05
2012-09-06 | 220:8687 | URBAN | Other | 873310 | 69 | 126.9 | 8756.1 | 0.0053499 | 0.0042158
2012-09-06 | ZN3425:PA12 | URBAN | Equipment Failure | 873344 | 1 | 218.9167 | 218.9167 | 0.00013376 | 6.1099e-05
2012-09-06 | 243:80083 | SHORT RURAL | Vegetation | 873355 | 342 | 361 | 54518 | 0.03331 | 0.020896
2012-09-06 | 224:80340 | SHORT RURAL | Other | 873362 | 1 | 131.9833 | 131.9833 | 8.064e-05 | 6.1099e-05
2012-09-06 | 523:33508 | SHORT RURAL | Other | 873405 | 1 | 31.3 | 31.3 | 1.9124e-05 | 6.1099e-05
2012-09-05 | 524:33580 | SHORT RURAL | Other | 873406 | 1 | 65 | 65 | 3.9714e-05 | 6.1099e-05
2012-09-06 | 810:74062 | SHORT RURAL | Other | 873410 | 61 | 15 | 915 | 0.00055905 | 0.003727
2012-09-05 | 512:48049 | SHORT RURAL | Other | 873434 | 1 | 18 | 18 | 1.0998e-05 | 6.1099e-05
2012-09-06 | 221:11897 | URBAN | Equipment Failure | 873449 | 3 | 144 | 432 | 0.00026395 | 0.0001833
2012-09-06 | 264:81240 | SHORT RURAL | Equipment Failure | 873497 | 11 | 182 | 2002 | 0.0012232 | 0.00067209
2012-09-06 | ZN1648:PA21 | URBAN | Vegetation | 873505 | 1 | 183.6667 | 183.6667 | 0.00011222 | 6.1099e-05
2012-09-06 | 224:80340 | SHORT RURAL | Other | 873543 | 1 | 116.8 | 116.8 | 7.1363e-05 | 6.1099e-05
2012-09-06 | 202:34260 | URBAN | Other | 873601 | 1 | 112.6333 | 112.6333 | 6.8817e-05 | 6.1099e-05
2012-09-06 | 208:56 | URBAN | Vegetation | 873625 | 1 | 146.1 | 146.1 | 8.9265e-05 | 6.1099e-05
2012-09-06 | ZN3472:PA31 | URBAN | Other | 873635 | 1 | 212.9167 | 212.9167 | 0.00013009 | 6.1099e-05
2012-09-06 | 512:48049 | SHORT RURAL | Equipment Failure | 873656 | 1 | 545 | 545 | 0.00033299 | 6.1099e-05
2012-08-23 | ZN965:PA22 | URBAN | Vegetation | 873667 | 1 | 483 | 483 | 0.00029511 | 6.1099e-05
2012-09-06 | 513:48058 | URBAN | Other | 873707 | 4 | 150 | 600 | 0.00036659 | 0.00024439
2012-09-06 | 240:34835 | URBAN | Vegetation | 873717 | 1 | 51.0167 | 51.0167 | 3.1171e-05 | 6.1099e-05
2012-09-06 | ZN10999:PA22 | URBAN | Equipment Failure | 873721 | 3 | 434 | 1302 | 0.0007955 | 0.0001833
2012-09-06 | 228:7491 | URBAN | Other | 873727 | 1 | 108.7167 | 108.7167 | 6.6424e-05 | 6.1099e-05
2012-09-06 | ZN80:PA24 | URBAN | Equipment Failure | 873731 | 1 | 280.6167 | 280.6167 | 0.00017145 | 6.1099e-05
2012-09-06 | ZN1193:PA15 | URBAN | Vegetation | 873742 | 1 | 163.75 | 163.75 | 0.00010005 | 6.1099e-05
2012-09-06 | 221:11900 | URBAN | Vegetation | 873751 | 1 | 159.7167 | 159.7167 | 9.7585e-05 | 6.1099e-05
2012-09-06 | 202:34260 | URBAN | Animals | 873810 | 1811 | 344 | 152590 | 0.09323 | 0.11065
2012-09-06 | 256:80635 | URBAN | Animals | 873810 | 2 | 344 | 130 | 7.9428e-05 | 0.0001222
2012-09-06 | 256:80650 | URBAN | Animals | 873810 | 617 | 344 | 40105 | 0.024504 | 0.037698
2012-09-06 | ZN262:PA32 | URBAN | Equipment Failure | 873821 | 80 | 157.2167 | 12577.3333 | 0.0076846 | 0.0048879
2012-09-06 | ZN12660:PA5 | SHORT RURAL | Vegetation | 873832 | 1 | 255.6 | 255.6 | 0.00015617 | 6.1099e-05
2012-09-07 | 217:33611 | URBAN | Animals | 873836 | 1513 | 260 | 161831 | 0.098877 | 0.092442
2012-09-07 | ZN12690:PA6 | URBAN | Equipment Failure | 873850 | 68 | 105.7833 | 7193.2667 | 0.004395 | 0.0041547
2012-09-07 | 210:8681 | URBAN | Other | 873913 | 1 | 140.05 | 140.05 | 8.5569e-05 | 6.1099e-05
2012-09-07 | ZN14892:PA19 | URBAN | Other | 873998 | 1 | 157.55 | 157.55 | 9.6261e-05 | 6.1099e-05
2012-09-07 | ZN72:PA14 | URBAN | Third Party Impacts | 874018 | 1 | 219.1167 | 219.1167 | 0.00013388 | 6.1099e-05
2012-09-07 | ZN14892:PA16 | URBAN | Equipment Failure | 874042 | 25 | 450 | 11250 | 0.0068736 | 0.0015275
2012-09-07 | ZN2602:PA21 | URBAN | Third Party Impacts | 874051 | 1 | 332.9 | 332.9 | 0.0002034 | 6.1099e-05
2012-09-07 | ZN14891:PA1 | SHORT RURAL | Equipment Failure | 874060 | 483 | 159 | 42987 | 0.026264 | 0.029511
2012-09-07 | ZN14891:PA10 | SHORT RURAL | Equipment Failure | 874060 | 2104 | 159 | 300705 | 0.18373 | 0.12855
2012-09-07 | ZN14891:PA3 | SHORT RURAL | Equipment Failure | 874060 | 21 | 159 | 1911 | 0.0011676 | 0.0012831
2012-09-07 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 874060 | 1411 | 159 | 129812 | 0.079313 | 0.08621
2012-09-07 | ZN14891:PA6 | URBAN | Equipment Failure | 874060 | 205 | 159 | 19065 | 0.011648 | 0.012525
2012-09-07 | ZN14891:PA8 | SHORT RURAL | Equipment Failure | 874060 | 1309 | 159 | 123046 | 0.075179 | 0.079978
2012-09-07 | ZN14891:PA9 | URBAN | Equipment Failure | 874060 | 1189 | 159 | 112955 | 0.069014 | 0.072646
2012-09-07 | ZN15008:PA1 | URBAN | Other | 874062 | 1 | 259.7333 | 259.7333 | 0.00015869 | 6.1099e-05
2012-09-07 | ZN1285:PA31 | URBAN | Vegetation | 874066 | 80 | 177.9333 | 14234.6667 | 0.0086972 | 0.0048879
2012-09-07 | ZN1287:PA22 | URBAN | Weather | 874082 | 60 | 101.0167 | 6061 | 0.0037032 | 0.0036659
2012-09-07 | ZN965:PA43 | URBAN | Vegetation | 874095 | 34 | 107.0167 | 3638.5667 | 0.0022231 | 0.0020774
2012-09-07 | ZN12620:PA2 | SHORT RURAL | Equipment Failure | 874107 | 1 | 406.8333 | 406.8333 | 0.00024857 | 6.1099e-05
2012-09-07 | 502:48010 | SHORT RURAL | Equipment Failure | 874110 | 1027 | 253 | 146896 | 0.089751 | 0.062748
2012-09-07 | ZN180:PA27 | URBAN | Other | 874112 | 1 | 183.1833 | 183.1833 | 0.00011192 | 6.1099e-05
2012-09-07 | 227:13015 | SHORT RURAL | Vegetation | 874127 | 317 | 177 | 56109 | 0.034282 | 0.019368
2012-09-07 | ZN12620:PA13 | SHORT RURAL | Third Party Impacts | 874128 | 1 | 229.9167 | 229.9167 | 0.00014048 | 6.1099e-05
2012-09-07 | ZN195:PA11 | URBAN | Vegetation | 874130 | 37 | 59.3667 | 2196.5667 | 0.0013421 | 0.0022607
2012-09-07 | ZN262:PA5 | URBAN | Vegetation | 874136 | 59 | 131.9 | 7782.1 | 0.0047548 | 0.0036048
2012-09-07 | 243:80081 | URBAN | Other | 874151 | 1 | 127.3333 | 127.3333 | 7.7799e-05 | 6.1099e-05
2012-09-07 | ZN12620:PA13 | SHORT RURAL | Third Party Impacts | 874159 | 1 | 213.3167 | 213.3167 | 0.00013033 | 6.1099e-05
2012-09-07 | 227:13020 | SHORT RURAL | Vegetation | 874160 | 1 | 167.0167 | 167.0167 | 0.00010204 | 6.1099e-05
2012-09-07 | ZN14891:PA21 | SHORT RURAL | Equipment Failure | 874164 | 525 | 111 | 38244 | 0.023367 | 0.032077
2012-09-07 | ZN15013:PA4 | URBAN | Vegetation | 874167 | 13 | 97 | 1261 | 0.00077045 | 0.00079428
2012-09-07 | ZN15013:PA6 | SHORT RURAL | Vegetation | 874167 | 221 | 97 | 21437 | 0.013098 | 0.013503
2012-09-07 | ZN965:PA33 | URBAN | Other | 874176 | 18 | 444.1167 | 7994.1 | 0.0048843 | 0.0010998
2012-09-07 | ZN12590:PA7 | SHORT RURAL | Vegetation | 874179 | 28 | 357 | 9996 | 0.0061074 | 0.0017108
2012-09-07 | ZN14891:PA5 | SHORT RURAL | Vegetation | 874181 | 1 | 120.0667 | 120.0667 | 7.3359e-05 | 6.1099e-05
2012-09-07 | ZN12620:PA3 | URBAN | Weather | 874183 | 13 | 378 | 4914 | 0.0030024 | 0.00079428
2012-09-07 | ZN12620:PA7 | URBAN | Weather | 874183 | 3 | 378 | 1134 | 0.00069286 | 0.0001833
2012-09-07 | ZN12620:PA7 | URBAN | Other | 874187 | 1 | 179 | 179 | 0.00010937 | 6.1099e-05
2012-09-07 | ZN847:PA5 | URBAN | Weather | 874200 | 18 | 101.75 | 1831.5 | 0.001119 | 0.0010998
2012-09-07 | ZN269:PA2 | URBAN | Third Party Impacts | 874208 | 108 | 126 | 12528 | 0.0076544 | 0.0065987
2012-09-07 | ZN269:PA9 | URBAN | Third Party Impacts | 874208 | 130 | 126 | 16380 | 0.010008 | 0.0079428
2012-09-07 | ZN1193:PA6 | URBAN | Vegetation | 874211 | 1 | 195.9667 | 195.9667 | 0.00011973 | 6.1099e-05
2012-09-07 | ZN12620:PA7 | URBAN | Other | 874233 | 1 | 143.7333 | 143.7333 | 8.7819e-05 | 6.1099e-05
2012-09-07 | ZN10993:PA5 | URBAN | Vegetation | 874253 | 1 | 199.5167 | 199.5167 | 0.0001219 | 6.1099e-05
2012-09-07 | 264:81240 | SHORT RURAL | Other | 874254 | 42 | 283 | 11886 | 0.0072622 | 0.0025661
2012-09-07 | ZN2568:PA6 | SHORT RURAL | Vegetation | 874258 | 40 | 165.9 | 6636 | 0.0040545 | 0.0024439
2012-09-07 | 219:1783 | SHORT RURAL | Other | 874261 | 1 | 359.9333 | 359.9333 | 0.00021991 | 6.1099e-05
2012-09-07 | 206:34438 | SHORT RURAL | Vegetation | 874264 | 590 | 33 | 19470 | 0.011896 | 0.036048
2012-09-07 | 217:33611 | URBAN | Vegetation | 874264 | 702 | 33 | 23166 | 0.014154 | 0.042891
2012-09-07 | ZN9118:PA11 | URBAN | Vegetation | 874270 | 1 | 385.5833 | 385.5833 | 0.00023559 | 6.1099e-05
2012-09-07 | ZN14891:PA5 | SHORT RURAL | Vegetation | 874298 | 1 | 84.6 | 84.6 | 5.1689e-05 | 6.1099e-05
2012-09-07 | ZN14892:PA13 | URBAN | Vegetation | 874310 | 1 | 377.3167 | 377.3167 | 0.00023054 | 6.1099e-05
2012-09-07 | 225:33676 | SHORT RURAL | Vegetation | 874313 | 1 | 164.6833 | 164.6833 | 0.00010062 | 6.1099e-05
2012-09-07 | 509:48039 | LONG RURAL | Other | 874340 | 1 | 1208.7167 | 1208.7167 | 0.00073851 | 6.1099e-05
2012-09-07 | ZN15008:PA9 | URBAN | Animals | 874358 | 2094 | 197 | 310506 | 0.18972 | 0.12794
2012-09-07 | ZN12630:PA1 | SHORT RURAL | Equipment Failure | 874372 | 7 | 310 | 2170 | 0.0013258 | 0.00042769
2012-09-07 | 813:89055 | SHORT RURAL | Other | 874377 | 1 | 92.3667 | 92.3667 | 5.6435e-05 | 6.1099e-05
2012-09-07 | ZN2400:PA18 | SHORT RURAL | Vegetation | 874378 | 181 | 14 | 2534 | 0.0015482 | 0.011059
2012-09-07 | ZN14891:PA8 | SHORT RURAL | Vegetation | 874379 | 5 | 323 | 1615 | 0.00098674 | 0.00030549
2012-09-07 | ZN15009:PA1 | URBAN | Other | 874396 | 2009 | 13 | 14063 | 0.0085923 | 0.12275
2012-09-07 | ZN15009:PA11 | URBAN | Other | 874396 | 2184 | 13 | 15288 | 0.0093408 | 0.13344
2012-09-07 | ZN15009:PA12 | URBAN | Other | 874396 | 54 | 13 | 378 | 0.00023095 | 0.0032993
2012-09-07 | ZN15009:PA3 | URBAN | Other | 874396 | 845 | 13 | 5915 | 0.003614 | 0.051628
2012-09-07 | ZN15009:PA5 | URBAN | Other | 874396 | 1847 | 13 | 12929 | 0.0078994 | 0.11285
2012-09-07 | ZN15009:PA7 | URBAN | Other | 874396 | 1575 | 13 | 11025 | 0.0067361 | 0.09623
2012-09-07 | ZN15009:PA9 | URBAN | Other | 874396 | 591 | 13 | 4137 | 0.0025277 | 0.036109
2012-09-07 | ZN15015:PA15 | URBAN | Other | 874396 | 309 | 13 | 4017 | 0.0024543 | 0.018879
2012-09-07 | ZN15015:PA5 | URBAN | Other | 874396 | 1642 | 13 | 21346 | 0.013042 | 0.10032
2012-09-07 | ZN847:PA44 | URBAN | Vegetation | 874400 | 1 | 1652.1667 | 1652.1667 | 0.0010095 | 6.1099e-05
2012-09-07 | 264:81236 | URBAN | Vegetation | 874414 | 1 | 307.8833 | 307.8833 | 0.00018811 | 6.1099e-05
2012-09-07 | 512:48047 | SHORT RURAL | Other | 874421 | 1 | 167.9833 | 167.9833 | 0.00010264 | 6.1099e-05
2012-09-07 | 813:89061 | LONG RURAL | Equipment Failure | 874434 | 1 | 910 | 910 | 0.000556 | 6.1099e-05
2012-09-07 | ZN1193:PA6 | URBAN | Other | 874440 | 1 | 211.1333 | 211.1333 | 0.000129 | 6.1099e-05
2012-09-07 | 524:33580 | SHORT RURAL | Equipment Failure | 874442 | 2 | 85 | 170 | 0.00010387 | 0.0001222
2012-09-08 | ZN12570:PA6 | SHORT RURAL | Third Party Impacts | 874464 | 1 | 198.15 | 198.15 | 0.00012107 | 6.1099e-05
2012-09-08 | 210:8679 | URBAN | Vegetation | 874482 | 1 | 44.2 | 44.2 | 2.7006e-05 | 6.1099e-05
2012-09-08 | 501:48122 | SHORT RURAL | Equipment Failure | 874507 | 1 | 178 | 178 | 0.00010876 | 6.1099e-05
2012-09-08 | 256:80635 | URBAN | Other | 874511 | 1 | 75.1333 | 75.1333 | 4.5905e-05 | 6.1099e-05
2012-09-08 | ZN9118:PA3 | SHORT RURAL | Vegetation | 874514 | 52 | 10 | 520 | 0.00031771 | 0.0031771
2012-09-08 | ZN12570:PA1 | SHORT RURAL | Vegetation | 874548 | 1 | 487.6833 | 487.6833 | 0.00029797 | 6.1099e-05
2012-09-08 | ZN15001:PA6 | URBAN | Third Party Impacts | 874552 | 47 | 90.4333 | 4250.3667 | 0.0025969 | 0.0028716
2012-09-08 | ZN14891:PA1 | SHORT RURAL | Vegetation | 874575 | 1 | 288.9667 | 288.9667 | 0.00017655 | 6.1099e-05
2012-09-08 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 874612 | 1 | 641.8167 | 641.8167 | 0.00039214 | 6.1099e-05
2012-09-08 | ZN12570:PA1 | SHORT RURAL | Vegetation | 874650 | 1 | 196.85 | 196.85 | 0.00012027 | 6.1099e-05
2012-09-09 | ZN2196:PA25 | URBAN | Equipment Failure | 874660 | 57 | 193.8167 | 11047.55 | 0.0067499 | 0.0034826
2012-09-09 | ZN12610:PA11 | URBAN | Equipment Failure | 874673 | 1 | 389.6833 | 389.6833 | 0.00023809 | 6.1099e-05
2012-09-09 | 526:34641 | SHORT RURAL | Equipment Failure | 874740 | 2 | 83 | 166 | 0.00010142 | 0.0001222
2012-09-09 | ZN1788:PA30 | URBAN | Vegetation | 874743 | 1 | 412.45 | 412.45 | 0.000252 | 6.1099e-05
2012-09-09 | 208:56 | URBAN | Other | 874752 | 1 | 65.5333 | 65.5333 | 4.004e-05 | 6.1099e-05
2012-09-09 | 813:89063 | SHORT RURAL | Equipment Failure | 874760 | 24 | 66 | 1584 | 0.0009678 | 0.0014664
2012-09-09 | 264:81244 | URBAN | Equipment Failure | 874773 | 67 | 551.0333 | 20750.1333 | 0.012678 | 0.0040936
2012-09-09 | ZN269:PA2 | URBAN | Other | 874779 | 120 | 36.5 | 4380 | 0.0026761 | 0.0073318
2012-09-10 | ZN901:PA2 | URBAN | Equipment Failure | 874786 | 147 | 69 | 10143 | 0.0061972 | 0.0089815
2012-09-10 | ZN9252:PA9 | URBAN | Vegetation | 874789 | 49 | 120 | 5880 | 0.0035926 | 0.0029938
2012-09-10 | ZN1193:PA16 | URBAN | Equipment Failure | 874803 | 1 | 139.5167 | 139.5167 | 8.5243e-05 | 6.1099e-05
2012-09-06 | 243:80081 | URBAN | Other | 874809 | 19 | 223 | 4237 | 0.0025888 | 0.0011609
2012-09-10 | ZN3425:PA24 | URBAN | Other | 874821 | 1 | 186.75 | 186.75 | 0.0001141 | 6.1099e-05
2012-09-10 | ZN15010:PA1 | URBAN | Equipment Failure | 874876 | 1 | 155.6833 | 155.6833 | 9.512e-05 | 6.1099e-05
2012-09-07 | 240:34852 | URBAN | Equipment Failure | 874903 | 1 | 42 | 42 | 2.5661e-05 | 6.1099e-05
2012-09-10 | ZN15008:PA7 | URBAN | Equipment Failure | 874956 | 1 | 225.35 | 225.35 | 0.00013769 | 6.1099e-05
2012-09-10 | 509:48039 | LONG RURAL | Vegetation | 874986 | 1 | 209.2167 | 209.2167 | 0.00012783 | 6.1099e-05
2012-09-10 | ZN901:PA18 | URBAN | Other | 875029 | 1 | 161.8 | 161.8 | 9.8858e-05 | 6.1099e-05
2012-09-03 | ZN129:PA24 | URBAN | Other | 875069 | 32 | 328 | 10496 | 0.0064129 | 0.0019552
2012-09-10 | ZN12690:PA24 | SHORT RURAL | Vegetation | 875101 | 1 | 248.45 | 248.45 | 0.0001518 | 6.1099e-05
2012-09-06 | 812:19065 | SHORT RURAL | Third Party Impacts | 875106 | 3 | 85 | 255 | 0.0001558 | 0.0001833
2012-09-06 | 516:48066 | SHORT RURAL | Equipment Failure | 875168 | 1 | 125 | 125 | 7.6373e-05 | 6.1099e-05
2012-09-10 | ZN187:PA13 | URBAN | Equipment Failure | 875273 | 852 | 214 | 114735 | 0.070102 | 0.052056
2012-09-10 | ZN187:PA17 | URBAN | Equipment Failure | 875273 | 96 | 214 | 20544 | 0.012552 | 0.0058655
2012-09-10 | ZN187:PA19 | URBAN | Equipment Failure | 875273 | 81 | 214 | 17334 | 0.010591 | 0.004949
2012-09-10 | ZN187:PA30 | URBAN | Equipment Failure | 875273 | 62 | 214 | 6882 | 0.0042048 | 0.0037881
2012-09-10 | ZN15009:PA7 | URBAN | Equipment Failure | 875308 | 65 | 42 | 2730 | 0.001668 | 0.0039714
2012-09-11 | 503:48076 | URBAN | Other | 875332 | 2 | 79.7167 | 128.9 | 7.8756e-05 | 0.0001222
2012-09-10 | 511:29873 | SHORT RURAL | Equipment Failure | 875430 | 13 | 60 | 780 | 0.00047657 | 0.00079428
2012-09-10 | 813:89055 | SHORT RURAL | Other | 875440 | 1 | 69 | 69 | 4.2158e-05 | 6.1099e-05
2012-09-11 | 524:33572 | SHORT RURAL | Other | 875453 | 1 | 175.1167 | 175.1167 | 0.00010699 | 6.1099e-05
2012-09-05 | ZN1673:PA7 | URBAN | Operational Error | 875586 | 351 | 3 | 1053 | 0.00064337 | 0.021446
2012-09-11 | ZN12640:PA10 | URBAN | Other | 875609 | 1 | 125.5 | 125.5 | 7.6679e-05 | 6.1099e-05
2012-09-11 | ZN9245:PA10 | URBAN | Vegetation | 875634 | 1772 | 109 | 172724 | 0.10553 | 0.10827
2012-09-11 | 224:80329 | SHORT RURAL | Vegetation | 875648 | 1 | 109.4833 | 109.4833 | 6.6893e-05 | 6.1099e-05
2012-09-11 | ZN10996:PA19 | URBAN | Vegetation | 875697 | 1 | 188.6167 | 188.6167 | 0.00011524 | 6.1099e-05
2012-09-11 | 202:34262 | URBAN | Other | 875706 | 1 | 1075.6667 | 1075.6667 | 0.00065722 | 6.1099e-05
2012-09-11 | ZN14891:PA14 | SHORT RURAL | Other | 875726 | 409 | 129 | 44767 | 0.027352 | 0.024989
2012-09-11 | ZN35600:PA25 | URBAN | Third Party Impacts | 875727 | 1 | 323.65 | 323.65 | 0.00019775 | 6.1099e-05
2012-09-11 | ZN116:PA48 | URBAN | Other | 875739 | 40 | 84 | 3360 | 0.0020529 | 0.0024439
2012-09-11 | ZN35600:PA25 | URBAN | Third Party Impacts | 875742 | 2 | 269.0667 | 538.1333 | 0.00032879 | 0.0001222
2012-09-11 | 520:48172 | SHORT RURAL | Equipment Failure | 875745 | 24 | 65 | 1560 | 0.00095314 | 0.0014664
2012-09-11 | ZN12690:PA7 | SHORT RURAL | Equipment Failure | 875764 | 1 | 1003.8 | 1003.8 | 0.00061331 | 6.1099e-05
2012-09-11 | ZN12690:PA6 | URBAN | Equipment Failure | 875779 | 29 | 63 | 1827 | 0.0011163 | 0.0017719
2012-09-12 | ZN398:PA15 | URBAN | Third Party Impacts | 875781 | 1 | 389.5 | 389.5 | 0.00023798 | 6.1099e-05
2012-09-12 | ZN14892:PA21 | URBAN | Equipment Failure | 875784 | 1076 | 231 | 173620 | 0.10608 | 0.065742
2012-09-12 | ZN14892:PA3 | SHORT RURAL | Equipment Failure | 875784 | 1196 | 231 | 29900 | 0.018269 | 0.073074
2012-09-12 | ZN690:PA24 | SHORT RURAL | Third Party Impacts | 875786 | 67 | 95.0167 | 6366.1167 | 0.0038896 | 0.0040936
2012-09-12 | 232:11457 | URBAN | Other | 875789 | 1 | 166.6667 | 166.6667 | 0.00010183 | 6.1099e-05
2012-09-12 | ZN5868:PA10 | URBAN | Third Party Impacts | 875790 | 7 | 93 | 651 | 0.00039775 | 0.00042769
2012-09-12 | 256:80646 | URBAN | Other | 875819 | 1 | 52 | 52 | 3.1771e-05 | 6.1099e-05
2012-09-12 | 202:34254 | URBAN | Other | 875856 | 1 | 62.7 | 62.7 | 3.8309e-05 | 6.1099e-05
2012-09-12 | ZN15006:PA13 | URBAN | Equipment Failure | 875971 | 1320 | 51 | 55007 | 0.033609 | 0.08065
2012-09-12 | 515:35193 | SHORT RURAL | Animals | 876017 | 1 | 37.9667 | 37.9667 | 2.3197e-05 | 6.1099e-05
2012-09-12 | ZN15006:PA15 | URBAN | Other | 876031 | 1 | 107.2 | 107.2 | 6.5498e-05 | 6.1099e-05
2012-09-12 | 203:8082 | URBAN | Equipment Failure | 876038 | 5 | 89.3167 | 446.5833 | 0.00027286 | 0.00030549
2012-09-12 | 811:74234 | SHORT RURAL | Other | 876099 | 1 | 74 | 74 | 4.5213e-05 | 6.1099e-05
2012-09-12 | 503:48078 | URBAN | Other | 876118 | 1 | 203.2167 | 203.2167 | 0.00012416 | 6.1099e-05
2012-09-12 | 509:48039 | LONG RURAL | Other | 876127 | 2 | 45 | 90 | 5.4989e-05 | 0.0001222
2012-09-12 | ZN12580:PA16 | URBAN | Vegetation | 876196 | 546 | 69 | 37674 | 0.023018 | 0.03336
2012-09-12 | 501:48122 | SHORT RURAL | Equipment Failure | 876198 | 523 | 909 | 205631 | 0.12564 | 0.031955
2012-09-13 | ZN14892:PA3 | SHORT RURAL | Other | 876201 | 1 | 299.6 | 299.6 | 0.00018282 | 6.1023e-05
2012-09-06 | 202:34260 | URBAN | Animals | 876217 | 837 | 96 | 80352 | 0.049094 | 0.05114
2012-09-12 | 232:11457 | URBAN | Equipment Failure | 876223 | 1 | 90 | 90 | 5.4989e-05 | 6.1099e-05
2012-09-13 | ZN195:PA11 | URBAN | Other | 876226 | 1 | 201.1667 | 201.1667 | 0.00012276 | 6.1023e-05
2012-09-12 | 203:8082 | URBAN | Equipment Failure | 876228 | 5 | 5 | 25 | 1.5275e-05 | 0.00030549
2012-09-13 | 801:74121 | SHORT RURAL | Equipment Failure | 876230 | 455 | 274 | 36782 | 0.022445 | 0.027765
2012-09-12 | 802:82225 | SHORT RURAL | Other | 876255 | 2 | 60 | 120 | 7.3318e-05 | 0.0001222
2012-09-13 | 803:74013 | SHORT RURAL | Other | 876257 | 103 | 60 | 6180 | 0.0037712 | 0.0062854
2012-09-13 | ZN9118:PA17 | URBAN | Vegetation | 876350 | 1 | 59.6667 | 59.6667 | 3.641e-05 | 6.1023e-05
2012-09-13 | ZN14892:PA13 | URBAN | Other | 876398 | 1 | 51.8333 | 51.8333 | 3.163e-05 | 6.1023e-05
2012-09-13 | 265:81649 | URBAN | Vegetation | 876493 | 25 | 1220.2333 | 1525 | 0.0009306 | 0.0015256
2012-09-13 | 265:81651 | URBAN | Vegetation | 876493 | 82 | 1220.2333 | 6523 | 0.0039805 | 0.0050039
2012-09-13 | ZN9118:PA13 | URBAN | Other | 876560 | 1 | 102.5333 | 102.5333 | 6.2569e-05 | 6.1023e-05
2012-09-13 | ZN9301:PA13 | SHORT RURAL | Equipment Failure | 876574 | 1 | 439.05 | 439.05 | 0.00026792 | 6.1023e-05
2012-09-13 | ZN35600:PA22 | URBAN | Equipment Failure | 876578 | 1 | 410.1167 | 410.1167 | 0.00025026 | 6.1023e-05
2012-09-13 | ZN12620:PA10 | SHORT RURAL | Equipment Failure | 876599 | 629 | 48 | 30192 | 0.018424 | 0.038383
2012-09-13 | ZN10994:PA10 | URBAN | Other | 876636 | 1 | 344.45 | 344.45 | 0.00021019 | 6.1023e-05
2012-09-13 | ZN2310:PA28 | URBAN | Other | 876637 | 1 | 207.1833 | 207.1833 | 0.00012643 | 6.1023e-05
2012-09-13 | 504:48031 | SHORT RURAL | Equipment Failure | 876639 | 15 | 80 | 1200 | 0.00073227 | 0.00091534
2012-09-13 | ZN12660:PA14 | SHORT RURAL | Equipment Failure | 876640 | 65 | 339 | 14901 | 0.009093 | 0.0039665
2012-09-13 | ZN12610:PA17 | URBAN | Vegetation | 876645 | 2 | 70.55 | 38.5 | 2.3494e-05 | 0.00012205
2012-09-13 | ZN12690:PA3 | SHORT RURAL | Vegetation | 876645 | 227 | 70.55 | 12258 | 0.0074802 | 0.013852
2012-09-13 | 264:81240 | SHORT RURAL | Other | 876659 | 21 | 73 | 1533 | 0.00093548 | 0.0012815
2012-09-13 | 202:34232 | URBAN | Vegetation | 876662 | 1 | 878.3833 | 878.3833 | 0.00053601 | 6.1023e-05
2012-09-13 | ZN12570:PA15 | SHORT RURAL | Vegetation | 876664 | 32 | 57 | 1824 | 0.0011131 | 0.0019527
2012-09-13 | ZN2568:PA21 | URBAN | Equipment Failure | 876685 | 1 | 38 | 38 | 2.3189e-05 | 6.1023e-05
2012-09-13 | ZN2568:PA40 | URBAN | Equipment Failure | 876685 | 49 | 38 | 1862 | 0.0011362 | 0.0029901
2012-09-13 | ZN8100:PA20 | URBAN | Equipment Failure | 876685 | 666 | 38 | 24054 | 0.014678 | 0.040641
2012-09-13 | ZN12660:PA14 | SHORT RURAL | Equipment Failure | 876692 | 1 | 49.1667 | 49.1667 | 3.0003e-05 | 6.1023e-05
2012-09-13 | 218:7478 | URBAN | Other | 876694 | 1 | 150.0833 | 150.0833 | 9.1585e-05 | 6.1023e-05
2012-09-13 | 511:29878 | SHORT RURAL | Equipment Failure | 876698 | 2 | 353 | 706 | 0.00043082 | 0.00012205
2012-09-13 | ZN14891:PA5 | SHORT RURAL | Other | 876710 | 6 | 295 | 1770 | 0.0010801 | 0.00036614
2012-09-13 | 225:13446 | URBAN | Other | 876714 | 1 | 817.5833 | 817.5833 | 0.00049891 | 6.1023e-05
2012-09-14 | ZN2466:PA20 | URBAN | Operational Error | 876763 | 4 | 178 | 712 | 0.00043422 | 0.00024394
2012-09-14 | 238:34141 | SHORT RURAL | Equipment Failure | 876765 | 1 | 240.1833 | 240.1833 | 0.00014648 | 6.0986e-05
2012-09-14 | ZN1850:PA10 | URBAN | Equipment Failure | 876822 | 1 | 207 | 207 | 0.00012624 | 6.0986e-05
2012-09-13 | ZN9118:PA17 | URBAN | Vegetation | 876827 | 18 | 15 | 270 | 0.00016476 | 0.0010984
2012-09-13 | 264:81240 | SHORT RURAL | Vegetation | 876884 | 2659 | 1293.7833 | 130055 | 0.079363 | 0.16226
2012-09-13 | 510:48164 | SHORT RURAL | Weather | 876940 | 603 | 1033 | 490690 | 0.29943 | 0.036797
2012-09-14 | 229:34989 | SHORT RURAL | Equipment Failure | 876942 | 1818 | 523 | 138114 | 0.08423 | 0.11087
2012-09-14 | ZN188:PA33 | URBAN | Equipment Failure | 876993 | 60 | 56 | 3360 | 0.0020491 | 0.0036591
2012-09-13 | 803:74013 | SHORT RURAL | Other | 877010 | 103 | 137 | 14111 | 0.0086109 | 0.0062854
2012-09-14 | ZN188:PA32 | URBAN | Other | 877022 | 1 | 49.4833 | 49.4833 | 3.0178e-05 | 6.0986e-05
2012-09-14 | ZN1164:PA23 | URBAN | Other | 877036 | 6 | 201 | 1206 | 0.00073549 | 0.00036591
2012-09-14 | 260:33353 | URBAN | Other | 877043 | 1 | 140.5667 | 140.5667 | 8.5726e-05 | 6.0986e-05
2012-09-14 | ZN3154:PA13 | URBAN | Vegetation | 877092 | 50 | 10 | 500 | 0.00030493 | 0.0030493
2012-09-14 | ZN12570:PA1 | SHORT RURAL | Other | 877103 | 1 | 1177.5 | 1177.5 | 0.00071811 | 6.0986e-05
2012-09-14 | ZN1164:PA21 | URBAN | Equipment Failure | 877116 | 33 | 138.9833 | 4586.45 | 0.0027971 | 0.0020125
2012-09-14 | 258:80784 | URBAN | Other | 877118 | 1 | 104.75 | 104.75 | 6.3883e-05 | 6.0986e-05
2012-09-14 | ZN10999:PA11 | URBAN | Equipment Failure | 877145 | 9 | 617.8833 | 5560.95 | 0.0033914 | 0.00054887
2012-09-15 | 802:82215 | SHORT RURAL | Third Party Impacts | 877150 | 6 | 137.9833 | 827.9 | 0.0005049 | 0.00036591
2012-09-15 | 264:81244 | URBAN | Other | 877185 | 1 | 416.05 | 416.05 | 0.00025373 | 6.0986e-05
2012-09-15 | ZN15010:PA1 | URBAN | Equipment Failure | 877190 | 1 | 243.0167 | 243.0167 | 0.00014821 | 6.0986e-05
2012-09-15 | ZN12580:PA4 | URBAN | Other | 877224 | 1 | 149.45 | 149.45 | 9.1143e-05 | 6.0986e-05
2012-09-15 | ZN965:PA24 | SHORT RURAL | Other | 877234 | 1 | 347.95 | 347.95 | 0.0002122 | 6.0986e-05
2012-09-15 | ZN398:PA16 | URBAN | Equipment Failure | 877268 | 148 | 84 | 12432 | 0.0075817 | 0.0090259
2012-09-16 | ZN12690:PA6 | URBAN | Equipment Failure | 877293 | 644 | 66 | 42504 | 0.025921 | 0.039275
2012-09-16 | ZN4545:PA31 | URBAN | Animals | 877302 | 123 | 169 | 20787 | 0.012677 | 0.0075012
2012-09-16 | ZN180:PA34 | URBAN | Equipment Failure | 877307 | 24 | 286.9333 | 6886.4 | 0.0041997 | 0.0014637
2012-09-16 | ZN10994:PA8 | URBAN | Animals | 877317 | 1 | 1416.3667 | 1416.3667 | 0.00086378 | 6.0986e-05
2012-09-16 | ZN3154:PA10 | URBAN | Equipment Failure | 877360 | 935 | 64 | 59840 | 0.036494 | 0.057022
2012-09-16 | ZN342:PA18 | URBAN | Equipment Failure | 877396 | 183 | 1688 | 133417 | 0.081365 | 0.01116
2012-09-16 | ZN342:PA26 | URBAN | Equipment Failure | 877396 | 101 | 1688 | 18483 | 0.011272 | 0.0061596
2012-09-16 | ZN931:PA2 | URBAN | Equipment Failure | 877396 | 10 | 1688 | 16880 | 0.010294 | 0.00060986
2012-09-16 | 202:34254 | URBAN | Other | 877401 | 1 | 278.4167 | 278.4167 | 0.00016979 | 6.0986e-05
2012-09-16 | ZN1850:PA11 | URBAN | Equipment Failure | 877416 | 1 | 230.5667 | 230.5667 | 0.00014061 | 6.0986e-05
2012-09-17 | 510:48164 | SHORT RURAL | Animals | 877420 | 2 | 103 | 206 | 0.00012563 | 0.00012197
2012-09-17 | ZN3922:PA12 | URBAN | Equipment Failure | 877424 | 1 | 251.4333 | 251.4333 | 0.00015334 | 6.0986e-05
2012-09-14 | 524:33572 | SHORT RURAL | Other | 877449 | 1 | 74 | 74 | 4.5129e-05 | 6.0986e-05
2012-09-17 | 510:48164 | SHORT RURAL | Equipment Failure | 877569 | 2 | 372 | 744 | 0.00045373 | 0.00012197
2012-09-17 | 803:74013 | SHORT RURAL | Equipment Failure | 877649 | 1 | 70.2833 | 70.2833 | 4.2863e-05 | 6.0986e-05
2012-09-17 | ZN2196:PA18 | URBAN | Equipment Failure | 877685 | 1 | 15.9 | 15.9 | 9.6967e-06 | 6.0986e-05
2012-09-17 | ZN1673:PA18 | URBAN | Other | 877721 | 28 | 78.5 | 2198 | 0.0013405 | 0.0017076
2012-09-17 | 523:33501 | SHORT RURAL | Other | 877740 | 3 | 126 | 378 | 0.00023053 | 0.00018296
2012-09-17 | ZN15013:PA6 | SHORT RURAL | Equipment Failure | 877750 | 1 | 264.3667 | 264.3667 | 0.00016123 | 6.0986e-05
2012-09-17 | 520:48172 | SHORT RURAL | Equipment Failure | 877772 | 55 | 107 | 5242 | 0.0031969 | 0.0033542
2012-09-17 | ZN15010:PA1 | URBAN | Other | 877787 | 1 | 147.85 | 147.85 | 9.0167e-05 | 6.0986e-05
2012-09-17 | ZN263:PA31 32GHJ | CBD | Other | 877847 | 42 | 101 | 4242 | 0.002587 | 0.0025614
2012-09-17 | 509:48039 | LONG RURAL | Other | 877873 | 3 | 172 | 516 | 0.00031469 | 0.00018296
2012-09-17 | 524:33576 | SHORT RURAL | Other | 877875 | 47 | 94 | 4350 | 0.0026529 | 0.0028663
2012-09-17 | 515:35197 | LONG RURAL | Other | 877878 | 10 | 173 | 1730 | 0.0010551 | 0.00060986
2012-09-17 | 526:34640 | SHORT RURAL | Equipment Failure | 877879 | 253 | 685 | 32077 | 0.019562 | 0.015429
2012-09-17 | 515:35197 | LONG RURAL | Other | 877881 | 23 | 148 | 3404 | 0.002076 | 0.0014027
2012-09-17 | 504:48031 | SHORT RURAL | Other | 877884 | 4 | 538 | 2152 | 0.0013124 | 0.00024394
2012-09-17 | 235:2123 | URBAN | Other | 877885 | 1 | 133.45 | 133.45 | 8.1385e-05 | 6.0986e-05
2012-09-17 | 811:74234 | SHORT RURAL | Other | 877886 | 2 | 112.45 | 216.7667 | 0.0001322 | 0.00012197
2012-09-17 | 515:35192 | SHORT RURAL | Operational Error | 877888 | 18 | 211 | 3798 | 0.0023162 | 0.0010977
2012-09-17 | 520:48172 | SHORT RURAL | Other | 877893 | 4 | 916.3667 | 3665.4667 | 0.0022354 | 0.00024394
2012-09-17 | 504:48026 | SHORT RURAL | Equipment Failure | 877894 | 4 | 251 | 1004 | 0.0006123 | 0.00024394
2012-09-17 | 524:33576 | SHORT RURAL | Other | 877901 | 4 | 333 | 1332 | 0.00081233 | 0.00024394
2012-09-17 | ZN12600:PA5 | URBAN | Equipment Failure | 877903 | 93 | 62 | 5596 | 0.0034128 | 0.0056717
2012-09-17 | ZN12600:PA13 | SHORT RURAL | Weather | 877904 | 3 | 106 | 318 | 0.00019393 | 0.00018296
2012-09-17 | 258:80775 | URBAN | Other | 877908 | 1 | 94.35 | 94.35 | 5.754e-05 | 6.0986e-05
2012-09-17 | ZN12620:PA3 | URBAN | Equipment Failure | 877916 | 1 | 224.1 | 224.1 | 0.00013667 | 6.0986e-05
2012-09-17 | 504:48031 | SHORT RURAL | Other | 877918 | 2 | 497 | 994 | 0.0006062 | 0.00012197
2012-09-17 | ZN12600:PA1 | SHORT RURAL | Other | 877919 | 1 | 807.45 | 807.45 | 0.00049243 | 6.0986e-05
2012-09-17 | ZN12570:PA35 | URBAN | Equipment Failure | 877922 | 2571 | 972 | 231338 | 0.14108 | 0.15679
2012-09-17 | 243:80083 | SHORT RURAL | Equipment Failure | 877923 | 1 | 63 | 63 | 3.8421e-05 | 6.0986e-05
2012-09-18 | 509:48040 | SHORT RURAL | Other | 877929 | 1 | 327.4167 | 327.4167 | 0.00019959 | 6.0958e-05
2012-09-18 | ZN398:PA20 | URBAN | Equipment Failure | 877930 | 1652 | 231 | 241749 | 0.14737 | 0.1007
2012-09-18 | ZN15014:PA19 | URBAN | Equipment Failure | 877938 | 1 | 95.7833 | 95.7833 | 5.8388e-05 | 6.0958e-05
2012-09-18 | ZN965:PA38 | URBAN | Other | 877939 | 31 | 253.9333 | 7871.9333 | 0.0047986 | 0.0018897
2012-09-18 | ZN398:PA16 | URBAN | Equipment Failure | 877940 | 2039 | 22 | 44858 | 0.027345 | 0.12429
2012-09-18 | ZN14144:PA4 | URBAN | Vegetation | 877949 | 62 | 254 | 15748 | 0.0095997 | 0.0037794
2012-09-18 | ZN9245:PA8 | SHORT RURAL | Animals | 877950 | 10 | 178 | 1780 | 0.0010851 | 0.00060958
2012-09-18 | 504:48031 | SHORT RURAL | Other | 877952 | 1 | 134 | 134 | 8.1684e-05 | 6.0958e-05
2012-09-18 | ZN15014:PA22 | URBAN | Equipment Failure | 877955 | 91 | 99 | 9009 | 0.0054917 | 0.0055472
2012-09-18 | ZN1673:PA13 | URBAN | Other | 877961 | 1 | 72.6 | 72.6 | 4.4256e-05 | 6.0958e-05
2012-09-18 | 504:48031 | SHORT RURAL | Equipment Failure | 877967 | 1 | 839 | 839 | 0.00051144 | 6.0958e-05
2012-09-18 | 509:48039 | LONG RURAL | Equipment Failure | 877968 | 32 | 468.35 | 13934.9333 | 0.0084945 | 0.0019507
2012-09-18 | 524:33572 | SHORT RURAL | Equipment Failure | 877968 | 1 | 468.35 | 269.65 | 0.00016437 | 6.0958e-05
2012-09-18 | 515:35200 | URBAN | Weather | 877975 | 1 | 190.8667 | 190.8667 | 0.00011635 | 6.0958e-05
2012-09-18 | 509:48040 | SHORT RURAL | Other | 878009 | 2 | 30 | 60 | 3.6575e-05 | 0.00012192
2012-09-17 | ZN2310:PA28 | URBAN | Other | 878012 | 163 | 241 | 39283 | 0.023957 | 0.0099407
2012-09-18 | 515:35192 | SHORT RURAL | Equipment Failure | 878013 | 11 | 190 | 2090 | 0.001274 | 0.00067054
2012-09-18 | ZN2466:PA5 | URBAN | Other | 878061 | 1 | 231.6 | 231.6 | 0.00014118 | 6.0958e-05
2012-09-18 | 509:48040 | SHORT RURAL | Equipment Failure | 878158 | 2 | 452 | 790.0833 | 0.00048162 | 0.00012192
2012-09-18 | 515:35192 | SHORT RURAL | Weather | 878189 | 1 | 214.6667 | 214.6667 | 0.00013086 | 6.0958e-05
2012-09-17 | 515:35197 | LONG RURAL | Other | 878217 | 3 | 489 | 1467 | 0.00089466 | 0.00018296
2012-09-17 | 515:35197 | LONG RURAL | Other | 878218 | 175 | 173 | 30275 | 0.018463 | 0.010672
2012-09-18 | 205:12205 | URBAN | Other | 878238 | 1 | 72.2333 | 72.2333 | 4.4032e-05 | 6.0958e-05
2012-09-18 | ZN1193:PA28 | URBAN | Third Party Impacts | 878266 | 1 | 223.8167 | 223.8167 | 0.00013643 | 6.0958e-05
2012-09-18 | 526:34636 | SHORT RURAL | Equipment Failure | 878268 | 1 | 1110 | 1110 | 0.00067664 | 6.0958e-05
2012-09-18 | ZN36300:PA11 | URBAN | Equipment Failure | 878276 | 1 | 181.1833 | 181.1833 | 0.00011045 | 6.0958e-05
2012-09-18 | 503:48017 | URBAN | Other | 878337 | 20 | 132.65 | 2653 | 0.0016172 | 0.0012192
2012-09-18 | ZN2835:PA23 | URBAN | Equipment Failure | 878446 | 1964 | 346 | 312590 | 0.19055 | 0.11972
2012-09-18 | ZN2835:PA9 | URBAN | Equipment Failure | 878446 | 369 | 346 | 66774 | 0.040704 | 0.022494
2012-09-18 | 524:33576 | SHORT RURAL | Equipment Failure | 878452 | 94 | 190 | 4280 | 0.002609 | 0.0057301
2012-09-18 | ZN12590:PA1 | SHORT RURAL | Weather | 878456 | 105 | 89 | 9345 | 0.0056965 | 0.0064006
2012-09-18 | ZN12590:PA2 | URBAN | Weather | 878456 | 1507 | 89 | 134123 | 0.081759 | 0.091864
2012-09-18 | ZN12590:PA3 | SHORT RURAL | Weather | 878456 | 1503 | 89 | 133767 | 0.081542 | 0.09162
2012-09-18 | ZN12590:PA4 | URBAN | Weather | 878456 | 605 | 89 | 53845 | 0.032823 | 0.03688
2012-09-18 | ZN12590:PA6 | SHORT RURAL | Weather | 878456 | 1348 | 89 | 119972 | 0.073133 | 0.082172
2012-09-18 | ZN12590:PA7 | SHORT RURAL | Weather | 878456 | 2233 | 89 | 198737 | 0.12115 | 0.13612
2012-09-18 | 801:74121 | SHORT RURAL | Other | 878474 | 9 | 35.55 | 319.95 | 0.00019504 | 0.00054862
2012-09-18 | 507:80925 | SHORT RURAL | Other | 878480 | 1 | 182.4833 | 182.4833 | 0.00011124 | 6.0958e-05
2012-09-18 | ZN72:PA31 | URBAN | Other | 878481 | 193 | 72.9 | 13986.4 | 0.0085258 | 0.011765
2012-09-18 | 526:34641 | SHORT RURAL | Other | 878486 | 6 | 231 | 1386 | 0.00084488 | 0.00036575
2012-09-18 | 501:48123 | SHORT RURAL | Other | 878490 | 1 | 242 | 242 | 0.00014752 | 6.0958e-05
2012-09-18 | ZN10993:PA5 | URBAN | Weather | 878492 | 1 | 66.2167 | 66.2167 | 4.0364e-05 | 6.0958e-05
2012-09-18 | 238:34141 | SHORT RURAL | Other | 878496 | 1 | 507 | 507 | 0.00030906 | 6.0958e-05
2012-09-18 | ZN15006:PA13 | URBAN | Equipment Failure | 878502 | 1 | 64.5833 | 64.5833 | 3.9369e-05 | 6.0958e-05
2012-09-18 | 526:34641 | SHORT RURAL | Other | 878504 | 1 | 274 | 274 | 0.00016703 | 6.0958e-05
2012-09-18 | 526:34641 | SHORT RURAL | Other | 878506 | 6 | 238 | 1428 | 0.00087048 | 0.00036575
2012-09-18 | ZN847:PA18 | URBAN | Weather | 878508 | 43 | 81.9333 | 3523.1333 | 0.0021476 | 0.0026212
2012-09-18 | 526:34640 | SHORT RURAL | Other | 878516 | 19 | 226 | 4294 | 0.0026175 | 0.0011582
2012-09-18 | ZN10999:PA10 | URBAN | Other | 878518 | 1 | 296.3667 | 296.3667 | 0.00018066 | 6.0958e-05
2012-09-18 | 524:33572 | SHORT RURAL | Equipment Failure | 878522 | 1698 | 129 | 189788 | 0.11569 | 0.10351
2012-09-19 | 514:18137 | SHORT RURAL | Equipment Failure | 878553 | 51 | 675 | 12963 | 0.007902 | 0.0031089
2012-09-19 | 504:48031 | SHORT RURAL | Equipment Failure | 878555 | 6 | 113 | 678 | 0.0004133 | 0.00036575
2012-09-19 | 260:33344 | URBAN | Other | 878558 | 1 | 202.45 | 202.45 | 0.00012341 | 6.0958e-05
2012-09-19 | 504:48031 | SHORT RURAL | Other | 878560 | 48 | 2 | 96 | 5.852e-05 | 0.002926
2012-09-19 | 813:89061 | LONG RURAL | Equipment Failure | 878570 | 2 | 362.5833 | 717.2333 | 0.00043721 | 0.00012192
2012-09-19 | 526:34640 | SHORT RURAL | Equipment Failure | 878582 | 4 | 621.1667 | 2402.8333 | 0.0014647 | 0.00024383
2012-09-19 | ZN965:PA21 | URBAN | Third Party Impacts | 878583 | 1 | 130 | 130 | 7.9246e-05 | 6.0958e-05
2012-09-19 | ZN965:PA35 | URBAN | Third Party Impacts | 878583 | 901 | 130 | 90029 | 0.05488 | 0.054923
2012-09-19 | 512:48047 | SHORT RURAL | Animals | 878589 | 1 | 271 | 271 | 0.0001652 | 6.0958e-05
2012-09-19 | ZN12600:PA11 | URBAN | Other | 878608 | 22 | 327.2667 | 7199.8667 | 0.0043889 | 0.0013411
2012-09-18 | ZN3472:PA29 | URBAN | Equipment Failure | 878620 | 2 | 305 | 610 | 0.00037184 | 0.00012192
2012-09-19 | 504:48028 | URBAN | Equipment Failure | 878634 | 135 | 196 | 26460 | 0.01613 | 0.0082294
2012-09-19 | 526:34641 | SHORT RURAL | Equipment Failure | 878662 | 4 | 279 | 1116 | 0.00068029 | 0.00024383
2012-09-19 | ZN12690:PA10 | URBAN | Vegetation | 878725 | 1 | 94.7 | 94.7 | 5.7727e-05 | 6.0958e-05
2012-09-19 | 524:33570 | SHORT RURAL | Other | 878731 | 1 | 89.6667 | 89.6667 | 5.4659e-05 | 6.0958e-05
2012-09-19 | ZN2602:PA20 | URBAN | Equipment Failure | 878758 | 1 | 329.8167 | 329.8167 | 0.00020105 | 6.0958e-05
2012-09-19 | ZN1788:PA36 | URBAN | Equipment Failure | 878864 | 646 | 43 | 26113 | 0.015918 | 0.039379
2012-09-19 | ZN2310:PA34 | URBAN | Vegetation | 878865 | 1 | 101.65 | 101.65 | 6.1964e-05 | 6.0958e-05
2012-09-19 | ZN1788:PA37 | SHORT RURAL | Equipment Failure | 878871 | 1 | 125.1167 | 125.1167 | 7.6269e-05 | 6.0958e-05
2012-09-19 | ZN1788:PA37 | SHORT RURAL | Equipment Failure | 878875 | 1 | 123.0333 | 123.0333 | 7.4999e-05 | 6.0958e-05
2012-09-18 | ZN630:PA41 | URBAN | Other | 878905 | 79 | 65 | 5135 | 0.0031302 | 0.0048157
2012-09-19 | 216:10726 | URBAN | Other | 878942 | 1 | 150.0833 | 150.0833 | 9.1488e-05 | 6.0958e-05
2012-09-19 | ZN14143:PA17 | SHORT RURAL | Other | 878943 | 1 | 272.3 | 272.3 | 0.00016599 | 6.0958e-05
2012-09-19 | ZN14891:PA5 | SHORT RURAL | Third Party Impacts | 879004 | 80 | 91.7667 | 7341.3333 | 0.0044752 | 0.0048767
2012-09-19 | ZN12630:PA2 | SHORT RURAL | Equipment Failure | 879031 | 2 | 106 | 212 | 0.00012923 | 0.00012192
2012-09-20 | 802:82220 | SHORT RURAL | Animals | 879059 | 2 | 150 | 300 | 0.00018288 | 0.00012192
2012-09-20 | 813:89061 | LONG RURAL | Other | 879115 | 1 | 450.5833 | 450.5833 | 0.00027467 | 6.096e-05
2012-09-20 | 243:80074 | URBAN | Equipment Failure | 879121 | 79 | 310.9 | 20625.9667 | 0.012574 | 0.0048158
2012-09-20 | 511:29876 | SHORT RURAL | Equipment Failure | 879196 | 12 | 305 | 3660 | 0.0022311 | 0.00073152
2012-09-20 | 229:34983 | SHORT RURAL | Third Party Impacts | 879204 | 29 | 283.5833 | 8223.9167 | 0.0050133 | 0.0017678
2012-09-20 | 507:80932 | SHORT RURAL | Other | 879214 | 1 | 77.3333 | 77.3333 | 4.7142e-05 | 6.096e-05
2012-09-20 | 803:74013 | SHORT RURAL | Equipment Failure | 879284 | 1 | 71.2667 | 71.2667 | 4.3444e-05 | 6.096e-05
2012-09-20 | ZN9035:PA11 | URBAN | Third Party Impacts | 879324 | 1 | 61.3 | 61.3 | 3.7368e-05 | 6.096e-05
2012-09-20 | ZN630:PA33 | URBAN | Third Party Impacts | 879431 | 2 | 352 | 704 | 0.00042916 | 0.00012192
2012-09-20 | 810:74062 | SHORT RURAL | Other | 879451 | 1 | 195.75 | 195.75 | 0.00011933 | 6.096e-05
2012-09-20 | 504:48031 | SHORT RURAL | Other | 879461 | 1 | 73 | 73 | 4.4501e-05 | 6.096e-05
2012-09-21 | ZN15005:PA10 | URBAN | Animals | 879492 | 771 | 263.5833 | 90207 | 0.054989 | 0.046999
2012-09-21 | ZN15005:PA12 | URBAN | Animals | 879492 | 1442 | 263.5833 | 168714 | 0.10285 | 0.087902
2012-09-21 | ZN15005:PA2 | URBAN | Animals | 879492 | 1902 | 263.5833 | 222534 | 0.13565 | 0.11594
2012-09-21 | ZN15005:PA4 | URBAN | Animals | 879492 | 1108 | 263.5833 | 129636 | 0.079024 | 0.067542
2012-09-21 | ZN15005:PA6 | URBAN | Animals | 879492 | 1366 | 263.5833 | 159822 | 0.097425 | 0.083269
2012-09-21 | ZN15005:PA8 | URBAN | Animals | 879492 | 1536 | 263.5833 | 179712 | 0.10955 | 0.093632
2012-09-21 | ZN2310:PA21 | URBAN | Third Party Impacts | 879494 | 41 | 65 | 2665 | 0.0016245 | 0.0024993
2012-09-21 | 206:34432 | URBAN | Equipment Failure | 879496 | 56 | 100.2167 | 5612.1333 | 0.0034211 | 0.0034137
2012-09-21 | 507:80917 | URBAN | Third Party Impacts | 879526 | 1 | 205.25 | 205.25 | 0.00012512 | 6.0959e-05
2012-09-21 | 229:34983 | SHORT RURAL | Equipment Failure | 879603 | 19 | 212 | 4028 | 0.0024554 | 0.0011582
2012-09-21 | ZN398:PA3 | URBAN | Third Party Impacts | 879660 | 107 | 61.2667 | 6555.5333 | 0.0039962 | 0.0065226
2012-09-21 | 256:80646 | URBAN | Other | 879669 | 1 | 45.5833 | 45.5833 | 2.7787e-05 | 6.0959e-05
2012-09-21 | ZN874:PA17 | URBAN | Other | 879681 | 1 | 189.2667 | 189.2667 | 0.00011537 | 6.0959e-05
2012-09-21 | 206:34434 | URBAN | Vegetation | 879695 | 1 | 135.35 | 135.35 | 8.2507e-05 | 6.0959e-05
2012-09-21 | ZN398:PA3 | URBAN | Equipment Failure | 879740 | 1 | 4.1833 | 4.1833 | 2.5501e-06 | 6.0959e-05
2012-09-21 | 227:13020 | SHORT RURAL | Vegetation | 879799 | 1 | 91.2 | 91.2 | 5.5594e-05 | 6.0959e-05
2012-09-21 | ZN12660:PA5 | SHORT RURAL | Vegetation | 879810 | 1 | 143.1833 | 143.1833 | 8.7283e-05 | 6.0959e-05
2012-09-21 | 264:81240 | SHORT RURAL | Equipment Failure | 879814 | 6 | 710 | 4260 | 0.0025968 | 0.00036575
2012-09-21 | 503:48011 | SHORT RURAL | Other | 879833 | 52 | 32 | 1664 | 0.0010144 | 0.0031698
2012-09-21 | ZN9252:PA12 | URBAN | Equipment Failure | 879855 | 1 | 166.0167 | 166.0167 | 0.0001012 | 6.0959e-05
2012-09-21 | 503:48011 | SHORT RURAL | Other | 879864 | 1 | 37.0167 | 37.0167 | 2.2565e-05 | 6.0959e-05
2012-09-21 | 503:48011 | SHORT RURAL | Other | 879870 | 1 | 75.8333 | 75.8333 | 4.6227e-05 | 6.0959e-05
2012-09-21 | 504:48031 | SHORT RURAL | Other | 879873 | 1 | 78 | 78 | 4.7548e-05 | 6.0959e-05
2012-09-22 | 243:80075 | SHORT RURAL | Other | 879879 | 3 | 70 | 210 | 0.00012801 | 0.00018288
2012-09-21 | 228:7487 | URBAN | Other | 879882 | 1 | 67.4333 | 67.4333 | 4.1106e-05 | 6.0959e-05
2012-09-22 | ZN14143:PA17 | SHORT RURAL | Animals | 879885 | 5 | 572 | 2860 | 0.0017434 | 0.00030479
2012-09-22 | 227:13019 | SHORT RURAL | Other | 879888 | 1 | 93.9 | 93.9 | 5.724e-05 | 6.0959e-05
2012-09-22 | 813:89061 | LONG RURAL | Equipment Failure | 879889 | 113 | 803 | 15065 | 0.0091834 | 0.0068883
2012-09-22 | ZN630:PA9 | URBAN | Equipment Failure | 879977 | 79 | 67 | 4153 | 0.0025316 | 0.0048157
2012-09-22 | 510:48164 | SHORT RURAL | Equipment Failure | 879983 | 284 | 120 | 34080 | 0.020775 | 0.017312
2012-09-22 | 264:81240 | SHORT RURAL | Other | 880006 | 1 | 82.55 | 82.55 | 5.0321e-05 | 6.0959e-05
2012-09-23 | ZN12640:PA10 | URBAN | Animals | 880012 | 98 | 86 | 8428 | 0.0051376 | 0.0059739
2012-09-23 | ZN2568:PA42 | URBAN | Third Party Impacts | 880017 | 58 | 224 | 12992 | 0.0079197 | 0.0035356
2012-09-23 | ZN262:PA34 | URBAN | Third Party Impacts | 880017 | 15 | 224 | 2925 | 0.001783 | 0.00091438
2012-09-23 | ZN15002:PA6 | URBAN | Third Party Impacts | 880018 | 37 | 86 | 3182 | 0.0019397 | 0.0022555
2012-09-23 | ZN15010:PA11 | URBAN | Vegetation | 880081 | 49 | 71.4833 | 3502.6833 | 0.0021352 | 0.002987
2012-09-23 | ZN12630:PA3 | SHORT RURAL | Equipment Failure | 880085 | 4 | 142 | 568 | 0.00034624 | 0.00024383
2012-09-23 | ZN874:PA17 | URBAN | Other | 880089 | 20 | 76 | 1520 | 0.00092657 | 0.0012192
2012-09-23 | ZN9118:PA21 | URBAN | Equipment Failure | 880095 | 44 | 127.65 | 5616.6 | 0.0034238 | 0.0026822
2012-09-23 | 504:48026 | SHORT RURAL | Equipment Failure | 880118 | 2 | 223 | 446 | 0.00027188 | 0.00012192
2012-09-24 | ZN874:PA4 | URBAN | Third Party Impacts | 880127 | 127 | 325 | 41275 | 0.025161 | 0.0077417
2012-09-24 | ZN5868:PA2 | URBAN | Equipment Failure | 880177 | 1 | 264.7333 | 264.7333 | 0.00016138 | 6.0959e-05
2012-09-24 | ZN3288:PA41 42DEF | CBD | Other | 880201 | 9 | 350 | 3150 | 0.0019202 | 0.00054863
2012-09-24 | ZN2635:PA12 | SHORT RURAL | Equipment Failure | 880261 | 1 | 503.05 | 503.05 | 0.00030665 | 6.0959e-05
2012-09-24 | ZN14144:PA5 | SHORT RURAL | Equipment Failure | 880291 | 28 | 104 | 2912 | 0.0017751 | 0.0017068
2012-09-24 | ZN14144:PA8 | URBAN | Equipment Failure | 880291 | 1 | 104 | 104 | 6.3397e-05 | 6.0959e-05
2012-09-24 | ZN116:PA44 | URBAN | Equipment Failure | 880305 | 2 | 70 | 130 | 7.9246e-05 | 0.00012192
2012-09-24 | ZN116:PA47 | URBAN | Equipment Failure | 880305 | 1294 | 70 | 87220 | 0.053168 | 0.07888
2012-09-24 | 513:48056 | SHORT RURAL | Equipment Failure | 880331 | 3 | 474 | 1422 | 0.00086683 | 0.00018288
2012-09-24 | ZN7481:PA1 | URBAN | Equipment Failure | 880395 | 1 | 210 | 210 | 0.00012801 | 6.0959e-05
2012-09-24 | ZN7481:PA19 | URBAN | Equipment Failure | 880395 | 145 | 210 | 15370 | 0.0093693 | 0.008839
2012-08-23 | ZN4545:PA31 | URBAN | Vegetation | 880468 | 98 | 501 | 49098 | 0.029998 | 0.0059877
2012-09-24 | 811:74234 | SHORT RURAL | Equipment Failure | 880471 | 3 | 110 | 330 | 0.00020116 | 0.00018288
2012-08-03 | ZN12620:PA11 | SHORT RURAL | Equipment Failure | 880473 | 264 | 103 | 27192 | 0.016614 | 0.01613
2012-09-24 | 813:89061 | LONG RURAL | Other | 880513 | 1 | 164.6667 | 164.6667 | 0.00010038 | 6.0959e-05
2012-09-24 | ZN10999:PA24 | URBAN | Third Party Impacts | 880518 | 1 | 120.45 | 120.45 | 7.3425e-05 | 6.0959e-05
2012-09-24 | ZN10999:PA24 | URBAN | Third Party Impacts | 880545 | 1 | 103.05 | 103.05 | 6.2818e-05 | 6.0959e-05
2012-09-24 | 232:33413 | SHORT RURAL | Operational Error | 880577 | 26 | 490 | 12740 | 0.0077661 | 0.0015849
2012-09-24 | ZN15014:PA11 | URBAN | Other | 880643 | 1 | 569.2 | 569.2 | 0.00034698 | 6.0959e-05
2012-09-25 | ZN129:PA11 | URBAN | Other | 880645 | 108 | 67 | 7236 | 0.00441 | 0.0065821
2012-09-25 | ZN129:PA12 | URBAN | Other | 880645 | 1295 | 67 | 86765 | 0.052879 | 0.078924
2012-09-25 | ZN129:PA16 | URBAN | Other | 880645 | 1260 | 67 | 84420 | 0.05145 | 0.076791
2012-09-25 | ZN129:PA18 | URBAN | Other | 880645 | 883 | 67 | 59161 | 0.036056 | 0.053814
2012-09-25 | ZN129:PA19 | URBAN | Other | 880645 | 1722 | 67 | 115374 | 0.070315 | 0.10495
2012-09-25 | ZN129:PA2 | URBAN | Other | 880645 | 857 | 67 | 57419 | 0.034994 | 0.05223
2012-09-25 | ZN129:PA21 | URBAN | Other | 880645 | 677 | 67 | 45359 | 0.027644 | 0.04126
2012-09-25 | ZN129:PA24 | URBAN | Other | 880645 | 1220 | 67 | 81740 | 0.049816 | 0.074353
2012-09-25 | ZN129:PA25 | URBAN | Other | 880645 | 95 | 67 | 6365 | 0.0038792 | 0.0057898
2012-09-25 | ZN129:PA27 | URBAN | Other | 880645 | 194 | 67 | 12998 | 0.0079216 | 0.011823
2012-09-25 | ZN129:PA28 | URBAN | Other | 880645 | 1287 | 67 | 86229 | 0.052552 | 0.078436
2012-09-25 | ZN129:PA3 | URBAN | Other | 880645 | 1411 | 67 | 94537 | 0.057616 | 0.085993
2012-09-25 | ZN129:PA4 | URBAN | Other | 880645 | 405 | 67 | 27135 | 0.016537 | 0.024683
2012-09-25 | ZN129:PA5 | URBAN | Other | 880645 | 896 | 67 | 60032 | 0.036587 | 0.054607
2012-09-25 | ZN129:PA8 | URBAN | Other | 880645 | 1108 | 67 | 74236 | 0.045243 | 0.067527
2012-09-25 | ZN129:PA9 | URBAN | Other | 880645 | 1096 | 67 | 73432 | 0.044753 | 0.066796
2012-09-25 | ZN9252:PA7 | URBAN | Animals | 880648 | 582 | 63 | 36666 | 0.022346 | 0.03547
2012-09-25 | ZN35500:PA31 | URBAN | Other | 880650 | 1 | 67 | 67 | 4.0833e-05 | 6.0945e-05
2012-09-25 | ZN269:PA1 | URBAN | Other | 880652 | 1 | 796.85 | 796.85 | 0.00048564 | 6.0945e-05
2012-09-25 | 515:35193 | SHORT RURAL | Equipment Failure | 880665 | 1 | 166 | 166 | 0.00010117 | 6.0945e-05
2012-09-25 | 516:48067 | SHORT RURAL | Other | 880667 | 1 | 99 | 99 | 6.0336e-05 | 6.0945e-05
2012-09-24 | 235:2857 | SHORT RURAL | Other | 880673 | 1 | 190 | 190 | 0.00011582 | 6.0959e-05
2012-09-25 | ZN188:PA33 | URBAN | Equipment Failure | 880775 | 60 | 39 | 2340 | 0.0014261 | 0.0036567
2012-09-25 | 234:14291 | URBAN | Other | 880831 | 141 | 89.0667 | 12558.4 | 0.0076537 | 0.0085933
2012-09-25 | 801:74123 | SHORT RURAL | Other | 881003 | 54 | 30.95 | 1671.3 | 0.0010186 | 0.003291
2012-09-25 | ZN35800:PA7 | URBAN | Other | 881019 | 16 | 48.45 | 775.2 | 0.00047245 | 0.00097512
2012-09-25 | ZN10999:PA24 | URBAN | Third Party Impacts | 881024 | 1 | 299.25 | 299.25 | 0.00018238 | 6.0945e-05
2012-09-25 | 222:2017 | URBAN | Animals | 881069 | 90 | 59.5667 | 5361 | 0.0032673 | 0.0054851
2012-09-26 | ZN15014:PA11 | URBAN | Animals | 881086 | 965 | 55 | 53075 | 0.032347 | 0.058812
2012-09-26 | ZN15014:PA20 | URBAN | Animals | 881086 | 1 | 55 | 55 | 3.352e-05 | 6.0945e-05
2012-09-26 | ZN2310:PA33 | URBAN | Third Party Impacts | 881088 | 1 | 430.9667 | 430.9667 | 0.00026265 | 6.0945e-05
2012-09-26 | 504:48028 | URBAN | Other | 881089 | 135 | 75.6833 | 10217.25 | 0.0062269 | 0.0082276
2012-09-26 | 509:48040 | SHORT RURAL | Equipment Failure | 881092 | 97 | 310 | 30070 | 0.018326 | 0.0059117
2012-09-26 | 513:48050 | SHORT RURAL | Animals | 881117 | 3 | 70 | 210 | 0.00012799 | 0.00018284
2012-09-26 | ZN10990:PA1 | URBAN | Other | 881131 | 1 | 95.8167 | 95.8167 | 5.8396e-05 | 6.0945e-05
2012-09-26 | ZN12570:PA33 | SHORT RURAL | Other | 881202 | 1 | 245.2667 | 245.2667 | 0.00014948 | 6.0945e-05
2012-09-26 | 223:14397 | URBAN | Other | 881231 | 1 | 146.9 | 146.9 | 8.9529e-05 | 6.0945e-05
2012-09-26 | 515:35197 | LONG RURAL | Other | 881262 | 1 | 118.1667 | 118.1667 | 7.2017e-05 | 6.0945e-05
2012-09-26 | 243:80084 | SHORT RURAL | Other | 881359 | 1 | 243.2167 | 243.2167 | 0.00014823 | 6.0945e-05
2012-09-26 | ZN1285:PA29 | URBAN | Equipment Failure | 881449 | 1 | 109 | 109 | 6.643e-05 | 6.0945e-05
2012-09-26 | ZN263:PA31 32GHJ | CBD | Equipment Failure | 881510 | 42 | 199 | 8358 | 0.0050938 | 0.0025597
2012-09-27 | 264:81240 | SHORT RURAL | Other | 881520 | 12 | 143 | 1716 | 0.0010458 | 0.00073134
2012-09-27 | ZN15009:PA11 | URBAN | Third Party Impacts | 881521 | 147 | 575 | 49600.3333 | 0.030229 | 0.008959
2012-09-27 | 813:89061 | LONG RURAL | Other | 881531 | 1 | 116.9167 | 116.9167 | 7.1255e-05 | 6.0945e-05
2012-09-26 | 231:8405 | SHORT RURAL | Equipment Failure | 881539 | 1 | 120 | 120 | 7.3134e-05 | 6.0945e-05
2012-09-27 | 205:12210 | URBAN | Other | 881623 | 1 | 51.2 | 51.2 | 3.1204e-05 | 6.0945e-05
2012-09-27 | ZN12620:PA11 | SHORT RURAL | Vegetation | 881736 | 1 | 78.4167 | 78.4167 | 4.7791e-05 | 6.0945e-05
2012-09-27 | ZN12630:PA4 | SHORT RURAL | Other | 881754 | 272 | 169 | 16708 | 0.010183 | 0.016577
2012-09-27 | 523:33501 | SHORT RURAL | Other | 881768 | 1 | 161.9667 | 161.9667 | 9.8711e-05 | 6.0945e-05
2012-09-27 | 813:89061 | LONG RURAL | Other | 881797 | 1 | 100.75 | 100.75 | 6.1402e-05 | 6.0945e-05
2012-09-27 | ZN15009:PA11 | URBAN | Equipment Failure | 881798 | 1 | 421.1167 | 421.1167 | 0.00025665 | 6.0945e-05
2012-09-27 | ZN195:PA29 | URBAN | Other | 881820 | 1 | 204.1167 | 204.1167 | 0.0001244 | 6.0945e-05
2012-09-27 | 513:48051 | URBAN | Other | 881892 | 28 | 78.1333 | 2187.7333 | 0.0013333 | 0.0017065
2012-09-27 | ZN690:PA15 | URBAN | Equipment Failure | 881902 | 11 | 156 | 1716 | 0.0010458 | 0.0006704
2012-09-27 | ZN2310:PA17 | URBAN | Vegetation | 881920 | 1 | 586.8833 | 586.8833 | 0.00035768 | 6.0945e-05
2012-09-28 | ZN847:PA22 | SHORT RURAL | Animals | 881924 | 60 | 70 | 4200 | 0.0025597 | 0.0036567
2012-09-28 | ZN15010:PA7 | URBAN | Equipment Failure | 881927 | 1 | 477.6667 | 477.6667 | 0.00029112 | 6.0945e-05
2012-09-28 | ZN965:PA15 | URBAN | Vegetation | 881929 | 80 | 496 | 39680 | 0.024183 | 0.0048756
2012-09-28 | ZN965:PA33 | URBAN | Vegetation | 881929 | 22 | 496 | 10912 | 0.0066504 | 0.0013408
2012-09-28 | 511:29878 | SHORT RURAL | Other | 881933 | 2 | 179 | 358 | 0.00021818 | 0.00012189
2012-09-27 | 240:34843 | URBAN | Other | 881992 | 2 | 20 | 40 | 2.4378e-05 | 0.00012189
2012-09-28 | ZN10993:PA13 | URBAN | Vegetation | 881999 | 81 | 97.6167 | 7906.95 | 0.0048189 | 0.0049366
2012-09-28 | ZN116:PA42 | URBAN | Vegetation | 882038 | 71 | 82.6667 | 5869.3333 | 0.0035771 | 0.0043271
2012-09-28 | ZN15012:PA4 | URBAN | Third Party Impacts | 882069 | 1 | 77 | 77 | 4.6928e-05 | 6.0945e-05
2012-09-28 | 264:81240 | SHORT RURAL | Equipment Failure | 882077 | 26 | 63 | 1638 | 0.00099829 | 0.0015846
2012-09-28 | ZN847:PA18 | URBAN | Weather | 882137 | 42 | 183.15 | 7692.3 | 0.0046881 | 0.0025597
2012-09-28 | ZN15012:PA8 | URBAN | Third Party Impacts | 882139 | 1151 | 487 | 57272 | 0.034905 | 0.070148
2012-09-28 | ZN12640:PA2 | URBAN | Equipment Failure | 882149 | 111 | 55.3833 | 6147.55 | 0.0037467 | 0.0067649
2012-09-28 | ZN80:PA37 | URBAN | Equipment Failure | 882154 | 1 | 382.8833 | 382.8833 | 0.00023335 | 6.0945e-05
2012-09-28 | ZN12640:PA19 | URBAN | Equipment Failure | 882158 | 145 | 80.4667 | 11667.6667 | 0.0071109 | 0.0088371
2012-09-28 | ZN1285:PA27 | URBAN | Third Party Impacts | 882162 | 59 | 58 | 3422 | 0.0020856 | 0.0035958
2012-09-28 | 227:13020 | SHORT RURAL | Other | 882169 | 17 | 200 | 3400 | 0.0020721 | 0.0010361
2012-09-28 | ZN35800:PA21 | URBAN | Other | 882182 | 37 | 80 | 2960 | 0.001804 | 0.002255
2012-09-28 | ZN15002:PA6 | URBAN | Equipment Failure | 882188 | 1 | 175 | 139 | 8.4714e-05 | 6.0945e-05
2012-09-28 | ZN15002:PA8 | URBAN | Equipment Failure | 882188 | 809 | 175 | 105350 | 0.064206 | 0.049305
2012-09-28 | 515:35197 | LONG RURAL | Animals | 882194 | 1 | 78 | 78 | 4.7537e-05 | 6.0945e-05
2012-09-28 | ZN180:PA18 | URBAN | Other | 882214 | 104 | 125.95 | 13098.8 | 0.0079831 | 0.0063383
2012-09-28 | ZN14144:PA8 | URBAN | Equipment Failure | 882238 | 1 | 304.4 | 304.4 | 0.00018552 | 6.0945e-05
2012-09-28 | ZN12640:PA10 | URBAN | Other | 882242 | 1 | 48.4167 | 48.4167 | 2.9508e-05 | 6.0945e-05
2012-09-28 | ZN1648:PA21 | URBAN | Other | 882255 | 1 | 821.0167 | 821.0167 | 0.00050037 | 6.0945e-05
2012-09-28 | 507:80922 | SHORT RURAL | Equipment Failure | 882274 | 5 | 246 | 1230 | 0.00074963 | 0.00030473
2012-09-28 | 256:80640 | URBAN | Equipment Failure | 882283 | 1 | 107.5 | 107.5 | 6.5516e-05 | 6.0945e-05
2012-09-28 | ZN12570:PA9 | SHORT RURAL | Vegetation | 882288 | 1059 | 30 | 31770 | 0.019362 | 0.064541
2012-09-28 | 507:80923 | SHORT RURAL | Equipment Failure | 882300 | 40 | 65 | 2600 | 0.0015846 | 0.0024378
2012-09-28 | ZN2835:PA21 | URBAN | Equipment Failure | 882303 | 222 | 47 | 10434 | 0.006359 | 0.01353
2012-09-28 | ZN2835:PA30 | URBAN | Equipment Failure | 882303 | 1 | 47 | 47 | 2.8644e-05 | 6.0945e-05
2012-09-28 | ZN1068:PA26 | URBAN | Equipment Failure | 882316 | 126 | 222.9333 | 28089.6 | 0.017119 | 0.0076791
2012-09-28 | 231:8415 | SHORT RURAL | Animals | 882327 | 3 | 94 | 282 | 0.00017187 | 0.00018284
2012-09-28 | ZN9700:PA23 | URBAN | Vegetation | 882328 | 54 | 276 | 14904 | 0.0090833 | 0.0032911
2012-09-28 | ZN9245:PA14 | URBAN | Other | 882331 | 1 | 963.6333 | 963.6333 | 0.00058729 | 6.0945e-05
2012-09-28 | ZN9550:PA31 | URBAN | Other | 882343 | 1 | 1300.3 | 1300.3 | 0.00079247 | 6.0945e-05
2012-09-28 | ZN12610:PA22 | URBAN | Third Party Impacts | 882346 | 185 | 81.6167 | 15099.0833 | 0.0092022 | 0.011275
2012-09-28 | ZN15008:PA7 | URBAN | Equipment Failure | 882349 | 1 | 92.8167 | 92.8167 | 5.6568e-05 | 6.0945e-05
2012-09-29 | ZN9252:PA10 | URBAN | Vegetation | 882356 | 1 | 792.2 | 792.2 | 0.00048281 | 6.0945e-05
2012-09-29 | 524:33576 | SHORT RURAL | Third Party Impacts | 882365 | 47 | 451 | 11283 | 0.0068765 | 0.0028644
2012-09-29 | 524:33576 | SHORT RURAL | Other | 882367 | 1 | 131.05 | 131.05 | 7.9869e-05 | 6.0945e-05
2012-09-29 | ZN12690:PA12 | SHORT RURAL | Other | 882369 | 1 | 177.05 | 177.05 | 0.0001079 | 6.0945e-05
2012-09-29 | ZN12590:PA3 | SHORT RURAL | Other | 882377 | 7 | 287 | 2009 | 0.0012244 | 0.00042662
2012-09-29 | ZN269:PA7 | URBAN | Other | 882378 | 104 | 105.65 | 10987.6 | 0.0066964 | 0.0063383
2012-09-29 | ZN1068:PA26 | URBAN | Other | 882379 | 1 | 60.05 | 60.05 | 3.6598e-05 | 6.0945e-05
2012-09-29 | ZN1068:PA26 | URBAN | Other | 882389 | 1 | 47.5 | 47.5 | 2.8949e-05 | 6.0945e-05
2012-09-29 | ZN9301:PA15 | SHORT RURAL | Other | 882398 | 1 | 187.25 | 187.25 | 0.00011412 | 6.0945e-05
2012-09-29 | 507:80925 | SHORT RURAL | Vegetation | 882434 | 24 | 56 | 1344 | 0.00081911 | 0.0014627
2012-09-29 | ZN12590:PA3 | SHORT RURAL | Other | 882441 | 1 | 61.9333 | 61.9333 | 3.7746e-05 | 6.0945e-05
2012-09-29 | 513:48056 | SHORT RURAL | Equipment Failure | 882450 | 2 | 64 | 128 | 7.801e-05 | 0.00012189
2012-09-29 | 224:80346 | URBAN | Other | 882455 | 1 | 43.9667 | 43.9667 | 2.6796e-05 | 6.0945e-05
2012-09-29 | 511:29878 | SHORT RURAL | Equipment Failure | 882458 | 216 | 412 | 32411 | 0.019753 | 0.013164
2012-09-29 | ZN847:PA18 | URBAN | Vegetation | 882462 | 79 | 186 | 7849 | 0.0047836 | 0.0048147
2012-09-29 | ZN14892:PA6 | SHORT RURAL | Other | 882463 | 1 | 166.3167 | 166.3167 | 0.00010136 | 6.0945e-05
2012-09-29 | 515:35192 | SHORT RURAL | Other | 882464 | 1 | 139 | 139 | 8.4714e-05 | 6.0945e-05
2012-09-29 | 227:13015 | SHORT RURAL | Vegetation | 882468 | 1 | 133.2667 | 133.2667 | 8.122e-05 | 6.0945e-05
2012-09-29 | 509:48039 | LONG RURAL | Equipment Failure | 882472 | 1133 | 119 | 128927 | 0.078575 | 0.069051
2012-09-29 | 509:48040 | SHORT RURAL | Equipment Failure | 882472 | 148 | 119 | 16040 | 0.0097756 | 0.0090199
2012-09-29 | ZN12690:PA16 | SHORT RURAL | Other | 882486 | 1 | 258.1333 | 258.1333 | 0.00015732 | 6.0945e-05
2012-09-29 | 507:80917 | URBAN | Equipment Failure | 882488 | 96 | 135 | 12960 | 0.0078985 | 0.0058508
2012-09-29 | ZN9700:PA23 | URBAN | Vegetation | 882492 | 79 | 158.3167 | 12507.0167 | 0.0076225 | 0.0048147
2012-09-29 | ZN2310:PA16 | URBAN | Other | 882509 | 1 | 111.05 | 111.05 | 6.768e-05 | 6.0945e-05
2012-09-29 | ZN12650:PA12 | URBAN | Other | 882513 | 1 | 103.5167 | 70.3833 | 4.2895e-05 | 6.0945e-05
2012-09-29 | ZN12650:PA17 | URBAN | Other | 882513 | 2346 | 103.5167 | 136112 | 0.082954 | 0.14298
2012-09-29 | ZN12650:PA5 | URBAN | Other | 882513 | 1 | 103.5167 | 40 | 2.4378e-05 | 6.0945e-05
2012-09-29 | ZN12650:PA9 | URBAN | Other | 882513 | 3 | 103.5167 | 211.8167 | 0.00012909 | 0.00018284
2012-09-29 | 806:74080 | SHORT RURAL | Other | 882525 | 1 | 184.7 | 184.7 | 0.00011257 | 6.0945e-05
2012-09-29 | ZN4545:PA17 | URBAN | Other | 882531 | 1 | 48.6333 | 48.6333 | 2.964e-05 | 6.0945e-05
2012-09-29 | ZN12610:PA18 | URBAN | Third Party Impacts | 882536 | 11 | 154 | 1694 | 0.0010324 | 0.0006704
2012-09-30 | ZN4545:PA36 | URBAN | Equipment Failure | 882546 | 82 | 133.6 | 10955.2 | 0.0066767 | 0.0049975
2012-09-30 | ZN263:PA33 34KLM | CBD | Other | 882552 | 38 | 55.7667 | 2119.1333 | 0.0012915 | 0.0023159
2012-09-30 | 238:34141 | SHORT RURAL | Other | 882577 | 1 | 126.2833 | 126.2833 | 7.6964e-05 | 6.0945e-05
2012-09-30 | ZN630:PA24 | URBAN | Other | 882606 | 10 | 111 | 1110 | 0.00067649 | 0.00060945
2012-09-30 | 232:11454 | SHORT RURAL | Equipment Failure | 882607 | 1 | 127.7333 | 127.7333 | 7.7848e-05 | 6.0945e-05
2012-09-30 | ZN15005:PA12 | URBAN | Vegetation | 882609 | 21 | 91.0833 | 1912.75 | 0.0011657 | 0.0012799
2012-09-30 | ZN398:PA19 | URBAN | Equipment Failure | 882647 | 1 | 185.9 | 185.9 | 0.0001133 | 6.0945e-05
2012-09-30 | ZN15011:PA2 | URBAN | Equipment Failure | 882648 | 857 | 34 | 29138 | 0.017758 | 0.05223
2012-09-30 | ZN340:PA27 | URBAN | Third Party Impacts | 882664 | 1 | 339.8167 | 339.8167 | 0.0002071 | 6.0945e-05
2012-10-01 | 812:19071 | SHORT RURAL | Third Party Impacts | 882665 | 71 | 296 | 21016 | 0.012808 | 0.0043271
2012-10-01 | 513:48059 | SHORT RURAL | Equipment Failure | 882674 | 7 | 217 | 1519 | 0.00092576 | 0.00042662
2012-10-01 | 501:48115 | SHORT RURAL | Other | 882691 | 1 | 148.9667 | 148.9667 | 9.0788e-05 | 6.0945e-05
2012-10-01 | 504:48029 | URBAN | Other | 882704 | 1 | 70.2333 | 70.2333 | 4.2804e-05 | 6.0945e-05
2012-10-01 | ZN340:PA2 | URBAN | Other | 882708 | 1 | 174.55 | 174.55 | 0.00010638 | 6.0945e-05
2012-10-01 | 511:29877 | SHORT RURAL | Other | 882722 | 15 | 45.6833 | 685.25 | 0.00041763 | 0.00091418
2012-10-01 | 208:72 | URBAN | Other | 882749 | 40 | 57.3833 | 2120 | 0.001292 | 0.0024378
2012-10-01 | 256:80652 | URBAN | Other | 882749 | 2 | 57.3833 | 112.45 | 6.8533e-05 | 0.00012189
2012-10-01 | ZN10994:PA14 | URBAN | Equipment Failure | 882766 | 1 | 77 | 67 | 4.0833e-05 | 6.0945e-05
2012-10-01 | ZN10994:PA20 | URBAN | Equipment Failure | 882766 | 2303 | 77 | 170331 | 0.10381 | 0.14036
2012-10-01 | ZN4545:PA25 | URBAN | Equipment Failure | 882768 | 2 | 146 | 292 | 0.00017796 | 0.00012189
2012-10-01 | ZN4545:PA27 | URBAN | Equipment Failure | 882768 | 70 | 146 | 10203.6667 | 0.0062187 | 0.0042662
2012-10-01 | 812:19066 | SHORT RURAL | Equipment Failure | 882778 | 1 | 31.3333 | 31.3333 | 1.9096e-05 | 6.0945e-05
2012-10-01 | ZN15012:PA6 | URBAN | Vegetation | 882782 | 1 | 323.05 | 323.05 | 0.00019688 | 6.0945e-05
2012-10-01 | ZN72:PA10 | URBAN | Other | 882793 | 75 | 83 | 6187.05 | 0.0037707 | 0.0045709
2012-10-01 | ZN35500:PA27 | URBAN | Animals | 882797 | 46 | 201 | 3818 | 0.0023269 | 0.0028035
2012-10-01 | ZN35500:PA28 | URBAN | Animals | 882797 | 3063 | 201 | 159689 | 0.097323 | 0.18668
2012-10-01 | ZN35500:PA34 | URBAN | Animals | 882797 | 161 | 201 | 23725 | 0.014459 | 0.0098122
2012-10-01 | ZN4545:PA4 | URBAN | Equipment Failure | 882801 | 2 | 310 | 620 | 0.00037786 | 0.00012189
2012-10-01 | ZN35500:PA34 | URBAN | Other | 882821 | 1 | 349.9833 | 349.9833 | 0.0002133 | 6.0945e-05
2012-10-01 | ZN12640:PA7 | URBAN | Other | 882824 | 1623 | 69 | 111987 | 0.068251 | 0.098914
2012-10-01 | ZN35500:PA34 | URBAN | Other | 882835 | 97 | 262 | 25414 | 0.015489 | 0.0059117
2012-10-01 | ZN12650:PA13 | SHORT RURAL | Other | 882841 | 68 | 105.4833 | 7172.8667 | 0.0043715 | 0.0041443
2012-10-02 | ZN35500:PA28 | URBAN | Other | 882844 | 148 | 39 | 5772 | 0.003517 | 0.0090179
2012-10-02 | 812:19071 | SHORT RURAL | Animals | 882849 | 1 | 259.3333 | 259.3333 | 0.00015802 | 6.0931e-05
2012-09-30 | 243:80083 | SHORT RURAL | Third Party Impacts | 882880 | 2 | 270 | 540 | 0.00032911 | 0.00012189
2012-10-02 | ZN14891:PA10 | SHORT RURAL | Other | 882899 | 1 | 377.4833 | 377.4833 | 0.00023001 | 6.0931e-05
2012-10-02 | ZN901:PA10 | URBAN | Other | 882988 | 52 | 187 | 9724 | 0.005925 | 0.0031684
2012-10-02 | ZN35500:PA34 | URBAN | Other | 883041 | 1 | 195.8 | 195.8 | 0.0001193 | 6.0931e-05
2012-10-02 | 807:74184 | SHORT RURAL | Equipment Failure | 883081 | 1 | 69.35 | 69.35 | 4.2256e-05 | 6.0931e-05
2012-10-02 | 225:33676 | SHORT RURAL | Other | 883087 | 1 | 95.4333 | 95.4333 | 5.8149e-05 | 6.0931e-05
2012-09-28 | 516:48067 | SHORT RURAL | Other | 883139 | 5 | 50 | 250 | 0.00015236 | 0.00030473
2012-10-02 | 511:29878 | SHORT RURAL | Other | 883178 | 1 | 165.6667 | 165.6667 | 0.00010094 | 6.0931e-05
2012-09-29 | 511:29878 | SHORT RURAL | Operational Error | 883207 | 131 | 9 | 1179 | 0.00071855 | 0.0079839
2012-10-02 | ZN3154:PA19 | URBAN | Third Party Impacts | 883243 | 28 | 134.3 | 3760.4 | 0.0022913 | 0.0017061
2012-10-02 | ZN4990:PA55 56GHJ | CBD | Other | 883281 | 1 | 131.5833 | 131.5833 | 8.0176e-05 | 6.0931e-05
2012-10-02 | 502:48010 | SHORT RURAL | Other | 883293 | 83 | 54 | 4482 | 0.0027309 | 0.0050573
2012-10-02 | ZN4990:PA55 56GHJ | CBD | Equipment Failure | 883365 | 1387 | 629 | 809058 | 0.49297 | 0.084512
2012-10-02 | ZN35600:PA14 | URBAN | Other | 883366 | 1 | 1033.25 | 1033.25 | 0.00062957 | 6.0931e-05
2012-10-03 | ZN847:PA5 | URBAN | Other | 883381 | 16 | 450 | 7200 | 0.0043871 | 0.0009749
2012-10-03 | ZN35600:PA14 | URBAN | Other | 883450 | 1 | 397.9167 | 397.9167 | 0.00024246 | 6.0932e-05
2012-10-03 | ZN116:PA50 | URBAN | Vegetation | 883498 | 1 | 116.8333 | 116.8333 | 7.1188e-05 | 6.0932e-05
2012-10-03 | 811:74234 | SHORT RURAL | Operational Error | 883574 | 254 | 18 | 4572 | 0.0027858 | 0.015477
2012-10-03 | 213:33771 | URBAN | Equipment Failure | 883579 | 1513 | 172 | 85344 | 0.052001 | 0.092189
2012-10-03 | ZN12610:PA20 | SHORT RURAL | Other | 883672 | 1 | 75.2833 | 75.2833 | 4.5871e-05 | 6.0932e-05
2012-10-03 | ZN195:PA28 | URBAN | Vegetation | 883743 | 27 | 71.85 | 1939.95 | 0.001182 | 0.0016452
2012-10-03 | ZN15006:PA12 | URBAN | Third Party Impacts | 883763 | 1 | 97.1667 | 97.1667 | 5.9205e-05 | 6.0932e-05
2012-10-03 | ZN9118:PA12 | URBAN | Third Party Impacts | 883767 | 1 | 221.7167 | 221.7167 | 0.0001351 | 6.0932e-05
2012-10-03 | ZN15010:PA5 | URBAN | Other | 883774 | 1 | 249.5667 | 249.5667 | 0.00015206 | 6.0932e-05
2012-10-03 | ZN35500:PA23 | URBAN | Third Party Impacts | 883776 | 24 | 105 | 2520 | 0.0015355 | 0.0014624
2012-10-03 | 807:74184 | SHORT RURAL | Other | 883809 | 1 | 94 | 94 | 5.7276e-05 | 6.0932e-05
2012-10-03 | ZN14892:PA16 | URBAN | Other | 883811 | 1 | 47.0833 | 47.0833 | 2.8689e-05 | 6.0932e-05
2012-10-03 | 515:35192 | SHORT RURAL | Equipment Failure | 883812 | 1 | 137 | 137 | 8.3476e-05 | 6.0932e-05
2012-10-03 | ZN12620:PA1 | SHORT RURAL | Animals | 883828 | 1700 | 186 | 135488 | 0.082555 | 0.10358
2012-10-03 | ZN2196:PA18 | URBAN | Third Party Impacts | 883831 | 1 | 258 | 258 | 0.0001572 | 6.0932e-05
2012-10-04 | ZN2310:PA38 | URBAN | Animals | 883833 | 110 | 119 | 13090 | 0.0079759 | 0.0067025
2012-10-04 | 515:35198 | SHORT RURAL | Equipment Failure | 883852 | 1 | 52.0667 | 52.0667 | 3.1725e-05 | 6.0932e-05
2012-10-03 | 511:29878 | SHORT RURAL | Third Party Impacts | 883873 | 1 | 30 | 30 | 1.8279e-05 | 6.0932e-05
2012-10-04 | ZN2835:PA32 | SHORT RURAL | Other | 883898 | 1 | 205.2 | 205.2 | 0.00012503 | 6.0932e-05
2012-10-03 | ZN269:PA3 | URBAN | Third Party Impacts | 883899 | 74 | 96 | 7104 | 0.0043286 | 0.0045089
2012-10-04 | ZN3154:PA19 | URBAN | Third Party Impacts | 883925 | 28 | 815.7667 | 22841.4667 | 0.013918 | 0.0017061
2012-10-04 | ZN80:PA31 | URBAN | Other | 883948 | 1 | 293.1833 | 293.1833 | 0.00017864 | 6.0932e-05
2012-10-04 | ZN15001:PA11 | URBAN | Third Party Impacts | 884013 | 26 | 82.9333 | 2156.2667 | 0.0013138 | 0.0015842
2012-10-04 | ZN263:PA33 34ABC | CBD | Other | 884043 | 1 | 136.6167 | 136.6167 | 8.3243e-05 | 6.0932e-05
2012-10-04 | ZN965:PA8 | URBAN | Other | 884208 | 5 | 248 | 1240 | 0.00075555 | 0.00030466
2012-10-04 | ZN4545:PA44 | URBAN | Third Party Impacts | 884217 | 163 | 50 | 8150 | 0.0049659 | 0.0099318
2012-10-04 | 509:48040 | SHORT RURAL | Equipment Failure | 884223 | 1 | 101 | 101 | 6.1541e-05 | 6.0932e-05
2012-10-04 | 264:81240 | SHORT RURAL | Other | 884226 | 1 | 123.8833 | 123.8833 | 7.5484e-05 | 6.0932e-05
2012-10-05 | ZN7900:PA12 | URBAN | Third Party Impacts | 884241 | 68 | 65 | 4420 | 0.0026975 | 0.00415
2012-10-05 | ZN9118:PA12 | URBAN | Other | 884249 | 32 | 271.3167 | 8682.1333 | 0.0052986 | 0.0019529
2012-10-02 | ZN4990:PA55 56GHJ | CBD | Equipment Failure | 884267 | 86 | 96 | 8256 | 0.0050305 | 0.0052401
2012-10-05 | ZN12610:PA18 | URBAN | Vegetation | 884271 | 34 | 204 | 6936 | 0.004233 | 0.002075
2012-10-02 | ZN4990:PA55 56GHJ | CBD | Equipment Failure | 884293 | 10 | 5 | 50 | 3.0466e-05 | 0.00060931
2012-10-05 | ZN2835:PA28 | URBAN | Vegetation | 884386 | 1 | 229.3833 | 229.3833 | 0.00013999 | 6.1029e-05
2012-10-05 | ZN2466:PA15 | URBAN | Other | 884408 | 3 | 127 | 381 | 0.00023252 | 0.00018309
2012-10-05 | ZN690:PA4 | URBAN | Other | 884418 | 46 | 87.3333 | 4017.3333 | 0.0024517 | 0.0028073
2012-10-05 | ZN12690:PA22 | URBAN | Other | 884442 | 1 | 114.15 | 114.15 | 6.9664e-05 | 6.1029e-05
2012-10-05 | ZN12570:PA2 | SHORT RURAL | Equipment Failure | 884487 | 1 | 198.7333 | 198.7333 | 0.00012128 | 6.1029e-05
2012-10-05 | 511:29877 | SHORT RURAL | Other | 884497 | 1 | 59.95 | 59.95 | 3.6587e-05 | 6.1029e-05
2012-10-05 | ZN35800:PA21 | URBAN | Third Party Impacts | 884502 | 37 | 76 | 2812 | 0.0017161 | 0.0022581
2012-10-05 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 884506 | 32 | 60 | 1920 | 0.0011718 | 0.0019529
2012-10-05 | ZN4545:PA25 | URBAN | Animals | 884550 | 113 | 52 | 5876 | 0.003586 | 0.0068962
2012-10-05 | ZN187:PA10 | URBAN | Other | 884566 | 26 | 177 | 4602 | 0.0028085 | 0.0015867
2012-10-05 | ZN187:PA4 | URBAN | Other | 884566 | 87 | 177 | 10179 | 0.0062121 | 0.0053095
2012-10-06 | 230:81434 | URBAN | Other | 884579 | 1 | 77.5 | 77.5 | 4.7297e-05 | 6.1029e-05
2012-10-06 | ZN195:PA22 | URBAN | Equipment Failure | 884592 | 521 | 59 | 26770 | 0.016337 | 0.031796
2012-10-06 | ZN12600:PA11 | URBAN | Other | 884597 | 1 | 274.6 | 274.6 | 0.00016758 | 6.1029e-05
2012-10-06 | ZN14144:PA10 | SHORT RURAL | Vegetation | 884606 | 14 | 214.05 | 2996.7 | 0.0018288 | 0.0008544
2012-10-06 | 507:80922 | SHORT RURAL | Other | 884607 | 1 | 73.5167 | 73.5167 | 4.4866e-05 | 6.1029e-05
2012-10-06 | ZN36300:PA17 | URBAN | Other | 884608 | 1 | 567.5 | 567.5 | 0.00034634 | 6.1029e-05
2012-10-06 | ZN9035:PA11 | URBAN | Other | 884628 | 1 | 127.05 | 127.05 | 7.7537e-05 | 6.1029e-05
2012-10-06 | ZN12620:PA1 | SHORT RURAL | Equipment Failure | 884632 | 1 | 262.9667 | 262.9667 | 0.00016049 | 6.1029e-05
2012-10-06 | 501:48118 | SHORT RURAL | Equipment Failure | 884636 | 49 | 20 | 980 | 0.00059808 | 0.0029904
2012-10-06 | ZN3155:PA23 | URBAN | Equipment Failure | 884638 | 2312 | 54 | 113178 | 0.069071 | 0.1411
2012-10-06 | ZN3155:PA34 | SHORT RURAL | Equipment Failure | 884638 | 65 | 54 | 3120 | 0.0019041 | 0.0039669
2012-10-06 | ZN965:PA15 | URBAN | Vegetation | 884666 | 1221 | 50 | 61050 | 0.037258 | 0.074516
2012-10-06 | ZN965:PA3 | URBAN | Vegetation | 884666 | 29 | 50 | 1450 | 0.00088492 | 0.0017698
2012-10-06 | ZN1673:PA19 | URBAN | Vegetation | 884684 | 46 | 104 | 4784 | 0.0029196 | 0.0028073
2012-10-06 | ZN1673:PA7 | URBAN | Vegetation | 884688 | 55 | 50 | 2750 | 0.0016783 | 0.0033566
2012-10-06 | ZN2568:PA42 | URBAN | Equipment Failure | 884703 | 40 | 127 | 5000 | 0.0030514 | 0.0024411
2012-10-06 | ZN262:PA13 | URBAN | Equipment Failure | 884703 | 21 | 127 | 2667 | 0.0016276 | 0.0012816
2012-10-06 | ZN262:PA14 | URBAN | Equipment Failure | 884703 | 19 | 127 | 2413 | 0.0014726 | 0.0011595
2012-10-06 | ZN262:PA15 | URBAN | Equipment Failure | 884703 | 2121 | 127 | 269367 | 0.16439 | 0.12944
2012-10-06 | ZN262:PA16 | URBAN | Equipment Failure | 884703 | 1883 | 127 | 239141 | 0.14594 | 0.11492
2012-10-06 | ZN262:PA17 | URBAN | Equipment Failure | 884703 | 1596 | 127 | 202692 | 0.1237 | 0.097402
2012-10-06 | ZN262:PA19 | URBAN | Equipment Failure | 884703 | 2198 | 127 | 279146 | 0.17036 | 0.13414
2012-10-06 | ZN262:PA20 | URBAN | Equipment Failure | 884703 | 612 | 127 | 77724 | 0.047434 | 0.03735
2012-10-06 | ZN262:PA21 | URBAN | Equipment Failure | 884703 | 127 | 127 | 16129 | 0.0098433 | 0.0077506
2012-10-06 | ZN262:PA25 | URBAN | Equipment Failure | 884703 | 144 | 127 | 18000 | 0.010985 | 0.0087881
2012-10-06 | ZN262:PA26 | URBAN | Equipment Failure | 884703 | 250 | 127 | 31250 | 0.019071 | 0.015257
2012-10-06 | ZN262:PA27 | URBAN | Equipment Failure | 884703 | 1082 | 127 | 135250 | 0.082541 | 0.066033
2012-10-06 | ZN262:PA28 | URBAN | Equipment Failure | 884703 | 152 | 127 | 19000 | 0.011595 | 0.0092764
2012-10-06 | ZN262:PA29 | URBAN | Equipment Failure | 884703 | 413 | 127 | 51625 | 0.031506 | 0.025205
2012-10-06 | ZN262:PA30 | URBAN | Equipment Failure | 884703 | 2043 | 127 | 255375 | 0.15585 | 0.12468
2012-10-06 | ZN262:PA31 | URBAN | Equipment Failure | 884703 | 1472 | 127 | 184000 | 0.11229 | 0.089834
2012-10-06 | ZN262:PA32 | URBAN | Equipment Failure | 884703 | 795 | 127 | 99375 | 0.060647 | 0.048518
2012-10-06 | ZN262:PA33 | URBAN | Equipment Failure | 884703 | 173 | 127 | 21625 | 0.013197 | 0.010558
2012-10-06 | ZN262:PA34 | URBAN | Equipment Failure | 884703 | 452 | 127 | 56500 | 0.034481 | 0.027585
2012-10-06 | ZN262:PA39 | URBAN | Equipment Failure | 884703 | 734 | 127 | 91750 | 0.055994 | 0.044795
2012-10-06 | ZN262:PA40 | URBAN | Equipment Failure | 884703 | 519 | 127 | 64875 | 0.039592 | 0.031674
2012-10-06 | ZN262:PA41 | URBAN | Equipment Failure | 884703 | 1046 | 127 | 130750 | 0.079795 | 0.063836
2012-10-06 | ZN262:PA42 | URBAN | Equipment Failure | 884703 | 2036 | 127 | 254500 | 0.15532 | 0.12425
2012-10-06 | ZN262:PA5 | URBAN | Equipment Failure | 884703 | 1494 | 127 | 189738 | 0.11579 | 0.091177
2012-10-06 | ZN262:PA6 | URBAN | Equipment Failure | 884703 | 1280 | 127 | 162560 | 0.099208 | 0.078117
2012-10-06 | ZN262:PA7 | URBAN | Equipment Failure | 884703 | 2089 | 127 | 265303 | 0.16191 | 0.12749
2012-10-06 | ZN262:PA8 | URBAN | Equipment Failure | 884703 | 116 | 127 | 14694 | 0.0089676 | 0.0070793
2012-10-06 | ZN398:PA24 | URBAN | Equipment Failure | 884703 | 122 | 127 | 15250 | 0.0093069 | 0.0074455
2012-10-06 | ZN9700:PA11 | URBAN | Other | 884715 | 1 | 184.2833 | 184.2833 | 0.00011247 | 6.1029e-05
2012-10-06 | ZN14891:PA12 | SHORT RURAL | Animals | 884717 | 8 | 248 | 1984 | 0.0012108 | 0.00048823
2012-10-06 | ZN3472:PA22 | URBAN | Other | 884725 | 1 | 681.5667 | 681.5667 | 0.00041595 | 6.1029e-05
2012-10-07 | 813:89061 | LONG RURAL | Equipment Failure | 884741 | 13 | 264.7167 | 3441.3167 | 0.0021002 | 0.00079337
2012-10-07 | ZN3922:PA10 | URBAN | Other | 884742 | 1 | 248.9833 | 248.9833 | 0.00015195 | 6.1029e-05
2012-10-07 | ZN2400:PA23 | URBAN | Vegetation | 884744 | 1 | 441.25 | 441.25 | 0.00026929 | 6.1029e-05
2012-10-07 | 515:35193 | SHORT RURAL | Equipment Failure | 884792 | 117 | 144 | 16848 | 0.010282 | 0.0071404
2012-10-07 | 243:80080 | SHORT RURAL | Other | 884803 | 4 | 268 | 1072 | 0.00065423 | 0.00024411
2012-10-07 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 884816 | 1 | 246.1833 | 246.1833 | 0.00015024 | 6.1029e-05
2012-10-07 | 258:80784 | URBAN | Other | 884823 | 1 | 91.2333 | 91.2333 | 5.5679e-05 | 6.1029e-05
2012-10-07 | ZN12610:PA13 | URBAN | Equipment Failure | 884854 | 1952 | 71 | 135817 | 0.082887 | 0.11913
2012-10-07 | ZN12610:PA22 | URBAN | Equipment Failure | 884854 | 184 | 71 | 13064 | 0.0079728 | 0.011229
2012-10-07 | ZN12610:PA13 | URBAN | Other | 884868 | 1 | 521.8 | 521.8 | 0.00031845 | 6.1029e-05
2012-10-07 | ZN35500:PA32 | URBAN | Other | 884869 | 63 | 782.1 | 49272.3 | 0.03007 | 0.0038448
2012-10-08 | 524:33570 | SHORT RURAL | Equipment Failure | 884873 | 1 | 78.4 | 78.4 | 4.7847e-05 | 6.1029e-05
2012-10-08 | ZN15008:PA7 | URBAN | Equipment Failure | 884878 | 72 | 115.6167 | 8324.4 | 0.0050803 | 0.0043941
2012-10-08 | ZN1788:PA21 | URBAN | Third Party Impacts | 884895 | 33 | 75 | 2400 | 0.0014647 | 0.0020139
2012-10-08 | 526:34636 | SHORT RURAL | Other | 884966 | 2 | 146 | 292 | 0.0001782 | 0.00012206
2012-10-08 | 240:34835 | URBAN | Equipment Failure | 884973 | 1 | 99.1 | 99.1 | 6.0479e-05 | 6.1029e-05
2012-10-08 | ZN965:PA29 | URBAN | Equipment Failure | 884974 | 31 | 75 | 2325 | 0.0014189 | 0.0018919
2012-10-05 | 515:35192 | SHORT RURAL | Equipment Failure | 884991 | 1 | 165 | 165 | 0.0001007 | 6.1029e-05
2012-10-08 | ZN3425:PA32 | URBAN | Equipment Failure | 885000 | 2 | 88.4 | 176.8 | 0.0001079 | 0.00012206
2012-10-08 | 801:74122 | URBAN | Other | 885016 | 1 | 106.45 | 106.45 | 6.4965e-05 | 6.1029e-05
2012-10-08 | ZN12610:PA16 | URBAN | Other | 885079 | 1 | 72.1333 | 72.1333 | 4.4022e-05 | 6.1029e-05
2012-10-08 | ZN10990:PA12 | URBAN | Equipment Failure | 885145 | 1 | 92.7167 | 92.7167 | 5.6584e-05 | 6.1029e-05
2012-10-06 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 885156 | 2 | 100 | 200 | 0.00012206 | 0.00012206
2012-10-07 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 885165 | 20 | 80 | 1600 | 0.00097646 | 0.0012206
2012-10-08 | 213:33775 | URBAN | Other | 885225 | 1 | 137.8 | 137.8 | 8.4098e-05 | 6.1029e-05
2012-10-08 | 213:33775 | URBAN | Other | 885275 | 1 | 87.0833 | 87.0833 | 5.3146e-05 | 6.1029e-05
2012-10-08 | ZN3155:PA32 | URBAN | Other | 885309 | 33 | 186 | 6138 | 0.0037459 | 0.0020139
2012-10-08 | ZN15014:PA19 | URBAN | Equipment Failure | 885364 | 1 | 273.45 | 273.45 | 0.00016688 | 6.1029e-05
2012-10-08 | 235:2123 | URBAN | Other | 885368 | 1 | 85.2167 | 85.2167 | 5.2007e-05 | 6.1029e-05
2012-10-08 | 801:74118 | URBAN | Other | 885369 | 1 | 97.9833 | 97.9833 | 5.9798e-05 | 6.1029e-05
2012-10-08 | 811:74234 | SHORT RURAL | Equipment Failure | 885389 | 5 | 170 | 850 | 0.00051874 | 0.00030514
2012-10-08 | ZN847:PA44 | URBAN | Third Party Impacts | 885415 | 74 | 65.4333 | 4842.0667 | 0.0029551 | 0.0045161
2012-10-08 | ZN2635:PA21 | URBAN | Equipment Failure | 885426 | 79 | 69.0333 | 5453.6333 | 0.0033283 | 0.0048213
2012-10-09 | ZN9118:PA8 | URBAN | Other | 885431 | 1 | 607.3167 | 607.3167 | 0.00037002 | 6.0927e-05
2012-10-09 | ZN1193:PA25 | URBAN | Other | 885433 | 1 | 350.8667 | 350.8667 | 0.00021377 | 6.0927e-05
2012-10-09 | ZN9118:PA12 | URBAN | Other | 885436 | 1 | 272.1 | 272.1 | 0.00016578 | 6.0927e-05
2012-10-09 | ZN340:PA21 | URBAN | Other | 885439 | 1 | 284.5 | 284.5 | 0.00017334 | 6.0927e-05
2012-10-09 | ZN3155:PA44 | URBAN | Other | 885441 | 53 | 600 | 31800 | 0.019375 | 0.0032291
2012-10-09 | 210:8681 | URBAN | Vegetation | 885479 | 1 | 92.05 | 92.05 | 5.6083e-05 | 6.0927e-05
2012-10-09 | 228:7490 | SHORT RURAL | Equipment Failure | 885531 | 1 | 295 | 295 | 0.00017973 | 6.0927e-05
2012-10-09 | 807:74179 | SHORT RURAL | Equipment Failure | 885697 | 1 | 117.6333 | 117.6333 | 7.167e-05 | 6.0927e-05
2012-10-09 | 231:8415 | SHORT RURAL | Other | 885727 | 3 | 181 | 543 | 0.00033083 | 0.00018278
2012-10-09 | ZN12610:PA22 | URBAN | Vegetation | 885729 | 1 | 87.35 | 87.35 | 5.322e-05 | 6.0927e-05
2012-10-09 | ZN15005:PA8 | URBAN | Other | 885781 | 1538 | 48.85 | 75131.3 | 0.045775 | 0.093706
2012-10-09 | 513:48059 | SHORT RURAL | Equipment Failure | 885794 | 1 | 224.8167 | 224.8167 | 0.00013697 | 6.0927e-05
2012-10-09 | ZN7900:PA6 | URBAN | Equipment Failure | 885795 | 1 | 111.8167 | 111.8167 | 6.8127e-05 | 6.0927e-05
2012-10-09 | ZN12640:PA10 | URBAN | Other | 885796 | 288 | 79 | 22752 | 0.013862 | 0.017547
2012-10-09 | 504:48033 | SHORT RURAL | Animals | 885800 | 1 | 75.9167 | 63.85 | 3.8902e-05 | 6.0927e-05
2012-10-09 | 509:48039 | LONG RURAL | Animals | 885800 | 6 | 75.9167 | 342.7 | 0.0002088 | 0.00036556
2012-10-09 | ZN15005:PA8 | URBAN | Other | 885809 | 1 | 149.6833 | 149.6833 | 9.1198e-05 | 6.0927e-05
2012-10-09 | ZN15005:PA8 | URBAN | Other | 885811 | 1 | 149.2833 | 149.2833 | 9.0954e-05 | 6.0927e-05
2012-10-09 | ZN15005:PA8 | URBAN | Other | 885820 | 1 | 148.85 | 148.85 | 9.069e-05 | 6.0927e-05
2012-10-10 | ZN35600:PA9 | URBAN | Equipment Failure | 885875 | 1 | 167.9167 | 167.9167 | 0.00010231 | 6.0927e-05
2012-10-10 | 224:80341 | URBAN | Other | 885886 | 1 | 117.9 | 117.9 | 7.1833e-05 | 6.0927e-05
2012-10-10 | 801:74123 | SHORT RURAL | Other | 885897 | 1 | 173.6167 | 173.6167 | 0.00010578 | 6.0927e-05
2012-10-10 | 813:89063 | SHORT RURAL | Other | 885943 | 1 | 129.0167 | 129.0167 | 7.8606e-05 | 6.0927e-05
2012-10-10 | 243:80077 | URBAN | Other | 885977 | 245 | 477 | 18297 | 0.011148 | 0.014927
2012-10-10 | 224:80332 | URBAN | Other | 886047 | 1 | 114.6333 | 114.6333 | 6.9843e-05 | 6.0927e-05
2012-10-10 | ZN15001:PA18 | URBAN | Third Party Impacts | 886077 | 1 | 374.65 | 374.65 | 0.00022826 | 6.0927e-05
2012-10-10 | 803:74010 | SHORT RURAL | Other | 886116 | 1 | 111.3833 | 111.3833 | 6.7863e-05 | 6.0927e-05
2012-10-10 | ZN1164:PA15 | URBAN | Other | 886126 | 1 | 135.8833 | 135.8833 | 8.279e-05 | 6.0927e-05
2012-10-10 | 240:34835 | URBAN | Equipment Failure | 886154 | 1 | 2313 | 182.4333 | 0.00011115 | 6.0927e-05
2012-10-10 | 240:34843 | URBAN | Equipment Failure | 886154 | 258 | 2313 | 39570 | 0.024109 | 0.015719
2012-10-10 | 219:1750 | URBAN | Equipment Failure | 886227 | 1 | 112.95 | 112.95 | 6.8817e-05 | 6.0927e-05
2012-10-10 | ZN12620:PA13 | SHORT RURAL | Other | 886253 | 1 | 247.6167 | 247.6167 | 0.00015087 | 6.0927e-05
2012-10-10 | ZN12620:PA13 | SHORT RURAL | Other | 886256 | 1 | 242.8167 | 242.8167 | 0.00014794 | 6.0927e-05
2012-10-10 | 803:74007 | SHORT RURAL | Equipment Failure | 886261 | 1 | 101 | 101 | 6.1536e-05 | 6.0927e-05
2012-10-10 | ZN874:PA16 | URBAN | Equipment Failure | 886313 | 28 | 58 | 1335 | 0.00081338 | 0.001706
2012-10-10 | ZN874:PA23 | URBAN | Equipment Failure | 886313 | 11 | 58 | 451 | 0.00027478 | 0.0006702
2012-10-10 | ZN1068:PA26 | URBAN | Other | 886347 | 1 | 377.2667 | 377.2667 | 0.00022986 | 6.0927e-05
2012-10-10 | ZN14892:PA14 | SHORT RURAL | Other | 886350 | 34 | 43.2667 | 1471.0667 | 0.00089628 | 0.0020715
2012-10-10 | ZN116:PA33 | URBAN | Equipment Failure | 886352 | 1 | 652.45 | 652.45 | 0.00039752 | 6.0927e-05
2012-10-11 | ZN2835:PA30 | URBAN | Equipment Failure | 886355 | 1 | 324.3667 | 324.3667 | 0.00019763 | 6.0927e-05
2012-10-11 | ZN965:PA26 | URBAN | Equipment Failure | 886356 | 1 | 327.8667 | 327.8667 | 0.00019976 | 6.0927e-05
2012-10-11 | ZN847:PA5 | URBAN | Equipment Failure | 886358 | 466 | 323 | 45262 | 0.027577 | 0.028392
2012-10-11 | ZN1290:PA12 | URBAN | Other | 886362 | 1 | 1960.4 | 1960.4 | 0.0011944 | 6.0927e-05
2012-10-11 | ZN1164:PA3 | URBAN | Equipment Failure | 886363 | 1 | 484.1 | 484.1 | 0.00029495 | 6.0927e-05
2012-10-11 | ZN7900:PA6 | URBAN | Equipment Failure | 886364 | 102 | 577.95 | 58950.9 | 0.035917 | 0.0062146
2012-10-11 | ZN1164:PA3 | URBAN | Equipment Failure | 886372 | 1 | 445.4167 | 445.4167 | 0.00027138 | 6.0927e-05
2012-10-11 | ZN9035:PA2 | URBAN | Vegetation | 886379 | 13 | 117 | 1521 | 0.0009267 | 0.00079205
2012-10-11 | ZN9118:PA22 | URBAN | Vegetation | 886379 | 8 | 117 | 936 | 0.00057028 | 0.00048742
2012-10-11 | ZN10996:PA10 | URBAN | Third Party Impacts | 886384 | 1 | 76.8333 | 76.8333 | 4.6812e-05 | 6.0927e-05
2012-10-11 | ZN262:PA7 | URBAN | Other | 886397 | 1 | 342.0833 | 342.0833 | 0.00020842 | 6.0927e-05
2012-10-11 | 509:48039 | LONG RURAL | Animals | 886398 | 2 | 156 | 312 | 0.00019009 | 0.00012185
2012-10-11 | 812:19071 | SHORT RURAL | Equipment Failure | 886412 | 1 | 123.9 | 123.9 | 7.5489e-05 | 6.0927e-05
2012-10-10 | 509:48040 | SHORT RURAL | Equipment Failure | 886493 | 22 | 15 | 330 | 0.00020106 | 0.0013404
2012-10-11 | 264:81240 | SHORT RURAL | Equipment Failure | 886495 | 1 | 300.3333 | 300.3333 | 0.00018298 | 6.0927e-05
2012-10-11 | 502:48010 | SHORT RURAL | Vegetation | 886534 | 1 | 153.1667 | 153.1667 | 9.332e-05 | 6.0927e-05
2012-10-11 | ZN12660:PA10 | SHORT RURAL | Equipment Failure | 886624 | 71 | 143.4167 | 10182.5833 | 0.006204 | 0.0043258
2012-10-11 | 232:33413 | SHORT RURAL | Vegetation | 886664 | 3 | 165 | 495 | 0.00030159 | 0.00018278
2012-10-11 | ZN4545:PA9 | URBAN | Equipment Failure | 886751 | 25 | 70 | 1750 | 0.0010662 | 0.0015232
2012-10-11 | 503:48011 | SHORT RURAL | Equipment Failure | 886776 | 29 | 193 | 5597 | 0.0034101 | 0.0017669
2012-10-11 | ZN12630:PA2 | SHORT RURAL | Equipment Failure | 886848 | 164 | 131 | 21484 | 0.01309 | 0.0099921
2012-10-12 | ZN690:PA28 | URBAN | Other | 886890 | 1 | 168.1833 | 168.1833 | 0.00010247 | 6.0927e-05
2012-10-12 | ZN263:PA31 32GHJ | CBD | Other | 886898 | 42 | 107 | 4494 | 0.0027381 | 0.0025589
2012-10-12 | ZN1193:PA26 | URBAN | Other | 886951 | 1 | 211.45 | 211.45 | 0.00012883 | 6.0927e-05
2012-10-12 | ZN3155:PA19 | URBAN | Vegetation | 886959 | 19 | 85 | 1615 | 0.00098398 | 0.0011576
2012-10-12 | 265:81651 | URBAN | Other | 886984 | 1 | 83.55 | 83.55 | 5.0905e-05 | 6.0927e-05
2012-10-12 | ZN1788:PA37 | SHORT RURAL | Equipment Failure | 887086 | 1 | 220.1833 | 203.5333 | 0.00012401 | 6.0927e-05
2012-10-12 | ZN1788:PA7 | SHORT RURAL | Equipment Failure | 887086 | 204 | 220.1833 | 27336 | 0.016655 | 0.012429
2012-10-12 | ZN15011:PA6 | URBAN | Vegetation | 887118 | 2 | 301.15 | 602.3 | 0.00036696 | 0.00012185
2012-10-12 | 232:11454 | SHORT RURAL | Other | 887123 | 1 | 256.8167 | 256.8167 | 0.00015647 | 6.0927e-05
2012-10-12 | 260:33353 | URBAN | Other | 887147 | 1 | 174.6667 | 174.6667 | 0.00010642 | 6.0927e-05
2012-10-12 | ZN14892:PA6 | SHORT RURAL | Other | 887160 | 1 | 168.8167 | 168.8167 | 0.00010286 | 6.0927e-05
2012-10-11 | ZN10999:PA36 | URBAN | Third Party Impacts | 887195 | 57 | 84 | 4788 | 0.0029172 | 0.0034729
2012-10-12 | ZN2568:PA6 | SHORT RURAL | Equipment Failure | 887197 | 1 | 413.65 | 413.65 | 0.00025203 | 6.0927e-05
2012-10-12 | ZN14891:PA8 | SHORT RURAL | Vegetation | 887202 | 74 | 209 | 8875 | 0.0054073 | 0.0045086
2012-10-12 | ZN3288:PA43 44DEF | CBD | Other | 887215 | 1 | 391.3 | 391.3 | 0.00023841 | 6.0927e-05
2012-10-12 | ZN263:PA31 32GHJ | CBD | Equipment Failure | 887242 | 42 | 314 | 13188 | 0.0080351 | 0.0025589
2012-10-12 | 510:48164 | SHORT RURAL | Equipment Failure | 887248 | 3 | 184.4167 | 534.1667 | 0.00032545 | 0.00018278
2012-10-12 | 507:80923 | SHORT RURAL | Vegetation | 887271 | 2 | 236 | 472 | 0.00028758 | 0.00012185
2012-10-12 | ZN1285:PA17 | SHORT RURAL | Other | 887287 | 12 | 157 | 1884 | 0.0011479 | 0.00073113
2012-10-12 | ZN1285:PA8 | URBAN | Other | 887287 | 9 | 157 | 1413 | 0.0008609 | 0.00054835
2012-10-12 | ZN12600:PA11 | URBAN | Other | 887290 | 1 | 336.5667 | 336.5667 | 0.00020506 | 6.0927e-05
2012-10-12 | ZN14891:PA5 | SHORT RURAL | Other | 887295 | 1 | 227.8 | 227.8 | 0.00013879 | 6.0927e-05
2012-10-12 | ZN10993:PA5 | URBAN | Other | 887301 | 75 | 59.15 | 4436.25 | 0.0027029 | 0.0045695
2012-10-12 | 512:48049 | SHORT RURAL | Other | 887309 | 8 | 103 | 824 | 0.00050204 | 0.00048742
2012-10-12 | 264:81236 | URBAN | Other | 887316 | 1 | 156.9333 | 156.9333 | 9.5615e-05 | 6.0927e-05
2012-10-12 | ZN3672:PA44 | URBAN | Vegetation | 887327 | 90 | 10 | 900 | 0.00054835 | 0.0054835
2012-10-12 | 515:35193 | SHORT RURAL | Equipment Failure | 887328 | 2 | 263 | 525.0833 | 0.00031992 | 0.00012185
2012-10-12 | 228:7487 | URBAN | Other | 887329 | 1 | 814.2333 | 814.2333 | 0.00049609 | 6.0927e-05
2012-10-12 | 214:8670 | URBAN | Other | 887344 | 1 | 209.3833 | 209.3833 | 0.00012757 | 6.0927e-05
2012-10-12 | ZN1164:PA12 | URBAN | Equipment Failure | 887345 | 1 | 297.8167 | 297.8167 | 0.00018145 | 6.0927e-05
2012-10-13 | ZN263:PA31 32GHJ | CBD | Equipment Failure | 887362 | 42 | 852 | 35784 | 0.021802 | 0.0025589
2012-10-13 | 258:80791 | URBAN | Other | 887363 | 1 | 39.4 | 39.4 | 2.4005e-05 | 6.0927e-05
2012-10-13 | 511:29878 | SHORT RURAL | Other | 887372 | 1 | 152.9833 | 152.9833 | 9.3209e-05 | 6.0927e-05
2012-10-13 | ZN3155:PA21 | URBAN | Equipment Failure | 887373 | 7 | 709.45 | 4966.15 | 0.0030257 | 0.00042649
2012-10-13 | ZN15009:PA11 | URBAN | Vegetation | 887376 | 1 | 616.6333 | 616.6333 | 0.0003757 | 6.0927e-05
2012-10-13 | ZN1068:PA26 | URBAN | Equipment Failure | 887393 | 1 | 246.55 | 246.55 | 0.00015022 | 6.0927e-05
2012-10-13 | ZN9550:PA27 | URBAN | Equipment Failure | 887399 | 1 | 380.25 | 380.25 | 0.00023168 | 6.0927e-05
2012-10-13 | 214:8669 | URBAN | Equipment Failure | 887409 | 80 | 30 | 2400 | 0.0014623 | 0.0048742
2012-10-13 | ZN12580:PA4 | URBAN | Other | 887442 | 1 | 188.5833 | 188.5833 | 0.0001149 | 6.0927e-05
2012-10-13 | ZN8000:PA19 | URBAN | Other | 887447 | 45 | 204.9333 | 9222 | 0.0056187 | 0.0027417
2012-10-13 | ZN15011:PA10 | URBAN | Other | 887448 | 1 | 62.9 | 62.9 | 3.8323e-05 | 6.0927e-05
2012-10-13 | ZN12610:PA22 | URBAN | Other | 887452 | 1 | 95.3167 | 95.3167 | 5.8074e-05 | 6.0927e-05
2012-10-14 | ZN4545:PA17 | URBAN | Equipment Failure | 887506 | 127 | 34 | 4318 | 0.0026308 | 0.0077378
2012-10-14 | 227:13020 | SHORT RURAL | Third Party Impacts | 887509 | 1 | 337.2 | 337.2 | 0.00020545 | 6.0927e-05
2012-10-14 | ZN12690:PA19 | URBAN | Animals | 887516 | 1197 | 35 | 41895 | 0.025525 | 0.07293
2012-10-14 | 515:35193 | SHORT RURAL | Other | 887535 | 79 | 54 | 4266 | 0.0025992 | 0.0048133
2012-10-14 | ZN12690:PA19 | URBAN | Vegetation | 887574 | 1 | 83.35 | 83.35 | 5.0783e-05 | 6.0927e-05
2012-10-14 | ZN12640:PA13 | SHORT RURAL | Other | 887606 | 1 | 159.5667 | 159.5667 | 9.722e-05 | 6.0927e-05
2012-10-15 | ZN931:PA13 | URBAN | Equipment Failure | 887612 | 504 | 92 | 46307 | 0.028214 | 0.030707
2012-10-15 | ZN15014:PA19 | URBAN | Equipment Failure | 887616 | 1886 | 86 | 154221 | 0.093963 | 0.11491
2012-10-15 | ZN12630:PA1 | SHORT RURAL | Animals | 887617 | 12 | 95 | 1140 | 0.00069457 | 0.00073113
2012-10-12 | ZN1788:PA7 | SHORT RURAL | Equipment Failure | 887718 | 1 | 134 | 134 | 8.1643e-05 | 6.0927e-05
2012-10-15 | ZN1788:PA36 | URBAN | Equipment Failure | 887726 | 1 | 95.2667 | 95.2667 | 5.8043e-05 | 6.0927e-05
2012-10-12 | 810:74058 | SHORT RURAL | Other | 887750 | 1 | 45 | 45 | 2.7417e-05 | 6.0927e-05
2012-10-15 | ZN80:PA40 | URBAN | Third Party Impacts | 887761 | 1 | 231.65 | 231.65 | 0.00014114 | 6.0927e-05
2012-10-15 | ZN9900:PA13 | URBAN | Equipment Failure | 887794 | 29 | 162.4833 | 4712.0167 | 0.0028709 | 0.0017669
2012-10-15 | ZN2310:PA34 | URBAN | Other | 887819 | 54 | 152.5833 | 8239.5 | 0.0050201 | 0.0032901
2012-10-15 | 510:48164 | SHORT RURAL | Other | 887871 | 1 | 67.65 | 67.65 | 4.1217e-05 | 6.0927e-05
2012-10-11 | 509:48040 | SHORT RURAL | Other | 887873 | 22 | 20 | 440 | 0.00026808 | 0.0013404
2012-10-15 | ZN9550:PA27 | URBAN | Equipment Failure | 887884 | 1 | 148.3333 | 148.3333 | 9.0375e-05 | 6.0927e-05
2012-10-15 | 515:35200 | URBAN | Equipment Failure | 887902 | 1 | 60 | 60 | 3.6556e-05 | 6.0927e-05
2012-10-12 | 509:48040 | SHORT RURAL | Equipment Failure | 887929 | 22 | 15 | 330 | 0.00020106 | 0.0013404
2012-10-14 | 511:29872 | URBAN | Equipment Failure | 887952 | 1 | 120 | 120 | 7.3113e-05 | 6.0927e-05
2012-10-15 | ZN15006:PA9 | URBAN | Vegetation | 888003 | 1 | 167.4 | 167.4 | 0.00010199 | 6.0927e-05
2012-10-15 | 227:13018 | URBAN | Other | 888010 | 1 | 98.05 | 98.05 | 5.9739e-05 | 6.0927e-05
2012-10-15 | 229:34983 | SHORT RURAL | Other | 888070 | 1 | 202.7167 | 202.7167 | 0.00012351 | 6.0927e-05
2012-10-15 | ZN12650:PA13 | SHORT RURAL | Other | 888080 | 1 | 160.2 | 160.2 | 9.7605e-05 | 6.0927e-05
2012-10-15 | ZN14143:PA12 | SHORT RURAL | Other | 888081 | 1 | 83.3 | 83.3 | 5.0752e-05 | 6.0927e-05
2012-10-15 | ZN269:PA19 | URBAN | Third Party Impacts | 888083 | 104 | 105 | 10920 | 0.0066533 | 0.0063364
2012-10-15 | ZN2310:PA34 | URBAN | Other | 888090 | 28 | 210 | 5880 | 0.0035825 | 0.001706
2012-10-15 | ZN12690:PA6 | URBAN | Equipment Failure | 888102 | 777 | 82 | 63714 | 0.038819 | 0.04734
2012-10-16 | 501:48122 | SHORT RURAL | Equipment Failure | 888112 | 580 | 405 | 46363 | 0.028232 | 0.035319
2012-10-16 | 503:48011 | SHORT RURAL | Equipment Failure | 888112 | 152 | 405 | 13832 | 0.0084229 | 0.0092559
2012-10-16 | 801:74121 | SHORT RURAL | Animals | 888122 | 3 | 107 | 321 | 0.00019547 | 0.00018268
2012-10-15 | 523:33501 | SHORT RURAL | Equipment Failure | 888147 | 1 | 105 | 105 | 6.3974e-05 | 6.0927e-05
2012-10-16 | 810:74054 | LONG RURAL | Animals | 888160 | 1 | 223 | 223 | 0.00013579 | 6.0894e-05
2012-10-16 | ZN9037:PA10 | URBAN | Equipment Failure | 888199 | 126 | 78 | 9828 | 0.0059847 | 0.0076727
2012-10-16 | ZN8000:PA19 | URBAN | Equipment Failure | 888219 | 171 | 614.6667 | 45678 | 0.027815 | 0.010413
2012-10-16 | ZN10990:PA2 | URBAN | Other | 888442 | 1996 | 44 | 87362 | 0.053199 | 0.12155
2012-10-16 | ZN15006:PA1 | URBAN | Other | 888485 | 1 | 63.45 | 63.45 | 3.8637e-05 | 6.0894e-05
2012-10-16 | 232:33413 | SHORT RURAL | Other | 888535 | 1 | 157.95 | 157.95 | 9.6183e-05 | 6.0894e-05
2012-10-16 | 509:48039 | LONG RURAL | Other | 888543 | 1 | 308.5667 | 308.5667 | 0.0001879 | 6.0894e-05
2012-10-16 | ZN2400:PA18 | SHORT RURAL | Other | 888555 | 2 | 51.7333 | 88.4167 | 5.3841e-05 | 0.00012179
2012-10-16 | ZN847:PA39 | URBAN | Other | 888593 | 1 | 257.9167 | 257.9167 | 0.00015706 | 6.0894e-05
2012-10-16 | ZN3472:PA40 | URBAN | Equipment Failure | 888617 | 23 | 42 | 966 | 0.00058824 | 0.0014006
2012-10-16 | 230:81440 | URBAN | Other | 888618 | 1 | 114.3667 | 114.3667 | 6.9643e-05 | 6.0894e-05
2012-10-16 | ZN35500:PA32 | URBAN | Other | 888631 | 63 | 86 | 5418 | 0.0032993 | 0.0038363
2012-10-17 | 256:80647 | URBAN | Equipment Failure | 888639 | 27 | 414 | 11178 | 0.0068068 | 0.0016442
2012-10-17 | ZN12610:PA6 | URBAN | Other | 888640 | 1 | 494.9667 | 494.9667 | 0.00030141 | 6.0895e-05
2012-10-17 | 515:35193 | SHORT RURAL | Equipment Failure | 888653 | 9 | 338.45 | 1823.45 | 0.0011104 | 0.00054805
2012-10-17 | ZN35370:PA2 | SHORT RURAL | Equipment Failure | 888685 | 1 | 134.4 | 134.4 | 8.1842e-05 | 6.0895e-05
2012-10-17 | ZN2310:PA3 | URBAN | Other | 888728 | 1 | 319.0167 | 319.0167 | 0.00019426 | 6.0895e-05
2012-10-17 | 217:33610 | URBAN | Other | 888732 | 1 | 169.8 | 169.8 | 0.0001034 | 6.0895e-05
2012-10-17 | 232:11455 | URBAN | Equipment Failure | 888804 | 1995 | 387 | 427453 | 0.2603 | 0.12148
2012-10-17 | ZN4545:PA35 | URBAN | Vegetation | 888857 | 156 | 141 | 21996 | 0.013394 | 0.0094996
2012-10-17 | 515:35197 | LONG RURAL | Other | 888879 | 140 | 353 | 49420 | 0.030094 | 0.0085252
2012-10-17 | 509:48039 | LONG RURAL | Other | 888892 | 1 | 322.1167 | 322.1167 | 0.00019615 | 6.0895e-05
2012-10-17 | 219:1785 | URBAN | Vegetation | 888919 | 1 | 46.5333 | 46.5333 | 2.8336e-05 | 6.0895e-05
2012-10-17 | ZN15006:PA1 | URBAN | Other | 888926 | 1 | 134.75 | 134.75 | 8.2055e-05 | 6.0895e-05
2012-10-17 | ZN2568:PA39 | URBAN | Other | 888987 | 1 | 1316.7333 | 1316.7333 | 0.00080182 | 6.0895e-05
2012-10-17 | ZN12690:PA3 | SHORT RURAL | Other | 889003 | 1 | 158.85 | 158.85 | 9.6731e-05 | 6.0895e-05
2012-10-17 | ZN10994:PA4 | URBAN | Equipment Failure | 889028 | 365 | 60 | 21900 | 0.013336 | 0.022227
2012-10-17 | ZN3472:PA40 | URBAN | Other | 889043 | 1 | 120.1833 | 120.1833 | 7.3185e-05 | 6.0895e-05
2012-10-17 | ZN2635:PA1 | URBAN | Other | 889055 | 1 | 118 | 85 | 5.176e-05 | 6.0895e-05
2012-10-17 | ZN2635:PA12 | SHORT RURAL | Other | 889055 | 902 | 118 | 86512 | 0.052681 | 0.054927
2012-10-17 | ZN847:PA14 | URBAN | Equipment Failure | 889074 | 1 | 937.5167 | 937.5167 | 0.0005709 | 6.0895e-05
2012-10-18 | ZN10991:PA6 | URBAN | Animals | 889115 | 1318 | 89 | 106594 | 0.06491 | 0.080259
2012-10-18 | 807:74179 | SHORT RURAL | Equipment Failure | 889125 | 1 | 292.3667 | 292.3667 | 0.00017804 | 6.0895e-05
2012-10-18 | ZN15013:PA6 | SHORT RURAL | Animals | 889130 | 18 | 147.9 | 2662.2 | 0.0016211 | 0.0010961
2012-10-18 | ZN2602:PA17 | URBAN | Other | 889134 | 1 | 156.5167 | 156.5167 | 9.531e-05 | 6.0895e-05
2012-10-18 | ZN4545:PA40 | URBAN | Third Party Impacts | 889137 | 46 | 132.75 | 6106.5 | 0.0037185 | 0.0028012
2012-10-18 | ZN14891:PA10 | SHORT RURAL | Equipment Failure | 889159 | 25 | 195 | 4875 | 0.0029686 | 0.0015224
2012-10-18 | ZN10991:PA7 | URBAN | Vegetation | 889263 | 94 | 65.5333 | 6160.1333 | 0.0037512 | 0.0057241
2012-10-18 | ZN10999:PA24 | URBAN | Third Party Impacts | 889394 | 1 | 97.0667 | 97.0667 | 5.9108e-05 | 6.0895e-05
2012-10-18 | ZN15006:PA1 | URBAN | Other | 889429 | 1 | 80.6167 | 80.6167 | 4.9091e-05 | 6.0895e-05
2012-10-18 | 511:29877 | SHORT RURAL | Other | 889458 | 1 | 66.8 | 66.8 | 4.0678e-05 | 6.0895e-05
2012-10-18 | 813:89055 | SHORT RURAL | Vegetation | 889496 | 2 | 279.4833 | 558.9667 | 0.00034038 | 0.00012179
2012-10-18 | ZN965:PA20 | URBAN | Third Party Impacts | 889525 | 1 | 81.3 | 81.3 | 4.9507e-05 | 6.0895e-05
2012-10-18 | 235:2123 | URBAN | Other | 889530 | 1 | 104.65 | 104.65 | 6.3726e-05 | 6.0895e-05
2012-10-18 | 264:81240 | SHORT RURAL | Other | 889533 | 1 | 157.2333 | 157.2333 | 9.5747e-05 | 6.0895e-05
2012-10-18 | 232:11455 | URBAN | Equipment Failure | 889536 | 131 | 15 | 1965 | 0.0011966 | 0.0079772
2012-10-19 | 225:33676 | SHORT RURAL | Equipment Failure | 889556 | 104 | 85.9667 | 8940.5333 | 0.0054443 | 0.0063331
2012-10-19 | 807:74184 | SHORT RURAL | Equipment Failure | 889572 | 1 | 110 | 110 | 6.6984e-05 | 6.0895e-05
2012-10-19 | ZN4545:PA24 | URBAN | Equipment Failure | 889575 | 1 | 785.6833 | 785.6833 | 0.00047844 | 6.0895e-05
2012-10-17 | ZN3472:PA17 | URBAN | Third Party Impacts | 889611 | 3 | 40 | 120 | 7.3074e-05 | 0.00018268
2012-10-19 | ZN15008:PA7 | URBAN | Equipment Failure | 889699 | 1 | 435.8833 | 435.8833 | 0.00026543 | 6.0895e-05
2012-10-19 | ZN398:PA24 | URBAN | Equipment Failure | 889708 | 1 | 602.1333 | 602.1333 | 0.00036667 | 6.0895e-05
2012-10-19 | ZN874:PA3 | URBAN | Equipment Failure | 889742 | 641 | 28 | 17948 | 0.010929 | 0.039034
2012-10-19 | ZN269:PA7 | URBAN | Operational Error | 889751 | 84 | 125 | 10500 | 0.006394 | 0.0051152
2012-10-19 | ZN188:PA9 | URBAN | Other | 889767 | 1 | 188.3 | 188.3 | 0.00011467 | 6.0895e-05
2012-10-19 | ZN2835:PA20 | URBAN | Equipment Failure | 889770 | 2 | 186.0333 | 372.0667 | 0.00022657 | 0.00012179
2012-10-19 | 511:29873 | SHORT RURAL | Other | 889799 | 1 | 407.0667 | 407.0667 | 0.00024788 | 6.0895e-05
2012-10-19 | ZN35500:PA28 | URBAN | Other | 889813 | 64 | 75 | 4794.6667 | 0.0029197 | 0.0038973
2012-10-19 | ZN4545:PA36 | URBAN | Other | 889813 | 82 | 75 | 6150 | 0.003745 | 0.0049934
2012-10-19 | ZN9035:PA2 | URBAN | Equipment Failure | 889842 | 650 | 52 | 33800 | 0.020582 | 0.039582
2012-10-19 | ZN690:PA17 | URBAN | Other | 889858 | 1 | 147.7833 | 147.7833 | 8.9992e-05 | 6.0895e-05
2012-10-19 | 515:35197 | LONG RURAL | Equipment Failure | 889860 | 1 | 274 | 274 | 0.00016685 | 6.0895e-05
2012-10-19 | 509:48039 | LONG RURAL | Vegetation | 889862 | 15 | 52 | 780 | 0.00047498 | 0.00091342
2012-10-19 | ZN12580:PA16 | URBAN | Equipment Failure | 889867 | 1 | 307.3333 | 307.3333 | 0.00018715 | 6.0895e-05
2012-10-19 | ZN2310:PA38 | URBAN | Third Party Impacts | 889879 | 1 | 497.0667 | 497.0667 | 0.00030269 | 6.0895e-05
2012-10-19 | 509:48039 | LONG RURAL | Vegetation | 889883 | 1 | 243.0167 | 243.0167 | 0.00014798 | 6.0895e-05
2012-10-19 | 235:2120 | SHORT RURAL | Equipment Failure | 889904 | 57 | 64 | 3648 | 0.0022214 | 0.003471
2012-10-19 | ZN12580:PA16 | URBAN | Vegetation | 889921 | 541 | 38 | 20558 | 0.012519 | 0.032944
2012-10-19 | ZN15006:PA1 | URBAN | Equipment Failure | 889922 | 1 | 1206.9167 | 1206.9167 | 0.00073495 | 6.0895e-05
2012-10-19 | ZN12650:PA1 | SHORT RURAL | Vegetation | 889948 | 2 | 144 | 288 | 0.00017538 | 0.00012179
2012-10-20 | ZN12570:PA34 | SHORT RURAL | Other | 889977 | 29 | 20 | 580 | 0.00035319 | 0.001766
2012-10-20 | ZN398:PA15 | URBAN | Equipment Failure | 890008 | 1824 | 56 | 102144 | 0.0622 | 0.11107
2012-10-20 | ZN398:PA16 | URBAN | Equipment Failure | 890008 | 2035 | 56 | 113960 | 0.069396 | 0.12392
2012-10-20 | ZN398:PA19 | URBAN | Equipment Failure | 890008 | 782 | 56 | 43792 | 0.026667 | 0.04762
2012-10-20 | ZN398:PA20 | URBAN | Equipment Failure | 890008 | 1652 | 56 | 92512 | 0.056335 | 0.1006
2012-10-20 | ZN398:PA22 | URBAN | Equipment Failure | 890008 | 274 | 56 | 15344 | 0.0093437 | 0.016685
2012-10-20 | ZN9118:PA24 | URBAN | Equipment Failure | 890033 | 1 | 151.65 | 151.65 | 9.2347e-05 | 6.0895e-05
2012-10-20 | ZN2568:PA16 | URBAN | Other | 890045 | 1 | 132.5833 | 132.5833 | 8.0736e-05 | 6.0895e-05
2012-10-20 | ZN262:PA15 | URBAN | Vegetation | 890061 | 86 | 66.2333 | 5696.0667 | 0.0034686 | 0.005237
2012-10-21 | ZN187:PA28 | URBAN | Equipment Failure | 890112 | 714 | 79 | 56406 | 0.034348 | 0.043479
2012-10-21 | 214:8670 | URBAN | Equipment Failure | 890128 | 1 | 112.55 | 112.55 | 6.8537e-05 | 6.0895e-05
2012-10-21 | ZN2473:PA21 | URBAN | Equipment Failure | 890153 | 1 | 231.5 | 231.5 | 0.00014097 | 6.0895e-05
2012-10-21 | ZN12600:PA2 | SHORT RURAL | Other | 890165 | 2 | 126 | 252 | 0.00015346 | 0.00012179
2012-10-21 | 504:48034 | URBAN | Other | 890192 | 1 | 122.8667 | 122.8667 | 7.4819e-05 | 6.0895e-05
2012-10-21 | 515:35192 | SHORT RURAL | Equipment Failure | 890200 | 335 | 406 | 123270 | 0.075065 | 0.0204
2012-10-21 | ZN1285:PA10 | URBAN | Other | 890217 | 15 | 183 | 2745 | 0.0016716 | 0.00091342
2012-10-22 | ZN1285:PA36 | URBAN | Other | 890220 | 1 | 26 | 26 | 1.5833e-05 | 6.0895e-05
2012-10-22 | ZN12610:PA10 | SHORT RURAL | Other | 890221 | 1 | 251.9833 | 251.9833 | 0.00015344 | 6.0895e-05
2012-10-18 | 232:11455 | URBAN | Equipment Failure | 890246 | 2 | 70 | 140 | 8.5253e-05 | 0.00012179
2012-10-22 | 502:48010 | SHORT RURAL | Equipment Failure | 890250 | 1 | 286.8667 | 286.8667 | 0.00017469 | 6.0895e-05
2012-10-20 | ZN12630:PA3 | SHORT RURAL | Equipment Failure | 890262 | 4 | 35 | 140 | 8.5253e-05 | 0.00024358
2012-10-18 | 509:48039 | LONG RURAL | Equipment Failure | 890271 | 3 | 58 | 174 | 0.00010596 | 0.00018268
2012-10-22 | ZN9118:PA11 | URBAN | Other | 890278 | 1 | 226.1667 | 226.1667 | 0.00013772 | 6.0895e-05
2012-10-22 | ZN1068:PA17 | URBAN | Other | 890322 | 1 | 327.3333 | 327.3333 | 0.00019933 | 6.0895e-05
2012-10-18 | 807:74179 | SHORT RURAL | Equipment Failure | 890378 | 1 | 293 | 293 | 0.00017842 | 6.0895e-05
2012-10-18 | 813:89055 | SHORT RURAL | Equipment Failure | 890382 | 13 | 60 | 780 | 0.00047498 | 0.00079163
2012-10-22 | 813:89061 | LONG RURAL | Equipment Failure | 890407 | 1 | 189.7333 | 189.7333 | 0.00011554 | 6.0895e-05
2012-10-22 | 507:80931 | URBAN | Other | 890428 | 1 | 149.9333 | 149.9333 | 9.1302e-05 | 6.0895e-05
2012-10-22 | 223:14393 | URBAN | Equipment Failure | 890432 | 1 | 1437.7833 | 1437.7833 | 0.00087554 | 6.0895e-05
2012-10-22 | ZN2568:PA6 | SHORT RURAL | Weather | 890489 | 40 | 60 | 2400 | 0.0014615 | 0.0024358
2012-10-22 | ZN9900:PA1 | URBAN | Weather | 890494 | 38 | 77.8833 | 2959.5667 | 0.0018022 | 0.002314
2012-10-22 | 243:80075 | SHORT RURAL | Vegetation | 890501 | 169 | 122 | 19012 | 0.011577 | 0.010291
2012-10-22 | ZN195:PA28 | URBAN | Vegetation | 890503 | 1 | 395.3333 | 395.3333 | 0.00024074 | 6.0895e-05
2012-10-22 | ZN10999:PA3 | URBAN | Vegetation | 890517 | 184 | 121.3667 | 22331.4667 | 0.013599 | 0.011205
2012-10-22 | ZN1648:PA20 | URBAN | Vegetation | 890575 | 93 | 147.3667 | 13705.1 | 0.0083457 | 0.0056632
2012-10-22 | ZN12600:PA13 | SHORT RURAL | Equipment Failure | 890599 | 14 | 301.4833 | 4220.7667 | 0.0025702 | 0.00085253
2012-10-22 | 202:34231 37 42 | URBAN | Other | 890610 | 1 | 86.0833 | 86.0833 | 5.242e-05 | 6.0895e-05
2012-10-22 | 503:48011 | SHORT RURAL | Other | 890612 | 14 | 240.7 | 3369.8 | 0.002052 | 0.00085253
2012-10-22 | ZN847:PA1 | URBAN | Vegetation | 890617 | 1 | 386.4 | 386.4 | 0.0002353 | 6.0895e-05
2012-10-22 | ZN14144:PA4 | URBAN | Other | 890638 | 827 | 90 | 74430 | 0.045324 | 0.05036
2012-10-22 | 812:19066 | SHORT RURAL | Other | 890640 | 1 | 52.7333 | 52.7333 | 3.2112e-05 | 6.0895e-05
2012-10-22 | ZN116:PA47 | URBAN | Other | 890648 | 40 | 82 | 3280 | 0.0019974 | 0.0024358
2012-10-22 | ZN12650:PA1 | SHORT RURAL | Vegetation | 890650 | 92 | 59 | 5428 | 0.0033054 | 0.0056023
2012-10-22 | ZN2400:PA26 | URBAN | Vegetation | 890652 | 953 | 112.75 | 107450.75 | 0.065432 | 0.058033
2012-10-22 | ZN80:PA21 | URBAN | Vegetation | 890658 | 30 | 70 | 2100 | 0.0012788 | 0.0018268
2012-10-22 | ZN2602:PA30 | URBAN | Other | 890666 | 1 | 185.65 | 185.65 | 0.00011305 | 6.0895e-05
2012-10-22 | ZN965:PA21 | URBAN | Vegetation | 890667 | 30 | 69.1333 | 2074 | 0.001263 | 0.0018268
2012-10-22 | ZN14892:PA19 | URBAN | Vegetation | 890685 | 40 | 45 | 1800 | 0.0010961 | 0.0024358
2012-10-22 | 205:12205 | URBAN | Vegetation | 890691 | 56 | 399.6833 | 22382.2667 | 0.01363 | 0.0034101
2012-10-22 | 813:89062 | SHORT RURAL | Vegetation | 890695 | 33 | 325 | 10725 | 0.006531 | 0.0020095
2012-10-22 | 206:34432 | URBAN | Vegetation | 890697 | 24 | 43.2333 | 1037.6 | 0.00063184 | 0.0014615
2012-10-22 | 235:2120 | SHORT RURAL | Other | 890698 | 1 | 149.7667 | 149.7667 | 9.12e-05 | 6.0895e-05
2012-10-22 | ZN167:PA2 | URBAN | Vegetation | 890704 | 9 | 133 | 1197 | 0.00072891 | 0.00054805
2012-10-22 | 214:8669 | URBAN | Equipment Failure | 890720 | 1 | 319.85 | 319.85 | 0.00019477 | 6.0895e-05
2012-10-22 | 260:33347 | SHORT RURAL | Other | 890721 | 1 | 82.55 | 82.55 | 5.0269e-05 | 6.0895e-05
2012-10-22 | ZN12590:PA3 | SHORT RURAL | Other | 890725 | 1135 | 93 | 91717 | 0.055851 | 0.069116
2012-10-22 | 205:12205 | URBAN | Vegetation | 890731 | 1 | 568.8833 | 568.8833 | 0.00034642 | 6.0895e-05
2012-10-22 | ZN965:PA26 | URBAN | Vegetation | 890734 | 10 | 185 | 1850 | 0.0011266 | 0.00060895
2012-10-22 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 890738 | 1702 | 223 | 166328 | 0.10129 | 0.10364
2012-10-22 | ZN15006:PA8 | URBAN | Vegetation | 890740 | 1 | 347.8 | 347.8 | 0.00021179 | 6.0895e-05
2012-10-22 | ZN1285:PA17 | SHORT RURAL | Vegetation | 890744 | 12 | 103 | 1236 | 0.00075266 | 0.00073074
2012-10-22 | ZN1285:PA8 | URBAN | Vegetation | 890744 | 9 | 103 | 927 | 0.0005645 | 0.00054805
2012-10-22 | 223:14398 | URBAN | Equipment Failure | 890768 | 39 | 195 | 7605 | 0.0046311 | 0.0023749
2012-10-22 | 243:80084 | SHORT RURAL | Vegetation | 890771 | 1812 | 487 | 232874 | 0.14181 | 0.11034
2012-10-22 | 243:80074 | URBAN | Vegetation | 890773 | 1 | 297.9333 | 297.9333 | 0.00018143 | 6.0895e-05
2012-10-22 | ZN12650:PA13 | SHORT RURAL | Vegetation | 890781 | 1 | 577.05 | 577.05 | 0.00035139 | 6.0895e-05
2012-10-22 | 227:13015 | SHORT RURAL | Other | 890799 | 318 | 597.2167 | 65232.4 | 0.039723 | 0.019365
2012-10-22 | ZN12640:PA8 | SHORT RURAL | Other | 890806 | 1 | 142.7167 | 142.7167 | 8.6907e-05 | 6.0895e-05
2012-10-22 | 224:80332 | URBAN | Vegetation | 890815 | 1 | 258.6 | 258.6 | 0.00015747 | 6.0895e-05
2012-10-22 | ZN4545:PA41 | URBAN | Vegetation | 890818 | 27 | 144.1333 | 3891.6 | 0.0023698 | 0.0016442
2012-10-22 | 218:7481 | URBAN | Vegetation | 890843 | 1 | 125.4833 | 125.4833 | 7.6413e-05 | 6.0895e-05
2012-10-22 | 260:33353 | URBAN | Vegetation | 890845 | 1604 | 98.4667 | 157940.5333 | 0.096178 | 0.097675
2012-10-22 | 217:33612 | URBAN | Equipment Failure | 890849 | 1851 | 1053 | 340220 | 0.20718 | 0.11272
2012-10-22 | 513:48059 | SHORT RURAL | Equipment Failure | 890873 | 11 | 200 | 2200 | 0.0013397 | 0.00066984
2012-10-22 | 205:12205 | URBAN | Vegetation | 890878 | 1 | 487.75 | 487.75 | 0.00029701 | 6.0895e-05
2012-10-22 | ZN690:PA17 | URBAN | Vegetation | 890879 | 1 | 339.4 | 339.4 | 0.00020668 | 6.0895e-05
2012-10-22 | ZN188:PA1 | URBAN | Weather | 890888 | 30 | 111 | 3303 | 0.0020114 | 0.0018268
2012-10-22 | ZN188:PA34 | URBAN | Weather | 890888 | 10 | 111 | 1110 | 0.00067593 | 0.00060895
2012-10-22 | 223:14393 | URBAN | Vegetation | 890889 | 1 | 224.5 | 224.5 | 0.00013671 | 6.0895e-05
2012-10-22 | ZN690:PA35 | URBAN | Vegetation | 890905 | 1 | 315.6833 | 315.6833 | 0.00019223 | 6.0895e-05
2012-10-22 | 224:80341 | URBAN | Vegetation | 890909 | 34 | 59.4667 | 2021.8667 | 0.0012312 | 0.0020704
2012-10-22 | 206:34434 | URBAN | Vegetation | 890911 | 19 | 125 | 2375 | 0.0014463 | 0.001157
2012-10-22 | 221:11897 | URBAN | Other | 890921 | 1 | 221.8167 | 221.8167 | 0.00013507 | 6.0895e-05
2012-10-22 | ZN35500:PA24 | URBAN | Equipment Failure | 890930 | 1 | 268.0833 | 268.0833 | 0.00016325 | 6.0895e-05
2012-10-22 | 202:34232 | URBAN | Other | 890941 | 1 | 111.45 | 111.45 | 6.7867e-05 | 6.0895e-05
2012-10-22 | ZN116:PA50 | URBAN | Equipment Failure | 890946 | 15 | 288.9 | 4333.5 | 0.0026389 | 0.00091342
2012-10-22 | 260:33353 | URBAN | Vegetation | 890965 | 82 | 256 | 20992 | 0.012783 | 0.0049934
2012-10-22 | ZN12640:PA7 | URBAN | Equipment Failure | 890966 | 1 | 1504.8 | 1504.8 | 0.00091635 | 6.0895e-05
2012-10-22 | ZN116:PA50 | URBAN | Vegetation | 890979 | 1 | 510.4667 | 510.4667 | 0.00031085 | 6.0895e-05
2012-10-22 | ZN12620:PA11 | SHORT RURAL | Vegetation | 890987 | 1 | 70.1167 | 70.1167 | 4.2697e-05 | 6.0895e-05
2012-10-22 | ZN12620:PA11 | SHORT RURAL | Other | 890989 | 1 | 347.0833 | 347.0833 | 0.00021136 | 6.0895e-05
2012-10-22 | ZN10995:PA13 | URBAN | Other | 890994 | 1 | 495.9333 | 495.9333 | 0.000302 | 6.0895e-05
2012-10-22 | 256:80650 | URBAN | Equipment Failure | 890995 | 1 | 172.7 | 172.7 | 0.00010517 | 6.0895e-05
2012-10-22 | ZN72:PA26 | URBAN | Other | 891003 | 1 | 472.8667 | 472.8667 | 0.00028795 | 6.0895e-05
2012-10-22 | 258:80784 | URBAN | Other | 891005 | 1 | 53.9667 | 53.9667 | 3.2863e-05 | 6.0895e-05
2012-10-22 | 507:80932 | SHORT RURAL | Other | 891008 | 1 | 188.5667 | 188.5667 | 0.00011483 | 6.0895e-05
2012-10-22 | ZN12660:PA14 | SHORT RURAL | Vegetation | 891015 | 45 | 74.9833 | 3374.25 | 0.0020547 | 0.0027403
2012-10-22 | 203:8086 | URBAN | Weather | 891016 | 1 | 111.6167 | 111.6167 | 6.7969e-05 | 6.0895e-05
2012-10-22 | ZN2635:PA16 | URBAN | Other | 891039 | 73 | 64.35 | 4697.55 | 0.0028606 | 0.0044453
2012-10-22 | ZN10999:PA4 | URBAN | Other | 891043 | 1 | 239.7833 | 239.7833 | 0.00014602 | 6.0895e-05
2012-10-23 | ZN12610:PA18 | URBAN | Equipment Failure | 891055 | 37 | 98.9 | 3659.3 | 0.0022275 | 0.0022523
2012-10-23 | ZN965:PA21 | URBAN | Vegetation | 891070 | 1 | 238.7 | 238.7 | 0.0001453 | 6.0872e-05
2012-10-23 | ZN12570:PA33 | SHORT RURAL | Other | 891074 | 1 | 283.0833 | 283.0833 | 0.00017232 | 6.0872e-05
2012-10-23 | ZN12650:PA13 | SHORT RURAL | Other | 891078 | 1 | 82.2333 | 82.2333 | 5.0057e-05 | 6.0872e-05
2012-10-23 | ZN12620:PA8 | SHORT RURAL | Animals | 891086 | 1 | 98.0833 | 98.0833 | 5.9706e-05 | 6.0872e-05
2012-10-22 | ZN3154:PA11 | URBAN | Vegetation | 891087 | 685 | 56 | 38360 | 0.023359 | 0.041713
2012-10-23 | 203:8085 | URBAN | Other | 891094 | 1 | 522.75 | 522.75 | 0.00031821 | 6.0872e-05
2012-10-22 | 227:13020 | SHORT RURAL | Vegetation | 891104 | 68 | 370 | 25160 | 0.015321 | 0.0041408
2012-10-23 | ZN12570:PA33 | SHORT RURAL | Equipment Failure | 891140 | 1 | 288.9333 | 288.9333 | 0.00017588 | 6.0872e-05
2012-10-23 | ZN12600:PA2 | SHORT RURAL | Other | 891154 | 1 | 413.7333 | 413.7333 | 0.00025185 | 6.0872e-05
2012-10-23 | ZN12640:PA15 | URBAN | Vegetation | 891183 | 1 | 64.35 | 64.35 | 3.9171e-05 | 6.0872e-05
2012-10-23 | 227:13018 | URBAN | Other | 891191 | 1 | 73.7167 | 73.7167 | 4.4873e-05 | 6.0872e-05
2012-10-23 | ZN12650:PA1 | SHORT RURAL | Vegetation | 891308 | 55 | 50 | 2750 | 0.001674 | 0.003348
2012-10-22 | 526:34636 | SHORT RURAL | Equipment Failure | 891314 | 2 | 35 | 70 | 4.2626e-05 | 0.00012179
2012-10-23 | ZN15014:PA19 | URBAN | Equipment Failure | 891315 | 1 | 209.9667 | 209.9667 | 0.00012781 | 6.0872e-05
2012-10-22 | 509:48039 | LONG RURAL | Vegetation | 891320 | 39 | 209 | 6171 | 0.0037578 | 0.0023749
2012-10-23 | ZN12690:PA3 | SHORT RURAL | Other | 891322 | 1 | 275.8167 | 275.8167 | 0.0001679 | 6.0872e-05
2012-10-22 | 803:74010 | SHORT RURAL | Other | 891325 | 1 | 60 | 60 | 3.6537e-05 | 6.0895e-05
2012-10-23 | ZN180:PA41 | URBAN | Vegetation | 891360 | 1 | 13 | 13 | 7.9134e-06 | 6.0872e-05
2012-10-23 | ZN180:PA41 | URBAN | Vegetation | 891368 | 57 | 242.6667 | 13832 | 0.0084199 | 0.0034697
2012-10-23 | ZN10994:PA12 | URBAN | Other | 891380 | 1 | 86.85 | 86.85 | 5.2868e-05 | 6.0872e-05
2012-10-21 | 516:48067 | SHORT RURAL | Other | 891451 | 2 | 2868.1 | 5736.2 | 0.0034931 | 0.00012179
2012-10-23 | ZN12620:PA11 | SHORT RURAL | Equipment Failure | 891496 | 1 | 470.3333 | 470.3333 | 0.0002863 | 6.0872e-05
2012-10-23 | ZN72:PA24 | SHORT RURAL | Equipment Failure | 891500 | 1 | 315.55 | 315.55 | 0.00019208 | 6.0872e-05
2012-10-23 | ZN12580:PA1 | URBAN | Other | 891510 | 1 | 69.95 | 69.95 | 4.258e-05 | 6.0872e-05
2012-10-23 | ZN195:PA25 | URBAN | Third Party Impacts | 891563 | 1 | 158.3167 | 158.3167 | 9.6371e-05 | 6.0872e-05
2012-10-23 | ZN9118:PA21 | URBAN | Other | 891620 | 1 | 310.7 | 310.7 | 0.00018913 | 6.0872e-05
2012-10-23 | ZN12660:PA14 | SHORT RURAL | Other | 891627 | 1 | 135.1167 | 135.1167 | 8.2249e-05 | 6.0872e-05
2012-10-23 | ZN14143:PA17 | SHORT RURAL | Vegetation | 891644 | 746 | 290 | 70908 | 0.043163 | 0.045411
2012-10-23 | ZN12620:PA7 | URBAN | Vegetation | 891646 | 63 | 125.5 | 7906.5 | 0.0048129 | 0.003835
2012-10-23 | 502:48010 | SHORT RURAL | Equipment Failure | 891655 | 82 | 92 | 7544 | 0.0045922 | 0.0049915
2012-10-24 | ZN35500:PA32 | URBAN | Other | 891756 | 63 | 139.9 | 8813.7 | 0.0053651 | 0.003835
2012-10-24 | 229:34989 | SHORT RURAL | Other | 891769 | 21 | 253.4 | 5130.3 | 0.0031229 | 0.0012783
2012-10-24 | ZN12610:PA9 | SHORT RURAL | Other | 891770 | 1 | 75.9167 | 75.9167 | 4.6212e-05 | 6.0872e-05
2012-10-24 | ZN9035:PA4 | URBAN | Equipment Failure | 891778 | 1 | 140.5 | 140.5 | 8.5526e-05 | 6.0872e-05
2012-10-23 | ZN9245:PA8 | SHORT RURAL | Equipment Failure | 891779 | 1 | 300 | 300 | 0.00018262 | 6.0872e-05
2012-10-24 | ZN12610:PA25 | SHORT RURAL | Equipment Failure | 891800 | 102 | 260 | 26520 | 0.016143 | 0.006209
2012-10-24 | ZN12610:PA9 | SHORT RURAL | Equipment Failure | 891800 | 37 | 260 | 9620 | 0.0058559 | 0.0022523
2012-10-24 | ZN195:PA29 | URBAN | Third Party Impacts | 891809 | 45 | 30 | 1350 | 0.00082178 | 0.0027393
2012-10-24 | ZN1068:PA27 | URBAN | Third Party Impacts | 891963 | 1 | 313.4167 | 313.4167 | 0.00019078 | 6.0872e-05
2012-10-24 | ZN1068:PA27 | URBAN | Third Party Impacts | 891969 | 1 | 305.1833 | 305.1833 | 0.00018577 | 6.0872e-05
2012-10-24 | 238:34140 | URBAN | Equipment Failure | 892033 | 1 | 175.25 | 175.25 | 0.00010668 | 6.0872e-05
2012-10-24 | 264:81236 | URBAN | Third Party Impacts | 892040 | 69 | 195 | 13455 | 0.0081904 | 0.0042002
2012-10-24 | ZN1850:PA13 | URBAN | Weather | 892051 | 1 | 1438.1333 | 1438.1333 | 0.00087543 | 6.0872e-05
2012-10-24 | ZN2568:PA42 | URBAN | Other | 892066 | 40 | 77.35 | 3094 | 0.0018834 | 0.0024349
2012-10-24 | ZN12640:PA7 | URBAN | Equipment Failure | 892076 | 73 | 44.2 | 3226.6 | 0.0019641 | 0.0044437
2012-10-24 | ZN3922:PA2 | SHORT RURAL | Equipment Failure | 892078 | 1135 | 204 | 227575 | 0.13853 | 0.06909
2012-10-24 | ZN14892:PA3 | SHORT RURAL | Equipment Failure | 892123 | 1 | 229.4667 | 229.4667 | 0.00013968 | 6.0872e-05
2012-10-24 | ZN116:PA44 | URBAN | Other | 892132 | 1 | 299.45 | 299.45 | 0.00018228 | 6.0872e-05
2012-10-24 | ZN847:PA36 | URBAN | Other | 892136 | 1 | 238.55 | 238.55 | 0.00014521 | 6.0872e-05
2012-10-24 | ZN129:PA16 | URBAN | Other | 892156 | 1 | 134.8333 | 134.8333 | 8.2076e-05 | 6.0872e-05
2012-10-24 | 516:48066 | SHORT RURAL | Other | 892163 | 4 | 75 | 300 | 0.00018262 | 0.00024349
2012-10-24 | 222:2017 | URBAN | Vegetation | 892204 | 1 | 171.2833 | 171.2833 | 0.00010426 | 6.0872e-05
2012-10-24 | 514:18137 | SHORT RURAL | Other | 892209 | 4 | 230 | 920 | 0.00056003 | 0.00024349
2012-10-24 | ZN9550:PA43 | URBAN | Equipment Failure | 892214 | 1 | 761 | 761 | 0.00046324 | 6.0872e-05
2012-10-24 | ZN15005:PA8 | URBAN | Other | 892216 | 22 | 62 | 1351.05 | 0.00082242 | 0.0013392
2012-10-24 | 230:81440 | URBAN | Other | 892228 | 1 | 96.8833 | 96.8833 | 5.8975e-05 | 6.0872e-05
2012-10-24 | ZN1673:PA1 | URBAN | Vegetation | 892237 | 29 | 231.5167 | 6713.9833 | 0.004087 | 0.0017653
2012-10-25 | ZN14144:PA7 | SHORT RURAL | Vegetation | 892245 | 1 | 593.3167 | 593.3167 | 0.00036117 | 6.0873e-05
2012-10-25 | 501:48122 | SHORT RURAL | Animals | 892247 | 1 | 246.8167 | 246.8167 | 0.00015024 | 6.0873e-05
2012-10-24 | 511:29873 | SHORT RURAL | Equipment Failure | 892249 | 98 | 511 | 20030 | 0.012193 | 0.0059655
2012-10-25 | 801:74123 | SHORT RURAL | Other | 892250 | 4 | 194.45 | 777.8 | 0.00047347 | 0.00024349
2012-10-25 | 510:48164 | SHORT RURAL | Equipment Failure | 892252 | 1 | 189.8333 | 189.8333 | 0.00011556 | 6.0873e-05
2012-10-25 | 219:1783 | SHORT RURAL | Vegetation | 892261 | 1 | 90.6833 | 90.6833 | 5.5201e-05 | 6.0873e-05
2012-10-25 | 512:48049 | SHORT RURAL | Other | 892265 | 1 | 132.95 | 132.95 | 8.093e-05 | 6.0873e-05
2012-10-24 | ZN15005:PA8 | URBAN | Operational Error | 892267 | 1538 | 4 | 6152 | 0.0037449 | 0.093622
2012-10-25 | 814:82283 | SHORT RURAL | Other | 892284 | 1 | 281.4833 | 281.4833 | 0.00017135 | 6.0873e-05
2012-10-25 | 510:48164 | SHORT RURAL | Other | 892287 | 4 | 118 | 472 | 0.00028732 | 0.00024349
2012-10-24 | 501:48123 | SHORT RURAL | Other | 892306 | 3 | 80 | 240 | 0.00014609 | 0.00018262
2012-10-24 | 512:48047 | SHORT RURAL | Third Party Impacts | 892314 | 5 | 15 | 75 | 4.5654e-05 | 0.00030436
2012-10-25 | 240:34835 | URBAN | Other | 892560 | 1 | 105.7167 | 105.7167 | 6.4352e-05 | 6.0873e-05
2012-10-25 | 501:48118 | SHORT RURAL | Other | 892571 | 1 | 128.4167 | 128.4167 | 7.817e-05 | 6.0873e-05
2012-10-25 | ZN14143:PA5 | URBAN | Equipment Failure | 892581 | 1 | 1041.1833 | 1041.1833 | 0.00063379 | 6.0873e-05
2012-10-25 | ZN167:PA2 | URBAN | Weather | 892602 | 1 | 224.7667 | 224.7667 | 0.00013682 | 6.0873e-05
2012-10-25 | ZN398:PA11 | URBAN | Equipment Failure | 892614 | 955 | 41 | 37770 | 0.022992 | 0.058133
2012-10-25 | 258:80793 | SHORT RURAL | Equipment Failure | 892622 | 33 | 1804.75 | 59556.75 | 0.036254 | 0.0020088
2012-10-25 | 203:8084 | URBAN | Equipment Failure | 892623 | 37 | 1419.2 | 52510.4 | 0.031964 | 0.0022523
2012-10-25 | 203:8085 | URBAN | Equipment Failure | 892623 | 1 | 1419.2 | 1411.6833 | 0.00085933 | 6.0873e-05
2012-10-25 | ZN188:PA42 | URBAN | Other | 892634 | 9 | 244.1 | 2196.9 | 0.0013373 | 0.00054785
2012-10-25 | ZN35500:PA16 | URBAN | Equipment Failure | 892649 | 1 | 45.65 | 10.6167 | 6.4626e-06 | 6.0873e-05
2012-10-25 | ZN4545:PA24 | URBAN | Equipment Failure | 892649 | 578 | 45.65 | 18496 | 0.011259 | 0.035184
2012-10-25 | ZN1287:PA17 | URBAN | Animals | 892684 | 1237 | 51 | 63087 | 0.038403 | 0.075299
2012-10-26 | ZN12570:PA1 | SHORT RURAL | Equipment Failure | 892698 | 112 | 271.15 | 30368.8 | 0.018486 | 0.0068177
2012-10-26 | 516:48067 | SHORT RURAL | Other | 892699 | 1 | 236.2833 | 236.2833 | 0.00014383 | 6.0873e-05
2012-10-26 | 802:82215 | SHORT RURAL | Other | 892701 | 40 | 78 | 3120 | 0.0018992 | 0.0024349
2012-10-26 | 802:82220 | SHORT RURAL | Other | 892701 | 60 | 78 | 4680 | 0.0028488 | 0.0036524
2012-10-26 | 802:82225 | SHORT RURAL | Other | 892701 | 105 | 78 | 8190 | 0.0049855 | 0.0063916
2012-10-26 | 810:74050 | SHORT RURAL | Other | 892701 | 91 | 78 | 7098 | 0.0043207 | 0.0055394
2012-10-26 | 810:74054 | LONG RURAL | Other | 892701 | 320 | 78 | 24960 | 0.015194 | 0.019479
2012-10-26 | 810:74058 | SHORT RURAL | Other | 892701 | 200 | 78 | 15600 | 0.0094961 | 0.012175
2012-10-26 | 810:74062 | SHORT RURAL | Other | 892701 | 607 | 78 | 47346 | 0.028821 | 0.03695
2012-10-26 | ZN2310:PA4 | URBAN | Third Party Impacts | 892710 | 1 | 222.5 | 222.5 | 0.00013544 | 6.0873e-05
2012-10-26 | 514:18137 | SHORT RURAL | Other | 892711 | 2 | 135 | 270 | 0.00016436 | 0.00012175
2012-10-26 | ZN12610:PA2 | URBAN | Vegetation | 892718 | 32 | 161 | 5152 | 0.0031362 | 0.0019479
2012-10-24 | ZN12610:PA9 | SHORT RURAL | Equipment Failure | 892734 | 37 | 1215 | 44955 | 0.027365 | 0.0022523
2012-10-26 | 214:8669 | URBAN | Other | 892790 | 1 | 181.4667 | 181.4667 | 0.00011046 | 6.0873e-05
2012-10-26 | ZN9035:PA7 | URBAN | Other | 892811 | 81 | 61 | 4941 | 0.0030077 | 0.0049307
2012-10-26 | 243:80081 | URBAN | Other | 892822 | 1 | 137.0167 | 137.0167 | 8.3406e-05 | 6.0873e-05
2012-10-26 | ZN14144:PA4 | URBAN | Other | 892865 | 1 | 133.3667 | 133.3667 | 8.1184e-05 | 6.0873e-05
2012-10-26 | ZN4545:PA36 | URBAN | Equipment Failure | 892893 | 1 | 209.2 | 209.2 | 0.00012735 | 6.0873e-05
2012-10-26 | 510:48164 | SHORT RURAL | Equipment Failure | 892903 | 1 | 167.9333 | 167.9333 | 0.00010223 | 6.0873e-05
2012-10-26 | 264:81236 | URBAN | Equipment Failure | 893066 | 1 | 100.8167 | 100.8167 | 6.137e-05 | 6.0873e-05
2012-10-26 | 524:33578 | URBAN | Other | 893067 | 1 | 183.2333 | 183.2333 | 0.00011154 | 6.0873e-05
2012-10-26 | 512:48047 | SHORT RURAL | Other | 893077 | 1 | 151 | 151 | 9.1918e-05 | 6.0873e-05
2012-10-26 | ZN1673:PA19 | URBAN | Vegetation | 893087 | 63 | 221 | 13923 | 0.0084753 | 0.003835
2012-10-26 | 220:8689 | URBAN | Other | 893101 | 1 | 96.2833 | 96.2833 | 5.861e-05 | 6.0873e-05
2012-10-27 | ZN3472:PA16 | URBAN | Equipment Failure | 893106 | 62 | 44 | 2530 | 0.0015401 | 0.0037741
2012-10-27 | ZN1610:PA26 | URBAN | Equipment Failure | 893136 | 1 | 230.1833 | 230.1833 | 0.00014012 | 6.0873e-05
2012-10-27 | 811:74234 | SHORT RURAL | Third Party Impacts | 893164 | 1 | 448 | 448 | 0.00027271 | 6.0873e-05
2012-10-27 | 229:34995 | SHORT RURAL | Other | 893179 | 1 | 137.05 | 137.05 | 8.3426e-05 | 6.0873e-05
2012-10-27 | ZN1164:PA26 | URBAN | Equipment Failure | 893198 | 51 | 268.05 | 13670.55 | 0.0083216 | 0.0031045
2012-10-27 | ZN1788:PA32 | URBAN | Other | 893202 | 1509 | 236 | 136488 | 0.083084 | 0.091857
2012-10-27 | ZN1788:PA6 | URBAN | Other | 893202 | 56 | 236 | 2688 | 0.0016363 | 0.0034089
2012-10-27 | ZN3672:PA44 | URBAN | Other | 893202 | 33 | 236 | 7611 | 0.004633 | 0.0020088
2012-10-27 | 224:80340 | SHORT RURAL | Other | 893216 | 1 | 107.2667 | 107.2667 | 6.5296e-05 | 6.0873e-05
2012-10-27 | ZN3922:PA18 | URBAN | Equipment Failure | 893220 | 71 | 287.75 | 20430.25 | 0.012436 | 0.004322
2012-10-28 | 511:29877 | SHORT RURAL | Other | 893269 | 1 | 106.75 | 106.75 | 6.4981e-05 | 6.0873e-05
2012-10-28 | ZN15015:PA5 | URBAN | Equipment Failure | 893280 | 1641 | 54 | 88031 | 0.053587 | 0.099892
2012-10-28 | 509:48039 | LONG RURAL | Vegetation | 893289 | 38 | 77 | 2926 | 0.0017811 | 0.0023132
2012-10-28 | 203:8085 | URBAN | Other | 893298 | 1 | 150.1667 | 150.1667 | 9.141e-05 | 6.0873e-05
2012-10-28 | ZN9550:PA35 | URBAN | Other | 893303 | 1 | 138.8833 | 138.8833 | 8.4542e-05 | 6.0873e-05
2012-10-28 | ZN384:PA3 | SHORT RURAL | Operational Error | 893309 | 903 | 203 | 39461 | 0.024021 | 0.054968
2012-10-28 | ZN7481:PA1 | URBAN | Operational Error | 893309 | 128 | 203 | 19662 | 0.011969 | 0.0077917
2012-10-28 | ZN7481:PA12 | URBAN | Operational Error | 893309 | 688 | 203 | 20640 | 0.012564 | 0.04188
2012-10-28 | ZN7481:PA13 | URBAN | Operational Error | 893309 | 430 | 203 | 12470 | 0.0075908 | 0.026175
2012-10-28 | ZN7481:PA14 | URBAN | Operational Error | 893309 | 426 | 203 | 12780 | 0.0077795 | 0.025932
2012-10-28 | ZN7481:PA16 | URBAN | Operational Error | 893309 | 97 | 203 | 2910 | 0.0017714 | 0.0059046
2012-10-28 | ZN7481:PA17 | URBAN | Operational Error | 893309 | 2213 | 203 | 78831 | 0.047986 | 0.13471
2012-10-28 | ZN7481:PA19 | URBAN | Operational Error | 893309 | 144 | 203 | 4176 | 0.002542 | 0.0087657
2012-10-28 | ZN7481:PA20 | URBAN | Operational Error | 893309 | 79 | 203 | 2370 | 0.0014427 | 0.0048089
2012-10-28 | ZN7481:PA21 | URBAN | Operational Error | 893309 | 121 | 203 | 3509 | 0.002136 | 0.0073656
2012-10-28 | 510:48164 | SHORT RURAL | Animals | 893351 | 1 | 105.6 | 105.6 | 6.4281e-05 | 6.0873e-05
2012-10-29 | ZN965:PA22 | URBAN | Other | 893354 | 561 | 94 | 48774 | 0.02969 | 0.03415
2012-10-29 | ZN1648:PA11 | URBAN | Other | 893355 | 52 | 99.65 | 5181.8 | 0.0031543 | 0.0031654
2012-10-29 | 520:48172 | SHORT RURAL | Animals | 893359 | 2 | 205 | 410 | 0.00024958 | 0.00012175
2012-10-29 | ZN2835:PA30 | URBAN | Other | 893362 | 1 | 265.3167 | 265.3167 | 0.00016151 | 6.0873e-05
2012-10-29 | ZN2635:PA16 | URBAN | Equipment Failure | 893366 | 72 | 185.4 | 13348.8 | 0.0081258 | 0.0043828
2012-10-29 | 501:48117 | URBAN | Equipment Failure | 893378 | 1 | 447.05 | 447.05 | 0.00027213 | 6.0873e-05
2012-10-29 | ZN12690:PA7 | SHORT RURAL | Other | 893405 | 1 | 150.5 | 150.5 | 9.1613e-05 | 6.0873e-05
2012-10-29 | 220:8692 | URBAN | Other | 893415 | 1 | 79.5333 | 79.5333 | 4.8414e-05 | 6.0873e-05
2012-10-29 | 520:48172 | SHORT RURAL | Equipment Failure | 893420 | 1 | 137.6167 | 137.6167 | 8.3771e-05 | 6.0873e-05
2012-10-25 | ZN1285:PA10 | URBAN | Equipment Failure | 893423 | 15 | 229 | 3435 | 0.002091 | 0.00091309
2012-10-29 | ZN1673:PA1 | URBAN | Vegetation | 893469 | 36 | 76.4333 | 2751.6 | 0.001675 | 0.0021914
2012-10-29 | ZN187:PA17 | URBAN | Other | 893513 | 1 | 70.2 | 70.2 | 4.2733e-05 | 6.0873e-05
2012-10-29 | 256:80647 | URBAN | Other | 893526 | 1 | 284.7333 | 284.7333 | 0.00017332 | 6.0873e-05
2012-10-29 | 514:18137 | SHORT RURAL | Other | 893543 | 1 | 102.2333 | 102.2333 | 6.2232e-05 | 6.0873e-05
2012-10-29 | 512:48046 | SHORT RURAL | Other | 893620 | 1 | 152 | 152 | 9.2526e-05 | 6.0873e-05
2012-10-29 | ZN690:PA28 | URBAN | Other | 893689 | 1 | 130.1 | 130.1 | 7.9195e-05 | 6.0873e-05
2012-10-29 | ZN262:PA6 | URBAN | Other | 893712 | 1 | 1623.7 | 1623.7 | 0.00098839 | 6.0873e-05
2012-10-29 | 512:48049 | SHORT RURAL | Other | 893714 | 1 | 181.8167 | 181.8167 | 0.00011068 | 6.0873e-05
2012-10-29 | 512:48049 | SHORT RURAL | Animals | 893719 | 2 | 156 | 312 | 0.00018992 | 0.00012175
2012-10-29 | ZN2310:PA33 | URBAN | Third Party Impacts | 893733 | 76 | 156 | 11856 | 0.0072171 | 0.0046263
2012-10-29 | ZN2635:PA21 | URBAN | Other | 893787 | 36 | 144.3833 | 5197.8 | 0.003164 | 0.0021914
2012-10-29 | ZN4545:PA27 | URBAN | Vegetation | 893792 | 1 | 444.5167 | 444.5167 | 0.00027059 | 6.0873e-05
2012-10-30 | 216:10728 | URBAN | Other | 893862 | 52 | 80 | 4160 | 0.0025317 | 0.0031647
2012-10-30 | ZN12620:PA10 | SHORT RURAL | Equipment Failure | 893909 | 31 | 174.1333 | 5398.1333 | 0.0032852 | 0.0018866
2012-10-30 | ZN2473:PA9 | URBAN | Vegetation | 893944 | 1 | 328.9167 | 328.9167 | 0.00020017 | 6.0859e-05
2012-10-26 | 813:89061 | LONG RURAL | Equipment Failure | 893974 | 3 | 115 | 345 | 0.00021001 | 0.00018262
2012-10-30 | 515:35197 | LONG RURAL | Other | 893975 | 2 | 114 | 228 | 0.00013876 | 0.00012172
2012-10-30 | ZN12570:PA33 | SHORT RURAL | Equipment Failure | 893991 | 1 | 27.1167 | 27.1167 | 1.6503e-05 | 6.0859e-05
2012-10-30 | 801:74121 | SHORT RURAL | Equipment Failure | 894003 | 1 | 277.9 | 277.9 | 0.00016913 | 6.0859e-05
2012-10-30 | ZN690:PA10 | URBAN | Other | 894028 | 547 | 9 | 4923 | 0.0029961 | 0.03329
2012-10-30 | ZN690:PA11 | URBAN | Other | 894028 | 2282 | 9 | 20538 | 0.012499 | 0.13888
2012-10-30 | ZN690:PA12 | URBAN | Other | 894028 | 1182 | 9 | 10638 | 0.0064742 | 0.071935
2012-10-30 | ZN690:PA14 | URBAN | Other | 894028 | 2185 | 9 | 19665 | 0.011968 | 0.13298
2012-10-30 | ZN690:PA15 | URBAN | Other | 894028 | 476 | 9 | 4284 | 0.0026072 | 0.028969
2012-10-30 | ZN690:PA3 | URBAN | Other | 894028 | 137 | 9 | 1233 | 0.00075039 | 0.0083377
2012-10-30 | ZN690:PA4 | URBAN | Other | 894028 | 2421 | 9 | 21789 | 0.013261 | 0.14734
2012-10-30 | ZN690:PA5 | URBAN | Other | 894028 | 461 | 9 | 4149 | 0.002525 | 0.028056
2012-10-30 | ZN690:PA6 | URBAN | Other | 894028 | 906 | 9 | 8154 | 0.0049624 | 0.055138
2012-10-30 | 216:10728 | URBAN | Equipment Failure | 894049 | 52 | 78.2667 | 4069.8667 | 0.0024769 | 0.0031647
2012-10-30 | ZN262:PA33 | URBAN | Other | 894252 | 1 | 104.4167 | 104.4167 | 6.3547e-05 | 6.0859e-05
2012-10-30 | 512:48046 | SHORT RURAL | Other | 894257 | 1 | 172.1833 | 172.1833 | 0.00010479 | 6.0859e-05
2012-10-30 | 225:13446 | URBAN | Other | 894267 | 1 | 89.95 | 89.95 | 5.4742e-05 | 6.0859e-05
2012-10-30 | ZN15002:PA2 | SHORT RURAL | Vegetation | 894285 | 33 | 180 | 5940 | 0.003615 | 0.0020083
2012-10-31 | 206:34435 | URBAN | Other | 894313 | 34 | 500 | 7700 | 0.0046861 | 0.0020692
2012-10-31 | ZN4545:PA6 | URBAN | Animals | 894322 | 154 | 131.15 | 20197.1 | 0.012292 | 0.0093723
2012-10-30 | ZN2196:PA6 | URBAN | Third Party Impacts | 894348 | 5 | 570 | 2850 | 0.0017345 | 0.00030429
2012-10-31 | ZN129:PA9 | URBAN | Third Party Impacts | 894436 | 1 | 99.2 | 99.2 | 6.0372e-05 | 6.0859e-05
2012-10-31 | ZN35600:PA12 | SHORT RURAL | Third Party Impacts | 894526 | 1 | 140.0167 | 140.0167 | 8.5213e-05 | 6.0859e-05
2012-10-31 | ZN4545:PA27 | URBAN | Equipment Failure | 894646 | 96 | 124 | 6372.6167 | 0.0038783 | 0.0058425
2012-10-31 | ZN4545:PA35 | URBAN | Equipment Failure | 894646 | 1186 | 124 | 138854 | 0.084505 | 0.072179
2012-10-31 | ZN4545:PA27 | URBAN | Equipment Failure | 894650 | 1 | 296.9167 | 296.9167 | 0.0001807 | 6.0859e-05
2012-10-31 | ZN1193:PA21 | URBAN | Vegetation | 894651 | 953 | 139 | 74183 | 0.045147 | 0.057998
2012-10-31 | ZN4545:PA27 | URBAN | Equipment Failure | 894652 | 1 | 171.4167 | 171.4167 | 0.00010432 | 6.0859e-05
2012-10-31 | 512:48049 | SHORT RURAL | Equipment Failure | 894657 | 2 | 133.8333 | 267.6667 | 0.0001629 | 0.00012172
2012-10-31 | ZN12600:PA13 | SHORT RURAL | Vegetation | 894670 | 851 | 16 | 13616 | 0.0082865 | 0.051791
2012-10-31 | ZN12690:PA12 | SHORT RURAL | Equipment Failure | 894684 | 1 | 100.8167 | 100.8167 | 6.1356e-05 | 6.0859e-05
2012-10-31 | 807:74184 | SHORT RURAL | Other | 894723 | 2 | 106 | 212 | 0.00012902 | 0.00012172
2012-10-31 | ZN1285:PA27 | URBAN | Third Party Impacts | 894759 | 14 | 228 | 3192 | 0.0019426 | 0.00085202
2012-10-31 | ZN2473:PA25 | URBAN | Other | 894763 | 1 | 43.2833 | 43.2833 | 2.6342e-05 | 6.0859e-05
2012-10-31 | ZN12610:PA13 | URBAN | Operational Error | 894769 | 774 | 7 | 4644 | 0.0028263 | 0.047105
2012-10-31 | ZN12620:PA1 | SHORT RURAL | Operational Error | 894769 | 976 | 7 | 6832 | 0.0041579 | 0.059398
2012-10-31 | ZN10993:PA2 | URBAN | Other | 894777 | 1 | 66 | 61 | 3.7124e-05 | 6.0859e-05
2012-10-31 | ZN10999:PA24 | URBAN | Other | 894777 | 2408 | 66 | 147122 | 0.089537 | 0.14655
2012-10-31 | ZN10999:PA7 | URBAN | Other | 894777 | 2 | 66 | 122 | 7.4248e-05 | 0.00012172
2012-11-01 | ZN1788:PA14 | URBAN | Weather | 894793 | 1 | 262.2 | 262.2 | 0.00015957 | 6.0859e-05
2012-11-01 | ZN1193:PA6 | URBAN | Vegetation | 894803 | 1 | 282.65 | 282.65 | 0.00017202 | 6.0859e-05
2012-11-01 | ZN340:PA3 | URBAN | Third Party Impacts | 894816 | 5 | 86.0167 | 430.0833 | 0.00026175 | 0.0003043
2012-11-01 | ZN15015:PA15 | URBAN | Animals | 894820 | 1 | 190.75 | 190.75 | 0.00011609 | 6.0859e-05
2012-11-01 | ZN10993:PA12 | URBAN | Other | 894827 | 1 | 169.5 | 169.5 | 0.00010316 | 6.0859e-05
2012-11-01 | ZN1285:PA24 | URBAN | Equipment Failure | 894914 | 1 | 277.4833 | 277.4833 | 0.00016887 | 6.0859e-05
2012-11-01 | 216:10723 | URBAN | Other | 894978 | 705 | 57 | 40185 | 0.024456 | 0.042906
2012-11-01 | 216:10724 | SHORT RURAL | Other | 894978 | 762 | 57 | 43434 | 0.026434 | 0.046375
2012-11-01 | 216:10726 | URBAN | Other | 894978 | 761 | 57 | 43377 | 0.026399 | 0.046314
2012-11-01 | 216:10727 | URBAN | Other | 894978 | 1476 | 57 | 84132 | 0.051202 | 0.089828
2012-11-01 | 216:10728 | URBAN | Other | 894978 | 793 | 57 | 45201 | 0.027509 | 0.048261
2012-11-01 | 216:10729 | URBAN | Other | 894978 | 981 | 57 | 55917 | 0.034031 | 0.059703
2012-11-01 | 224:80340 | SHORT RURAL | Other | 894978 | 1058 | 57 | 60306 | 0.036702 | 0.064389
2012-11-01 | ZN847:PA46 | URBAN | Vegetation | 895019 | 1 | 219.8167 | 219.8167 | 0.00013378 | 6.0859e-05
2012-11-01 | ZN10994:PA12 | URBAN | Equipment Failure | 895028 | 1 | 34.0167 | 34.0167 | 2.0702e-05 | 6.0859e-05
2012-11-01 | 224:80340 | SHORT RURAL | Other | 895069 | 1070 | 59 | 63130 | 0.03842 | 0.065119
2012-11-01 | ZN3155:PA33 | URBAN | Other | 895086 | 87 | 306.0667 | 26627.8 | 0.016205 | 0.0052948
2012-11-01 | ZN874:PA25 | URBAN | Weather | 895169 | 38 | 132 | 5016 | 0.0030527 | 0.0023126
2012-11-01 | ZN12630:PA1 | SHORT RURAL | Vegetation | 895173 | 1 | 298.65 | 298.65 | 0.00018176 | 6.0859e-05
2012-11-01 | 514:18137 | SHORT RURAL | Other | 895181 | 252 | 71 | 17892 | 0.010889 | 0.015337
2012-11-01 | ZN10995:PA8 | URBAN | Other | 895196 | 1 | 157.0333 | 157.0333 | 9.5569e-05 | 6.0859e-05
2012-11-01 | ZN12570:PA35 | URBAN | Vegetation | 895197 | 1 | 707.9167 | 707.9167 | 0.00043083 | 6.0859e-05
2012-11-01 | ZN10999:PA3 | URBAN | Weather | 895203 | 184 | 51.6667 | 9506.6667 | 0.0057857 | 0.011198
2012-11-01 | ZN12650:PA20 | URBAN | Other | 895205 | 1 | 65.8167 | 65.8167 | 4.0055e-05 | 6.0859e-05
2012-11-01 | ZN2466:PA5 | URBAN | Animals | 895214 | 2 | 125 | 249.5 | 0.00015184 | 0.00012172
2012-11-01 | 803:74016 | SHORT RURAL | Other | 895217 | 1 | 46.1833 | 46.1833 | 2.8107e-05 | 6.0859e-05
2012-11-02 | ZN9118:PA2 | URBAN | Vegetation | 895223 | 82 | 82 | 6724 | 0.0040922 | 0.0049905
2012-11-02 | ZN9118:PA2 | URBAN | Vegetation | 895234 | 1 | 449.35 | 449.35 | 0.00027347 | 6.0859e-05
2012-11-02 | ZN10996:PA9 | URBAN | Third Party Impacts | 895236 | 1 | 92.7667 | 92.7667 | 5.6457e-05 | 6.0859e-05
2012-11-02 | ZN12640:PA6 | URBAN | Equipment Failure | 895238 | 1 | 195.5167 | 195.5167 | 0.00011899 | 6.0859e-05
2012-11-02 | ZN116:PA32 | URBAN | Other | 895242 | 1 | 185.8167 | 185.8167 | 0.00011309 | 6.0859e-05
2012-11-02 | ZN72:PA15 | URBAN | Equipment Failure | 895243 | 67 | 350 | 23450 | 0.014272 | 0.0040776
2012-11-02 | 523:33501 | SHORT RURAL | Equipment Failure | 895249 | 1 | 149.0333 | 149.0333 | 9.0701e-05 | 6.0859e-05
2012-11-02 | 256:80650 | URBAN | Equipment Failure | 895251 | 83 | 75.85 | 6295.55 | 0.0038314 | 0.0050513
2012-11-02 | 523:33501 | SHORT RURAL | Equipment Failure | 895252 | 1 | 143.8 | 143.8 | 8.7516e-05 | 6.0859e-05
2012-11-02 | 516:48065 | SHORT RURAL | Other | 895255 | 1 | 185.3833 | 185.3833 | 0.00011282 | 6.0859e-05
2012-11-02 | ZN12590:PA2 | URBAN | Other | 895259 | 1 | 129.65 | 129.65 | 7.8904e-05 | 6.0859e-05
2012-11-02 | 235:2120 | SHORT RURAL | Third Party Impacts | 895265 | 1 | 129.2833 | 129.2833 | 7.8681e-05 | 6.0859e-05
2012-11-02 | ZN15002:PA8 | URBAN | Vegetation | 895290 | 73 | 124 | 9052 | 0.005509 | 0.0044427
2012-11-02 | ZN14892:PA16 | URBAN | Other | 895305 | 1 | 253.1667 | 253.1667 | 0.00015408 | 6.0859e-05
2012-11-02 | ZN4545:PA31 | URBAN | Third Party Impacts | 895369 | 53 | 140 | 7396.6 | 0.0045015 | 0.0032255
2012-11-02 | ZN15014:PA22 | URBAN | Other | 895370 | 1 | 4.8167 | 4.8167 | 2.9314e-06 | 6.0859e-05
2012-11-02 | ZN1850:PA11 | URBAN | Equipment Failure | 895392 | 8 | 35 | 280 | 0.00017041 | 0.00048687
2012-11-02 | ZN1850:PA14 | URBAN | Equipment Failure | 895392 | 426 | 35 | 14910 | 0.0090741 | 0.025926
2012-11-02 | 512:48046 | SHORT RURAL | Other | 895398 | 1 | 219.6 | 219.6 | 0.00013365 | 6.0859e-05
2012-11-02 | 512:48049 | SHORT RURAL | Animals | 895426 | 2 | 105 | 210 | 0.0001278 | 0.00012172
2012-11-02 | ZN4545:PA27 | URBAN | Vegetation | 895438 | 1 | 281.5167 | 281.5167 | 0.00017133 | 6.0859e-05
2012-11-02 | ZN4545:PA27 | URBAN | Vegetation | 895440 | 1 | 278.5333 | 278.5333 | 0.00016951 | 6.0859e-05
2012-11-02 | ZN262:PA7 | URBAN | Weather | 895442 | 134 | 126.4667 | 16946.5333 | 0.010314 | 0.0081551
2012-11-02 | ZN262:PA15 | URBAN | Third Party Impacts | 895486 | 62 | 101 | 6262 | 0.003811 | 0.0037733
2012-11-02 | ZN2635:PA3 | URBAN | Other | 895493 | 1 | 90.7333 | 90.7333 | 5.522e-05 | 6.0859e-05
2012-11-02 | ZN15001:PA18 | URBAN | Other | 895526 | 1 | 427.95 | 427.95 | 0.00026045 | 6.0859e-05
2012-11-02 | ZN690:PA11 | URBAN | Equipment Failure | 895571 | 1 | 221.8333 | 221.8333 | 0.00013501 | 6.0859e-05
2012-11-03 | ZN9700:PA15 | URBAN | Other | 895648 | 1 | 560.3 | 560.3 | 0.00034099 | 6.0859e-05
2012-11-03 | ZN10994:PA1 | URBAN | Other | 895650 | 1 | 547.1167 | 547.1167 | 0.00033297 | 6.0859e-05
2012-11-03 | ZN9252:PA11 | URBAN | Other | 895652 | 1 | 492.9833 | 492.9833 | 0.00030003 | 6.0859e-05
2012-11-03 | ZN2196:PA25 | URBAN | Equipment Failure | 895653 | 1 | 828.4667 | 828.4667 | 0.0005042 | 6.0859e-05
2012-11-03 | ZN9252:PA11 | URBAN | Other | 895654 | 1 | 42.55 | 42.55 | 2.5896e-05 | 6.0859e-05
2012-11-03 | ZN2196:PA9 | URBAN | Equipment Failure | 895656 | 1 | 900.0833 | 900.0833 | 0.00054778 | 6.0859e-05
2012-11-03 | ZN9037:PA8 | URBAN | Other | 895669 | 1 | 380.9333 | 380.9333 | 0.00023183 | 6.0859e-05
2012-11-03 | ZN384:PA33 | URBAN | Other | 895679 | 34 | 58 | 1972 | 0.0012001 | 0.0020692
2012-11-03 | ZN9700:PA23 | URBAN | Equipment Failure | 895686 | 1 | 426.0333 | 426.0333 | 0.00025928 | 6.0859e-05
2012-11-03 | ZN36300:PA3 | URBAN | Other | 895688 | 1 | 297.5167 | 297.5167 | 0.00018107 | 6.0859e-05
2012-11-03 | ZN1287:PA21 | URBAN | Equipment Failure | 895692 | 1 | 344.8667 | 344.8667 | 0.00020988 | 6.0859e-05
2012-11-03 | 205:12203 | URBAN | Animals | 895696 | 62 | 42.6833 | 2646.3667 | 0.0016106 | 0.0037733
2012-11-03 | ZN2196:PA9 | URBAN | Equipment Failure | 895717 | 1 | 560.55 | 560.55 | 0.00034115 | 6.0859e-05
2012-11-03 | ZN129:PA18 | URBAN | Other | 895720 | 1 | 525.8667 | 525.8667 | 0.00032004 | 6.0859e-05
2012-11-03 | ZN3472:PA31 | URBAN | Other | 895722 | 1 | 303.9 | 303.9 | 0.00018495 | 6.0859e-05
2012-11-03 | ZN2835:PA16 | URBAN | Other | 895725 | 21 | 75.8833 | 1593.55 | 0.00096982 | 0.001278
2012-11-03 | ZN36300:PA11 | URBAN | Other | 895739 | 1 | 286.3167 | 286.3167 | 0.00017425 | 6.0859e-05
2012-11-03 | ZN690:PA26 | URBAN | Other | 895742 | 1 | 234.9333 | 234.9333 | 0.00014298 | 6.0859e-05
2012-11-03 | ZN1290:PA4 | URBAN | Equipment Failure | 895746 | 1 | 578.3833 | 578.3833 | 0.000352 | 6.0859e-05
2012-11-03 | 227:13015 | SHORT RURAL | Other | 895752 | 1 | 114.0333 | 114.0333 | 6.94e-05 | 6.0859e-05
2012-11-03 | ZN4545:PA41 | URBAN | Equipment Failure | 895754 | 1 | 408.9333 | 408.9333 | 0.00024887 | 6.0859e-05
2012-11-03 | ZN1193:PA7 | URBAN | Other | 895756 | 1 | 281.55 | 281.55 | 0.00017135 | 6.0859e-05
2012-11-03 | 502:48008 | URBAN | Other | 895758 | 1 | 128.6833 | 128.6833 | 7.8316e-05 | 6.0859e-05
2012-11-03 | ZN15008:PA5 | URBAN | Equipment Failure | 895763 | 51 | 106 | 5405.3167 | 0.0032896 | 0.0031038
2012-11-03 | ZN847:PA1 | URBAN | Other | 895769 | 1 | 500.25 | 500.25 | 0.00030445 | 6.0859e-05
2012-11-03 | ZN9118:PA26 | URBAN | Other | 895778 | 1 | 497.1333 | 497.1333 | 0.00030255 | 6.0859e-05
2012-11-03 | ZN1287:PA24 | URBAN | Other | 895779 | 1 | 544.5167 | 544.5167 | 0.00033139 | 6.0859e-05
2012-11-03 | ZN1287:PA24 | URBAN | Other | 895784 | 1 | 534.05 | 534.05 | 0.00032502 | 6.0859e-05
2012-11-03 | 516:48065 | SHORT RURAL | Other | 895806 | 1 | 232 | 232 | 0.00014119 | 6.0859e-05
2012-11-03 | ZN15014:PA11 | URBAN | Other | 895847 | 1 | 242.5333 | 242.5333 | 0.0001476 | 6.0859e-05
2012-11-03 | ZN3922:PA17 | SHORT RURAL | Equipment Failure | 895849 | 1 | 973.8833 | 973.8833 | 0.0005927 | 6.0859e-05
2012-11-03 | 232:11457 | URBAN | Other | 895858 | 1 | 254.6167 | 254.6167 | 0.00015496 | 6.0859e-05
2012-11-04 | ZN12570:PA1 | SHORT RURAL | Other | 895863 | 1 | 259.1833 | 259.1833 | 0.00015774 | 6.0859e-05
2012-11-04 | ZN9118:PA21 | URBAN | Other | 895865 | 1 | 693.5833 | 693.5833 | 0.00042211 | 6.0859e-05
2012-11-04 | ZN9252:PA4 | URBAN | Other | 895867 | 1 | 351.7 | 351.7 | 0.00021404 | 6.0859e-05
2012-11-04 | ZN3155:PA24 | URBAN | Other | 895869 | 1 | 525.4833 | 525.4833 | 0.00031981 | 6.0859e-05
2012-11-04 | ZN3155:PA35 | URBAN | Other | 895871 | 1 | 704.0167 | 704.0167 | 0.00042846 | 6.0859e-05
2012-11-04 | ZN10991:PA12 | URBAN | Other | 895872 | 1 | 165.9333 | 165.9333 | 0.00010099 | 6.0859e-05
2012-11-04 | ZN116:PA47 | URBAN | Other | 895881 | 1 | 365.0833 | 365.0833 | 0.00022219 | 6.0859e-05
2012-11-04 | 515:35197 | LONG RURAL | Third Party Impacts | 895893 | 23 | 85.8167 | 1973.7833 | 0.0012012 | 0.0013998
2012-11-04 | ZN398:PA29 | URBAN | Equipment Failure | 895900 | 1 | 280.0833 | 280.0833 | 0.00017046 | 6.0859e-05
2012-11-04 | 256:80644 | URBAN | Other | 895948 | 1 | 31.55 | 31.55 | 1.9201e-05 | 6.0859e-05
2012-11-04 | 232:33413 | SHORT RURAL | Other | 895950 | 1 | 136.15 | 136.15 | 8.286e-05 | 6.0859e-05
2012-11-04 | ZN9252:PA11 | URBAN | Other | 895953 | 1 | 179.5667 | 179.5667 | 0.00010928 | 6.0859e-05
2012-11-04 | ZN8700:PA61 62GHJ | CBD | Other | 895956 | 39 | 51 | 1989 | 0.0012105 | 0.0023735
2012-11-04 | ZN12600:PA2 | SHORT RURAL | Equipment Failure | 895958 | 5 | 140 | 700 | 0.00042602 | 0.0003043
2012-11-04 | 243:80080 | SHORT RURAL | Vegetation | 895964 | 1 | 105.65 | 105.65 | 6.4298e-05 | 6.0859e-05
2012-11-04 | ZN14892:PA14 | SHORT RURAL | Equipment Failure | 895971 | 36 | 120 | 4320 | 0.0026291 | 0.0021909
2012-11-04 | 264:81240 | SHORT RURAL | Other | 895979 | 1 | 132 | 132 | 8.0334e-05 | 6.0859e-05
2012-11-04 | ZN180:PA31 | URBAN | Equipment Failure | 895981 | 1 | 249.9 | 249.9 | 0.00015209 | 6.0859e-05
2012-11-04 | ZN10999:PA10 | URBAN | Equipment Failure | 895990 | 27 | 675 | 18225 | 0.011092 | 0.0016432
2012-11-04 | ZN129:PA3 | URBAN | Animals | 895993 | 1406 | 167 | 220254 | 0.13405 | 0.085568
2012-11-05 | 220:8689 | URBAN | Other | 895997 | 81 | 41 | 3321 | 0.0020211 | 0.0049296
2012-11-05 | 202:34250 | URBAN | Animals | 896000 | 179 | 229.4167 | 34189 | 0.020807 | 0.010894
2012-11-05 | 202:34254 | URBAN | Animals | 896000 | 98 | 229.4167 | 12965.4 | 0.0078907 | 0.0059642
2012-11-05 | 814:82283 | SHORT RURAL | Equipment Failure | 896001 | 188 | 40 | 7520 | 0.0045766 | 0.011442
2012-11-05 | ZN9037:PA2 | URBAN | Other | 896014 | 1 | 125.7 | 125.7 | 7.65e-05 | 6.0859e-05
2012-11-05 | 512:48049 | SHORT RURAL | Other | 896024 | 1 | 220.9333 | 220.9333 | 0.00013446 | 6.0859e-05
2012-11-05 | 217:33607 | SHORT RURAL | Other | 896082 | 43 | 45 | 1935 | 0.0011776 | 0.002617
2012-11-05 | ZN36300:PA5 | URBAN | Equipment Failure | 896096 | 1 | 265.4167 | 265.4167 | 0.00016153 | 6.0859e-05
2012-11-05 | ZN12570:PA11 | URBAN | Third Party Impacts | 896133 | 1 | 328.3333 | 328.3333 | 0.00019982 | 6.0859e-05
2012-11-05 | 256:80640 | URBAN | Other | 896148 | 1 | 92.1833 | 92.1833 | 5.6102e-05 | 6.0859e-05
2012-11-05 | ZN2568:PA9 | URBAN | Other | 896163 | 1 | 136.2833 | 136.2833 | 8.2941e-05 | 6.0859e-05
2012-11-02 | 229:34995 | SHORT RURAL | Other | 896177 | 16 | 30 | 480 | 0.00029212 | 0.00097375
2012-11-05 | ZN1164:PA13 | URBAN | Other | 896187 | 1 | 231.7833 | 231.7833 | 0.00014106 | 6.0859e-05
2012-11-05 | 214:8671 | URBAN | Other | 896197 | 23 | 39.0667 | 898.5333 | 0.00054684 | 0.0013998
2012-11-05 | ZN1285:PA27 | URBAN | Equipment Failure | 896214 | 1 | 568.9667 | 568.9667 | 0.00034627 | 6.0859e-05
2012-11-05 | ZN384:PA9 | URBAN | Other | 896264 | 1 | 47.05 | 47.05 | 2.8634e-05 | 6.0859e-05
2012-11-02 | 515:35192 | SHORT RURAL | Equipment Failure | 896298 | 1 | 55 | 55 | 3.3473e-05 | 6.0859e-05
2012-11-05 | 524:33572 | SHORT RURAL | Other | 896307 | 140 | 52 | 7280 | 0.0044306 | 0.0085203
2012-11-02 | ZN1290:PA16 | URBAN | Third Party Impacts | 896312 | 27 | 61 | 1647 | 0.0010024 | 0.0016432
2012-11-05 | ZN9037:PA9 | URBAN | Vegetation | 896317 | 21 | 142 | 2982 | 0.0018148 | 0.001278
2012-11-03 | 814:82283 | SHORT RURAL | Equipment Failure | 896319 | 188 | 56 | 10528 | 0.0064073 | 0.011442
2012-11-05 | ZN4545:PA44 | URBAN | Third Party Impacts | 896393 | 1 | 1116.8667 | 1116.8667 | 0.00067972 | 6.0859e-05
2012-11-05 | ZN14891:PA10 | SHORT RURAL | Vegetation | 896431 | 1 | 219.5333 | 219.5333 | 0.00013361 | 6.0859e-05
2012-11-05 | ZN12600:PA13 | SHORT RURAL | Equipment Failure | 896442 | 1 | 100.55 | 100.55 | 6.1194e-05 | 6.0859e-05
2012-11-05 | 524:33572 | SHORT RURAL | Equipment Failure | 896458 | 14 | 191.1167 | 2675.6333 | 0.0016284 | 0.00085203
2012-11-05 | 238:34141 | SHORT RURAL | Other | 896459 | 1 | 112.3333 | 112.3333 | 6.8365e-05 | 6.0859e-05
2012-11-05 | ZN188:PA20 | URBAN | Vegetation | 896489 | 11 | 88.4333 | 972.7667 | 0.00059202 | 0.00066945
2012-11-05 | ZN15010:PA7 | URBAN | Other | 896506 | 1 | 173.5167 | 173.5167 | 0.0001056 | 6.0859e-05
2012-11-06 | ZN15010:PA7 | URBAN | Vegetation | 896508 | 88 | 30 | 2640 | 0.0016064 | 0.0053547
2012-11-05 | ZN342:PA15 | URBAN | Other | 896517 | 10 | 55 | 550 | 0.00033473 | 0.00060859
2012-11-05 | ZN342:PA23 | URBAN | Other | 896517 | 15 | 55 | 825 | 0.00050209 | 0.00091289
2012-11-06 | ZN180:PA10 | URBAN | Equipment Failure | 896527 | 63 | 56.0833 | 3533.25 | 0.0021499 | 0.0038334
2012-11-05 | 803:74016 | SHORT RURAL | Other | 896556 | 1 | 65 | 65 | 3.9559e-05 | 6.0859e-05
2012-11-05 | 512:48049 | SHORT RURAL | Equipment Failure | 896559 | 2 | 58 | 116 | 7.0597e-05 | 0.00012172
2012-11-05 | 514:18137 | SHORT RURAL | Equipment Failure | 896563 | 5 | 70 | 350 | 0.00021301 | 0.0003043
2012-11-06 | ZN15008:PA10 | URBAN | Other | 896569 | 1 | 174.7333 | 174.7333 | 0.00010632 | 6.0848e-05
2012-11-06 | ZN15010:PA7 | URBAN | Third Party Impacts | 896571 | 1 | 352.6 | 352.6 | 0.00021455 | 6.0848e-05
2012-11-06 | ZN15002:PA6 | URBAN | Other | 896577 | 1 | 420.05 | 420.05 | 0.00025559 | 6.0848e-05
2012-11-06 | ZN340:PA27 | URBAN | Other | 896610 | 58 | 78 | 4524 | 0.0027528 | 0.0035292
2012-11-06 | ZN630:PA14 | SHORT RURAL | Other | 896610 | 11 | 78 | 858 | 0.00052208 | 0.00066933
2012-11-06 | ZN129:PA24 | URBAN | Other | 896613 | 125 | 230.5167 | 21095.2333 | 0.012836 | 0.007606
2012-11-06 | ZN129:PA9 | URBAN | Other | 896613 | 1 | 230.5167 | 210.9 | 0.00012833 | 6.0848e-05
2012-11-06 | ZN12690:PA10 | URBAN | Other | 896718 | 1 | 83.55 | 83.55 | 5.0839e-05 | 6.0848e-05
2012-11-06 | 516:48065 | SHORT RURAL | Other | 896739 | 1 | 147 | 147 | 8.9447e-05 | 6.0848e-05
2012-11-06 | ZN1648:PA4 | URBAN | Equipment Failure | 896766 | 640 | 77 | 49280 | 0.029986 | 0.038943
2012-11-06 | ZN12610:PA25 | SHORT RURAL | Equipment Failure | 896827 | 418 | 41 | 17138 | 0.010428 | 0.025435
2012-11-06 | 260:33347 | SHORT RURAL | Other | 896846 | 1 | 152.1333 | 152.1333 | 9.2571e-05 | 6.0848e-05
2012-11-05 | ZN384:PA9 | URBAN | Other | 896857 | 2 | 245 | 490 | 0.00029821 | 0.00012172
2012-11-06 | ZN1850:PA13 | URBAN | Third Party Impacts | 896864 | 1 | 238.9167 | 238.9167 | 0.00014538 | 6.0848e-05
2012-11-06 | ZN12660:PA5 | SHORT RURAL | Equipment Failure | 896880 | 32 | 113 | 3616 | 0.0022003 | 0.0019471
2012-11-06 | ZN340:PA27 | URBAN | Equipment Failure | 896888 | 58 | 282 | 16356 | 0.0099524 | 0.0035292
2012-11-06 | ZN630:PA14 | SHORT RURAL | Equipment Failure | 896888 | 10 | 282 | 2820 | 0.0017159 | 0.00060848
2012-11-06 | ZN262:PA40 | URBAN | Equipment Failure | 896890 | 520 | 35 | 18200 | 0.011074 | 0.031641
2012-11-06 | 235:2120 | SHORT RURAL | Other | 896893 | 1 | 113.15 | 113.15 | 6.885e-05 | 6.0848e-05
2012-11-06 | 219:1740 | SHORT RURAL | Other | 896940 | 1 | 114.8 | 114.8 | 6.9854e-05 | 6.0848e-05
2012-11-06 | 232:11454 | SHORT RURAL | Other | 896947 | 1 | 136.5667 | 136.5667 | 8.3099e-05 | 6.0848e-05
2012-11-06 | ZN262:PA15 | URBAN | Vegetation | 896957 | 87 | 165 | 14301.9667 | 0.0087025 | 0.0052938
2012-11-06 | ZN342:PA15 | URBAN | Equipment Failure | 896972 | 10 | 71 | 710 | 0.00043202 | 0.00060848
2012-11-06 | ZN342:PA23 | URBAN | Equipment Failure | 896972 | 23 | 71 | 1633 | 0.00099365 | 0.0013995
2012-11-06 | 232:11454 | SHORT RURAL | Other | 896983 | 1 | 84.9167 | 84.9167 | 5.167e-05 | 6.0848e-05
2012-11-06 | ZN35370:PA2 | SHORT RURAL | Equipment Failure | 897003 | 1 | 132.0333 | 132.0333 | 8.034e-05 | 6.0848e-05
2012-11-06 | ZN1068:PA26 | URBAN | Equipment Failure | 897007 | 13 | 577.55 | 7508.15 | 0.0045686 | 0.00079103
2012-11-06 | 264:81240 | SHORT RURAL | Other | 897012 | 2 | 167 | 333.4667 | 0.00020291 | 0.0001217
2012-11-06 | ZN2602:PA21 | URBAN | Equipment Failure | 897024 | 41 | 72 | 2419 | 0.0014719 | 0.0024948
2012-11-06 | ZN2602:PA30 | URBAN | Equipment Failure | 897024 | 1923 | 72 | 130383 | 0.079336 | 0.11701
2012-11-06 | ZN847:PA18 | URBAN | Equipment Failure | 897025 | 638 | 103 | 65714 | 0.039986 | 0.038821
2012-11-06 | ZN2602:PA8 | URBAN | Other | 897026 | 1 | 71.5167 | 71.5167 | 4.3517e-05 | 6.0848e-05
2012-11-07 | ZN12580:PA10 | URBAN | Other | 897057 | 1488 | 86 | 127968 | 0.077867 | 0.090543
2012-11-07 | ZN9252:PA12 | URBAN | Other | 897059 | 1 | 187.6167 | 187.6167 | 0.00011416 | 6.0848e-05
2012-11-07 | ZN9252:PA12 | URBAN | Other | 897060 | 1 | 172.4333 | 172.4333 | 0.00010492 | 6.0848e-05
2012-11-07 | ZN3154:PA19 | URBAN | Other | 897118 | 1 | 320.0333 | 320.0333 | 0.00019474 | 6.0848e-05
2012-11-06 | ZN12610:PA25 | SHORT RURAL | Equipment Failure | 897147 | 309 | 4 | 1236 | 0.00075209 | 0.018802
2012-11-07 | ZN262:PA13 | URBAN | Other | 897157 | 1 | 201.7167 | 201.7167 | 0.00012274 | 6.0848e-05
2012-11-07 | 219:1783 | SHORT RURAL | Equipment Failure | 897249 | 39 | 39.2167 | 1529.45 | 0.00093065 | 0.0023731
2012-11-07 | 219:1783 | SHORT RURAL | Other | 897285 | 1 | 119.6667 | 119.6667 | 7.2815e-05 | 6.0848e-05
2012-11-07 | ZN12600:PA13 | SHORT RURAL | Equipment Failure | 897293 | 7 | 122 | 854 | 0.00051965 | 0.00042594
2012-11-07 | 219:1783 | SHORT RURAL | Other | 897295 | 1 | 125.4667 | 125.4667 | 7.6345e-05 | 6.0848e-05
2012-11-07 | ZN15002:PA2 | SHORT RURAL | Vegetation | 897311 | 1 | 72.3167 | 72.3167 | 4.4004e-05 | 6.0848e-05
2012-11-03 | ZN35500:PA34 | URBAN | Equipment Failure | 897328 | 315 | 154 | 29695 | 0.018072 | 0.019171
2012-11-07 | 216:10728 | URBAN | Other | 897335 | 1 | 88.7667 | 88.7667 | 5.4013e-05 | 6.0848e-05
2012-11-07 | ZN2400:PA26 | URBAN | Weather | 897438 | 953 | 113 | 97801 | 0.05951 | 0.057989
2012-11-07 | 501:48115 | SHORT RURAL | Other | 897461 | 1 | 134.2833 | 134.2833 | 8.1709e-05 | 6.0848e-05
2012-11-07 | 515:35192 | SHORT RURAL | Other | 897462 | 1 | 222.0833 | 222.0833 | 0.00013513 | 6.0848e-05
2012-11-07 | ZN12610:PA22 | URBAN | Other | 897463 | 1 | 444.85 | 444.85 | 0.00027068 | 6.0848e-05
2012-11-07 | ZN14892:PA19 | URBAN | Other | 897464 | 1 | 59.7333 | 59.7333 | 3.6347e-05 | 6.0848e-05
2012-11-07 | ZN14892:PA19 | URBAN | Other | 897466 | 1 | 46.25 | 46.25 | 2.8142e-05 | 6.0848e-05
2012-11-07 | ZN12610:PA22 | URBAN | Other | 897467 | 1 | 1338.85 | 1338.85 | 0.00081467 | 6.0848e-05
2012-11-07 | 501:48115 | SHORT RURAL | Other | 897471 | 1 | 452.3167 | 452.3167 | 0.00027523 | 6.0848e-05
2012-11-07 | ZN12610:PA7 | URBAN | Other | 897472 | 1 | 1454.5333 | 1454.5333 | 0.00088506 | 6.0848e-05
2012-11-07 | 224:80337 | URBAN | Other | 897483 | 1 | 299.2833 | 299.2833 | 0.00018211 | 6.0848e-05
2012-11-07 | 520:48172 | SHORT RURAL | Other | 897485 | 1 | 165.2333 | 165.2333 | 0.00010054 | 6.0848e-05
2012-11-07 | 501:48123 | SHORT RURAL | Other | 897492 | 1 | 167.6 | 167.6 | 0.00010198 | 6.0848e-05
2012-11-07 | 235:2123 | URBAN | Other | 897496 | 1 | 186.15 | 186.15 | 0.00011327 | 6.0848e-05
2012-11-07 | ZN14891:PA5 | SHORT RURAL | Vegetation | 897497 | 81 | 147 | 10059 | 0.0061208 | 0.0049287
2012-11-07 | 219:1785 | URBAN | Other | 897499 | 1 | 83.9 | 83.9 | 5.1052e-05 | 6.0848e-05
2012-11-07 | ZN12620:PA11 | SHORT RURAL | Other | 897505 | 1 | 362.0833 | 362.0833 | 0.00022032 | 6.0848e-05
2012-11-07 | ZN14891:PA10 | SHORT RURAL | Other | 897506 | 1 | 357.9167 | 357.9167 | 0.00021779 | 6.0848e-05
2012-11-07 | 501:48122 | SHORT RURAL | Other | 897508 | 1 | 259 | 259 | 0.0001576 | 6.0848e-05
2012-11-07 | 515:35192 | SHORT RURAL | Other | 897511 | 4 | 80 | 320 | 0.00019472 | 0.00024339
2012-11-07 | 501:48123 | SHORT RURAL | Other | 897517 | 1 | 120.8 | 120.8 | 7.3505e-05 | 6.0848e-05
2012-11-07 | 232:11457 | URBAN | Other | 897519 | 1 | 279.9333 | 279.9333 | 0.00017034 | 6.0848e-05
2012-11-07 | 229:34995 | SHORT RURAL | Other | 897526 | 1 | 348.5 | 348.5 | 0.00021206 | 6.0848e-05
2012-11-07 | 223:14393 | URBAN | Other | 897528 | 1 | 152.7 | 152.7 | 9.2916e-05 | 6.0848e-05
2012-11-07 | 260:33353 | URBAN | Other | 897534 | 1 | 345.4333 | 345.4333 | 0.00021019 | 6.0848e-05
2012-11-07 | 219:1785 | URBAN | Other | 897535 | 1 | 613.2333 | 613.2333 | 0.00037314 | 6.0848e-05
2012-11-07 | 238:34140 | URBAN | Equipment Failure | 897546 | 1 | 636.8833 | 636.8833 | 0.00038753 | 6.0848e-05
2012-11-08 | ZN3425:PA30 | URBAN | Other | 897550 | 1018 | 139 | 141502 | 0.086102 | 0.061944
2012-11-08 | ZN12610:PA6 | URBAN | Other | 897563 | 1 | 172.9667 | 172.9667 | 0.00010525 | 6.0849e-05
2012-10-24 | ZN14143:PA17 | SHORT RURAL | Equipment Failure | 897611 | 10 | 174 | 1398 | 0.000851 | 0.00060872
2012-11-08 | 228:7487 | URBAN | Equipment Failure | 897632 | 1 | 259.7833 | 259.7833 | 0.00015807 | 6.0849e-05
2012-11-08 | ZN10999:PA39 | URBAN | Third Party Impacts | 897676 | 1 | 41.9667 | 41.9667 | 2.5536e-05 | 6.0849e-05
2012-11-08 | ZN10999:PA16 | URBAN | Third Party Impacts | 897677 | 80 | 77 | 6160 | 0.0037483 | 0.0048679
2012-11-08 | ZN12610:PA16 | URBAN | Other | 897688 | 1 | 66.15 | 66.15 | 4.0251e-05 | 6.0849e-05
2012-10-11 | ZN901:PA11 | URBAN | Equipment Failure | 897689 | 60 | 105 | 6300 | 0.0038384 | 0.0036556
2012-11-08 | ZN14891:PA17 | SHORT RURAL | Other | 897701 | 1 | 303.0167 | 303.0167 | 0.00018438 | 6.0849e-05
2012-11-08 | 264:81241 | SHORT RURAL | Equipment Failure | 897831 | 1500 | 141 | 148548 | 0.090389 | 0.091273
2012-11-08 | 810:74054 | LONG RURAL | Other | 897937 | 1 | 35.8667 | 35.8667 | 2.1824e-05 | 6.0849e-05
2012-11-08 | 219:1740 | SHORT RURAL | Other | 897944 | 1 | 101.7333 | 101.7333 | 6.1903e-05 | 6.0849e-05
2012-11-08 | 219:1740 | SHORT RURAL | Other | 897945 | 1 | 101.1833 | 101.1833 | 6.1569e-05 | 6.0849e-05
2012-11-08 | 219:1740 | SHORT RURAL | Equipment Failure | 897946 | 1 | 228.5833 | 228.5833 | 0.00013909 | 6.0849e-05
2012-11-08 | ZN14892:PA19 | URBAN | Other | 897980 | 1 | 63.4 | 63.4 | 3.8578e-05 | 6.0849e-05
2012-11-08 | ZN14892:PA19 | URBAN | Other | 898010 | 1 | 313.8167 | 313.8167 | 0.00019095 | 6.0849e-05
2012-11-08 | ZN3155:PA24 | URBAN | Other | 898014 | 1 | 333.0333 | 333.0333 | 0.00020265 | 6.0849e-05
2012-11-08 | ZN3472:PA20 | URBAN | Equipment Failure | 898016 | 1 | 297.55 | 297.55 | 0.00018106 | 6.0849e-05
2012-11-08 | ZN10990:PA11 | URBAN | Other | 898020 | 1 | 401.25 | 401.25 | 0.00024416 | 6.0849e-05
2012-11-08 | ZN12610:PA18 | URBAN | Other | 898028 | 1 | 1446.2167 | 1446.2167 | 0.00088 | 6.0849e-05
2012-11-08 | 813:89055 | SHORT RURAL | Equipment Failure | 898032 | 153 | 491 | 9793 | 0.0059589 | 0.0093098
2012-11-08 | ZN9700:PA20 | URBAN | Weather | 898033 | 1801 | 68 | 98504 | 0.059938 | 0.10959
2012-11-08 | ZN12690:PA12 | SHORT RURAL | Other | 898046 | 1 | 21.0833 | 21.0833 | 1.2829e-05 | 6.0849e-05
2012-11-08 | ZN12610:PA10 | SHORT RURAL | Equipment Failure | 898053 | 1 | 427.4833 | 427.4833 | 0.00026012 | 6.0849e-05
2012-11-08 | ZN9245:PA10 | URBAN | Other | 898072 | 1 | 198.5167 | 198.5167 | 0.00012079 | 6.0849e-05
2012-11-08 | ZN9252:PA2 | URBAN | Other | 898080 | 1 | 700.9 | 700.9 | 0.00042649 | 6.0849e-05
2012-11-08 | ZN12610:PA10 | SHORT RURAL | Other | 898086 | 1 | 340.1833 | 340.1833 | 0.000207 | 6.0849e-05
2012-11-08 | 217:33611 | URBAN | Other | 898098 | 1 | 133.1167 | 133.1167 | 8.1e-05 | 6.0849e-05
2012-11-08 | ZN12610:PA25 | SHORT RURAL | Other | 898100 | 1 | 561.65 | 561.65 | 0.00034176 | 6.0849e-05
2012-11-08 | ZN9035:PA11 | URBAN | Other | 898103 | 1 | 151.6167 | 151.6167 | 9.2257e-05 | 6.0849e-05
2012-11-08 | 222:2015 | SHORT RURAL | Other | 898105 | 1 | 16.0333 | 16.0333 | 9.7561e-06 | 6.0849e-05
2012-11-08 | 504:48026 | SHORT RURAL | Other | 898106 | 1 | 74.4333 | 74.4333 | 4.5292e-05 | 6.0849e-05
2012-11-08 | 223:14393 | URBAN | Other | 898109 | 1 | 30.3333 | 30.3333 | 1.8457e-05 | 6.0849e-05
2012-11-08 | 217:33611 | URBAN | Other | 898113 | 1 | 89.9667 | 89.9667 | 5.4743e-05 | 6.0849e-05
2012-11-08 | 801:74118 | URBAN | Other | 898120 | 32 | 50 | 1600 | 0.00097358 | 0.0019472
2012-11-08 | ZN10990:PA11 | URBAN | Other | 898122 | 1 | 166.9333 | 166.9333 | 0.00010158 | 6.0849e-05
2012-11-08 | 513:48059 | SHORT RURAL | Other | 898125 | 1 | 135.6833 | 135.6833 | 8.2561e-05 | 6.0849e-05
2012-11-08 | 513:48056 | SHORT RURAL | Vegetation | 898129 | 1 | 346.0667 | 346.0667 | 0.00021058 | 6.0849e-05
2012-11-08 | ZN12600:PA2 | SHORT RURAL | Other | 898147 | 10 | 23 | 230 | 0.00013995 | 0.00060849
2012-11-08 | 513:48051 | URBAN | Equipment Failure | 898148 | 25 | 185 | 4625 | 0.0028142 | 0.0015212
2012-11-08 | ZN1285:PA24 | URBAN | Other | 898157 | 1 | 748.2833 | 748.2833 | 0.00045532 | 6.0849e-05
2012-11-08 | ZN10990:PA1 | URBAN | Other | 898158 | 45 | 167 | 7515 | 0.0045728 | 0.0027382
2012-11-09 | ZN12580:PA16 | URBAN | Vegetation | 898164 | 1224 | 52 | 63648 | 0.038729 | 0.074479
2012-11-09 | ZN12690:PA12 | SHORT RURAL | Other | 898168 | 248 | 614 | 16326 | 0.0099342 | 0.01509
2012-11-09 | ZN2400:PA18 | SHORT RURAL | Vegetation | 898170 | 398 | 164 | 65272 | 0.039717 | 0.024218
2012-11-09 | ZN690:PA14 | URBAN | Equipment Failure | 898182 | 2185 | 57 | 116457 | 0.070863 | 0.13295
2012-11-09 | ZN12590:PA7 | SHORT RURAL | Vegetation | 898183 | 95 | 73 | 6935 | 0.0042199 | 0.0057806
2012-11-09 | ZN72:PA14 | URBAN | Other | 898186 | 1 | 648.0833 | 648.0833 | 0.00039435 | 6.0849e-05
2012-11-09 | ZN14891:PA10 | SHORT RURAL | Other | 898192 | 1 | 444.9833 | 444.9833 | 0.00027077 | 6.0849e-05
2012-11-09 | ZN4545:PA41 | URBAN | Equipment Failure | 898196 | 1 | 365.7667 | 365.7667 | 0.00022256 | 6.0849e-05
2012-11-09 | ZN36300:PA11 | URBAN | Animals | 898199 | 3547 | 237 | 690965 | 0.42044 | 0.21583
2012-11-09 | ZN129:PA5 | URBAN | Equipment Failure | 898202 | 34 | 317.9833 | 10811.4333 | 0.0065786 | 0.0020689
2012-11-09 | 513:48059 | SHORT RURAL | Other | 898206 | 1 | 286.9333 | 286.9333 | 0.0001746 | 6.0849e-05
2012-11-09 | ZN12570:PA33 | SHORT RURAL | Equipment Failure | 898212 | 1 | 152.6833 | 152.6833 | 9.2906e-05 | 6.0849e-05
2012-11-09 | ZN874:PA7 | URBAN | Equipment Failure | 898213 | 1 | 521.1333 | 521.1333 | 0.0003171 | 6.0849e-05
2012-11-09 | 504:48031 | SHORT RURAL | Other | 898218 | 1 | 168 | 168 | 0.00010223 | 6.0849e-05
2012-11-09 | ZN9118:PA17 | URBAN | Equipment Failure | 898228 | 1 | 702.3167 | 702.3167 | 0.00042735 | 6.0849e-05
2012-11-09 | ZN116:PA34 | URBAN | Vegetation | 898231 | 1 | 440.2 | 440.2 | 0.00026786 | 6.0849e-05
2012-11-09 | ZN12620:PA1 | SHORT RURAL | Other | 898242 | 1 | 368.9833 | 368.9833 | 0.00022452 | 6.0849e-05
2012-11-09 | 240:34840 | URBAN | Vegetation | 898280 | 1 | 65.5667 | 65.5667 | 3.9896e-05 | 6.0849e-05
2012-11-08 | 228:7490 | SHORT RURAL | Equipment Failure | 898299 | 78 | 1523.8667 | 19734 | 0.012008 | 0.0047462
2012-11-09 | 513:48050 | SHORT RURAL | Other | 898354 | 1 | 99.4167 | 99.4167 | 6.0494e-05 | 6.0849e-05
2012-11-09 | 218:7482 | URBAN | Equipment Failure | 898360 | 1 | 253.8833 | 253.8833 | 0.00015448 | 6.0849e-05
2012-11-09 | ZN9550:PA32 | URBAN | Equipment Failure | 898367 | 1 | 232.15 | 232.15 | 0.00014126 | 6.0849e-05
2012-11-09 | ZN1164:PA4 | URBAN | Other | 898371 | 1 | 847.3167 | 847.3167 | 0.00051558 | 6.0849e-05
2012-11-09 | ZN116:PA34 | URBAN | Vegetation | 898414 | 1 | 203.3 | 203.3 | 0.00012371 | 6.0849e-05
2012-11-09 | ZN7900:PA23 | URBAN | Other | 898424 | 2 | 631 | 1262 | 0.00076791 | 0.0001217
2012-11-09 | 810:74054 | LONG RURAL | Weather | 898455 | 1 | 90.8 | 90.8 | 5.5251e-05 | 6.0849e-05
2012-11-09 | ZN269:PA3 | URBAN | Other | 898460 | 83 | 373.0167 | 30960.3833 | 0.018839 | 0.0050504
2012-11-09 | 501:48125 | URBAN | Other | 898477 | 17 | 45.5 | 773.5 | 0.00047066 | 0.0010344
2012-11-09 | ZN342:PA15 | URBAN | Other | 898499 | 12 | 97 | 1164 | 0.00070828 | 0.00073018
2012-11-09 | ZN342:PA23 | URBAN | Other | 898499 | 39 | 97 | 3783 | 0.0023019 | 0.0023731
2012-11-09 | ZN2310:PA10 | URBAN | Equipment Failure | 898505 | 1 | 226.4333 | 226.4333 | 0.00013778 | 6.0849e-05
2012-11-09 | ZN35500:PA24 | URBAN | Vegetation | 898515 | 1 | 693.3667 | 693.3667 | 0.0004219 | 6.0849e-05
2012-11-09 | ZN9118:PA12 | URBAN | Other | 898518 | 1 | 346.0833 | 346.0833 | 0.00021059 | 6.0849e-05
2012-11-09 | ZN874:PA22 | URBAN | Vegetation | 898524 | 110 | 196 | 21560 | 0.013119 | 0.0066934
2012-11-09 | ZN2466:PA30 | URBAN | Vegetation | 898531 | 1 | 331.5333 | 331.5333 | 0.00020173 | 6.0849e-05
2012-11-09 | ZN129:PA3 | URBAN | Vegetation | 898532 | 36 | 102.2833 | 3682.2 | 0.0022406 | 0.0021906
2012-11-09 | 232:33413 | SHORT RURAL | Vegetation | 898543 | 1 | 180.5 | 180.5 | 0.00010983 | 6.0849e-05
2012-11-09 | ZN2835:PA15 | URBAN | Other | 898556 | 48 | 315 | 15120 | 0.0092003 | 0.0029207
2012-11-09 | 225:33676 | SHORT RURAL | Vegetation | 898567 | 1 | 66.2833 | 66.2833 | 4.0333e-05 | 6.0849e-05
2012-11-09 | ZN12570:PA24 | SHORT RURAL | Equipment Failure | 898581 | 63 | 82.5833 | 5202.75 | 0.0031658 | 0.0038335
2012-11-09 | ZN874:PA3 | URBAN | Equipment Failure | 898589 | 52 | 115.7833 | 6020.7333 | 0.0036635 | 0.0031641
2012-11-09 | 223:14397 | URBAN | Other | 898601 | 1 | 40.9667 | 40.9667 | 2.4928e-05 | 6.0849e-05
2012-11-09 | 223:14397 | URBAN | Other | 898602 | 1 | 37.05 | 37.05 | 2.2544e-05 | 6.0849e-05
2012-11-09 | ZN188:PA1 | URBAN | Other | 898604 | 1 | 152.3833 | 152.3833 | 9.2723e-05 | 6.0849e-05
2012-11-09 | ZN1164:PA9 | URBAN | Other | 898605 | 2 | 594.7167 | 1189.4333 | 0.00072375 | 0.0001217
2012-11-09 | 512:48046 | SHORT RURAL | Equipment Failure | 898611 | 1 | 142.6167 | 142.6167 | 8.678e-05 | 6.0849e-05
2012-11-09 | ZN15005:PA2 | URBAN | Equipment Failure | 898625 | 61 | 77.8833 | 4750.8833 | 0.0028908 | 0.0037118
2012-11-09 | ZN35600:PA1 | URBAN | Equipment Failure | 898630 | 1 | 317.7833 | 317.7833 | 0.00019337 | 6.0849e-05
2012-11-09 | 507:80917 | URBAN | Other | 898641 | 1 | 131.45 | 131.45 | 7.9986e-05 | 6.0849e-05
2012-11-09 | ZN2466:PA30 | URBAN | Equipment Failure | 898650 | 39 | 97.5667 | 3805.1 | 0.0023154 | 0.0023731
2012-11-09 | 214:8667 | URBAN | Vegetation | 898654 | 1 | 65 | 65 | 3.9552e-05 | 6.0849e-05
2012-11-09 | ZN2466:PA41 | URBAN | Other | 898663 | 1 | 306.9833 | 306.9833 | 0.0001868 | 6.0849e-05
2012-11-09 | ZN3472:PA15 | URBAN | Vegetation | 898671 | 29 | 85 | 2465 | 0.0014999 | 0.0017646
2012-11-09 | 223:14397 | URBAN | Equipment Failure | 898674 | 1132 | 724 | 225673 | 0.13732 | 0.068881
2012-11-09 | 512:48046 | SHORT RURAL | Third Party Impacts | 898705 | 54 | 113.5167 | 6129.9 | 0.00373 | 0.0032858
2012-11-09 | 510:48164 | SHORT RURAL | Equipment Failure | 898718 | 2 | 133.4833 | 266.9667 | 0.00016245 | 0.0001217
2012-11-09 | ZN1850:PA15 | URBAN | Other | 898728 | 1 | 285.9167 | 285.9167 | 0.00017398 | 6.0849e-05
2012-11-09 | ZN874:PA22 | URBAN | Vegetation | 898734 | 1 | 250.3333 | 250.3333 | 0.00015232 | 6.0849e-05
2012-11-09 | ZN2466:PA5 | URBAN | Other | 898740 | 15 | 158 | 2370 | 0.0014421 | 0.00091273
2012-11-09 | ZN12660:PA16 | URBAN | Vegetation | 898750 | 29 | 193 | 5597 | 0.0034057 | 0.0017646
2012-11-09 | 223:14397 | URBAN | Other | 898762 | 1 | 66.1833 | 66.1833 | 4.0272e-05 | 6.0849e-05
2012-11-09 | ZN14143:PA17 | SHORT RURAL | Animals | 898767 | 747 | 91 | 67977 | 0.041363 | 0.045454
2012-11-09 | ZN12620:PA1 | SHORT RURAL | Equipment Failure | 898771 | 930 | 79 | 70680 | 0.043008 | 0.056589
2012-11-09 | ZN12620:PA10 | SHORT RURAL | Equipment Failure | 898771 | 1074 | 79 | 81807 | 0.049778 | 0.065351
2012-11-09 | ZN12650:PA1 | SHORT RURAL | Vegetation | 898778 | 17 | 359 | 2879 | 0.0017518 | 0.0010344
2012-11-10 | 224:80332 | URBAN | Animals | 898783 | 1796 | 100 | 170010 | 0.10345 | 0.10928
2012-11-10 | 520:48172 | SHORT RURAL | Other | 898813 | 1 | 213.8167 | 213.8167 | 0.0001301 | 6.0849e-05
2012-11-10 | 813:89061 | LONG RURAL | Other | 898833 | 1 | 75 | 75 | 4.5637e-05 | 6.0849e-05
2012-11-10 | ZN167:PA21 | URBAN | Other | 898843 | 1 | 248.8667 | 248.8667 | 0.00015143 | 6.0849e-05
2012-11-10 | 218:7478 | URBAN | Other | 898857 | 1 | 131.7333 | 131.7333 | 8.0158e-05 | 6.0849e-05
2012-11-10 | 502:48008 | URBAN | Other | 898868 | 834 | 109 | 90906 | 0.055315 | 0.050748
2012-11-10 | 524:33570 | SHORT RURAL | Other | 898901 | 1 | 57.4333 | 57.4333 | 3.4947e-05 | 6.0849e-05
2012-11-10 | 258:80790 | URBAN | Third Party Impacts | 898904 | 10 | 90 | 900 | 0.00054764 | 0.00060849
2012-11-10 | ZN9700:PA12 | URBAN | Other | 898906 | 10 | 122 | 1220 | 0.00074235 | 0.00060849
2012-11-10 | 511:29877 | SHORT RURAL | Third Party Impacts | 898918 | 1111 | 352 | 135655 | 0.082544 | 0.067603
2012-11-10 | ZN10999:PA12 | URBAN | Other | 898925 | 1 | 66.25 | 66.25 | 4.0312e-05 | 6.0849e-05
2012-11-11 | ZN965:PA11 | URBAN | Other | 898928 | 41 | 190 | 7790 | 0.0047401 | 0.0024948
2012-11-11 | ZN12620:PA13 | SHORT RURAL | Equipment Failure | 898929 | 412 | 449 | 3708 | 0.0022563 | 0.02507
2012-11-11 | ZN12620:PA3 | URBAN | Equipment Failure | 898929 | 52 | 449 | 23348 | 0.014207 | 0.0031641
2012-11-11 | ZN12570:PA37 | SHORT RURAL | Equipment Failure | 898932 | 7 | 216 | 1512 | 0.00092003 | 0.00042594
2012-11-11 | ZN14892:PA6 | SHORT RURAL | Other | 898936 | 1 | 526.8833 | 526.8833 | 0.0003206 | 6.0849e-05
2012-11-11 | 260:33347 | SHORT RURAL | Other | 898964 | 1 | 84.15 | 84.15 | 5.1204e-05 | 6.0849e-05
2012-11-11 | 507:80923 | SHORT RURAL | Equipment Failure | 898984 | 1219 | 367 | 82683 | 0.050312 | 0.074175
2012-11-11 | ZN12620:PA3 | URBAN | Other | 898986 | 1 | 237.7167 | 237.7167 | 0.00014465 | 6.0849e-05
2012-11-11 | ZN14891:PA20 | SHORT RURAL | Equipment Failure | 898995 | 1 | 462.1 | 462.1 | 0.00028118 | 6.0849e-05
2012-11-11 | ZN9118:PA12 | URBAN | Other | 899017 | 32 | 81.05 | 2593.6 | 0.0015782 | 0.0019472
2012-11-11 | 515:35198 | SHORT RURAL | Equipment Failure | 899032 | 141 | 382 | 10097 | 0.0061439 | 0.0085797
2012-11-12 | ZN9118:PA8 | URBAN | Other | 899045 | 29 | 96.8667 | 2809.1333 | 0.0017093 | 0.0017646
2012-11-12 | ZN129:PA3 | URBAN | Other | 899047 | 2 | 163 | 326 | 0.00019837 | 0.0001217
2012-11-12 | ZN129:PA5 | URBAN | Other | 899047 | 34 | 163 | 5542 | 0.0033722 | 0.0020689
2012-11-12 | ZN36300:PA7 | URBAN | Equipment Failure | 899053 | 1 | 379.3333 | 379.3333 | 0.00023082 | 6.0849e-05
2012-11-12 | ZN35370:PA8 | SHORT RURAL | Equipment Failure | 899057 | 1 | 206.6833 | 206.6833 | 0.00012576 | 6.0849e-05
2012-11-12 | 813:89058 | SHORT RURAL | Other | 899077 | 1 | 121.1833 | 121.1833 | 7.3738e-05 | 6.0849e-05
2012-11-09 | 222:2017 | URBAN | Equipment Failure | 899078 | 1 | 377 | 377 | 0.0002294 | 6.0849e-05
2012-11-08 | ZN342:PA22 | URBAN | Equipment Failure | 899080 | 55 | 80 | 4400 | 0.0026773 | 0.0033467
2012-11-12 | ZN2310:PA27 | URBAN | Other | 899245 | 23 | 103 | 2369 | 0.0014415 | 0.0013995
2012-11-12 | ZN630:PA33 | URBAN | Equipment Failure | 899271 | 1 | 219.9333 | 219.9333 | 0.00013383 | 6.0849e-05
2012-11-12 | 222:2015 | SHORT RURAL | Other | 899292 | 1 | 87.1333 | 87.1333 | 5.3019e-05 | 6.0849e-05
2012-11-12 | 507:80923 | SHORT RURAL | Other | 899306 | 4 | 111 | 444 | 0.00027017 | 0.00024339
2012-11-12 | ZN342:PA24 | URBAN | Third Party Impacts | 899324 | 1 | 292.6667 | 292.6667 | 0.00017808 | 6.0849e-05
2012-11-12 | ZN12610:PA13 | URBAN | Other | 899354 | 1 | 625.9167 | 625.9167 | 0.00038086 | 6.0849e-05
2012-11-12 | ZN12610:PA18 | URBAN | Equipment Failure | 899367 | 704 | 143 | 100672 | 0.061258 | 0.042837
2012-11-12 | ZN14144:PA10 | SHORT RURAL | Vegetation | 899368 | 1 | 171.15 | 171.15 | 0.00010414 | 6.0849e-05
2012-11-09 | 802:82225 | SHORT RURAL | Equipment Failure | 899370 | 1 | 275 | 275 | 0.00016733 | 6.0849e-05
2012-11-12 | 515:35197 | LONG RURAL | Equipment Failure | 899404 | 2 | 506 | 1012 | 0.00061579 | 0.0001217
2012-11-12 | ZN2602:PA10 | URBAN | Equipment Failure | 899419 | 725 | 54 | 39150 | 0.023822 | 0.044115
2012-11-12 | 504:48033 | SHORT RURAL | Other | 899431 | 1 | 131.45 | 131.45 | 7.9986e-05 | 6.0849e-05
2012-11-12 | ZN35370:PA10 | SHORT RURAL | Vegetation | 899462 | 517 | 103 | 35643 | 0.021688 | 0.031459
2012-11-12 | ZN965:PA4 | URBAN | Vegetation | 899462 | 299 | 103 | 30797 | 0.01874 | 0.018194
2012-11-12 | ZN2310:PA34 | URBAN | Other | 899492 | 1 | 149.65 | 149.65 | 9.106e-05 | 6.0849e-05
2012-11-12 | 504:48026 | SHORT RURAL | Other | 899514 | 1 | 75.1833 | 75.1833 | 4.5748e-05 | 6.0849e-05
2012-11-12 | ZN15008:PA9 | URBAN | Other | 899540 | 1 | 63.6667 | 63.6667 | 3.874e-05 | 6.0849e-05
2012-11-12 | ZN3425:PA28 | URBAN | Vegetation | 899542 | 1 | 582.4667 | 582.4667 | 0.00035442 | 6.0849e-05
2012-11-13 | ZN874:PA25 | URBAN | Third Party Impacts | 899547 | 72 | 144 | 10368 | 0.006308 | 0.0043806
2012-11-13 | ZN874:PA22 | URBAN | Third Party Impacts | 899550 | 41 | 77 | 3157 | 0.0019208 | 0.0024945
2012-11-13 | ZN80:PA32 | URBAN | Equipment Failure | 899558 | 65 | 110.1167 | 7157.5833 | 0.0043548 | 0.0039547
2012-11-13 | ZN10999:PA4 | URBAN | Equipment Failure | 899569 | 1 | 356.85 | 356.85 | 0.00021711 | 6.0841e-05
2012-11-13 | ZN167:PA20 | URBAN | Equipment Failure | 899617 | 16 | 102.0833 | 1633.3333 | 0.00099374 | 0.00097346
2012-10-15 | ZN15014:PA11 | URBAN | Equipment Failure | 899701 | 967 | 41 | 39647 | 0.024156 | 0.058917
2012-10-15 | ZN15014:PA19 | URBAN | Equipment Failure | 899701 | 895 | 41 | 36695 | 0.022357 | 0.05453
2012-10-15 | ZN15014:PA20 | URBAN | Equipment Failure | 899701 | 1 | 41 | 41 | 2.498e-05 | 6.0927e-05
2012-11-13 | ZN965:PA33 | URBAN | Other | 899757 | 1 | 1413.3167 | 1413.3167 | 0.00085988 | 6.0841e-05
2012-11-13 | 224:80332 | URBAN | Equipment Failure | 899783 | 172 | 39.15 | 6733.8 | 0.0040969 | 0.010465
2012-11-13 | 801:74123 | SHORT RURAL | Other | 899859 | 1 | 44.4333 | 44.4333 | 2.7034e-05 | 6.0841e-05
2012-11-13 | ZN180:PA18 | URBAN | Equipment Failure | 899905 | 52 | 135.9 | 7066.8 | 0.0042995 | 0.0031637
2012-11-13 | ZN35600:PA1 | URBAN | Other | 899933 | 1 | 1200.3833 | 1200.3833 | 0.00073033 | 6.0841e-05
2012-11-13 | 801:74121 | SHORT RURAL | Other | 899956 | 1 | 186.6667 | 186.6667 | 0.00011357 | 6.0841e-05
2012-11-13 | ZN1285:PA19 | URBAN | Other | 900014 | 1 | 184.6333 | 184.6333 | 0.00011233 | 6.0841e-05
2012-11-13 | 501:48123 | SHORT RURAL | Other | 900016 | 1 | 131.8333 | 131.8333 | 8.0209e-05 | 6.0841e-05
2012-11-13 | ZN3155:PA29 | URBAN | Other | 900022 | 862 | 103 | 46622 | 0.028365 | 0.052445
2012-11-13 | ZN3155:PA44 | URBAN | Other | 900022 | 602 | 103 | 45875 | 0.027911 | 0.036626
2012-11-13 | ZN3155:PA44 | URBAN | Equipment Failure | 900030 | 1 | 135.5333 | 135.5333 | 8.246e-05 | 6.0841e-05
2012-11-13 | ZN12690:PA6 | URBAN | Other | 900036 | 1 | 138.3667 | 138.3667 | 8.4184e-05 | 6.0841e-05
2012-11-13 | ZN2196:PA11 | URBAN | Equipment Failure | 900043 | 22 | 261 | 5742 | 0.0034935 | 0.0013385
2012-11-13 | 513:48058 | URBAN | Other | 900046 | 1 | 597.3333 | 597.3333 | 0.00036343 | 6.0841e-05
2012-11-13 | 214:8670 | URBAN | Other | 900047 | 1 | 206.9167 | 206.9167 | 0.00012589 | 6.0841e-05
2012-11-13 | ZN72:PA10 | URBAN | Other | 900051 | 1 | 448.1167 | 448.1167 | 0.00027264 | 6.0841e-05
2012-11-13 | ZN72:PA10 | URBAN | Other | 900052 | 1 | 447.1333 | 447.1333 | 0.00027204 | 6.0841e-05
2012-11-13 | ZN72:PA10 | URBAN | Other | 900054 | 1 | 440.6667 | 440.6667 | 0.00026811 | 6.0841e-05
2012-11-13 | ZN188:PA2 | URBAN | Other | 900055 | 1 | 330.2167 | 330.2167 | 0.00020091 | 6.0841e-05
2012-11-13 | 221:11893 | URBAN | Third Party Impacts | 900056 | 1 | 45.45 | 45.45 | 2.7652e-05 | 6.0841e-05
2012-11-13 | ZN1610:PA11 | URBAN | Other | 900057 | 1 | 560.7333 | 560.7333 | 0.00034116 | 6.0841e-05
2012-11-13 | ZN15005:PA2 | URBAN | Other | 900058 | 1 | 516.9167 | 516.9167 | 0.0003145 | 6.0841e-05
2012-11-14 | ZN262:PA31 | URBAN | Other | 900059 | 1 | 902.9833 | 902.9833 | 0.00054938 | 6.0841e-05
2012-11-14 | ZN2835:PA15 | URBAN | Other | 900060 | 1 | 631.95 | 631.95 | 0.00038448 | 6.0841e-05
2012-11-14 | ZN4545:PA4 | URBAN | Other | 900061 | 45 | 529.25 | 23816.25 | 0.01449 | 0.0027378
2012-11-14 | ZN1285:PA16 | URBAN | Other | 900065 | 1 | 116.9667 | 116.9667 | 7.1164e-05 | 6.0841e-05
2012-11-14 | ZN1285:PA33 | URBAN | Other | 900067 | 1 | 119.4167 | 119.4167 | 7.2654e-05 | 6.0841e-05
2012-11-14 | ZN2835:PA19 | URBAN | Equipment Failure | 900068 | 1 | 312.5333 | 312.5333 | 0.00019015 | 6.0841e-05
2012-11-14 | ZN15011:PA2 | URBAN | Other | 900069 | 1 | 455.6 | 455.6 | 0.00027719 | 6.0841e-05
2012-11-14 | 806:74080 | SHORT RURAL | Other | 900073 | 1 | 137 | 137 | 8.3352e-05 | 6.0841e-05
2012-11-14 | 224:80346 | URBAN | Other | 900074 | 1 | 85.7667 | 85.7667 | 5.2181e-05 | 6.0841e-05
2012-11-13 | 810:74050 | SHORT RURAL | Equipment Failure | 900092 | 1 | 50 | 50 | 3.0421e-05 | 6.0841e-05
2012-11-14 | ZN180:PA9 | URBAN | Third Party Impacts | 900122 | 1 | 212.8833 | 212.8833 | 0.00012952 | 6.0841e-05
2012-11-14 | ZN2835:PA15 | URBAN | Other | 900143 | 1 | 128.25 | 128.25 | 7.8029e-05 | 6.0841e-05
2012-11-14 | ZN3155:PA23 | URBAN | Other | 900155 | 1 | 207.1333 | 207.1333 | 0.00012602 | 6.0841e-05
2012-11-14 | ZN116:PA41 | URBAN | Operational Error | 900157 | 1 | 173.05 | 173.05 | 0.00010529 | 6.0841e-05
2012-11-13 | ZN2196:PA12 | URBAN | Other | 900236 | 1 | 296 | 296 | 0.00018009 | 6.0841e-05
2012-11-14 | ZN847:PA26 | URBAN | Equipment Failure | 900271 | 1 | 152.15 | 152.15 | 9.257e-05 | 6.0841e-05
2012-10-24 | 203:8085 | URBAN | Equipment Failure | 900274 | 449 | 315 | 139384 | 0.084846 | 0.027332
2012-11-14 | ZN262:PA32 | URBAN | Other | 900377 | 1 | 206.6167 | 206.6167 | 0.00012571 | 6.0841e-05
2012-11-14 | 203:8084 | URBAN | Vegetation | 900394 | 1 | 111.5333 | 111.5333 | 6.7858e-05 | 6.0841e-05
2012-11-14 | ZN35600:PA14 | URBAN | Other | 900420 | 1 | 349.2667 | 349.2667 | 0.0002125 | 6.0841e-05
2012-11-14 | 213:33771 | URBAN | Equipment Failure | 900433 | 1 | 203.35 | 203.35 | 0.00012372 | 6.0841e-05
2012-11-14 | 514:18137 | SHORT RURAL | Other | 900452 | 1 | 116.3333 | 116.3333 | 7.0778e-05 | 6.0841e-05
2012-11-14 | ZN3472:PA27 | URBAN | Other | 900457 | 1 | 2408 | 2408 | 0.0014651 | 6.0841e-05
2012-11-14 | 526:34636 | SHORT RURAL | Other | 900463 | 1 | 140.4667 | 140.4667 | 8.5461e-05 | 6.0841e-05
2012-11-14 | ZN2568:PA32 | URBAN | Other | 900474 | 1 | 143.3833 | 143.3833 | 8.7236e-05 | 6.0841e-05
2012-11-15 | ZN3155:PA44 | URBAN | Other | 900479 | 1 | 219.1333 | 219.1333 | 0.00013332 | 6.0841e-05
2012-11-15 | ZN262:PA30 | URBAN | Other | 900481 | 1 | 406.6333 | 406.6333 | 0.0002474 | 6.0841e-05
2012-11-15 | ZN8000:PA16 | URBAN | Third Party Impacts | 900483 | 1 | 269.9667 | 269.9667 | 0.00016425 | 6.0841e-05
2012-11-15 | ZN129:PA16 | URBAN | Equipment Failure | 900484 | 1 | 441.3333 | 441.3333 | 0.00026851 | 6.0841e-05
2012-11-15 | ZN847:PA22 | SHORT RURAL | Third Party Impacts | 900485 | 53 | 26.8 | 1420.4 | 0.00086419 | 0.0032246
2012-11-14 | ZN14891:PA12 | SHORT RURAL | Vegetation | 900487 | 1 | 315 | 315 | 0.00019165 | 6.0841e-05
2012-11-15 | ZN167:PA21 | URBAN | Equipment Failure | 900494 | 1 | 273.6667 | 273.6667 | 0.0001665 | 6.0841e-05
2012-11-15 | ZN690:PA26 | URBAN | Vegetation | 900497 | 56 | 382.6333 | 21427.4667 | 0.013037 | 0.0034071
2012-11-15 | 258:80779 | URBAN | Other | 900566 | 1 | 95.45 | 95.45 | 5.8073e-05 | 6.0841e-05
2012-11-13 | ZN80:PA32 | URBAN | Other | 900578 | 2869 | 87 | 177648 | 0.10808 | 0.17455
2012-11-15 | 202:34231 37 42 | URBAN | Other | 900617 | 1 | 36.8 | 36.8 | 2.239e-05 | 6.0841e-05
2012-11-15 | ZN3472:PA33 | URBAN | Third Party Impacts | 900675 | 1 | 303.5667 | 303.5667 | 0.00018469 | 6.0841e-05
2012-11-15 | 513:48056 | SHORT RURAL | Other | 900676 | 1 | 189.5333 | 189.5333 | 0.00011531 | 6.0841e-05
2012-11-15 | 227:13015 | SHORT RURAL | Other | 900709 | 1 | 272 | 272 | 0.00016549 | 6.0841e-05
2012-11-15 | 210:8676 | URBAN | Equipment Failure | 900746 | 1 | 52.8333 | 52.8333 | 3.2144e-05 | 6.0841e-05
2012-11-15 | 512:48049 | SHORT RURAL | Equipment Failure | 900830 | 28 | 69.6667 | 1950.6667 | 0.0011868 | 0.0017035
2012-11-15 | ZN384:PA9 | URBAN | Equipment Failure | 900857 | 2 | 144 | 288 | 0.00017522 | 0.00012168
2012-11-15 | ZN9900:PA5 | URBAN | Equipment Failure | 900885 | 1 | 393.5 | 393.5 | 0.00023941 | 6.0841e-05
2012-11-15 | ZN262:PA30 | URBAN | Equipment Failure | 900909 | 1 | 12 | 12 | 7.3009e-06 | 6.0841e-05
2012-11-15 | 227:13020 | SHORT RURAL | Other | 900913 | 1 | 121.0333 | 121.0333 | 7.3638e-05 | 6.0841e-05
2012-11-15 | 807:74184 | SHORT RURAL | Other | 900916 | 4 | 1080 | 4320 | 0.0026283 | 0.00024336
2012-11-15 | ZN3672:PA9 | URBAN | Other | 900931 | 1 | 638.5167 | 638.5167 | 0.00038848 | 6.0841e-05
2012-11-16 | ZN9037:PA8 | URBAN | Animals | 900933 | 135 | 82.2333 | 11101.5 | 0.0067543 | 0.0082135
2012-11-16 | 222:2018 | URBAN | Other | 900944 | 1 | 138.95 | 138.95 | 8.4539e-05 | 6.0841e-05
2012-11-16 | 511:29878 | SHORT RURAL | Equipment Failure | 900945 | 1 | 73.3833 | 73.3833 | 4.4647e-05 | 6.0841e-05
2012-11-16 | ZN10990:PA2 | URBAN | Other | 900957 | 1 | 81.7667 | 81.7667 | 4.9748e-05 | 6.0841e-05
2012-11-16 | ZN3472:PA21 | URBAN | Other | 900959 | 1 | 151.55 | 151.55 | 9.2205e-05 | 6.0841e-05
2012-11-16 | ZN4545:PA24 | URBAN | Equipment Failure | 900976 | 39 | 205.4333 | 8011.9 | 0.0048745 | 0.0023728
2012-11-16 | ZN129:PA16 | URBAN | Other | 900984 | 1 | 644.3833 | 644.3833 | 0.00039205 | 6.0841e-05
2012-11-16 | ZN72:PA10 | URBAN | Other | 900986 | 1 | 101.8667 | 101.8667 | 6.1977e-05 | 6.0841e-05
2012-11-16 | ZN2310:PA10 | URBAN | Equipment Failure | 900990 | 1 | 40.5667 | 40.5667 | 2.4681e-05 | 6.0841e-05
2012-11-16 | ZN12570:PA24 | SHORT RURAL | Equipment Failure | 900993 | 1 | 2003.5 | 2003.5 | 0.001219 | 6.0841e-05
2012-11-16 | ZN12660:PA11 | URBAN | Equipment Failure | 901013 | 72 | 241 | 17319.6 | 0.010537 | 0.0043806
2012-11-16 | ZN12660:PA13 | URBAN | Equipment Failure | 901013 | 6 | 241 | 1446 | 0.00087976 | 0.00036505
2012-11-16 | 222:2018 | URBAN | Other | 901017 | 1 | 120.5667 | 120.5667 | 7.3354e-05 | 6.0841e-05
2012-11-16 | ZN129:PA4 | URBAN | Equipment Failure | 901032 | 1 | 328.3 | 328.3 | 0.00019974 | 6.0841e-05
2012-11-16 | ZN12580:PA12 | SHORT RURAL | Equipment Failure | 901038 | 1 | 71.5333 | 71.5333 | 4.3522e-05 | 6.0841e-05
2012-11-16 | ZN4545:PA31 | URBAN | Equipment Failure | 901043 | 1 | 548.2833 | 548.2833 | 0.00033358 | 6.0841e-05
2012-11-16 | ZN9245:PA15 | URBAN | Vegetation | 901075 | 1 | 363.0333 | 363.0333 | 0.00022087 | 6.0841e-05
2012-11-16 | ZN1068:PA20 | URBAN | Equipment Failure | 901085 | 1 | 169.4 | 169.4 | 0.00010306 | 6.0841e-05
2012-11-16 | 213:33775 | URBAN | Other | 901100 | 1 | 163.5667 | 163.5667 | 9.9516e-05 | 6.0841e-05
2012-11-16 | 210:8676 | URBAN | Other | 901122 | 1 | 64.1667 | 64.1667 | 3.904e-05 | 6.0841e-05
2012-11-16 | 502:48010 | SHORT RURAL | Other | 901234 | 1 | 128.3667 | 128.3667 | 7.81e-05 | 6.0841e-05
2012-11-16 | 240:34835 | URBAN | Other | 901242 | 1 | 157.2167 | 157.2167 | 9.5652e-05 | 6.0841e-05
2012-11-16 | ZN9037:PA16 | URBAN | Other | 901248 | 1 | 313.6167 | 313.6167 | 0.00019081 | 6.0841e-05
2012-11-16 | ZN10999:PA4 | URBAN | Other | 901259 | 1 | 256.3833 | 256.3833 | 0.00015599 | 6.0841e-05
2012-11-16 | ZN1285:PA33 | URBAN | Third Party Impacts | 901263 | 67 | 319.6333 | 21415.4333 | 0.013029 | 0.0040764
2012-11-16 | ZN35370:PA2 | SHORT RURAL | Vegetation | 901264 | 35 | 85 | 2975 | 0.00181 | 0.0021294
2012-11-16 | ZN12570:PA34 | SHORT RURAL | Vegetation | 901268 | 779 | 26 | 20254 | 0.012323 | 0.047395
2012-11-16 | 256:80640 | URBAN | Other | 901269 | 1 | 62.35 | 62.35 | 3.7934e-05 | 6.0841e-05
2012-11-16 | ZN72:PA25 | URBAN | Other | 901276 | 1 | 574.2833 | 574.2833 | 0.0003494 | 6.0841e-05
2012-11-16 | 206:34441 | URBAN | Other | 901286 | 1 | 59.0333 | 59.0333 | 3.5917e-05 | 6.0841e-05
2012-11-16 | ZN15001:PA6 | URBAN | Other | 901288 | 1 | 725.2333 | 725.2333 | 0.00044124 | 6.0841e-05
2012-11-16 | ZN12570:PA41 | URBAN | Other | 901296 | 1 | 3607.9167 | 3607.9167 | 0.0021951 | 6.0841e-05
2012-11-16 | ZN690:PA25 | URBAN | Other | 901297 | 1 | 165.4167 | 165.4167 | 0.00010064 | 6.0841e-05
2012-11-16 | ZN1287:PA6 | URBAN | Other | 901301 | 1 | 312.6333 | 312.6333 | 0.00019021 | 6.0841e-05
2012-11-16 | ZN690:PA24 | SHORT RURAL | Other | 901303 | 1 | 127.6 | 127.6 | 7.7633e-05 | 6.0841e-05
2012-11-16 | ZN690:PA25 | URBAN | Other | 901304 | 1 | 125.7167 | 125.7167 | 7.6487e-05 | 6.0841e-05
2012-11-16 | ZN10995:PA2 | URBAN | Other | 901306 | 1 | 713.9333 | 713.9333 | 0.00043436 | 6.0841e-05
2012-11-16 | ZN2835:PA23 | URBAN | Other | 901308 | 1 | 976.7 | 976.7 | 0.00059423 | 6.0841e-05
2012-11-17 | ZN3425:PA32 | URBAN | Other | 901313 | 1 | 680.05 | 680.05 | 0.00041375 | 6.0841e-05
2012-11-17 | 507:80932 | SHORT RURAL | Equipment Failure | 901316 | 1 | 728.9 | 728.9 | 0.00044347 | 6.0841e-05
2012-11-17 | 810:74054 | LONG RURAL | Equipment Failure | 901339 | 5 | 188.5167 | 942.5833 | 0.00057348 | 0.00030421
2012-11-17 | 807:74183 | SHORT RURAL | Equipment Failure | 901348 | 46 | 160 | 7360 | 0.0044779 | 0.0027987
2012-11-17 | ZN1285:PA33 | URBAN | Third Party Impacts | 901370 | 1 | 367.1667 | 367.1667 | 0.00022339 | 6.0841e-05
2012-11-17 | ZN931:PA12 | URBAN | Equipment Failure | 901386 | 1 | 94.45 | 94.45 | 5.7464e-05 | 6.0841e-05
2012-11-17 | 235:8684 | SHORT RURAL | Third Party Impacts | 901412 | 117 | 442 | 15809 | 0.0096184 | 0.0071184
2012-11-17 | 203:8084 | URBAN | Other | 901432 | 1 | 86.4333 | 86.4333 | 5.2587e-05 | 6.0841e-05
2012-11-18 | 502:48010 | SHORT RURAL | Equipment Failure | 901444 | 2 | 150 | 300 | 0.00018252 | 0.00012168
2012-11-18 | ZN129:PA9 | URBAN | Vegetation | 901461 | 1 | 264.2667 | 264.2667 | 0.00016078 | 6.0841e-05
2012-11-18 | 806:74080 | SHORT RURAL | Animals | 901476 | 1 | 161.2667 | 161.2667 | 9.8116e-05 | 6.0841e-05
2012-11-18 | ZN80:PA21 | URBAN | Vegetation | 901485 | 47 | 53.7167 | 2524.6833 | 0.001536 | 0.0028595
2012-11-18 | ZN12650:PA6 | URBAN | Vegetation | 901506 | 24 | 62 | 1488 | 0.00090532 | 0.0014602
2012-11-18 | ZN14144:PA4 | URBAN | Vegetation | 901537 | 826 | 85 | 62272 | 0.037887 | 0.050255
2012-11-18 | ZN9245:PA8 | SHORT RURAL | Other | 901543 | 1 | 235.95 | 235.95 | 0.00014355 | 6.0841e-05
2012-11-19 | ZN847:PA39 | URBAN | Other | 901548 | 60 | 92 | 5520 | 0.0033584 | 0.0036505
2012-11-19 | ZN12620:PA1 | SHORT RURAL | Other | 901549 | 1 | 180.3667 | 180.3667 | 0.00010974 | 6.0841e-05
2012-11-19 | 813:89061 | LONG RURAL | Other | 901555 | 1 | 165.8333 | 165.8333 | 0.00010089 | 6.0841e-05
2012-11-19 | ZN2310:PA31 | URBAN | Equipment Failure | 901568 | 1676 | 116 | 172641 | 0.10504 | 0.10197
2012-11-19 | 810:74058 | SHORT RURAL | Vegetation | 901573 | 1 | 160.6333 | 160.6333 | 9.7731e-05 | 6.0841e-05
2012-11-19 | 514:18137 | SHORT RURAL | Other | 901632 | 1 | 30.6333 | 30.6333 | 1.8638e-05 | 6.0841e-05
2012-11-19 | ZN269:PA7 | URBAN | Third Party Impacts | 901708 | 103 | 125 | 12875 | 0.0078333 | 0.0062666
2012-11-19 | ZN1164:PA27 | URBAN | Third Party Impacts | 901777 | 78 | 163.8667 | 12781.6 | 0.0077765 | 0.0047456
2012-11-19 | ZN35370:PA10 | SHORT RURAL | Other | 901924 | 518 | 141 | 59974 | 0.036489 | 0.031516
2012-11-19 | ZN965:PA4 | URBAN | Other | 901924 | 298 | 141 | 42018 | 0.025564 | 0.018131
2012-11-19 | ZN1193:PA28 | URBAN | Equipment Failure | 901933 | 238 | 81 | 19278 | 0.011729 | 0.01448
2012-11-19 | ZN14891:PA12 | SHORT RURAL | Vegetation | 901953 | 473 | 36.8833 | 17445.8167 | 0.010614 | 0.028778
2012-11-19 | 806:74080 | SHORT RURAL | Other | 902024 | 232 | 31 | 6317 | 0.0038433 | 0.014115
2012-11-19 | ZN12590:PA4 | URBAN | Equipment Failure | 902032 | 97 | 100 | 9700 | 0.0059016 | 0.0059016
2012-11-19 | 235:2857 | SHORT RURAL | Equipment Failure | 902039 | 46 | 130.4167 | 5999.1667 | 0.00365 | 0.0027987
2012-11-19 | 504:48031 | SHORT RURAL | Other | 902058 | 1 | 206.75 | 206.75 | 0.00012579 | 6.0841e-05
2012-11-19 | ZN180:PA34 | URBAN | Other | 902061 | 1 | 117.55 | 117.55 | 7.1519e-05 | 6.0841e-05
2012-11-19 | ZN3472:PA17 | URBAN | Other | 902068 | 1 | 204.85 | 204.85 | 0.00012463 | 6.0841e-05
2012-11-19 | ZN12600:PA1 | SHORT RURAL | Animals | 902074 | 1150 | 109 | 49588 | 0.03017 | 0.069967
2012-11-20 | ZN129:PA24 | URBAN | Other | 902099 | 1 | 108.2167 | 108.2167 | 6.5833e-05 | 6.0835e-05
2012-11-20 | 511:29877 | SHORT RURAL | Other | 902103 | 2 | 83 | 166 | 0.00010099 | 0.00012167
2012-11-20 | ZN12570:PA33 | SHORT RURAL | Vegetation | 902106 | 6 | 220 | 1320 | 0.00080302 | 0.00036501
2012-11-20 | 220:8692 | URBAN | Equipment Failure | 902107 | 898 | 35 | 17960 | 0.010926 | 0.054629
2012-11-20 | ZN12650:PA8 | URBAN | Third Party Impacts | 902182 | 180 | 49 | 8820 | 0.0053656 | 0.01095
2012-11-20 | ZN1788:PA32 | URBAN | Vegetation | 902215 | 1 | 311.6167 | 311.6167 | 0.00018957 | 6.0835e-05
2012-11-20 | ZN35800:PA4 | URBAN | Third Party Impacts | 902282 | 1 | 48.3333 | 48.3333 | 2.9403e-05 | 6.0835e-05
2012-11-20 | ZN10994:PA19 | URBAN | Vegetation | 902288 | 33 | 63.6833 | 2101.55 | 0.0012785 | 0.0020075
2012-11-20 | 813:89061 | LONG RURAL | Other | 902292 | 13 | 101 | 1313 | 0.00079876 | 0.00079085
2012-11-20 | 235:2123 | URBAN | Other | 902302 | 1 | 42.4333 | 42.4333 | 2.5814e-05 | 6.0835e-05
2012-11-20 | ZN1850:PA11 | URBAN | Other | 902336 | 13 | 176 | 2288 | 0.0013919 | 0.00079085
2012-11-20 | 812:19072 | SHORT RURAL | Equipment Failure | 902387 | 7 | 137 | 959 | 0.0005834 | 0.00042584
2012-11-20 | ZN12610:PA11 | URBAN | Other | 902412 | 1 | 76.9333 | 76.9333 | 4.6802e-05 | 6.0835e-05
2012-11-20 | 806:74080 | SHORT RURAL | Equipment Failure | 902477 | 233 | 487 | 79031 | 0.048078 | 0.014174
2012-11-20 | 264:81240 | SHORT RURAL | Other | 902501 | 1 | 173.15 | 173.15 | 0.00010533 | 6.0835e-05
2012-11-20 | 243:80080 | SHORT RURAL | Equipment Failure | 902525 | 19 | 264 | 5016 | 0.0030515 | 0.0011559
2012-11-20 | 807:74180 | SHORT RURAL | Equipment Failure | 902560 | 1 | 105 | 105 | 6.3876e-05 | 6.0835e-05
2012-11-21 | ZN398:PA22 | URBAN | Third Party Impacts | 902563 | 95 | 198.3333 | 18841.6667 | 0.011463 | 0.0057796
2012-11-21 | ZN4545:PA44 | URBAN | Equipment Failure | 902610 | 1 | 61.0833 | 61.0833 | 3.7162e-05 | 6.0838e-05
2012-11-19 | ZN12590:PA1 | SHORT RURAL | Operational Error | 902668 | 106 | 4 | 424 | 0.00025797 | 0.0064492
2012-11-21 | ZN9037:PA2 | URBAN | Vegetation | 902773 | 1 | 33.7333 | 33.7333 | 2.0523e-05 | 6.0838e-05
2012-11-21 | ZN9037:PA2 | URBAN | Vegetation | 902790 | 1 | 157.1833 | 157.1833 | 9.5627e-05 | 6.0838e-05
2012-11-21 | ZN1285:PA27 | URBAN | Third Party Impacts | 902880 | 1 | 1081.8167 | 1081.8167 | 0.00065816 | 6.0838e-05
2012-11-21 | 511:29878 | SHORT RURAL | Equipment Failure | 902881 | 1 | 384.6667 | 384.6667 | 0.00023402 | 6.0838e-05
2012-11-21 | ZN690:PA33 | URBAN | Equipment Failure | 902883 | 1 | 284.4167 | 284.4167 | 0.00017303 | 6.0838e-05
2012-11-21 | 504:48026 | SHORT RURAL | Other | 902910 | 1 | 189.0333 | 189.0333 | 0.000115 | 6.0838e-05
2012-11-21 | ZN116:PA45 | URBAN | Operational Error | 902923 | 13 | 375 | 4875 | 0.0029659 | 0.0007909
2012-11-21 | 803:74010 | SHORT RURAL | Other | 902928 | 2 | 56.05 | 112.1 | 6.82e-05 | 0.00012168
2012-11-22 | ZN2602:PA41 | URBAN | Weather | 902960 | 69 | 321 | 22149 | 0.013474 | 0.0041976
2012-11-22 | ZN1788:PA7 | SHORT RURAL | Vegetation | 902964 | 72 | 105.9833 | 7630.8 | 0.0046422 | 0.0043801
2012-11-22 | ZN10999:PA24 | URBAN | Vegetation | 902971 | 1 | 144.7167 | 144.7167 | 8.8039e-05 | 6.0835e-05
2012-11-22 | ZN3425:PA24 | URBAN | Vegetation | 902977 | 1 | 94.1667 | 94.1667 | 5.7286e-05 | 6.0835e-05
2012-11-22 | ZN9118:PA3 | SHORT RURAL | Weather | 902983 | 27 | 234.45 | 6330.15 | 0.003851 | 0.0016426
2012-11-22 | ZN15011:PA2 | URBAN | Vegetation | 902991 | 1 | 133.2333 | 133.2333 | 8.1053e-05 | 6.0835e-05
2012-11-22 | 807:74184 | SHORT RURAL | Equipment Failure | 902997 | 3 | 243 | 729 | 0.00044349 | 0.00018251
2012-11-22 | 516:48065 | SHORT RURAL | Other | 903008 | 1 | 190.5833 | 190.5833 | 0.00011594 | 6.0835e-05
2012-11-22 | 814:82283 | SHORT RURAL | Other | 903082 | 1 | 183.65 | 183.65 | 0.00011172 | 6.0835e-05
2012-11-22 | ZN9550:PA27 | URBAN | Equipment Failure | 903120 | 1 | 32.9 | 32.9 | 2.0015e-05 | 6.0835e-05
2012-11-22 | ZN4545:PA40 | URBAN | Equipment Failure | 903190 | 1607 | 104 | 166437 | 0.10125 | 0.097762
2012-11-22 | ZN4545:PA41 | URBAN | Equipment Failure | 903190 | 4 | 104 | 416 | 0.00025307 | 0.00024334
2012-11-22 | ZN1290:PA4 | URBAN | Other | 903223 | 21 | 132.9667 | 2792.3 | 0.0016987 | 0.0012775
2012-11-22 | 513:48050 | SHORT RURAL | Other | 903226 | 1 | 60.3 | 60.3 | 3.6684e-05 | 6.0835e-05
2012-11-22 | ZN1164:PA9 | URBAN | Vegetation | 903244 | 1 | 440.6 | 440.6 | 0.00026804 | 6.0835e-05
2012-11-22 | ZN1164:PA9 | URBAN | Other | 903270 | 1 | 100 | 100 | 6.0835e-05 | 6.0835e-05
2012-11-22 | ZN1788:PA30 | URBAN | Vegetation | 903300 | 1 | 382.05 | 382.05 | 0.00023242 | 6.0835e-05
2012-11-22 | ZN15004:PA9 | URBAN | Other | 903332 | 1 | 605.95 | 605.95 | 0.00036863 | 6.0835e-05
2012-11-23 | ZN15004:PA3 | URBAN | Other | 903342 | 1 | 99.5167 | 99.5167 | 6.0541e-05 | 6.0835e-05
2012-11-23 | ZN80:PA40 | URBAN | Other | 903375 | 1 | 67.05 | 67.05 | 4.079e-05 | 6.0835e-05
2012-11-23 | 203:8086 | URBAN | Other | 903379 | 1 | 97.4333 | 97.4333 | 5.9274e-05 | 6.0835e-05
2012-11-23 | ZN2835:PA31 | URBAN | Vegetation | 903393 | 1 | 131.3167 | 131.3167 | 7.9887e-05 | 6.0835e-05
2012-11-23 | ZN129:PA16 | URBAN | Other | 903409 | 55 | 38 | 2090 | 0.0012715 | 0.003346
2012-11-23 | 507:80922 | SHORT RURAL | Other | 903459 | 1 | 183.3333 | 183.3333 | 0.00011153 | 6.0835e-05
2012-11-23 | ZN9252:PA12 | URBAN | Equipment Failure | 903496 | 1 | 371.4333 | 371.4333 | 0.00022596 | 6.0835e-05
2012-11-23 | ZN2473:PA32 | URBAN | Equipment Failure | 903539 | 36 | 368.8 | 13276.8 | 0.008077 | 0.0021901
2012-11-23 | 515:35193 | SHORT RURAL | Equipment Failure | 903575 | 79 | 109 | 8187 | 0.0049806 | 0.004806
2012-11-23 | ZN2196:PA25 | URBAN | Equipment Failure | 903576 | 1 | 417.0667 | 417.0667 | 0.00025372 | 6.0835e-05
2012-11-23 | 264:81244 | URBAN | Other | 903579 | 1 | 107.0667 | 107.0667 | 6.5135e-05 | 6.0835e-05
2012-11-23 | 238:34136 | URBAN | Other | 903588 | 1 | 82.7667 | 82.7667 | 5.0351e-05 | 6.0835e-05
2012-11-23 | ZN2310:PA28 | URBAN | Third Party Impacts | 903594 | 87 | 45 | 3858.9 | 0.0023476 | 0.0052927
2012-11-24 | ZN12610:PA22 | URBAN | Animals | 903608 | 75 | 96 | 7200 | 0.0043802 | 0.0045627
2012-11-24 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 903611 | 13 | 164.6667 | 2140.6667 | 0.0013023 | 0.00079086
2012-11-24 | ZN3472:PA20 | URBAN | Other | 903655 | 19 | 55.1333 | 1047.5333 | 0.00063727 | 0.0011559
2012-11-24 | ZN35370:PA10 | SHORT RURAL | Equipment Failure | 903657 | 1 | 188.2833 | 188.2833 | 0.00011454 | 6.0835e-05
2012-11-24 | ZN7900:PA15 | URBAN | Equipment Failure | 903666 | 195 | 32 | 6240 | 0.0037961 | 0.011863
2012-11-24 | ZN690:PA11 | URBAN | Weather | 903673 | 12 | 125 | 1500 | 0.00091253 | 0.00073003
2012-11-24 | 806:74080 | SHORT RURAL | Other | 903674 | 1 | 124 | 124 | 7.5436e-05 | 6.0835e-05
2012-11-24 | ZN7481:PA9 | URBAN | Other | 903680 | 1 | 165.2333 | 165.2333 | 0.00010052 | 6.0835e-05
2012-11-24 | 806:74080 | SHORT RURAL | Other | 903689 | 36 | 320 | 10500 | 0.0063877 | 0.0021901
2012-11-25 | 806:74080 | SHORT RURAL | Other | 903691 | 2 | 290 | 580 | 0.00035285 | 0.00012167
2012-11-24 | 504:48028 | URBAN | Equipment Failure | 903700 | 57 | 76 | 4332 | 0.0026354 | 0.0034676
2012-11-25 | 514:18137 | SHORT RURAL | Other | 903712 | 10 | 180 | 1800 | 0.001095 | 0.00060835
2012-11-25 | ZN2568:PA16 | URBAN | Equipment Failure | 903716 | 123 | 141 | 17343 | 0.010551 | 0.0074828
2012-11-25 | ZN2568:PA32 | URBAN | Equipment Failure | 903716 | 2342 | 141 | 224554 | 0.13661 | 0.14248
2012-11-25 | ZN14891:PA20 | SHORT RURAL | Equipment Failure | 903720 | 8 | 237 | 1896 | 0.0011534 | 0.00048668
2012-11-25 | 810:74054 | LONG RURAL | Other | 903721 | 1 | 103.8 | 103.8 | 6.3147e-05 | 6.0835e-05
2012-11-25 | 231:8415 | SHORT RURAL | Other | 903723 | 40 | 220.5167 | 8820.6667 | 0.0053661 | 0.0024334
2012-11-25 | 810:74054 | LONG RURAL | Other | 903725 | 3 | 317 | 551 | 0.0003352 | 0.00018251
2012-11-25 | 810:74050 | SHORT RURAL | Other | 903727 | 1 | 233 | 233 | 0.00014175 | 6.0835e-05
2012-11-25 | ZN12660:PA6 | SHORT RURAL | Other | 903743 | 1 | 51.3167 | 51.3167 | 3.1219e-05 | 6.0835e-05
2012-11-25 | 810:74054 | LONG RURAL | Other | 903747 | 1 | 206.2167 | 206.2167 | 0.00012545 | 6.0835e-05
2012-11-25 | 810:74054 | LONG RURAL | Other | 903751 | 1 | 79.0333 | 79.0333 | 4.808e-05 | 6.0835e-05
2012-11-25 | ZN12630:PA4 | SHORT RURAL | Other | 903763 | 1 | 137.95 | 137.95 | 8.3923e-05 | 6.0835e-05
2012-11-25 | ZN10990:PA7 | URBAN | Equipment Failure | 903775 | 1566 | 107 | 88012 | 0.053543 | 0.095268
2012-11-25 | ZN10990:PA12 | URBAN | Other | 903780 | 37 | 150 | 5550 | 0.0033764 | 0.0022509
2012-11-25 | 801:74123 | SHORT RURAL | Other | 903784 | 1 | 35 | 35 | 2.1292e-05 | 6.0835e-05
2012-11-25 | 224:80332 | URBAN | Equipment Failure | 903785 | 332 | 192 | 21876 | 0.013308 | 0.020197
2012-11-25 | 225:33679 | URBAN | Equipment Failure | 903785 | 1416 | 192 | 49058 | 0.029845 | 0.086143
2012-11-25 | 229:34995 | SHORT RURAL | Vegetation | 903793 | 1 | 98.7 | 98.7 | 6.0045e-05 | 6.0835e-05
2012-11-25 | 229:34983 | SHORT RURAL | Vegetation | 903794 | 1 | 131.5333 | 131.5333 | 8.0019e-05 | 6.0835e-05
2012-11-25 | 514:18137 | SHORT RURAL | Other | 903799 | 2 | 75 | 150 | 9.1253e-05 | 0.00012167
2012-11-25 | 812:19072 | SHORT RURAL | Other | 903803 | 1 | 60 | 60 | 3.6501e-05 | 6.0835e-05
2012-11-25 | ZN398:PA3 | URBAN | Other | 903814 | 1 | 237.4 | 237.4 | 0.00014442 | 6.0835e-05
2012-11-25 | 501:48118 | SHORT RURAL | Equipment Failure | 903817 | 273 | 110 | 30030 | 0.018269 | 0.016608
2012-11-25 | 227:13019 | SHORT RURAL | Other | 903821 | 51 | 105.2167 | 5366.05 | 0.0032645 | 0.0031026
2012-11-25 | ZN80:PA28 | URBAN | Equipment Failure | 903831 | 1 | 980.6 | 980.6 | 0.00059655 | 6.0835e-05
2012-11-25 | 810:74054 | LONG RURAL | Other | 903833 | 1 | 70 | 70 | 4.2585e-05 | 6.0835e-05
2012-11-25 | 501:48118 | SHORT RURAL | Equipment Failure | 903839 | 15 | 252 | 3780 | 0.0022996 | 0.00091253
2012-11-25 | 227:13019 | SHORT RURAL | Other | 903842 | 51 | 221.9833 | 11321.15 | 0.0068873 | 0.0031026
2012-11-25 | 510:48164 | SHORT RURAL | Equipment Failure | 903847 | 1 | 515 | 515 | 0.0003133 | 6.0835e-05
2012-11-25 | 260:33344 | URBAN | Animals | 903854 | 101 | 55.8167 | 5637.4833 | 0.0034296 | 0.0061444
2012-11-25 | 514:18137 | SHORT RURAL | Equipment Failure | 903864 | 1 | 172 | 172 | 0.00010464 | 6.0835e-05
2012-11-25 | 227:13019 | SHORT RURAL | Equipment Failure | 903866 | 51 | 903.6 | 46083.6 | 0.028035 | 0.0031026
2012-11-26 | 504:48033 | SHORT RURAL | Other | 903911 | 14 | 41 | 574 | 0.0003492 | 0.0008517
2012-11-26 | 202:34260 | URBAN | Other | 903930 | 1 | 99.3333 | 99.3333 | 6.043e-05 | 6.0835e-05
2012-11-26 | 801:74118 | URBAN | Animals | 903937 | 1 | 29.1667 | 29.1667 | 1.7744e-05 | 6.0835e-05
2012-11-26 | 801:74118 | URBAN | Animals | 903939 | 1 | 26.8333 | 26.8333 | 1.6324e-05 | 6.0835e-05
2012-11-26 | ZN4545:PA21 | URBAN | Equipment Failure | 903952 | 1 | 249.7167 | 249.7167 | 0.00015192 | 6.0835e-05
2012-11-24 | 520:48172 | SHORT RURAL | Equipment Failure | 904004 | 39 | 22 | 858 | 0.00052197 | 0.0023726
2012-11-26 | ZN2835:PA16 | URBAN | Equipment Failure | 904028 | 113 | 217 | 21518 | 0.013091 | 0.0068744
2012-11-26 | 811:74234 | SHORT RURAL | Weather | 904057 | 1 | 96.6167 | 96.6167 | 5.8777e-05 | 6.0835e-05
2012-11-26 | 811:74234 | SHORT RURAL | Other | 904060 | 1 | 64.75 | 64.75 | 3.9391e-05 | 6.0835e-05
2012-11-25 | 516:48066 | SHORT RURAL | Other | 904100 | 103 | 208 | 21424 | 0.013033 | 0.0062661
2012-11-26 | ZN1673:PA19 | URBAN | Other | 904109 | 1 | 49.65 | 49.65 | 3.0205e-05 | 6.0835e-05
2012-11-26 | ZN12590:PA6 | SHORT RURAL | Third Party Impacts | 904110 | 1 | 209.0167 | 209.0167 | 0.00012716 | 6.0835e-05
2012-11-26 | ZN2310:PA28 | URBAN | Equipment Failure | 904117 | 1 | 258.5833 | 258.5833 | 0.00015731 | 6.0835e-05
2012-11-26 | ZN9700:PA17 | URBAN | Equipment Failure | 904135 | 1 | 300.5667 | 300.5667 | 0.00018285 | 6.0835e-05
2012-11-26 | 810:74054 | LONG RURAL | Other | 904137 | 1 | 113 | 113 | 6.8744e-05 | 6.0835e-05
2012-11-25 | 811:74234 | SHORT RURAL | Equipment Failure | 904153 | 255 | 304 | 25048 | 0.015238 | 0.015513
2012-11-26 | 502:48004 | URBAN | Other | 904159 | 1 | 348.9667 | 348.9667 | 0.0002123 | 6.0835e-05
2012-11-26 | ZN9700:PA17 | URBAN | Equipment Failure | 904169 | 1 | 248.75 | 248.75 | 0.00015133 | 6.0835e-05
2012-11-26 | 526:34641 | SHORT RURAL | Other | 904195 | 1 | 146.5667 | 146.5667 | 8.9165e-05 | 6.0835e-05
2012-11-26 | 514:18137 | SHORT RURAL | Other | 904219 | 288 | 283 | 50857 | 0.030939 | 0.017521
2012-11-26 | 524:33570 | SHORT RURAL | Vegetation | 904235 | 1 | 82.7167 | 82.7167 | 5.0321e-05 | 6.0835e-05
2012-11-26 | 514:18137 | SHORT RURAL | Other | 904246 | 226 | 134 | 30284 | 0.018423 | 0.013749
2012-11-26 | ZN2400:PA15 | URBAN | Other | 904264 | 1 | 448.55 | 448.55 | 0.00027288 | 6.0835e-05
2012-11-26 | ZN15005:PA2 | URBAN | Vegetation | 904277 | 1903 | 121 | 119536 | 0.07272 | 0.11577
2012-11-26 | ZN2400:PA26 | URBAN | Equipment Failure | 904281 | 953 | 145 | 90697 | 0.055176 | 0.057976
2012-11-26 | ZN1164:PA12 | URBAN | Other | 904293 | 1 | 244.05 | 244.05 | 0.00014847 | 6.0835e-05
2012-11-26 | 814:82283 | SHORT RURAL | Other | 904297 | 23 | 537 | 12351 | 0.0075138 | 0.0013992
2012-11-26 | ZN12630:PA1 | SHORT RURAL | Weather | 904311 | 1 | 125 | 125 | 7.6044e-05 | 6.0835e-05
2012-11-26 | 807:74183 | SHORT RURAL | Other | 904312 | 97 | 101 | 9797 | 0.0059601 | 0.005901
2012-11-26 | ZN12610:PA9 | SHORT RURAL | Other | 904320 | 1 | 267.5 | 267.5 | 0.00016273 | 6.0835e-05
2012-11-26 | 807:74184 | SHORT RURAL | Other | 904332 | 2 | 125 | 250 | 0.00015209 | 0.00012167
2012-11-26 | 801:74118 | URBAN | Other | 904337 | 76 | 150.1 | 11407.6 | 0.0069399 | 0.0046235
2012-11-26 | ZN12610:PA10 | SHORT RURAL | Other | 904338 | 1 | 93.5 | 93.5 | 5.6881e-05 | 6.0835e-05
2012-11-26 | 810:74054 | LONG RURAL | Other | 904340 | 1 | 58 | 58 | 3.5285e-05 | 6.0835e-05
2012-11-26 | 803:74016 | SHORT RURAL | Equipment Failure | 904344 | 51 | 16 | 816 | 0.00049642 | 0.0031026
2012-11-26 | 524:33578 | URBAN | Other | 904347 | 1 | 105.95 | 105.95 | 6.4455e-05 | 6.0835e-05
2012-11-26 | ZN12690:PA12 | SHORT RURAL | Other | 904348 | 1 | 560.4333 | 560.4333 | 0.00034094 | 6.0835e-05
2012-11-26 | 221:11894 | URBAN | Other | 904350 | 1 | 38.7667 | 38.7667 | 2.3584e-05 | 6.0835e-05
2012-11-26 | 526:34637 | SHORT RURAL | Other | 904352 | 1 | 231 | 231 | 0.00014053 | 6.0835e-05
2012-11-26 | 512:48049 | SHORT RURAL | Other | 904356 | 4 | 179 | 716 | 0.00043558 | 0.00024334
2012-11-26 | 810:74054 | LONG RURAL | Other | 904357 | 2 | 120 | 240 | 0.00014601 | 0.00012167
2012-11-26 | 512:48049 | SHORT RURAL | Other | 904359 | 7 | 429 | 3003 | 0.0018269 | 0.00042585
2012-11-26 | ZN10994:PA12 | URBAN | Other | 904361 | 140 | 42 | 5812.2667 | 0.0035359 | 0.008517
2012-11-26 | 803:74016 | SHORT RURAL | Other | 904369 | 1 | 157 | 157 | 9.5512e-05 | 6.0835e-05
2012-11-26 | 801:74121 | SHORT RURAL | Other | 904372 | 12 | 414 | 4968 | 0.0030223 | 0.00073003
2012-11-26 | 502:48010 | SHORT RURAL | Other | 904373 | 7 | 224.7333 | 1573.1333 | 0.00095702 | 0.00042585
2012-11-26 | ZN901:PA11 | URBAN | Equipment Failure | 904374 | 2478 | 6 | 14868 | 0.009045 | 0.15075
2012-11-26 | ZN901:PA12 | URBAN | Equipment Failure | 904374 | 466 | 6 | 2796 | 0.001701 | 0.028349
2012-11-26 | ZN901:PA13 | URBAN | Equipment Failure | 904374 | 1677 | 6 | 10062 | 0.0061213 | 0.10202
2012-11-26 | ZN901:PA14 | URBAN | Equipment Failure | 904374 | 955 | 6 | 5730 | 0.0034859 | 0.058098
2012-11-26 | ZN901:PA17 | URBAN | Equipment Failure | 904374 | 146 | 6 | 876 | 0.00053292 | 0.008882
2012-11-26 | ZN901:PA18 | URBAN | Equipment Failure | 904374 | 1090 | 6 | 6540 | 0.0039786 | 0.066311
2012-11-26 | ZN901:PA19 | URBAN | Equipment Failure | 904374 | 748 | 6 | 4488 | 0.0027303 | 0.045505
2012-11-26 | ZN901:PA20 | URBAN | Equipment Failure | 904374 | 1242 | 6 | 7452 | 0.0045335 | 0.075558
2012-11-26 | 507:80923 | SHORT RURAL | Other | 904382 | 17 | 490 | 8330 | 0.0050676 | 0.0010342
2012-11-26 | 507:80932 | SHORT RURAL | Other | 904390 | 3 | 569 | 1707 | 0.0010385 | 0.00018251
2012-11-26 | 512:48049 | SHORT RURAL | Other | 904397 | 11 | 124 | 1364 | 0.0008298 | 0.00066919
2012-11-26 | 238:34147 | URBAN | Equipment Failure | 904400 | 1170 | 230 | 173628 | 0.10563 | 0.071177
2012-11-26 | 235:2857 | SHORT RURAL | Other | 904402 | 1 | 148.9833 | 148.9833 | 9.0635e-05 | 6.0835e-05
2012-11-26 | 264:81240 | SHORT RURAL | Other | 904416 | 43 | 159.4333 | 6855.6333 | 0.0041707 | 0.0026159
2012-11-26 | ZN35500:PA31 | URBAN | Equipment Failure | 904419 | 1 | 141.6167 | 141.6167 | 8.6153e-05 | 6.0835e-05
2012-11-26 | 526:34640 | SHORT RURAL | Equipment Failure | 904425 | 7 | 399 | 2793 | 0.0016991 | 0.00042585
2012-11-26 | ZN1788:PA30 | URBAN | Other | 904431 | 1 | 205.8667 | 205.8667 | 0.00012524 | 6.0835e-05
2012-11-26 | ZN3922:PA1 | URBAN | Other | 904447 | 1 | 162.3333 | 162.3333 | 9.8756e-05 | 6.0835e-05
2012-11-26 | 206:34434 | URBAN | Equipment Failure | 904450 | 1 | 104.6667 | 104.6667 | 6.3674e-05 | 6.0835e-05
2012-11-26 | ZN129:PA19 | URBAN | Other | 904451 | 1 | 874.9167 | 874.9167 | 0.00053226 | 6.0835e-05
2012-11-26 | ZN15006:PA15 | URBAN | Other | 904452 | 1 | 954.2 | 954.2 | 0.00058049 | 6.0835e-05
2012-11-27 | 507:80925 | SHORT RURAL | Other | 904459 | 1 | 255.55 | 255.55 | 0.00015547 | 6.0836e-05
2012-11-27 | 514:18137 | SHORT RURAL | Equipment Failure | 904460 | 72 | 795 | 23288 | 0.014168 | 0.0043802
2012-11-27 | ZN35800:PA14 | URBAN | Equipment Failure | 904464 | 1877 | 125 | 213133 | 0.12966 | 0.11419
2012-11-27 | ZN15014:PA7 | URBAN | Other | 904466 | 1 | 517.8167 | 517.8167 | 0.00031502 | 6.0836e-05
2012-11-27 | ZN15010:PA1 | URBAN | Other | 904468 | 1 | 296.2 | 296.2 | 0.0001802 | 6.0836e-05
2012-11-27 | 514:18137 | SHORT RURAL | Other | 904473 | 2 | 146 | 292 | 0.00017764 | 0.00012167
2012-11-27 | 511:29877 | SHORT RURAL | Other | 904481 | 5 | 268.8833 | 1344.4167 | 0.00081789 | 0.00030418
2012-11-27 | ZN15010:PA1 | URBAN | Equipment Failure | 904483 | 1 | 289.5167 | 289.5167 | 0.00017613 | 6.0836e-05
2012-11-27 | 264:81240 | SHORT RURAL | Other | 904484 | 2 | 155 | 310 | 0.00018859 | 0.00012167
2012-11-27 | ZN129:PA9 | URBAN | Other | 904485 | 1 | 317.75 | 317.75 | 0.00019331 | 6.0836e-05
2012-11-27 | 801:74121 | SHORT RURAL | Other | 904489 | 1 | 95 | 95 | 5.7795e-05 | 6.0836e-05
2012-11-27 | 516:48067 | SHORT RURAL | Other | 904498 | 2 | 269 | 538 | 0.0003273 | 0.00012167
2012-11-27 | 515:35197 | LONG RURAL | Weather | 904499 | 1 | 140.4167 | 140.4167 | 8.5424e-05 | 6.0836e-05
2012-11-27 | ZN116:PA30 | URBAN | Equipment Failure | 904500 | 64 | 130 | 3712 | 0.0022582 | 0.0038935
2012-11-27 | ZN116:PA34 | URBAN | Equipment Failure | 904500 | 1370 | 130 | 131520 | 0.080012 | 0.083346
2012-11-27 | 264:81240 | SHORT RURAL | Other | 904501 | 2 | 174.95 | 349.9 | 0.00021287 | 0.00012167
2012-11-26 | 234:14291 | URBAN | Weather | 904502 | 592 | 630.8 | 31968 | 0.019448 | 0.036015
2012-11-26 | 234:2001 | URBAN | Weather | 904502 | 939 | 630.8 | 50706 | 0.030847 | 0.057125
2012-11-27 | 264:81240 | SHORT RURAL | Other | 904503 | 3 | 117 | 351 | 0.00021354 | 0.00018251
2012-11-27 | 264:81240 | SHORT RURAL | Other | 904511 | 21 | 204.3167 | 4290.65 | 0.0026103 | 0.0012776
2012-11-27 | 264:81240 | SHORT RURAL | Equipment Failure | 904512 | 16 | 377.25 | 4506.1 | 0.0027413 | 0.00097338
2012-11-26 | 264:81240 | SHORT RURAL | Other | 904516 | 1 | 188 | 188 | 0.00011437 | 6.0835e-05
2012-11-27 | ZN9301:PA8 | URBAN | Other | 904517 | 1 | 239.1833 | 239.1833 | 0.00014551 | 6.0836e-05
2012-11-27 | ZN15010:PA1 | URBAN | Other | 904520 | 1 | 134.4333 | 134.4333 | 8.1784e-05 | 6.0836e-05
2012-11-27 | ZN12630:PA1 | SHORT RURAL | Other | 904521 | 1 | 123.0667 | 123.0667 | 7.4869e-05 | 6.0836e-05
2012-11-27 | 811:74234 | SHORT RURAL | Other | 904531 | 3 | 262 | 786 | 0.00047817 | 0.00018251
2012-11-27 | 807:74183 | SHORT RURAL | Other | 904533 | 1 | 127 | 127 | 7.7262e-05 | 6.0836e-05
2012-11-27 | 218:7478 | URBAN | Equipment Failure | 904537 | 57 | 121.6 | 6931.2 | 0.0042167 | 0.0034677
2012-11-27 | 524:33570 | SHORT RURAL | Other | 904540 | 56 | 222.4 | 12454.4 | 0.0075768 | 0.0034068
2012-11-27 | 502:48009 | URBAN | Other | 904578 | 45 | 204.3667 | 9196.5 | 0.0055948 | 0.0027376
2012-11-26 | ZN15014:PA20 | URBAN | Other | 904587 | 1 | 875.8333 | 875.8333 | 0.00053282 | 6.0835e-05
2012-11-27 | ZN12600:PA3 | URBAN | Other | 904616 | 19 | 132.1 | 2509.9 | 0.0015269 | 0.0011559
2012-11-27 | 526:34637 | SHORT RURAL | Other | 904626 | 1 | 27.2333 | 27.2333 | 1.6568e-05 | 6.0836e-05
2012-11-27 | ZN15001:PA4 | URBAN | Other | 904639 | 1 | 513.5833 | 513.5833 | 0.00031245 | 6.0836e-05
2012-11-27 | ZN384:PA9 | URBAN | Equipment Failure | 904658 | 2 | 656 | 1312 | 0.00079817 | 0.00012167
2012-11-27 | ZN15014:PA12 | SHORT RURAL | Other | 904692 | 1 | 241.6833 | 241.6833 | 0.00014703 | 6.0836e-05
2012-11-27 | 801:74121 | SHORT RURAL | Other | 904699 | 7 | 177 | 1239 | 0.00075376 | 0.00042585
2012-11-27 | 502:48009 | URBAN | Equipment Failure | 904725 | 1 | 118.1833 | 118.1833 | 7.1898e-05 | 6.0836e-05
2012-11-27 | ZN14892:PA8 | URBAN | Equipment Failure | 904728 | 1 | 1789.5 | 1789.5 | 0.0010887 | 6.0836e-05
2012-11-27 | ZN10999:PA11 | URBAN | Equipment Failure | 904732 | 5 | 404.4833 | 2022.4167 | 0.0012304 | 0.00030418
2012-11-26 | ZN2400:PA21 | URBAN | Weather | 904743 | 112 | 92 | 10304 | 0.0062685 | 0.0068136
2012-11-27 | 526:34637 | SHORT RURAL | Other | 904781 | 1 | 235.2833 | 235.2833 | 0.00014314 | 6.0836e-05
2012-11-27 | 526:34640 | SHORT RURAL | Equipment Failure | 904798 | 21 | 60 | 1260 | 0.00076654 | 0.0012776
2012-11-27 | ZN12610:PA2 | URBAN | Equipment Failure | 904804 | 1 | 1153.1667 | 1153.1667 | 0.00070154 | 6.0836e-05
2012-11-26 | 801:74118 | URBAN | Other | 904809 | 799 | 6 | 4794 | 0.0029165 | 0.048608
2012-11-08 | ZN965:PA37 | URBAN | Other | 904815 | 75 | 109 | 8175 | 0.0049744 | 0.0045636
2012-11-27 | ZN3154:PA24 | URBAN | Equipment Failure | 904817 | 91 | 102 | 9221.3333 | 0.0056099 | 0.0055361
2012-11-27 | ZN3154:PA25 | URBAN | Equipment Failure | 904817 | 7 | 102 | 714 | 0.00043437 | 0.00042585
2012-11-26 | 811:74234 | SHORT RURAL | Equipment Failure | 904819 | 5 | 70 | 350 | 0.00021292 | 0.00030418
2012-11-27 | ZN1290:PA10 | URBAN | Equipment Failure | 904826 | 34 | 55 | 1789 | 0.0010884 | 0.0020684
2012-11-26 | 814:82283 | SHORT RURAL | Other | 904844 | 3 | 197 | 591 | 0.00035954 | 0.00018251
2012-11-27 | ZN14144:PA4 | URBAN | Equipment Failure | 904885 | 38 | 164 | 6232 | 0.0037913 | 0.0023118
2012-11-27 | 814:82283 | SHORT RURAL | Other | 904893 | 1 | 167.6333 | 167.6333 | 0.00010198 | 6.0836e-05
2012-11-27 | 512:48049 | SHORT RURAL | Other | 904929 | 4 | 251 | 1004 | 0.0006108 | 0.00024335
2012-11-27 | 206:34432 | URBAN | Equipment Failure | 904939 | 1 | 2295.1667 | 2295.1667 | 0.0013963 | 6.0836e-05
2012-11-27 | 232:11459 | SHORT RURAL | Other | 904945 | 1 | 134.4833 | 134.4833 | 8.1815e-05 | 6.0836e-05
2012-11-27 | ZN36300:PA19 | URBAN | Other | 904956 | 1 | 1074.6833 | 1074.6833 | 0.0006538 | 6.0836e-05
2012-11-27 | ZN9037:PA8 | URBAN | Other | 904958 | 1 | 79.55 | 79.55 | 4.8395e-05 | 6.0836e-05
2012-11-27 | 803:74010 | SHORT RURAL | Other | 904964 | 1 | 159.7667 | 159.7667 | 9.7196e-05 | 6.0836e-05
2012-11-27 | 807:74184 | SHORT RURAL | Equipment Failure | 904968 | 1 | 110 | 110 | 6.692e-05 | 6.0836e-05
2012-11-27 | ZN9245:PA10 | URBAN | Other | 904971 | 1 | 55.6667 | 55.6667 | 3.3866e-05 | 6.0836e-05
2012-11-27 | 813:89061 | LONG RURAL | Other | 904973 | 1 | 277 | 277 | 0.00016852 | 6.0836e-05
2012-11-27 | ZN35600:PA19 | URBAN | Other | 904979 | 1 | 104.1167 | 104.1167 | 6.3341e-05 | 6.0836e-05
2012-11-27 | 512:48049 | SHORT RURAL | Equipment Failure | 904985 | 1 | 215.1333 | 215.1333 | 0.00013088 | 6.0836e-05
2012-11-27 | ZN35600:PA19 | URBAN | Other | 904986 | 1 | 86.4333 | 86.4333 | 5.2583e-05 | 6.0836e-05
2012-11-27 | ZN15015:PA5 | URBAN | Other | 904990 | 1 | 175.25 | 175.25 | 0.00010662 | 6.0836e-05
2012-11-27 | ZN2602:PA9 | URBAN | Other | 904993 | 1 | 186.25 | 186.25 | 0.00011331 | 6.0836e-05
2012-11-27 | 803:74010 | SHORT RURAL | Other | 904994 | 1 | 80 | 80 | 4.8669e-05 | 6.0836e-05
2012-11-27 | 264:81236 | URBAN | Other | 904995 | 1 | 330.0333 | 330.0333 | 0.00020078 | 6.0836e-05
2012-11-27 | ZN9252:PA2 | URBAN | Other | 905007 | 1 | 682.3 | 682.3 | 0.00041509 | 6.0836e-05
2012-11-27 | 214:8665 | URBAN | Other | 905013 | 1 | 760.6167 | 760.6167 | 0.00046273 | 6.0836e-05
2012-11-28 | ZN15002:PA6 | URBAN | Other | 905021 | 1 | 492.6 | 492.6 | 0.00029968 | 6.0836e-05
2012-11-28 | ZN3155:PA29 | URBAN | Vegetation | 905024 | 1 | 430.1833 | 430.1833 | 0.00026171 | 6.0836e-05
2012-11-28 | 520:48172 | SHORT RURAL | Other | 905032 | 2 | 168.8 | 337.6 | 0.00020538 | 0.00012167
2012-11-28 | 803:74010 | SHORT RURAL | Equipment Failure | 905033 | 3 | 294.05 | 882.15 | 0.00053667 | 0.00018251
2012-11-28 | ZN2602:PA15 | URBAN | Equipment Failure | 905036 | 1 | 392.9667 | 392.9667 | 0.00023907 | 6.0836e-05
2012-11-28 | ZN15008:PA10 | URBAN | Other | 905037 | 1 | 359.5333 | 359.5333 | 0.00021873 | 6.0836e-05
2012-11-28 | ZN3922:PA21 | SHORT RURAL | Other | 905040 | 1 | 183.8167 | 183.8167 | 0.00011183 | 6.0836e-05
2012-11-28 | 238:34141 | SHORT RURAL | Equipment Failure | 905044 | 7 | 78.1833 | 547.2833 | 0.00033295 | 0.00042585
2012-11-28 | ZN12660:PA5 | SHORT RURAL | Equipment Failure | 905045 | 38 | 245.6167 | 9333.4333 | 0.0056781 | 0.0023118
2012-11-28 | ZN2602:PA42 | URBAN | Other | 905050 | 1 | 379.0333 | 379.0333 | 0.00023059 | 6.0836e-05
2012-11-28 | 526:34640 | SHORT RURAL | Other | 905052 | 4 | 121.15 | 484.6 | 0.00029481 | 0.00024335
2012-11-28 | 509:48039 | LONG RURAL | Other | 905053 | 1 | 227.85 | 227.85 | 0.00013862 | 6.0836e-05
2012-11-28 | ZN167:PA20 | URBAN | Equipment Failure | 905067 | 1 | 157.4667 | 157.4667 | 9.5797e-05 | 6.0836e-05
2012-11-28 | ZN5868:PA14 | URBAN | Equipment Failure | 905074 | 1 | 198.2167 | 198.2167 | 0.00012059 | 6.0836e-05
2012-11-28 | 814:82283 | SHORT RURAL | Other | 905076 | 2 | 75 | 150 | 9.1255e-05 | 0.00012167
2012-11-28 | ZN15010:PA5 | URBAN | Other | 905085 | 1 | 96.5333 | 96.5333 | 5.8727e-05 | 6.0836e-05
2012-11-26 | 512:48046 | SHORT RURAL | Equipment Failure | 905092 | 69 | 842 | 6709 | 0.0040815 | 0.0041976
2012-11-28 | ZN1193:PA28 | URBAN | Third Party Impacts | 905097 | 13 | 340 | 4420 | 0.002689 | 0.00079087
2012-11-28 | 232:11454 | SHORT RURAL | Other | 905099 | 1 | 442.6 | 442.6 | 0.00026926 | 6.0836e-05
2012-11-28 | ZN187:PA30 | URBAN | Third Party Impacts | 905106 | 64 | 137 | 8768 | 0.0053341 | 0.0038935
2012-11-28 | ZN129:PA5 | URBAN | Other | 905155 | 34 | 113.9833 | 3875.4333 | 0.0023577 | 0.0020684
2012-11-28 | ZN1193:PA6 | URBAN | Equipment Failure | 905176 | 113 | 27 | 3051 | 0.0018561 | 0.0068745
2012-11-28 | ZN80:PA31 | URBAN | Equipment Failure | 905176 | 251 | 27 | 6777 | 0.0041229 | 0.01527
2012-11-28 | ZN10994:PA18 | SHORT RURAL | Other | 905294 | 1 | 118.0167 | 118.0167 | 7.1797e-05 | 6.0836e-05
2012-11-28 | ZN35370:PA10 | SHORT RURAL | Vegetation | 905310 | 187 | 69.0833 | 12918.5833 | 0.0078592 | 0.011376
2012-11-28 | ZN35370:PA2 | SHORT RURAL | Vegetation | 905310 | 78 | 69.0833 | 5388.5 | 0.0032782 | 0.0047452
2012-11-27 | 227:13020 | SHORT RURAL | Other | 905318 | 1 | 20 | 20 | 1.2167e-05 | 6.0836e-05
2012-11-27 | 235:8684 | SHORT RURAL | Other | 905327 | 17 | 270 | 4590 | 0.0027924 | 0.0010342
2012-11-27 | 264:81240 | SHORT RURAL | Other | 905342 | 6 | 46 | 276 | 0.00016791 | 0.00036502
2012-11-28 | ZN4545:PA6 | URBAN | Equipment Failure | 905349 | 16 | 247 | 3952 | 0.0024043 | 0.00097338
2012-11-27 | 526:34637 | SHORT RURAL | Other | 905355 | 1 | 216 | 216 | 0.00013141 | 6.0836e-05
2012-11-28 | ZN15012:PA8 | URBAN | Other | 905384 | 1 | 170.7333 | 170.7333 | 0.00010387 | 6.0836e-05
2012-11-28 | ZN10995:PA5 | URBAN | Other | 905389 | 1 | 98.75 | 98.75 | 6.0076e-05 | 6.0836e-05
2012-11-28 | 523:33508 | SHORT RURAL | Other | 905462 | 1 | 87.05 | 87.05 | 5.2958e-05 | 6.0836e-05
2012-11-28 | 220:8689 | URBAN | Other | 905490 | 1 | 115.6333 | 115.6333 | 7.0347e-05 | 6.0836e-05
2012-11-28 | 803:74010 | SHORT RURAL | Other | 905507 | 1190 | 194 | 119378 | 0.072625 | 0.072395
2012-11-28 | 256:80635 | URBAN | Other | 905537 | 1 | 57.7667 | 57.7667 | 3.5143e-05 | 6.0836e-05
2012-11-28 | 229:34983 | SHORT RURAL | Other | 905542 | 1 | 93.9833 | 93.9833 | 5.7176e-05 | 6.0836e-05
2012-11-28 | ZN12630:PA3 | SHORT RURAL | Weather | 905545 | 5 | 189 | 944.9833 | 0.00057489 | 0.00030418
2012-11-28 | ZN14891:PA12 | SHORT RURAL | Other | 905547 | 1 | 10.6167 | 10.6167 | 6.4588e-06 | 6.0836e-05
2012-11-28 | ZN12630:PA3 | SHORT RURAL | Weather | 905558 | 6 | 81.7333 | 490.4 | 0.00029834 | 0.00036502
2012-11-28 | 802:82220 | SHORT RURAL | Vegetation | 905564 | 26 | 843 | 9198 | 0.0055957 | 0.0015817
2012-11-28 | ZN14892:PA8 | URBAN | Other | 905566 | 1 | 453.8667 | 453.8667 | 0.00027612 | 6.0836e-05
2012-11-28 | 258:80793 | SHORT RURAL | Equipment Failure | 905573 | 1 | 98.9167 | 98.9167 | 6.0177e-05 | 6.0836e-05
2012-11-29 | 217:33610 | URBAN | Equipment Failure | 905579 | 1 | 133.0833 | 133.0833 | 8.0963e-05 | 6.0837e-05
2012-11-29 | 507:80932 | SHORT RURAL | Other | 905585 | 24 | 192 | 4608 | 0.0028033 | 0.0014601
2012-11-29 | ZN1290:PA1 | URBAN | Equipment Failure | 905588 | 33 | 47 | 1551 | 0.00094357 | 0.0020076
2012-11-29 | ZN15006:PA1 | URBAN | Equipment Failure | 905595 | 201 | 278 | 55878 | 0.033994 | 0.012228
2012-11-29 | ZN3154:PA13 | URBAN | Vegetation | 905603 | 44 | 120.4833 | 5301.2667 | 0.0032251 | 0.0026768
2012-11-28 | 502:48010 | SHORT RURAL | Equipment Failure | 905636 | 4 | 330 | 1320 | 0.00080304 | 0.00024335
2012-11-28 | 513:48059 | SHORT RURAL | Other | 905639 | 3 | 30 | 90 | 5.4753e-05 | 0.00018251
2012-11-29 | ZN711:PA33 | URBAN | Vegetation | 905674 | 1 | 18.8167 | 18.8167 | 1.1447e-05 | 6.0837e-05
2012-11-29 | ZN711:PA33 | URBAN | Third Party Impacts | 905679 | 1 | 142.9167 | 142.9167 | 8.6946e-05 | 6.0837e-05
2012-11-29 | 813:89062 | SHORT RURAL | Other | 905705 | 1 | 162 | 162 | 9.8555e-05 | 6.0837e-05
2012-11-29 | 509:48039 | LONG RURAL | Equipment Failure | 905773 | 15 | 98.6167 | 1479.25 | 0.00089992 | 0.00091255
2012-11-29 | ZN12660:PA10 | SHORT RURAL | Equipment Failure | 905784 | 42 | 25 | 1050 | 0.00063878 | 0.0025551
2012-11-29 | ZN2310:PA40 | URBAN | Third Party Impacts | 905801 | 1 | 84.0333 | 84.0333 | 5.1123e-05 | 6.0837e-05
2012-11-29 | 813:89061 | LONG RURAL | Weather | 905830 | 4 | 130 | 520 | 0.00031635 | 0.00024335
2012-11-29 | ZN12580:PA4 | URBAN | Other | 905893 | 1 | 47.0167 | 47.0167 | 2.8603e-05 | 6.0837e-05
2012-11-29 | 258:80781 | SHORT RURAL | Vegetation | 905908 | 1 | 59.2333 | 59.2333 | 3.6035e-05 | 6.0837e-05
2012-11-29 | 264:81240 | SHORT RURAL | Other | 905909 | 417 | 30 | 12510 | 0.0076106 | 0.025369
2012-11-30 | ZN2473:PA20 | URBAN | Other | 905918 | 71 | 125 | 8875 | 0.0053992 | 0.0043194
2012-11-29 | ZN12660:PA14 | SHORT RURAL | Other | 905920 | 1288 | 168 | 169396 | 0.10305 | 0.078357
2012-11-29 | ZN12660:PA16 | URBAN | Other | 905920 | 829 | 168 | 65080 | 0.039592 | 0.050433
2012-11-29 | 232:11455 | URBAN | Other | 905932 | 1 | 87.3333 | 87.3333 | 5.3131e-05 | 6.0837e-05
2012-11-29 | 219:1783 | SHORT RURAL | Other | 905958 | 1 | 149.8 | 149.8 | 9.1133e-05 | 6.0837e-05
2012-11-29 | ZN4545:PA17 | URBAN | Other | 905967 | 944 | 74 | 55528 | 0.033781 | 0.05743
2012-11-29 | ZN3154:PA13 | URBAN | Other | 905976 | 1 | 342.1667 | 342.1667 | 0.00020816 | 6.0837e-05
2012-11-29 | ZN398:PA30 | URBAN | Other | 905977 | 1 | 1087.1833 | 1087.1833 | 0.0006614 | 6.0837e-05
2012-11-29 | ZN12660:PA14 | SHORT RURAL | Equipment Failure | 905986 | 61 | 94 | 5734 | 0.0034884 | 0.003711
2012-11-29 | ZN129:PA16 | URBAN | Animals | 905993 | 55 | 44 | 2420 | 0.0014722 | 0.003346
2012-11-29 | ZN129:PA3 | URBAN | Animals | 905993 | 1406 | 44 | 61864 | 0.037636 | 0.085536
2012-11-29 | ZN129:PA5 | URBAN | Animals | 905993 | 4 | 44 | 176 | 0.00010707 | 0.00024335
2012-11-29 | ZN129:PA8 | URBAN | Animals | 905993 | 67 | 44 | 2948 | 0.0017935 | 0.004076
2012-11-30 | ZN847:PA23 | URBAN | Vegetation | 906020 | 1 | 175.2333 | 175.2333 | 0.00010661 | 6.0837e-05
2012-11-30 | 526:34636 | SHORT RURAL | Equipment Failure | 906025 | 1 | 52 | 52 | 3.1635e-05 | 6.0837e-05
2012-11-30 | ZN4545:PA27 | URBAN | Other | 906047 | 31 | 120 | 3720 | 0.0022631 | 0.0018859
2012-11-30 | ZN12600:PA1 | SHORT RURAL | Equipment Failure | 906077 | 90 | 64.8167 | 5833.5 | 0.0035489 | 0.0054753
2012-11-30 | ZN847:PA5 | URBAN | Vegetation | 906084 | 1 | 164.2333 | 164.2333 | 9.9914e-05 | 6.0837e-05
2012-11-30 | 205:12213 | URBAN | Vegetation | 906090 | 1 | 88.4833 | 88.4833 | 5.383e-05 | 6.0837e-05
2012-11-30 | ZN398:PA10 | URBAN | Third Party Impacts | 906154 | 1 | 133.2 | 133.2 | 8.1034e-05 | 6.0837e-05
2012-11-30 | ZN2635:PA3 | URBAN | Equipment Failure | 906186 | 1 | 138 | 138 | 8.3954e-05 | 6.0837e-05
2012-11-30 | ZN2635:PA4 | URBAN | Equipment Failure | 906186 | 1 | 138 | 138 | 8.3954e-05 | 6.0837e-05
2012-11-30 | ZN9301:PA13 | SHORT RURAL | Equipment Failure | 906221 | 2 | 328 | 656 | 0.00039909 | 0.00012167
2012-11-30 | ZN9301:PA8 | URBAN | Equipment Failure | 906221 | 1 | 328 | 327.4667 | 0.00019922 | 6.0837e-05
2012-11-30 | ZN15013:PA1 | URBAN | Equipment Failure | 906227 | 260 | 146 | 36028 | 0.021918 | 0.015818
2012-11-30 | ZN12570:PA33 | SHORT RURAL | Vegetation | 906228 | 3 | 42 | 126 | 7.6654e-05 | 0.00018251
2012-11-30 | ZN12570:PA40 | SHORT RURAL | Vegetation | 906228 | 1194 | 42 | 50148 | 0.030508 | 0.072639
2012-11-30 | ZN690:PA15 | URBAN | Other | 906246 | 18 | 81 | 1458 | 0.000887 | 0.0010951
2012-11-30 | ZN690:PA34 | URBAN | Other | 906246 | 38 | 81 | 3042.5333 | 0.001851 | 0.0023118
2012-11-30 | 202:34245 | URBAN | Other | 906252 | 110 | 36.0667 | 3967.3333 | 0.0024136 | 0.006692
2012-11-30 | ZN12610:PA25 | SHORT RURAL | Other | 906255 | 1 | 401.75 | 401.75 | 0.00024441 | 6.0837e-05
2012-11-30 | 224:80340 | SHORT RURAL | Other | 906256 | 1 | 212.25 | 212.25 | 0.00012913 | 6.0837e-05
2012-11-30 | ZN9118:PA3 | SHORT RURAL | Equipment Failure | 906264 | 1 | 255.0333 | 255.0333 | 0.00015515 | 6.0837e-05
2012-11-30 | 235:2123 | URBAN | Equipment Failure | 906270 | 43 | 376.4833 | 16188.7833 | 0.0098487 | 0.002616
2012-11-30 | 512:48049 | SHORT RURAL | Other | 906286 | 1 | 96.7333 | 96.7333 | 5.8849e-05 | 6.0837e-05
2012-11-30 | ZN4545:PA44 | URBAN | Vegetation | 906298 | 81 | 23 | 1863 | 0.0011334 | 0.0049278
2012-11-30 | ZN269:PA16 | URBAN | Equipment Failure | 906318 | 83 | 150 | 12450 | 0.0075741 | 0.0050494
2012-11-30 | 205:12203 | URBAN | Other | 906333 | 1 | 210.9833 | 210.9833 | 0.00012835 | 6.0837e-05
2012-11-30 | ZN12640:PA8 | SHORT RURAL | Equipment Failure | 906336 | 1 | 351.9667 | 351.9667 | 0.00021412 | 6.0837e-05
2012-11-30 | 227:13015 | SHORT RURAL | Other | 906344 | 1 | 100.0667 | 100.0667 | 6.0877e-05 | 6.0837e-05
2012-11-30 | 509:48039 | LONG RURAL | Weather | 906375 | 2 | 211.25 | 422.5 | 0.00025703 | 0.00012167
2012-11-30 | 509:48039 | LONG RURAL | Other | 906385 | 75 | 82.0333 | 6152.5 | 0.003743 | 0.0045627
2012-11-30 | 205:12210 | URBAN | Other | 906392 | 123 | 52.35 | 6439.05 | 0.0039173 | 0.0074829
2012-11-30 | ZN3154:PA11 | URBAN | Equipment Failure | 906395 | 743 | 83 | 59562 | 0.036235 | 0.045202
2012-11-30 | 512:48046 | SHORT RURAL | Equipment Failure | 906402 | 2 | 130.7667 | 261.5333 | 0.00015911 | 0.00012167
2012-11-30 | ZN4545:PA17 | URBAN | Equipment Failure | 906406 | 128 | 283.1167 | 36238.9333 | 0.022047 | 0.0077871
2012-11-30 | 509:48039 | LONG RURAL | Weather | 906413 | 1 | 41.1833 | 41.1833 | 2.5055e-05 | 6.0837e-05
2012-11-30 | ZN965:PA15 | URBAN | Other | 906417 | 71 | 180.2667 | 12798.9333 | 0.0077864 | 0.0043194
2012-11-30 | 524:33576 | SHORT RURAL | Weather | 906420 | 2 | 387.0167 | 774.0333 | 0.0004709 | 0.00012167
2012-11-30 | 526:34636 | SHORT RURAL | Weather | 906427 | 1 | 212 | 212 | 0.00012897 | 6.0837e-05
2012-11-30 | ZN35370:PA10 | SHORT RURAL | Equipment Failure | 906434 | 9 | 186.9667 | 1682.7 | 0.0010237 | 0.00054753
2012-11-30 | ZN1164:PA15 | URBAN | Other | 906438 | 1 | 204.55 | 204.55 | 0.00012444 | 6.0837e-05
2012-11-30 | 526:34637 | SHORT RURAL | Weather | 906440 | 5 | 170 | 850 | 0.00051711 | 0.00030418
2012-11-30 | 225:13446 | URBAN | Equipment Failure | 906446 | 44 | 112.6667 | 4957.3333 | 0.0030159 | 0.0026768
2012-11-30 | ZN12620:PA2 | SHORT RURAL | Weather | 906449 | 13 | 83.2167 | 1081.8167 | 0.00065814 | 0.00079088
2012-12-01 | 509:48040 | SHORT RURAL | Other | 906472 | 2 | 656 | 1312 | 0.00079818 | 0.00012167
2012-12-01 | ZN10995:PA12 | URBAN | Other | 906473 | 1 | 627.15 | 627.15 | 0.00038154 | 6.0837e-05
2012-12-01 | 807:74184 | SHORT RURAL | Animals | 906477 | 2 | 342 | 684 | 0.00041612 | 0.00012167
2012-12-01 | ZN10995:PA6 | URBAN | Other | 906478 | 1 | 729.1 | 729.1 | 0.00044356 | 6.0837e-05
2012-12-01 | ZN269:PA6 | URBAN | Equipment Failure | 906480 | 94 | 201.25 | 18917.5 | 0.011509 | 0.0057186
2012-12-01 | ZN9301:PA13 | SHORT RURAL | Equipment Failure | 906482 | 4 | 383.2333 | 720 | 0.00043802 | 0.00024335
2012-12-01 | ZN9301:PA8 | URBAN | Equipment Failure | 906482 | 1 | 383.2333 | 383.2333 | 0.00023315 | 6.0837e-05
2012-12-01 | ZN10994:PA19 | URBAN | Vegetation | 906495 | 1 | 470.5167 | 470.5167 | 0.00028625 | 6.0837e-05
2012-12-01 | 524:33570 | SHORT RURAL | Other | 906496 | 1 | 552.3167 | 552.3167 | 0.00033601 | 6.0837e-05
2012-12-01 | 801:74118 | URBAN | Other | 906510 | 34 | 85.7 | 2913.8 | 0.0017727 | 0.0020684
2012-12-01 | ZN3425:PA30 | URBAN | Other | 906514 | 1 | 691.4333 | 691.4333 | 0.00042064 | 6.0837e-05
2012-12-01 | 520:48172 | SHORT RURAL | Equipment Failure | 906528 | 43 | 93.6667 | 4027.6667 | 0.0024503 | 0.002616
2012-12-01 | ZN1193:PA25 | URBAN | Other | 906535 | 1 | 534.9833 | 534.9833 | 0.00032547 | 6.0837e-05
2012-12-01 | 258:80779 | URBAN | Other | 906540 | 1 | 346.9667 | 346.9667 | 0.00021108 | 6.0837e-05
2012-12-01 | 810:74054 | LONG RURAL | Other | 906541 | 1 | 368.8167 | 368.8167 | 0.00022438 | 6.0837e-05
2012-12-01 | ZN15013:PA10 | SHORT RURAL | Vegetation | 906542 | 15 | 84.9 | 1273.5 | 0.00077475 | 0.00091255
2012-12-01 | ZN12660:PA17 | URBAN | Equipment Failure | 906545 | 1 | 203.6667 | 203.6667 | 0.0001239 | 6.0837e-05
2012-12-01 | 515:35192 | SHORT RURAL | Animals | 906561 | 1 | 94 | 94 | 5.7186e-05 | 6.0837e-05
2012-12-01 | 264:81244 | URBAN | Other | 906584 | 1 | 156.0833 | 156.0833 | 9.4956e-05 | 6.0837e-05
2012-12-01 | 803:74010 | SHORT RURAL | Other | 906592 | 1 | 82 | 82 | 4.9886e-05 | 6.0837e-05
2012-12-01 | 256:80644 | URBAN | Other | 906609 | 1 | 111.4333 | 111.4333 | 6.7792e-05 | 6.0837e-05
2012-12-01 | ZN10994:PA4 | URBAN | Equipment Failure | 906619 | 1 | 65 | 32 | 1.9468e-05 | 6.0837e-05
2012-12-01 | ZN10995:PA1 | URBAN | Equipment Failure | 906619 | 2084 | 65 | 69608 | 0.042347 | 0.12678
2012-12-01 | ZN10996:PA20 | URBAN | Animals | 906629 | 281 | 66 | 18546 | 0.011283 | 0.017095
2012-12-01 | 502:48010 | SHORT RURAL | Other | 906631 | 25 | 194 | 4850 | 0.0029506 | 0.0015209
2012-12-01 | 202:34254 | URBAN | Equipment Failure | 906635 | 98 | 80.1167 | 7851.4333 | 0.0047765 | 0.005962
2012-12-01 | ZN9245:PA4 | URBAN | Vegetation | 906639 | 29 | 243 | 7047 | 0.0042872 | 0.0017643
2012-12-01 | 526:34636 | SHORT RURAL | Equipment Failure | 906648 | 8 | 306.0667 | 2448.5333 | 0.0014896 | 0.00048669
2012-12-01 | ZN10994:PA20 | URBAN | Other | 906649 | 59 | 136.0333 | 8025.9667 | 0.0048827 | 0.0035894
2012-12-01 | ZN10994:PA7 | URBAN | Other | 906660 | 182 | 154 | 28028 | 0.017051 | 0.011072
2012-12-01 | 524:33576 | SHORT RURAL | Other | 906668 | 5 | 323 | 1615 | 0.00098251 | 0.00030418
2012-12-01 | 224:80337 | URBAN | Other | 906678 | 1 | 356.1667 | 356.1667 | 0.00021668 | 6.0837e-05
2012-12-01 | 507:80917 | URBAN | Other | 906680 | 1 | 364.1833 | 364.1833 | 0.00022156 | 6.0837e-05
2012-12-01 | 507:80923 | SHORT RURAL | Equipment Failure | 906681 | 62 | 95.2667 | 5906.5333 | 0.0035933 | 0.0037719
2012-12-01 | ZN195:PA11 | URBAN | Equipment Failure | 906685 | 43 | 182 | 7819.7 | 0.0047572 | 0.002616
2012-12-01 | 238:34147 | URBAN | Equipment Failure | 906691 | 92 | 110 | 10120 | 0.0061567 | 0.005597
2012-12-01 | 515:35197 | LONG RURAL | Other | 906696 | 3 | 103.05 | 309.15 | 0.00018808 | 0.00018251
2012-12-01 | 502:48010 | SHORT RURAL | Equipment Failure | 906708 | 1 | 1420.5167 | 1420.5167 | 0.00086419 | 6.0837e-05
2012-12-01 | 806:74080 | SHORT RURAL | Other | 906709 | 1 | 192.5167 | 192.5167 | 0.00011712 | 6.0837e-05
2012-12-01 | 501:48122 | SHORT RURAL | Weather | 906713 | 1 | 823.7 | 823.7 | 0.00050111 | 6.0837e-05
2012-12-01 | 512:48049 | SHORT RURAL | Other | 906717 | 7 | 166.1833 | 1163.2833 | 0.0007077 | 0.00042586
2012-12-01 | 503:48011 | SHORT RURAL | Other | 906721 | 1 | 206.9333 | 206.9333 | 0.00012589 | 6.0837e-05
2012-12-01 | 230:81432 | URBAN | Weather | 906722 | 114 | 912 | 9120 | 0.0055483 | 0.0069354
2012-12-01 | 231:8415 | SHORT RURAL | Weather | 906722 | 932 | 912 | 259229 | 0.15771 | 0.0567
2012-12-01 | 238:34141 | SHORT RURAL | Other | 906725 | 7 | 381 | 2667 | 0.0016225 | 0.00042586
2012-12-01 | 232:33411 | SHORT RURAL | Vegetation | 906727 | 1526 | 740 | 618668 | 0.37638 | 0.092837
2012-12-01 | 813:89055 | SHORT RURAL | Other | 906729 | 1 | 279.9333 | 279.9333 | 0.0001703 | 6.0837e-05
2012-12-01 | ZN262:PA34 | URBAN | Other | 906732 | 1 | 257.4833 | 257.4833 | 0.00015664 | 6.0837e-05
2012-12-01 | 232:11454 | SHORT RURAL | Other | 906750 | 1 | 1417.5167 | 1417.5167 | 0.00086237 | 6.0837e-05
2012-12-01 | 510:48164 | SHORT RURAL | Other | 906765 | 1 | 184 | 184 | 0.00011194 | 6.0837e-05
2012-12-01 | ZN129:PA18 | URBAN | Other | 906769 | 26 | 110 | 2860 | 0.0017399 | 0.0015818
2012-12-01 | ZN129:PA4 | URBAN | Other | 906769 | 39 | 110 | 3510 | 0.0021354 | 0.0023726
2012-12-02 | ZN15002:PA6 | URBAN | Equipment Failure | 906773 | 1603 | 681 | 244154 | 0.14853 | 0.097521
2012-12-02 | ZN12610:PA9 | SHORT RURAL | Other | 906774 | 1 | 670.1667 | 670.1667 | 0.00040771 | 6.0837e-05
2012-12-02 | ZN15004:PA3 | URBAN | Other | 906776 | 1 | 565.5 | 565.5 | 0.00034403 | 6.0837e-05
2012-12-02 | 512:48046 | SHORT RURAL | Weather | 906779 | 21 | 557.5333 | 11708.2 | 0.0071229 | 0.0012776
2012-12-02 | 802:82215 | SHORT RURAL | Vegetation | 906782 | 40 | 414 | 16560 | 0.010075 | 0.0024335
2012-12-02 | 802:82220 | SHORT RURAL | Vegetation | 906782 | 60 | 414 | 24840 | 0.015112 | 0.0036502
2012-12-02 | 802:82225 | SHORT RURAL | Vegetation | 906782 | 105 | 414 | 43470 | 0.026446 | 0.0063878
2012-12-02 | 810:74050 | SHORT RURAL | Vegetation | 906782 | 91 | 414 | 37674 | 0.02292 | 0.0055361
2012-12-02 | 810:74054 | LONG RURAL | Vegetation | 906782 | 320 | 414 | 132480 | 0.080596 | 0.019468
2012-12-02 | 810:74058 | SHORT RURAL | Vegetation | 906782 | 200 | 414 | 82800 | 0.050373 | 0.012167
2012-12-02 | 810:74062 | SHORT RURAL | Vegetation | 906782 | 607 | 414 | 251298 | 0.15288 | 0.036928
2012-12-02 | 812:19065 | SHORT RURAL | Equipment Failure | 906791 | 1 | 945.3 | 945.3 | 0.00057509 | 6.0837e-05
2012-12-02 | 264:81240 | SHORT RURAL | Other | 906792 | 42 | 781.8167 | 32836.3 | 0.019976 | 0.0025551
2012-12-02 | 501:48122 | SHORT RURAL | Equipment Failure | 906797 | 1 | 496.4333 | 496.4333 | 0.00030201 | 6.0837e-05
2012-12-02 | ZN4545:PA41 | URBAN | Vegetation | 906799 | 37 | 61.8 | 2286.6 | 0.0013911 | 0.002251
2012-12-02 | 813:89055 | SHORT RURAL | Other | 906804 | 5 | 329 | 1645 | 0.0010008 | 0.00030418
2012-12-02 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 906807 | 2 | 93.0833 | 186.1667 | 0.00011326 | 0.00012167
2012-12-02 | ZN35370:PA2 | SHORT RURAL | Equipment Failure | 906812 | 24 | 175 | 4200 | 0.0025551 | 0.0014601
2012-12-02 | 514:18137 | SHORT RURAL | Equipment Failure | 906816 | 1 | 223 | 223 | 0.00013567 | 6.0837e-05
2012-12-02 | 503:48011 | SHORT RURAL | Weather | 906819 | 3 | 384 | 1152 | 0.00070084 | 0.00018251
2012-12-02 | 232:33411 | SHORT RURAL | Other | 906827 | 1 | 876.7667 | 876.7667 | 0.00053339 | 6.0837e-05
2012-12-02 | 510:48164 | SHORT RURAL | Third Party Impacts | 906833 | 1 | 673.9 | 673.9 | 0.00040998 | 6.0837e-05
2012-12-02 | 512:48049 | SHORT RURAL | Other | 906839 | 1 | 190 | 190 | 0.00011559 | 6.0837e-05
2012-12-02 | ZN12570:PA41 | URBAN | Animals | 906850 | 486 | 25 | 7776 | 0.0047306 | 0.029567
2012-12-02 | ZN14144:PA8 | URBAN | Animals | 906850 | 481 | 25 | 8362 | 0.0050872 | 0.029262
2012-12-02 | 507:80917 | URBAN | Third Party Impacts | 906856 | 1 | 302.0667 | 302.0667 | 0.00018377 | 6.0837e-05
2012-12-02 | 803:74016 | SHORT RURAL | Animals | 906858 | 1 | 155 | 155 | 9.4297e-05 | 6.0837e-05
2012-12-02 | 232:33411 | SHORT RURAL | Other | 906866 | 2 | 717.4667 | 1434.9333 | 0.00087296 | 0.00012167
2012-12-02 | 510:48164 | SHORT RURAL | Other | 906870 | 1 | 100 | 100 | 6.0837e-05 | 6.0837e-05
2012-12-02 | 232:33411 | SHORT RURAL | Other | 906880 | 1 | 688.15 | 688.15 | 0.00041865 | 6.0837e-05
2012-12-02 | 232:11454 | SHORT RURAL | Vegetation | 906893 | 1 | 489.5 | 489.5 | 0.00029779 | 6.0837e-05
2012-12-02 | 807:74184 | SHORT RURAL | Other | 906896 | 1 | 39.4333 | 39.4333 | 2.399e-05 | 6.0837e-05
2012-12-02 | 807:74180 | SHORT RURAL | Other | 906905 | 3 | 49 | 147 | 8.943e-05 | 0.00018251
2012-12-02 | 503:48012 | URBAN | Third Party Impacts | 906916 | 1 | 333.3667 | 333.3667 | 0.00020281 | 6.0837e-05
2012-12-02 | 516:48067 | SHORT RURAL | Other | 906917 | 2 | 395 | 790 | 0.00048061 | 0.00012167
2012-12-02 | ZN874:PA4 | URBAN | Equipment Failure | 906918 | 232 | 53 | 12296 | 0.0074805 | 0.014114
2012-12-02 | 232:11454 | SHORT RURAL | Vegetation | 906927 | 1 | 310.6 | 310.6 | 0.00018896 | 6.0837e-05
2012-12-02 | ZN12610:PA9 | SHORT RURAL | Third Party Impacts | 906930 | 104 | 39 | 4056 | 0.0024675 | 0.006327
2012-12-02 | 232:11454 | SHORT RURAL | Other | 906937 | 1 | 394.0667 | 394.0667 | 0.00023974 | 6.0837e-05
2012-12-02 | 232:33411 | SHORT RURAL | Vegetation | 906938 | 1 | 524.1667 | 524.1667 | 0.00031888 | 6.0837e-05
2012-12-02 | 801:74120 | SHORT RURAL | Equipment Failure | 906939 | 1 | 89.5167 | 89.5167 | 5.4459e-05 | 6.0837e-05
2012-12-02 | 230:81434 | URBAN | Vegetation | 906941 | 1 | 345.5833 | 345.5833 | 0.00021024 | 6.0837e-05
2012-12-02 | 810:74058 | SHORT RURAL | Other | 906943 | 1 | 119.4667 | 119.4667 | 7.2679e-05 | 6.0837e-05
2012-12-02 | 503:48011 | SHORT RURAL | Vegetation | 906947 | 1 | 183.7167 | 183.7167 | 0.00011177 | 6.0837e-05
2012-12-02 | ZN965:PA15 | URBAN | Other | 906948 | 1 | 980.4 | 980.4 | 0.00059644 | 6.0837e-05
2012-12-02 | 232:33409 | URBAN | Other | 906949 | 1 | 837.8667 | 837.8667 | 0.00050973 | 6.0837e-05
2012-12-02 | ZN2473:PA31 | URBAN | Animals | 906953 | 1 | 50.3833 | 50.3833 | 3.0651e-05 | 6.0837e-05
2012-12-02 | 232:33411 | SHORT RURAL | Vegetation | 906956 | 1 | 151.1667 | 151.1667 | 9.1965e-05 | 6.0837e-05
2012-12-02 | 810:74054 | LONG RURAL | Other | 906966 | 1 | 64.5833 | 64.5833 | 3.929e-05 | 6.0837e-05
2012-12-02 | 264:81240 | SHORT RURAL | Other | 906968 | 1 | 901.8167 | 901.8167 | 0.00054863 | 6.0837e-05
2012-12-02 | 810:74054 | LONG RURAL | Other | 906969 | 1 | 116 | 116 | 7.057e-05 | 6.0837e-05
2012-12-02 | 814:82283 | SHORT RURAL | Equipment Failure | 906973 | 23 | 111.7 | 2569.1 | 0.001563 | 0.0013992
2012-12-02 | ZN15008:PA7 | URBAN | Other | 906977 | 1 | 125.0667 | 125.0667 | 7.6086e-05 | 6.0837e-05
2012-12-02 | 232:11454 | SHORT RURAL | Vegetation | 906985 | 1 | 93.6833 | 93.6833 | 5.6994e-05 | 6.0837e-05
2012-12-02 | 235:2120 | SHORT RURAL | Other | 906993 | 1 | 69 | 69 | 4.1977e-05 | 6.0837e-05
2012-12-02 | 216:10726 | URBAN | Other | 906996 | 1 | 73.8 | 73.8 | 4.4897e-05 | 6.0837e-05
2012-12-02 | 810:74054 | LONG RURAL | Other | 906997 | 1 | 141.1167 | 141.1167 | 8.585e-05 | 6.0837e-05
2012-12-02 | 258:80775 | URBAN | Other | 907008 | 1 | 696.9333 | 696.9333 | 0.00042399 | 6.0837e-05
2012-12-03 | ZN12640:PA13 | SHORT RURAL | Equipment Failure | 907015 | 1 | 285.6833 | 285.6833 | 0.0001738 | 6.0837e-05
2012-12-03 | 206:34432 | URBAN | Other | 907018 | 1 | 99 | 99 | 6.0228e-05 | 6.0837e-05
2012-12-03 | ZN1164:PA23 | URBAN | Equipment Failure | 907026 | 1 | 296.9 | 296.9 | 0.00018062 | 6.0837e-05
2012-12-03 | ZN80:PA32 | URBAN | Other | 907027 | 1 | 266.8333 | 266.8333 | 0.00016233 | 6.0837e-05
2012-12-03 | ZN3155:PA23 | URBAN | Other | 907029 | 1 | 502.6167 | 502.6167 | 0.00030577 | 6.0837e-05
2012-11-27 | ZN2310:PA4 | URBAN | Equipment Failure | 907059 | 29 | 92 | 2668 | 0.0016231 | 0.0017643
2012-12-03 | 222:2018 | URBAN | Other | 907066 | 1 | 265.5167 | 265.5167 | 0.00016153 | 6.0837e-05
2012-11-30 | ZN3472:PA11 | URBAN | Third Party Impacts | 907074 | 7 | 90 | 630 | 0.00038327 | 0.00042586
2012-12-03 | ZN3154:PA24 | URBAN | Other | 907077 | 1 | 56.95 | 56.95 | 3.4646e-05 | 6.0837e-05
2012-12-03 | 515:35197 | LONG RURAL | Other | 907083 | 2 | 144 | 288 | 0.00017521 | 0.00012167
2012-12-03 | ZN3155:PA24 | URBAN | Equipment Failure | 907088 | 1 | 88.65 | 88.65 | 5.3932e-05 | 6.0837e-05
2012-12-03 | 520:48172 | SHORT RURAL | Other | 907096 | 115 | 125 | 8381 | 0.0050987 | 0.0069962
2012-12-03 | 813:89059 | URBAN | Weather | 907103 | 1 | 135.45 | 135.45 | 8.2403e-05 | 6.0837e-05
2012-12-03 | 520:48172 | SHORT RURAL | Other | 907108 | 2 | 107 | 214 | 0.00013019 | 0.00012167
2012-12-03 | 520:48172 | SHORT RURAL | Other | 907111 | 2 | 90 | 180 | 0.00010951 | 0.00012167
2012-12-03 | 520:48172 | SHORT RURAL | Weather | 907114 | 1 | 137.7833 | 137.7833 | 8.3823e-05 | 6.0837e-05
2012-12-03 | 520:48172 | SHORT RURAL | Equipment Failure | 907121 | 1 | 220 | 220 | 0.00013384 | 6.0837e-05
2012-12-03 | 520:48172 | SHORT RURAL | Other | 907136 | 2 | 136 | 272 | 0.00016548 | 0.00012167
2012-12-03 | 523:33501 | SHORT RURAL | Other | 907171 | 1 | 57.6167 | 57.6167 | 3.5052e-05 | 6.0837e-05
2012-12-03 | 513:48052 | URBAN | Third Party Impacts | 907222 | 1 | 96.8667 | 96.8667 | 5.893e-05 | 6.0837e-05
2012-12-03 | 232:33411 | SHORT RURAL | Vegetation | 907254 | 1 | 210.1167 | 210.1167 | 0.00012783 | 6.0837e-05
2012-12-03 | 524:33572 | SHORT RURAL | Other | 907283 | 3 | 135 | 405 | 0.00024639 | 0.00018251
2012-12-03 | ZN2466:PA6 | URBAN | Equipment Failure | 907285 | 23 | 71 | 1617 | 0.00098373 | 0.0013992
2012-12-03 | 520:48172 | SHORT RURAL | Other | 907299 | 2 | 87 | 174 | 0.00010586 | 0.00012167
2012-11-30 | ZN12630:PA5 | SHORT RURAL | Other | 907315 | 42 | 10 | 420 | 0.00025551 | 0.0025551
2012-12-03 | ZN12610:PA16 | URBAN | Third Party Impacts | 907405 | 1 | 82.6667 | 82.6667 | 5.0292e-05 | 6.0837e-05
2012-12-03 | ZN180:PA15 | URBAN | Other | 907408 | 53 | 236 | 12508 | 0.0076094 | 0.0032243
2012-12-03 | 232:33409 | URBAN | Other | 907439 | 1 | 215.5667 | 215.5667 | 0.00013114 | 6.0837e-05
2012-12-03 | ZN2602:PA36 | URBAN | Other | 907440 | 1 | 182.1833 | 182.1833 | 0.00011083 | 6.0837e-05
2012-12-03 | ZN12650:PA1 | SHORT RURAL | Vegetation | 907446 | 1476 | 82 | 116916 | 0.071128 | 0.089795
2012-12-03 | ZN12600:PA11 | URBAN | Other | 907491 | 1 | 217.4333 | 217.4333 | 0.00013228 | 6.0837e-05
2012-12-03 | 264:81240 | SHORT RURAL | Equipment Failure | 907498 | 21 | 77.7667 | 1633.1 | 0.00099352 | 0.0012776
2012-12-03 | 811:74234 | SHORT RURAL | Animals | 907511 | 1 | 67.3 | 67.3 | 4.0943e-05 | 6.0837e-05
2012-12-03 | 501:48122 | SHORT RURAL | Other | 907515 | 1 | 93.7 | 93.7 | 5.7004e-05 | 6.0837e-05
2012-12-03 | ZN9900:PA2 | URBAN | Other | 907527 | 1 | 965.85 | 965.85 | 0.00058759 | 6.0837e-05
2012-12-03 | ZN15008:PA7 | URBAN | Other | 907751 | 1 | 131.75 | 131.75 | 8.0152e-05 | 6.0837e-05
2012-12-03 | ZN2466:PA41 | URBAN | Other | 907755 | 1 | 104.9167 | 104.9167 | 6.3828e-05 | 6.0837e-05
2012-12-03 | ZN10990:PA2 | URBAN | Equipment Failure | 907756 | 1 | 667.6667 | 667.6667 | 0.00040619 | 6.0837e-05
2012-12-03 | ZN15006:PA9 | URBAN | Other | 907760 | 1 | 610.3833 | 610.3833 | 0.00037134 | 6.0837e-05
2012-12-04 | ZN188:PA15 | URBAN | Equipment Failure | 907761 | 2 | 97 | 148 | 9.0039e-05 | 0.00012167
2012-12-04 | ZN8100:PA10 | URBAN | Equipment Failure | 907761 | 253 | 97 | 19307 | 0.011746 | 0.015392
2012-12-04 | 264:81240 | SHORT RURAL | Equipment Failure | 907764 | 21 | 396.0667 | 8317.4 | 0.0050601 | 0.0012776
2012-12-04 | ZN180:PA43 | URBAN | Third Party Impacts | 907774 | 23 | 60.3 | 1386.9 | 0.00084375 | 0.0013993
2012-12-04 | ZN9252:PA12 | URBAN | Vegetation | 907781 | 1221 | 157 | 113498 | 0.069049 | 0.074282
2012-12-04 | ZN9252:PA7 | URBAN | Vegetation | 907781 | 581 | 157 | 84655 | 0.051502 | 0.035346
2012-12-04 | ZN15010:PA7 | URBAN | Equipment Failure | 907785 | 6 | 266.4333 | 1598.6 | 0.00097254 | 0.00036502
2012-12-04 | 814:82283 | SHORT RURAL | Other | 907786 | 4 | 85.9667 | 154.9667 | 9.4277e-05 | 0.00024335
2012-12-04 | 807:74184 | SHORT RURAL | Animals | 907789 | 2 | 165 | 317.7333 | 0.0001933 | 0.00012167
2012-12-04 | 526:34637 | SHORT RURAL | Equipment Failure | 907821 | 1 | 85 | 85 | 5.1712e-05 | 6.0837e-05
2012-12-04 | ZN15010:PA9 | SHORT RURAL | Equipment Failure | 907852 | 1 | 272.6167 | 272.6167 | 0.00016585 | 6.0837e-05
2012-12-04 | 232:11457 | URBAN | Vegetation | 907866 | 1 | 146.4833 | 146.4833 | 8.9116e-05 | 6.0837e-05
2012-12-04 | 520:48172 | SHORT RURAL | Other | 907868 | 1 | 65 | 65 | 3.9544e-05 | 6.0837e-05
2012-12-01 | ZN3922:PA14 | URBAN | Operational Error | 907881 | 49 | 55 | 2695 | 0.0016395 | 0.002981
2012-12-04 | ZN12600:PA13 | SHORT RURAL | Equipment Failure | 907913 | 14 | 95.1 | 1331.4 | 0.00080999 | 0.00085172
2012-12-04 | ZN14891:PA12 | SHORT RURAL | Third Party Impacts | 907975 | 1 | 114.05 | 114.05 | 6.9385e-05 | 6.0837e-05
2012-12-04 | ZN9035:PA11 | URBAN | Equipment Failure | 907978 | 95 | 198.5667 | 18863.8333 | 0.011476 | 0.0057795
2012-12-04 | ZN3155:PA32 | URBAN | Vegetation | 907995 | 1 | 263.1333 | 263.1333 | 0.00016008 | 6.0837e-05
2012-12-04 | 507:80931 | URBAN | Equipment Failure | 908008 | 1 | 243.7333 | 243.7333 | 0.00014828 | 6.0837e-05
2012-12-04 | ZN180:PA22 | URBAN | Equipment Failure | 908010 | 18 | 1367.6667 | 24618 | 0.014977 | 0.0010951
2012-12-04 | 502:48010 | SHORT RURAL | Animals | 908055 | 83 | 286.1667 | 21139.95 | 0.012861 | 0.0050495
2012-12-04 | 260:33353 | URBAN | Other | 908069 | 51 | 214.0333 | 10915.7 | 0.0066408 | 0.0031027
2012-12-04 | ZN2310:PA17 | URBAN | Third Party Impacts | 908085 | 49 | 75 | 3675 | 0.0022358 | 0.002981
2012-12-04 | 515:35197 | LONG RURAL | Other | 908097 | 1 | 164.3833 | 164.3833 | 0.00010001 | 6.0837e-05
2012-12-04 | ZN2310:PA22 | URBAN | Other | 908120 | 84 | 43 | 3566 | 0.0021695 | 0.0051103
2012-12-04 | ZN2310:PA28 | URBAN | Other | 908120 | 9 | 43 | 387 | 0.00023544 | 0.00054753
2012-12-04 | 208:53 | URBAN | Other | 908136 | 1 | 67 | 67 | 4.0761e-05 | 6.0837e-05
2012-12-04 | ZN10990:PA2 | URBAN | Third Party Impacts | 908143 | 1 | 144.4167 | 144.4167 | 8.7859e-05 | 6.0837e-05
2012-12-04 | ZN2835:PA27 | URBAN | Vegetation | 908161 | 48 | 74.6333 | 3582.4 | 0.0021794 | 0.0029202
2012-12-04 | ZN2568:PA32 | URBAN | Third Party Impacts | 908201 | 1 | 223.5667 | 223.5667 | 0.00013601 | 6.0837e-05
2012-12-04 | ZN847:PA1 | URBAN | Vegetation | 908202 | 29 | 178 | 5138.2 | 0.0031259 | 0.0017643
2012-12-05 | 811:74234 | SHORT RURAL | Animals | 908225 | 1 | 106 | 106 | 6.4488e-05 | 6.0838e-05
2012-12-05 | 206:34432 | URBAN | Other | 908226 | 1 | 74 | 74 | 4.502e-05 | 6.0838e-05
2012-12-05 | ZN1673:PA19 | URBAN | Third Party Impacts | 908230 | 1 | 135.2333 | 135.2333 | 8.2273e-05 | 6.0838e-05
2012-12-05 | 503:48076 | URBAN | Other | 908234 | 1 | 140.95 | 140.95 | 8.575e-05 | 6.0838e-05
2012-12-05 | 810:74050 | SHORT RURAL | Other | 908256 | 2 | 206.35 | 324.35 | 0.00019733 | 0.00012168
2012-12-05 | 523:33501 | SHORT RURAL | Other | 908288 | 93 | 73.5333 | 6838.6 | 0.0041604 | 0.0056579
2012-12-05 | 523:33501 | SHORT RURAL | Other | 908301 | 1 | 36.95 | 36.95 | 2.2479e-05 | 6.0838e-05
2012-12-05 | 803:74016 | SHORT RURAL | Equipment Failure | 908302 | 1 | 104 | 104 | 6.3271e-05 | 6.0838e-05
2012-12-05 | ZN9171:PA1 | URBAN | Vegetation | 908369 | 4 | 472 | 248 | 0.00015088 | 0.00024335
2012-12-05 | ZN9171:PA3 | SHORT RURAL | Vegetation | 908369 | 2 | 472 | 124 | 7.5439e-05 | 0.00012168
2012-12-05 | ZN12620:PA7 | URBAN | Equipment Failure | 908388 | 1 | 75.1333 | 75.1333 | 4.5709e-05 | 6.0838e-05
2012-12-05 | ZN2568:PA6 | SHORT RURAL | Other | 908439 | 1 | 175.3167 | 175.3167 | 0.00010666 | 6.0838e-05
2012-12-05 | 208:58 | URBAN | Vegetation | 908441 | 1 | 165.2 | 165.2 | 0.0001005 | 6.0838e-05
2012-12-05 | ZN2310:PA22 | URBAN | Vegetation | 908451 | 42 | 76.9333 | 3231.2 | 0.0019658 | 0.0025552
2012-12-05 | 509:48040 | SHORT RURAL | Other | 908455 | 1 | 339.2167 | 339.2167 | 0.00020637 | 6.0838e-05
2012-12-05 | 227:13015 | SHORT RURAL | Vegetation | 908462 | 69 | 15 | 1035 | 0.00062967 | 0.0041978
2012-12-05 | ZN340:PA8 | URBAN | Equipment Failure | 908477 | 1 | 53.8667 | 53.8667 | 3.2771e-05 | 6.0838e-05
2012-12-05 | ZN188:PA14 | URBAN | Equipment Failure | 908489 | 305 | 96 | 27132 | 0.016506 | 0.018555
2012-12-05 | ZN188:PA32 | URBAN | Equipment Failure | 908489 | 1162 | 96 | 111552 | 0.067865 | 0.070693
2012-12-05 | 801:74123 | SHORT RURAL | Equipment Failure | 908512 | 10 | 90 | 900 | 0.00054754 | 0.00060838
2012-12-05 | ZN1193:PA28 | URBAN | Vegetation | 908516 | 1 | 250.3833 | 250.3833 | 0.00015233 | 6.0838e-05
2012-12-05 | ZN3155:PA17 | URBAN | Equipment Failure | 908519 | 51 | 1598 | 81498 | 0.049581 | 0.0031027
2012-12-04 | ZN340:PA2 | URBAN | Third Party Impacts | 908542 | 18 | 68 | 1224 | 0.00074465 | 0.0010951
2012-12-05 | 230:81440 | URBAN | Vegetation | 908548 | 1 | 538.8333 | 538.8333 | 0.00032781 | 6.0838e-05
2012-12-05 | ZN12690:PA24 | SHORT RURAL | Equipment Failure | 908579 | 7 | 187 | 1309 | 0.00079636 | 0.00042586
2012-12-05 | ZN1673:PA19 | URBAN | Vegetation | 908607 | 1 | 125.0833 | 125.0833 | 7.6098e-05 | 6.0838e-05
2012-12-05 | ZN15005:PA12 | URBAN | Vegetation | 908649 | 1 | 213.6833 | 213.6833 | 0.00013 | 6.0838e-05
2012-12-05 | 507:80925 | SHORT RURAL | Other | 908672 | 1 | 72.0667 | 72.0667 | 4.3844e-05 | 6.0838e-05
2012-12-05 | 234:2001 | URBAN | Other | 908676 | 1 | 140.4 | 140.4 | 8.5416e-05 | 6.0838e-05
2012-12-05 | ZN965:PA15 | URBAN | Vegetation | 908677 | 1 | 287.65 | 287.65 | 0.000175 | 6.0838e-05
2012-12-05 | 520:48172 | SHORT RURAL | Other | 908680 | 3 | 66 | 198 | 0.00012046 | 0.00018251
2012-12-05 | ZN1287:PA6 | URBAN | Equipment Failure | 908681 | 1 | 337.6667 | 337.6667 | 0.00020543 | 6.0838e-05
2012-12-07 | ZN12570:PA24 | SHORT RURAL | Other | 908685 | 4 | 30 | 120 | 7.3006e-05 | 0.00024335
2012-12-05 | ZN15014:PA22 | URBAN | Equipment Failure | 908689 | 1 | 834.8333 | 834.8333 | 0.00050789 | 6.0838e-05
2012-12-05 | ZN1164:PA15 | URBAN | Other | 908698 | 1 | 71.8 | 71.8 | 4.3681e-05 | 6.0838e-05
2012-12-05 | ZN342:PA17 | URBAN | Other | 908701 | 1 | 505.4667 | 505.4667 | 0.00030751 | 6.0838e-05
2012-12-06 | 206:34432 | URBAN | Other | 908718 | 1 | 59 | 59 | 3.5894e-05 | 6.0838e-05
2012-12-06 | 520:48172 | SHORT RURAL | Equipment Failure | 908719 | 3 | 85 | 255 | 0.00015514 | 0.00018251
2012-12-06 | ZN2196:PA17 | URBAN | Other | 908724 | 1 | 234.4833 | 234.4833 | 0.00014265 | 6.0838e-05
2012-12-04 | ZN2310:PA4 | URBAN | Other | 908784 | 5 | 69 | 345 | 0.00020989 | 0.00030419
2012-12-06 | 223:14394 | URBAN | Other | 908794 | 1 | 79.1333 | 79.1333 | 4.8143e-05 | 6.0838e-05
2012-12-01 | 231:8405 | SHORT RURAL | Other | 908811 | 95 | 137 | 13015 | 0.0079179 | 0.0057795
2012-12-01 | 264:81240 | SHORT RURAL | Other | 908845 | 1 | 452 | 452 | 0.00027498 | 6.0837e-05
2012-12-06 | ZN10999:PA24 | URBAN | Other | 908879 | 1 | 114.9 | 114.9 | 6.9903e-05 | 6.0838e-05
2012-12-06 | ZN8100:PA10 | URBAN | Other | 908880 | 61 | 31.1833 | 1902.1833 | 0.0011572 | 0.0037111
2012-12-06 | ZN8100:PA20 | URBAN | Other | 908896 | 52 | 48 | 2496 | 0.0015185 | 0.0031636
2012-12-06 | 513:48050 | SHORT RURAL | Other | 908926 | 1 | 26.6667 | 26.6667 | 1.6223e-05 | 6.0838e-05
2012-12-06 | ZN15014:PA19 | URBAN | Equipment Failure | 908937 | 1 | 276.25 | 276.25 | 0.00016806 | 6.0838e-05
2012-12-06 | 515:35197 | LONG RURAL | Other | 908947 | 3 | 52 | 156 | 9.4907e-05 | 0.00018251
2012-12-03 | ZN129:PA16 | URBAN | Other | 908948 | 55 | 200 | 11000 | 0.006692 | 0.003346
2012-12-04 | ZN4545:PA25 | URBAN | Third Party Impacts | 908952 | 36 | 404 | 14544 | 0.0088482 | 0.0021901
2012-12-02 | 503:48011 | SHORT RURAL | Equipment Failure | 908961 | 8 | 685 | 5480 | 0.0033338 | 0.00048669
2012-12-06 | ZN2835:PA29 | URBAN | Weather | 908965 | 5 | 223 | 1115 | 0.00067834 | 0.00030419
2012-12-06 | ZN2835:PA32 | SHORT RURAL | Weather | 908965 | 132 | 223 | 29436 | 0.017908 | 0.0080306
2012-12-06 | ZN129:PA3 | URBAN | Vegetation | 909000 | 62 | 115 | 7130 | 0.0043377 | 0.0037719
2012-12-06 | ZN129:PA5 | URBAN | Vegetation | 909000 | 1 | 115 | 115 | 6.9964e-05 | 6.0838e-05
2012-12-01 | ZN10994:PA7 | URBAN | Other | 909010 | 71 | 133 | 9443 | 0.0057448 | 0.0043194
2012-12-02 | 501:48122 | SHORT RURAL | Equipment Failure | 909025 | 4 | 110 | 440 | 0.00026768 | 0.00024335
2012-12-03 | 501:48123 | SHORT RURAL | Equipment Failure | 909045 | 52 | 78 | 4056 | 0.0024675 | 0.0031635
2012-12-06 | ZN15004:PA3 | URBAN | Other | 909049 | 1 | 69.1167 | 69.1167 | 4.2049e-05 | 6.0838e-05
2012-12-02 | 810:74054 | LONG RURAL | Other | 909077 | 48 | 871 | 41808 | 0.025435 | 0.0029202
2012-12-02 | 810:74054 | LONG RURAL | Other | 909082 | 54 | 240 | 12960 | 0.0078844 | 0.0032852
2012-12-06 | 807:74183 | SHORT RURAL | Equipment Failure | 909109 | 1 | 90.3667 | 90.3667 | 5.4977e-05 | 6.0838e-05
2012-12-06 | ZN14891:PA14 | SHORT RURAL | Equipment Failure | 909123 | 5 | 542 | 2710 | 0.0016487 | 0.00030419
2012-12-06 | ZN2310:PA33 | URBAN | Operational Error | 909135 | 64 | 194.6 | 12454.4 | 0.007577 | 0.0038936
2012-12-06 | 813:89061 | LONG RURAL | Equipment Failure | 909137 | 30 | 344 | 6180 | 0.0037598 | 0.0018251
2012-12-07 | 525:34589 | URBAN | Other | 909147 | 1 | 80 | 80 | 4.8671e-05 | 6.0838e-05
2012-12-07 | 206:34432 | URBAN | Other | 909150 | 1 | 52 | 52 | 3.1636e-05 | 6.0838e-05
2012-12-07 | 513:48052 | URBAN | Other | 909152 | 1 | 465.3333 | 465.3333 | 0.0002831 | 6.0838e-05
2012-12-02 | 810:74058 | SHORT RURAL | Other | 909160 | 33 | 758 | 25014 | 0.015218 | 0.0020076
2012-12-07 | ZN10995:PA6 | URBAN | Third Party Impacts | 909164 | 33 | 61.4833 | 2028.95 | 0.0012344 | 0.0020077
2012-12-02 | 807:74180 | SHORT RURAL | Other | 909176 | 8 | 265 | 2120 | 0.0012897 | 0.00048669
2012-12-02 | 514:18137 | SHORT RURAL | Other | 909186 | 3 | 163 | 489 | 0.00029749 | 0.00018251
2012-12-02 | 514:18137 | SHORT RURAL | Equipment Failure | 909191 | 2 | 323 | 646 | 0.000393 | 0.00012167
2012-12-07 | ZN12650:PA10 | URBAN | Third Party Impacts | 909212 | 1047 | 252 | 73499 | 0.044715 | 0.063698
2012-12-07 | ZN12650:PA12 | URBAN | Third Party Impacts | 909212 | 4 | 252 | 118 | 7.1789e-05 | 0.00024335
2012-12-07 | ZN12650:PA14 | URBAN | Third Party Impacts | 909212 | 1 | 252 | 252 | 0.00015331 | 6.0838e-05
2012-12-07 | 231:8415 | SHORT RURAL | Vegetation | 909228 | 24 | 52.6 | 1262.4 | 0.00076802 | 0.0014601
2012-12-07 | 232:33413 | SHORT RURAL | Other | 909230 | 1 | 677.1333 | 677.1333 | 0.00041196 | 6.0838e-05
2012-12-07 | ZN12610:PA16 | URBAN | Third Party Impacts | 909235 | 1 | 129.65 | 129.65 | 7.8877e-05 | 6.0838e-05
2012-12-07 | ZN262:PA5 | URBAN | Third Party Impacts | 909236 | 1 | 256 | 256 | 0.00015575 | 6.0838e-05
2012-12-07 | ZN10993:PA12 | URBAN | Equipment Failure | 909240 | 1 | 87.0167 | 87.0167 | 5.2939e-05 | 6.0838e-05
2012-12-07 | ZN9550:PA36 | URBAN | Other | 909245 | 1 | 92.7167 | 92.7167 | 5.6407e-05 | 6.0838e-05
2012-12-03 | 520:48172 | SHORT RURAL | Other | 909251 | 120 | 2 | 240 | 0.00014601 | 0.0073004
2012-12-03 | 813:89061 | LONG RURAL | Other | 909264 | 1 | 60 | 60 | 3.6502e-05 | 6.0837e-05
2012-12-04 | 810:74058 | SHORT RURAL | Equipment Failure | 909333 | 2 | 120 | 240 | 0.00014601 | 0.00012167
2012-12-05 | 503:48076 | URBAN | Other | 909344 | 72 | 95 | 6840 | 0.0041613 | 0.0043803
2012-12-05 | 511:29878 | SHORT RURAL | Third Party Impacts | 909351 | 9 | 50 | 450 | 0.00027377 | 0.00054754
2012-12-07 | 214:8669 | URBAN | Other | 909380 | 1 | 325.95 | 325.95 | 0.0001983 | 6.0838e-05
2012-12-07 | 232:11457 | URBAN | Other | 909415 | 2084 | 13 | 19287 | 0.011734 | 0.12679
2012-12-07 | 509:48039 | LONG RURAL | Other | 909440 | 1 | 257.45 | 257.45 | 0.00015663 | 6.0838e-05
2012-12-07 | 225:33676 | SHORT RURAL | Other | 909509 | 1 | 75.7833 | 75.7833 | 4.6105e-05 | 6.0838e-05
2012-12-07 | 807:74180 | SHORT RURAL | Weather | 909526 | 1 | 143.2333 | 143.2333 | 8.7141e-05 | 6.0838e-05
2012-12-07 | 807:74183 | SHORT RURAL | Other | 909551 | 1 | 85 | 85 | 5.1712e-05 | 6.0838e-05
2012-12-07 | 813:89061 | LONG RURAL | Equipment Failure | 909555 | 2 | 198 | 396 | 0.00024092 | 0.00012168
2012-12-07 | ZN12690:PA19 | URBAN | Other | 909571 | 1 | 116.3833 | 116.3833 | 7.0805e-05 | 6.0838e-05
2012-12-08 | ZN12570:PA33 | SHORT RURAL | Animals | 909574 | 12 | 40 | 480 | 0.00029202 | 0.00073006
2012-12-08 | ZN12690:PA19 | URBAN | Vegetation | 909575 | 30 | 348 | 10440 | 0.0063515 | 0.0018251
2012-12-08 | 232:33411 | SHORT RURAL | Vegetation | 909612 | 1526 | 39 | 59514 | 0.036207 | 0.092839
2012-12-08 | ZN9118:PA3 | SHORT RURAL | Vegetation | 909616 | 1 | 91.7833 | 91.7833 | 5.5839e-05 | 6.0838e-05
2012-12-08 | 524:33572 | SHORT RURAL | Other | 909633 | 1 | 79.5667 | 79.5667 | 4.8407e-05 | 6.0838e-05
2012-12-08 | ZN12690:PA12 | SHORT RURAL | Equipment Failure | 909635 | 34 | 107 | 3638 | 0.0022133 | 0.0020685
2012-12-08 | ZN129:PA5 | URBAN | Equipment Failure | 909660 | 1 | 422.3333 | 422.3333 | 0.00025694 | 6.0838e-05
2012-12-08 | ZN195:PA25 | URBAN | Vegetation | 909666 | 33 | 119.65 | 3948.45 | 0.0024022 | 0.0020077
2012-12-08 | ZN180:PA24 | URBAN | Vegetation | 909677 | 31 | 166.3167 | 5155.8167 | 0.0031367 | 0.001886
2012-12-08 | ZN15002:PA2 | SHORT RURAL | Vegetation | 909681 | 1 | 40 | 40 | 2.4335e-05 | 6.0838e-05
2012-12-08 | ZN15002:PA4 | URBAN | Vegetation | 909681 | 697 | 40 | 27880 | 0.016962 | 0.042404
2012-12-08 | ZN2635:PA10 | URBAN | Equipment Failure | 909686 | 2300 | 54 | 121900 | 0.074162 | 0.13993
2012-12-08 | ZN2635:PA21 | URBAN | Equipment Failure | 909686 | 220 | 54 | 8360 | 0.0050861 | 0.013384
2012-12-08 | ZN2635:PA4 | URBAN | Equipment Failure | 909686 | 1 | 54 | 38 | 2.3119e-05 | 6.0838e-05
2012-12-08 | 501:48122 | SHORT RURAL | Other | 909688 | 108 | 98 | 10584 | 0.0064391 | 0.0065705
2012-12-08 | 232:11454 | SHORT RURAL | Other | 909718 | 1 | 199.1167 | 199.1167 | 0.00012114 | 6.0838e-05
2012-12-09 | ZN195:PA30 | URBAN | Vegetation | 909721 | 741 | 57 | 42237 | 0.025696 | 0.045081
2012-12-09 | ZN874:PA17 | URBAN | Equipment Failure | 909764 | 1 | 172.4833 | 172.4833 | 0.00010494 | 6.0838e-05
2012-12-09 | ZN2602:PA21 | URBAN | Vegetation | 909767 | 86 | 130 | 11180 | 0.0068017 | 0.0052321
2012-12-09 | ZN10991:PA12 | URBAN | Weather | 909769 | 11 | 326 | 3584.5333 | 0.0021808 | 0.00066922
2012-12-09 | ZN10991:PA8 | URBAN | Weather | 909769 | 31 | 326 | 10106 | 0.0061483 | 0.001886
2012-12-09 | ZN9035:PA11 | URBAN | Vegetation | 909772 | 102 | 20.0333 | 2043.4 | 0.0012432 | 0.0062055
2012-12-09 | ZN3154:PA18 | URBAN | Third Party Impacts | 909774 | 119 | 500 | 53858 | 0.032766 | 0.0072397
2012-12-09 | ZN9245:PA14 | URBAN | Vegetation | 909790 | 49 | 280.6333 | 13751.0333 | 0.0083659 | 0.0029811
2012-12-09 | ZN14892:PA19 | URBAN | Weather | 909796 | 92 | 134 | 12328 | 0.0075001 | 0.0055971
2012-12-09 | ZN262:PA34 | URBAN | Third Party Impacts | 909797 | 108 | 156.45 | 16896.6 | 0.01028 | 0.0065705
2012-12-09 | ZN188:PA17 | URBAN | Vegetation | 909798 | 267 | 162 | 43254 | 0.026315 | 0.016244
2012-12-09 | ZN1287:PA3 | URBAN | Vegetation | 909803 | 1 | 698.4333 | 698.4333 | 0.00042491 | 6.0838e-05
2012-12-09 | ZN9118:PA17 | URBAN | Vegetation | 909813 | 39 | 68 | 2652 | 0.0016134 | 0.0023727
2012-12-09 | ZN1788:PA17 | URBAN | Equipment Failure | 909820 | 31 | 84 | 2604 | 0.0015842 | 0.001886
2012-12-09 | ZN1788:PA2 | URBAN | Equipment Failure | 909820 | 95 | 84 | 7980 | 0.0048549 | 0.0057796
2012-12-09 | ZN10999:PA17 | URBAN | Vegetation | 909828 | 167 | 133 | 22211 | 0.013513 | 0.01016
2012-12-09 | ZN35500:PA27 | URBAN | Equipment Failure | 909842 | 3 | 84 | 252 | 0.00015331 | 0.00018251
2012-12-09 | 503:48016 | URBAN | Other | 909845 | 74 | 156.4667 | 10836.8167 | 0.0065929 | 0.004502
2012-12-09 | ZN9700:PA15 | URBAN | Vegetation | 909856 | 1 | 496.4167 | 496.4167 | 0.00030201 | 6.0838e-05
2012-12-09 | ZN2310:PA37 | URBAN | Vegetation | 909857 | 41 | 54.2667 | 2224.9333 | 0.0013536 | 0.0024944
2012-12-09 | 515:35197 | LONG RURAL | Other | 909865 | 10 | 60 | 600 | 0.00036503 | 0.00060838
2012-12-09 | ZN874:PA17 | URBAN | Equipment Failure | 909869 | 15 | 443.4667 | 6652 | 0.004047 | 0.00091257
2012-12-09 | ZN9700:PA20 | URBAN | Weather | 909870 | 1799 | 158 | 213913 | 0.13014 | 0.10945
2012-12-09 | ZN690:PA3 | URBAN | Vegetation | 909873 | 33 | 151.6833 | 5005.55 | 0.0030453 | 0.0020077
2012-12-09 | 502:48010 | SHORT RURAL | Other | 909875 | 1 | 200.5167 | 200.5167 | 0.00012199 | 6.0838e-05
2012-12-09 | ZN35800:PA18 | URBAN | Other | 909879 | 45 | 114.7833 | 5165.25 | 0.0031424 | 0.0027377
2012-12-09 | 222:2018 | URBAN | Other | 909885 | 1 | 98.2667 | 98.2667 | 5.9784e-05 | 6.0838e-05
2012-12-09 | 513:48056 | SHORT RURAL | Equipment Failure | 909889 | 4 | 783.7167 | 3134.8667 | 0.0019072 | 0.00024335
2012-12-09 | 813:89062 | SHORT RURAL | Equipment Failure | 909890 | 392 | 473 | 28242 | 0.017182 | 0.023849
2012-12-09 | ZN14144:PA2 | SHORT RURAL | Vegetation | 909897 | 1003 | 29 | 29087 | 0.017696 | 0.061021
2012-12-09 | 512:48046 | SHORT RURAL | Other | 909903 | 1 | 226.3833 | 226.3833 | 0.00013773 | 6.0838e-05
2012-12-09 | ZN3672:PA13 | URBAN | Equipment Failure | 909908 | 1 | 485.5167 | 485.5167 | 0.00029538 | 6.0838e-05
2012-12-09 | 513:48056 | SHORT RURAL | Other | 909909 | 14 | 416.4833 | 5830.7667 | 0.0035473 | 0.00085173
2012-12-09 | ZN12690:PA12 | SHORT RURAL | Equipment Failure | 909910 | 108 | 185 | 11904 | 0.0072422 | 0.0065705
2012-12-09 | 515:35197 | LONG RURAL | Other | 909920 | 1 | 51 | 51 | 3.1027e-05 | 6.0838e-05
2012-12-09 | 230:81432 | URBAN | Other | 909922 | 1 | 94.3833 | 94.3833 | 5.7421e-05 | 6.0838e-05
2012-12-09 | 514:18137 | SHORT RURAL | Other | 909923 | 1 | 203.5833 | 203.5833 | 0.00012386 | 6.0838e-05
2012-12-09 | ZN384:PA9 | URBAN | Vegetation | 909924 | 133 | 47 | 6251 | 0.003803 | 0.0080915
2012-12-09 | ZN2602:PA18 | URBAN | Vegetation | 909931 | 45 | 116.85 | 5258.25 | 0.003199 | 0.0027377
2012-12-09 | 513:48056 | SHORT RURAL | Other | 909936 | 11 | 335 | 3685 | 0.0022419 | 0.00066922
2012-12-09 | ZN5868:PA30 | URBAN | Vegetation | 909939 | 36 | 47 | 1692 | 0.0010294 | 0.0021902
2012-12-09 | 515:35197 | LONG RURAL | Other | 909942 | 1 | 58.4 | 58.4 | 3.5529e-05 | 6.0838e-05
2012-12-09 | 514:18137 | SHORT RURAL | Other | 909943 | 1 | 173.9833 | 173.9833 | 0.00010585 | 6.0838e-05
2012-12-09 | 515:35197 | LONG RURAL | Equipment Failure | 909945 | 4 | 105 | 420 | 0.00025552 | 0.00024335
2012-12-09 | 206:34434 | URBAN | Vegetation | 909948 | 43 | 59 | 2537 | 0.0015435 | 0.002616
2012-12-09 | 811:74234 | SHORT RURAL | Other | 909950 | 1 | 362 | 362 | 0.00022023 | 6.0838e-05
2012-12-09 | 515:35197 | LONG RURAL | Other | 909953 | 1 | 43.9167 | 43.9167 | 2.6718e-05 | 6.0838e-05
2012-12-09 | 514:18137 | SHORT RURAL | Other | 909954 | 49 | 231 | 11319 | 0.0068863 | 0.0029811
2012-12-09 | 208:58 | URBAN | Other | 909961 | 1 | 144.75 | 144.75 | 8.8063e-05 | 6.0838e-05
2012-12-09 | 515:35198 | SHORT RURAL | Other | 909971 | 1 | 387.8333 | 387.8333 | 0.00023595 | 6.0838e-05
2012-12-09 | ZN398:PA3 | URBAN | Vegetation | 909972 | 106 | 126 | 13291.8667 | 0.0080865 | 0.0064488
2012-12-09 | ZN10995:PA7 | URBAN | Vegetation | 909973 | 1 | 753.8 | 753.8 | 0.0004586 | 6.0838e-05
2012-12-09 | 513:48056 | SHORT RURAL | Other | 909975 | 1 | 359.15 | 359.15 | 0.0002185 | 6.0838e-05
2012-12-09 | 223:14393 | URBAN | Other | 909979 | 1 | 86.15 | 86.15 | 5.2412e-05 | 6.0838e-05
2012-12-09 | ZN9118:PA11 | URBAN | Vegetation | 909985 | 24 | 163.9333 | 3934.4 | 0.0023936 | 0.0014601
2012-12-09 | ZN1290:PA12 | URBAN | Other | 909995 | 1050 | 106 | 77334 | 0.047049 | 0.06388
2012-12-09 | 232:33411 | SHORT RURAL | Other | 909998 | 1 | 107.5333 | 107.5333 | 6.5421e-05 | 6.0838e-05
2012-12-09 | 507:80932 | SHORT RURAL | Other | 910006 | 1 | 79.65 | 79.65 | 4.8458e-05 | 6.0838e-05
2012-12-09 | 807:74179 | SHORT RURAL | Equipment Failure | 910007 | 4 | 173 | 692 | 0.000421 | 0.00024335
2012-12-09 | 813:89055 | SHORT RURAL | Equipment Failure | 910009 | 1 | 185 | 185 | 0.00011255 | 6.0838e-05
2012-12-09 | 813:89055 | SHORT RURAL | Other | 910012 | 1 | 257.1667 | 257.1667 | 0.00015646 | 6.0838e-05
2012-12-09 | ZN15012:PA8 | URBAN | Other | 910024 | 1 | 161.4 | 161.4 | 9.8193e-05 | 6.0838e-05
2012-12-09 | 811:74234 | SHORT RURAL | Other | 910031 | 1 | 267.4167 | 267.4167 | 0.00016269 | 6.0838e-05
2012-12-09 | ZN398:PA3 | URBAN | Other | 910045 | 104 | 101.8667 | 10594.1333 | 0.0064453 | 0.0063272
2012-12-09 | ZN9245:PA8 | SHORT RURAL | Vegetation | 910046 | 1 | 229.9167 | 229.9167 | 0.00013988 | 6.0838e-05
2012-12-09 | ZN15008:PA7 | URBAN | Equipment Failure | 910047 | 1 | 863.6667 | 863.6667 | 0.00052544 | 6.0838e-05
2012-12-09 | 223:14394 | URBAN | Other | 910050 | 1 | 156.5167 | 156.5167 | 9.5222e-05 | 6.0838e-05
2012-12-09 | 223:14394 | URBAN | Other | 910071 | 1 | 112.4833 | 112.4833 | 6.8433e-05 | 6.0838e-05
2012-12-09 | 202:34250 | URBAN | Equipment Failure | 910073 | 1 | 84.0833 | 72.9167 | 4.4361e-05 | 6.0838e-05
2012-12-09 | 202:34254 | URBAN | Equipment Failure | 910073 | 879 | 84.0833 | 14682 | 0.0089323 | 0.053477
2012-12-09 | 202:34260 | URBAN | Equipment Failure | 910073 | 1 | 84.0833 | 54.2667 | 3.3015e-05 | 6.0838e-05
2012-12-09 | ZN2568:PA29 | URBAN | Equipment Failure | 910078 | 58 | 195 | 11310 | 0.0068808 | 0.0035286
2012-12-09 | ZN1290:PA12 | URBAN | Equipment Failure | 910090 | 1 | 22.0667 | 22.0667 | 1.3425e-05 | 6.0838e-05
2012-12-09 | 813:89061 | LONG RURAL | Other | 910093 | 1 | 153 | 153 | 9.3082e-05 | 6.0838e-05
2012-12-09 | 513:48056 | SHORT RURAL | Other | 910096 | 2 | 133.6833 | 227.8 | 0.00013859 | 0.00012168
2012-12-09 | 256:80635 | URBAN | Other | 910112 | 1 | 93.65 | 93.65 | 5.6975e-05 | 6.0838e-05
2012-12-10 | ZN12620:PA11 | SHORT RURAL | Equipment Failure | 910113 | 1631 | 205 | 23562 | 0.014335 | 0.099227
2012-12-09 | ZN10991:PA12 | URBAN | Weather | 910114 | 2 | 137 | 273.3 | 0.00016627 | 0.00012168
2012-12-09 | ZN10991:PA8 | URBAN | Weather | 910114 | 31 | 137 | 4247 | 0.0025838 | 0.001886
2012-12-10 | ZN188:PA17 | URBAN | Equipment Failure | 910120 | 267 | 54 | 14418 | 0.0087716 | 0.016244
2012-12-10 | 228:7490 | SHORT RURAL | Other | 910123 | 1 | 259.85 | 259.85 | 0.00015809 | 6.0838e-05
2012-12-10 | 224:80337 | URBAN | Equipment Failure | 910125 | 1 | 982.6167 | 982.6167 | 0.00059781 | 6.0838e-05
2012-12-10 | ZN847:PA15 | URBAN | Vegetation | 910130 | 1238 | 73 | 90374 | 0.054982 | 0.075318
2012-12-10 | ZN8000:PA25 | URBAN | Equipment Failure | 910132 | 1 | 890.3833 | 890.3833 | 0.00054169 | 6.0838e-05
2012-12-10 | ZN15004:PA3 | URBAN | Other | 910135 | 1 | 547.3333 | 547.3333 | 0.00033299 | 6.0838e-05
2012-12-10 | 228:7491 | URBAN | Vegetation | 910137 | 1 | 469.5 | 469.5 | 0.00028564 | 6.0838e-05
2012-12-10 | ZN180:PA34 | URBAN | Other | 910138 | 1 | 414.05 | 414.05 | 0.0002519 | 6.0838e-05
2012-12-10 | ZN9700:PA21 | URBAN | Vegetation | 910146 | 1 | 297.4 | 297.4 | 0.00018093 | 6.0838e-05
2012-12-10 | 232:11457 | URBAN | Equipment Failure | 910152 | 2247 | 320 | 125399 | 0.07629 | 0.1367
2012-12-10 | ZN72:PA10 | URBAN | Other | 910154 | 1 | 299.15 | 299.15 | 0.000182 | 6.0838e-05
2012-12-10 | 507:80917 | URBAN | Other | 910160 | 1 | 103.8333 | 103.8333 | 6.317e-05 | 6.0838e-05
2012-12-10 | ZN398:PA4 | URBAN | Other | 910164 | 1 | 406.55 | 406.55 | 0.00024734 | 6.0838e-05
2012-12-10 | 813:89062 | SHORT RURAL | Weather | 910166 | 1 | 326.7333 | 326.7333 | 0.00019878 | 6.0838e-05
2012-12-10 | ZN1164:PA26 | URBAN | Equipment Failure | 910167 | 1 | 244.75 | 244.75 | 0.0001489 | 6.0838e-05
2012-12-10 | ZN1610:PA20 | SHORT RURAL | Equipment Failure | 910172 | 40 | 74 | 2375 | 0.0014449 | 0.0024335
2012-12-10 | ZN1610:PA26 | URBAN | Equipment Failure | 910172 | 3 | 74 | 177 | 0.00010768 | 0.00018251
2012-12-10 | ZN10994:PA18 | SHORT RURAL | Other | 910173 | 1 | 391.15 | 391.15 | 0.00023797 | 6.0838e-05
2012-12-10 | 813:89062 | SHORT RURAL | Other | 910177 | 1 | 225.9 | 225.9 | 0.00013743 | 6.0838e-05
2012-12-10 | ZN15008:PA7 | URBAN | Other | 910185 | 1 | 332.2333 | 332.2333 | 0.00020212 | 6.0838e-05
2012-12-10 | ZN15014:PA16 | URBAN | Other | 910186 | 1 | 659.9333 | 659.9333 | 0.00040149 | 6.0838e-05
2012-12-10 | ZN262:PA30 | URBAN | Other | 910195 | 42 | 134.7 | 5657.4 | 0.0034419 | 0.0025552
2012-12-10 | ZN965:PA15 | URBAN | Equipment Failure | 910202 | 1 | 76.3 | 76.3 | 4.642e-05 | 6.0838e-05
2012-12-10 | ZN15010:PA9 | SHORT RURAL | Equipment Failure | 910215 | 1 | 321.5167 | 321.5167 | 0.0001956 | 6.0838e-05
2012-12-10 | ZN12660:PA5 | SHORT RURAL | Equipment Failure | 910216 | 16 | 131 | 2096 | 0.0012752 | 0.00097341
2012-12-10 | ZN129:PA18 | URBAN | Equipment Failure | 910219 | 1 | 110.1667 | 110.1667 | 6.7023e-05 | 6.0838e-05
2012-12-10 | 224:80337 | URBAN | Equipment Failure | 910230 | 1 | 527.3167 | 527.3167 | 0.00032081 | 6.0838e-05
2012-12-10 | 514:18137 | SHORT RURAL | Equipment Failure | 910242 | 8 | 296 | 2368 | 0.0014406 | 0.00048671
2012-12-09 | ZN901:PA14 | URBAN | Third Party Impacts | 910245 | 9 | 125 | 1125 | 0.00068443 | 0.00054754
2012-12-10 | 214:8669 | URBAN | Other | 910265 | 1 | 294.5 | 294.5 | 0.00017917 | 6.0838e-05
2012-12-10 | ZN2635:PA17 | URBAN | Equipment Failure | 910272 | 1 | 176.9 | 176.9 | 0.00010762 | 6.0838e-05
2012-12-09 | 222:2018 | URBAN | Other | 910277 | 113 | 157 | 17741 | 0.010793 | 0.0068747
2012-12-10 | 264:81240 | SHORT RURAL | Equipment Failure | 910290 | 3 | 455 | 1365 | 0.00083044 | 0.00018251
2012-12-10 | 813:89063 | SHORT RURAL | Other | 910325 | 1 | 190.45 | 190.45 | 0.00011587 | 6.0838e-05
2012-12-10 | 221:11900 | URBAN | Other | 910354 | 1 | 195.1333 | 195.1333 | 0.00011872 | 6.0838e-05
2012-12-10 | ZN847:PA15 | URBAN | Vegetation | 910355 | 1241 | 236 | 108656 | 0.066104 | 0.0755
2012-12-07 | 235:2120 | SHORT RURAL | Equipment Failure | 910369 | 4 | 115 | 460 | 0.00027986 | 0.00024335
2012-12-09 | ZN2310:PA40 | URBAN | Other | 910376 | 32 | 142 | 4544 | 0.0027645 | 0.0019468
2012-12-10 | 516:48067 | SHORT RURAL | Other | 910417 | 1 | 47.95 | 47.95 | 2.9172e-05 | 6.0838e-05
2012-12-10 | 224:80337 | URBAN | Equipment Failure | 910418 | 1 | 358.4333 | 358.4333 | 0.00021806 | 6.0838e-05
2012-12-09 | 513:48056 | SHORT RURAL | Other | 910426 | 82 | 2 | 164 | 9.9775e-05 | 0.0049887
2012-12-10 | 210:8681 | URBAN | Vegetation | 910445 | 1 | 84.25 | 84.25 | 5.1256e-05 | 6.0838e-05
2012-12-10 | ZN7900:PA2 | URBAN | Equipment Failure | 910496 | 1 | 927.4667 | 927.4667 | 0.00056425 | 6.0838e-05
2012-12-10 | ZN12620:PA1 | SHORT RURAL | Other | 910572 | 1 | 109.6667 | 109.6667 | 6.6719e-05 | 6.0838e-05
2012-12-10 | ZN9118:PA22 | URBAN | Equipment Failure | 910599 | 105 | 72 | 7473.3333 | 0.0045466 | 0.006388
2012-12-10 | 504:48026 | SHORT RURAL | Other | 910614 | 1 | 88.2167 | 88.2167 | 5.3669e-05 | 6.0838e-05
2012-12-10 | 509:48040 | SHORT RURAL | Equipment Failure | 910623 | 2 | 125 | 250 | 0.0001521 | 0.00012168
2012-12-10 | 205:12203 | URBAN | Other | 910637 | 1 | 301.5167 | 301.5167 | 0.00018344 | 6.0838e-05
2012-12-10 | 813:89061 | LONG RURAL | Equipment Failure | 910670 | 1 | 263 | 263 | 0.00016 | 6.0838e-05
2012-12-10 | 214:8670 | URBAN | Other | 910672 | 1 | 85.9833 | 85.9833 | 5.2311e-05 | 6.0838e-05
2012-12-10 | 222:2015 | SHORT RURAL | Equipment Failure | 910685 | 781 | 369 | 153663 | 0.093486 | 0.047515
2012-12-10 | 231:8415 | SHORT RURAL | Other | 910686 | 1 | 116.8833 | 116.8833 | 7.111e-05 | 6.0838e-05
2012-12-11 | 238:34141 | SHORT RURAL | Equipment Failure | 910702 | 1 | 215 | 215 | 0.0001308 | 6.0835e-05
2012-12-10 | ZN14892:PA13 | URBAN | Vegetation | 910715 | 1 | 308.2333 | 308.2333 | 0.00018752 | 6.0838e-05
2012-12-10 | ZN12590:PA7 | SHORT RURAL | Other | 910722 | 1 | 278.0833 | 278.0833 | 0.00016918 | 6.0838e-05
2012-12-10 | ZN14892:PA13 | URBAN | Other | 910725 | 1 | 59.7833 | 59.7833 | 3.6371e-05 | 6.0838e-05
2012-12-10 | ZN36300:PA1 | URBAN | Other | 910744 | 1 | 61.7833 | 61.7833 | 3.7588e-05 | 6.0838e-05
2012-12-10 | ZN2602:PA36 | URBAN | Other | 910745 | 1 | 636.8833 | 636.8833 | 0.00038747 | 6.0838e-05
2012-12-10 | ZN36300:PA1 | URBAN | Other | 910749 | 1 | 242.2667 | 242.2667 | 0.00014739 | 6.0838e-05
2012-12-10 | ZN14892:PA19 | URBAN | Other | 910750 | 1 | 749.4833 | 749.4833 | 0.00045597 | 6.0838e-05
2012-12-10 | ZN3922:PA14 | URBAN | Other | 910751 | 1 | 768.2 | 768.2 | 0.00046736 | 6.0838e-05
2012-12-11 | 232:11457 | URBAN | Other | 910759 | 1 | 244.5667 | 244.5667 | 0.00014878 | 6.0835e-05
2012-12-11 | 205:12213 | URBAN | Other | 910761 | 1 | 9.5833 | 9.5833 | 5.83e-06 | 6.0835e-05
2012-12-11 | 206:34440 | URBAN | Other | 910793 | 1 | 571.4667 | 571.4667 | 0.00034765 | 6.0835e-05
2012-12-10 | 813:89062 | SHORT RURAL | Equipment Failure | 910802 | 4 | 465 | 1860 | 0.0011316 | 0.00024335
2012-12-11 | 509:48039 | LONG RURAL | Equipment Failure | 910806 | 4 | 392 | 1568 | 0.00095389 | 0.00024334
2012-12-11 | 243:80083 | SHORT RURAL | Equipment Failure | 910840 | 6 | 340 | 2040 | 0.001241 | 0.00036501
2012-12-11 | ZN3922:PA10 | URBAN | Other | 910846 | 1 | 232.3333 | 232.3333 | 0.00014134 | 6.0835e-05
2012-12-10 | ZN1610:PA17 | URBAN | Other | 910865 | 325 | 2 | 650 | 0.00039545 | 0.019772
2012-11-26 | 512:48049 | SHORT RURAL | Other | 910901 | 1 | 310 | 310 | 0.00018859 | 6.0835e-05
2012-12-11 | ZN14891:PA6 | URBAN | Equipment Failure | 910907 | 364 | 478 | 15778 | 0.0095986 | 0.022144
2012-11-26 | 512:48048 | SHORT RURAL | Other | 910998 | 42 | 224 | 9408 | 0.0057234 | 0.0025551
2012-12-11 | 513:48059 | SHORT RURAL | Other | 911020 | 2 | 62 | 124 | 7.5435e-05 | 0.00012167
2012-11-30 | 524:33572 | SHORT RURAL | Other | 911032 | 24 | 449 | 10776 | 0.0065557 | 0.0014601
2012-12-01 | 503:48011 | SHORT RURAL | Equipment Failure | 911059 | 25 | 1025 | 17505 | 0.010649 | 0.0015209
2012-12-11 | 221:11900 | URBAN | Other | 911193 | 1 | 110.1333 | 110.1333 | 6.7e-05 | 6.0835e-05
2012-12-11 | ZN15006:PA13 | URBAN | Equipment Failure | 911207 | 40 | 114 | 4560 | 0.0027741 | 0.0024334
2012-12-12 | 214:8667 | URBAN | Equipment Failure | 911220 | 68 | 130 | 8840 | 0.0053778 | 0.0041368
2012-12-11 | ZN12640:PA10 | URBAN | Third Party Impacts | 911223 | 1 | 294.6667 | 294.6667 | 0.00017926 | 6.0835e-05
2012-12-11 | ZN167:PA12 | URBAN | Third Party Impacts | 911227 | 1 | 210 | 210 | 0.00012775 | 6.0835e-05
2012-12-11 | ZN15014:PA7 | URBAN | Other | 911237 | 1 | 144.2667 | 144.2667 | 8.7765e-05 | 6.0835e-05
2012-12-11 | ZN195:PA9 | URBAN | Vegetation | 911242 | 39 | 210 | 8190 | 0.0049824 | 0.0023726
2012-12-11 | ZN630:PA38 | URBAN | Other | 911253 | 1 | 588.65 | 588.65 | 0.00035811 | 6.0835e-05
2012-12-11 | ZN12600:PA3 | URBAN | Animals | 911258 | 1446 | 57 | 64807 | 0.039425 | 0.087967
2012-12-11 | ZN12650:PA1 | SHORT RURAL | Animals | 911258 | 2 | 57 | 88 | 5.3535e-05 | 0.00012167
2012-12-12 | ZN1164:PA20 | URBAN | Other | 911261 | 99 | 129.9833 | 12868.35 | 0.0078285 | 0.0060227
2012-12-12 | ZN2835:PA15 | URBAN | Other | 911269 | 1 | 448.6833 | 448.6833 | 0.00027296 | 6.0835e-05
2012-12-12 | ZN35370:PA4 | URBAN | Vegetation | 911271 | 164 | 90 | 12870 | 0.0078295 | 0.009977
2012-12-12 | ZN262:PA19 | URBAN | Equipment Failure | 911284 | 1 | 228.8 | 228.8 | 0.00013919 | 6.0835e-05
2012-12-12 | ZN3922:PA18 | URBAN | Other | 911290 | 1 | 311.4833 | 311.4833 | 0.00018949 | 6.0835e-05
2012-12-12 | ZN3922:PA14 | URBAN | Other | 911291 | 1 | 186.3 | 186.3 | 0.00011334 | 6.0835e-05
2012-12-12 | ZN3672:PA44 | URBAN | Other | 911293 | 1 | 236.85 | 236.85 | 0.00014409 | 6.0835e-05
2012-12-12 | ZN3922:PA18 | URBAN | Other | 911297 | 1 | 283.8333 | 283.8333 | 0.00017267 | 6.0835e-05
2012-12-12 | ZN9118:PA7 | URBAN | Equipment Failure | 911308 | 909 | 100 | 62984 | 0.038316 | 0.055299
2012-12-12 | 202:34261 | SHORT RURAL | Other | 911313 | 42 | 75 | 3150 | 0.0019163 | 0.0025551
2012-12-12 | ZN4545:PA24 | URBAN | Equipment Failure | 911323 | 1 | 54.9333 | 54.9333 | 3.3419e-05 | 6.0835e-05
2012-12-12 | ZN2602:PA41 | URBAN | Other | 911353 | 1 | 2994.8833 | 2994.8833 | 0.0018219 | 6.0835e-05
2012-12-12 | ZN9118:PA26 | URBAN | Equipment Failure | 911393 | 28 | 323 | 9041.6667 | 0.0055005 | 0.0017034
2012-12-12 | ZN9118:PA8 | URBAN | Equipment Failure | 911393 | 1 | 323 | 323 | 0.0001965 | 6.0835e-05
2012-12-12 | ZN4545:PA24 | URBAN | Other | 911434 | 1 | 226.9333 | 226.9333 | 0.00013806 | 6.0835e-05
2012-12-12 | ZN12650:PA9 | URBAN | Other | 911478 | 1 | 141.6333 | 141.6333 | 8.6163e-05 | 6.0835e-05
2012-12-12 | ZN12650:PA9 | URBAN | Third Party Impacts | 911482 | 1 | 94.9333 | 94.9333 | 5.7753e-05 | 6.0835e-05
2012-12-12 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 911582 | 56 | 98 | 5488 | 0.0033386 | 0.0034068
2012-12-12 | ZN965:PA15 | URBAN | Vegetation | 911600 | 7 | 46 | 322 | 0.00019589 | 0.00042585
2012-12-12 | ZN965:PA33 | URBAN | Vegetation | 911600 | 1272 | 46 | 58512 | 0.035596 | 0.077382
2012-12-12 | ZN965:PA8 | URBAN | Vegetation | 911600 | 51 | 46 | 2346 | 0.0014272 | 0.0031026
2012-12-12 | 803:74016 | SHORT RURAL | Equipment Failure | 911607 | 1 | 50 | 50 | 3.0418e-05 | 6.0835e-05
2012-12-12 | 514:18146 | SHORT RURAL | Equipment Failure | 911646 | 4 | 125 | 500 | 0.00030418 | 0.00024334
2012-12-12 | ZN965:PA33 | URBAN | Other | 911670 | 8 | 45 | 360 | 0.00021901 | 0.00048668
2012-12-12 | ZN14143:PA17 | SHORT RURAL | Other | 911701 | 1 | 846.9667 | 846.9667 | 0.00051525 | 6.0835e-05
2012-12-12 | ZN5868:PA5 | URBAN | Other | 911707 | 1 | 32.9333 | 32.9333 | 2.0035e-05 | 6.0835e-05
2012-12-12 | ZN35500:PA24 | URBAN | Equipment Failure | 911710 | 136 | 29.5167 | 4014.2667 | 0.0024421 | 0.0082736
2012-12-20 | ZN1193:PA6 | URBAN | Vegetation | 911714 | 26 | 59 | 1534 | 0.00093324 | 0.0015818
2012-12-12 | ZN965:PA21 | URBAN | Vegetation | 911718 | 47 | 180 | 8460 | 0.0051466 | 0.0028592
2012-12-13 | 801:74117 | SHORT RURAL | Other | 911758 | 1 | 298.1667 | 298.1667 | 0.00018139 | 6.0836e-05
2012-12-13 | ZN3425:PA15 | URBAN | Equipment Failure | 911764 | 59 | 141.2667 | 8334.7333 | 0.0050705 | 0.0035893
2012-12-09 | ZN1290:PA12 | URBAN | Other | 911768 | 40 | 113 | 4520 | 0.0027499 | 0.0024335
2012-12-13 | ZN2568:PA14 | URBAN | Third Party Impacts | 911785 | 88 | 110 | 9680 | 0.0058889 | 0.0053535
2012-12-13 | ZN2568:PA29 | URBAN | Third Party Impacts | 911785 | 1799 | 110 | 188407 | 0.11462 | 0.10944
2012-12-13 | ZN2568:PA32 | URBAN | Third Party Impacts | 911785 | 1 | 110 | 101 | 6.1444e-05 | 6.0836e-05
2012-12-13 | ZN15009:PA7 | URBAN | Equipment Failure | 911793 | 1 | 72.4167 | 72.4167 | 4.4055e-05 | 6.0836e-05
2012-12-13 | 202:34261 | SHORT RURAL | Other | 911827 | 2 | 75.8667 | 151.7333 | 9.2308e-05 | 0.00012167
2012-12-09 | ZN195:PA9 | URBAN | Equipment Failure | 911830 | 1246 | 127 | 158242 | 0.096272 | 0.075804
2012-12-13 | 813:89061 | LONG RURAL | Other | 911859 | 1 | 72 | 72 | 4.3802e-05 | 6.0836e-05
2012-12-13 | ZN12660:PA5 | SHORT RURAL | Third Party Impacts | 911945 | 1 | 71.2833 | 71.2833 | 4.3366e-05 | 6.0836e-05
2012-12-13 | 243:80075 | SHORT RURAL | Other | 911959 | 1 | 81 | 81 | 4.9277e-05 | 6.0836e-05
2012-12-13 | 523:33503 | URBAN | Other | 911979 | 1 | 46.5833 | 46.5833 | 2.8339e-05 | 6.0836e-05
2012-12-13 | ZN398:PA11 | URBAN | Equipment Failure | 911980 | 965 | 79 | 76235 | 0.046378 | 0.058706
2012-12-13 | ZN398:PA22 | URBAN | Equipment Failure | 911980 | 1 | 79 | 79 | 4.806e-05 | 6.0836e-05
2012-12-13 | ZN398:PA31 | URBAN | Equipment Failure | 911980 | 22 | 79 | 1738 | 0.0010573 | 0.0013384
2012-12-13 | ZN12640:PA10 | URBAN | Other | 912023 | 1 | 140.0167 | 140.0167 | 8.518e-05 | 6.0836e-05
2012-12-13 | ZN180:PA24 | URBAN | Other | 912038 | 54 | 16.15 | 872.1 | 0.00053055 | 0.0032851
2012-12-13 | 231:8415 | SHORT RURAL | Other | 912045 | 1 | 158.9333 | 158.9333 | 9.6688e-05 | 6.0836e-05
2012-12-13 | ZN3472:PA20 | URBAN | Other | 912061 | 1 | 149.0167 | 149.0167 | 9.0655e-05 | 6.0836e-05
2012-12-13 | 515:35192 | SHORT RURAL | Other | 912065 | 1 | 234.4 | 234.4 | 0.0001426 | 6.0836e-05
2012-12-13 | ZN15006:PA15 | URBAN | Other | 912128 | 1 | 198.8333 | 198.8333 | 0.00012096 | 6.0836e-05
2012-12-13 | ZN3472:PA11 | URBAN | Other | 912132 | 1 | 886.6667 | 886.6667 | 0.00053941 | 6.0836e-05
2012-12-14 | ZN36300:PA3 | URBAN | Other | 912142 | 1 | 416.3 | 416.3 | 0.00025326 | 6.0836e-05
2012-12-14 | 229:34983 | SHORT RURAL | Animals | 912144 | 47 | 140.8 | 6617.6 | 0.0040259 | 0.0028593
2012-12-14 | 801:74117 | SHORT RURAL | Other | 912149 | 1 | 369.2667 | 369.2667 | 0.00022465 | 6.0836e-05
2012-12-14 | ZN12690:PA16 | SHORT RURAL | Equipment Failure | 912163 | 75 | 249 | 18675 | 0.011361 | 0.0045627
2012-12-13 | 511:29877 | SHORT RURAL | Other | 912182 | 1 | 45 | 45 | 2.7376e-05 | 6.0836e-05
2012-12-14 | ZN9252:PA4 | URBAN | Third Party Impacts | 912264 | 74 | 123.7667 | 9158.7333 | 0.0055718 | 0.0045019
2012-12-14 | ZN690:PA17 | URBAN | Other | 912280 | 1 | 185.9667 | 185.9667 | 0.00011313 | 6.0836e-05
2012-12-14 | ZN12570:PA21 | SHORT RURAL | Equipment Failure | 912359 | 1 | 372.5667 | 372.5667 | 0.00022665 | 6.0836e-05
2012-12-14 | ZN9700:PA17 | URBAN | Other | 912424 | 39 | 54 | 2106 | 0.0012812 | 0.0023726
2012-12-14 | 507:80923 | SHORT RURAL | Equipment Failure | 912433 | 1 | 65.8333 | 65.8333 | 4.005e-05 | 6.0836e-05
2012-12-14 | ZN12570:PA33 | SHORT RURAL | Equipment Failure | 912440 | 110 | 75 | 8250 | 0.005019 | 0.006692
2012-12-14 | 206:34434 | URBAN | Equipment Failure | 912450 | 14 | 155 | 2170 | 0.0013201 | 0.0008517
2012-12-14 | ZN1193:PA28 | URBAN | Vegetation | 912467 | 247 | 40 | 9880 | 0.0060106 | 0.015027
2012-12-14 | ZN80:PA31 | URBAN | Vegetation | 912467 | 788 | 40 | 31520 | 0.019176 | 0.047939
2012-12-14 | 260:33347 | SHORT RURAL | Other | 912480 | 1 | 110.7333 | 110.7333 | 6.7366e-05 | 6.0836e-05
2012-12-14 | ZN1068:PA26 | URBAN | Equipment Failure | 912495 | 1 | 332.35 | 332.35 | 0.00020219 | 6.0836e-05
2012-12-14 | ZN180:PA18 | URBAN | Vegetation | 912509 | 24 | 40 | 960 | 0.00058403 | 0.0014601
2012-12-14 | 507:80922 | SHORT RURAL | Other | 912513 | 4 | 77 | 308 | 0.00018738 | 0.00024334
2012-12-14 | ZN10996:PA11 | URBAN | Other | 912531 | 1 | 781.0667 | 781.0667 | 0.00047517 | 6.0836e-05
2012-12-15 | 264:81236 | URBAN | Equipment Failure | 912536 | 1 | 320.15 | 320.15 | 0.00019477 | 6.0836e-05
2012-12-15 | ZN1287:PA23 | URBAN | Animals | 912538 | 882 | 84 | 72540 | 0.04413 | 0.053657
2012-12-15 | 504:48033 | SHORT RURAL | Animals | 912540 | 2 | 92 | 184 | 0.00011194 | 0.00012167
2012-12-15 | 232:33413 | SHORT RURAL | Other | 912541 | 181 | 16 | 2896 | 0.0017618 | 0.011011
2012-12-15 | 810:74054 | LONG RURAL | Weather | 912574 | 6 | 135 | 810 | 0.00049277 | 0.00036502
2012-12-15 | 224:80341 | URBAN | Other | 912576 | 1 | 73.85 | 73.85 | 4.4927e-05 | 6.0836e-05
2012-12-15 | 243:80084 | SHORT RURAL | Other | 912581 | 1 | 113.55 | 113.55 | 6.9079e-05 | 6.0836e-05
2012-12-15 | 235:2120 | SHORT RURAL | Other | 912587 | 1 | 101.3333 | 101.3333 | 6.1647e-05 | 6.0836e-05
2012-12-15 | ZN5868:PA2 | URBAN | Equipment Failure | 912594 | 1 | 253.7 | 253.7 | 0.00015434 | 6.0836e-05
2012-12-15 | 232:33413 | SHORT RURAL | Other | 912605 | 1 | 193.6833 | 193.6833 | 0.00011783 | 6.0836e-05
2012-12-15 | ZN12610:PA22 | URBAN | Other | 912614 | 1 | 259.6 | 259.6 | 0.00015793 | 6.0836e-05
2012-12-15 | 803:74007 | SHORT RURAL | Other | 912641 | 1 | 174.1333 | 174.1333 | 0.00010594 | 6.0836e-05
2012-12-15 | ZN12650:PA8 | URBAN | Equipment Failure | 912659 | 180 | 61 | 10980 | 0.0066798 | 0.01095
2012-12-16 | ZN10995:PA8 | URBAN | Equipment Failure | 912665 | 1 | 387.7833 | 387.7833 | 0.00023591 | 6.0836e-05
2012-12-16 | 526:34636 | SHORT RURAL | Equipment Failure | 912687 | 154 | 302 | 40806 | 0.024825 | 0.0093688
2012-12-16 | ZN3672:PA44 | URBAN | Equipment Failure | 912698 | 32 | 42.6333 | 1364.2667 | 0.00082997 | 0.0019468
2012-12-16 | 258:80784 | URBAN | Other | 912706 | 1 | 49.9 | 49.9 | 3.0357e-05 | 6.0836e-05
2012-12-16 | ZN3472:PA34 | URBAN | Equipment Failure | 912721 | 1 | 185.7 | 185.7 | 0.00011297 | 6.0836e-05
2012-12-16 | 513:48059 | SHORT RURAL | Equipment Failure | 912728 | 47 | 214.2333 | 10068.9667 | 0.0061256 | 0.0028593
2012-12-16 | 232:33411 | SHORT RURAL | Equipment Failure | 912742 | 1 | 77 | 77 | 4.6844e-05 | 6.0836e-05
2012-12-16 | 801:74121 | SHORT RURAL | Other | 912743 | 9 | 36.1833 | 325.65 | 0.00019811 | 0.00054752
2012-12-16 | ZN2602:PA27 | URBAN | Equipment Failure | 912751 | 1 | 275.8667 | 275.8667 | 0.00016783 | 6.0836e-05
2012-12-16 | 504:48026 | SHORT RURAL | Other | 912759 | 111 | 59.3833 | 6591.55 | 0.00401 | 0.0067528
2012-12-16 | 501:48123 | SHORT RURAL | Vegetation | 912770 | 1 | 78.8167 | 78.8167 | 4.7949e-05 | 6.0836e-05
2012-12-16 | 514:18137 | SHORT RURAL | Other | 912774 | 2 | 80 | 160 | 9.7338e-05 | 0.00012167
2012-12-16 | ZN9252:PA12 | URBAN | Vegetation | 912781 | 45 | 366 | 16470 | 0.01002 | 0.0027376
2012-12-16 | ZN3922:PA29 | URBAN | Vegetation | 912791 | 69 | 133 | 9177 | 0.0055829 | 0.0041977
2012-12-16 | ZN1164:PA12 | URBAN | Other | 912796 | 1 | 414.4333 | 414.4333 | 0.00025212 | 6.0836e-05
2012-12-16 | ZN9252:PA4 | URBAN | Other | 912797 | 1 | 458.9833 | 458.9833 | 0.00027923 | 6.0836e-05
2012-12-16 | ZN262:PA30 | URBAN | Vegetation | 912798 | 42 | 88 | 3696 | 0.0022485 | 0.0025551
2012-12-16 | ZN262:PA25 | URBAN | Other | 912804 | 1 | 339.8333 | 339.8333 | 0.00020674 | 6.0836e-05
2012-12-17 | ZN7900:PA7 | URBAN | Equipment Failure | 912807 | 1 | 360.1333 | 360.1333 | 0.00021909 | 6.0836e-05
2012-12-17 | ZN12650:PA17 | URBAN | Animals | 912812 | 92 | 65 | 5980 | 0.003638 | 0.0055969
2012-12-17 | ZN3472:PA34 | URBAN | Equipment Failure | 912820 | 15 | 191 | 2865 | 0.001743 | 0.00091254
2012-12-17 | 526:34636 | SHORT RURAL | Animals | 912823 | 1 | 237.0167 | 237.0167 | 0.00014419 | 6.0836e-05
2012-12-17 | ZN180:PA21 | URBAN | Equipment Failure | 912831 | 66 | 159.3833 | 10519.3 | 0.0063995 | 0.0040152
2012-12-17 | ZN12570:PA24 | SHORT RURAL | Equipment Failure | 912867 | 1 | 146.9 | 146.9 | 8.9368e-05 | 6.0836e-05
2012-12-17 | 206:34434 | URBAN | Other | 912872 | 1 | 62.65 | 62.65 | 3.8114e-05 | 6.0836e-05
2012-12-17 | ZN1287:PA22 | URBAN | Equipment Failure | 912888 | 1 | 170.7667 | 170.7667 | 0.00010389 | 6.0836e-05
2012-12-17 | ZN9900:PA13 | URBAN | Equipment Failure | 912902 | 1 | 492.7 | 492.7 | 0.00029974 | 6.0836e-05
2012-12-17 | ZN2310:PA20 | URBAN | Equipment Failure | 912912 | 1 | 259.6833 | 259.6833 | 0.00015798 | 6.0836e-05
2012-12-17 | ZN9118:PA20 | URBAN | Third Party Impacts | 912925 | 130 | 77 | 10010 | 0.0060897 | 0.0079087
2012-12-17 | ZN12650:PA12 | URBAN | Equipment Failure | 912944 | 1 | 585.2667 | 585.2667 | 0.00035605 | 6.0836e-05
2012-12-17 | ZN180:PA29 | URBAN | Equipment Failure | 912948 | 1 | 14.2167 | 14.2167 | 8.6489e-06 | 6.0836e-05
2012-12-17 | ZN12610:PA24 | SHORT RURAL | Other | 912957 | 1 | 246.3333 | 246.3333 | 0.00014986 | 6.0836e-05
2012-12-17 | ZN3472:PA34 | URBAN | Equipment Failure | 913009 | 15 | 119 | 1785 | 0.0010859 | 0.00091254
2012-12-17 | ZN901:PA31 | URBAN | Equipment Failure | 913055 | 880 | 55 | 48400 | 0.029445 | 0.053536
2012-12-14 | 516:48065 | SHORT RURAL | Equipment Failure | 913065 | 1 | 65 | 65 | 3.9543e-05 | 6.0836e-05
2012-12-17 | ZN15005:PA12 | URBAN | Equipment Failure | 913076 | 1 | 184.9167 | 184.9167 | 0.0001125 | 6.0836e-05
2012-12-17 | ZN3472:PA34 | URBAN | Equipment Failure | 913131 | 15 | 115 | 1725 | 0.0010494 | 0.00091254
2012-12-17 | ZN15005:PA12 | URBAN | Third Party Impacts | 913138 | 40 | 92.2833 | 3691.3333 | 0.0022457 | 0.0024334
2012-12-13 | ZN2635:PA19 | URBAN | Vegetation | 913150 | 54 | 8 | 432 | 0.00026281 | 0.0032851
2012-12-17 | ZN2635:PA17 | URBAN | Equipment Failure | 913152 | 74 | 183 | 13542 | 0.0082384 | 0.0045019
2012-12-17 | ZN10993:PA7 | URBAN | Third Party Impacts | 913162 | 1 | 294.2333 | 294.2333 | 0.000179 | 6.0836e-05
2012-12-17 | 515:35197 | LONG RURAL | Animals | 913219 | 23 | 76.8 | 1766.4 | 0.0010746 | 0.0013992
2012-12-17 | 202:34253 | URBAN | Other | 913232 | 1 | 127.6333 | 127.6333 | 7.7647e-05 | 6.0836e-05
2012-12-17 | ZN9700:PA23 | URBAN | Animals | 913236 | 1688 | 32 | 54016 | 0.032861 | 0.10269
2012-12-17 | 238:34140 | URBAN | Equipment Failure | 913247 | 39 | 301.3 | 11750.7 | 0.0071487 | 0.0023726
2012-12-18 | 229:34995 | SHORT RURAL | Vegetation | 913259 | 1 | 269.2333 | 269.2333 | 0.00016379 | 6.0837e-05
2012-12-18 | 264:81241 | SHORT RURAL | Other | 913261 | 6 | 310.7833 | 1864.7 | 0.0011344 | 0.00036502
2012-12-17 | 227:13016 | SHORT RURAL | Equipment Failure | 913278 | 15 | 262 | 3930 | 0.0023909 | 0.00091254
2012-12-13 | ZN847:PA44 | URBAN | Third Party Impacts | 913284 | 74 | 105 | 7770 | 0.0047269 | 0.0045018
2012-12-18 | ZN4545:PA17 | URBAN | Animals | 913286 | 947 | 102 | 83427 | 0.050754 | 0.057612
2012-12-18 | ZN4545:PA19 | URBAN | Animals | 913286 | 7 | 102 | 483 | 0.00029384 | 0.00042586
2012-12-17 | 807:74184 | SHORT RURAL | Animals | 913295 | 2 | 185 | 370 | 0.00022509 | 0.00012167
2012-12-18 | ZN1193:PA9 | URBAN | Other | 913311 | 1 | 128.0167 | 128.0167 | 7.7881e-05 | 6.0837e-05
2012-12-18 | 807:74184 | SHORT RURAL | Other | 913328 | 1 | 310.1833 | 310.1833 | 0.00018871 | 6.0837e-05
2012-12-18 | ZN3922:PA1 | URBAN | Other | 913344 | 1 | 154.0833 | 154.0833 | 9.3739e-05 | 6.0837e-05
2012-12-18 | ZN2635:PA21 | URBAN | Other | 913356 | 41 | 133.35 | 5467.35 | 0.0033262 | 0.0024943
2012-12-17 | ZN167:PA21 | URBAN | Equipment Failure | 913390 | 1 | 130 | 130 | 7.9087e-05 | 6.0836e-05
2012-12-18 | ZN2835:PA27 | URBAN | Other | 913398 | 1 | 460.9333 | 460.9333 | 0.00028042 | 6.0837e-05
2012-12-18 | ZN340:PA21 | URBAN | Weather | 913414 | 1 | 267.9667 | 267.9667 | 0.00016302 | 6.0837e-05
2012-12-18 | 509:48040 | SHORT RURAL | Other | 913480 | 1 | 220.3333 | 220.3333 | 0.00013404 | 6.0837e-05
2012-12-18 | 243:80083 | SHORT RURAL | Other | 913528 | 113 | 200 | 22600 | 0.013749 | 0.0068745
2012-12-18 | ZN9035:PA1 | URBAN | Equipment Failure | 913531 | 2 | 82 | 164 | 9.9772e-05 | 0.00012167
2012-12-18 | ZN9035:PA4 | URBAN | Equipment Failure | 913531 | 14 | 82 | 1134.9333 | 0.00069046 | 0.00085171
2012-12-18 | 222:2015 | SHORT RURAL | Other | 913540 | 1 | 50.65 | 50.65 | 3.0814e-05 | 6.0837e-05
2012-12-18 | 216:10726 | URBAN | Third Party Impacts | 913553 | 1 | 954.9167 | 954.9167 | 0.00058094 | 6.0837e-05
2012-12-18 | ZN15010:PA1 | URBAN | Equipment Failure | 913587 | 1 | 344.65 | 344.65 | 0.00020967 | 6.0837e-05
2012-12-18 | 803:74010 | SHORT RURAL | Other | 913609 | 1 | 148 | 148 | 9.0038e-05 | 6.0837e-05
2012-12-18 | ZN3922:PA2 | SHORT RURAL | Other | 913612 | 296 | 103 | 30488 | 0.018548 | 0.018008
2012-12-18 | 232:11454 | SHORT RURAL | Other | 913633 | 1 | 244.3667 | 244.3667 | 0.00014866 | 6.0837e-05
2012-12-19 | ZN9037:PA8 | URBAN | Animals | 913645 | 135 | 48 | 6480 | 0.0039422 | 0.0082129
2012-12-19 | ZN15004:PA9 | URBAN | Equipment Failure | 913647 | 73 | 333.6167 | 24354.0167 | 0.014816 | 0.0044411
2012-12-19 | ZN2466:PA20 | URBAN | Equipment Failure | 913651 | 25 | 178 | 4450 | 0.0027072 | 0.0015209
2012-12-19 | ZN3472:PA12 | URBAN | Equipment Failure | 913651 | 50 | 178 | 8890 | 0.0054084 | 0.0030418
2012-12-19 | ZN3154:PA18 | URBAN | Equipment Failure | 913659 | 42 | 54.4667 | 2287.6 | 0.0013917 | 0.0025551
2012-12-19 | 235:2120 | SHORT RURAL | Equipment Failure | 913767 | 60 | 433 | 13900 | 0.0084563 | 0.0036502
2012-12-19 | 812:19072 | SHORT RURAL | Other | 913821 | 1 | 227.7 | 227.7 | 0.00013853 | 6.0837e-05
2012-12-19 | 513:48059 | SHORT RURAL | Other | 913860 | 1 | 130.1833 | 130.1833 | 7.9199e-05 | 6.0837e-05
2012-12-19 | ZN12600:PA2 | SHORT RURAL | Vegetation | 913941 | 1 | 149.6833 | 149.6833 | 9.1062e-05 | 6.0837e-05
2012-11-26 | 238:34141 | SHORT RURAL | Equipment Failure | 913978 | 1808 | 1468 | 163892 | 0.099704 | 0.10999
2012-12-19 | ZN3922:PA21 | SHORT RURAL | Other | 914009 | 1 | 239.85 | 239.85 | 0.00014592 | 6.0837e-05
2012-12-19 | ZN12650:PA6 | URBAN | Third Party Impacts | 914026 | 1 | 265.4 | 265.4 | 0.00016146 | 6.0837e-05
2012-12-19 | ZN15001:PA2 | URBAN | Equipment Failure | 914070 | 45 | 195.45 | 8795.25 | 0.0053507 | 0.0027376
2012-12-19 | ZN12570:PA35 | URBAN | Operational Error | 914075 | 269 | 196 | 52724 | 0.032076 | 0.016365
2012-12-19 | 526:34640 | SHORT RURAL | Other | 914076 | 30 | 69 | 2070 | 0.0012593 | 0.0018251
2012-12-19 | 509:48039 | LONG RURAL | Equipment Failure | 914084 | 77 | 825 | 18965 | 0.011538 | 0.0046844
2012-12-20 | 264:81240 | SHORT RURAL | Equipment Failure | 914093 | 2 | 160 | 320 | 0.00019468 | 0.00012167
2012-12-19 | 510:48164 | SHORT RURAL | Equipment Failure | 914095 | 6 | 232 | 1392 | 0.00084685 | 0.00036502
2012-12-20 | ZN847:PA19 | URBAN | Other | 914112 | 60 | 56 | 3360 | 0.0020441 | 0.0036502
2012-12-20 | 264:81240 | SHORT RURAL | Equipment Failure | 914136 | 1 | 35 | 35 | 2.1293e-05 | 6.0837e-05
2012-12-20 | 216:10728 | URBAN | Other | 914196 | 1 | 123.2667 | 123.2667 | 7.4992e-05 | 6.0837e-05
2012-12-20 | 235:2120 | SHORT RURAL | Other | 914253 | 65 | 77 | 5005 | 0.0030449 | 0.0039544
2012-12-20 | ZN1164:PA13 | URBAN | Third Party Impacts | 914318 | 1 | 281.5 | 281.5 | 0.00017126 | 6.0837e-05
2012-12-20 | ZN15008:PA5 | URBAN | Equipment Failure | 914322 | 85 | 84 | 7140 | 0.0043438 | 0.0051711
2012-12-20 | ZN9252:PA12 | URBAN | Vegetation | 914330 | 50 | 9.15 | 457.5 | 0.00027833 | 0.0030418
2012-12-20 | 206:34441 | URBAN | Vegetation | 914331 | 1 | 131.6333 | 131.6333 | 8.0082e-05 | 6.0837e-05
2012-12-20 | ZN10999:PA16 | URBAN | Other | 914342 | 13 | 217 | 2821 | 0.0017162 | 0.00079088
2012-12-20 | ZN72:PA30 | URBAN | Other | 914363 | 1 | 174.4 | 174.4 | 0.0001061 | 6.0837e-05
2012-12-20 | ZN965:PA8 | URBAN | Vegetation | 914365 | 17 | 84 | 1428 | 0.00086875 | 0.0010342
2012-12-20 | ZN12610:PA2 | URBAN | Third Party Impacts | 914368 | 1 | 272.6667 | 272.6667 | 0.00016588 | 6.0837e-05
2012-12-20 | ZN5868:PA30 | URBAN | Equipment Failure | 914373 | 27 | 221 | 5961.3667 | 0.0036267 | 0.0016426
2012-12-20 | 514:18137 | SHORT RURAL | Other | 914391 | 2 | 94.2667 | 188.5333 | 0.0001147 | 0.00012167
2012-12-20 | 512:48049 | SHORT RURAL | Other | 914442 | 2 | 69.1667 | 138.3333 | 8.4158e-05 | 0.00012167
2012-12-20 | 520:48172 | SHORT RURAL | Other | 914447 | 2 | 126 | 252 | 0.00015331 | 0.00012167
2012-12-20 | ZN3472:PA30 | URBAN | Weather | 914448 | 60 | 80.45 | 4827 | 0.0029366 | 0.0036502
2012-12-20 | ZN2602:PA41 | URBAN | Vegetation | 914461 | 94 | 52 | 4888 | 0.0029737 | 0.0057187
2012-12-20 | 235:2120 | SHORT RURAL | Other | 914465 | 1 | 167.1167 | 167.1167 | 0.00010167 | 6.0837e-05
2012-12-20 | 520:48172 | SHORT RURAL | Equipment Failure | 914466 | 1 | 215.25 | 215.25 | 0.00013095 | 6.0837e-05
2012-12-20 | ZN12600:PA1 | SHORT RURAL | Other | 914486 | 600 | 27 | 16200 | 0.0098556 | 0.036502
2012-12-20 | ZN12600:PA11 | URBAN | Other | 914486 | 928 | 27 | 25056 | 0.015243 | 0.056457
2012-12-20 | ZN12600:PA12 | URBAN | Other | 914486 | 273 | 27 | 7371 | 0.0044843 | 0.016608
2012-12-20 | ZN12600:PA13 | SHORT RURAL | Other | 914486 | 853 | 27 | 23031 | 0.014011 | 0.051894
2012-12-20 | ZN12600:PA2 | SHORT RURAL | Other | 914486 | 777 | 27 | 20979 | 0.012763 | 0.04727
2012-12-20 | ZN12600:PA3 | URBAN | Other | 914486 | 1445 | 27 | 39015 | 0.023736 | 0.087909
2012-12-20 | ZN12600:PA5 | URBAN | Other | 914486 | 93 | 27 | 2511 | 0.0015276 | 0.0056578
2012-12-20 | ZN12600:PA9 | SHORT RURAL | Other | 914486 | 1711 | 27 | 46197 | 0.028105 | 0.10409
2012-12-20 | ZN12650:PA1 | SHORT RURAL | Other | 914486 | 2 | 27 | 54 | 3.2852e-05 | 0.00012167
2012-12-21 | ZN965:PA47 | URBAN | Third Party Impacts | 914506 | 50 | 31 | 1550 | 0.00094297 | 0.0030418
2012-12-21 | ZN35370:PA4 | URBAN | Other | 914507 | 15 | 81 | 1215 | 0.00073917 | 0.00091255
2012-12-21 | 512:48049 | SHORT RURAL | Other | 914509 | 2 | 93.5667 | 163.5167 | 9.9479e-05 | 0.00012167
2012-12-21 | 238:34137 | URBAN | Other | 914512 | 1 | 55 | 55 | 3.346e-05 | 6.0837e-05
2012-12-21 | ZN187:PA13 | URBAN | Other | 914515 | 1 | 216.1833 | 216.1833 | 0.00013152 | 6.0837e-05
2012-12-21 | ZN14891:PA5 | SHORT RURAL | Other | 914550 | 1 | 57.65 | 57.65 | 3.5073e-05 | 6.0837e-05
2012-12-21 | 512:48049 | SHORT RURAL | Animals | 914552 | 4 | 86 | 312.7333 | 0.00019026 | 0.00024335
2012-12-21 | ZN36300:PA19 | URBAN | Third Party Impacts | 914572 | 1 | 321.05 | 321.05 | 0.00019532 | 6.0837e-05
2012-12-21 | 203:8090 | URBAN | Other | 914657 | 1 | 45 | 45 | 2.7377e-05 | 6.0837e-05
2012-12-21 | 232:11454 | SHORT RURAL | Other | 914726 | 1 | 184.8667 | 184.8667 | 0.00011247 | 6.0837e-05
2012-12-21 | 510:48164 | SHORT RURAL | Third Party Impacts | 914728 | 2 | 205 | 410 | 0.00024943 | 0.00012167
2012-12-21 | 507:80932 | SHORT RURAL | Other | 914756 | 1 | 82.2667 | 82.2667 | 5.0049e-05 | 6.0837e-05
2012-12-21 | ZN965:PA29 | URBAN | Equipment Failure | 914780 | 1 | 156.1 | 156.1 | 9.4967e-05 | 6.0837e-05
2012-12-21 | 261:81870 | URBAN | Other | 914787 | 4 | 94 | 376 | 0.00022875 | 0.00024335
2012-12-22 | ZN2602:PA35 | URBAN | Other | 914790 | 1 | 668.2833 | 668.2833 | 0.00040656 | 6.0837e-05
2012-12-22 | ZN129:PA2 | URBAN | Third Party Impacts | 914815 | 54 | 104 | 5616 | 0.0034166 | 0.0032852
2012-12-22 | ZN9035:PA4 | URBAN | Equipment Failure | 914824 | 1 | 162.0333 | 162.0333 | 9.8576e-05 | 6.0837e-05
2012-12-22 | ZN2602:PA35 | URBAN | Other | 914826 | 1 | 234.4333 | 234.4333 | 0.00014262 | 6.0837e-05
2012-12-22 | 807:74179 | SHORT RURAL | Other | 914835 | 3 | 174.5333 | 518.5167 | 0.00031545 | 0.00018251
2012-12-22 | ZN129:PA2 | URBAN | Other | 914857 | 69 | 90 | 6210 | 0.003778 | 0.0041978
2012-12-22 | ZN35500:PA24 | URBAN | Other | 914857 | 24 | 90 | 2160 | 0.0013141 | 0.0014601
2012-12-22 | 813:89055 | SHORT RURAL | Other | 914894 | 8 | 133 | 1064 | 0.00064731 | 0.0004867
2012-12-22 | 503:48011 | SHORT RURAL | Other | 914898 | 1 | 63 | 63 | 3.8327e-05 | 6.0837e-05
2012-12-22 | ZN10999:PA12 | URBAN | Equipment Failure | 914903 | 1 | 153.45 | 153.45 | 9.3354e-05 | 6.0837e-05
2012-12-23 | ZN9900:PA13 | URBAN | Third Party Impacts | 914951 | 23 | 85 | 1955 | 0.0011894 | 0.0013993
2012-12-23 | ZN116:PA42 | URBAN | Third Party Impacts | 914959 | 47 | 342.65 | 15134 | 0.0092071 | 0.0028593
2012-12-23 | ZN262:PA16 | URBAN | Third Party Impacts | 914959 | 1 | 342.65 | 175.65 | 0.00010686 | 6.0837e-05
2012-12-23 | ZN262:PA19 | URBAN | Third Party Impacts | 914959 | 88 | 342.65 | 27456 | 0.016703 | 0.0053537
2012-12-23 | ZN187:PA17 | URBAN | Other | 914969 | 1 | 139.8 | 139.8 | 8.505e-05 | 6.0837e-05
2012-12-23 | 238:34144 | URBAN | Equipment Failure | 914971 | 2499 | 94 | 41110 | 0.02501 | 0.15203
2012-12-23 | ZN1193:PA25 | URBAN | Vegetation | 915011 | 71 | 186 | 13206 | 0.0080341 | 0.0043194
2012-12-23 | ZN129:PA21 | URBAN | Vegetation | 915018 | 679 | 74.9333 | 50879.7333 | 0.030954 | 0.041308
2012-12-23 | ZN342:PA18 | URBAN | Equipment Failure | 915022 | 12 | 278.5 | 3342 | 0.0020332 | 0.00073004
2012-12-23 | ZN262:PA19 | URBAN | Third Party Impacts | 915023 | 1 | 229.8 | 229.8 | 0.0001398 | 6.0837e-05
2012-12-23 | 507:80923 | SHORT RURAL | Other | 915027 | 1 | 227.4 | 227.4 | 0.00013834 | 6.0837e-05
2012-12-23 | ZN9118:PA12 | URBAN | Equipment Failure | 915030 | 32 | 54.1333 | 1732.2667 | 0.0010539 | 0.0019468
2012-12-23 | 803:74010 | SHORT RURAL | Other | 915038 | 1 | 66.9833 | 66.9833 | 4.0751e-05 | 6.0837e-05
2012-12-23 | 803:74010 | SHORT RURAL | Other | 915040 | 1 | 58.9167 | 58.9167 | 3.5843e-05 | 6.0837e-05
2012-12-23 | 807:74179 | SHORT RURAL | Vegetation | 915048 | 302 | 134 | 13380 | 0.00814 | 0.018373
2012-12-23 | ZN15010:PA11 | URBAN | Vegetation | 915049 | 1 | 315.6833 | 315.6833 | 0.00019205 | 6.0837e-05
2012-12-23 | 802:82215 | SHORT RURAL | Other | 915052 | 1 | 164 | 164 | 9.9773e-05 | 6.0837e-05
2012-12-23 | ZN36300:PA11 | URBAN | Equipment Failure | 915063 | 1 | 185.9333 | 185.9333 | 0.00011312 | 6.0837e-05
2012-12-23 | 223:14398 | URBAN | Other | 915070 | 1 | 52.6667 | 52.6667 | 3.2041e-05 | 6.0837e-05
2012-12-23 | ZN15011:PA2 | URBAN | Other | 915083 | 1 | 1129.0167 | 1129.0167 | 0.00068686 | 6.0837e-05
2012-12-24 | ZN180:PA21 | URBAN | Equipment Failure | 915090 | 1 | 518.65 | 518.65 | 0.00031553 | 6.0837e-05
2012-12-24 | 807:74180 | SHORT RURAL | Other | 915093 | 1 | 142 | 142 | 8.6389e-05 | 6.0837e-05
2012-12-24 | 220:8691 | URBAN | Other | 915095 | 1 | 171.35 | 171.35 | 0.00010424 | 6.0837e-05
2012-12-24 | 258:80785 | URBAN | Other | 915101 | 1 | 109.3833 | 109.3833 | 6.6546e-05 | 6.0837e-05
2012-12-24 | 801:74118 | URBAN | Animals | 915109 | 797 | 177 | 36793 | 0.022384 | 0.048487
2012-12-19 | 260:33350 | SHORT RURAL | Equipment Failure | 915113 | 1 | 55 | 55 | 3.346e-05 | 6.0837e-05
2012-12-24 | 258:80785 | URBAN | Other | 915118 | 1 | 17.75 | 17.75 | 1.0799e-05 | 6.0837e-05
2012-12-24 | 206:34438 | SHORT RURAL | Other | 915131 | 1 | 86.2 | 86.2 | 5.2441e-05 | 6.0837e-05
2012-12-24 | 801:74118 | URBAN | Other | 915139 | 1 | 134.0333 | 134.0333 | 8.1542e-05 | 6.0837e-05
2012-12-24 | ZN9118:PA12 | URBAN | Equipment Failure | 915174 | 1 | 595.7 | 595.7 | 0.00036241 | 6.0837e-05
2012-12-24 | ZN180:PA21 | URBAN | Equipment Failure | 915178 | 2 | 292.45 | 584.9 | 0.00035584 | 0.00012167
2012-12-21 | 512:48046 | SHORT RURAL | Other | 915231 | 1769 | 4 | 7076 | 0.0043048 | 0.10762
2012-12-21 | 526:34636 | SHORT RURAL | Equipment Failure | 915234 | 1 | 85 | 85 | 5.1711e-05 | 6.0837e-05
2012-12-24 | 256:80644 | URBAN | Other | 915236 | 1 | 60.9333 | 60.9333 | 3.707e-05 | 6.0837e-05
2012-12-24 | 807:74184 | SHORT RURAL | Other | 915240 | 1 | 96 | 96 | 5.8404e-05 | 6.0837e-05
2012-12-24 | ZN9118:PA8 | URBAN | Equipment Failure | 915252 | 1 | 214.3333 | 214.3333 | 0.00013039 | 6.0837e-05
2012-12-24 | 208:59 | URBAN | Other | 915262 | 1 | 95.1833 | 95.1833 | 5.7907e-05 | 6.0837e-05
2012-12-24 | 256:80638 | URBAN | Other | 915292 | 1 | 37.9333 | 37.9333 | 2.3077e-05 | 6.0837e-05
2012-12-24 | ZN80:PA37 | URBAN | Equipment Failure | 915296 | 41 | 122.8167 | 5035.4833 | 0.0030634 | 0.0024943
2012-12-20 | 512:48049 | SHORT RURAL | Equipment Failure | 915316 | 2 | 70 | 140 | 8.5172e-05 | 0.00012167
2012-12-21 | 514:18137 | SHORT RURAL | Equipment Failure | 915332 | 1 | 116 | 116 | 7.0571e-05 | 6.0837e-05
2012-12-24 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 915348 | 94 | 164 | 8563 | 0.0052095 | 0.0057187
2012-12-24 | 232:11457 | URBAN | Other | 915398 | 1 | 228.0833 | 228.0833 | 0.00013876 | 6.0837e-05
2012-12-24 | ZN180:PA21 | URBAN | Equipment Failure | 915425 | 64 | 272.05 | 17411.2 | 0.010592 | 0.0038936
2012-12-24 | 507:80922 | SHORT RURAL | Other | 915449 | 1 | 71.1667 | 71.1667 | 4.3296e-05 | 6.0837e-05
2012-12-24 | 503:48016 | URBAN | Other | 915460 | 1 | 154.65 | 154.65 | 9.4084e-05 | 6.0837e-05
2012-12-24 | 238:34144 | URBAN | Other | 915466 | 1 | 214.2333 | 214.2333 | 0.00013033 | 6.0837e-05
2012-12-24 | ZN15012:PA6 | URBAN | Other | 915467 | 1 | 151.0667 | 151.0667 | 9.1904e-05 | 6.0837e-05
2012-12-24 | ZN12630:PA3 | SHORT RURAL | Weather | 915475 | 420 | 78 | 32130 | 0.019547 | 0.025552
2012-12-24 | ZN12630:PA5 | SHORT RURAL | Vegetation | 915479 | 159 | 75 | 11925 | 0.0072548 | 0.0096731
2012-12-24 | ZN12630:PA4 | SHORT RURAL | Equipment Failure | 915483 | 3 | 190 | 570 | 0.00034677 | 0.00018251
2012-12-24 | ZN12630:PA5 | SHORT RURAL | Equipment Failure | 915498 | 6 | 138 | 828 | 0.00050373 | 0.00036502
2012-12-24 | 504:48031 | SHORT RURAL | Other | 915499 | 6 | 61.8667 | 371.2 | 0.00022583 | 0.00036502
2012-12-24 | 810:74050 | SHORT RURAL | Other | 915501 | 1 | 83 | 83 | 5.0495e-05 | 6.0837e-05
2012-12-24 | ZN2602:PA21 | URBAN | Equipment Failure | 915513 | 1 | 209.1667 | 209.1667 | 0.00012725 | 6.0837e-05
2012-12-24 | 243:80080 | SHORT RURAL | Other | 915528 | 9 | 63.6333 | 572.7 | 0.00034841 | 0.00054753
2012-12-24 | 243:80080 | SHORT RURAL | Other | 915529 | 663 | 23 | 15249 | 0.009277 | 0.040335
2012-12-24 | ZN15014:PA7 | URBAN | Equipment Failure | 915530 | 1 | 167.95 | 167.95 | 0.00010218 | 6.0837e-05
2012-12-24 | ZN14892:PA6 | SHORT RURAL | Equipment Failure | 915531 | 2 | 68 | 136 | 8.2738e-05 | 0.00012167
2012-12-24 | ZN12610:PA22 | URBAN | Other | 915533 | 2 | 877.5 | 1753.5167 | 0.0010668 | 0.00012167
2012-12-24 | ZN2400:PA21 | URBAN | Equipment Failure | 915541 | 647 | 924.5833 | 598205.4167 | 0.36393 | 0.039362
2012-12-24 | ZN15001:PA18 | URBAN | Other | 915546 | 1 | 805.9167 | 805.9167 | 0.0004903 | 6.0837e-05
2012-12-24 | 515:35192 | SHORT RURAL | Other | 915554 | 1 | 432 | 432 | 0.00026282 | 6.0837e-05
2012-12-24 | ZN15004:PA9 | URBAN | Other | 915560 | 1 | 1096.55 | 1096.55 | 0.00066711 | 6.0837e-05
2012-12-24 | ZN12630:PA4 | SHORT RURAL | Weather | 915563 | 1 | 259.85 | 259.85 | 0.00015808 | 6.0837e-05
2012-12-24 | 515:35192 | SHORT RURAL | Other | 915564 | 1 | 283 | 283 | 0.00017217 | 6.0837e-05
2012-12-24 | 515:35197 | LONG RURAL | Other | 915565 | 1 | 445.3833 | 445.3833 | 0.00027096 | 6.0837e-05
2012-12-24 | 513:48059 | SHORT RURAL | Equipment Failure | 915566 | 460 | 309 | 25071 | 0.015252 | 0.027985
2012-12-24 | 520:48172 | SHORT RURAL | Other | 915567 | 14 | 87 | 1218 | 0.00074099 | 0.00085172
2012-12-24 | 512:48049 | SHORT RURAL | Other | 915568 | 1 | 75 | 75 | 4.5628e-05 | 6.0837e-05
2012-12-24 | ZN3672:PA13 | URBAN | Other | 915569 | 1 | 192.85 | 192.85 | 0.00011732 | 6.0837e-05
2012-12-24 | ZN3672:PA44 | URBAN | Other | 915571 | 2 | 1396.15 | 2770.7 | 0.0016856 | 0.00012167
2012-12-24 | ZN10999:PA29 | URBAN | Other | 915576 | 1 | 227.3167 | 227.3167 | 0.00013829 | 6.0837e-05
2012-12-24 | 238:34141 | SHORT RURAL | Other | 915578 | 1 | 69.4833 | 69.4833 | 4.2272e-05 | 6.0837e-05
2012-12-24 | ZN12610:PA13 | URBAN | Other | 915581 | 4 | 806 | 3224 | 0.0019614 | 0.00024335
2012-12-24 | 520:48172 | SHORT RURAL | Other | 915586 | 1 | 315.9833 | 315.9833 | 0.00019223 | 6.0837e-05
2012-12-24 | ZN3472:PA18 | URBAN | Vegetation | 915593 | 35 | 106 | 3710 | 0.0022571 | 0.0021293
2012-12-24 | ZN690:PA27 | URBAN | Other | 915595 | 1 | 898.0833 | 898.0833 | 0.00054637 | 6.0837e-05
2012-12-24 | ZN12620:PA8 | SHORT RURAL | Equipment Failure | 915596 | 1254 | 38 | 47652 | 0.02899 | 0.07629
2012-12-24 | ZN12620:PA10 | SHORT RURAL | Equipment Failure | 915597 | 1077 | 39 | 42003 | 0.025553 | 0.065521
2012-12-24 | ZN167:PA21 | URBAN | Other | 915599 | 1 | 997.4667 | 997.4667 | 0.00060683 | 6.0837e-05
2012-12-24 | ZN14891:PA20 | SHORT RURAL | Other | 915601 | 513 | 115 | 58995 | 0.035891 | 0.031209
2012-12-24 | 515:35192 | SHORT RURAL | Other | 915602 | 2 | 184 | 368 | 0.00022388 | 0.00012167
2012-12-24 | ZN15008:PA9 | URBAN | Other | 915604 | 1 | 715.0667 | 715.0667 | 0.00043502 | 6.0837e-05
2012-12-24 | ZN14892:PA6 | SHORT RURAL | Other | 915615 | 1 | 469.8333 | 469.8333 | 0.00028583 | 6.0837e-05
2012-12-24 | 243:80080 | SHORT RURAL | Equipment Failure | 915628 | 5 | 581 | 2905 | 0.0017673 | 0.00030418
2012-12-24 | 243:80080 | SHORT RURAL | Other | 915629 | 1 | 163.6 | 163.6 | 9.9529e-05 | 6.0837e-05
2012-12-24 | 243:80080 | SHORT RURAL | Equipment Failure | 915632 | 48 | 97 | 4656 | 0.0028326 | 0.0029202
2012-12-25 | 223:14395 | SHORT RURAL | Other | 915633 | 93 | 150 | 13950 | 0.0084809 | 0.0056539
2012-12-24 | 520:48172 | SHORT RURAL | Other | 915638 | 2 | 227 | 454 | 0.0002762 | 0.00012167
2012-12-24 | ZN262:PA31 | URBAN | Equipment Failure | 915646 | 1 | 590.4333 | 590.4333 | 0.0003592 | 6.0837e-05
2012-12-24 | 801:74122 | URBAN | Other | 915647 | 1 | 66.3167 | 66.3167 | 4.0345e-05 | 6.0837e-05
2012-12-24 | ZN2196:PA25 | URBAN | Equipment Failure | 915649 | 1 | 611.5833 | 611.5833 | 0.00037207 | 6.0837e-05
2012-12-24 | ZN35370:PA4 | URBAN | Equipment Failure | 915653 | 1 | 304.75 | 304.75 | 0.0001854 | 6.0837e-05
2012-12-25 | 513:48056 | SHORT RURAL | Other | 915657 | 6 | 292 | 1752 | 0.0010651 | 0.00036477
2012-12-25 | ZN15009:PA11 | URBAN | Other | 915658 | 1 | 918.1167 | 918.1167 | 0.00055817 | 6.0795e-05
2012-12-25 | ZN1290:PA4 | URBAN | Other | 915659 | 21 | 133.7 | 2807.7 | 0.0017069 | 0.0012767
2012-12-25 | ZN398:PA15 | URBAN | Equipment Failure | 915662 | 1 | 763.8167 | 763.8167 | 0.00046436 | 6.0795e-05
2012-12-25 | ZN2602:PA20 | URBAN | Equipment Failure | 915665 | 1 | 723.7667 | 723.7667 | 0.00044001 | 6.0795e-05
2012-12-25 | ZN2835:PA19 | URBAN | Other | 915669 | 1 | 705.1 | 705.1 | 0.00042866 | 6.0795e-05
2012-12-25 | ZN2835:PA23 | URBAN | Other | 915672 | 1 | 676.2667 | 676.2667 | 0.00041113 | 6.0795e-05
2012-12-25 | 223:14399 | SHORT RURAL | Other | 915674 | 73 | 55 | 4015 | 0.0024409 | 0.004438
2012-12-25 | ZN398:PA15 | URBAN | Equipment Failure | 915677 | 1 | 636.6 | 636.6 | 0.00038702 | 6.0795e-05
2012-12-25 | 520:48172 | SHORT RURAL | Other | 915681 | 3 | 175 | 525 | 0.00031917 | 0.00018238
2012-12-25 | 511:29878 | SHORT RURAL | Other | 915682 | 1 | 138.2667 | 138.2667 | 8.4059e-05 | 6.0795e-05
2012-12-25 | ZN9118:PA17 | URBAN | Vegetation | 915683 | 1 | 390.2167 | 390.2167 | 0.00023723 | 6.0795e-05
2012-12-25 | 503:48078 | URBAN | Other | 915684 | 1 | 85.5667 | 85.5667 | 5.202e-05 | 6.0795e-05
2012-12-25 | ZN9118:PA13 | URBAN | Equipment Failure | 915685 | 1 | 364.9 | 364.9 | 0.00022184 | 6.0795e-05
2012-12-25 | ZN1290:PA4 | URBAN | Equipment Failure | 915687 | 21 | 174.4167 | 3662.75 | 0.0022268 | 0.0012767
2012-12-25 | ZN15001:PA8 | URBAN | Other | 915689 | 1 | 297.6333 | 297.6333 | 0.00018095 | 6.0795e-05
2012-12-25 | ZN14891:PA5 | SHORT RURAL | Weather | 915692 | 4 | 180.85 | 723.4 | 0.00043979 | 0.00024318
2012-12-25 | ZN12620:PA3 | URBAN | Other | 915695 | 1 | 328.3 | 328.3 | 0.00019959 | 6.0795e-05
2012-12-25 | 512:48049 | SHORT RURAL | Other | 915696 | 4 | 447 | 1788 | 0.001087 | 0.00024318
2012-12-25 | ZN12630:PA4 | SHORT RURAL | Equipment Failure | 915700 | 1 | 210.3 | 210.3 | 0.00012785 | 6.0795e-05
2012-12-24 | 227:13020 | SHORT RURAL | Other | 915701 | 6 | 548 | 3288 | 0.0020003 | 0.00036502
2012-12-25 | ZN12650:PA13 | SHORT RURAL | Vegetation | 915704 | 1730 | 59 | 96062 | 0.058401 | 0.10517
2012-12-25 | ZN12650:PA6 | URBAN | Vegetation | 915704 | 2 | 59 | 110 | 6.6874e-05 | 0.00012159
2012-12-25 | ZN10990:PA6 | URBAN | Other | 915715 | 61 | 64.5 | 3934.5 | 0.002392 | 0.0037085
2012-12-25 | 520:48172 | SHORT RURAL | Other | 915720 | 1 | 259.8 | 259.8 | 0.00015794 | 6.0795e-05
2012-12-25 | 807:74184 | SHORT RURAL | Other | 915724 | 1 | 121 | 121 | 7.3562e-05 | 6.0795e-05
2012-12-25 | 224:80346 | URBAN | Other | 915725 | 1 | 128.8667 | 128.8667 | 7.8344e-05 | 6.0795e-05
2012-12-25 | ZN12620:PA3 | URBAN | Other | 915728 | 1 | 479.4167 | 479.4167 | 0.00029146 | 6.0795e-05
2012-12-25 | 512:48049 | SHORT RURAL | Other | 915731 | 2 | 71 | 142 | 8.6328e-05 | 0.00012159
2012-12-25 | 512:48049 | SHORT RURAL | Other | 915743 | 2 | 76 | 152 | 9.2408e-05 | 0.00012159
2012-12-25 | ZN9118:PA20 | URBAN | Equipment Failure | 915745 | 15 | 253.2333 | 3798.5 | 0.0023093 | 0.00091192
2012-12-25 | 513:48059 | SHORT RURAL | Other | 915747 | 2 | 80 | 160 | 9.7271e-05 | 0.00012159
2012-12-25 | ZN1610:PA26 | URBAN | Equipment Failure | 915748 | 49 | 66 | 3234 | 0.0019661 | 0.0029789
2012-12-25 | 217:33611 | URBAN | Other | 915750 | 1 | 156 | 156 | 9.484e-05 | 6.0795e-05
2012-12-25 | 515:35192 | SHORT RURAL | Equipment Failure | 915753 | 1 | 130 | 130 | 7.9033e-05 | 6.0795e-05
2012-12-25 | ZN10990:PA11 | URBAN | Animals | 915755 | 1147 | 35 | 40145 | 0.024406 | 0.069731
2012-12-25 | ZN9118:PA12 | URBAN | Equipment Failure | 915757 | 32 | 85.85 | 2747.2 | 0.0016702 | 0.0019454
2012-12-25 | ZN14891:PA5 | SHORT RURAL | Other | 915759 | 1 | 69.1833 | 69.1833 | 4.206e-05 | 6.0795e-05
2012-12-25 | 512:48049 | SHORT RURAL | Equipment Failure | 915764 | 8 | 299 | 2392 | 0.0014542 | 0.00048636
2012-12-25 | 515:35192 | SHORT RURAL | Other | 915772 | 1 | 95 | 95 | 5.7755e-05 | 6.0795e-05
2012-12-25 | 243:80083 | SHORT RURAL | Other | 915773 | 2 | 159 | 318 | 0.00019333 | 0.00012159
2012-12-25 | ZN2568:PA27 | URBAN | Equipment Failure | 915779 | 83 | 343.0833 | 28475.9167 | 0.017312 | 0.005046
2012-12-25 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 915801 | 1 | 238.0333 | 238.0333 | 0.00014471 | 6.0795e-05
2012-12-25 | ZN14143:PA17 | SHORT RURAL | Equipment Failure | 915811 | 1 | 302 | 302 | 0.0001836 | 6.0795e-05
2012-12-25 | 802:82225 | SHORT RURAL | Equipment Failure | 915817 | 1 | 362 | 362 | 0.00022008 | 6.0795e-05
2012-12-25 | 810:74054 | LONG RURAL | Other | 915819 | 18 | 98 | 1764 | 0.0010724 | 0.0010943
2012-12-25 | 243:80080 | SHORT RURAL | Equipment Failure | 915820 | 663 | 126 | 83538 | 0.050787 | 0.040307
2012-12-25 | 810:74054 | LONG RURAL | Equipment Failure | 915828 | 1 | 333 | 333 | 0.00020245 | 6.0795e-05
2012-12-25 | 810:74050 | SHORT RURAL | Other | 915829 | 2 | 181.0667 | 362.1333 | 0.00022016 | 0.00012159
2012-12-25 | 810:74050 | SHORT RURAL | Other | 915830 | 1 | 124 | 124 | 7.5385e-05 | 6.0795e-05
2012-12-25 | ZN931:PA11 | URBAN | Equipment Failure | 915835 | 1 | 316.5833 | 316.5833 | 0.00019247 | 6.0795e-05
2012-12-25 | ZN14143:PA17 | SHORT RURAL | Equipment Failure | 915843 | 747 | 194 | 53402 | 0.032466 | 0.045414
2012-12-25 | 512:48049 | SHORT RURAL | Other | 915847 | 5 | 497 | 2485 | 0.0015107 | 0.00030397
2012-12-25 | 813:89061 | LONG RURAL | Other | 915852 | 2 | 116 | 232 | 0.00014104 | 0.00012159
2012-12-25 | ZN35370:PA10 | SHORT RURAL | Equipment Failure | 915855 | 101 | 228 | 23028 | 0.014 | 0.0061403
2012-12-25 | ZN9037:PA2 | URBAN | Vegetation | 915859 | 43 | 40 | 1720 | 0.0010457 | 0.0026142
2012-12-25 | 264:81240 | SHORT RURAL | Other | 915860 | 529 | 331 | 31481 | 0.019139 | 0.03216
2012-12-25 | 229:34989 | SHORT RURAL | Vegetation | 915870 | 1 | 69.2833 | 69.2833 | 4.2121e-05 | 6.0795e-05
2012-12-25 | ZN14144:PA2 | SHORT RURAL | Vegetation | 915878 | 164 | 110 | 18040 | 0.010967 | 0.0099703
2012-12-25 | 813:89062 | SHORT RURAL | Other | 915879 | 33 | 101 | 3333 | 0.0020263 | 0.0020062
2012-12-25 | 232:11453 | SHORT RURAL | Other | 915890 | 1 | 258 | 258 | 0.00015685 | 6.0795e-05
2012-12-25 | 812:19066 | SHORT RURAL | Equipment Failure | 915891 | 4688 | 1202 | 313291 | 0.19046 | 0.28501
2012-12-26 | 812:19072 | SHORT RURAL | Other | 915892 | 24 | 317 | 7608 | 0.0046253 | 0.0014591
2012-12-25 | ZN3154:PA17 | URBAN | Other | 915901 | 32 | 166.2333 | 5319.4667 | 0.003234 | 0.0019454
2012-12-25 | ZN180:PA18 | URBAN | Other | 915913 | 1 | 79.7167 | 79.7167 | 4.8463e-05 | 6.0795e-05
2012-12-25 | 230:81434 | URBAN | Other | 915914 | 1 | 107.6667 | 107.6667 | 6.5456e-05 | 6.0795e-05
2012-12-25 | 814:82283 | SHORT RURAL | Other | 915915 | 23 | 370.5 | 8521.5 | 0.0051806 | 0.0013983
2012-12-25 | 238:34141 | SHORT RURAL | Other | 915918 | 15 | 95 | 1425 | 0.00086632 | 0.00091192
2012-12-25 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 915919 | 6 | 1113.15 | 6533.15 | 0.0039718 | 0.00036477
2012-12-25 | 202:34231 37 42 | URBAN | Other | 915928 | 1 | 88.3 | 69.7 | 4.2374e-05 | 6.0795e-05
2012-12-25 | 202:34256 | URBAN | Other | 915928 | 2 | 88.3 | 80.4 | 4.8879e-05 | 0.00012159
2012-12-25 | 202:34261 | SHORT RURAL | Other | 915928 | 42 | 88.3 | 3708.6 | 0.0022546 | 0.0025534
2012-12-25 | 813:89061 | LONG RURAL | Other | 915931 | 1 | 222 | 222 | 0.00013496 | 6.0795e-05
2012-12-25 | ZN269:PA7 | URBAN | Other | 915932 | 104 | 80.5833 | 8380.6667 | 0.005095 | 0.0063226
2012-12-25 | 513:48056 | SHORT RURAL | Equipment Failure | 915934 | 50 | 116 | 5800 | 0.0035261 | 0.0030397
2012-12-25 | 503:48076 | URBAN | Other | 915937 | 72 | 50 | 3600 | 0.0021886 | 0.0043772
2012-12-25 | 503:48076 | URBAN | Other | 915952 | 72 | 71 | 5112 | 0.0031078 | 0.0043772
2012-12-25 | 238:34141 | SHORT RURAL | Equipment Failure | 915954 | 32 | 190.3167 | 6090.1333 | 0.0037025 | 0.0019454
2012-12-25 | ZN12570:PA39 | URBAN | Other | 915957 | 1 | 377.9833 | 377.9833 | 0.00022979 | 6.0795e-05
2012-12-26 | ZN195:PA9 | URBAN | Vegetation | 915968 | 27 | 60 | 1620 | 0.00098487 | 0.0016415
2012-12-26 | 238:34147 | URBAN | Other | 915974 | 2 | 79.1333 | 150.9667 | 9.178e-05 | 0.00012159
2012-12-26 | 515:35192 | SHORT RURAL | Other | 915983 | 4 | 118 | 472 | 0.00028695 | 0.00024318
2012-12-26 | ZN15014:PA22 | URBAN | Other | 915984 | 1 | 316.45 | 316.45 | 0.00019238 | 6.0795e-05
2012-12-26 | 813:89062 | SHORT RURAL | Other | 915986 | 1 | 250.8 | 250.8 | 0.00015247 | 6.0795e-05
2012-12-26 | 813:89061 | LONG RURAL | Other | 915998 | 1 | 385.45 | 385.45 | 0.00023433 | 6.0795e-05
2012-12-26 | 513:48059 | SHORT RURAL | Other | 916003 | 3 | 50 | 150 | 9.1192e-05 | 0.00018238
2012-12-26 | 810:74054 | LONG RURAL | Other | 916008 | 1 | 131.2833 | 131.2833 | 7.9813e-05 | 6.0795e-05
2012-12-26 | 238:34141 | SHORT RURAL | Equipment Failure | 916014 | 19 | 74.7 | 1419.3 | 0.00086286 | 0.0011551
2012-12-26 | 814:82283 | SHORT RURAL | Other | 916015 | 23 | 195 | 4485 | 0.0027266 | 0.0013983
2012-12-26 | ZN13000:PA1 | URBAN | Other | 916021 | 1 | 237.4 | 237.4 | 0.00014433 | 6.0795e-05
2012-12-26 | 807:74184 | SHORT RURAL | Equipment Failure | 916036 | 1 | 160.2 | 160.2 | 9.7393e-05 | 6.0795e-05
2012-12-26 | 242:81539 | URBAN | Other | 916037 | 1 | 331.5167 | 331.5167 | 0.00020154 | 6.0795e-05
2012-12-26 | 812:19072 | SHORT RURAL | Other | 916049 | 1 | 71 | 71 | 4.3164e-05 | 6.0795e-05
2012-12-26 | ZN1285:PA27 | URBAN | Equipment Failure | 916055 | 1 | 472.7833 | 472.7833 | 0.00028743 | 6.0795e-05
2012-12-26 | 801:74122 | URBAN | Other | 916068 | 1 | 236.65 | 236.65 | 0.00014387 | 6.0795e-05
2012-12-26 | 512:48049 | SHORT RURAL | Equipment Failure | 916078 | 1 | 116.85 | 116.85 | 7.1038e-05 | 6.0795e-05
2012-12-26 | 513:48059 | SHORT RURAL | Other | 916080 | 1 | 51.0667 | 51.0667 | 3.1046e-05 | 6.0795e-05
2012-12-26 | ZN10994:PA11 | URBAN | Vegetation | 916081 | 47 | 60.1167 | 2825.4833 | 0.0017177 | 0.0028573
2012-12-26 | ZN13000:PA5 | SHORT RURAL | Equipment Failure | 916098 | 1 | 88.5167 | 88.5167 | 5.3813e-05 | 6.0795e-05
2012-12-26 | 512:48046 | SHORT RURAL | Other | 916099 | 1 | 252.1 | 252.1 | 0.00015326 | 6.0795e-05
2012-12-26 | 503:48011 | SHORT RURAL | Equipment Failure | 916108 | 7 | 310.2667 | 2171.8667 | 0.0013204 | 0.00042556
2012-12-26 | 801:74123 | SHORT RURAL | Other | 916124 | 1 | 105.05 | 105.05 | 6.3865e-05 | 6.0795e-05
2012-12-26 | ZN10991:PA12 | URBAN | Vegetation | 916125 | 1 | 381 | 381 | 0.00023163 | 6.0795e-05
2012-12-26 | 264:81240 | SHORT RURAL | Third Party Impacts | 916128 | 74 | 358 | 6486 | 0.0039431 | 0.0044988
2012-12-26 | ZN15005:PA10 | URBAN | Other | 916134 | 1 | 203.0167 | 203.0167 | 0.00012342 | 6.0795e-05
2012-12-26 | 515:35197 | LONG RURAL | Other | 916138 | 2 | 44 | 88 | 5.3499e-05 | 0.00012159
2012-12-26 | 243:80080 | SHORT RURAL | Other | 916141 | 2 | 65 | 130 | 7.9033e-05 | 0.00012159
2012-12-26 | ZN14891:PA8 | SHORT RURAL | Equipment Failure | 916160 | 1316 | 250 | 286231 | 0.17401 | 0.080006
2012-12-27 | ZN36300:PA17 | URBAN | Vegetation | 916165 | 1380 | 73 | 92874 | 0.056462 | 0.083897
2012-12-27 | ZN14144:PA2 | SHORT RURAL | Equipment Failure | 916166 | 34 | 115.9667 | 3942.8667 | 0.002397 | 0.002067
2012-12-24 | ZN12630:PA5 | SHORT RURAL | Equipment Failure | 916186 | 3 | 240 | 720 | 0.00043803 | 0.00018251
2012-12-27 | ZN384:PA41 | URBAN | Equipment Failure | 916241 | 475 | 32 | 13967 | 0.0084912 | 0.028877
2012-12-27 | 515:35197 | LONG RURAL | Weather | 916246 | 1 | 133.75 | 133.75 | 8.1313e-05 | 6.0795e-05
2012-12-27 | 812:19066 | SHORT RURAL | Equipment Failure | 916255 | 81 | 125 | 10125 | 0.0061555 | 0.0049244
2012-12-25 | ZN14143:PA5 | URBAN | Animals | 916267 | 408 | 630 | 55011 | 0.033444 | 0.024804
2012-12-25 | 243:80080 | SHORT RURAL | Other | 916285 | 2 | 82 | 164 | 9.9703e-05 | 0.00012159
2012-12-27 | ZN14891:PA20 | SHORT RURAL | Equipment Failure | 916297 | 9 | 267 | 2388 | 0.0014518 | 0.00054715
2012-12-27 | 807:74184 | SHORT RURAL | Equipment Failure | 916318 | 1 | 215.7 | 215.7 | 0.00013113 | 6.0795e-05
2012-12-27 | 803:74016 | SHORT RURAL | Other | 916342 | 3 | 99.2 | 254.2 | 0.00015454 | 0.00018238
2012-12-27 | 813:89061 | LONG RURAL | Other | 916375 | 2 | 245 | 490 | 0.00029789 | 0.00012159
2012-12-26 | 503:48076 | URBAN | Equipment Failure | 916397 | 72 | 240 | 17280 | 0.010505 | 0.0043772
2012-12-27 | 232:11457 | URBAN | Other | 916406 | 1 | 241.6833 | 241.6833 | 0.00014693 | 6.0795e-05
2012-12-27 | ZN3154:PA11 | URBAN | Other | 916409 | 1 | 340.3667 | 340.3667 | 0.00020692 | 6.0795e-05
2012-12-27 | ZN12570:PA34 | SHORT RURAL | Vegetation | 916467 | 1 | 191.4167 | 191.4167 | 0.00011637 | 6.0795e-05
2012-12-27 | ZN15009:PA1 | URBAN | Equipment Failure | 916470 | 16 | 809 | 12944 | 0.0078693 | 0.00097271
2012-12-28 | 813:89055 | SHORT RURAL | Other | 916503 | 1 | 180 | 180 | 0.00010943 | 6.0793e-05
2012-12-28 | 264:81244 | URBAN | Equipment Failure | 916504 | 385 | 9 | 3465 | 0.0021065 | 0.023405
2012-12-28 | 810:74054 | LONG RURAL | Other | 916518 | 1 | 120 | 120 | 7.2952e-05 | 6.0793e-05
2012-12-28 | 810:74050 | SHORT RURAL | Weather | 916543 | 1 | 139.2833 | 139.2833 | 8.4675e-05 | 6.0793e-05
2012-12-28 | 813:89055 | SHORT RURAL | Equipment Failure | 916560 | 1 | 330 | 330 | 0.00020062 | 6.0793e-05
2012-12-28 | 513:48056 | SHORT RURAL | Other | 916590 | 4 | 76 | 304 | 0.00018481 | 0.00024317
2012-12-28 | ZN2602:PA21 | URBAN | Equipment Failure | 916629 | 1 | 165.2 | 165.2 | 0.00010043 | 6.0793e-05
2012-12-28 | ZN1673:PA1 | URBAN | Equipment Failure | 916683 | 19 | 82 | 1330 | 0.00080855 | 0.0011551
2012-12-28 | ZN847:PA15 | URBAN | Equipment Failure | 916683 | 1238 | 82 | 90836 | 0.055222 | 0.075262
2012-12-28 | 504:48032 | URBAN | Equipment Failure | 916688 | 572 | 1437 | 84960 | 0.05165 | 0.034774
2012-12-28 | 801:74121 | SHORT RURAL | Other | 916707 | 1 | 26 | 26 | 1.5806e-05 | 6.0793e-05
2012-12-28 | ZN690:PA3 | URBAN | Vegetation | 916710 | 33 | 138.15 | 4558.95 | 0.0027715 | 0.0020062
2012-12-28 | ZN12580:PA4 | URBAN | Vegetation | 916711 | 71 | 150 | 10650 | 0.0064745 | 0.0043163
2012-12-28 | ZN12570:PA22 | URBAN | Equipment Failure | 916715 | 63 | 69 | 4347 | 0.0026427 | 0.00383
2012-12-28 | 232:33411 | SHORT RURAL | Other | 916721 | 97 | 162.7833 | 12380.2833 | 0.0075264 | 0.005897
2012-12-28 | ZN2310:PA27 | URBAN | Other | 916728 | 82 | 96.4333 | 7907.5333 | 0.0048073 | 0.0049851
2012-12-28 | 523:33508 | SHORT RURAL | Third Party Impacts | 916748 | 1 | 106.2833 | 106.2833 | 6.4613e-05 | 6.0793e-05
2012-12-28 | ZN10997:PA12 | URBAN | Vegetation | 916753 | 1 | 608.6167 | 608.6167 | 0.00037 | 6.0793e-05
2012-12-28 | ZN35600:PA22 | URBAN | Equipment Failure | 916755 | 51 | 30 | 1530 | 0.00093014 | 0.0031005
2012-12-28 | ZN965:PA2 | URBAN | Vegetation | 916760 | 1 | 473.4833 | 473.4833 | 0.00028785 | 6.0793e-05
2012-12-28 | ZN7481:PA17 | URBAN | Other | 916764 | 96 | 92 | 8832 | 0.0053693 | 0.0058362
2012-12-28 | ZN1673:PA13 | URBAN | Other | 916765 | 31 | 183.8833 | 5700.3833 | 0.0034655 | 0.0018846
2012-12-28 | ZN965:PA3 | URBAN | Vegetation | 916775 | 18 | 104 | 1872 | 0.0011381 | 0.0010943
2012-12-28 | ZN129:PA19 | URBAN | Vegetation | 916783 | 1 | 348.5333 | 348.5333 | 0.00021188 | 6.0793e-05
2012-12-28 | ZN72:PA14 | URBAN | Other | 916789 | 1 | 111.9667 | 111.9667 | 6.8068e-05 | 6.0793e-05
2012-12-28 | 813:89055 | SHORT RURAL | Other | 916795 | 1 | 85 | 85 | 5.1674e-05 | 6.0793e-05
2012-12-28 | ZN3922:PA10 | URBAN | Other | 916801 | 31 | 79 | 2449 | 0.0014888 | 0.0018846
2012-12-28 | ZN1287:PA11 | URBAN | Equipment Failure | 916804 | 1 | 217.0167 | 217.0167 | 0.00013193 | 6.0793e-05
2012-12-28 | ZN72:PA34 | URBAN | Other | 916808 | 1 | 48.85 | 48.85 | 2.9698e-05 | 6.0793e-05
2012-12-28 | 222:2018 | URBAN | Equipment Failure | 916809 | 1 | 158.7333 | 158.7333 | 9.6499e-05 | 6.0793e-05
2012-12-28 | ZN9700:PA15 | URBAN | Other | 916810 | 40 | 79.85 | 3194 | 0.0019417 | 0.0024317
2012-12-28 | ZN10999:PA10 | URBAN | Other | 916811 | 1 | 255.0167 | 255.0167 | 0.00015503 | 6.0793e-05
2012-12-28 | 232:11460 | URBAN | Equipment Failure | 916814 | 1641 | 86 | 105752 | 0.06429 | 0.099762
2012-12-28 | 227:13020 | SHORT RURAL | Other | 916827 | 1 | 204.0667 | 204.0667 | 0.00012406 | 6.0793e-05
2012-12-28 | 264:81240 | SHORT RURAL | Other | 916828 | 1 | 173.8333 | 173.8333 | 0.00010568 | 6.0793e-05
2012-12-28 | ZN9252:PA9 | URBAN | Vegetation | 916831 | 1 | 142.05 | 142.05 | 8.6357e-05 | 6.0793e-05
2012-12-28 | 238:34141 | SHORT RURAL | Equipment Failure | 916833 | 14 | 207 | 2898 | 0.0017618 | 0.00085111
2012-12-28 | 510:48164 | SHORT RURAL | Other | 916836 | 1 | 242.7 | 242.7 | 0.00014755 | 6.0793e-05
2012-12-28 | 510:48164 | SHORT RURAL | Weather | 916839 | 14 | 210 | 2940 | 0.0017873 | 0.00085111
2012-12-28 | ZN12610:PA22 | URBAN | Other | 916846 | 1 | 13.9167 | 13.9167 | 8.4604e-06 | 6.0793e-05
2012-12-28 | ZN12660:PA8 | URBAN | Vegetation | 916876 | 1 | 171.5333 | 171.5333 | 0.00010428 | 6.0793e-05
2012-12-28 | ZN9245:PA10 | URBAN | Vegetation | 916878 | 1 | 143.4 | 143.4 | 8.7178e-05 | 6.0793e-05
2012-12-28 | 514:18137 | SHORT RURAL | Other | 916884 | 50 | 52 | 2536 | 0.0015417 | 0.0030397
2012-12-28 | ZN4545:PA6 | URBAN | Equipment Failure | 916887 | 1 | 121.0167 | 121.0167 | 7.357e-05 | 6.0793e-05
2012-12-28 | ZN12650:PA1 | SHORT RURAL | Vegetation | 916899 | 1 | 955.9167 | 955.9167 | 0.00058113 | 6.0793e-05
2012-12-28 | 214:8667 | URBAN | Other | 916910 | 1 | 86.2667 | 86.2667 | 5.2444e-05 | 6.0793e-05
2012-12-29 | 210:8676 | URBAN | Other | 916919 | 122 | 30 | 3660 | 0.002225 | 0.0074168
2012-12-29 | 243:80084 | SHORT RURAL | Other | 916930 | 1 | 97.2167 | 97.2167 | 5.9101e-05 | 6.0793e-05
2012-12-29 | 232:11453 | SHORT RURAL | Other | 916931 | 1 | 178.4 | 178.4 | 0.00010846 | 6.0793e-05
2012-12-29 | 526:34640 | SHORT RURAL | Other | 916944 | 1 | 75.4 | 75.4 | 4.5838e-05 | 6.0793e-05
2012-12-29 | 813:89062 | SHORT RURAL | Animals | 916954 | 1 | 140.4667 | 140.4667 | 8.5394e-05 | 6.0793e-05
2012-12-29 | ZN2196:PA10 | URBAN | Equipment Failure | 916963 | 10 | 126 | 1260 | 0.000766 | 0.00060793
2012-12-29 | ZN2196:PA17 | URBAN | Equipment Failure | 916963 | 6 | 126 | 756 | 0.0004596 | 0.00036476
2012-12-29 | ZN12610:PA11 | URBAN | Other | 916968 | 1 | 458.2667 | 458.2667 | 0.0002786 | 6.0793e-05
2012-12-29 | ZN15008:PA5 | URBAN | Other | 916970 | 1 | 93.65 | 93.65 | 5.6933e-05 | 6.0793e-05
2012-12-29 | 227:13020 | SHORT RURAL | Other | 916972 | 1 | 207.5333 | 207.5333 | 0.00012617 | 6.0793e-05
2012-12-29 | 813:89055 | SHORT RURAL | Other | 916974 | 1 | 153 | 153 | 9.3014e-05 | 6.0793e-05
2012-12-29 | ZN9245:PA10 | URBAN | Vegetation | 916982 | 1 | 217.5333 | 217.5333 | 0.00013225 | 6.0793e-05
2012-12-29 | 243:80083 | SHORT RURAL | Other | 916985 | 1 | 1187 | 1187 | 0.00072162 | 6.0793e-05
2012-12-29 | 510:48164 | SHORT RURAL | Other | 917000 | 1 | 128.4 | 128.4 | 7.8059e-05 | 6.0793e-05
2012-12-29 | 208:58 | URBAN | Other | 917006 | 1 | 55.0667 | 55.0667 | 3.3477e-05 | 6.0793e-05
2012-12-29 | 515:35197 | LONG RURAL | Animals | 917024 | 2 | 60 | 120 | 7.2952e-05 | 0.00012159
2012-12-29 | 229:34983 | SHORT RURAL | Equipment Failure | 917029 | 48 | 65.6833 | 3018.4667 | 0.001835 | 0.0029181
2012-12-30 | ZN1193:PA7 | URBAN | Other | 917047 | 1 | 279.2833 | 279.2833 | 0.00016979 | 6.0793e-05
2012-12-30 | ZN9550:PA43 | URBAN | Equipment Failure | 917049 | 29 | 101.75 | 2950.75 | 0.0017939 | 0.001763
2012-12-30 | ZN2635:PA16 | URBAN | Other | 917050 | 1 | 327.4167 | 327.4167 | 0.00019905 | 6.0793e-05
2012-12-30 | ZN1290:PA1 | URBAN | Equipment Failure | 917055 | 33 | 90 | 2970 | 0.0018056 | 0.0020062
2012-12-30 | ZN2602:PA30 | URBAN | Equipment Failure | 917065 | 1 | 42.1833 | 42.1833 | 2.5645e-05 | 6.0793e-05
2012-12-30 | ZN2602:PA30 | URBAN | Equipment Failure | 917067 | 1 | 30.85 | 30.85 | 1.8755e-05 | 6.0793e-05
2012-12-30 | ZN262:PA40 | URBAN | Other | 917071 | 1 | 276.45 | 276.45 | 0.00016806 | 6.0793e-05
2012-12-30 | ZN2602:PA30 | URBAN | Equipment Failure | 917076 | 1 | 3.7 | 3.7 | 2.2494e-06 | 6.0793e-05
2012-12-30 | ZN12570:PA24 | SHORT RURAL | Vegetation | 917081 | 25 | 225.6833 | 5642.0833 | 0.00343 | 0.0015198
2012-12-30 | ZN874:PA25 | URBAN | Other | 917090 | 1 | 285 | 285 | 0.00017326 | 6.0793e-05
2012-12-30 | ZN9118:PA11 | URBAN | Vegetation | 917094 | 1 | 339.1167 | 339.1167 | 0.00020616 | 6.0793e-05
2012-12-30 | ZN262:PA42 | URBAN | Equipment Failure | 917098 | 1 | 320 | 320 | 0.00019454 | 6.0793e-05
2012-12-30 | ZN262:PA42 | URBAN | Equipment Failure | 917099 | 1 | 339.7667 | 339.7667 | 0.00020656 | 6.0793e-05
2012-12-30 | 230:81440 | URBAN | Other | 917107 | 1 | 103.0167 | 103.0167 | 6.2627e-05 | 6.0793e-05
2012-12-30 | 227:13018 | URBAN | Other | 917114 | 15 | 47.6167 | 714.25 | 0.00043422 | 0.0009119
2012-12-30 | 512:48049 | SHORT RURAL | Vegetation | 917122 | 910 | 261 | 94914 | 0.057701 | 0.055322
2012-12-30 | 511:29878 | SHORT RURAL | Other | 917135 | 2 | 80 | 160 | 9.7269e-05 | 0.00012159
2012-12-30 | 807:74184 | SHORT RURAL | Other | 917146 | 1 | 117.2833 | 117.2833 | 7.13e-05 | 6.0793e-05
2012-12-30 | 514:18137 | SHORT RURAL | Weather | 917151 | 50 | 143 | 3718 | 0.0022603 | 0.0030397
2012-12-30 | 503:48078 | URBAN | Other | 917155 | 1 | 141.2333 | 141.2333 | 8.586e-05 | 6.0793e-05
2012-12-30 | 227:13020 | SHORT RURAL | Equipment Failure | 917166 | 1731 | 549 | 124646 | 0.075776 | 0.10523
2012-12-30 | 243:80081 | URBAN | Other | 917169 | 1 | 624.3667 | 624.3667 | 0.00037957 | 6.0793e-05
2012-12-31 | ZN630:PA8 | URBAN | Other | 917190 | 91 | 142 | 12922 | 0.0078557 | 0.0055322
2012-12-31 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 917202 | 94 | 394 | 7622 | 0.0046337 | 0.0057146
2012-12-31 | 514:18137 | SHORT RURAL | Weather | 917221 | 6 | 51.25 | 307.5 | 0.00018694 | 0.00036476
2012-12-31 | ZN630:PA38 | URBAN | Equipment Failure | 917276 | 1 | 192.5167 | 192.5167 | 0.00011704 | 6.0793e-05
2012-12-31 | ZN12640:PA19 | URBAN | Other | 917301 | 1 | 231.65 | 231.65 | 0.00014083 | 6.0793e-05
2012-12-31 | ZN9550:PA11 | URBAN | Third Party Impacts | 917311 | 1 | 219.2333 | 219.2333 | 0.00013328 | 6.0793e-05
2012-12-31 | 242:81539 | URBAN | Other | 917313 | 113 | 102.4833 | 11580.6167 | 0.0070402 | 0.0068696
2012-12-31 | 810:74054 | LONG RURAL | Other | 917325 | 1 | 92.6167 | 92.6167 | 5.6305e-05 | 6.0793e-05
2012-12-31 | 511:29878 | SHORT RURAL | Other | 917351 | 1 | 121.45 | 121.45 | 7.3833e-05 | 6.0793e-05
2012-12-31 | 258:80785 | URBAN | Other | 917370 | 1 | 26.6833 | 26.6833 | 1.6222e-05 | 6.0793e-05
2012-12-31 | 230:81434 | URBAN | Other | 917393 | 1 | 152.25 | 152.25 | 9.2558e-05 | 6.0793e-05
2012-12-31 | 802:82225 | SHORT RURAL | Other | 917395 | 1 | 158.1667 | 158.1667 | 9.6155e-05 | 6.0793e-05
2012-12-31 | 230:81434 | URBAN | Other | 917397 | 1 | 148.7667 | 148.7667 | 9.044e-05 | 6.0793e-05
2012-12-31 | 503:48017 | URBAN | Vegetation | 917401 | 78 | 30 | 2340 | 0.0014226 | 0.0047419
2012-12-31 | ZN80:PA40 | URBAN | Other | 917406 | 1 | 61.65 | 61.65 | 3.7479e-05 | 6.0793e-05
2012-12-31 | 806:74080 | SHORT RURAL | Equipment Failure | 917413 | 231 | 1107 | 35879 | 0.021812 | 0.014043
2012-12-31 | 507:80925 | SHORT RURAL | Other | 917435 | 1 | 92.1 | 92.1 | 5.5991e-05 | 6.0793e-05
2012-12-31 | 225:33670 | SHORT RURAL | Other | 917447 | 1 | 74.6833 | 74.6833 | 4.5402e-05 | 6.0793e-05
2012-12-31 | ZN15002:PA2 | SHORT RURAL | Vegetation | 917455 | 31 | 109.25 | 3386.75 | 0.0020589 | 0.0018846
2013-01-01 | ZN3472:PA12 | URBAN | Other | 917466 | 46 | 94 | 4324 | 0.0026278 | 0.0027955
2013-01-01 | 814:82283 | SHORT RURAL | Other | 917472 | 3 | 150 | 450 | 0.00027347 | 0.00018231
2013-01-01 | ZN262:PA31 | URBAN | Other | 917487 | 1 | 213 | 213 | 0.00012944 | 6.0772e-05
2013-01-01 | 220:8687 | URBAN | Other | 917489 | 1 | 102.1 | 102.1 | 6.2048e-05 | 6.0772e-05
2013-01-01 | 260:33347 | SHORT RURAL | Vegetation | 917498 | 1 | 103.45 | 103.45 | 6.2868e-05 | 6.0772e-05
2013-01-01 | 524:33580 | SHORT RURAL | Equipment Failure | 917506 | 25 | 215.2 | 5380 | 0.0032695 | 0.0015193
2013-01-01 | 240:34835 | URBAN | Equipment Failure | 917514 | 1 | 47.9833 | 47.9833 | 2.916e-05 | 6.0772e-05
2013-01-01 | 803:74016 | SHORT RURAL | Other | 917521 | 5 | 184.1667 | 920.8333 | 0.0005596 | 0.00030386
2013-01-01 | 216:10727 | URBAN | Equipment Failure | 917522 | 1 | 53.6833 | 53.6833 | 3.2624e-05 | 6.0772e-05
2013-01-01 | 513:48051 | URBAN | Vegetation | 917524 | 1214 | 97 | 44253 | 0.026893 | 0.073777
2013-01-01 | ZN35370:PA8 | SHORT RURAL | Vegetation | 917536 | 1 | 269.6167 | 269.6167 | 0.00016385 | 6.0772e-05
2013-01-01 | ZN13000:PA11 | URBAN | Vegetation | 917540 | 1 | 278.8 | 278.8 | 0.00016943 | 6.0772e-05
2013-01-01 | ZN9550:PA29 | URBAN | Vegetation | 917542 | 113 | 206.6667 | 23353.3333 | 0.014192 | 0.0068672
2013-01-01 | ZN2196:PA21 | URBAN | Other | 917546 | 80 | 106.85 | 8548 | 0.0051948 | 0.0048617
2013-01-01 | 813:89061 | LONG RURAL | Equipment Failure | 917553 | 24 | 1042 | 9315 | 0.0056609 | 0.0014585
2013-01-01 | 238:34140 | URBAN | Equipment Failure | 917576 | 39 | 54.7167 | 2133.95 | 0.0012968 | 0.0023701
2013-01-01 | ZN129:PA24 | URBAN | Equipment Failure | 917583 | 1219 | 132 | 103740 | 0.063044 | 0.074081
2013-01-01 | ZN129:PA9 | URBAN | Equipment Failure | 917583 | 1 | 132 | 125.2833 | 7.6137e-05 | 6.0772e-05
2013-01-02 | 235:2124 | URBAN | Equipment Failure | 917590 | 935 | 130 | 121550 | 0.073868 | 0.056821
2013-01-02 | 514:18137 | SHORT RURAL | Other | 917598 | 1 | 284.7333 | 284.7333 | 0.00017304 | 6.0772e-05
2013-01-02 | ZN9118:PA12 | URBAN | Equipment Failure | 917599 | 32 | 83.7333 | 2679.4667 | 0.0016284 | 0.0019447
2013-01-02 | 232:11453 | SHORT RURAL | Other | 917606 | 1 | 17.7833 | 17.7833 | 1.0807e-05 | 6.0772e-05
2013-01-02 | 803:74007 | SHORT RURAL | Weather | 917620 | 1 | 160.4 | 160.4 | 9.7478e-05 | 6.0772e-05
2013-01-02 | ZN3472:PA17 | URBAN | Equipment Failure | 917621 | 1 | 194.8167 | 194.8167 | 0.00011839 | 6.0772e-05
2012-12-25 | 512:48049 | SHORT RURAL | Equipment Failure | 917635 | 2 | 400 | 800 | 0.00048636 | 0.00012159
2012-12-25 | 515:35192 | SHORT RURAL | Other | 917639 | 1 | 458 | 458 | 0.00027844 | 6.0795e-05
2013-01-02 | ZN1850:PA12 | URBAN | Equipment Failure | 917646 | 38 | 61 | 2318 | 0.0014087 | 0.0023093
2013-01-02 | ZN1850:PA13 | URBAN | Equipment Failure | 917646 | 1249 | 61 | 76189 | 0.046301 | 0.075904
2013-01-02 | 524:33578 | URBAN | Other | 917672 | 1 | 67.9167 | 67.9167 | 4.1274e-05 | 6.0772e-05
2013-01-02 | ZN13000:PA5 | SHORT RURAL | Other | 917737 | 1 | 147.3167 | 147.3167 | 8.9527e-05 | 6.0772e-05
2013-01-02 | ZN12630:PA1 | SHORT RURAL | Equipment Failure | 917740 | 1 | 457.1167 | 457.1167 | 0.0002778 | 6.0772e-05
2012-12-26 | 810:74054 | LONG RURAL | Other | 917769 | 1 | 154 | 154 | 9.3624e-05 | 6.0795e-05
2013-01-02 | 801:74122 | URBAN | Equipment Failure | 917789 | 1 | 79.6667 | 79.6667 | 4.8415e-05 | 6.0772e-05
2012-12-30 | ZN2310:PA22 | URBAN | Other | 917805 | 42 | 110 | 4620 | 0.0028087 | 0.0025533
2012-12-30 | ZN2310:PA22 | URBAN | Equipment Failure | 917807 | 42 | 12 | 504 | 0.0003064 | 0.0025533
2013-01-02 | 502:48010 | SHORT RURAL | Other | 917814 | 1 | 182.6833 | 182.6833 | 0.00011102 | 6.0772e-05
2013-01-02 | ZN9035:PA4 | URBAN | Vegetation | 917834 | 1 | 50.4667 | 50.4667 | 3.0669e-05 | 6.0772e-05
2013-01-02 | 232:11457 | URBAN | Other | 917838 | 1 | 114.45 | 114.45 | 6.9553e-05 | 6.0772e-05
2013-01-02 | 524:33578 | URBAN | Equipment Failure | 917839 | 1 | 112.1 | 112.1 | 6.8125e-05 | 6.0772e-05
2013-01-02 | 216:10724 | SHORT RURAL | Vegetation | 917840 | 1 | 42.0167 | 42.0167 | 2.5534e-05 | 6.0772e-05
2013-01-02 | ZN12660:PA6 | SHORT RURAL | Other | 917876 | 1 | 83.9333 | 83.9333 | 5.1008e-05 | 6.0772e-05
2013-01-02 | 264:81240 | SHORT RURAL | Other | 917902 | 1 | 109.9333 | 109.9333 | 6.6808e-05 | 6.0772e-05
2013-01-02 | ZN2196:PA21 | URBAN | Equipment Failure | 917904 | 80 | 123.7167 | 9897.3333 | 0.0060148 | 0.0048617
2013-01-02 | 813:89055 | SHORT RURAL | Vegetation | 917906 | 1 | 83.75 | 83.75 | 5.0896e-05 | 6.0772e-05
2013-01-02 | 507:80922 | SHORT RURAL | Equipment Failure | 917910 | 8 | 490 | 3920 | 0.0023822 | 0.00048617
2013-01-02 | ZN2196:PA21 | URBAN | Equipment Failure | 917920 | 80 | 107.25 | 8580 | 0.0052142 | 0.0048617
2013-01-02 | ZN1850:PA13 | URBAN | Other | 917926 | 1 | 286.55 | 286.55 | 0.00017414 | 6.0772e-05
2013-01-02 | ZN3672:PA44 | URBAN | Other | 917927 | 32 | 127 | 4064 | 0.0024698 | 0.0019447
2013-01-03 | 503:48016 | URBAN | Equipment Failure | 917929 | 2 | 85.75 | 171.5 | 0.00010422 | 0.00012154
2013-01-03 | 812:19066 | SHORT RURAL | Other | 917931 | 1 | 47.4333 | 47.4333 | 2.8826e-05 | 6.0772e-05
2012-12-27 | 501:48122 | SHORT RURAL | Equipment Failure | 917941 | 2 | 55 | 110 | 6.6874e-05 | 0.00012159
2013-01-03 | 523:33501 | SHORT RURAL | Animals | 917942 | 1 | 80.7833 | 80.7833 | 4.9093e-05 | 6.0772e-05
2012-12-27 | 807:74184 | SHORT RURAL | Other | 917965 | 1 | 30 | 30 | 1.8238e-05 | 6.0795e-05
2013-01-03 | 232:11457 | URBAN | Third Party Impacts | 917969 | 1 | 60 | 60 | 3.6463e-05 | 6.0772e-05
2013-01-03 | ZN12580:PA14 | URBAN | Equipment Failure | 917988 | 1 | 209.5 | 209.5 | 0.00012732 | 6.0772e-05
2013-01-03 | ZN12630:PA2 | SHORT RURAL | Other | 918071 | 1 | 290.4833 | 290.4833 | 0.00017653 | 6.0772e-05
2013-01-03 | 523:33508 | SHORT RURAL | Equipment Failure | 918150 | 4 | 115 | 460 | 0.00027955 | 0.00024309
2013-01-02 | 803:74007 | SHORT RURAL | Other | 918164 | 1 | 30 | 30 | 1.8231e-05 | 6.0772e-05
2013-01-03 | ZN180:PA41 | URBAN | Vegetation | 918167 | 1 | 91.5833 | 91.5833 | 5.5657e-05 | 6.0772e-05
2013-01-02 | 512:48049 | SHORT RURAL | Other | 918174 | 2 | 115 | 230 | 0.00013977 | 0.00012154
2013-01-03 | 507:80922 | SHORT RURAL | Other | 918190 | 1 | 137.6 | 137.6 | 8.3622e-05 | 6.0772e-05
2013-01-04 | ZN1290:PA9 | URBAN | Equipment Failure | 918232 | 70 | 112 | 6460 | 0.0039259 | 0.004254
2013-01-04 | ZN12660:PA10 | SHORT RURAL | Vegetation | 918237 | 19 | 147.2833 | 2798.3833 | 0.0017006 | 0.0011547
2012-12-28 | 513:48059 | SHORT RURAL | Equipment Failure | 918249 | 232 | 221 | 22411 | 0.013624 | 0.014104
2013-01-04 | 202:34245 | URBAN | Other | 918283 | 1 | 57 | 57 | 3.464e-05 | 6.0772e-05
2013-01-04 | ZN1673:PA19 | URBAN | Other | 918286 | 47 | 49 | 2280 | 0.0013856 | 0.0028563
2013-01-04 | 807:74179 | SHORT RURAL | Equipment Failure | 918333 | 1 | 161.8667 | 161.8667 | 9.8369e-05 | 6.0772e-05
2013-01-04 | 242:81535 | URBAN | Equipment Failure | 918381 | 1 | 468.15 | 468.15 | 0.0002845 | 6.0772e-05
2013-01-04 | ZN10999:PA28 | URBAN | Equipment Failure | 918386 | 15 | 162.35 | 2435.25 | 0.0014799 | 0.00091158
2013-01-04 | ZN15014:PA14 | SHORT RURAL | Other | 918423 | 1 | 127.2333 | 127.2333 | 7.7322e-05 | 6.0772e-05
2013-01-04 | ZN14144:PA1 | URBAN | Vegetation | 918432 | 1 | 267.85 | 267.85 | 0.00016278 | 6.0772e-05
2013-01-04 | ZN10999:PA1 | URBAN | Equipment Failure | 918447 | 59 | 101.85 | 6009.15 | 0.0036519 | 0.0035855
2013-01-04 | 232:11454 | SHORT RURAL | Equipment Failure | 918461 | 22 | 86.2167 | 1896.7667 | 0.0011527 | 0.001337
2013-01-04 | 507:80932 | SHORT RURAL | Equipment Failure | 918476 | 4 | 79 | 316 | 0.00019204 | 0.00024309
2013-01-04 | 503:48017 | URBAN | Vegetation | 918487 | 50 | 170 | 8500 | 0.0051656 | 0.0030386
2013-01-04 | 238:34144 | URBAN | Other | 918504 | 1 | 230.9667 | 230.9667 | 0.00014036 | 6.0772e-05
2013-01-04 | 520:48172 | SHORT RURAL | Other | 918506 | 1 | 152 | 152 | 9.2373e-05 | 6.0772e-05
2013-01-04 | 810:74054 | LONG RURAL | Equipment Failure | 918530 | 1 | 193.95 | 193.95 | 0.00011787 | 6.0772e-05
2013-01-04 | ZN12570:PA29 | SHORT RURAL | Vegetation | 918532 | 35 | 145.25 | 5083.75 | 0.0030895 | 0.002127
2013-01-05 | ZN1193:PA26 | URBAN | Vegetation | 918540 | 48 | 72 | 3456 | 0.0021003 | 0.002917
2013-01-04 | ZN15005:PA4 | URBAN | Equipment Failure | 918541 | 80 | 65.3667 | 5229.3333 | 0.003178 | 0.0048617
2013-01-04 | 231:8415 | SHORT RURAL | Animals | 918547 | 815 | 50 | 40750 | 0.024764 | 0.049529
2013-01-05 | 520:48172 | SHORT RURAL | Equipment Failure | 918560 | 1 | 41 | 41 | 2.4916e-05 | 6.0772e-05
2013-01-05 | 516:48065 | SHORT RURAL | Other | 918565 | 1 | 380 | 380 | 0.00023093 | 6.0772e-05
2013-01-05 | ZN10990:PA2 | URBAN | Equipment Failure | 918578 | 1 | 223.7667 | 223.7667 | 0.00013599 | 6.0772e-05
2013-01-05 | 229:34983 | SHORT RURAL | Vegetation | 918603 | 1 | 159.85 | 159.85 | 9.7144e-05 | 6.0772e-05
2013-01-05 | ZN14892:PA16 | URBAN | Other | 918609 | 1 | 245.4833 | 245.4833 | 0.00014918 | 6.0772e-05
2013-01-05 | ZN2310:PA11 | URBAN | Equipment Failure | 918613 | 26 | 51 | 1326 | 0.00080583 | 0.0015801
2013-01-05 | ZN2310:PA16 | URBAN | Equipment Failure | 918613 | 975 | 51 | 31200 | 0.018961 | 0.059252
2013-01-05 | ZN1673:PA7 | URBAN | Vegetation | 918614 | 78 | 203 | 15834 | 0.0096226 | 0.0047402
2013-01-05 | ZN12610:PA18 | URBAN | Equipment Failure | 918619 | 64 | 68 | 4352 | 0.0026448 | 0.0038894
2013-01-05 | ZN9118:PA11 | URBAN | Equipment Failure | 918626 | 95 | 85.9833 | 8168.4167 | 0.0049641 | 0.0057733
2013-01-05 | ZN36300:PA3 | URBAN | Other | 918629 | 1 | 120.9333 | 120.9333 | 7.3493e-05 | 6.0772e-05
2013-01-05 | 813:89061 | LONG RURAL | Vegetation | 918642 | 30 | 80 | 2400 | 0.0014585 | 0.0018232
2013-01-05 | ZN180:PA34 | URBAN | Vegetation | 918647 | 6 | 143 | 858 | 0.00052142 | 0.00036463
2013-01-05 | ZN12570:PA37 | SHORT RURAL | Vegetation | 918671 | 1 | 793.7167 | 793.7167 | 0.00048236 | 6.0772e-05
2013-01-06 | ZN12610:PA2 | URBAN | Other | 918675 | 115 | 434 | 49910 | 0.030331 | 0.0069888
2013-01-06 | ZN965:PA8 | URBAN | Other | 918677 | 1 | 452.1 | 452.1 | 0.00027475 | 6.0772e-05
2013-01-06 | ZN13000:PA2 | URBAN | Equipment Failure | 918679 | 10 | 166 | 1660 | 0.0010088 | 0.00060772
2013-01-06 | 243:80083 | SHORT RURAL | Other | 918680 | 4 | 90 | 360 | 0.00021878 | 0.00024309
2013-01-06 | ZN12640:PA2 | URBAN | Equipment Failure | 918693 | 119 | 71 | 8449 | 0.0051346 | 0.0072318
2013-01-06 | ZN12660:PA17 | URBAN | Equipment Failure | 918693 | 5 | 71 | 355 | 0.00021574 | 0.00030386
2013-01-06 | ZN3425:PA27 | URBAN | Other | 918694 | 37 | 40.85 | 1511.45 | 0.00091853 | 0.0022486
2013-01-06 | ZN630:PA34 | URBAN | Equipment Failure | 918696 | 80 | 41 | 3046 | 0.0018511 | 0.0048617
2013-01-06 | ZN72:PA31 | URBAN | Other | 918713 | 68 | 70 | 4697.3 | 0.0028546 | 0.0041325
2013-01-06 | ZN3425:PA27 | URBAN | Equipment Failure | 918720 | 37 | 434.5667 | 16078.9667 | 0.0097715 | 0.0022486
2013-01-06 | ZN3154:PA16 | URBAN | Vegetation | 918723 | 1 | 361.3 | 361.3 | 0.00021957 | 6.0772e-05
2013-01-06 | ZN965:PA26 | URBAN | Vegetation | 918729 | 912 | 60 | 48343 | 0.029379 | 0.055424
2013-01-06 | ZN72:PA31 | URBAN | Equipment Failure | 918742 | 115 | 207 | 23697.65 | 0.014401 | 0.0069888
2013-01-06 | 812:19071 | SHORT RURAL | Other | 918753 | 1 | 107.7 | 107.7 | 6.5451e-05 | 6.0772e-05
2013-01-06 | ZN72:PA22 | URBAN | Equipment Failure | 918761 | 78 | 43 | 3198 | 0.0019435 | 0.0047402
2013-01-06 | ZN72:PA26 | URBAN | Equipment Failure | 918761 | 976 | 43 | 41664 | 0.02532 | 0.059313
2013-01-06 | ZN72:PA31 | URBAN | Equipment Failure | 918761 | 1 | 43 | 43 | 2.6132e-05 | 6.0772e-05
2013-01-06 | 810:74050 | SHORT RURAL | Other | 918773 | 1 | 20 | 20 | 1.2154e-05 | 6.0772e-05
2013-01-06 | ZN10994:PA10 | URBAN | Equipment Failure | 918780 | 12 | 187.9167 | 2255 | 0.0013704 | 0.00072926
2013-01-06 | ZN398:PA26 | URBAN | Other | 918782 | 123 | 216.7333 | 26658.2 | 0.016201 | 0.0074749
2013-01-06 | 503:48017 | URBAN | Other | 918785 | 1 | 179.9 | 179.9 | 0.00010933 | 6.0772e-05
2013-01-06 | ZN9118:PA16 | URBAN | Equipment Failure | 918786 | 1 | 748.7667 | 748.7667 | 0.00045504 | 6.0772e-05
2013-01-06 | 214:8669 | URBAN | Animals | 918803 | 65 | 178 | 11570 | 0.0070313 | 0.0039502
2013-01-06 | ZN14143:PA17 | SHORT RURAL | Equipment Failure | 918808 | 1 | 187.1333 | 187.1333 | 0.00011372 | 6.0772e-05
2013-01-07 | 811:74234 | SHORT RURAL | Equipment Failure | 918818 | 255 | 113 | 26739 | 0.01625 | 0.015497
2013-01-07 | ZN1788:PA8 | URBAN | Third Party Impacts | 918823 | 1 | 199.7333 | 199.7333 | 0.00012138 | 6.0772e-05
2013-01-07 | 520:48172 | SHORT RURAL | Other | 918833 | 1 | 64.2333 | 64.2333 | 3.9036e-05 | 6.0772e-05
2013-01-07 | 512:48046 | SHORT RURAL | Equipment Failure | 918852 | 1 | 135.5 | 135.5 | 8.2346e-05 | 6.0772e-05
2013-01-07 | ZN15002:PA6 | URBAN | Other | 918872 | 1 | 104 | 104 | 6.3203e-05 | 6.0772e-05
2013-01-07 | ZN12660:PA14 | SHORT RURAL | Other | 918887 | 1 | 66.05 | 66.05 | 4.014e-05 | 6.0772e-05
2013-01-07 | 807:74184 | SHORT RURAL | Equipment Failure | 918894 | 1 | 167.1 | 167.1 | 0.00010155 | 6.0772e-05
2013-01-02 | ZN1850:PA13 | URBAN | Other | 918897 | 56 | 57 | 3192 | 0.0019398 | 0.0034032
2013-01-07 | ZN188:PA15 | URBAN | Vegetation | 918933 | 62 | 11.7333 | 727.4667 | 0.00044209 | 0.0037678
2013-01-07 | ZN3155:PA17 | URBAN | Equipment Failure | 918943 | 85 | 1005.05 | 85429.25 | 0.051917 | 0.0051656
2013-01-07 | ZN10994:PA12 | URBAN | Equipment Failure | 918965 | 1 | 459.6833 | 459.6833 | 0.00027936 | 6.0772e-05
2013-01-07 | 502:48010 | SHORT RURAL | Equipment Failure | 919034 | 1 | 211.3 | 211.3 | 0.00012841 | 6.0772e-05
2013-01-07 | 516:48067 | SHORT RURAL | Equipment Failure | 919079 | 1 | 160 | 160 | 9.7235e-05 | 6.0772e-05
2012-09-26 | 240:34843 | URBAN | Equipment Failure | 919092 | 256 | 68 | 14004 | 0.0085348 | 0.015602
2013-01-07 | 256:80650 | URBAN | Other | 919106 | 1 | 288.0333 | 288.0333 | 0.00017504 | 6.0772e-05
2013-01-07 | ZN1287:PA5 | URBAN | Other | 919108 | 1 | 202.3667 | 202.3667 | 0.00012298 | 6.0772e-05
2013-01-07 | ZN8000:PA19 | URBAN | Other | 919167 | 42 | 130.95 | 5499.9 | 0.0033424 | 0.0025524
2013-01-07 | ZN9700:PA24 | URBAN | Vegetation | 919185 | 1 | 257.6667 | 257.6667 | 0.00015659 | 6.0772e-05
2013-01-07 | ZN35600:PA9 | URBAN | Other | 919191 | 1 | 458.9167 | 458.9167 | 0.00027889 | 6.0772e-05
2013-01-07 | ZN3155:PA22 | URBAN | Equipment Failure | 919198 | 28 | 180 | 5040 | 0.0030629 | 0.0017016
2013-01-08 | 219:1740 | SHORT RURAL | Animals | 919213 | 135 | 86.8 | 11718 | 0.0071214 | 0.0082043
2013-01-08 | 507:80926 | URBAN | Third Party Impacts | 919218 | 44 | 239 | 10516 | 0.0063909 | 0.002674
2013-01-08 | ZN35370:PA8 | SHORT RURAL | Animals | 919220 | 26 | 290 | 7540 | 0.0045823 | 0.0015801
2013-01-08 | ZN12620:PA3 | URBAN | Equipment Failure | 919221 | 1050 | 99 | 87464 | 0.053154 | 0.063812
2013-01-08 | 807:74184 | SHORT RURAL | Vegetation | 919227 | 59 | 281 | 15219 | 0.009249 | 0.0035856
2013-01-08 | 227:13019 | SHORT RURAL | Vegetation | 919229 | 120 | 183 | 21800 | 0.013249 | 0.0072928
2013-01-08 | ZN12630:PA1 | SHORT RURAL | Third Party Impacts | 919242 | 1 | 270.9833 | 270.9833 | 0.00016468 | 6.0773e-05
2013-01-08 | 216:10727 | URBAN | Vegetation | 919244 | 1 | 35.8167 | 35.8167 | 2.1767e-05 | 6.0773e-05
2013-01-04 | 513:48059 | SHORT RURAL | Equipment Failure | 919269 | 1 | 60 | 60 | 3.6463e-05 | 6.0772e-05
2013-01-08 | ZN630:PA27 | URBAN | Equipment Failure | 919285 | 243 | 131 | 19929 | 0.012111 | 0.014768
2013-01-08 | ZN630:PA41 | URBAN | Equipment Failure | 919285 | 72 | 131 | 5832 | 0.0035443 | 0.0043757
2013-01-08 | ZN12610:PA22 | URBAN | Equipment Failure | 919337 | 34 | 152.3333 | 3206.7667 | 0.0019488 | 0.0020663
2013-01-08 | ZN12610:PA6 | URBAN | Equipment Failure | 919337 | 1 | 152.3333 | 131.0667 | 7.9653e-05 | 6.0773e-05
2013-01-07 | ZN2310:PA37 | URBAN | Animals | 919345 | 157 | 2 | 314 | 0.00019082 | 0.0095412
2013-01-08 | ZN14144:PA10 | SHORT RURAL | Vegetation | 919353 | 94 | 131 | 3878 | 0.0023568 | 0.0057127
2013-01-08 | ZN10999:PA17 | URBAN | Equipment Failure | 919396 | 1537 | 190 | 132148 | 0.08031 | 0.093408
2013-01-08 | 264:81236 | URBAN | Vegetation | 919432 | 1 | 231.7833 | 231.7833 | 0.00014086 | 6.0773e-05
2013-01-08 | ZN15010:PA11 | URBAN | Vegetation | 919445 | 1 | 138.5333 | 138.5333 | 8.4191e-05 | 6.0773e-05
2013-01-08 | ZN9900:PA1 | URBAN | Equipment Failure | 919446 | 2254 | 1171 | 139588 | 0.084832 | 0.13698
2013-01-08 | 240:34843 | URBAN | Equipment Failure | 919449 | 1 | 95.7667 | 95.7667 | 5.82e-05 | 6.0773e-05
2013-01-08 | 512:48046 | SHORT RURAL | Other | 919451 | 2 | 76 | 152 | 9.2375e-05 | 0.00012155
2013-01-08 | ZN965:PA21 | URBAN | Vegetation | 919459 | 1 | 237 | 237 | 0.00014403 | 6.0773e-05
2013-01-08 | ZN15008:PA9 | URBAN | Other | 919468 | 2100 | 103 | 72940 | 0.044328 | 0.12762
2013-01-08 | ZN3154:PA10 | URBAN | Vegetation | 919483 | 39 | 76.6333 | 2988.7 | 0.0018163 | 0.0023701
2013-01-08 | 217:33612 | URBAN | Other | 919489 | 30 | 91.7 | 2751 | 0.0016719 | 0.0018232
2013-01-08 | 217:33612 | URBAN | Other | 919491 | 1 | 90.1833 | 90.1833 | 5.4807e-05 | 6.0773e-05
2013-01-08 | ZN12610:PA18 | URBAN | Equipment Failure | 919505 | 1119 | 193 | 167670 | 0.1019 | 0.068005
2013-01-08 | ZN14144:PA7 | SHORT RURAL | Equipment Failure | 919505 | 1 | 193 | 168 | 0.0001021 | 6.0773e-05
2013-01-08 | ZN10996:PA19 | URBAN | Equipment Failure | 919508 | 681 | 77 | 36437 | 0.022144 | 0.041386
2013-01-08 | ZN10999:PA11 | URBAN | Equipment Failure | 919508 | 2 | 77 | 104 | 6.3204e-05 | 0.00012155
2013-01-08 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 919512 | 16 | 332 | 5312 | 0.0032283 | 0.00097237
2013-01-08 | ZN80:PA22 | URBAN | Other | 919514 | 25 | 138 | 3450 | 0.0020967 | 0.0015193
2013-01-08 | ZN36300:PA19 | URBAN | Equipment Failure | 919515 | 1899 | 450 | 190764.1 | 0.11593 | 0.11541
2013-01-08 | 501:48116 | URBAN | Other | 919519 | 35 | 78.4167 | 2744.5833 | 0.001668 | 0.0021271
2013-01-08 | ZN9550:PA36 | URBAN | Equipment Failure | 919527 | 74 | 253.4667 | 18756.5333 | 0.011399 | 0.0044972
2013-01-08 | ZN9035:PA1 | URBAN | Equipment Failure | 919532 | 468 | 292 | 48425 | 0.029429 | 0.028442
2013-01-08 | ZN9118:PA26 | URBAN | Equipment Failure | 919532 | 2 | 292 | 230 | 0.00013978 | 0.00012155
2013-01-08 | ZN9118:PA7 | URBAN | Equipment Failure | 919532 | 96 | 292 | 28032 | 0.017036 | 0.0058342
2013-01-08 | ZN9550:PA11 | URBAN | Equipment Failure | 919532 | 1 | 292 | 99.35 | 6.0378e-05 | 6.0773e-05
2013-01-07 | 810:74050 | SHORT RURAL | Other | 919535 | 9 | 101 | 909 | 0.00055242 | 0.00054695
2013-01-08 | ZN847:PA2 | URBAN | Equipment Failure | 919537 | 100 | 76.1333 | 7613.3333 | 0.0046268 | 0.0060773
2013-01-08 | 206:34441 | URBAN | Other | 919546 | 142 | 41.65 | 5914.3 | 0.0035943 | 0.0086298
2013-01-08 | ZN901:PA12 | URBAN | Other | 919570 | 34 | 93 | 3162 | 0.0019216 | 0.0020663
2013-01-08 | ZN180:PA19 | URBAN | Other | 919578 | 95 | 74.0667 | 7036.3333 | 0.0042762 | 0.0057734
2013-01-08 | ZN12570:PA29 | SHORT RURAL | Equipment Failure | 919583 | 11 | 227.8 | 2505.8 | 0.0015228 | 0.0006685
2013-01-08 | ZN12570:PA22 | URBAN | Equipment Failure | 919586 | 2365 | 151 | 146201 | 0.088851 | 0.14373
2013-01-08 | ZN12600:PA1 | SHORT RURAL | Other | 919592 | 600 | 129 | 62835 | 0.038187 | 0.036464
2013-01-08 | ZN12600:PA13 | SHORT RURAL | Other | 919592 | 2 | 129 | 188 | 0.00011425 | 0.00012155
2013-01-08 | ZN12600:PA5 | URBAN | Other | 919592 | 17 | 129 | 1938 | 0.0011778 | 0.0010331
2013-01-08 | ZN2635:PA17 | URBAN | Vegetation | 919603 | 53 | 45 | 2385 | 0.0014494 | 0.003221
2013-01-08 | ZN9252:PA2 | URBAN | Other | 919611 | 1169 | 66 | 77154 | 0.046889 | 0.071044
2013-01-08 | ZN12570:PA37 | SHORT RURAL | Animals | 919612 | 1 | 127 | 127 | 7.7182e-05 | 6.0773e-05
2013-01-08 | ZN12580:PA1 | URBAN | Animals | 919612 | 3 | 127 | 381 | 0.00023154 | 0.00018232
2013-01-08 | ZN12580:PA10 | URBAN | Animals | 919612 | 1502 | 127 | 190754 | 0.11593 | 0.091281
2013-01-08 | ZN15011:PA6 | URBAN | Other | 919662 | 84 | 97 | 8147.0667 | 0.0049512 | 0.0051049
2013-01-08 | 807:74183 | SHORT RURAL | Other | 919664 | 1 | 48 | 48 | 2.9171e-05 | 6.0773e-05
2013-01-08 | ZN12690:PA12 | SHORT RURAL | Vegetation | 919665 | 1307 | 246 | 136018 | 0.082662 | 0.07943
2013-01-08 | ZN4545:PA17 | URBAN | Other | 919667 | 121 | 203 | 847 | 0.00051475 | 0.0073535
2013-01-08 | ZN4545:PA19 | URBAN | Other | 919667 | 197 | 203 | 27754 | 0.016867 | 0.011972
2013-01-08 | ZN4545:PA21 | URBAN | Other | 919667 | 30 | 203 | 1860 | 0.0011304 | 0.0018232
2013-01-08 | 205:12210 | URBAN | Other | 919670 | 123 | 79.0667 | 9725.2 | 0.0059103 | 0.0074751
2013-01-08 | ZN10990:PA11 | URBAN | Equipment Failure | 919674 | 963 | 130 | 125190 | 0.076082 | 0.058524
2013-01-08 | ZN10999:PA12 | URBAN | Equipment Failure | 919674 | 1 | 130 | 130 | 7.9005e-05 | 6.0773e-05
2013-01-08 | ZN1193:PA6 | URBAN | Vegetation | 919684 | 26 | 60 | 1560 | 0.00094806 | 0.0015801
2013-01-08 | ZN10999:PA4 | URBAN | Equipment Failure | 919685 | 116 | 444.1167 | 51517.5333 | 0.031309 | 0.0070497
2013-01-08 | 503:48077 | URBAN | Equipment Failure | 919687 | 29 | 181 | 5249 | 0.00319 | 0.0017624
2013-01-08 | ZN15006:PA1 | URBAN | Equipment Failure | 919698 | 1490 | 86 | 110020 | 0.066862 | 0.090552
2013-01-08 | ZN12690:PA19 | URBAN | Equipment Failure | 919701 | 71 | 88 | 6248 | 0.0037971 | 0.0043149
2013-01-08 | ZN10994:PA11 | URBAN | Other | 919710 | 56 | 258.75 | 14490 | 0.008806 | 0.0034033
2013-01-08 | ZN2310:PA38 | URBAN | Other | 919711 | 65 | 295.4833 | 19206.4167 | 0.011672 | 0.0039502
2013-01-08 | 260:33353 | URBAN | Equipment Failure | 919715 | 66 | 77.7833 | 5133.7 | 0.0031199 | 0.004011
2013-01-08 | ZN3154:PA5 | URBAN | Vegetation | 919716 | 1 | 375.6667 | 375.6667 | 0.0002283 | 6.0773e-05
2013-01-08 | ZN3154:PA23 | URBAN | Vegetation | 919718 | 1 | 167.9167 | 167.9167 | 0.00010205 | 6.0773e-05
2013-01-08 | 205:12203 | URBAN | Other | 919725 | 124 | 35 | 4340 | 0.0026375 | 0.0075358
2013-01-08 | ZN9550:PA28 | URBAN | Other | 919727 | 154 | 539 | 83006 | 0.050445 | 0.009359
2013-01-08 | ZN12640:PA6 | URBAN | Equipment Failure | 919728 | 159 | 82.1833 | 13067.15 | 0.0079413 | 0.0096629
2013-01-08 | ZN3922:PA22 | URBAN | Equipment Failure | 919734 | 905 | 97 | 84585 | 0.051405 | 0.055
2013-01-08 | ZN2310:PA38 | URBAN | Other | 919739 | 101 | 286.85 | 28971.85 | 0.017607 | 0.0061381
2013-01-08 | ZN1285:PA27 | URBAN | Other | 919740 | 125 | 246 | 30750 | 0.018688 | 0.0075966
2013-01-08 | ZN1285:PA31 | URBAN | Other | 919740 | 97 | 246 | 23850.8 | 0.014495 | 0.005895
2013-01-08 | ZN1287:PA4 | URBAN | Weather | 919742 | 87 | 133.1833 | 11586.95 | 0.0070417 | 0.0052872
2013-01-08 | ZN3922:PA2 | SHORT RURAL | Equipment Failure | 919761 | 342 | 132 | 45144 | 0.027435 | 0.020784
2013-01-08 | ZN3922:PA5 | URBAN | Equipment Failure | 919761 | 2372 | 132 | 279966 | 0.17014 | 0.14415
2013-01-08 | ZN10994:PA11 | URBAN | Other | 919771 | 56 | 84.6167 | 4738.5333 | 0.0028797 | 0.0034033
2013-01-08 | ZN14892:PA16 | URBAN | Equipment Failure | 919774 | 76 | 103.3667 | 7855.8667 | 0.0047742 | 0.0046187
2013-01-08 | ZN3922:PA13 | URBAN | Equipment Failure | 919781 | 69 | 314 | 21666 | 0.013167 | 0.0041933
2013-01-08 | ZN3922:PA2 | SHORT RURAL | Equipment Failure | 919781 | 419 | 314 | 112110 | 0.068133 | 0.025464
2013-01-08 | ZN3922:PA29 | URBAN | Equipment Failure | 919781 | 79 | 314 | 24798.1 | 0.015071 | 0.0048011
2013-01-08 | ZN3922:PA5 | URBAN | Equipment Failure | 919781 | 159 | 314 | 10920.4333 | 0.0066367 | 0.0096629
2013-01-08 | ZN14892:PA13 | URBAN | Equipment Failure | 919788 | 1 | 229.3333 | 229.3333 | 0.00013937 | 6.0773e-05
2013-01-08 | 502:48010 | SHORT RURAL | Other | 919791 | 1 | 73.7167 | 73.7167 | 4.48e-05 | 6.0773e-05
2013-01-08 | ZN36300:PA19 | URBAN | Vegetation | 919792 | 71 | 103 | 7313 | 0.0044443 | 0.0043149
2013-01-08 | 260:33347 | SHORT RURAL | Other | 919796 | 104 | 60 | 6240 | 0.0037922 | 0.0063204
2013-01-08 | 243:80084 | SHORT RURAL | Vegetation | 919820 | 53 | 77.2167 | 4092.4833 | 0.0024871 | 0.003221
2013-01-08 | ZN9550:PA36 | URBAN | Other | 919823 | 74 | 384 | 28398.7333 | 0.017259 | 0.0044972
2013-01-08 | ZN9550:PA6 | URBAN | Other | 919823 | 44 | 384 | 16896 | 0.010268 | 0.002674
2013-01-08 | ZN3154:PA18 | URBAN | Vegetation | 919829 | 1 | 89.6167 | 89.6167 | 5.4463e-05 | 6.0773e-05
2013-01-08 | 260:33353 | URBAN | Other | 919839 | 88 | 72 | 6336 | 0.0038506 | 0.005348
2013-01-08 | ZN3155:PA44 | URBAN | Other | 919841 | 60 | 119.3667 | 7162 | 0.0043526 | 0.0036464
2013-01-08 | ZN1193:PA28 | URBAN | Vegetation | 919857 | 34 | 160 | 5440 | 0.003306 | 0.0020663
2013-01-08 | ZN35800:PA7 | URBAN | Other | 919867 | 98 | 105.2167 | 10311.2333 | 0.0062664 | 0.0059557
2013-01-09 | 223:14395 | SHORT RURAL | Equipment Failure | 919874 | 40 | 599.4 | 23976 | 0.014571 | 0.0024309
2013-01-09 | ZN14891:PA16 | SHORT RURAL | Other | 919876 | 30 | 275 | 8227.2833 | 0.005 | 0.0018232
2013-01-09 | 227:13014 | SHORT RURAL | Equipment Failure | 919878 | 56 | 535 | 27182 | 0.016519 | 0.0034033
2013-01-09 | ZN9900:PA13 | URBAN | Vegetation | 919879 | 37 | 322.2 | 11921.4 | 0.007245 | 0.0022486
2013-01-09 | ZN12660:PA5 | SHORT RURAL | Vegetation | 919889 | 1 | 227.6 | 227.6 | 0.00013832 | 6.0773e-05
2013-01-09 | 807:74184 | SHORT RURAL | Other | 919892 | 59 | 181 | 8998 | 0.0054683 | 0.0035856
2013-01-09 | ZN1164:PA4 | URBAN | Equipment Failure | 919914 | 1 | 350.25 | 350.25 | 0.00021286 | 6.0773e-05
2013-01-09 | 223:14397 | URBAN | Equipment Failure | 919927 | 1 | 159.65 | 159.65 | 9.7024e-05 | 6.0773e-05
2013-01-04 | ZN9700:PA17 | URBAN | Equipment Failure | 919939 | 44 | 180 | 7920 | 0.0048131 | 0.002674
2013-01-09 | ZN15006:PA1 | URBAN | Vegetation | 919951 | 68 | 325 | 22100 | 0.013431 | 0.0041326
2013-01-09 | ZN3922:PA21 | SHORT RURAL | Equipment Failure | 919975 | 21 | 201 | 4221 | 0.0025652 | 0.0012762
2013-01-09 | ZN10993:PA7 | URBAN | Equipment Failure | 919997 | 38 | 159.05 | 6043.9 | 0.0036731 | 0.0023094
2013-01-09 | ZN10993:PA7 | URBAN | Third Party Impacts | 920011 | 1 | 9.7833 | 9.7833 | 5.9456e-06 | 6.0773e-05
2013-01-09 | 228:7490 | SHORT RURAL | Other | 920020 | 1 | 295.3167 | 295.3167 | 0.00017947 | 6.0773e-05
2013-01-09 | ZN2310:PA33 | URBAN | Equipment Failure | 920053 | 7 | 718 | 5026 | 0.0030544 | 0.00042541
2013-01-09 | ZN1287:PA11 | URBAN | Vegetation | 920059 | 1 | 215.8 | 215.8 | 0.00013115 | 6.0773e-05
2013-01-03 | 801:74121 | SHORT RURAL | Equipment Failure | 920082 | 2 | 37 | 74 | 4.4971e-05 | 0.00012154
2013-01-09 | 513:48056 | SHORT RURAL | Other | 920085 | 734 | 346 | 57246 | 0.03479 | 0.044607
2013-01-03 | 523:33501 | SHORT RURAL | Other | 920088 | 2 | 153 | 306 | 0.00018596 | 0.00012154
2013-01-09 | ZN13000:PA2 | URBAN | Other | 920114 | 70 | 216 | 15120 | 0.0091889 | 0.0042541
2013-01-09 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 920115 | 1 | 198.05 | 198.05 | 0.00012036 | 6.0773e-05
2013-01-09 | ZN14144:PA10 | SHORT RURAL | Vegetation | 920137 | 1 | 154.15 | 154.15 | 9.3681e-05 | 6.0773e-05
2013-01-08 | ZN15010:PA11 | URBAN | Vegetation | 920142 | 51 | 120 | 6120 | 0.0037193 | 0.0030994
2013-01-09 | ZN12600:PA11 | URBAN | Vegetation | 920146 | 1 | 167.5833 | 167.5833 | 0.00010185 | 6.0773e-05
2013-01-09 | 516:48065 | SHORT RURAL | Other | 920147 | 1 | 555.8 | 555.8 | 0.00033778 | 6.0773e-05
2013-01-09 | 221:11894 | URBAN | Other | 920205 | 1 | 88.9167 | 88.9167 | 5.4037e-05 | 6.0773e-05
2013-01-09 | ZN342:PA22 | URBAN | Equipment Failure | 920211 | 121 | 107 | 12947 | 0.0078683 | 0.0073535
2013-01-09 | 214:8670 | URBAN | Third Party Impacts | 920215 | 1 | 218.0833 | 218.0833 | 0.00013254 | 6.0773e-05
2013-01-09 | 515:35197 | LONG RURAL | Other | 920263 | 2 | 349 | 698 | 0.00042419 | 0.00012155
2013-01-09 | ZN15008:PA7 | URBAN | Equipment Failure | 920276 | 1 | 135.6667 | 135.6667 | 8.2449e-05 | 6.0773e-05
2013-01-09 | ZN1673:PA19 | URBAN | Vegetation | 920288 | 16 | 186 | 2976 | 0.0018086 | 0.00097237
2013-01-09 | 203:8084 | URBAN | Other | 920307 | 1 | 64.3833 | 64.3833 | 3.9128e-05 | 6.0773e-05
2013-01-09 | 512:48049 | SHORT RURAL | Other | 920308 | 1 | 544.5833 | 544.5833 | 0.00033096 | 6.0773e-05
2013-01-09 | 510:48164 | SHORT RURAL | Other | 920314 | 2 | 90 | 180 | 0.00010939 | 0.00012155
2013-01-10 | ZN9301:PA8 | URBAN | Equipment Failure | 920316 | 721 | 785 | 80237 | 0.048762 | 0.043817
2013-01-10 | ZN12610:PA17 | URBAN | Animals | 920320 | 94 | 89 | 8366 | 0.0050843 | 0.0057127
2013-01-08 | ZN15006:PA2 | URBAN | Vegetation | 920358 | 37 | 160 | 5920 | 0.0035978 | 0.0022486
2013-01-10 | 807:74180 | SHORT RURAL | Other | 920412 | 5 | 10 | 50 | 3.0386e-05 | 0.00030386
2013-01-10 | 502:48010 | SHORT RURAL | Vegetation | 920415 | 1 | 159.7833 | 159.7833 | 9.7105e-05 | 6.0773e-05
2013-01-10 | ZN12630:PA2 | SHORT RURAL | Third Party Impacts | 920416 | 194 | 324 | 27703 | 0.016836 | 0.01179
2013-01-10 | ZN180:PA34 | URBAN | Other | 920418 | 1 | 134.3 | 134.3 | 8.1618e-05 | 6.0773e-05
2013-01-10 | 223:14394 | URBAN | Other | 920456 | 1 | 1226.8167 | 1226.8167 | 0.00074557 | 6.0773e-05
2013-01-10 | ZN12610:PA9 | SHORT RURAL | Equipment Failure | 920500 | 1 | 139.9833 | 139.9833 | 8.5072e-05 | 6.0773e-05
2013-01-10 | ZN342:PA24 | URBAN | Equipment Failure | 920504 | 35 | 375.65 | 13147.75 | 0.0079903 | 0.0021271
2013-01-10 | 213:33770 | URBAN | Equipment Failure | 920538 | 1690 | 88 | 89040 | 0.054112 | 0.10271
2013-01-10 | ZN9037:PA16 | URBAN | Equipment Failure | 920595 | 280 | 31 | 8680 | 0.0052751 | 0.017016
2013-01-10 | 205:12203 | URBAN | Other | 920618 | 1 | 53.5 | 53.5 | 3.2514e-05 | 6.0773e-05
2013-01-10 | 515:35200 | URBAN | Equipment Failure | 920619 | 6 | 113 | 678 | 0.00041204 | 0.00036464
2013-01-10 | 258:80793 | SHORT RURAL | Other | 920655 | 1 | 105.1833 | 105.1833 | 6.3923e-05 | 6.0773e-05
2013-01-10 | 258:80775 | URBAN | Vegetation | 920680 | 1 | 68.6333 | 68.6333 | 4.171e-05 | 6.0773e-05
2013-01-10 | 514:18137 | SHORT RURAL | Other | 920684 | 1 | 157.8333 | 157.8333 | 9.592e-05 | 6.0773e-05
2013-01-10 | 524:33572 | SHORT RURAL | Other | 920700 | 1 | 125.8 | 125.8 | 7.6452e-05 | 6.0773e-05
2013-01-10 | ZN2310:PA4 | URBAN | Equipment Failure | 920704 | 1 | 229.15 | 229.15 | 0.00013926 | 6.0773e-05
2013-01-10 | ZN1673:PA11 | URBAN | Other | 920715 | 1 | 75.8667 | 75.8667 | 4.6106e-05 | 6.0773e-05
2013-01-10 | ZN1673:PA11 | URBAN | Other | 920716 | 1 | 68.1167 | 68.1167 | 4.1396e-05 | 6.0773e-05
2013-01-11 | ZN14891:PA12 | SHORT RURAL | Other | 920727 | 56 | 151 | 7091 | 0.0043094 | 0.0034033
2013-01-11 | ZN1285:PA18 | URBAN | Equipment Failure | 920781 | 1 | 74 | 74 | 4.4972e-05 | 6.0773e-05
2013-01-11 | ZN3472:PA23 | URBAN | Equipment Failure | 920781 | 18 | 74 | 864 | 0.00052508 | 0.0010939
2013-01-11 | ZN3472:PA31 | URBAN | Equipment Failure | 920781 | 1841 | 74 | 117618 | 0.07148 | 0.11188
2013-01-11 | 516:48067 | SHORT RURAL | Equipment Failure | 920793 | 1 | 664 | 664 | 0.00040353 | 6.0773e-05
2013-01-11 | ZN1285:PA19 | URBAN | Other | 920809 | 111 | 182 | 20202 | 0.012277 | 0.0067458
2013-01-11 | ZN2310:PA38 | URBAN | Other | 920810 | 1 | 89.4167 | 89.4167 | 5.4341e-05 | 6.0773e-05
2013-01-11 | ZN167:PA20 | URBAN | Equipment Failure | 920864 | 1 | 448.3667 | 448.3667 | 0.00027249 | 6.0773e-05
2013-01-11 | ZN80:PA31 | URBAN | Other | 920866 | 1 | 118.6 | 118.6 | 7.2077e-05 | 6.0773e-05
2013-01-11 | 509:48039 | LONG RURAL | Vegetation | 920877 | 283 | 504 | 77462 | 0.047076 | 0.017199
2013-01-11 | ZN12580:PA1 | URBAN | Equipment Failure | 920928 | 1 | 267.9667 | 267.9667 | 0.00016285 | 6.0773e-05
2013-01-11 | ZN1290:PA4 | URBAN | Equipment Failure | 920943 | 21 | 101.9833 | 2141.65 | 0.0013015 | 0.0012762
2013-01-11 | ZN167:PA1 | URBAN | Third Party Impacts | 920947 | 1 | 48.4833 | 48.4833 | 2.9465e-05 | 6.0773e-05
2013-01-11 | ZN398:PA4 | URBAN | Other | 920949 | 1 | 543.5667 | 543.5667 | 0.00033034 | 6.0773e-05
2013-01-11 | 507:80922 | SHORT RURAL | Equipment Failure | 921000 | 2 | 119 | 238 | 0.00014464 | 0.00012155
2013-01-11 | ZN80:PA22 | URBAN | Third Party Impacts | 921003 | 27 | 103 | 2781 | 0.0016901 | 0.0016409
2013-01-11 | ZN80:PA25 | URBAN | Third Party Impacts | 921003 | 1 | 103 | 103 | 6.2596e-05 | 6.0773e-05
2013-01-11 | ZN9037:PA8 | URBAN | Vegetation | 921004 | 1 | 243.4667 | 243.4667 | 0.00014796 | 6.0773e-05
2013-01-11 | ZN188:PA33 | URBAN | Other | 921010 | 47 | 49.3333 | 2318.6667 | 0.0014091 | 0.0028563
2013-01-11 | ZN188:PA38 | URBAN | Equipment Failure | 921013 | 221 | 44 | 9724 | 0.0059096 | 0.013431
2013-01-11 | ZN10994:PA21 | URBAN | Equipment Failure | 921032 | 83 | 144 | 11952 | 0.0072636 | 0.0050442
2013-01-11 | 512:48049 | SHORT RURAL | Other | 921056 | 3 | 224 | 672 | 0.00040839 | 0.00018232
2013-01-11 | 264:81240 | SHORT RURAL | Other | 921057 | 43 | 123.3333 | 5303.3333 | 0.003223 | 0.0026132
2013-01-11 | 507:80932 | SHORT RURAL | Other | 921066 | 1 | 91.3333 | 91.3333 | 5.5506e-05 | 6.0773e-05
2013-01-11 | 504:48031 | SHORT RURAL | Equipment Failure | 921073 | 5 | 172 | 860 | 0.00052265 | 0.00030386
2013-01-11 | 509:48039 | LONG RURAL | Other | 921081 | 27 | 335 | 8845 | 0.0053754 | 0.0016409
2013-01-11 | ZN12690:PA16 | SHORT RURAL | Other | 921087 | 368 | 98 | 29509 | 0.017933 | 0.022364
2013-01-12 | 526:34640 | SHORT RURAL | Other | 921088 | 1 | 825 | 825 | 0.00050138 | 6.0773e-05
2013-01-12 | 526:34635 | SHORT RURAL | Animals | 921104 | 1 | 110.4 | 110.4 | 6.7093e-05 | 6.0773e-05
2013-01-12 | 202:34254 | URBAN | Other | 921116 | 1 | 66.3833 | 66.3833 | 4.0343e-05 | 6.0773e-05
2013-01-12 | 813:89062 | SHORT RURAL | Vegetation | 921118 | 5 | 105 | 525 | 0.00031906 | 0.00030386
2013-01-12 | ZN2310:PA38 | URBAN | Other | 921124 | 1 | 202.45 | 202.45 | 0.00012303 | 6.0773e-05
2013-01-12 | 501:48123 | SHORT RURAL | Equipment Failure | 921125 | 12 | 430.5333 | 5166.4 | 0.0031398 | 0.00072927
2013-01-12 | 225:13446 | URBAN | Other | 921130 | 88 | 79 | 6952 | 0.0042249 | 0.005348
2013-01-12 | 228:7487 | URBAN | Other | 921138 | 1 | 73.25 | 73.25 | 4.4516e-05 | 6.0773e-05
2013-01-12 | 238:34141 | SHORT RURAL | Vegetation | 921148 | 1 | 132.15 | 132.15 | 8.0311e-05 | 6.0773e-05
2013-01-12 | ZN12610:PA11 | URBAN | Equipment Failure | 921152 | 1 | 399.0333 | 399.0333 | 0.0002425 | 6.0773e-05
2013-01-12 | ZN12620:PA7 | URBAN | Equipment Failure | 921167 | 1 | 228.2167 | 228.2167 | 0.00013869 | 6.0773e-05
2013-01-12 | ZN12570:PA24 | SHORT RURAL | Equipment Failure | 921168 | 61 | 107 | 6527 | 0.0039666 | 0.0037071
2013-01-12 | 512:48049 | SHORT RURAL | Equipment Failure | 921175 | 16 | 250 | 4000 | 0.0024309 | 0.00097237
2013-01-12 | 515:35192 | SHORT RURAL | Other | 921179 | 1 | 241 | 241 | 0.00014646 | 6.0773e-05
2013-01-12 | ZN3672:PA44 | URBAN | Equipment Failure | 921180 | 32 | 3295 | 105440 | 0.064079 | 0.0019447
2013-01-12 | 508:82578 | SHORT RURAL | Other | 921189 | 29 | 63 | 1827 | 0.0011103 | 0.0017624
2013-01-12 | 507:80923 | SHORT RURAL | Equipment Failure | 921201 | 12 | 1006 | 12072 | 0.0073365 | 0.00072927
2013-01-12 | ZN847:PA18 | URBAN | Vegetation | 921208 | 1578 | 91 | 143598 | 0.087269 | 0.0959
2013-01-12 | 504:48028 | URBAN | Other | 921212 | 66 | 139.95 | 9236.7 | 0.0056134 | 0.004011
2013-01-12 | ZN1673:PA7 | URBAN | Vegetation | 921226 | 51 | 30 | 1530 | 0.00092983 | 0.0030994
2013-01-12 | 516:48066 | SHORT RURAL | Other | 921230 | 102 | 103 | 10506 | 0.0063848 | 0.0061988
2013-01-12 | 812:19065 | SHORT RURAL | Other | 921232 | 5 | 213 | 1065 | 0.00064723 | 0.00030386
2013-01-12 | ZN1673:PA18 | URBAN | Other | 921233 | 1 | 365.6 | 365.6 | 0.00022219 | 6.0773e-05
2013-01-12 | 214:8665 | URBAN | Other | 921240 | 79 | 24.2 | 1911.8 | 0.0011619 | 0.0048011
2013-01-12 | 513:48056 | SHORT RURAL | Other | 921244 | 252 | 93 | 23436 | 0.014243 | 0.015315
2013-01-12 | 524:33580 | SHORT RURAL | Other | 921246 | 311 | 54 | 16794 | 0.010206 | 0.0189
2013-01-12 | 814:82283 | SHORT RURAL | Other | 921247 | 1 | 1018.4833 | 1018.4833 | 0.00061896 | 6.0773e-05
2013-01-12 | 515:35193 | SHORT RURAL | Other | 921255 | 79 | 70 | 5530 | 0.0033607 | 0.0048011
2013-01-12 | 513:48059 | SHORT RURAL | Other | 921257 | 157 | 130 | 14922 | 0.0090685 | 0.0095413
2013-01-12 | 523:33501 | SHORT RURAL | Other | 921262 | 688 | 204 | 139931 | 0.08504 | 0.041812
2013-01-12 | 512:48048 | SHORT RURAL | Other | 921281 | 304 | 181.45 | 55160.8 | 0.033523 | 0.018475
2013-01-12 | 802:82215 | SHORT RURAL | Other | 921283 | 40 | 294 | 11760 | 0.0071469 | 0.0024309
2013-01-12 | 261:81882 | URBAN | Other | 921285 | 1 | 188.6333 | 188.6333 | 0.00011464 | 6.0773e-05
2013-01-12 | 511:29878 | SHORT RURAL | Other | 921288 | 1 | 222 | 222 | 0.00013492 | 6.0773e-05
2013-01-12 | 801:74121 | SHORT RURAL | Other | 921296 | 127 | 105 | 13335 | 0.0081041 | 0.0077182
2013-01-12 | 526:34641 | SHORT RURAL | Other | 921302 | 133 | 141 | 18753 | 0.011397 | 0.0080828
2013-01-12 | 813:89062 | SHORT RURAL | Other | 921310 | 198 | 151 | 29898 | 0.01817 | 0.012033
2013-01-12 | ZN15005:PA8 | URBAN | Vegetation | 921316 | 1539 | 187 | 115479 | 0.07018 | 0.09353
2013-01-13 | 512:48049 | SHORT RURAL | Other | 921330 | 5 | 229 | 1145 | 0.00069585 | 0.00030386
2013-01-12 | 806:74076 | SHORT RURAL | Other | 921339 | 40 | 180 | 7200 | 0.0043756 | 0.0024309
2013-01-12 | 511:29877 | SHORT RURAL | Other | 921341 | 1 | 339.7167 | 339.7167 | 0.00020646 | 6.0773e-05
2013-01-12 | 813:89055 | SHORT RURAL | Other | 921353 | 43 | 252 | 10836 | 0.0065854 | 0.0026132
2013-01-12 | 514:18137 | SHORT RURAL | Other | 921356 | 36 | 243.4 | 8762.4 | 0.0053252 | 0.0021878
2013-01-12 | 524:33580 | SHORT RURAL | Other | 921363 | 25 | 353.0667 | 8826.6667 | 0.0053642 | 0.0015193
2013-01-12 | 503:48078 | URBAN | Other | 921366 | 1 | 798.45 | 798.45 | 0.00048524 | 6.0773e-05
2013-01-12 | 523:33501 | SHORT RURAL | Other | 921383 | 1 | 39.4167 | 39.4167 | 2.3955e-05 | 6.0773e-05
2013-01-12 | ZN12640:PA16 | URBAN | Equipment Failure | 921384 | 1 | 204.55 | 204.55 | 0.00012431 | 6.0773e-05
2013-01-12 | 513:48050 | SHORT RURAL | Equipment Failure | 921386 | 74 | 578 | 41596.25 | 0.025279 | 0.0044972
2013-01-12 | ZN36300:PA3 | URBAN | Equipment Failure | 921387 | 43 | 86.0333 | 3699.4333 | 0.0022483 | 0.0026132
2013-01-12 | ZN12640:PA16 | URBAN | Equipment Failure | 921395 | 1 | 153.8 | 153.8 | 9.3469e-05 | 6.0773e-05
2013-01-12 | 515:35193 | SHORT RURAL | Other | 921400 | 3 | 70 | 210 | 0.00012762 | 0.00018232
2013-01-12 | 801:74121 | SHORT RURAL | Other | 921401 | 1 | 95 | 95 | 5.7734e-05 | 6.0773e-05
2013-01-13 | 523:33501 | SHORT RURAL | Other | 921404 | 3 | 134 | 402 | 0.00024431 | 0.00018232
2013-01-13 | ZN12610:PA22 | URBAN | Other | 921406 | 1 | 118.8 | 118.8 | 7.2198e-05 | 6.0773e-05
2013-01-13 | 502:48009 | URBAN | Vegetation | 921410 | 1 | 124.4667 | 124.4667 | 7.5642e-05 | 6.0773e-05
2013-01-13 | 217:33611 | URBAN | Animals | 921411 | 102 | 64 | 6528 | 0.0039673 | 0.0061988
2013-01-13 | ZN9550:PA1 | URBAN | Equipment Failure | 921413 | 113 | 284.9833 | 32203.1167 | 0.019571 | 0.0068673
2013-01-13 | 222:2018 | URBAN | Other | 921417 | 1 | 118.2833 | 118.2833 | 7.1884e-05 | 6.0773e-05
2013-01-14 | 526:34640 | SHORT RURAL | Equipment Failure | 921418 | 5 | 203 | 1015 | 0.00061685 | 0.00030386
2013-01-13 | 258:80778 | URBAN | Equipment Failure | 921419 | 43 | 35 | 1505 | 0.00091463 | 0.0026132
2013-01-13 | 520:48172 | SHORT RURAL | Other | 921429 | 1 | 256 | 256 | 0.00015558 | 6.0773e-05
2013-01-13 | 526:34640 | SHORT RURAL | Other | 921430 | 5 | 330 | 1650 | 0.0010028 | 0.00030386
2013-01-13 | 810:74054 | LONG RURAL | Other | 921433 | 404 | 271 | 75140 | 0.045665 | 0.024552
2013-01-12 | 806:74080 | SHORT RURAL | Other | 921443 | 31 | 875 | 27125 | 0.016485 | 0.001884
2013-01-13 | 512:48049 | SHORT RURAL | Other | 921446 | 1 | 200 | 200 | 0.00012155 | 6.0773e-05
2013-01-13 | 515:35197 | LONG RURAL | Other | 921447 | 2 | 265 | 530 | 0.0003221 | 0.00012155
2013-01-13 | 526:34636 | SHORT RURAL | Other | 921448 | 2 | 261 | 522 | 0.00031723 | 0.00012155
2013-01-13 | 512:48049 | SHORT RURAL | Other | 921449 | 4 | 542.4667 | 2169.8667 | 0.0013187 | 0.00024309
2013-01-13 | 512:48049 | SHORT RURAL | Equipment Failure | 921450 | 4 | 803 | 3212 | 0.001952 | 0.00024309
2013-01-13 | 511:29878 | SHORT RURAL | Other | 921461 | 1 | 400.7667 | 400.4833 | 0.00024339 | 6.0773e-05
2013-01-13 | 526:34636 | SHORT RURAL | Other | 921461 | 2 | 400.7667 | 694 | 0.00042176 | 0.00012155
2013-01-13 | 520:48172 | SHORT RURAL | Other | 921464 | 2 | 321 | 642 | 0.00039016 | 0.00012155
2013-01-13 | 520:48172 | SHORT RURAL | Other | 921466 | 1 | 268 | 268 | 0.00016287 | 6.0773e-05
2013-01-13 | 512:48049 | SHORT RURAL | Other | 921471 | 1 | 436.2833 | 436.2833 | 0.00026514 | 6.0773e-05
2013-01-13 | 503:48011 | SHORT RURAL | Equipment Failure | 921488 | 1 | 365 | 365 | 0.00022182 | 6.0773e-05
2013-01-13 | 806:74080 | SHORT RURAL | Other | 921489 | 1 | 119 | 119 | 7.232e-05 | 6.0773e-05
2013-01-13 | 513:48056 | SHORT RURAL | Other | 921491 | 2 | 269 | 538 | 0.00032696 | 0.00012155
2013-01-13 | 526:34635 | SHORT RURAL | Other | 921494 | 1 | 204 | 204 | 0.00012398 | 6.0773e-05
2013-01-13 | ZN1285:PA19 | URBAN | Equipment Failure | 921498 | 70 | 66 | 4060 | 0.0024674 | 0.0042541
2013-01-13 | ZN3472:PA23 | URBAN | Equipment Failure | 921498 | 17 | 66 | 986 | 0.00059922 | 0.0010331
2013-01-13 | ZN3472:PA31 | URBAN | Equipment Failure | 921498 | 1841 | 66 | 109434 | 0.066506 | 0.11188
2013-01-13 | 512:48049 | SHORT RURAL | Other | 921503 | 2 | 57 | 114 | 6.9281e-05 | 0.00012155
2013-01-13 | 801:74118 | URBAN | Vegetation | 921505 | 1 | 322.15 | 322.15 | 0.00019578 | 6.0773e-05
2013-01-13 | 507:80923 | SHORT RURAL | Other | 921508 | 1 | 330.1333 | 330.1333 | 0.00020063 | 6.0773e-05
2013-01-13 | 812:19066 | SHORT RURAL | Other | 921512 | 1 | 372.1333 | 372.1333 | 0.00022616 | 6.0773e-05
2013-01-13 | 512:48049 | SHORT RURAL | Other | 921514 | 1 | 88.95 | 88.95 | 5.4058e-05 | 6.0773e-05
2013-01-13 | ZN12580:PA10 | URBAN | Third Party Impacts | 921515 | 1502 | 100 | 149115 | 0.090622 | 0.091281
2013-01-13 | ZN9035:PA11 | URBAN | Other | 921540 | 1 | 454.85 | 454.85 | 0.00027643 | 6.0773e-05
2013-01-13 | ZN9252:PA10 | URBAN | Equipment Failure | 921544 | 1 | 439.6833 | 439.6833 | 0.00026721 | 6.0773e-05
2013-01-13 | ZN9118:PA2 | URBAN | Other | 921545 | 1 | 143.5667 | 143.5667 | 8.725e-05 | 6.0773e-05
2013-01-13 | ZN15012:PA6 | URBAN | Other | 921554 | 1 | 133.6333 | 133.6333 | 8.1213e-05 | 6.0773e-05
2013-01-13 | 810:74054 | LONG RURAL | Vegetation | 921559 | 1 | 456.4 | 456.4 | 0.00027737 | 6.0773e-05
2013-01-13 | ZN36300:PA11 | URBAN | Other | 921565 | 1 | 210.3333 | 210.3333 | 0.00012783 | 6.0773e-05
2013-01-13 | ZN1285:PA27 | URBAN | Equipment Failure | 921566 | 116 | 36.9 | 4280.4 | 0.0026013 | 0.0070497
2013-01-13 | ZN2635:PA21 | URBAN | Equipment Failure | 921571 | 1 | 548.7333 | 548.7333 | 0.00033348 | 6.0773e-05
2013-01-13 | 520:48172 | SHORT RURAL | Other | 921574 | 14 | 515 | 7210 | 0.0043817 | 0.00085082
2013-01-13 | ZN965:PA37 | URBAN | Other | 921589 | 1 | 209.1833 | 209.1833 | 0.00012713 | 6.0773e-05
2013-01-13 | ZN3672:PA46 | URBAN | Other | 921593 | 1 | 978.4667 | 978.4667 | 0.00059464 | 6.0773e-05
2013-01-13 | ZN269:PA3 | URBAN | Vegetation | 921595 | 1 | 114.05 | 114.05 | 6.9312e-05 | 6.0773e-05
2013-01-13 | ZN2635:PA21 | URBAN | Equipment Failure | 921596 | 1 | 534.5833 | 534.5833 | 0.00032488 | 6.0773e-05
2013-01-13 | ZN35600:PA7 | URBAN | Other | 921601 | 1 | 887.8667 | 887.8667 | 0.00053958 | 6.0773e-05
2013-01-13 | 810:74050 | SHORT RURAL | Other | 921603 | 1 | 225.5833 | 225.5833 | 0.00013709 | 6.0773e-05
2013-01-13 | ZN15011:PA2 | URBAN | Other | 921609 | 1 | 177.4333 | 177.4333 | 0.00010783 | 6.0773e-05
2013-01-13 | ZN129:PA18 | URBAN | Other | 921611 | 1 | 760.3333 | 760.3333 | 0.00046208 | 6.0773e-05
2013-01-13 | ZN35500:PA16 | URBAN | Equipment Failure | 921614 | 1 | 98.5167 | 98.5167 | 5.9871e-05 | 6.0773e-05
2013-01-13 | ZN965:PA37 | URBAN | Equipment Failure | 921619 | 1 | 165.35 | 165.35 | 0.00010049 | 6.0773e-05
2013-01-13 | ZN35600:PA14 | URBAN | Other | 921624 | 1 | 302.55 | 302.55 | 0.00018387 | 6.0773e-05
2013-01-13 | ZN2835:PA32 | SHORT RURAL | Other | 921628 | 1 | 480.5333 | 480.5333 | 0.00029203 | 6.0773e-05
2013-01-13 | ZN398:PA9 | URBAN | Other | 921633 | 1 | 473.3833 | 473.3833 | 0.00028769 | 6.0773e-05
2013-01-13 | ZN116:PA50 | URBAN | Other | 921646 | 1 | 465.3667 | 465.3667 | 0.00028282 | 6.0773e-05
2013-01-13 | ZN1287:PA17 | URBAN | Other | 921649 | 1 | 1018.95 | 1018.95 | 0.00061925 | 6.0773e-05
2013-01-13 | 813:89062 | SHORT RURAL | Equipment Failure | 921650 | 33 | 259 | 8547 | 0.0051943 | 0.0020055
2013-01-13 | ZN35600:PA14 | URBAN | Other | 921654 | 1 | 281.1 | 281.1 | 0.00017083 | 6.0773e-05
2013-01-13 | ZN269:PA1 | URBAN | Vegetation | 921659 | 1 | 65.6333 | 65.6333 | 3.9887e-05 | 6.0773e-05
2013-01-13 | ZN2602:PA22 | URBAN | Other | 921661 | 1 | 724.6333 | 724.6333 | 0.00044038 | 6.0773e-05
2013-01-13 | 806:74076 | SHORT RURAL | Equipment Failure | 921662 | 40 | 3769.5167 | 16080 | 0.0097723 | 0.0024309
2013-01-13 | 806:74080 | SHORT RURAL | Equipment Failure | 921662 | 231 | 3769.5167 | 92862 | 0.056435 | 0.014039
2013-01-13 | ZN630:PA3 | URBAN | Other | 921665 | 1 | 1685.3833 | 1685.3833 | 0.0010243 | 6.0773e-05
2013-01-13 | ZN9245:PA4 | URBAN | Equipment Failure | 921670 | 1627 | 53 | 78047 | 0.047431 | 0.098878
2013-01-13 | ZN690:PA14 | URBAN | Equipment Failure | 921671 | 100 | 160 | 16000 | 0.0097237 | 0.0060773
2013-01-13 | ZN15008:PA9 | URBAN | Equipment Failure | 921677 | 2047 | 154 | 227606 | 0.13832 | 0.1244
2013-01-13 | ZN2602:PA22 | URBAN | Other | 921680 | 1 | 708.4 | 708.4 | 0.00043052 | 6.0773e-05
2013-01-13 | ZN35600:PA14 | URBAN | Other | 921681 | 1 | 473.5667 | 473.5667 | 0.0002878 | 6.0773e-05
2013-01-13 | ZN4545:PA27 | URBAN | Vegetation | 921688 | 148 | 164 | 24272 | 0.014751 | 0.0089944
2013-01-13 | ZN3155:PA24 | URBAN | Other | 921697 | 1 | 468.1167 | 468.1167 | 0.00028449 | 6.0773e-05
2013-01-13 | ZN12570:PA40 | SHORT RURAL | Equipment Failure | 921704 | 1195 | 64 | 63530 | 0.038609 | 0.072624
2013-01-13 | ZN2602:PA17 | URBAN | Other | 921708 | 1 | 355.9667 | 355.9667 | 0.00021633 | 6.0773e-05
2013-01-13 | ZN2602:PA17 | URBAN | Vegetation | 921711 | 1 | 353.8167 | 353.8167 | 0.00021502 | 6.0773e-05
2013-01-13 | 810:74058 | SHORT RURAL | Other | 921713 | 2 | 394 | 788 | 0.00047889 | 0.00012155
2013-01-13 | 813:89055 | SHORT RURAL | Vegetation | 921717 | 1 | 364.2167 | 364.2167 | 0.00022135 | 6.0773e-05
2013-01-13 | 512:48049 | SHORT RURAL | Other | 921720 | 1 | 616.4833 | 616.4833 | 0.00037465 | 6.0773e-05
2013-01-13 | 507:80923 | SHORT RURAL | Equipment Failure | 921723 | 100 | 250.4333 | 25043.3333 | 0.01522 | 0.0060773
2013-01-13 | ZN12620:PA2 | SHORT RURAL | Other | 921728 | 1 | 431.2 | 431.2 | 0.00026205 | 6.0773e-05
2013-01-13 | ZN14891:PA16 | SHORT RURAL | Other | 921729 | 1 | 308.0667 | 308.0667 | 0.00018722 | 6.0773e-05
2013-01-13 | ZN14891:PA16 | SHORT RURAL | Other | 921731 | 1 | 231.4833 | 231.4833 | 0.00014068 | 6.0773e-05
2013-01-13 | ZN12600:PA11 | URBAN | Vegetation | 921739 | 39 | 67 | 2613 | 0.001588 | 0.0023701
2013-01-14 | ZN1068:PA26 | URBAN | Other | 921743 | 1 | 182.5 | 182.5 | 0.00011091 | 6.0773e-05
2013-01-13 | 812:19072 | SHORT RURAL | Equipment Failure | 921744 | 1 | 187.25 | 187.25 | 0.0001138 | 6.0773e-05
2013-01-13 | ZN1164:PA20 | URBAN | Other | 921749 | 1 | 228.2167 | 228.2167 | 0.00013869 | 6.0773e-05
2013-01-13 | 810:74058 | SHORT RURAL | Other | 921754 | 14 | 316.8667 | 4436.1333 | 0.002696 | 0.00085082
2013-01-13 | 812:19072 | SHORT RURAL | Weather | 921757 | 1 | 162.8 | 162.8 | 9.8938e-05 | 6.0773e-05
2013-01-13 | ZN12620:PA11 | SHORT RURAL | Other | 921758 | 1 | 642.6167 | 642.6167 | 0.00039054 | 6.0773e-05
2013-01-13 | 812:19072 | SHORT RURAL | Weather | 921759 | 1 | 161.3 | 161.3 | 9.8027e-05 | 6.0773e-05
2013-01-13 | ZN35600:PA14 | URBAN | Other | 921760 | 1 | 182.8333 | 182.8333 | 0.00011111 | 6.0773e-05
2013-01-13 | ZN15006:PA8 | URBAN | Other | 921765 | 1 | 314.6667 | 314.6667 | 0.00019123 | 6.0773e-05
2013-01-13 | 216:10728 | URBAN | Other | 921770 | 1 | 101.2167 | 101.2167 | 6.1512e-05 | 6.0773e-05
2013-01-13 | 810:74050 | SHORT RURAL | Other | 921780 | 1 | 420.3 | 420.3 | 0.00025543 | 6.0773e-05
2013-01-13 | ZN180:PA23 | URBAN | Equipment Failure | 921785 | 1 | 41.55 | 41.55 | 2.5251e-05 | 6.0773e-05
2013-01-13 | ZN1164:PA27 | URBAN | Other | 921786 | 1 | 490.3167 | 490.3167 | 0.00029798 | 6.0773e-05
2013-01-13 | 523:33501 | SHORT RURAL | Other | 921789 | 1 | 210 | 210 | 0.00012762 | 6.0773e-05
2013-01-13 | 504:48031 | SHORT RURAL | Other | 921790 | 87 | 232 | 20184 | 0.012266 | 0.0052872
2013-01-13 | 803:74010 | SHORT RURAL | Other | 921792 | 15 | 261 | 3915 | 0.0023793 | 0.00091159
2013-01-13 | 512:48049 | SHORT RURAL | Equipment Failure | 921797 | 5 | 93 | 465 | 0.00028259 | 0.00030386
2013-01-13 | 216:10724 | SHORT RURAL | Other | 921802 | 1 | 288.3333 | 288.3333 | 0.00017523 | 6.0773e-05
2013-01-13 | 813:89062 | SHORT RURAL | Other | 921808 | 2 | 400 | 800 | 0.00048618 | 0.00012155
2013-01-13 | 801:74123 | SHORT RURAL | Equipment Failure | 921809 | 1 | 1677.8667 | 1677.8667 | 0.0010197 | 6.0773e-05
2013-01-13 | ZN35370:PA2 | SHORT RURAL | Weather | 921810 | 76 | 167 | 11918 | 0.0072429 | 0.0046187
2013-01-13 | 813:89061 | LONG RURAL | Other | 921820 | 2 | 214 | 428 | 0.00026011 | 0.00012155
2013-01-13 | ZN4545:PA42 | URBAN | Equipment Failure | 921823 | 1 | 542.3667 | 542.3667 | 0.00032961 | 6.0773e-05
2013-01-13 | ZN1164:PA27 | URBAN | Other | 921830 | 1 | 416.95 | 416.95 | 0.00025339 | 6.0773e-05
2013-01-13 | ZN874:PA25 | URBAN | Other | 921834 | 1 | 501.2833 | 501.2833 | 0.00030464 | 6.0773e-05
2013-01-13 | 202:34260 | URBAN | Other | 921837 | 2429 | 5 | 12145 | 0.0073809 | 0.14762
2013-01-13 | ZN1164:PA20 | URBAN | Other | 921841 | 1 | 94.8667 | 94.8667 | 5.7653e-05 | 6.0773e-05
2013-01-13 | 221:11900 | URBAN | Other | 921844 | 1 | 237.6333 | 237.6333 | 0.00014442 | 6.0773e-05
2013-01-13 | ZN931:PA7 | URBAN | Equipment Failure | 921847 | 1 | 321.6667 | 321.6667 | 0.00019549 | 6.0773e-05
2013-01-13 | 811:74234 | SHORT RURAL | Other | 921849 | 2 | 210 | 420 | 0.00025525 | 0.00012155
2013-01-13 | 240:34835 | URBAN | Other | 921850 | 1 | 303.85 | 303.85 | 0.00018466 | 6.0773e-05
2013-01-13 | 526:34640 | SHORT RURAL | Other | 921852 | 5 | 101 | 505 | 0.0003069 | 0.00030386
2013-01-13 | ZN15006:PA12 | URBAN | Third Party Impacts | 921853 | 805 | 49.15 | 39565.75 | 0.024045 | 0.048922
2013-01-13 | ZN2196:PA2 | URBAN | Equipment Failure | 921862 | 1 | 361.1333 | 361.1333 | 0.00021947 | 6.0773e-05
2013-01-13 | ZN35500:PA24 | URBAN | Other | 921863 | 1 | 870.3667 | 870.3667 | 0.00052895 | 6.0773e-05
2013-01-13 | ZN9037:PA8 | URBAN | Other | 921864 | 1 | 164.4833 | 164.4833 | 9.9961e-05 | 6.0773e-05
2013-01-13 | 514:18137 | SHORT RURAL | Other | 921868 | 1 | 247.85 | 247.85 | 0.00015063 | 6.0773e-05
2013-01-13 | ZN187:PA7 | URBAN | Other | 921871 | 2 | 197 | 394 | 0.00023945 | 0.00012155
2013-01-13 | ZN5868:PA27 | URBAN | Other | 921871 | 15 | 197 | 2940.75 | 0.0017872 | 0.00091159
2013-01-13 | ZN2196:PA5 | URBAN | Other | 921873 | 1 | 250.1 | 250.1 | 0.00015199 | 6.0773e-05
2013-01-13 | ZN3672:PA13 | URBAN | Other | 921877 | 1 | 693.7167 | 693.7167 | 0.00042159 | 6.0773e-05
2013-01-13 | ZN269:PA9 | URBAN | Other | 921878 | 86 | 119.3333 | 10262.6667 | 0.0062369 | 0.0052265
2013-01-13 | 503:48016 | URBAN | Other | 921880 | 1 | 341.6333 | 341.6333 | 0.00020762 | 6.0773e-05
2013-01-13 | 803:74016 | SHORT RURAL | Other | 921881 | 2 | 192 | 384 | 0.00023337 | 0.00012155
2013-01-13 | ZN36300:PA9 | URBAN | Other | 921889 | 1 | 94.3 | 94.3 | 5.7309e-05 | 6.0773e-05
2013-01-13 | ZN2310:PA37 | URBAN | Other | 921890 | 1 | 387.9833 | 387.9833 | 0.00023579 | 6.0773e-05
2013-01-13 | ZN188:PA1 | URBAN | Equipment Failure | 921891 | 983 | 57 | 52902 | 0.03215 | 0.05974
2013-01-13 | ZN188:PA17 | URBAN | Equipment Failure | 921891 | 1102 | 57 | 62814 | 0.038174 | 0.066972
2013-01-13 | 515:35193 | SHORT RURAL | Equipment Failure | 921896 | 6 | 286 | 1716 | 0.0010429 | 0.00036464
2013-01-13 | ZN13000:PA8 | SHORT RURAL | Equipment Failure | 921898 | 135 | 202 | 17400 | 0.010574 | 0.0082043
2013-01-13 | 224:80340 | SHORT RURAL | Other | 921905 | 1 | 875.3833 | 875.3833 | 0.000532 | 6.0773e-05
2013-01-13 | ZN690:PA26 | URBAN | Other | 921916 | 1 | 341.1 | 341.1 | 0.0002073 | 6.0773e-05
2013-01-13 | 501:48123 | SHORT RURAL | Other | 921919 | 1 | 344.2833 | 344.2833 | 0.00020923 | 6.0773e-05
2013-01-13 | ZN10995:PA2 | URBAN | Other | 921921 | 1 | 312.2167 | 312.2167 | 0.00018974 | 6.0773e-05
2013-01-13 | ZN931:PA7 | URBAN | Equipment Failure | 921923 | 1 | 120.5667 | 120.5667 | 7.3272e-05 | 6.0773e-05
2013-01-13 | ZN8000:PA19 | URBAN | Equipment Failure | 921927 | 42 | 89 | 3738 | 0.0022717 | 0.0025525
2013-01-14 | ZN9550:PA42 | URBAN | Vegetation | 921940 | 1 | 206.8667 | 206.8667 | 0.00012572 | 6.0773e-05
2013-01-14 | ZN965:PA33 | URBAN | Vegetation | 921946 | 20 | 112 | 2240 | 0.0013613 | 0.0012155
2013-01-14 | 806:74080 | SHORT RURAL | Other | 921964 | 1 | 328.6 | 328.6 | 0.0001997 | 6.0773e-05
2013-01-14 | ZN35600:PA14 | URBAN | Other | 921967 | 1 | 152.6333 | 152.6333 | 9.276e-05 | 6.0773e-05
2013-01-14 | 217:33612 | URBAN | Equipment Failure | 921969 | 1 | 1017.4833 | 1017.4833 | 0.00061835 | 6.0773e-05
2013-01-14 | 235:2123 | URBAN | Other | 921970 | 1 | 52.9167 | 52.9167 | 3.2159e-05 | 6.0773e-05
2013-01-14 | 515:35193 | SHORT RURAL | Equipment Failure | 921973 | 17 | 769.4667 | 13080.9333 | 0.0079497 | 0.0010331
2013-01-14 | 514:18137 | SHORT RURAL | Equipment Failure | 921974 | 1 | 145 | 145 | 8.8121e-05 | 6.0773e-05
2013-01-14 | 813:89062 | SHORT RURAL | Vegetation | 921976 | 1 | 446.1667 | 446.1667 | 0.00027115 | 6.0773e-05
2013-01-14 | ZN9037:PA10 | URBAN | Other | 921979 | 1 | 181.9833 | 181.9833 | 0.0001106 | 6.0773e-05
2013-01-14 | 235:2120 | SHORT RURAL | Equipment Failure | 921981 | 1 | 58 | 58 | 3.5248e-05 | 6.0773e-05
2013-01-14 | 243:80084 | SHORT RURAL | Operational Error | 922000 | 18 | 89 | 1602 | 0.00097358 | 0.0010939
2013-01-14 | ZN15008:PA7 | URBAN | Other | 922014 | 1 | 475.3833 | 475.3833 | 0.0002889 | 6.0773e-05
2013-01-14 | 811:74234 | SHORT RURAL | Weather | 922015 | 1 | 292.75 | 292.75 | 0.00017791 | 6.0773e-05
2013-01-14 | 802:82215 | SHORT RURAL | Other | 922018 | 2 | 132 | 264 | 0.00016044 | 0.00012155
2013-01-14 | 813:89061 | LONG RURAL | Weather | 922020 | 1 | 232.9667 | 232.9667 | 0.00014158 | 6.0773e-05
2013-01-14 | 801:74121 | SHORT RURAL | Other | 922025 | 2 | 285 | 570 | 0.00034641 | 0.00012155
2013-01-14 | ZN1068:PA17 | URBAN | Other | 922062 | 1 | 360.35 | 360.35 | 0.000219 | 6.0773e-05
2013-01-14 | ZN12620:PA8 | SHORT RURAL | Equipment Failure | 922074 | 64 | 50.1167 | 3207.4667 | 0.0019493 | 0.0038895
2013-01-14 | 509:48039 | LONG RURAL | Other | 922080 | 2 | 345 | 690 | 0.00041933 | 0.00012155
2013-01-14 | ZN340:PA27 | URBAN | Other | 922081 | 1 | 183.85 | 183.85 | 0.00011173 | 6.0773e-05
2013-01-14 | 803:74010 | SHORT RURAL | Weather | 922121 | 1 | 138.3167 | 138.3167 | 8.4059e-05 | 6.0773e-05
2013-01-14 | ZN340:PA27 | URBAN | Other | 922130 | 1 | 134.4333 | 134.4333 | 8.1699e-05 | 6.0773e-05
2013-01-14 | ZN269:PA18 | URBAN | Other | 922133 | 1 | 132.6167 | 132.6167 | 8.0595e-05 | 6.0773e-05
2013-01-14 | 801:74118 | URBAN | Vegetation | 922149 | 1 | 55.2667 | 55.2667 | 3.3587e-05 | 6.0773e-05
2013-01-14 | 504:48031 | SHORT RURAL | Other | 922163 | 1 | 422.4333 | 422.4333 | 0.00025673 | 6.0773e-05
2013-01-14 | 511:29878 | SHORT RURAL | Equipment Failure | 922164 | 1 | 158.3167 | 158.3167 | 9.6214e-05 | 6.0773e-05
2013-01-14 | ZN12610:PA18 | URBAN | Equipment Failure | 922188 | 37 | 225.2 | 8332.4 | 0.0050638 | 0.0022486
2013-01-14 | ZN13000:PA2 | URBAN | Equipment Failure | 922194 | 1 | 101.8167 | 101.8167 | 6.1877e-05 | 6.0773e-05
2013-01-14 | 813:89061 | LONG RURAL | Equipment Failure | 922195 | 1 | 300 | 300 | 0.00018232 | 6.0773e-05
2013-01-14 | 515:35198 | SHORT RURAL | Weather | 922207 | 1 | 555.4167 | 555.4167 | 0.00033754 | 6.0773e-05
2013-01-14 | ZN12650:PA6 | URBAN | Equipment Failure | 922215 | 1632 | 190 | 112982 | 0.068662 | 0.099181
2013-01-14 | 813:89061 | LONG RURAL | Weather | 922220 | 1 | 2.1333 | 2.1333 | 1.2965e-06 | 6.0773e-05
2013-01-14 | 806:74080 | SHORT RURAL | Vegetation | 922234 | 1 | 68.15 | 68.15 | 4.1417e-05 | 6.0773e-05
2013-01-12 | 526:34636 | SHORT RURAL | Other | 922249 | 379 | 53 | 20087 | 0.012207 | 0.023033
2013-01-14 | ZN398:PA16 | URBAN | Other | 922250 | 1 | 192.5333 | 192.5333 | 0.00011701 | 6.0773e-05
2013-01-14 | ZN2196:PA5 | URBAN | Vegetation | 922257 | 26 | 68 | 1768 | 0.0010745 | 0.0015801
2013-01-14 | 806:74080 | SHORT RURAL | Other | 922269 | 1 | 185 | 185 | 0.00011243 | 6.0773e-05
2013-01-14 | ZN15008:PA7 | URBAN | Other | 922272 | 1 | 282.4667 | 282.4667 | 0.00017166 | 6.0773e-05
2013-01-14 | 803:74007 | SHORT RURAL | Other | 922277 | 1 | 163.7667 | 163.7667 | 9.9526e-05 | 6.0773e-05
2013-01-14 | ZN15008:PA7 | URBAN | Equipment Failure | 922284 | 1 | 312.5167 | 312.5167 | 0.00018993 | 6.0773e-05
2013-01-14 | 224:80340 | SHORT RURAL | Vegetation | 922302 | 1 | 91.7 | 91.7 | 5.5729e-05 | 6.0773e-05
2013-01-14 | 206:34441 | URBAN | Other | 922311 | 1 | 225.05 | 225.05 | 0.00013677 | 6.0773e-05
2013-01-14 | 260:33344 | URBAN | Other | 922327 | 1 | 120.1333 | 120.1333 | 7.3009e-05 | 6.0773e-05
2013-01-13 | 526:34640 | SHORT RURAL | Other | 922334 | 5 | 123 | 615 | 0.00037375 | 0.00030386
2013-01-14 | 806:74076 | SHORT RURAL | Vegetation | 922344 | 1 | 60 | 60 | 3.6464e-05 | 6.0773e-05
2013-01-14 | ZN847:PA10 | URBAN | Vegetation | 922347 | 119 | 228 | 27132 | 0.016489 | 0.007232
2013-01-14 | 801:74121 | SHORT RURAL | Other | 922367 | 4 | 198.8 | 795.2 | 0.00048327 | 0.00024309
2013-01-14 | ZN14892:PA19 | URBAN | Equipment Failure | 922383 | 1 | 200.3667 | 200.3667 | 0.00012177 | 6.0773e-05
2013-01-14 | 217:33612 | URBAN | Other | 922399 | 1 | 47.4333 | 47.4333 | 2.8827e-05 | 6.0773e-05
2013-01-14 | 224:80340 | SHORT RURAL | Vegetation | 922401 | 1 | 164.25 | 164.25 | 9.982e-05 | 6.0773e-05
2013-01-14 | 227:13015 | SHORT RURAL | Other | 922414 | 1 | 94.7833 | 94.7833 | 5.7603e-05 | 6.0773e-05
2013-01-14 | ZN1287:PA15 | URBAN | Vegetation | 922419 | 1 | 381.1167 | 381.1167 | 0.00023162 | 6.0773e-05
2013-01-14 | ZN3472:PA28 | URBAN | Equipment Failure | 922420 | 1 | 141.2833 | 141.2833 | 8.5862e-05 | 6.0773e-05
2013-01-14 | 264:81240 | SHORT RURAL | Equipment Failure | 922425 | 1 | 158.95 | 158.95 | 9.6599e-05 | 6.0773e-05
2013-01-14 | 803:74010 | SHORT RURAL | Other | 922431 | 2 | 120 | 240 | 0.00014585 | 0.00012155
2013-01-14 | ZN342:PA17 | URBAN | Equipment Failure | 922438 | 1 | 233.5167 | 233.5167 | 0.00014191 | 6.0773e-05
2013-01-14 | 813:89061 | LONG RURAL | Other | 922446 | 4 | 255 | 1020 | 0.00061988 | 0.00024309
2013-01-14 | 813:89055 | SHORT RURAL | Equipment Failure | 922457 | 1 | 59 | 59 | 3.5856e-05 | 6.0773e-05
2013-01-14 | 813:89062 | SHORT RURAL | Other | 922461 | 5 | 305 | 1525 | 0.00092679 | 0.00030386
2013-01-14 | ZN36300:PA9 | URBAN | Equipment Failure | 922462 | 1 | 59.1 | 59.1 | 3.5917e-05 | 6.0773e-05
2013-01-14 | ZN690:PA17 | URBAN | Other | 922464 | 1 | 233.4 | 233.4 | 0.00014184 | 6.0773e-05
2013-01-14 | ZN80:PA32 | URBAN | Vegetation | 922469 | 56 | 137 | 7672 | 0.0046625 | 0.0034033
2013-01-14 | 813:89061 | LONG RURAL | Other | 922474 | 598 | 120 | 71760 | 0.043611 | 0.036342
2013-01-15 | ZN15004:PA5 | URBAN | Animals | 922481 | 1447 | 76 | 109972 | 0.066833 | 0.087938
2013-01-15 | ZN14891:PA5 | SHORT RURAL | Other | 922482 | 1 | 419.85 | 419.85 | 0.00025516 | 6.0773e-05
2013-01-15 | 243:80083 | SHORT RURAL | Other | 922483 | 342 | 21 | 7182 | 0.0043647 | 0.020784
2013-01-15 | 261:81864 | URBAN | Other | 922491 | 44 | 73.3667 | 3228.1333 | 0.0019618 | 0.002674
2013-01-10 | 803:74016 | SHORT RURAL | Other | 922502 | 1 | 260 | 260 | 0.00015801 | 6.0773e-05
2013-01-10 | 513:48059 | SHORT RURAL | Other | 922505 | 1 | 30 | 30 | 1.8232e-05 | 6.0773e-05
2013-01-15 | ZN4545:PA35 | URBAN | Other | 922509 | 1 | 127.8 | 127.8 | 7.7668e-05 | 6.0773e-05
2013-01-10 | 801:74121 | SHORT RURAL | Other | 922517 | 2 | 35 | 70 | 4.2541e-05 | 0.00012155
2013-01-15 | 813:89061 | LONG RURAL | Operational Error | 922521 | 1 | 92 | 92 | 5.5911e-05 | 6.0773e-05
2013-01-10 | 523:33501 | SHORT RURAL | Other | 922525 | 8 | 62 | 496 | 0.00030143 | 0.00048618
2013-01-12 | 513:48050 | SHORT RURAL | Other | 922594 | 177 | 210 | 37170 | 0.022589 | 0.010757
2013-01-15 | ZN12630:PA5 | SHORT RURAL | Equipment Failure | 922603 | 1 | 320.1 | 320.1 | 0.00019453 | 6.0773e-05
2013-01-12 | ZN1673:PA7 | URBAN | Vegetation | 922624 | 67 | 30 | 2010 | 0.0012215 | 0.0040718
2013-01-12 | 512:48049 | SHORT RURAL | Other | 922639 | 909 | 658 | 370856 | 0.22538 | 0.055243
2013-01-12 | 513:48059 | SHORT RURAL | Other | 922659 | 232 | 356 | 82592 | 0.050194 | 0.014099
2013-01-12 | 520:48172 | SHORT RURAL | Other | 922662 | 255 | 280 | 71400 | 0.043392 | 0.015497
2013-01-12 | 813:89062 | SHORT RURAL | Other | 922697 | 1 | 350 | 350 | 0.00021271 | 6.0773e-05
2013-01-15 | 217:33612 | URBAN | Other | 922719 | 1 | 74.7 | 74.7 | 4.5397e-05 | 6.0773e-05
2013-01-15 | 229:34986 | SHORT RURAL | Other | 922733 | 1 | 104.3167 | 104.3167 | 6.3396e-05 | 6.0773e-05
2013-01-13 | 512:48049 | SHORT RURAL | Other | 922735 | 3 | 300 | 900 | 0.00054696 | 0.00018232
2013-01-15 | 208:53 | URBAN | Other | 922755 | 1 | 144.85 | 144.85 | 8.803e-05 | 6.0773e-05
2013-01-15 | 814:82283 | SHORT RURAL | Equipment Failure | 922771 | 1 | 35.3833 | 35.3833 | 2.1503e-05 | 6.0773e-05
2013-01-13 | 801:74121 | SHORT RURAL | Other | 922789 | 2 | 540 | 1080 | 0.00065635 | 0.00012155
2013-01-13 | 513:48059 | SHORT RURAL | Other | 922818 | 2 | 238 | 476 | 0.00028928 | 0.00012155
2013-01-15 | 801:74118 | URBAN | Equipment Failure | 922837 | 1 | 61.9167 | 61.9167 | 3.7629e-05 | 6.0773e-05
2013-01-13 | 806:74080 | SHORT RURAL | Equipment Failure | 922839 | 15 | 80 | 1200 | 0.00072927 | 0.00091159
2013-01-15 | ZN12570:PA24 | SHORT RURAL | Equipment Failure | 922854 | 8 | 172 | 1376 | 0.00083624 | 0.00048618
2013-01-15 | 514:18146 | SHORT RURAL | Other | 922892 | 1 | 77 | 77 | 4.6795e-05 | 6.0773e-05
2013-01-15 | 813:89062 | SHORT RURAL | Other | 922909 | 2 | 125 | 250 | 0.00015193 | 0.00012155
2013-01-15 | 229:34992 | URBAN | Other | 922914 | 1 | 158.45 | 158.45 | 9.6295e-05 | 6.0773e-05
2013-01-15 | ZN1285:PA10 | URBAN | Other | 922918 | 1 | 151.85 | 151.85 | 9.2284e-05 | 6.0773e-05
2013-01-15 | ZN965:PA35 | URBAN | Equipment Failure | 922921 | 1 | 99.8 | 99.8 | 6.0651e-05 | 6.0773e-05
2013-01-15 | 807:74184 | SHORT RURAL | Other | 922935 | 7 | 60 | 420 | 0.00025525 | 0.00042541
2013-01-15 | ZN9118:PA21 | URBAN | Equipment Failure | 922948 | 45 | 111 | 2337.4 | 0.0014205 | 0.0027348
2013-01-15 | ZN2196:PA5 | URBAN | Equipment Failure | 922963 | 1 | 231.1167 | 231.1167 | 0.00014046 | 6.0773e-05
2013-01-16 | ZN3155:PA44 | URBAN | Other | 922969 | 218 | 118 | 25724 | 0.015633 | 0.013248
2013-01-16 | ZN262:PA42 | URBAN | Equipment Failure | 922977 | 1 | 327.3333 | 327.3333 | 0.00019893 | 6.0773e-05
2013-01-16 | ZN262:PA42 | URBAN | Equipment Failure | 922979 | 1 | 261.05 | 261.05 | 0.00015865 | 6.0773e-05
2013-01-16 | 240:34843 | URBAN | Third Party Impacts | 922981 | 1 | 491.2 | 491.2 | 0.00029852 | 6.0773e-05
2013-01-16 | ZN9900:PA1 | URBAN | Other | 922982 | 59 | 140 | 8244.4 | 0.0050104 | 0.0035856
2013-01-16 | ZN9900:PA6 | URBAN | Other | 922982 | 1 | 140 | 140 | 8.5082e-05 | 6.0773e-05
2013-01-16 | ZN1193:PA9 | URBAN | Equipment Failure | 922994 | 1 | 111.3833 | 111.3833 | 6.7691e-05 | 6.0773e-05
2013-01-16 | ZN36300:PA11 | URBAN | Equipment Failure | 923006 | 1 | 251.5333 | 251.5333 | 0.00015286 | 6.0773e-05
2013-01-16 | ZN10999:PA11 | URBAN | Third Party Impacts | 923012 | 39 | 143.5167 | 5597.15 | 0.0034016 | 0.0023701
2013-01-16 | 514:18137 | SHORT RURAL | Other | 923027 | 1 | 218.6333 | 218.6333 | 0.00013287 | 6.0773e-05
2013-01-13 | 513:48059 | SHORT RURAL | Other | 923047 | 1 | 295 | 295 | 0.00017928 | 6.0773e-05
2013-01-13 | 811:74234 | SHORT RURAL | Equipment Failure | 923115 | 1 | 1402 | 1402 | 0.00085204 | 6.0773e-05
2013-01-14 | 811:74234 | SHORT RURAL | Other | 923116 | 6 | 20 | 120 | 7.2927e-05 | 0.00036464
2013-01-14 | 811:74234 | SHORT RURAL | Other | 923117 | 6 | 20 | 120 | 7.2927e-05 | 0.00036464
2013-01-16 | ZN14892:PA16 | URBAN | Other | 923123 | 1 | 110.2833 | 110.2833 | 6.7022e-05 | 6.0773e-05
2013-01-16 | 232:11454 | SHORT RURAL | Other | 923126 | 1 | 498.8833 | 498.8833 | 0.00030319 | 6.0773e-05
2013-01-16 | ZN10990:PA5 | URBAN | Equipment Failure | 923153 | 172 | 59 | 10148 | 0.0061672 | 0.010453
2013-01-14 | 507:80923 | SHORT RURAL | Equipment Failure | 923160 | 100 | 30 | 3000 | 0.0018232 | 0.0060773
2013-01-14 | 813:89062 | SHORT RURAL | Other | 923163 | 1 | 288 | 288 | 0.00017503 | 6.0773e-05
2013-01-14 | 806:74080 | SHORT RURAL | Other | 923174 | 1 | 285 | 285 | 0.0001732 | 6.0773e-05
2013-01-16 | 240:34835 | URBAN | Other | 923204 | 1 | 236.5667 | 236.5667 | 0.00014377 | 6.0773e-05
2013-01-16 | ZN129:PA3 | URBAN | Equipment Failure | 923205 | 81 | 276.2333 | 22374.9 | 0.013598 | 0.0049226
2013-01-14 | 813:89061 | LONG RURAL | Other | 923207 | 3 | 119 | 357 | 0.00021696 | 0.00018232
2013-01-09 | ZN1788:PA30 | URBAN | Equipment Failure | 923212 | 60 | 114 | 6840 | 0.0041569 | 0.0036464
2013-01-16 | 216:10727 | URBAN | Equipment Failure | 923249 | 1 | 237.7333 | 237.7333 | 0.00014448 | 6.0773e-05
2013-01-16 | ZN10991:PA12 | URBAN | Equipment Failure | 923252 | 1 | 111.9833 | 111.9833 | 6.8056e-05 | 6.0773e-05
2013-01-16 | 802:82215 | SHORT RURAL | Equipment Failure | 923291 | 1 | 309 | 309 | 0.00018779 | 6.0773e-05
2013-01-11 | ZN10996:PA19 | URBAN | Equipment Failure | 923312 | 90 | 3 | 270 | 0.00016409 | 0.0054696
2013-01-16 | ZN2310:PA27 | URBAN | Third Party Impacts | 923328 | 188 | 219 | 41172 | 0.025021 | 0.011425
2013-01-16 | ZN9037:PA3 | URBAN | Third Party Impacts | 923332 | 1 | 280.4167 | 280.4167 | 0.00017042 | 6.0773e-05
2013-01-16 | ZN965:PA38 | URBAN | Equipment Failure | 923363 | 14 | 192.3833 | 2693.3667 | 0.0016368 | 0.00085082
2013-01-16 | ZN269:PA3 | URBAN | Equipment Failure | 923369 | 1 | 330.2167 | 330.2167 | 0.00020068 | 6.0773e-05
2013-01-16 | 513:48059 | SHORT RURAL | Other | 923371 | 4 | 55 | 220 | 0.0001337 | 0.00024309
2013-01-16 | 223:14398 | URBAN | Other | 923428 | 1 | 123.9667 | 123.9667 | 7.5338e-05 | 6.0773e-05
2013-01-17 | 514:18137 | SHORT RURAL | Equipment Failure | 923451 | 29 | 166 | 1342 | 0.0008204 | 0.0017728
2013-01-16 | 802:82215 | SHORT RURAL | Other | 923475 | 39 | 2 | 78 | 4.7403e-05 | 0.0023701
2013-01-17 | 503:48078 | URBAN | Third Party Impacts | 923553 | 1591 | 55 | 84418 | 0.051607 | 0.097262
2013-01-17 | 228:7490 | SHORT RURAL | Other | 923554 | 1 | 54.2 | 54.2 | 3.3134e-05 | 6.1132e-05
2013-01-17 | ZN1290:PA12 | URBAN | Third Party Impacts | 923566 | 32 | 120.6167 | 3859.7333 | 0.0023595 | 0.0019562
2013-01-17 | 258:80779 | URBAN | Equipment Failure | 923589 | 1 | 124.9333 | 124.9333 | 7.6375e-05 | 6.1132e-05
2013-01-17 | 814:82283 | SHORT RURAL | Other | 923602 | 1 | 142 | 142 | 8.6808e-05 | 6.1132e-05
2013-01-17 | ZN72:PA17 | URBAN | Other | 923646 | 73 | 12.05 | 879.65 | 0.00053775 | 0.0044627
2013-01-17 | 264:81240 | SHORT RURAL | Other | 923658 | 1 | 122.0333 | 122.0333 | 7.4602e-05 | 6.1132e-05
2013-01-17 | 217:33610 | URBAN | Other | 923672 | 1 | 82.8167 | 82.8167 | 5.0628e-05 | 6.1132e-05
2013-01-17 | 238:34141 | SHORT RURAL | Other | 923683 | 1 | 310.65 | 310.65 | 0.00018991 | 6.1132e-05
2013-01-17 | ZN12570:PA40 | SHORT RURAL | Vegetation | 923699 | 1 | 298.0167 | 298.0167 | 0.00018218 | 6.1132e-05
2013-01-17 | ZN15006:PA12 | URBAN | Other | 923719 | 1 | 37.95 | 37.95 | 2.32e-05 | 6.1132e-05
2013-01-17 | ZN2568:PA32 | URBAN | Equipment Failure | 923752 | 64 | 70 | 4438.4833 | 0.0027133 | 0.0039125
2013-01-17 | 523:33501 | SHORT RURAL | Other | 923764 | 3 | 68 | 204 | 0.00012471 | 0.0001834
2013-01-17 | 214:8669 | URBAN | Other | 923766 | 1 | 199.2333 | 199.2333 | 0.0001218 | 6.1132e-05
2013-01-17 | ZN35500:PA28 | URBAN | Vegetation | 923768 | 1 | 232.0833 | 232.0833 | 0.00014188 | 6.1132e-05
2013-01-17 | ZN3425:PA8 | URBAN | Equipment Failure | 923774 | 273 | 51 | 13901 | 0.008498 | 0.016689
2013-01-17 | ZN15010:PA11 | URBAN | Equipment Failure | 923789 | 58 | 45.6833 | 2649.6333 | 0.0016198 | 0.0035457
2013-01-18 | 208:62 | URBAN | Equipment Failure | 923795 | 94 | 60 | 5640 | 0.0034479 | 0.0057465
2013-01-18 | ZN847:PA5 | URBAN | Equipment Failure | 923811 | 1030 | 92 | 89951 | 0.054989 | 0.062967
2013-01-18 | ZN690:PA30 | URBAN | Other | 923831 | 1 | 211.95 | 211.95 | 0.00012957 | 6.1133e-05
2013-01-18 | ZN269:PA1 | URBAN | Equipment Failure | 923864 | 1 | 33.7667 | 33.7667 | 2.0642e-05 | 6.1133e-05
2013-01-18 | 216:10724 | SHORT RURAL | Equipment Failure | 923865 | 16 | 95 | 1520 | 0.00092921 | 0.00097812
2013-01-18 | 258:80781 | SHORT RURAL | Other | 923875 | 1 | 64.5667 | 64.5667 | 3.9471e-05 | 6.1133e-05
2013-01-12 | 806:74080 | SHORT RURAL | Other | 923916 | 200 | 249 | 45528 | 0.027669 | 0.012155
2013-01-18 | ZN1788:PA29 | URBAN | Other | 923946 | 42 | 65.9667 | 2770.6 | 0.0016937 | 0.0025676
2013-01-18 | ZN2568:PA38 | URBAN | Equipment Failure | 923948 | 1 | 483.6833 | 483.6833 | 0.00029569 | 6.1133e-05
2013-01-18 | 261:81885 | URBAN | Other | 923950 | 71 | 107.25 | 7614.75 | 0.0046551 | 0.0043404
2013-01-18 | 813:89055 | SHORT RURAL | Equipment Failure | 923956 | 1 | 116.4667 | 116.4667 | 7.1199e-05 | 6.1133e-05
2013-01-14 | ZN10994:PA21 | URBAN | Vegetation | 923969 | 32 | 140 | 4480 | 0.0027226 | 0.0019447
2013-01-18 | 813:89061 | LONG RURAL | Weather | 923978 | 1 | 4.6167 | 4.6167 | 2.8223e-06 | 6.1133e-05
2013-01-18 | ZN2568:PA30 | URBAN | Third Party Impacts | 923981 | 10 | 133 | 1330 | 0.00081306 | 0.00061133
2013-01-18 | 513:48059 | SHORT RURAL | Vegetation | 923986 | 1 | 88.6667 | 88.6667 | 5.4204e-05 | 6.1133e-05
2013-01-18 | 801:74121 | SHORT RURAL | Equipment Failure | 924003 | 1 | 230.9333 | 230.9333 | 0.00014118 | 6.1133e-05
2013-01-18 | ZN187:PA21 | URBAN | Vegetation | 924004 | 100 | 43.4167 | 4341.6667 | 0.0026542 | 0.0061133
2013-01-18 | ZN14892:PA16 | URBAN | Equipment Failure | 924009 | 1 | 160.7167 | 160.7167 | 9.825e-05 | 6.1133e-05
2013-01-18 | ZN14892:PA16 | URBAN | Equipment Failure | 924012 | 1 | 152.65 | 152.65 | 9.3319e-05 | 6.1133e-05
2013-01-18 | ZN12650:PA5 | URBAN | Equipment Failure | 924014 | 369 | 1054 | 57120 | 0.034919 | 0.022558
2013-01-18 | ZN15004:PA9 | URBAN | Equipment Failure | 924016 | 35 | 266 | 9310 | 0.0056914 | 0.0021396
2013-01-18 | ZN10994:PA20 | URBAN | Equipment Failure | 924027 | 1 | 92 | 92 | 5.6242e-05 | 6.1133e-05
2013-01-18 | ZN10994:PA4 | URBAN | Equipment Failure | 924027 | 1612 | 92 | 90822 | 0.055522 | 0.098546
2013-01-18 | ZN10995:PA1 | URBAN | Equipment Failure | 924027 | 40 | 92 | 3680 | 0.0022497 | 0.0024453
2013-01-18 | ZN10995:PA2 | URBAN | Equipment Failure | 924027 | 1 | 92 | 44 | 2.6898e-05 | 6.1133e-05
2013-01-18 | ZN12610:PA10 | SHORT RURAL | Equipment Failure | 924072 | 2547 | 124 | 98510 | 0.060222 | 0.1557
2013-01-18 | ZN12610:PA18 | URBAN | Equipment Failure | 924072 | 789 | 124 | 82056 | 0.050163 | 0.048234
2013-01-18 | 811:74234 | SHORT RURAL | Other | 924078 | 1 | 145 | 145 | 8.8642e-05 | 6.1133e-05
2013-01-18 | ZN1788:PA29 | URBAN | Equipment Failure | 924088 | 1 | 295.6667 | 295.6667 | 0.00018075 | 6.1133e-05
2013-01-18 | ZN13000:PA11 | URBAN | Equipment Failure | 924105 | 18 | 655 | 11790 | 0.0072075 | 0.0011004
2013-01-18 | 258:80781 | SHORT RURAL | Other | 924108 | 1 | 210.2833 | 210.2833 | 0.00012855 | 6.1133e-05
2013-01-18 | 810:74054 | LONG RURAL | Other | 924111 | 1 | 5 | 5 | 3.0566e-06 | 6.1133e-05
2013-01-18 | ZN1788:PA11 | URBAN | Equipment Failure | 924114 | 11 | 176 | 1936 | 0.0011835 | 0.00067246
2013-01-18 | ZN3672:PA42 | URBAN | Equipment Failure | 924114 | 26 | 176 | 4576 | 0.0027974 | 0.0015894
2013-01-18 | 214:8666 | URBAN | Other | 924133 | 1 | 118.8333 | 118.8333 | 7.2646e-05 | 6.1133e-05
2013-01-18 | ZN14892:PA13 | URBAN | Equipment Failure | 924143 | 53 | 630 | 33390 | 0.020412 | 0.00324
2013-01-18 | ZN1290:PA12 | URBAN | Equipment Failure | 924145 | 1050 | 443 | 82506 | 0.050438 | 0.064189
2013-01-18 | ZN12570:PA41 | URBAN | Equipment Failure | 924147 | 4 | 1229 | 4916 | 0.0030053 | 0.00024453
2013-01-18 | ZN12610:PA10 | SHORT RURAL | Equipment Failure | 924148 | 2 | 214 | 198 | 0.00012104 | 0.00012227
2013-01-18 | ZN12610:PA16 | URBAN | Equipment Failure | 924148 | 1 | 214 | 198 | 0.00012104 | 6.1133e-05
2013-01-18 | ZN12610:PA22 | URBAN | Equipment Failure | 924148 | 2162 | 214 | 351993 | 0.21518 | 0.13217
2013-01-18 | ZN3472:PA34 | URBAN | Equipment Failure | 924176 | 529 | 85 | 41971 | 0.025658 | 0.032339
2013-01-18 | ZN14143:PA17 | SHORT RURAL | Equipment Failure | 924179 | 40 | 1471 | 58840 | 0.03597 | 0.0024453
2013-01-18 | ZN9252:PA2 | URBAN | Other | 924182 | 42 | 1313 | 55146 | 0.033712 | 0.0025676
2013-01-18 | ZN9252:PA8 | URBAN | Other | 924182 | 56 | 1313 | 72128 | 0.044094 | 0.0034234
2013-01-18 | 240:34835 | URBAN | Other | 924191 | 1 | 201.7167 | 201.7167 | 0.00012331 | 6.1133e-05
2013-01-18 | ZN3154:PA23 | URBAN | Equipment Failure | 924193 | 474 | 118 | 49785 | 0.030435 | 0.028977
2013-01-18 | ZN13000:PA7 | SHORT RURAL | Vegetation | 924200 | 1 | 582.6 | 582.6 | 0.00035616 | 6.1133e-05
2013-01-18 | ZN13000:PA7 | SHORT RURAL | Vegetation | 924202 | 1 | 581.15 | 581.15 | 0.00035527 | 6.1133e-05
2013-01-18 | ZN3425:PA32 | URBAN | Other | 924218 | 8 | 101 | 808 | 0.00049395 | 0.00048906
2013-01-18 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 924222 | 688 | 288 | 54352 | 0.033227 | 0.042059
2013-01-18 | ZN14891:PA14 | SHORT RURAL | Equipment Failure | 924222 | 410 | 288 | 32800 | 0.020051 | 0.025064
2013-01-18 | ZN14891:PA16 | SHORT RURAL | Equipment Failure | 924222 | 1636 | 288 | 130880 | 0.08001 | 0.10001
2013-01-18 | ZN14891:PA19 | URBAN | Equipment Failure | 924222 | 192 | 288 | 45108 | 0.027576 | 0.011737
2013-01-18 | ZN14891:PA20 | SHORT RURAL | Equipment Failure | 924222 | 513 | 288 | 41040 | 0.025089 | 0.031361
2013-01-18 | ZN14891:PA21 | SHORT RURAL | Equipment Failure | 924222 | 537 | 288 | 43497 | 0.026591 | 0.032828
2013-01-18 | ZN8100:PA20 | URBAN | Other | 924228 | 40 | 181.25 | 7250 | 0.0044321 | 0.0024453
2013-01-18 | ZN12570:PA22 | URBAN | Equipment Failure | 924230 | 1591 | 125 | 154814 | 0.094642 | 0.097262
2013-01-18 | ZN12660:PA6 | SHORT RURAL | Equipment Failure | 924230 | 1 | 125 | 125 | 7.6416e-05 | 6.1133e-05
2013-01-18 | ZN35500:PA14 | URBAN | Equipment Failure | 924236 | 75 | 99 | 7025 | 0.0042946 | 0.0045849
2013-01-18 | 504:48028 | URBAN | Other | 924253 | 1 | 121.0667 | 121.0667 | 7.4011e-05 | 6.1133e-05
2013-01-18 | ZN72:PA30 | URBAN | Equipment Failure | 924259 | 84 | 419.65 | 35250.6 | 0.02155 | 0.0051351
2013-01-18 | 258:80775 | URBAN | Other | 924260 | 1 | 156.6333 | 156.6333 | 9.5754e-05 | 6.1133e-05
2013-01-18 | ZN8100:PA10 | URBAN | Equipment Failure | 924269 | 117 | 172 | 20124 | 0.012302 | 0.0071525
2013-01-18 | ZN3425:PA30 | URBAN | Equipment Failure | 924310 | 1 | 52.0167 | 52.0167 | 3.1799e-05 | 6.1133e-05
2013-01-18 | ZN12620:PA1 | SHORT RURAL | Equipment Failure | 924361 | 443 | 546 | 153947 | 0.094112 | 0.027082
2013-01-18 | 232:11457 | URBAN | Other | 924364 | 1 | 346.2667 | 346.2667 | 0.00021168 | 6.1133e-05
2013-01-18 | ZN13000:PA7 | SHORT RURAL | Equipment Failure | 924369 | 111 | 272.9667 | 30299.3 | 0.018523 | 0.0067857
2013-01-18 | 258:80776 | URBAN | Other | 924394 | 319 | 54 | 17226 | 0.010531 | 0.019501
2013-01-18 | ZN35370:PA10 | SHORT RURAL | Vegetation | 924395 | 3 | 110 | 330 | 0.00020174 | 0.0001834
2013-01-18 | ZN35370:PA2 | SHORT RURAL | Vegetation | 924395 | 15 | 110 | 1650 | 0.0010087 | 0.00091699
2013-01-18 | ZN12580:PA16 | URBAN | Equipment Failure | 924398 | 12 | 976.6167 | 11719.4 | 0.0071644 | 0.00073359
2013-01-18 | ZN965:PA26 | URBAN | Vegetation | 924401 | 32 | 117.4667 | 3758.9333 | 0.0022979 | 0.0019562
2013-01-18 | ZN12570:PA35 | URBAN | Equipment Failure | 924409 | 2 | 247.05 | 494.1 | 0.00030206 | 0.00012227
2013-01-18 | 234:2001 | URBAN | Other | 924413 | 1 | 128.95 | 128.95 | 7.883e-05 | 6.1133e-05
2013-01-18 | ZN3472:PA30 | URBAN | Weather | 924420 | 84 | 109 | 9156 | 0.0055973 | 0.0051351
2013-01-18 | ZN9245:PA15 | URBAN | Equipment Failure | 924422 | 1 | 193.6 | 193.6 | 0.00011835 | 6.1133e-05
2013-01-18 | ZN9245:PA3 | URBAN | Equipment Failure | 924422 | 45 | 193.6 | 7125.75 | 0.0043562 | 0.002751
2013-01-18 | 202:34250 | URBAN | Other | 924425 | 114 | 87.5 | 9975 | 0.006098 | 0.0069691
2013-01-18 | ZN12650:PA17 | URBAN | Equipment Failure | 924440 | 53 | 1075.1833 | 56984.7167 | 0.034836 | 0.00324
2013-01-18 | 520:48172 | SHORT RURAL | Other | 924441 | 1 | 69 | 69 | 4.2181e-05 | 6.1133e-05
2013-01-18 | ZN1285:PA19 | URBAN | Weather | 924453 | 1325 | 12 | 15900 | 0.0097201 | 0.081001
2013-01-18 | ZN3472:PA30 | URBAN | Weather | 924453 | 1440 | 12 | 17280 | 0.010564 | 0.088031
2013-01-18 | ZN15013:PA6 | SHORT RURAL | Vegetation | 924454 | 221 | 71 | 15691 | 0.0095923 | 0.01351
2013-01-18 | ZN15013:PA10 | SHORT RURAL | Vegetation | 924462 | 272 | 989 | 104978 | 0.064176 | 0.016628
2013-01-18 | 810:74058 | SHORT RURAL | Other | 924467 | 1 | 176.5167 | 176.5167 | 0.00010791 | 6.1133e-05
2013-01-18 | ZN3154:PA4 | URBAN | Vegetation | 924470 | 50 | 523.45 | 26172.5 | 0.016 | 0.0030566
2013-01-18 | ZN2568:PA27 | URBAN | Other | 924473 | 124 | 50 | 6200 | 0.0037902 | 0.0075804
2013-01-18 | 224:80337 | URBAN | Other | 924475 | 1 | 375.8 | 375.8 | 0.00022974 | 6.1133e-05
2013-01-18 | ZN15005:PA2 | URBAN | Other | 924476 | 1 | 59.8333 | 59.8333 | 3.6578e-05 | 6.1133e-05
2013-01-18 | ZN2466:PA45 | URBAN | Vegetation | 924483 | 54 | 266.2333 | 14376.6 | 0.0087888 | 0.0033012
2013-01-18 | ZN12640:PA13 | SHORT RURAL | Equipment Failure | 924484 | 43 | 978 | 42054 | 0.025709 | 0.0026287
2013-01-18 | ZN12690:PA7 | SHORT RURAL | Equipment Failure | 924503 | 50 | 152.3333 | 7616.6667 | 0.0046563 | 0.0030566
2013-01-18 | ZN10999:PA32 | URBAN | Vegetation | 924517 | 46 | 71.8167 | 3303.5667 | 0.0020196 | 0.0028121
2013-01-18 | ZN12600:PA9 | SHORT RURAL | Equipment Failure | 924531 | 9 | 1067 | 9603 | 0.0058706 | 0.00055019
2013-01-18 | 205:12203 | URBAN | Other | 924540 | 124 | 49 | 6076 | 0.0037144 | 0.0075804
2013-01-18 | 261:81864 | URBAN | Other | 924552 | 31 | 122.3 | 3791.3 | 0.0023177 | 0.0018951
2013-01-18 | 264:81244 | URBAN | Other | 924556 | 66 | 26.9667 | 1779.8 | 0.001088 | 0.0040347
2013-01-18 | 512:48046 | SHORT RURAL | Other | 924561 | 58 | 64 | 3712 | 0.0022692 | 0.0035457
2013-01-18 | 258:80784 | URBAN | Other | 924575 | 140 | 68 | 9520 | 0.0058198 | 0.0085586
2013-01-18 | 515:35197 | LONG RURAL | Vegetation | 924576 | 383 | 92 | 26107 | 0.01596 | 0.023414
2013-01-18 | 202:34260 | URBAN | Equipment Failure | 924583 | 201 | 234 | 47034 | 0.028753 | 0.012288
2013-01-18 | ZN4545:PA24 | URBAN | Other | 924596 | 69 | 1050.25 | 72467.25 | 0.044301 | 0.0042181
2013-01-18 | 217:33610 | URBAN | Other | 924601 | 112 | 84 | 9408 | 0.0057513 | 0.0068468
2013-01-18 | 238:34140 | URBAN | Equipment Failure | 924605 | 39 | 110.3833 | 4304.95 | 0.0026317 | 0.0023842
2013-01-18 | ZN10999:PA32 | URBAN | Equipment Failure | 924608 | 46 | 465.0667 | 21393.0667 | 0.013078 | 0.0028121
2013-01-18 | 515:35198 | SHORT RURAL | Other | 924611 | 75 | 47 | 3525 | 0.0021549 | 0.0045849
2013-01-18 | 264:81240 | SHORT RURAL | Other | 924616 | 16 | 369 | 5904 | 0.0036093 | 0.00097812
2013-01-18 | ZN9550:PA42 | URBAN | Vegetation | 924619 | 1 | 143.45 | 143.45 | 8.7695e-05 | 6.1133e-05
2013-01-18 | ZN1287:PA4 | URBAN | Vegetation | 924620 | 1 | 438.65 | 438.65 | 0.00026816 | 6.1133e-05
2013-01-18 | ZN4545:PA17 | URBAN | Other | 924621 | 41 | 74 | 3034 | 0.0018548 | 0.0025064
2013-01-18 | ZN4545:PA21 | URBAN | Other | 924621 | 38 | 74 | 2793 | 0.0017074 | 0.002323
2013-01-18 | 512:48049 | SHORT RURAL | Equipment Failure | 924622 | 180 | 881 | 52026 | 0.031805 | 0.011004
2013-01-18 | 258:80791 | URBAN | Other | 924623 | 1 | 127.0667 | 127.0667 | 7.7679e-05 | 6.1133e-05
2013-01-18 | ZN1287:PA24 | URBAN | Equipment Failure | 924627 | 152 | 141.8167 | 21556.1333 | 0.013178 | 0.0092921
2013-01-18 | 516:48067 | SHORT RURAL | Other | 924634 | 282 | 196 | 48262 | 0.029504 | 0.017239
2013-01-18 | ZN2310:PA38 | URBAN | Other | 924639 | 1 | 240.6333 | 240.6333 | 0.00014711 | 6.1133e-05
2013-01-18 | ZN10994:PA13 | URBAN | Vegetation | 924643 | 1070 | 150 | 92329 | 0.056443 | 0.065412
2013-01-18 | ZN10994:PA7 | URBAN | Vegetation | 924643 | 1 | 150 | 150 | 9.1699e-05 | 6.1133e-05
2013-01-18 | 526:34636 | SHORT RURAL | Other | 924648 | 2 | 115 | 230 | 0.0001406 | 0.00012227
2013-01-18 | ZN2835:PA41 | URBAN | Equipment Failure | 924651 | 1 | 118.0667 | 118.0667 | 7.2177e-05 | 6.1133e-05
2013-01-18 | 520:48172 | SHORT RURAL | Other | 924655 | 120 | 308 | 34187 | 0.020899 | 0.0073359
2013-01-18 | ZN2310:PA38 | URBAN | Other | 924657 | 1 | 226.0333 | 226.0333 | 0.00013818 | 6.1133e-05
2013-01-18 | ZN9550:PA42 | URBAN | Other | 924665 | 1 | 192.4833 | 192.4833 | 0.00011767 | 6.1133e-05
2013-01-18 | ZN10994:PA10 | URBAN | Vegetation | 924673 | 34 | 969.3333 | 32957.3333 | 0.020148 | 0.0020785
2013-01-18 | ZN167:PA12 | URBAN | Vegetation | 924685 | 1 | 468.7667 | 468.7667 | 0.00028657 | 6.1133e-05
2013-01-18 | ZN72:PA10 | URBAN | Vegetation | 924686 | 1 | 340.9667 | 340.9667 | 0.00020844 | 6.1133e-05
2013-01-18 | ZN167:PA10 | URBAN | Vegetation | 924687 | 50 | 445 | 22250 | 0.013602 | 0.0030566
2013-01-18 | ZN3922:PA12 | URBAN | Vegetation | 924699 | 1 | 1229.1333 | 1229.1333 | 0.0007514 | 6.1133e-05
2013-01-18 | ZN9550:PA33 | URBAN | Equipment Failure | 924708 | 77 | 288.1167 | 22184.9833 | 0.013562 | 0.0047072
2013-01-18 | ZN2400:PA15 | URBAN | Vegetation | 924710 | 32 | 148 | 4736 | 0.0028952 | 0.0019562
2013-01-18 | ZN2400:PA22 | URBAN | Vegetation | 924710 | 2 | 148 | 295.5667 | 0.00018069 | 0.00012227
2013-01-18 | 801:74123 | SHORT RURAL | Equipment Failure | 924721 | 8 | 195 | 1560 | 0.00095367 | 0.00048906
2013-01-18 | ZN15008:PA1 | URBAN | Other | 924723 | 1 | 72.7 | 72.7 | 4.4443e-05 | 6.1133e-05
2013-01-18 | 814:82283 | SHORT RURAL | Other | 924724 | 23 | 73 | 1679 | 0.0010264 | 0.001406
2013-01-18 | ZN1285:PA31 | URBAN | Vegetation | 924726 | 73 | 197 | 14381 | 0.0087915 | 0.0044627
2013-01-18 | ZN690:PA18 | URBAN | Vegetation | 924727 | 66 | 355.8667 | 23487.2 | 0.014358 | 0.0040347
2013-01-18 | 523:33501 | SHORT RURAL | Other | 924737 | 1 | 1091.4 | 1091.4 | 0.0006672 | 6.1133e-05
2013-01-18 | ZN2310:PA37 | URBAN | Vegetation | 924739 | 41 | 287.8333 | 11801.1667 | 0.0072144 | 0.0025064
2013-01-18 | ZN9700:PA15 | URBAN | Vegetation | 924740 | 66 | 209 | 13794 | 0.0084326 | 0.0040347
2013-01-18 | ZN3472:PA40 | URBAN | Third Party Impacts | 924744 | 1 | 361.0167 | 361.0167 | 0.0002207 | 6.1133e-05
2013-01-18 | ZN10999:PA32 | URBAN | Vegetation | 924745 | 56 | 312.0667 | 17475.7333 | 0.010683 | 0.0034234
2013-01-18 | ZN9245:PA10 | URBAN | Vegetation | 924747 | 47 | 905 | 42535 | 0.026003 | 0.0028732
2013-01-18 | 227:13014 | SHORT RURAL | Other | 924751 | 1 | 192.3167 | 192.3167 | 0.00011757 | 6.1133e-05
2013-01-18 | ZN398:PA25 | URBAN | Equipment Failure | 924753 | 1 | 1332.8833 | 1332.8833 | 0.00081483 | 6.1133e-05
2013-01-18 | ZN690:PA3 | URBAN | Vegetation | 924758 | 33 | 828 | 27324 | 0.016704 | 0.0020174
2013-01-18 | ZN690:PA33 | URBAN | Vegetation | 924758 | 1 | 828 | 828 | 0.00050618 | 6.1133e-05
2013-01-18 | ZN1285:PA31 | URBAN | Vegetation | 924762 | 80 | 159 | 12720 | 0.0077761 | 0.0048906
2013-01-18 | ZN384:PA4 | URBAN | Other | 924764 | 1 | 39.7333 | 39.7333 | 2.429e-05 | 6.1133e-05
2013-01-18 | ZN1285:PA31 | URBAN | Other | 924767 | 1 | 819.2667 | 819.2667 | 0.00050084 | 6.1133e-05
2013-01-18 | ZN1648:PA21 | URBAN | Weather | 924771 | 35 | 260 | 9100 | 0.0055631 | 0.0021396
2013-01-18 | 520:48172 | SHORT RURAL | Other | 924779 | 1 | 839 | 839 | 0.0005129 | 6.1133e-05
2013-01-18 | ZN3922:PA2 | SHORT RURAL | Vegetation | 924783 | 31 | 132 | 4092 | 0.0025015 | 0.0018951
2013-01-18 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 924786 | 6 | 738 | 4428 | 0.0027069 | 0.0003668
2013-01-18 | ZN398:PA25 | URBAN | Equipment Failure | 924796 | 1 | 1300.5167 | 1300.5167 | 0.00079504 | 6.1133e-05
2013-01-18 | ZN9252:PA9 | URBAN | Equipment Failure | 924797 | 1 | 442.5333 | 442.5333 | 0.00027053 | 6.1133e-05
2013-01-18 | ZN9900:PA1 | URBAN | Vegetation | 924815 | 39 | 104.7333 | 4084.6 | 0.002497 | 0.0023842
2013-01-18 | ZN187:PA6 | URBAN | Other | 924824 | 1 | 232.7 | 232.7 | 0.00014226 | 6.1133e-05
2013-01-18 | ZN15002:PA2 | SHORT RURAL | Other | 924830 | 1 | 136.9 | 136.9 | 8.369e-05 | 6.1133e-05
2013-01-18 | 513:48059 | SHORT RURAL | Other | 924839 | 4 | 607.7333 | 2430.9333 | 0.0014861 | 0.00024453
2013-01-18 | 513:48059 | SHORT RURAL | Other | 924842 | 2 | 588.8833 | 1177.7667 | 0.00072 | 0.00012227
2013-01-18 | ZN630:PA8 | URBAN | Equipment Failure | 924847 | 91 | 679 | 61789 | 0.037773 | 0.0055631
2013-01-18 | ZN10991:PA7 | URBAN | Vegetation | 924848 | 48 | 483.3167 | 23199.2 | 0.014182 | 0.0029344
2013-01-18 | 516:48067 | SHORT RURAL | Other | 924854 | 3 | 55 | 165 | 0.00010087 | 0.0001834
2013-01-18 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 924855 | 12 | 652 | 7824 | 0.004783 | 0.00073359
2013-01-18 | ZN4545:PA24 | URBAN | Other | 924860 | 48 | 140.95 | 6765.6 | 0.004136 | 0.0029344
2013-01-18 | ZN3154:PA17 | URBAN | Vegetation | 924861 | 1 | 1031 | 1031 | 0.00063028 | 6.1133e-05
2013-01-19 | ZN2310:PA10 | URBAN | Other | 924866 | 31 | 462.1833 | 3890.5 | 0.0023784 | 0.0018951
2013-01-19 | ZN2310:PA28 | URBAN | Other | 924866 | 1 | 462.1833 | 457.1833 | 0.00027949 | 6.1133e-05
2013-01-18 | ZN1193:PA28 | URBAN | Vegetation | 924872 | 44 | 238 | 10472 | 0.0064018 | 0.0026898
2013-01-18 | ZN3154:PA17 | URBAN | Vegetation | 924881 | 1 | 974.8333 | 974.8333 | 0.00059594 | 6.1133e-05
2013-01-18 | ZN12690:PA19 | URBAN | Other | 924890 | 1199 | 106 | 127094 | 0.077696 | 0.073298
2013-01-19 | 516:48067 | SHORT RURAL | Other | 924913 | 2 | 660 | 1320 | 0.00080695 | 0.00012227
2013-01-19 | 515:35197 | LONG RURAL | Equipment Failure | 924916 | 3 | 807 | 2421 | 0.00148 | 0.0001834
2013-01-18 | ZN10994:PA13 | URBAN | Other | 924917 | 57 | 680 | 38760 | 0.023695 | 0.0034846
2013-01-19 | 526:34636 | SHORT RURAL | Other | 924922 | 4 | 346.2 | 1204.35 | 0.00073625 | 0.00024453
2013-01-19 | 520:48172 | SHORT RURAL | Other | 924925 | 11 | 82 | 902 | 0.00055142 | 0.00067246
2013-01-19 | ZN1648:PA4 | URBAN | Other | 924928 | 1 | 424.7333 | 424.7333 | 0.00025965 | 6.1133e-05
2013-01-19 | 512:48049 | SHORT RURAL | Other | 924933 | 4 | 325.3333 | 1301.3333 | 0.00079554 | 0.00024453
2013-01-19 | 520:48172 | SHORT RURAL | Other | 924934 | 3 | 292 | 876 | 0.00053552 | 0.0001834
2013-01-19 | ZN72:PA30 | URBAN | Other | 924940 | 84 | 473 | 39732 | 0.024289 | 0.0051351
2013-01-19 | 520:48172 | SHORT RURAL | Other | 924943 | 3 | 152 | 456 | 0.00027876 | 0.0001834
2013-01-19 | 526:34636 | SHORT RURAL | Other | 924950 | 1 | 244.8667 | 244.8667 | 0.00014969 | 6.1133e-05
2013-01-19 | 520:48172 | SHORT RURAL | Other | 924960 | 1 | 349.95 | 349.95 | 0.00021393 | 6.1133e-05
2013-01-19 | ZN12640:PA8 | SHORT RURAL | Equipment Failure | 924963 | 57 | 218.4333 | 12450.7 | 0.0076114 | 0.0034846
2013-01-19 | 222:2015 | SHORT RURAL | Vegetation | 924965 | 1 | 186.8167 | 186.8167 | 0.00011421 | 6.1133e-05
2013-01-19 | 513:48056 | SHORT RURAL | Other | 924967 | 1 | 154.5 | 154.5 | 9.445e-05 | 6.1133e-05
2013-01-19 | 258:80787 | URBAN | Equipment Failure | 924981 | 3 | 549 | 1647 | 0.0010069 | 0.0001834
2013-01-19 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 924987 | 7 | 484 | 3388 | 0.0020712 | 0.00042793
2013-01-19 | 812:19072 | SHORT RURAL | Vegetation | 924989 | 6 | 629 | 3774 | 0.0023071 | 0.0003668
2013-01-19 | 503:48011 | SHORT RURAL | Other | 924994 | 1 | 337.9833 | 337.9833 | 0.00020662 | 6.1133e-05
2013-01-19 | ZN12660:PA10 | SHORT RURAL | Equipment Failure | 925008 | 454 | 315 | 43925 | 0.026852 | 0.027754
2013-01-19 | ZN9245:PA15 | URBAN | Equipment Failure | 925016 | 1 | 466.35 | 466.35 | 0.00028509 | 6.1133e-05
2013-01-19 | 507:80923 | SHORT RURAL | Other | 925021 | 1 | 257 | 257 | 0.00015711 | 6.1133e-05
2013-01-19 | 221:11893 | URBAN | Equipment Failure | 925022 | 1 | 121.8167 | 121.8167 | 7.447e-05 | 6.1133e-05
2013-01-19 | ZN10994:PA8 | URBAN | Equipment Failure | 925024 | 109 | 57.8333 | 6303.8333 | 0.0038537 | 0.0066634
2013-01-19 | 261:81870 | URBAN | Other | 925032 | 1 | 181.3333 | 181.3333 | 0.00011085 | 6.1133e-05
2013-01-19 | ZN116:PA44 | URBAN | Vegetation | 925033 | 1 | 539.3667 | 539.3667 | 0.00032973 | 6.1133e-05
2013-01-19 | ZN2466:PA5 | URBAN | Other | 925035 | 1 | 351 | 351 | 0.00021458 | 6.1133e-05
2013-01-19 | 228:7491 | URBAN | Other | 925036 | 1 | 199.4667 | 199.4667 | 0.00012194 | 6.1133e-05
2013-01-19 | 261:81870 | URBAN | Equipment Failure | 925039 | 2 | 90 | 180 | 0.00011004 | 0.00012227
2013-01-19 | 261:81864 | URBAN | Vegetation | 925040 | 1 | 119.9167 | 119.9167 | 7.3308e-05 | 6.1133e-05
2013-01-19 | 515:35197 | LONG RURAL | Other | 925046 | 2 | 258 | 516 | 0.00031544 | 0.00012227
2013-01-19 | ZN965:PA43 | URBAN | Equipment Failure | 925058 | 1 | 208.9333 | 208.9333 | 0.00012773 | 6.1133e-05
2013-01-19 | 243:80075 | SHORT RURAL | Other | 925060 | 1 | 229.65 | 229.65 | 0.00014039 | 6.1133e-05
2013-01-19 | ZN15002:PA6 | URBAN | Vegetation | 925061 | 1 | 308.5333 | 308.5333 | 0.00018861 | 6.1133e-05
2013-01-19 | 232:33413 | SHORT RURAL | Third Party Impacts | 925065 | 4 | 65 | 260 | 0.00015894 | 0.00024453
2013-01-19 | ZN12610:PA10 | SHORT RURAL | Vegetation | 925068 | 1 | 57.0833 | 57.0833 | 3.4896e-05 | 6.1133e-05
2013-01-19 | ZN690:PA11 | URBAN | Equipment Failure | 925085 | 1 | 234.7333 | 234.7333 | 0.0001435 | 6.1133e-05
2013-01-19 | 509:48039 | LONG RURAL | Equipment Failure | 925096 | 1 | 377.4167 | 377.4167 | 0.00023072 | 6.1133e-05
2013-01-19 | 507:80925 | SHORT RURAL | Other | 925110 | 1 | 582.75 | 582.75 | 0.00035625 | 6.1133e-05
2013-01-19 | ZN14143:PA17 | SHORT RURAL | Equipment Failure | 925111 | 3 | 80 | 240 | 0.00014672 | 0.0001834
2013-01-19 | 509:48039 | LONG RURAL | Equipment Failure | 925113 | 1 | 306.4333 | 306.4333 | 0.00018733 | 6.1133e-05
2013-01-19 | 512:48049 | SHORT RURAL | Other | 925119 | 2 | 152 | 304 | 0.00018584 | 0.00012227
2013-01-19 | ZN15014:PA19 | URBAN | Equipment Failure | 925123 | 1 | 376.9667 | 376.9667 | 0.00023045 | 6.1133e-05
2013-01-19 | 520:48172 | SHORT RURAL | Equipment Failure | 925138 | 1 | 300 | 300 | 0.0001834 | 6.1133e-05
2013-01-19 | 526:34636 | SHORT RURAL | Equipment Failure | 925140 | 1 | 336 | 336 | 0.00020541 | 6.1133e-05
2013-01-19 | ZN15008:PA7 | URBAN | Vegetation | 925142 | 1 | 187.1167 | 187.1167 | 0.00011439 | 6.1133e-05
2013-01-19 | ZN9550:PA43 | URBAN | Vegetation | 925143 | 1 | 496.85 | 496.85 | 0.00030374 | 6.1133e-05
2013-01-19 | ZN12610:PA9 | SHORT RURAL | Other | 925160 | 1 | 101.8333 | 101.8333 | 6.2253e-05 | 6.1133e-05
2013-01-19 | ZN12610:PA24 | SHORT RURAL | Other | 925165 | 1 | 293.4333 | 293.4333 | 0.00017938 | 6.1133e-05
2013-01-19 | ZN12610:PA9 | SHORT RURAL | Other | 925173 | 1 | 15.2667 | 15.2667 | 9.3329e-06 | 6.1133e-05
2013-01-19 | ZN965:PA43 | URBAN | Vegetation | 925174 | 68 | 17 | 1156 | 0.00070669 | 0.004157
2013-01-19 | 501:48115 | SHORT RURAL | Other | 925178 | 1 | 148.8667 | 148.8667 | 9.1006e-05 | 6.1133e-05
2013-01-19 | ZN12610:PA22 | URBAN | Other | 925179 | 1 | 138.9167 | 138.9167 | 8.4923e-05 | 6.1133e-05
2013-01-19 | 515:35197 | LONG RURAL | Other | 925180 | 1 | 170.1333 | 170.1333 | 0.00010401 | 6.1133e-05
2013-01-19 | ZN12570:PA22 | URBAN | Other | 925182 | 1 | 100.6167 | 100.6167 | 6.151e-05 | 6.1133e-05
2013-01-19 | 232:11457 | URBAN | Other | 925191 | 1 | 99.5333 | 99.5333 | 6.0847e-05 | 6.1133e-05
2013-01-20 | ZN36300:PA1 | URBAN | Other | 925194 | 1 | 102.6667 | 102.6667 | 6.2763e-05 | 6.1133e-05
2013-01-20 | ZN1287:PA6 | URBAN | Other | 925197 | 42 | 250.3167 | 10513.3 | 0.006427 | 0.0025676
2013-01-20 | 221:11900 | URBAN | Other | 925198 | 1 | 49.3 | 49.3 | 3.0138e-05 | 6.1133e-05
2013-01-20 | 231:8415 | SHORT RURAL | Equipment Failure | 925207 | 1630 | 307 | 151092 | 0.092366 | 0.099646
2013-01-20 | 258:80775 | URBAN | Other | 925210 | 54 | 62.4167 | 3370.5 | 0.0020605 | 0.0033012
2013-01-20 | 807:74181 | SHORT RURAL | Other | 925212 | 24 | 93 | 2232 | 0.0013645 | 0.0014672
2013-01-20 | 803:74010 | SHORT RURAL | Animals | 925218 | 2 | 62 | 124 | 7.5804e-05 | 0.00012227
2013-01-20 | 801:74123 | SHORT RURAL | Equipment Failure | 925221 | 1 | 166 | 166 | 0.00010148 | 6.1133e-05
2013-01-20 | ZN14892:PA19 | URBAN | Other | 925226 | 1 | 103.8 | 103.8 | 6.3456e-05 | 6.1133e-05
2013-01-20 | 503:48017 | URBAN | Other | 925229 | 1 | 125.2667 | 125.2667 | 7.6579e-05 | 6.1133e-05
2013-01-20 | ZN12660:PA14 | SHORT RURAL | Other | 925243 | 613 | 366 | 49099 | 0.030015 | 0.037474
2013-01-20 | 512:48049 | SHORT RURAL | Vegetation | 925260 | 1 | 65.6833 | 65.6833 | 4.0154e-05 | 6.1133e-05
2013-01-20 | ZN1287:PA6 | URBAN | Equipment Failure | 925266 | 42 | 137.4667 | 5773.6 | 0.0035295 | 0.0025676
2013-01-20 | 216:10727 | URBAN | Other | 925267 | 8 | 134.1167 | 1072.9333 | 0.00065591 | 0.00048906
2013-01-20 | ZN690:PA27 | URBAN | Equipment Failure | 925272 | 172 | 317 | 13547 | 0.0082816 | 0.010515
2013-01-20 | ZN15010:PA5 | URBAN | Other | 925276 | 1 | 318.5833 | 318.5833 | 0.00019476 | 6.1133e-05
2013-01-20 | ZN14143:PA17 | SHORT RURAL | Equipment Failure | 925278 | 401 | 420 | 167940 | 0.10267 | 0.024514
2013-01-20 | 231:8415 | SHORT RURAL | Other | 925279 | 1 | 25 | 25 | 1.5283e-05 | 6.1133e-05
2013-01-20 | ZN847:PA22 | SHORT RURAL | Equipment Failure | 925289 | 1 | 387.4 | 387.4 | 0.00023683 | 6.1133e-05
2013-01-20 | ZN1287:PA4 | URBAN | Vegetation | 925300 | 1 | 274.4833 | 274.4833 | 0.0001678 | 6.1133e-05
2013-01-20 | 511:29880 | URBAN | Other | 925301 | 1 | 110.9667 | 110.9667 | 6.7837e-05 | 6.1133e-05
2013-01-20 | 235:2124 | URBAN | Other | 925314 | 1 | 71.3667 | 71.3667 | 4.3628e-05 | 6.1133e-05
2013-01-20 | 232:11455 | URBAN | Other | 925325 | 67 | 118 | 7906 | 0.0048331 | 0.0040959
2013-01-20 | ZN1193:PA9 | URBAN | Equipment Failure | 925337 | 1 | 475.1 | 475.1 | 0.00029044 | 6.1133e-05
2013-01-20 | ZN15014:PA14 | SHORT RURAL | Vegetation | 925340 | 327 | 45 | 14715 | 0.0089957 | 0.01999
2013-01-20 | ZN3922:PA7 | URBAN | Other | 925345 | 1 | 333.0667 | 333.0667 | 0.00020361 | 6.1133e-05
2013-01-20 | ZN398:PA3 | URBAN | Equipment Failure | 925349 | 1 | 153.9 | 153.9 | 9.4083e-05 | 6.1133e-05
2013-01-20 | ZN15010:PA11 | URBAN | Other | 925359 | 1 | 196.1167 | 196.1167 | 0.00011989 | 6.1133e-05
2013-01-20 | ZN4545:PA31 | URBAN | Other | 925361 | 1 | 258.7333 | 258.7333 | 0.00015817 | 6.1133e-05
2013-01-20 | ZN14891:PA10 | SHORT RURAL | Other | 925367 | 1 | 610.25 | 610.25 | 0.00037306 | 6.1133e-05
2013-01-20 | ZN2310:PA31 | URBAN | Other | 925372 | 1 | 134.7 | 134.7 | 8.2346e-05 | 6.1133e-05
2013-01-21 | ZN3472:PA12 | URBAN | Equipment Failure | 925389 | 1 | 184.1333 | 184.1333 | 0.00011257 | 6.1133e-05
2013-01-21 | ZN9700:PA17 | URBAN | Other | 925397 | 1 | 98.0333 | 98.0333 | 5.993e-05 | 6.1133e-05
2013-01-21 | ZN35500:PA28 | URBAN | Equipment Failure | 925449 | 1 | 856.9 | 856.9 | 0.00052384 | 6.1133e-05
2013-01-21 | 234:2001 | URBAN | Other | 925454 | 1 | 82.1 | 82.1 | 5.019e-05 | 6.1133e-05
2013-01-21 | ZN847:PA10 | URBAN | Vegetation | 925458 | 1 | 753.6333 | 753.6333 | 0.00046072 | 6.1133e-05
2013-01-21 | ZN3154:PA5 | URBAN | Third Party Impacts | 925479 | 38 | 61.0167 | 2318.6333 | 0.0014174 | 0.002323
2013-01-18 | 264:81240 | SHORT RURAL | Other | 925496 | 129 | 4 | 516 | 0.00031544 | 0.0078861
2013-01-21 | 202:34254 | URBAN | Equipment Failure | 925502 | 6 | 120 | 720 | 0.00044015 | 0.0003668
2013-01-18 | 229:34983 | SHORT RURAL | Other | 925514 | 55 | 3 | 165 | 0.00010087 | 0.0033623
2013-01-21 | ZN72:PA34 | URBAN | Equipment Failure | 925527 | 1 | 238.75 | 238.75 | 0.00014595 | 6.1133e-05
2013-01-21 | 223:14395 | SHORT RURAL | Other | 925530 | 1 | 116.6167 | 116.6167 | 7.1291e-05 | 6.1133e-05
2013-01-21 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 925596 | 27 | 186 | 5022 | 0.0030701 | 0.0016506
2013-01-20 | 264:81240 | SHORT RURAL | Other | 925599 | 129 | 6 | 774 | 0.00047317 | 0.0078861
2013-01-21 | ZN3472:PA34 | URBAN | Equipment Failure | 925647 | 1 | 338.4833 | 338.4833 | 0.00020692 | 6.1133e-05
2013-01-21 | 813:89055 | SHORT RURAL | Equipment Failure | 925650 | 1 | 156.2667 | 156.2667 | 9.553e-05 | 6.1133e-05
2013-01-21 | 256:80646 | URBAN | Equipment Failure | 925660 | 99 | 130 | 12870 | 0.0078678 | 0.0060521
2013-01-21 | ZN14144:PA1 | URBAN | Equipment Failure | 925673 | 1 | 150.4667 | 150.4667 | 9.1984e-05 | 6.1133e-05
2013-01-21 | ZN15005:PA8 | URBAN | Vegetation | 925676 | 39 | 17.45 | 680.55 | 0.00041604 | 0.0023842
2013-01-18 | 810:74054 | LONG RURAL | Other | 925680 | 1 | 45 | 45 | 2.751e-05 | 6.1133e-05
2013-01-21 | ZN1788:PA29 | URBAN | Equipment Failure | 925691 | 42 | 163.9333 | 6885.2 | 0.0042091 | 0.0025676
2013-01-21 | ZN3154:PA17 | URBAN | Vegetation | 925695 | 8 | 82 | 656 | 0.00040103 | 0.00048906
2013-01-21 | 229:34995 | SHORT RURAL | Vegetation | 925716 | 1 | 130.3667 | 130.3667 | 7.9696e-05 | 6.1133e-05
2013-01-21 | ZN80:PA30 | URBAN | Other | 925738 | 1 | 227 | 227 | 0.00013877 | 6.1133e-05
2013-01-21 | 514:18137 | SHORT RURAL | Other | 925744 | 2 | 70 | 140 | 8.5586e-05 | 0.00012227
2013-01-21 | ZN2473:PA9 | URBAN | Other | 925760 | 25 | 455 | 11375 | 0.0069538 | 0.0015283
2013-01-21 | ZN13000:PA11 | URBAN | Equipment Failure | 925765 | 93 | 112 | 10416 | 0.0063676 | 0.0056853
2013-01-14 | ZN3155:PA24 | URBAN | Equipment Failure | 925784 | 63 | 15 | 945 | 0.0005743 | 0.0038287
2013-01-21 | ZN9035:PA1 | URBAN | Other | 925785 | 1 | 53 | 53 | 3.24e-05 | 6.1133e-05
2013-01-21 | ZN9035:PA4 | URBAN | Other | 925785 | 1818 | 53 | 96354 | 0.058904 | 0.11114
2013-01-21 | ZN965:PA38 | URBAN | Equipment Failure | 925838 | 25 | 1555 | 28375 | 0.017346 | 0.0015283
2013-01-21 | ZN180:PA21 | URBAN | Equipment Failure | 925844 | 125 | 1607 | 200875 | 0.1228 | 0.0076416
2013-01-21 | 810:74054 | LONG RURAL | Other | 925874 | 1 | 162.3333 | 162.3333 | 9.9238e-05 | 6.1133e-05
2013-01-21 | ZN9900:PA8 | URBAN | Vegetation | 926007 | 1 | 179.45 | 179.45 | 0.0001097 | 6.1133e-05
2013-01-21 | ZN116:PA49 | URBAN | Vegetation | 926010 | 97 | 90 | 8723.6667 | 0.005333 | 0.0059299
2013-01-21 | ZN9118:PA21 | URBAN | Equipment Failure | 926014 | 1 | 280.8333 | 280.8333 | 0.00017168 | 6.1133e-05
2013-01-21 | 260:33347 | SHORT RURAL | Other | 926016 | 1 | 82.0833 | 82.0833 | 5.018e-05 | 6.1133e-05
2013-01-21 | ZN12570:PA22 | URBAN | Vegetation | 926021 | 1 | 257.0833 | 257.0833 | 0.00015716 | 6.1133e-05
2013-01-21 | ZN15002:PA6 | URBAN | Animals | 926022 | 1 | 55 | 55 | 3.3623e-05 | 6.1133e-05
2013-01-21 | ZN15002:PA8 | URBAN | Animals | 926022 | 814 | 55 | 44770 | 0.027369 | 0.049762
2013-01-22 | 507:80932 | SHORT RURAL | Equipment Failure | 926028 | 3 | 85 | 255 | 0.00015589 | 0.0001834
2013-01-21 | ZN12650:PA17 | URBAN | Equipment Failure | 926030 | 2350 | 107 | 155898 | 0.095304 | 0.14366
2013-01-21 | ZN12650:PA9 | URBAN | Equipment Failure | 926030 | 1 | 107 | 77 | 4.7072e-05 | 6.1133e-05
2013-01-22 | 264:81241 | SHORT RURAL | Equipment Failure | 926037 | 1 | 1062.35 | 1062.35 | 0.00064945 | 6.1133e-05
2013-01-22 | ZN14892:PA8 | URBAN | Equipment Failure | 926048 | 1 | 250 | 250 | 0.00015283 | 6.1133e-05
2013-01-22 | ZN2473:PA9 | URBAN | Equipment Failure | 926054 | 25 | 552.9667 | 13824.1667 | 0.0084512 | 0.0015283
2013-01-22 | 206:34441 | URBAN | Other | 926117 | 1 | 81.6833 | 81.6833 | 4.9936e-05 | 6.1133e-05
2013-01-22 | 256:80640 | URBAN | Other | 926131 | 1 | 106.85 | 106.85 | 6.5321e-05 | 6.1133e-05
2013-01-18 | ZN12650:PA14 | URBAN | Equipment Failure | 926141 | 470 | 4 | 1880 | 0.0011493 | 0.028732
2013-01-22 | 261:81870 | URBAN | Other | 926155 | 1 | 38.25 | 38.25 | 2.3383e-05 | 6.1133e-05
2013-01-19 | 520:48172 | SHORT RURAL | Other | 926167 | 1 | 52 | 52 | 3.1789e-05 | 6.1133e-05
2013-01-22 | 514:18137 | SHORT RURAL | Other | 926202 | 3 | 57 | 171 | 0.00010454 | 0.0001834
2013-01-22 | 224:80341 | URBAN | Other | 926215 | 1 | 100.35 | 100.35 | 6.1347e-05 | 6.1133e-05
2013-01-22 | ZN2602:PA4 | URBAN | Equipment Failure | 926250 | 1 | 458.5333 | 458.5333 | 0.00028032 | 6.1133e-05
2013-01-22 | 513:48056 | SHORT RURAL | Equipment Failure | 926258 | 114 | 255 | 8079 | 0.004939 | 0.0069692
2013-01-22 | 238:34144 | URBAN | Equipment Failure | 926274 | 67 | 195.85 | 13121.95 | 0.0080219 | 0.0040959
2013-01-22 | ZN847:PA39 | URBAN | Vegetation | 926343 | 51 | 303 | 15453 | 0.0094469 | 0.0031178
2013-01-18 | ZN15013:PA4 | URBAN | Vegetation | 926351 | 70 | 65 | 4550 | 0.0027815 | 0.0042793
2013-01-22 | 221:11894 | URBAN | Other | 926355 | 1 | 57.05 | 57.05 | 3.4877e-05 | 6.1133e-05
2013-01-19 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 926362 | 2 | 95 | 190 | 0.00011615 | 0.00012227
2013-01-22 | 810:74058 | SHORT RURAL | Equipment Failure | 926389 | 1 | 174.0333 | 174.0333 | 0.00010639 | 6.1133e-05
2013-01-22 | 225:33679 | URBAN | Other | 926393 | 1 | 124.5167 | 124.5167 | 7.6121e-05 | 6.1133e-05
2013-01-22 | ZN15005:PA2 | URBAN | Other | 926434 | 1 | 85.5167 | 85.5167 | 5.2279e-05 | 6.1133e-05
2013-01-22 | ZN15004:PA9 | URBAN | Other | 926440 | 1 | 217.5333 | 217.5333 | 0.00013299 | 6.1133e-05
2013-01-22 | ZN4545:PA36 | URBAN | Other | 926454 | 10 | 469 | 4690 | 0.0028672 | 0.00061133
2013-01-22 | ZN9700:PA23 | URBAN | Weather | 926456 | 1688 | 110 | 149030 | 0.091107 | 0.10319
2013-01-22 | 515:35197 | LONG RURAL | Vegetation | 926457 | 1 | 116.35 | 116.35 | 7.1129e-05 | 6.1133e-05
2013-01-22 | 509:48039 | LONG RURAL | Equipment Failure | 926471 | 216 | 1243 | 42006 | 0.02568 | 0.013205
2013-01-22 | ZN15002:PA6 | URBAN | Equipment Failure | 926487 | 1 | 1015.5833 | 1015.5833 | 0.00062086 | 6.1133e-05
2013-01-22 | 509:48039 | LONG RURAL | Other | 926488 | 18 | 555 | 9990 | 0.0061072 | 0.0011004
2013-01-22 | 515:35197 | LONG RURAL | Other | 926489 | 1 | 98.8667 | 98.8667 | 6.044e-05 | 6.1133e-05
2013-01-22 | ZN9037:PA8 | URBAN | Weather | 926493 | 106 | 75 | 7950 | 0.0048601 | 0.0064801
2013-01-22 | 515:35192 | SHORT RURAL | Other | 926499 | 1 | 381.85 | 381.85 | 0.00023344 | 6.1133e-05
2013-01-22 | 512:48049 | SHORT RURAL | Other | 926500 | 1 | 241 | 241 | 0.00014733 | 6.1133e-05
2013-01-22 | ZN12690:PA12 | SHORT RURAL | Other | 926503 | 1 | 287.8333 | 287.8333 | 0.00017596 | 6.1133e-05
2013-01-22 | 516:48066 | SHORT RURAL | Other | 926504 | 102 | 190 | 19380 | 0.011848 | 0.0062356
2013-01-22 | ZN12650:PA20 | URBAN | Other | 926507 | 1 | 89.2 | 89.2 | 5.4531e-05 | 6.1133e-05
2013-01-22 | ZN12650:PA20 | URBAN | Other | 926510 | 1 | 104.8 | 104.8 | 6.4068e-05 | 6.1133e-05
2013-01-22 | 513:48056 | SHORT RURAL | Equipment Failure | 926516 | 17 | 1040 | 17680 | 0.010808 | 0.0010393
2013-01-22 | 812:19072 | SHORT RURAL | Other | 926518 | 24 | 104.1333 | 2499.2 | 0.0015278 | 0.0014672
2013-01-22 | ZN9035:PA11 | URBAN | Equipment Failure | 926531 | 1 | 474.1833 | 474.1833 | 0.00028988 | 6.1133e-05
2013-01-22 | 258:80784 | URBAN | Other | 926536 | 1 | 177.5 | 177.5 | 0.00010851 | 6.1133e-05
2013-01-22 | 513:48056 | SHORT RURAL | Equipment Failure | 926542 | 6 | 359.8167 | 2158.9 | 0.0013198 | 0.0003668
2013-01-22 | 516:48065 | SHORT RURAL | Other | 926544 | 2 | 264.9333 | 474.9333 | 0.00029034 | 0.00012227
2013-01-22 | 806:74080 | SHORT RURAL | Equipment Failure | 926550 | 35 | 860 | 24925 | 0.015237 | 0.0021397
2013-01-22 | 523:33501 | SHORT RURAL | Other | 926552 | 3 | 379.9 | 1139.7 | 0.00069674 | 0.0001834
2013-01-22 | ZN12600:PA9 | SHORT RURAL | Equipment Failure | 926555 | 1341 | 273 | 199906 | 0.12221 | 0.08198
2013-01-22 | ZN12580:PA4 | URBAN | Other | 926557 | 851 | 99 | 84249 | 0.051504 | 0.052024
2013-01-22 | ZN15014:PA12 | SHORT RURAL | Equipment Failure | 926560 | 30 | 114 | 3420 | 0.0020908 | 0.001834
2013-01-22 | ZN180:PA7 | URBAN | Equipment Failure | 926580 | 67 | 80.5167 | 5394.6167 | 0.0032979 | 0.0040959
2013-01-22 | 512:48049 | SHORT RURAL | Other | 926583 | 1 | 271 | 271 | 0.00016567 | 6.1133e-05
2013-01-22 | ZN874:PA17 | URBAN | Equipment Failure | 926584 | 71 | 58.25 | 4135.75 | 0.0025283 | 0.0043405
2013-01-22 | ZN2196:PA2 | URBAN | Equipment Failure | 926587 | 1 | 36.6333 | 36.6333 | 2.2395e-05 | 6.1133e-05
2013-01-22 | 512:48049 | SHORT RURAL | Other | 926594 | 1 | 110 | 110 | 6.7247e-05 | 6.1133e-05
2013-01-23 | ZN12600:PA9 | SHORT RURAL | Other | 926610 | 342 | 343.8 | 117579.6 | 0.071881 | 0.020908
2013-01-23 | 512:48049 | SHORT RURAL | Other | 926614 | 2 | 231 | 462 | 0.00028244 | 0.00012227
2013-01-23 | ZN187:PA19 | URBAN | Other | 926615 | 1 | 617.4333 | 617.4333 | 0.00037746 | 6.1134e-05
2013-01-23 | 807:74184 | SHORT RURAL | Other | 926625 | 2 | 113 | 226 | 0.00013816 | 0.00012227
2013-01-23 | 512:48049 | SHORT RURAL | Other | 926633 | 2 | 147 | 294 | 0.00017973 | 0.00012227
2013-01-23 | 513:48059 | SHORT RURAL | Other | 926641 | 5 | 66 | 330 | 0.00020174 | 0.00030567
2013-01-22 | 234:2001 | URBAN | Other | 926653 | 7 | 90 | 630 | 0.00038514 | 0.00042793
2013-01-23 | ZN10995:PA12 | URBAN | Equipment Failure | 926656 | 1 | 325.35 | 325.35 | 0.0001989 | 6.1134e-05
2013-01-23 | 811:74234 | SHORT RURAL | Weather | 926681 | 1 | 571 | 571 | 0.00034908 | 6.1134e-05
2013-01-23 | 214:8669 | URBAN | Other | 926683 | 1 | 139.1667 | 139.1667 | 8.5078e-05 | 6.1134e-05
2013-01-22 | 512:48049 | SHORT RURAL | Other | 926688 | 909 | 104 | 94536 | 0.057793 | 0.05557
2013-01-23 | 802:82215 | SHORT RURAL | Other | 926701 | 1 | 85.0167 | 85.0167 | 5.1974e-05 | 6.1134e-05
2013-01-23 | ZN1673:PA11 | URBAN | Other | 926724 | 1 | 171.25 | 171.25 | 0.00010469 | 6.1134e-05
2013-01-23 | 811:74234 | SHORT RURAL | Other | 926731 | 5 | 314 | 1570 | 0.00095981 | 0.00030567
2013-01-23 | ZN3154:PA12 | URBAN | Vegetation | 926786 | 49 | 112 | 5488 | 0.003355 | 0.0029956
2013-01-22 | 516:48065 | SHORT RURAL | Other | 926798 | 1 | 225 | 225 | 0.00013755 | 6.1133e-05
2013-01-21 | ZN13000:PA11 | URBAN | Equipment Failure | 926811 | 18 | 60 | 1080 | 0.00066023 | 0.0011004
2013-01-23 | ZN2602:PA35 | URBAN | Other | 926825 | 1 | 94.15 | 94.15 | 5.7558e-05 | 6.1134e-05
2013-01-23 | 222:2017 | URBAN | Other | 926845 | 25 | 230 | 5750 | 0.0035152 | 0.0015284
2013-01-18 | ZN2473:PA26 | URBAN | Other | 926848 | 13 | 420 | 5460 | 0.0033378 | 0.00079472
2013-01-23 | ZN269:PA16 | URBAN | Third Party Impacts | 926870 | 117 | 67 | 7839 | 0.0047923 | 0.0071527
2013-01-23 | ZN9252:PA7 | URBAN | Vegetation | 926985 | 1 | 399.25 | 399.25 | 0.00024408 | 6.1134e-05
2013-01-23 | 221:11900 | URBAN | Other | 927083 | 98 | 55 | 5390 | 0.0032951 | 0.0059912
2013-01-22 | ZN1193:PA6 | URBAN | Other | 927094 | 1 | 1451.9167 | 1451.9167 | 0.0008876 | 6.1133e-05
2013-01-23 | 227:13015 | SHORT RURAL | Equipment Failure | 927098 | 10 | 238 | 2380 | 0.001455 | 0.00061134
2013-01-23 | ZN15004:PA1 | URBAN | Other | 927110 | 67 | 19.4333 | 1302.0333 | 0.00079599 | 0.004096
2013-01-23 | 243:80084 | SHORT RURAL | Other | 927122 | 1 | 142.3833 | 142.3833 | 8.7045e-05 | 6.1134e-05
2013-01-23 | ZN7481:PA1 | URBAN | Other | 927129 | 1 | 759.9 | 759.9 | 0.00046456 | 6.1134e-05
2013-01-24 | ZN9245:PA10 | URBAN | Other | 927151 | 1 | 115.8667 | 115.8667 | 7.0847e-05 | 6.1145e-05
2013-01-24 | 810:74054 | LONG RURAL | Other | 927165 | 1 | 245 | 245 | 0.00014981 | 6.1145e-05
2013-01-24 | ZN690:PA25 | URBAN | Third Party Impacts | 927221 | 1 | 248.8 | 248.8 | 0.00015213 | 6.1145e-05
2013-01-24 | 810:74058 | SHORT RURAL | Other | 927231 | 1 | 150.7667 | 150.7667 | 9.2186e-05 | 6.1145e-05
2013-01-23 | 202:34232 | URBAN | Other | 927309 | 21 | 24 | 504 | 0.00030812 | 0.0012838
2013-01-24 | 524:33572 | SHORT RURAL | Third Party Impacts | 927318 | 1 | 67.0333 | 67.0333 | 4.0987e-05 | 6.1145e-05
2013-01-24 | 258:80787 | URBAN | Third Party Impacts | 927360 | 1523 | 938 | 64862 | 0.03966 | 0.093124
2013-01-24 | 801:74121 | SHORT RURAL | Equipment Failure | 927386 | 1 | 117 | 117 | 7.154e-05 | 6.1145e-05
2013-01-24 | ZN3472:PA23 | URBAN | Vegetation | 927395 | 17 | 334 | 5678 | 0.0034718 | 0.0010395
2013-01-23 | 512:48049 | SHORT RURAL | Other | 927400 | 1 | 195 | 195 | 0.00011921 | 6.1134e-05
2013-01-23 | 811:74234 | SHORT RURAL | Other | 927421 | 1 | 344 | 344 | 0.0002103 | 6.1134e-05
2013-01-24 | ZN35500:PA27 | URBAN | Vegetation | 927431 | 62 | 107.6833 | 6676.3667 | 0.0040823 | 0.003791
2013-01-23 | 513:48059 | SHORT RURAL | Equipment Failure | 927443 | 1 | 69 | 69 | 4.2183e-05 | 6.1134e-05
2013-01-24 | 807:74183 | SHORT RURAL | Third Party Impacts | 927454 | 1 | 61.9833 | 61.9833 | 3.79e-05 | 6.1145e-05
2013-01-24 | 256:80652 | URBAN | Other | 927455 | 1 | 141.85 | 141.85 | 8.6734e-05 | 6.1145e-05
2013-01-24 | ZN3922:PA30 | URBAN | Vegetation | 927463 | 88 | 107.1 | 9424.8 | 0.0057628 | 0.0053808
2013-01-18 | ZN35500:PA14 | URBAN | Other | 927468 | 4 | 30 | 120 | 7.3359e-05 | 0.00024453
2013-01-24 | 507:80923 | SHORT RURAL | Other | 927480 | 1 | 108 | 108 | 6.6037e-05 | 6.1145e-05
2013-01-24 | ZN188:PA4 | URBAN | Equipment Failure | 927506 | 119 | 88 | 10472 | 0.0064031 | 0.0072762
2013-01-24 | ZN901:PA14 | URBAN | Equipment Failure | 927506 | 949 | 88 | 83512 | 0.051063 | 0.058027
2013-01-24 | ZN901:PA32 | URBAN | Equipment Failure | 927506 | 61 | 88 | 5368 | 0.0032823 | 0.0037298
2013-01-25 | ZN901:PA19 | URBAN | Equipment Failure | 927618 | 746 | 64 | 44474 | 0.027189 | 0.045607
2013-01-25 | ZN690:PA18 | URBAN | Other | 927626 | 1 | 384.1667 | 384.1667 | 0.00023486 | 6.1135e-05
2013-01-25 | ZN15008:PA5 | URBAN | Other | 927628 | 1 | 112.2333 | 112.2333 | 6.8614e-05 | 6.1135e-05
2013-01-25 | 813:89061 | LONG RURAL | Weather | 927633 | 1 | 218.1167 | 218.1167 | 0.00013335 | 6.1135e-05
2013-01-25 | ZN15008:PA10 | URBAN | Other | 927655 | 1 | 231.0167 | 231.0167 | 0.00014123 | 6.1135e-05
2013-01-25 | ZN3472:PA35 | URBAN | Equipment Failure | 927716 | 1 | 477.5167 | 477.5167 | 0.00029193 | 6.1135e-05
2013-01-25 | 202:34254 | URBAN | Equipment Failure | 927750 | 163 | 211.85 | 34531.55 | 0.021111 | 0.0099651
2013-01-25 | ZN1287:PA24 | URBAN | Third Party Impacts | 927787 | 1 | 203.5667 | 203.5667 | 0.00012445 | 6.1135e-05
2013-01-25 | 206:34432 | URBAN | Third Party Impacts | 927795 | 1 | 237.9333 | 237.9333 | 0.00014546 | 6.1135e-05
2013-01-25 | ZN1287:PA24 | URBAN | Third Party Impacts | 927803 | 1 | 176.4667 | 176.4667 | 0.00010788 | 6.1135e-05
2013-01-25 | ZN12620:PA3 | URBAN | Other | 927835 | 1 | 358.15 | 358.15 | 0.00021896 | 6.1135e-05
2013-01-25 | ZN195:PA30 | URBAN | Vegetation | 927837 | 44 | 60.4667 | 2660.5333 | 0.0016265 | 0.00269
2013-01-25 | 258:80775 | URBAN | Other | 927853 | 54 | 56.8167 | 3068.1 | 0.0018757 | 0.0033013
2013-01-25 | ZN9301:PA8 | URBAN | Equipment Failure | 927865 | 1 | 246.6333 | 246.6333 | 0.00015078 | 6.1135e-05
2013-01-25 | ZN188:PA15 | URBAN | Other | 927885 | 1 | 44 | 44 | 2.69e-05 | 6.1135e-05
2013-01-25 | ZN8100:PA10 | URBAN | Other | 927885 | 33 | 44 | 1452 | 0.00088769 | 0.0020175
2013-01-25 | 810:74054 | LONG RURAL | Equipment Failure | 927900 | 1 | 70 | 70 | 4.2795e-05 | 6.1135e-05
2013-01-25 | ZN10991:PA1 | URBAN | Vegetation | 927945 | 1 | 215.4 | 215.4 | 0.00013169 | 6.1135e-05
2013-01-25 | ZN847:PA15 | URBAN | Vegetation | 927949 | 34 | 181 | 6154 | 0.0037623 | 0.0020786
2013-01-25 | ZN2635:PA10 | URBAN | Vegetation | 927963 | 58 | 73 | 4234 | 0.0025885 | 0.0035459
2013-01-25 | ZN14144:PA10 | SHORT RURAL | Vegetation | 927967 | 9 | 143 | 1287 | 0.00078681 | 0.00055022
2013-01-25 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 927975 | 2 | 71.4667 | 142.9333 | 8.7383e-05 | 0.00012227
2013-01-25 | 512:48048 | SHORT RURAL | Other | 927981 | 3 | 67.25 | 201.75 | 0.00012334 | 0.00018341
2013-01-25 | ZN2400:PA26 | URBAN | Equipment Failure | 927990 | 461 | 88 | 36518 | 0.022325 | 0.028183
2013-01-25 | ZN2310:PA31 | URBAN | Vegetation | 928000 | 1 | 330.6167 | 330.6167 | 0.00020212 | 6.1135e-05
2013-01-25 | 810:74054 | LONG RURAL | Other | 928016 | 1 | 94 | 94 | 5.7467e-05 | 6.1135e-05
2013-01-25 | ZN965:PA42 | URBAN | Third Party Impacts | 928026 | 1 | 475.45 | 475.45 | 0.00029067 | 6.1135e-05
2013-01-25 | 223:14397 | URBAN | Equipment Failure | 928029 | 1 | 118.5333 | 118.5333 | 7.2466e-05 | 6.1135e-05
2013-01-26 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 928032 | 90 | 363 | 32670 | 0.019973 | 0.0055022
2013-01-26 | ZN14144:PA2 | SHORT RURAL | Equipment Failure | 928050 | 7 | 137.7167 | 964.0167 | 0.00058936 | 0.00042795
2013-01-26 | 513:48059 | SHORT RURAL | Other | 928052 | 1 | 60 | 60 | 3.6681e-05 | 6.1135e-05
2013-01-26 | 504:48034 | URBAN | Equipment Failure | 928064 | 55 | 105.1667 | 5784.1667 | 0.0035362 | 0.0033625
2013-01-26 | 504:48026 | SHORT RURAL | Other | 928080 | 1 | 111.8667 | 111.8667 | 6.839e-05 | 6.1135e-05
2013-01-26 | 508:82578 | SHORT RURAL | Equipment Failure | 928102 | 419 | 424 | 50984 | 0.031169 | 0.025616
2013-01-26 | 513:48056 | SHORT RURAL | Other | 928110 | 252 | 76 | 19152 | 0.011709 | 0.015406
2013-01-26 | ZN7900:PA12 | URBAN | Equipment Failure | 928115 | 1 | 232.3833 | 232.3833 | 0.00014207 | 6.1135e-05
2013-01-26 | ZN12610:PA11 | URBAN | Other | 928125 | 1 | 148.7667 | 148.7667 | 9.0949e-05 | 6.1135e-05
2013-01-26 | ZN3154:PA3 | URBAN | Other | 928134 | 1 | 163.5667 | 163.5667 | 9.9997e-05 | 6.1135e-05
2013-01-26 | 513:48056 | SHORT RURAL | Other | 928149 | 252 | 101 | 25452 | 0.01556 | 0.015406
2013-01-26 | ZN12570:PA22 | URBAN | Other | 928155 | 1 | 111.5833 | 111.5833 | 6.8217e-05 | 6.1135e-05
2013-01-26 | ZN36300:PA19 | URBAN | Other | 928157 | 1 | 243.7833 | 243.7833 | 0.00014904 | 6.1135e-05
2013-01-26 | ZN262:PA42 | URBAN | Vegetation | 928159 | 72 | 199 | 14328 | 0.0087595 | 0.0044018
2013-01-26 | ZN2400:PA21 | URBAN | Other | 928168 | 1 | 132.6333 | 132.6333 | 8.1086e-05 | 6.1135e-05
2013-01-26 | ZN9550:PA29 | URBAN | Vegetation | 928170 | 85 | 50 | 4250 | 0.0025983 | 0.0051965
2013-01-26 | ZN965:PA2 | URBAN | Vegetation | 928178 | 28 | 55 | 1540 | 0.00094149 | 0.0017118
2013-01-26 | ZN965:PA42 | URBAN | Vegetation | 928178 | 4 | 55 | 220 | 0.0001345 | 0.00024454
2013-01-26 | ZN690:PA36 | URBAN | Vegetation | 928184 | 24 | 157 | 3768 | 0.0023036 | 0.0014673
2013-01-26 | ZN2310:PA27 | URBAN | Equipment Failure | 928199 | 64 | 56.25 | 3600 | 0.0022009 | 0.0039127
2013-01-26 | ZN72:PA23 | URBAN | Weather | 928202 | 66 | 100.1167 | 6607.7 | 0.0040397 | 0.0040349
2013-01-26 | ZN5868:PA30 | URBAN | Vegetation | 928211 | 1 | 196.9333 | 196.9333 | 0.0001204 | 6.1135e-05
2013-01-26 | ZN12620:PA10 | SHORT RURAL | Other | 928220 | 1 | 207.3167 | 207.3167 | 0.00012674 | 6.1135e-05
2013-01-26 | ZN15005:PA2 | URBAN | Vegetation | 928225 | 61 | 55 | 3355 | 0.0020511 | 0.0037293
2013-01-26 | ZN188:PA2 | URBAN | Equipment Failure | 928231 | 48 | 123.9833 | 5951.2 | 0.0036383 | 0.0029345
2013-01-26 | ZN180:PA18 | URBAN | Equipment Failure | 928240 | 186 | 283 | 52638 | 0.032181 | 0.011371
2013-01-26 | ZN180:PA29 | URBAN | Equipment Failure | 928240 | 88 | 283 | 24892.2667 | 0.015218 | 0.0053799
2013-01-27 | 216:10726 | URBAN | Equipment Failure | 928249 | 31 | 135 | 4185 | 0.0025585 | 0.0018952
2013-01-27 | 813:89062 | SHORT RURAL | Equipment Failure | 928251 | 33 | 265 | 5936 | 0.003629 | 0.0020175
2013-01-27 | 807:74180 | SHORT RURAL | Other | 928253 | 2 | 188 | 376 | 0.00022987 | 0.00012227
2013-01-27 | ZN398:PA16 | URBAN | Other | 928255 | 1 | 523.8167 | 523.8167 | 0.00032024 | 6.1135e-05
2013-01-27 | ZN35500:PA18 | SHORT RURAL | Other | 928257 | 1 | 1067.9833 | 1067.9833 | 0.00065292 | 6.1135e-05
2013-01-27 | ZN3922:PA7 | URBAN | Other | 928259 | 1 | 366.8833 | 366.8833 | 0.0002243 | 6.1135e-05
2013-01-27 | 230:81440 | URBAN | Vegetation | 928260 | 713 | 76 | 53470 | 0.032689 | 0.04359
2013-01-27 | ZN35500:PA22 | URBAN | Equipment Failure | 928262 | 1 | 1029.2333 | 1029.2333 | 0.00062923 | 6.1135e-05
2013-01-27 | ZN180:PA22 | URBAN | Other | 928263 | 1 | 813.25 | 813.25 | 0.00049718 | 6.1135e-05
2013-01-27 | 222:2018 | URBAN | Other | 928273 | 1 | 229.65 | 229.65 | 0.0001404 | 6.1135e-05
2013-01-27 | ZN12610:PA17 | URBAN | Equipment Failure | 928275 | 1178 | 380 | 128540 | 0.078584 | 0.072018
2013-01-27 | ZN129:PA3 | URBAN | Other | 928277 | 1 | 757.15 | 757.15 | 0.00046289 | 6.1135e-05
2013-01-27 | ZN10999:PA4 | URBAN | Equipment Failure | 928281 | 15 | 120 | 1800 | 0.0011004 | 0.00091703
2013-01-27 | ZN80:PA32 | URBAN | Other | 928283 | 1 | 3159.3167 | 3159.3167 | 0.0019315 | 6.1135e-05
2013-01-27 | ZN15013:PA4 | URBAN | Vegetation | 928286 | 122 | 91 | 11102 | 0.0067873 | 0.0074585
2013-01-27 | 526:34636 | SHORT RURAL | Other | 928289 | 2 | 87 | 174 | 0.00010638 | 0.00012227
2013-01-27 | ZN14144:PA10 | SHORT RURAL | Vegetation | 928295 | 7 | 115 | 805 | 0.00049214 | 0.00042795
2013-01-27 | ZN342:PA26 | URBAN | Equipment Failure | 928307 | 2835 | 46 | 93850 | 0.057376 | 0.17332
2013-01-27 | ZN3672:PA44 | URBAN | Vegetation | 928313 | 161 | 188 | 30268 | 0.018504 | 0.0098428
2013-01-27 | ZN965:PA35 | URBAN | Vegetation | 928316 | 28 | 141 | 3948 | 0.0024136 | 0.0017118
2013-01-27 | ZN35600:PA1 | URBAN | Other | 928324 | 1 | 345.3833 | 345.3833 | 0.00021115 | 6.1135e-05
2013-01-27 | ZN269:PA7 | URBAN | Other | 928354 | 104 | 137.0333 | 14251.4667 | 0.0087127 | 0.0063581
2013-01-27 | 258:80784 | URBAN | Vegetation | 928360 | 1 | 280.3667 | 280.3667 | 0.0001714 | 6.1135e-05
2013-01-27 | 516:48066 | SHORT RURAL | Other | 928363 | 1 | 177.2833 | 177.2833 | 0.00010838 | 6.1135e-05
2013-01-27 | ZN14891:PA10 | SHORT RURAL | Other | 928367 | 1 | 540.8667 | 540.8667 | 0.00033066 | 6.1135e-05
2013-01-27 | 261:81886 | URBAN | Other | 928382 | 1 | 132.9167 | 132.9167 | 8.1259e-05 | 6.1135e-05
2013-01-27 | 232:11457 | URBAN | Equipment Failure | 928384 | 52 | 183.9333 | 9564.5333 | 0.0058473 | 0.003179
2013-01-27 | ZN9252:PA7 | URBAN | Equipment Failure | 928393 | 585 | 247 | 56491 | 0.034536 | 0.035764
2013-01-27 | 813:89061 | LONG RURAL | Other | 928403 | 13 | 105.1833 | 1367.3833 | 0.00083596 | 0.00079476
2013-01-27 | 511:29880 | URBAN | Other | 928416 | 1 | 255.9833 | 255.9833 | 0.0001565 | 6.1135e-05
2013-01-27 | ZN9252:PA8 | URBAN | Equipment Failure | 928435 | 82 | 199.7833 | 16382.2333 | 0.010015 | 0.0050131
2013-01-27 | ZN12620:PA13 | SHORT RURAL | Equipment Failure | 928439 | 1 | 534.0833 | 534.0833 | 0.00032651 | 6.1135e-05
2013-01-27 | 227:13020 | SHORT RURAL | Vegetation | 928440 | 1 | 225.3 | 225.3 | 0.00013774 | 6.1135e-05
2013-01-27 | 221:11893 | URBAN | Equipment Failure | 928459 | 19 | 306.4667 | 5822.8667 | 0.0035598 | 0.0011616
2013-01-27 | 807:74179 | SHORT RURAL | Equipment Failure | 928462 | 2 | 257 | 514 | 0.00031424 | 0.00012227
2013-01-27 | ZN14144:PA1 | URBAN | Other | 928464 | 3 | 109 | 228 | 0.00013939 | 0.00018341
2013-01-27 | ZN14144:PA7 | SHORT RURAL | Other | 928464 | 1024 | 109 | 98665 | 0.060319 | 0.062603
2013-01-27 | ZN9252:PA12 | URBAN | Other | 928489 | 1 | 193.9167 | 193.9167 | 0.00011855 | 6.1135e-05
2013-01-27 | ZN12620:PA2 | SHORT RURAL | Equipment Failure | 928495 | 6 | 197 | 552 | 0.00033747 | 0.00036681
2013-01-27 | ZN12620:PA8 | SHORT RURAL | Equipment Failure | 928495 | 1237 | 197 | 181159 | 0.11075 | 0.075625
2013-01-27 | ZN2473:PA32 | URBAN | Equipment Failure | 928513 | 128 | 53.0167 | 6786.1333 | 0.0041487 | 0.0078253
2013-01-27 | ZN269:PA7 | URBAN | Equipment Failure | 928517 | 104 | 279.7833 | 29097.4667 | 0.017789 | 0.0063581
2013-01-27 | ZN12690:PA12 | SHORT RURAL | Vegetation | 928519 | 164 | 60 | 8988 | 0.0054949 | 0.010026
2013-01-27 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 928563 | 177 | 1207 | 21369 | 0.013064 | 0.010821
2013-01-27 | 213:33775 | URBAN | Other | 928581 | 1 | 177.3833 | 177.3833 | 0.00010844 | 6.1135e-05
2013-01-27 | ZN14891:PA9 | URBAN | Other | 928587 | 1 | 1005.9167 | 1005.9167 | 0.00061497 | 6.1135e-05
2013-01-27 | ZN12580:PA10 | URBAN | Equipment Failure | 928597 | 1501 | 65 | 92651 | 0.056643 | 0.091764
2013-01-27 | ZN1850:PA13 | URBAN | Equipment Failure | 928605 | 1 | 239.2167 | 239.2167 | 0.00014625 | 6.1135e-05
2013-01-27 | ZN129:PA8 | URBAN | Equipment Failure | 928606 | 1 | 602.7 | 602.7 | 0.00036846 | 6.1135e-05
2013-01-27 | ZN167:PA21 | URBAN | Other | 928609 | 1 | 459.8833 | 459.8833 | 0.00028115 | 6.1135e-05
2013-01-28 | 229:34983 | SHORT RURAL | Other | 928616 | 1243 | 14 | 17402 | 0.010639 | 0.075991
2013-01-27 | ZN12690:PA8 | URBAN | Animals | 928618 | 59 | 56 | 3304 | 0.0020199 | 0.003607
2013-01-27 | 240:34852 | URBAN | Equipment Failure | 928630 | 466 | 402 | 51452 | 0.031455 | 0.028489
2013-01-27 | 258:80781 | SHORT RURAL | Other | 928638 | 1 | 111.3333 | 111.3333 | 6.8064e-05 | 6.1135e-05
2013-01-27 | ZN195:PA9 | URBAN | Vegetation | 928639 | 34 | 134 | 4556 | 0.0027853 | 0.0020786
2013-01-28 | ZN10995:PA1 | URBAN | Other | 928643 | 1 | 535.7333 | 535.7333 | 0.00032752 | 6.1135e-05
2013-01-28 | ZN180:PA21 | URBAN | Other | 928644 | 1 | 50 | 49.5 | 3.0262e-05 | 6.1135e-05
2013-01-28 | ZN180:PA7 | URBAN | Other | 928644 | 67 | 50 | 3350 | 0.002048 | 0.0040961
2013-01-28 | ZN10991:PA7 | URBAN | Other | 928646 | 1 | 352.5167 | 352.5167 | 0.00021551 | 6.1135e-05
2013-01-28 | ZN15006:PA8 | URBAN | Other | 928659 | 1 | 166.8833 | 166.8833 | 0.00010202 | 6.1135e-05
2013-01-28 | ZN1193:PA21 | URBAN | Vegetation | 928689 | 1 | 1190.9667 | 1190.9667 | 0.0007281 | 6.1135e-05
2013-01-28 | 509:48039 | LONG RURAL | Other | 928695 | 1 | 212.3 | 212.3 | 0.00012979 | 6.1135e-05
2013-01-28 | 243:80081 | URBAN | Other | 928708 | 1 | 96.3 | 96.3 | 5.8873e-05 | 6.1135e-05
2013-01-28 | ZN12610:PA7 | URBAN | Equipment Failure | 928716 | 1 | 765.9167 | 765.9167 | 0.00046825 | 6.1135e-05
2013-01-28 | ZN2466:PA16 | URBAN | Other | 928719 | 1 | 543.35 | 543.35 | 0.00033218 | 6.1135e-05
2013-01-28 | 501:48123 | SHORT RURAL | Other | 928741 | 1 | 127.3 | 127.3 | 7.7825e-05 | 6.1135e-05
2013-01-28 | ZN12610:PA13 | URBAN | Other | 928756 | 42 | 229 | 9618 | 0.00588 | 0.0025677
2013-01-28 | ZN10999:PA32 | URBAN | Other | 928764 | 1 | 241.0667 | 241.0667 | 0.00014738 | 6.1135e-05
2013-01-28 | ZN180:PA10 | URBAN | Equipment Failure | 928770 | 1 | 166.45 | 166.45 | 0.00010176 | 6.1135e-05
2013-01-28 | ZN4545:PA40 | URBAN | Vegetation | 928791 | 46 | 57.15 | 2628.9 | 0.0016072 | 0.0028122
2013-01-28 | 256:80635 | URBAN | Equipment Failure | 928797 | 45 | 234.5833 | 10556.25 | 0.0064536 | 0.0027511
2013-01-28 | ZN690:PA35 | URBAN | Other | 928807 | 1 | 350.65 | 350.65 | 0.00021437 | 6.1135e-05
2013-01-28 | ZN690:PA35 | URBAN | Other | 928814 | 1 | 330.6667 | 330.6667 | 0.00020215 | 6.1135e-05
2013-01-28 | ZN14144:PA10 | SHORT RURAL | Vegetation | 928819 | 665 | 178 | 44967 | 0.027491 | 0.040655
2013-01-28 | ZN12610:PA6 | URBAN | Vegetation | 928832 | 59 | 48 | 2832 | 0.0017314 | 0.003607
2013-01-28 | 512:48049 | SHORT RURAL | Other | 928846 | 1 | 119.8167 | 119.8167 | 7.3251e-05 | 6.1135e-05
2013-01-28 | ZN36300:PA9 | URBAN | Vegetation | 928852 | 1 | 273.8833 | 273.8833 | 0.00016744 | 6.1135e-05
2013-01-28 | ZN12650:PA10 | URBAN | Other | 928861 | 1 | 267.8 | 267.8 | 0.00016372 | 6.1135e-05
2013-01-28 | ZN1673:PA13 | URBAN | Weather | 928878 | 867 | 164 | 89467 | 0.054696 | 0.053004
2013-01-28 | ZN1673:PA7 | URBAN | Weather | 928878 | 42 | 164 | 4578 | 0.0027988 | 0.0025677
2013-01-28 | 230:81440 | URBAN | Vegetation | 928879 | 1587 | 125 | 52215 | 0.031922 | 0.097022
2013-01-28 | ZN3154:PA17 | URBAN | Other | 928884 | 1 | 296.4833 | 296.4833 | 0.00018126 | 6.1135e-05
2013-01-28 | ZN9301:PA8 | URBAN | Other | 928893 | 1 | 607.7667 | 607.7667 | 0.00037156 | 6.1135e-05
2013-01-28 | ZN116:PA42 | URBAN | Vegetation | 928894 | 71 | 260.05 | 18463.55 | 0.011288 | 0.0043406
2013-01-28 | ZN12690:PA24 | SHORT RURAL | Other | 928897 | 8 | 163 | 1303.9667 | 0.00079719 | 0.00048908
2013-01-28 | ZN3154:PA17 | URBAN | Vegetation | 928901 | 1 | 449.3833 | 449.3833 | 0.00027473 | 6.1135e-05
2013-01-28 | ZN2473:PA9 | URBAN | Other | 928903 | 1 | 107.1667 | 107.1667 | 6.5517e-05 | 6.1135e-05
2013-01-28 | ZN2400:PA18 | SHORT RURAL | Vegetation | 928904 | 86 | 53.8333 | 4629.6667 | 0.0028304 | 0.0052577
2013-01-28 | ZN1673:PA7 | URBAN | Equipment Failure | 928907 | 17 | 170 | 2890 | 0.0017668 | 0.0010393
2013-01-28 | ZN1788:PA2 | URBAN | Vegetation | 928917 | 1 | 560.5833 | 560.5833 | 0.00034272 | 6.1135e-05
2013-01-28 | ZN2310:PA28 | URBAN | Equipment Failure | 928919 | 2450 | 70 | 126826 | 0.077536 | 0.14978
2013-01-28 | ZN35370:PA8 | SHORT RURAL | Vegetation | 928941 | 482 | 229 | 94870 | 0.057999 | 0.029467
2013-01-28 | ZN965:PA47 | URBAN | Vegetation | 928947 | 1 | 590.8167 | 590.8167 | 0.0003612 | 6.1135e-05
2013-01-28 | ZN10999:PA24 | URBAN | Vegetation | 928962 | 58 | 56 | 3248 | 0.0019857 | 0.0035459
2013-01-28 | 510:48164 | SHORT RURAL | Vegetation | 928973 | 1 | 188.8833 | 188.8833 | 0.00011547 | 6.1135e-05
2013-01-28 | 504:48033 | SHORT RURAL | Other | 928976 | 1 | 90.9667 | 90.9667 | 5.5613e-05 | 6.1135e-05
2013-01-28 | ZN195:PA22 | URBAN | Vegetation | 928977 | 91 | 433 | 39403 | 0.024089 | 0.0055633
2013-01-28 | ZN965:PA21 | URBAN | Vegetation | 928993 | 63 | 166 | 10458 | 0.0063935 | 0.0038515
2013-01-28 | ZN965:PA21 | URBAN | Vegetation | 929021 | 1 | 166 | 166 | 0.00010148 | 6.1135e-05
2013-01-28 | 232:33413 | SHORT RURAL | Vegetation | 929029 | 41 | 680.8667 | 19114.4833 | 0.011686 | 0.0025066
2013-01-28 | 515:35192 | SHORT RURAL | Equipment Failure | 929035 | 1 | 316.6333 | 316.6333 | 0.00019358 | 6.1135e-05
2013-01-28 | ZN2310:PA40 | URBAN | Other | 929037 | 1 | 336.3667 | 336.3667 | 0.00020564 | 6.1135e-05
2013-01-28 | 216:10727 | URBAN | Equipment Failure | 929038 | 8 | 857.6 | 6860.8 | 0.0041944 | 0.00048908
2013-01-28 | ZN1193:PA9 | URBAN | Vegetation | 929045 | 24 | 128.4833 | 3083.6 | 0.0018852 | 0.0014673
2013-01-28 | 242:81539 | URBAN | Vegetation | 929046 | 1 | 1375.35 | 1375.35 | 0.00084083 | 6.1135e-05
2013-01-28 | ZN1193:PA6 | URBAN | Equipment Failure | 929063 | 997 | 119 | 107558 | 0.065756 | 0.060952
2013-01-28 | ZN9700:PA17 | URBAN | Equipment Failure | 929070 | 2065 | 109 | 159122 | 0.09728 | 0.12624
2013-01-28 | 229:34983 | SHORT RURAL | Vegetation | 929073 | 1 | 302.45 | 302.45 | 0.0001849 | 6.1135e-05
2013-01-28 | ZN10995:PA12 | URBAN | Equipment Failure | 929076 | 1 | 1226.05 | 1226.05 | 0.00074955 | 6.1135e-05
2013-01-28 | 509:48039 | LONG RURAL | Equipment Failure | 929086 | 341 | 342 | 36182 | 0.02212 | 0.020847
2013-01-28 | ZN10995:PA12 | URBAN | Equipment Failure | 929087 | 1 | 1216.05 | 1216.05 | 0.00074344 | 6.1135e-05
2013-01-28 | ZN10995:PA12 | URBAN | Equipment Failure | 929088 | 1 | 1216.5 | 1216.5 | 0.00074371 | 6.1135e-05
2013-01-28 | 229:34983 | SHORT RURAL | Vegetation | 929091 | 1 | 285.5 | 285.5 | 0.00017454 | 6.1135e-05
2013-01-28 | ZN35370:PA2 | SHORT RURAL | Vegetation | 929099 | 76 | 282 | 20395 | 0.012469 | 0.0046463
2013-01-28 | 810:74062 | SHORT RURAL | Other | 929105 | 1 | 100.0667 | 100.0667 | 6.1176e-05 | 6.1135e-05
2013-01-28 | 210:8682 | URBAN | Other | 929107 | 1 | 98.4167 | 98.4167 | 6.0168e-05 | 6.1135e-05
2013-01-28 | ZN9252:PA8 | URBAN | Other | 929108 | 1 | 622.1167 | 622.1167 | 0.00038033 | 6.1135e-05
2013-01-28 | 515:35197 | LONG RURAL | Other | 929121 | 1 | 211.4667 | 211.4667 | 0.00012928 | 6.1135e-05
2013-01-28 | ZN14892:PA13 | URBAN | Other | 929125 | 1 | 162.8167 | 162.8167 | 9.9539e-05 | 6.1135e-05
2013-01-28 | 224:80346 | URBAN | Other | 929130 | 1 | 300.4 | 300.4 | 0.00018365 | 6.1135e-05
2013-01-28 | 509:48039 | LONG RURAL | Other | 929136 | 187 | 904.4167 | 169125.9167 | 0.1034 | 0.011432
2013-01-28 | 258:80775 | URBAN | Other | 929140 | 1 | 310.9333 | 310.9333 | 0.00019009 | 6.1135e-05
2013-01-28 | ZN12570:PA33 | SHORT RURAL | Vegetation | 929161 | 759 | 965 | 43279 | 0.026459 | 0.046402
2013-01-28 | 203:8086 | URBAN | Other | 929165 | 1 | 294.1833 | 294.1833 | 0.00017985 | 6.1135e-05
2013-01-28 | 501:48115 | SHORT RURAL | Other | 929173 | 1 | 100.9 | 100.9 | 6.1686e-05 | 6.1135e-05
2013-01-28 | ZN1193:PA9 | URBAN | Third Party Impacts | 929178 | 1 | 1156.15 | 1156.15 | 0.00070682 | 6.1135e-05
2013-01-28 | 230:81440 | URBAN | Vegetation | 929179 | 2 | 966 | 1931.2667 | 0.0011807 | 0.00012227
2013-01-28 | ZN12660:PA14 | SHORT RURAL | Vegetation | 929188 | 1 | 1078.7167 | 1078.7167 | 0.00065948 | 6.1135e-05
2013-01-28 | ZN2400:PA18 | SHORT RURAL | Vegetation | 929207 | 1 | 284 | 284 | 0.00017362 | 6.1135e-05
2013-01-28 | 225:13444 | URBAN | Equipment Failure | 929208 | 440 | 115 | 50600 | 0.030935 | 0.0269
2013-01-28 | ZN2568:PA26 | URBAN | Other | 929212 | 1 | 1169.8667 | 1169.8667 | 0.0007152 | 6.1135e-05
2013-01-28 | 242:81538 | URBAN | Vegetation | 929213 | 68 | 371.2167 | 25242.7333 | 0.015432 | 0.0041572
2013-01-28 | ZN12630:PA5 | SHORT RURAL | Vegetation | 929216 | 159 | 183 | 20820 | 0.012728 | 0.0097205
2013-01-28 | ZN14144:PA4 | URBAN | Other | 929220 | 59 | 46.3167 | 2732.6833 | 0.0016706 | 0.003607
2013-01-28 | 210:8679 | URBAN | Other | 929231 | 1 | 44.0667 | 44.0667 | 2.694e-05 | 6.1135e-05
2013-01-28 | 222:2015 | SHORT RURAL | Other | 929257 | 106 | 71 | 7526 | 0.0046011 | 0.0064804
2013-01-28 | 208:62 | URBAN | Equipment Failure | 929258 | 1 | 92 | 92 | 5.6245e-05 | 6.1135e-05
2013-01-28 | ZN12630:PA1 | SHORT RURAL | Vegetation | 929274 | 231 | 323 | 24452 | 0.014949 | 0.014122
2013-01-28 | ZN12650:PA1 | SHORT RURAL | Vegetation | 929279 | 117 | 931 | 22971 | 0.014043 | 0.0071529
2013-01-28 | ZN15011:PA1 | URBAN | Equipment Failure | 929281 | 96 | 77 | 7236 | 0.0044238 | 0.005869
2013-01-28 | ZN12630:PA3 | SHORT RURAL | Vegetation | 929296 | 2 | 5379 | 10758 | 0.006577 | 0.00012227
2013-01-28 | ZN195:PA11 | URBAN | Vegetation | 929306 | 31 | 222 | 6882 | 0.0042073 | 0.0018952
2013-01-28 | ZN14891:PA16 | SHORT RURAL | Other | 929308 | 1 | 163.1667 | 163.1667 | 9.9753e-05 | 6.1135e-05
2013-01-28 | 222:2018 | URBAN | Other | 929312 | 88 | 67.8667 | 5972.2667 | 0.0036512 | 0.0053799
2013-01-29 | ZN15013:PA2 | URBAN | Vegetation | 929336 | 69 | 282 | 16238 | 0.0099333 | 0.0042209
2013-01-29 | ZN10991:PA5 | URBAN | Equipment Failure | 929342 | 1 | 462.9667 | 462.9667 | 0.00028321 | 6.1173e-05
2013-01-29 | ZN1164:PA20 | URBAN | Equipment Failure | 929344 | 69 | 921 | 63549 | 0.038875 | 0.0042209
2013-01-29 | ZN1648:PA13 | URBAN | Equipment Failure | 929350 | 64 | 101 | 6451 | 0.0039463 | 0.0039151
2013-01-29 | ZN14892:PA19 | URBAN | Other | 929353 | 1 | 106.2 | 106.2 | 6.4966e-05 | 6.1173e-05
2013-01-29 | ZN14892:PA19 | URBAN | Other | 929358 | 1 | 93.4167 | 93.4167 | 5.7146e-05 | 6.1173e-05
2013-01-29 | ZN8000:PA6 | URBAN | Vegetation | 929361 | 1 | 88 | 88 | 5.3832e-05 | 6.1173e-05
2013-01-29 | ZN1068:PA21 | SHORT RURAL | Equipment Failure | 929370 | 29 | 218.0833 | 6324.4167 | 0.0038688 | 0.001774
2013-01-29 | ZN847:PA39 | URBAN | Equipment Failure | 929376 | 59 | 238.7333 | 14085.2667 | 0.0086164 | 0.0036092
2013-01-29 | 225:33670 | SHORT RURAL | Other | 929382 | 1 | 316.5833 | 316.5833 | 0.00019366 | 6.1173e-05
2013-01-29 | ZN15012:PA8 | URBAN | Equipment Failure | 929384 | 1152 | 213 | 73248 | 0.044808 | 0.070471
2013-01-29 | ZN9900:PA21 | URBAN | Equipment Failure | 929386 | 34 | 497 | 16898 | 0.010337 | 0.0020799
2013-01-29 | ZN35500:PA32 | URBAN | Equipment Failure | 929390 | 64 | 261.5667 | 16740.2667 | 0.010241 | 0.0039151
2013-01-29 | 509:48039 | LONG RURAL | Equipment Failure | 929400 | 10 | 55 | 550 | 0.00033645 | 0.00061173
2013-01-29 | ZN9252:PA7 | URBAN | Vegetation | 929405 | 46 | 578 | 17288 | 0.010576 | 0.002814
2013-01-29 | ZN847:PA5 | URBAN | Equipment Failure | 929413 | 40 | 301.1 | 12044 | 0.0073677 | 0.0024469
2013-01-29 | 232:33413 | SHORT RURAL | Vegetation | 929416 | 2 | 56 | 112 | 6.8514e-05 | 0.00012235
2013-01-29 | ZN12620:PA8 | SHORT RURAL | Equipment Failure | 929420 | 1 | 123.6167 | 123.6167 | 7.562e-05 | 6.1173e-05
2013-01-28 | ZN15014:PA12 | SHORT RURAL | Equipment Failure | 929442 | 23 | 683 | 15709 | 0.0096038 | 0.0014061
2013-01-29 | ZN15008:PA7 | URBAN | Equipment Failure | 929451 | 1 | 201.2833 | 201.2833 | 0.00012313 | 6.1173e-05
2013-01-29 | ZN9245:PA14 | URBAN | Equipment Failure | 929460 | 1 | 146.7833 | 146.7833 | 8.9792e-05 | 6.1173e-05
2013-01-29 | 229:34983 | SHORT RURAL | Equipment Failure | 929462 | 1 | 161.2167 | 161.2167 | 9.8621e-05 | 6.1173e-05
2013-01-29 | ZN9700:PA17 | URBAN | Equipment Failure | 929468 | 1 | 231.9667 | 231.9667 | 0.0001419 | 6.1173e-05
2013-01-29 | ZN2400:PA21 | URBAN | Vegetation | 929471 | 1 | 169.5667 | 169.5667 | 0.00010373 | 6.1173e-05
2013-01-29 | 205:12205 | URBAN | Other | 929478 | 1 | 323.2167 | 323.2167 | 0.00019772 | 6.1173e-05
2013-01-29 | ZN847:PA22 | SHORT RURAL | Vegetation | 929484 | 1 | 189.3 | 189.3 | 0.0001158 | 6.1173e-05
2013-01-29 | ZN9700:PA12 | URBAN | Other | 929487 | 10 | 334 | 3340 | 0.0020432 | 0.00061173
2013-01-29 | 264:81240 | SHORT RURAL | Vegetation | 929494 | 1 | 438.7 | 438.7 | 0.00026837 | 6.1173e-05
2013-01-29 | ZN12600:PA13 | SHORT RURAL | Vegetation | 929498 | 1 | 119.8833 | 119.8833 | 7.3336e-05 | 6.1173e-05
2013-01-29 | ZN1193:PA28 | URBAN | Equipment Failure | 929499 | 17 | 215 | 3655 | 0.0022359 | 0.0010399
2013-01-29 | 210:8682 | URBAN | Vegetation | 929566 | 1 | 630.3333 | 630.3333 | 0.00038559 | 6.1173e-05
2013-01-29 | ZN2466:PA16 | URBAN | Other | 929580 | 1 | 42.1833 | 42.1833 | 2.5805e-05 | 6.1173e-05
2013-01-29 | ZN12690:PA24 | SHORT RURAL | Other | 929583 | 7 | 86 | 602 | 0.00036826 | 0.00042821
2013-01-29 | 507:80932 | SHORT RURAL | Other | 929589 | 1 | 110.2167 | 110.2167 | 6.7423e-05 | 6.1173e-05
2013-01-29 | 242:81539 | URBAN | Equipment Failure | 929602 | 1 | 484.75 | 484.75 | 0.00029654 | 6.1173e-05
2013-01-29 | ZN15008:PA5 | URBAN | Other | 929610 | 37 | 184 | 6808 | 0.0041647 | 0.0022634
2013-01-29 | ZN1068:PA21 | SHORT RURAL | Equipment Failure | 929654 | 1 | 134.1 | 134.1 | 8.2033e-05 | 6.1173e-05
2013-01-29 | ZN1648:PA16 | URBAN | Equipment Failure | 929695 | 1 | 118.8833 | 118.8833 | 7.2724e-05 | 6.1173e-05
2013-01-29 | ZN2310:PA28 | URBAN | Equipment Failure | 929710 | 2 | 80 | 160 | 9.7877e-05 | 0.00012235
2013-01-29 | ZN35800:PA14 | URBAN | Equipment Failure | 929710 | 1948 | 80 | 153920 | 0.094157 | 0.11916
2013-01-29 | ZN15014:PA19 | URBAN | Other | 929742 | 1 | 129.4667 | 129.4667 | 7.9199e-05 | 6.1173e-05
2013-01-29 | ZN9252:PA12 | URBAN | Other | 929758 | 2 | 267.2167 | 534.4333 | 0.00032693 | 0.00012235
2013-01-29 | ZN1068:PA21 | SHORT RURAL | Equipment Failure | 929761 | 1 | 253.3333 | 253.3333 | 0.00015497 | 6.1173e-05
2013-01-29 | 504:48029 | URBAN | Equipment Failure | 929763 | 368 | 484 | 36615 | 0.022398 | 0.022512
2013-01-29 | 238:34141 | SHORT RURAL | Equipment Failure | 929783 | 109 | 237 | 16350 | 0.010002 | 0.0066679
2013-01-29 | 510:48164 | SHORT RURAL | Equipment Failure | 929783 | 827 | 237 | 61938 | 0.037889 | 0.05059
2013-01-29 | 261:81882 | URBAN | Other | 929833 | 2 | 257.2667 | 514.5333 | 0.00031476 | 0.00012235
2013-01-29 | ZN12630:PA2 | SHORT RURAL | Vegetation | 929839 | 1 | 223.8 | 223.8 | 0.00013691 | 6.1173e-05
2013-01-23 | ZN35370:PA2 | SHORT RURAL | Vegetation | 929871 | 50 | 3 | 150 | 9.1701e-05 | 0.0030567
2013-01-29 | 232:33413 | SHORT RURAL | Vegetation | 929885 | 1 | 136.2 | 136.2 | 8.3318e-05 | 6.1173e-05
2013-01-29 | ZN188:PA26 | URBAN | Equipment Failure | 929900 | 1 | 759.3667 | 759.3667 | 0.00046453 | 6.1173e-05
2013-01-29 | ZN15014:PA14 | SHORT RURAL | Other | 929903 | 27 | 171 | 4617 | 0.0028244 | 0.0016517
2013-01-29 | ZN72:PA30 | URBAN | Equipment Failure | 929904 | 1 | 93.35 | 93.35 | 5.7105e-05 | 6.1173e-05
2013-01-29 | ZN14144:PA2 | SHORT RURAL | Equipment Failure | 929968 | 1 | 170.45 | 170.45 | 0.00010427 | 6.1173e-05
2013-01-29 | 504:48031 | SHORT RURAL | Equipment Failure | 930027 | 88 | 233 | 11990 | 0.0073346 | 0.0053832
2013-01-29 | ZN14143:PA12 | SHORT RURAL | Equipment Failure | 930084 | 1 | 524.4667 | 524.4667 | 0.00032083 | 6.1173e-05
2013-01-29 | ZN2835:PA19 | URBAN | Other | 930086 | 1 | 256.4833 | 256.4833 | 0.0001569 | 6.1173e-05
2013-01-29 | 524:33572 | SHORT RURAL | Equipment Failure | 930087 | 1 | 466.35 | 466.35 | 0.00028528 | 6.1173e-05
2013-01-29 | ZN12660:PA6 | SHORT RURAL | Vegetation | 930088 | 1 | 251 | 251 | 0.00015354 | 6.1173e-05
2013-01-29 | ZN8000:PA6 | URBAN | Vegetation | 930129 | 1 | 109.85 | 109.85 | 6.7199e-05 | 6.1173e-05
2013-01-29 | 516:48066 | SHORT RURAL | Other | 930151 | 1 | 86.1667 | 68 | 4.1598e-05 | 6.1173e-05
2013-01-29 | 516:48067 | SHORT RURAL | Other | 930151 | 1 | 86.1667 | 85.55 | 5.2333e-05 | 6.1173e-05
2013-01-24 | ZN3425:PA32 | URBAN | Equipment Failure | 930160 | 179 | 56 | 9304 | 0.0056889 | 0.010945
2013-01-29 | 810:74054 | LONG RURAL | Other | 930195 | 5 | 308.2167 | 1541.0833 | 0.00094273 | 0.00030586
2013-01-29 | ZN965:PA8 | URBAN | Equipment Failure | 930197 | 28 | 91.1 | 2550.8 | 0.0015604 | 0.0017128
2013-01-29 | 216:10724 | SHORT RURAL | Other | 930210 | 73 | 83.1167 | 6067.5167 | 0.0037117 | 0.0044656
2013-01-29 | ZN10999:PA24 | URBAN | Vegetation | 930230 | 1 | 619.9167 | 619.9167 | 0.00037922 | 6.1173e-05
2013-01-25 | ZN35500:PA18 | SHORT RURAL | Equipment Failure | 930242 | 118 | 54 | 6372 | 0.0038956 | 0.007214
2013-01-29 | 503:48017 | URBAN | Equipment Failure | 930245 | 313 | 335 | 60980 | 0.037303 | 0.019147
2013-01-29 | 232:33413 | SHORT RURAL | Other | 930247 | 1 | 149.2833 | 149.2833 | 9.1321e-05 | 6.1173e-05
2013-01-29 | ZN2602:PA33 | URBAN | Equipment Failure | 930263 | 1 | 803.1667 | 803.1667 | 0.00049132 | 6.1173e-05
2013-01-29 | ZN3154:PA18 | URBAN | Vegetation | 930270 | 39 | 186.15 | 7259.85 | 0.0044411 | 0.0023857
2013-01-29 | ZN12650:PA1 | SHORT RURAL | Vegetation | 930276 | 17 | 353 | 2283 | 0.0013966 | 0.0010399
2013-01-29 | ZN15014:PA18 | URBAN | Equipment Failure | 930290 | 1 | 385.7667 | 385.7667 | 0.00023598 | 6.1173e-05
2013-01-29 | ZN14144:PA10 | SHORT RURAL | Vegetation | 930296 | 11 | 65 | 715 | 0.00043739 | 0.0006729
2013-01-29 | ZN965:PA20 | URBAN | Equipment Failure | 930303 | 1 | 454.1167 | 454.1167 | 0.0002778 | 6.1173e-05
2013-01-29 | ZN9245:PA12 | URBAN | Vegetation | 930312 | 377 | 58 | 19763 | 0.01209 | 0.023062
2013-01-29 | ZN15014:PA19 | URBAN | Other | 930324 | 2 | 355.25 | 710.5 | 0.00043463 | 0.00012235
2013-01-29 | 507:80931 | URBAN | Other | 930327 | 1 | 127.2833 | 127.2833 | 7.7863e-05 | 6.1173e-05
2013-01-29 | 230:81440 | URBAN | Vegetation | 930340 | 1 | 354.15 | 354.15 | 0.00021664 | 6.1173e-05
2013-01-29 | ZN1788:PA17 | URBAN | Other | 930348 | 1 | 157.15 | 157.15 | 9.6133e-05 | 6.1173e-05
2013-01-29 | ZN3922:PA5 | URBAN | Other | 930358 | 105 | 70 | 7350 | 0.0044962 | 0.0064232
2013-01-29 | ZN195:PA28 | URBAN | Third Party Impacts | 930360 | 2 | 690 | 1370.2833 | 0.00083824 | 0.00012235
2013-01-29 | ZN2196:PA9 | URBAN | Other | 930361 | 1 | 1054.5167 | 1054.5167 | 0.00064508 | 6.1173e-05
2013-01-29 | 524:33578 | URBAN | Other | 930368 | 1 | 128.1667 | 128.1667 | 7.8403e-05 | 6.1173e-05
2013-01-29 | ZN180:PA21 | URBAN | Equipment Failure | 930374 | 44 | 30 | 1320 | 0.00080748 | 0.0026916
2013-01-29 | 242:81541 | URBAN | Other | 930381 | 1 | 149.2667 | 149.2667 | 9.1311e-05 | 6.1173e-05
2013-01-29 | ZN7481:PA1 | URBAN | Other | 930385 | 1 | 419.8833 | 419.8833 | 0.00025686 | 6.1173e-05
2013-01-30 | ZN180:PA30 | URBAN | Vegetation | 930403 | 44 | 37 | 1628 | 0.00099404 | 0.0026866
2013-01-29 | ZN1673:PA19 | URBAN | Other | 930415 | 1 | 509.7833 | 509.7833 | 0.00031185 | 6.1173e-05
2013-01-29 | ZN10999:PA19 | URBAN | Equipment Failure | 930424 | 1 | 677.2167 | 677.2167 | 0.00041427 | 6.1173e-05
2013-01-29 | ZN80:PA32 | URBAN | Vegetation | 930428 | 59 | 100 | 5900 | 0.0036092 | 0.0036092
2013-01-29 | ZN3154:PA25 | URBAN | Vegetation | 930430 | 18 | 240 | 4320 | 0.0026427 | 0.0011011
2013-01-29 | ZN2602:PA21 | URBAN | Animals | 930438 | 1 | 433.1167 | 433.1167 | 0.00026495 | 6.1173e-05
2013-01-29 | 511:29880 | URBAN | Other | 930450 | 20 | 107 | 2140 | 0.0013091 | 0.0012235
2013-01-30 | ZN3472:PA15 | URBAN | Equipment Failure | 930453 | 949 | 102 | 46164 | 0.028187 | 0.057945
2013-01-30 | ZN180:PA21 | URBAN | Other | 930454 | 1 | 124 | 124 | 7.5713e-05 | 6.1059e-05
2013-01-30 | ZN180:PA7 | URBAN | Other | 930454 | 67 | 124 | 8261.1 | 0.0050441 | 0.0040909
2013-01-30 | 503:48017 | URBAN | Other | 930477 | 25 | 59.3667 | 1484.1667 | 0.00090622 | 0.0015265
2013-01-30 | ZN12610:PA2 | URBAN | Other | 930480 | 1 | 146.1167 | 146.1167 | 8.9217e-05 | 6.1059e-05
2013-01-30 | ZN180:PA29 | URBAN | Other | 930486 | 43 | 44.5167 | 1914.2167 | 0.0011688 | 0.0026255
2013-01-25 | ZN2310:PA21 | URBAN | Weather | 930487 | 64 | 75 | 4800 | 0.0029345 | 0.0039127
2013-01-30 | ZN180:PA27 | URBAN | Other | 930491 | 77 | 45 | 3465 | 0.0021157 | 0.0047015
2013-01-30 | ZN180:PA19 | URBAN | Equipment Failure | 930514 | 77 | 270 | 20790 | 0.012694 | 0.0047015
2013-01-30 | 811:74234 | SHORT RURAL | Other | 930551 | 1 | 150.4 | 150.4 | 9.1833e-05 | 6.1059e-05
2013-01-29 | ZN15013:PA2 | URBAN | Vegetation | 930556 | 20 | 25 | 500 | 0.00030586 | 0.0012235
2013-01-28 | 509:48039 | LONG RURAL | Other | 930577 | 1 | 180 | 180 | 0.00011004 | 6.1135e-05
2013-01-25 | 813:89061 | LONG RURAL | Other | 930645 | 1 | 119 | 119 | 7.2751e-05 | 6.1135e-05
2013-01-30 | ZN3472:PA29 | URBAN | Third Party Impacts | 930658 | 60 | 49.4 | 2964 | 0.0018098 | 0.0036635
2013-01-30 | ZN10990:PA8 | URBAN | Third Party Impacts | 930793 | 1 | 165 | 165 | 0.00010075 | 6.1059e-05
2013-01-30 | ZN180:PA7 | URBAN | Equipment Failure | 930848 | 70 | 79.1833 | 5542.8333 | 0.0033844 | 0.0042741
2013-01-30 | ZN180:PA7 | URBAN | Other | 930860 | 117 | 91.1333 | 10662.6 | 0.0065105 | 0.0071439
2013-01-30 | 806:74080 | SHORT RURAL | Animals | 930874 | 1 | 308.7 | 308.7 | 0.00018849 | 6.1059e-05
2013-01-30 | 213:33771 | URBAN | Other | 930876 | 1 | 141.5 | 141.5 | 8.6398e-05 | 6.1059e-05
2013-01-30 | ZN116:PA44 | URBAN | Other | 930877 | 1 | 110.5833 | 110.5833 | 6.7521e-05 | 6.1059e-05
2013-01-30 | 504:48033 | SHORT RURAL | Equipment Failure | 930895 | 1 | 26 | 26 | 1.5875e-05 | 6.1059e-05
2013-01-30 | 227:13020 | SHORT RURAL | Other | 930992 | 1 | 109.6333 | 109.6333 | 6.6941e-05 | 6.1059e-05
2013-01-29 | ZN9245:PA8 | SHORT RURAL | Vegetation | 930994 | 67 | 41 | 2747 | 0.0016804 | 0.0040986
2013-01-30 | ZN3154:PA18 | URBAN | Other | 930997 | 1 | 628.9833 | 628.9833 | 0.00038405 | 6.1059e-05
2013-01-29 | ZN9245:PA12 | URBAN | Vegetation | 930999 | 44 | 41 | 1804 | 0.0011036 | 0.0026916
2013-01-30 | ZN14892:PA17 | URBAN | Other | 931010 | 1 | 1298.1833 | 1298.1833 | 0.00079266 | 6.1059e-05
2013-01-30 | ZN4545:PA4 | URBAN | Other | 931046 | 45 | 93.1167 | 4190.25 | 0.0025585 | 0.0027477
2013-01-30 | 513:48057 | URBAN | Other | 931062 | 1 | 52.3167 | 52.3167 | 3.1944e-05 | 6.1059e-05
2013-01-30 | 504:48028 | URBAN | Other | 931072 | 1 | 132.1667 | 132.1667 | 8.07e-05 | 6.1059e-05
2013-01-30 | 230:81438 | SHORT RURAL | Other | 931078 | 1 | 140.2333 | 140.2333 | 8.5625e-05 | 6.1059e-05
2013-01-30 | ZN12660:PA8 | URBAN | Equipment Failure | 931085 | 44 | 255 | 11220 | 0.0068508 | 0.0026866
2013-01-30 | 516:48067 | SHORT RURAL | Equipment Failure | 931096 | 1 | 168.7 | 168.7 | 0.00010301 | 6.1059e-05
2013-01-30 | 232:11454 | SHORT RURAL | Other | 931103 | 1 | 130.1167 | 130.1167 | 7.9448e-05 | 6.1059e-05
2013-01-30 | 224:80329 | SHORT RURAL | Equipment Failure | 931108 | 51 | 76.35 | 3893.85 | 0.0023775 | 0.003114
2013-01-31 | 214:8670 | URBAN | Other | 931115 | 68 | 61 | 4148 | 0.0025327 | 0.004152
2013-01-31 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 931118 | 13 | 109 | 1417 | 0.00086521 | 0.00079377
2013-01-30 | 504:48029 | URBAN | Other | 931160 | 1 | 60 | 60 | 3.6635e-05 | 6.1059e-05
2013-01-29 | ZN10993:PA1 | URBAN | Other | 931165 | 227 | 4 | 908 | 0.00055545 | 0.013886
2013-01-29 | ZN10993:PA2 | URBAN | Other | 931165 | 1136 | 4 | 4544 | 0.0027797 | 0.069492
2013-01-29 | ZN10993:PA5 | URBAN | Other | 931165 | 1821 | 4 | 7284 | 0.0044558 | 0.1114
2013-01-29 | ZN10993:PA6 | URBAN | Other | 931165 | 595 | 4 | 2380 | 0.0014559 | 0.036398
2013-01-31 | 243:80083 | SHORT RURAL | Equipment Failure | 931214 | 1 | 145.2667 | 145.2667 | 8.8699e-05 | 6.1059e-05
2013-01-31 | ZN15008:PA5 | URBAN | Third Party Impacts | 931232 | 1 | 291.3833 | 291.3833 | 0.00017792 | 6.1059e-05
2013-01-31 | ZN10995:PA13 | URBAN | Other | 931250 | 1 | 298.95 | 298.95 | 0.00018254 | 6.1059e-05
2013-01-31 | ZN12630:PA3 | SHORT RURAL | Vegetation | 931267 | 1 | 250.3333 | 250.3333 | 0.00015285 | 6.1059e-05
2013-01-29 | ZN1164:PA12 | URBAN | Other | 931283 | 1 | 421 | 421 | 0.00025754 | 6.1173e-05
2013-01-31 | ZN2196:PA20 | URBAN | Equipment Failure | 931350 | 2 | 410 | 820 | 0.00050069 | 0.00012212
2013-01-31 | 242:81539 | URBAN | Vegetation | 931386 | 1 | 253.6833 | 253.6833 | 0.0001549 | 6.1059e-05
2013-01-31 | 513:48051 | URBAN | Other | 931390 | 1 | 66.9 | 66.9 | 4.0849e-05 | 6.1059e-05
2013-01-31 | 222:2018 | URBAN | Equipment Failure | 931407 | 111 | 46.1667 | 5124.5 | 0.003129 | 0.0067776
2013-01-31 | 224:80341 | URBAN | Other | 931428 | 1 | 37.9 | 37.9 | 2.3142e-05 | 6.1059e-05
2013-01-30 | ZN12690:PA3 | SHORT RURAL | Other | 931472 | 2 | 25 | 50 | 3.0529e-05 | 0.00012212
2013-01-31 | 230:81440 | URBAN | Other | 931476 | 1 | 45 | 45 | 2.7477e-05 | 6.1059e-05
2013-01-31 | ZN12580:PA12 | SHORT RURAL | Vegetation | 931485 | 1 | 57.1167 | 57.1167 | 3.4875e-05 | 6.1059e-05
2013-01-31 | 813:89062 | SHORT RURAL | Equipment Failure | 931511 | 1 | 387.7667 | 387.7667 | 0.00023677 | 6.1059e-05
2013-01-31 | 504:48033 | SHORT RURAL | Equipment Failure | 931522 | 1151 | 553 | 170650 | 0.1042 | 0.070279
2013-01-31 | 525:34580 | SHORT RURAL | Equipment Failure | 931522 | 3 | 553 | 258 | 0.00015753 | 0.00018318
2013-01-31 | 525:34586 | SHORT RURAL | Equipment Failure | 931522 | 3 | 553 | 258 | 0.00015753 | 0.00018318
2013-01-31 | 525:34589 | URBAN | Equipment Failure | 931522 | 1 | 553 | 86 | 5.2511e-05 | 6.1059e-05
2013-01-31 | 801:74121 | SHORT RURAL | Other | 931578 | 3 | 193 | 579 | 0.00035353 | 0.00018318
2013-01-31 | ZN12660:PA5 | SHORT RURAL | Other | 931586 | 1 | 253.1 | 253.1 | 0.00015454 | 6.1059e-05
2013-01-31 | ZN9245:PA10 | URBAN | Vegetation | 931629 | 1 | 80.0333 | 80.0333 | 4.8868e-05 | 6.1059e-05
2013-01-31 | ZN9245:PA10 | URBAN | Vegetation | 931630 | 1 | 94.2833 | 94.2833 | 5.7569e-05 | 6.1059e-05
2013-01-31 | 223:14393 | URBAN | Other | 931641 | 1 | 153.5833 | 153.5833 | 9.3777e-05 | 6.1059e-05
2013-01-31 | ZN9245:PA10 | URBAN | Vegetation | 931642 | 1 | 29.9167 | 29.9167 | 1.8267e-05 | 6.1059e-05
2013-01-31 | 265:81651 | URBAN | Equipment Failure | 931643 | 81 | 114 | 9234 | 0.0056382 | 0.0049458
2013-01-31 | 507:80932 | SHORT RURAL | Equipment Failure | 931649 | 6 | 271 | 1626 | 0.00099283 | 0.00036636
2013-02-01 | 524:33570 | SHORT RURAL | Equipment Failure | 931658 | 94 | 53.55 | 5033.7 | 0.0030736 | 0.0057397
2013-02-01 | 501:48123 | SHORT RURAL | Vegetation | 931665 | 8 | 118 | 944 | 0.00057641 | 0.00048848
2013-02-01 | ZN36300:PA5 | URBAN | Equipment Failure | 931685 | 1 | 434.8333 | 434.8333 | 0.00026551 | 6.106e-05
2013-01-30 | ZN1285:PA27 | URBAN | Vegetation | 931704 | 14 | 118 | 1652 | 0.0010087 | 0.00085482
2013-02-01 | 524:33572 | SHORT RURAL | Equipment Failure | 931708 | 86 | 49.8667 | 4288.5333 | 0.0026186 | 0.0052512
2013-02-01 | 504:48026 | SHORT RURAL | Animals | 931711 | 46 | 42 | 1932 | 0.0011797 | 0.0028088
2013-01-31 | 810:74058 | SHORT RURAL | Other | 931734 | 2 | 105 | 210 | 0.00012822 | 0.00012212
2013-02-01 | ZN2196:PA20 | URBAN | Equipment Failure | 931735 | 1 | 643.1667 | 643.1667 | 0.00039272 | 6.106e-05
2013-02-01 | ZN384:PA9 | URBAN | Vegetation | 931774 | 133 | 66.8167 | 8886.6167 | 0.0054262 | 0.008121
2013-02-01 | ZN9252:PA2 | URBAN | Vegetation | 931779 | 1 | 442.9 | 442.9 | 0.00027044 | 6.106e-05
2013-02-01 | ZN2466:PA20 | URBAN | Other | 931815 | 20 | 281 | 5620 | 0.0034316 | 0.0012212
2013-02-01 | ZN14891:PA10 | SHORT RURAL | Vegetation | 931817 | 1 | 159.6333 | 159.6333 | 9.7473e-05 | 6.106e-05
2013-02-01 | 502:48010 | SHORT RURAL | Other | 931822 | 1 | 79.6 | 79.6 | 4.8604e-05 | 6.106e-05
2013-01-28 | ZN965:PA20 | URBAN | Vegetation | 931826 | 56 | 134 | 5992 | 0.0036632 | 0.0034236
2013-01-28 | ZN965:PA42 | URBAN | Vegetation | 931826 | 255 | 134 | 30106 | 0.018405 | 0.01559
2013-02-01 | 502:48010 | SHORT RURAL | Other | 931829 | 1 | 73.3833 | 73.3833 | 4.4808e-05 | 6.106e-05
2013-02-01 | ZN3472:PA29 | URBAN | Third Party Impacts | 931849 | 1 | 135.6167 | 135.6167 | 8.2808e-05 | 6.106e-05
2013-01-31 | ZN12690:PA26 | URBAN | Equipment Failure | 931853 | 3 | 431 | 1293 | 0.0007895 | 0.00018318
2013-02-01 | ZN1164:PA8 | URBAN | Other | 931854 | 1 | 219.2333 | 219.2333 | 0.00013386 | 6.106e-05
2013-02-01 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 931856 | 20 | 158 | 3160 | 0.0019295 | 0.0012212
2013-02-01 | ZN3155:PA44 | URBAN | Vegetation | 931861 | 122 | 58.1333 | 7092.2667 | 0.0043306 | 0.0074494
2013-02-01 | ZN965:PA21 | URBAN | Vegetation | 931867 | 47 | 67.7667 | 3185.0333 | 0.0019448 | 0.0028698
2013-02-01 | ZN12610:PA13 | URBAN | Weather | 931895 | 1965 | 63 | 117516 | 0.071756 | 0.11998
2013-02-01 | 806:74080 | SHORT RURAL | Equipment Failure | 931906 | 17 | 471 | 6691 | 0.0040855 | 0.001038
2013-02-01 | ZN12690:PA16 | SHORT RURAL | Vegetation | 931924 | 1 | 79.8667 | 79.8667 | 4.8767e-05 | 6.106e-05
2013-02-01 | ZN35500:PA28 | URBAN | Equipment Failure | 931935 | 1 | 131.0333 | 131.0333 | 8.0009e-05 | 6.106e-05
2013-02-01 | ZN3155:PA44 | URBAN | Vegetation | 931937 | 1 | 10.0667 | 10.0667 | 6.1467e-06 | 6.106e-05
2013-02-01 | ZN2466:PA41 | URBAN | Other | 931939 | 16 | 1346 | 21536 | 0.01315 | 0.00097696
2013-02-01 | ZN1164:PA15 | URBAN | Other | 931943 | 1 | 693.4833 | 693.4833 | 0.00042344 | 6.106e-05
2013-02-01 | ZN262:PA6 | URBAN | Other | 931956 | 1 | 107.0667 | 107.0667 | 6.5375e-05 | 6.106e-05
2013-02-01 | ZN10990:PA11 | URBAN | Vegetation | 931957 | 88 | 347 | 30536 | 0.018645 | 0.0053733
2013-02-01 | ZN9252:PA10 | URBAN | Vegetation | 931958 | 1 | 24.6333 | 24.6333 | 1.5041e-05 | 6.106e-05
2013-02-01 | 524:33572 | SHORT RURAL | Other | 931970 | 13 | 70.3 | 913.9 | 0.00055803 | 0.00079378
2013-01-18 | ZN9037:PA2 | URBAN | Equipment Failure | 931980 | 102 | 110 | 11220 | 0.0068591 | 0.0062355
2013-02-01 | ZN12650:PA1 | SHORT RURAL | Other | 931995 | 1 | 1483.45 | 1483.45 | 0.0009058 | 6.106e-05
2013-02-01 | 238:34144 | URBAN | Equipment Failure | 932002 | 837 | 3742 | 69274 | 0.042299 | 0.051107
2013-02-01 | ZN10996:PA14 | URBAN | Vegetation | 932026 | 54 | 153.5 | 8289 | 0.0050613 | 0.0032973
2013-02-01 | ZN9245:PA15 | URBAN | Vegetation | 932031 | 1 | 318.7167 | 318.7167 | 0.00019461 | 6.106e-05
2013-02-01 | ZN9245:PA15 | URBAN | Vegetation | 932040 | 1 | 293.3333 | 293.3333 | 0.00017911 | 6.106e-05
2013-02-01 | ZN2568:PA30 | URBAN | Vegetation | 932062 | 1 | 1295.6833 | 1295.6833 | 0.00079115 | 6.106e-05
2013-02-01 | ZN15012:PA4 | URBAN | Equipment Failure | 932076 | 1186 | 67 | 70830 | 0.043249 | 0.072417
2013-02-01 | 509:48039 | LONG RURAL | Vegetation | 932077 | 56 | 150 | 8400 | 0.0051291 | 0.0034194
2013-02-01 | ZN15012:PA6 | URBAN | Other | 932078 | 1 | 171.6833 | 171.6833 | 0.00010483 | 6.106e-05
2013-02-01 | ZN187:PA10 | URBAN | Equipment Failure | 932083 | 1 | 148.7833 | 148.7833 | 9.0848e-05 | 6.106e-05
2013-02-01 | ZN12690:PA24 | SHORT RURAL | Vegetation | 932085 | 9 | 201.1333 | 1476.85 | 0.00090177 | 0.00054954
2013-02-01 | ZN35600:PA7 | URBAN | Weather | 932089 | 1 | 120.8833 | 120.8833 | 7.3812e-05 | 6.106e-05
2013-02-01 | ZN180:PA23 | URBAN | Other | 932097 | 1 | 235.3 | 235.3 | 0.00014367 | 6.106e-05
2013-02-01 | 515:35197 | LONG RURAL | Other | 932101 | 6 | 96.5667 | 579.4 | 0.00035378 | 0.00036636
2013-02-01 | ZN10995:PA2 | URBAN | Weather | 932108 | 140 | 186 | 26040 | 0.0159 | 0.0085484
2013-02-01 | 515:35197 | LONG RURAL | Equipment Failure | 932111 | 4 | 584 | 2336 | 0.0014264 | 0.00024424
2013-02-01 | 261:81865 | URBAN | Vegetation | 932113 | 1 | 79.6667 | 79.6667 | 4.8645e-05 | 6.106e-05
2013-02-01 | 811:74234 | SHORT RURAL | Equipment Failure | 932133 | 13 | 101.35 | 1317.55 | 0.0008045 | 0.00079378
2013-02-01 | ZN9252:PA10 | URBAN | Equipment Failure | 932135 | 1516 | 57 | 78593 | 0.047989 | 0.092567
2013-02-01 | ZN3672:PA44 | URBAN | Vegetation | 932153 | 130 | 43 | 5590 | 0.0034133 | 0.0079378
2013-02-01 | ZN12600:PA1 | SHORT RURAL | Equipment Failure | 932177 | 601 | 135 | 79507 | 0.048547 | 0.036697
2013-02-01 | ZN2310:PA3 | URBAN | Other | 932180 | 1 | 220.4167 | 220.4167 | 0.00013459 | 6.106e-05
2013-02-01 | ZN3425:PA12 | URBAN | Equipment Failure | 932189 | 17 | 620.7 | 10551.9 | 0.006443 | 0.001038
2013-02-01 | 504:48033 | SHORT RURAL | Equipment Failure | 932224 | 110 | 229 | 25190 | 0.015381 | 0.0067166
2013-02-01 | ZN80:PA40 | URBAN | Equipment Failure | 932238 | 1 | 1043.95 | 1043.95 | 0.00063744 | 6.106e-05
2013-02-01 | 512:48049 | SHORT RURAL | Equipment Failure | 932254 | 6 | 189 | 1134 | 0.00069242 | 0.00036636
2013-02-01 | ZN9700:PA12 | URBAN | Equipment Failure | 932260 | 10 | 885.2333 | 8852.3333 | 0.0054053 | 0.0006106
2013-02-01 | 520:48172 | SHORT RURAL | Equipment Failure | 932269 | 1 | 344 | 344 | 0.00021005 | 6.106e-05
2013-02-01 | 509:48039 | LONG RURAL | Other | 932276 | 1 | 246.0333 | 246.0333 | 0.00015023 | 6.106e-05
2013-02-01 | ZN2568:PA22 | URBAN | Other | 932279 | 1 | 330.9333 | 330.9333 | 0.00020207 | 6.106e-05
2013-02-01 | 242:81539 | URBAN | Vegetation | 932283 | 1 | 170.4667 | 170.4667 | 0.00010409 | 6.106e-05
2013-02-01 | ZN9035:PA4 | URBAN | Other | 932293 | 1 | 81.0333 | 81.0333 | 4.9479e-05 | 6.106e-05
2013-02-01 | ZN15014:PA11 | URBAN | Vegetation | 932294 | 39 | 50 | 1950 | 0.0011907 | 0.0023814
2013-02-01 | ZN12690:PA24 | SHORT RURAL | Vegetation | 932300 | 6 | 10 | 60 | 3.6636e-05 | 0.00036636
2013-02-01 | ZN12690:PA24 | SHORT RURAL | Vegetation | 932306 | 1 | 1210.3 | 1210.3 | 0.00073901 | 6.106e-05
2013-02-01 | ZN10999:PA17 | URBAN | Other | 932309 | 1 | 1121.8667 | 1121.8667 | 0.00068501 | 6.106e-05
2013-02-01 | ZN2568:PA26 | URBAN | Other | 932326 | 1 | 103.6 | 103.6 | 6.3258e-05 | 6.106e-05
2013-02-01 | ZN3472:PA30 | URBAN | Equipment Failure | 932334 | 1 | 244.6167 | 244.6167 | 0.00014936 | 6.106e-05
2013-02-01 | ZN80:PA32 | URBAN | Other | 932335 | 1 | 32.9 | 32.9 | 2.0089e-05 | 6.106e-05
2013-02-01 | ZN80:PA32 | URBAN | Animals | 932342 | 123 | 88 | 10824 | 0.0066092 | 0.0075104
2013-02-01 | ZN384:PA9 | URBAN | Equipment Failure | 932348 | 1 | 729.45 | 729.45 | 0.0004454 | 6.106e-05
2013-02-01 | ZN12650:PA17 | URBAN | Other | 932354 | 39 | 185 | 7215 | 0.0044055 | 0.0023814
2013-02-01 | ZN9550:PA42 | URBAN | Vegetation | 932359 | 4 | 113 | 452 | 0.00027599 | 0.00024424
2013-02-01 | ZN9700:PA17 | URBAN | Equipment Failure | 932364 | 1 | 687.9167 | 687.9167 | 0.00042004 | 6.106e-05
2013-02-01 | ZN4545:PA35 | URBAN | Other | 932369 | 1 | 73.5167 | 57.6833 | 3.5222e-05 | 6.106e-05
2013-02-01 | ZN4545:PA41 | URBAN | Other | 932369 | 5 | 73.5167 | 225 | 0.00013739 | 0.0003053
2013-02-01 | ZN4545:PA44 | URBAN | Other | 932369 | 1051 | 73.5167 | 47640 | 0.029089 | 0.064174
2013-02-01 | ZN4545:PA6 | URBAN | Other | 932369 | 694 | 73.5167 | 29842 | 0.018222 | 0.042376
2013-02-02 | ZN14143:PA17 | SHORT RURAL | Other | 932379 | 747 | 117 | 70281 | 0.042914 | 0.045612
2013-02-02 | 515:35197 | LONG RURAL | Equipment Failure | 932380 | 2 | 595 | 1190 | 0.00072662 | 0.00012212
2013-02-02 | ZN2310:PA34 | URBAN | Equipment Failure | 932387 | 1 | 165.85 | 165.85 | 0.00010127 | 6.106e-05
2013-02-02 | ZN2310:PA34 | URBAN | Equipment Failure | 932388 | 1 | 160.7 | 160.7 | 9.8124e-05 | 6.106e-05
2013-02-02 | ZN15014:PA12 | SHORT RURAL | Other | 932389 | 1 | 718.85 | 718.85 | 0.00043893 | 6.106e-05
2013-02-02 | ZN4545:PA42 | URBAN | Other | 932390 | 218 | 239 | 41732 | 0.025482 | 0.013311
2013-02-02 | ZN4545:PA44 | URBAN | Other | 932390 | 15 | 239 | 2910 | 0.0017769 | 0.0009159
2013-02-02 | 225:33670 | SHORT RURAL | Other | 932392 | 1 | 414.4667 | 414.4667 | 0.00025307 | 6.106e-05
2013-02-02 | 261:81876 | URBAN | Other | 932403 | 1 | 55.9 | 55.9 | 3.4133e-05 | 6.106e-05
2013-02-02 | ZN1193:PA6 | URBAN | Vegetation | 932404 | 61 | 151.6667 | 9251.6667 | 0.0056491 | 0.0037247
2013-02-02 | ZN12630:PA4 | SHORT RURAL | Vegetation | 932415 | 11 | 85 | 935 | 0.00057091 | 0.00067166
2013-02-02 | 261:81870 | URBAN | Other | 932427 | 1 | 286.3333 | 286.3333 | 0.00017484 | 6.106e-05
2013-02-02 | ZN12630:PA3 | SHORT RURAL | Vegetation | 932434 | 29 | 115.4667 | 3348.5333 | 0.0020446 | 0.0017707
2013-02-02 | ZN2400:PA11 | SHORT RURAL | Equipment Failure | 932437 | 86 | 39.2333 | 3374.0667 | 0.0020602 | 0.0052512
2013-02-02 | ZN10999:PA24 | URBAN | Third Party Impacts | 932438 | 51 | 45 | 2295 | 0.0014013 | 0.0031141
2013-02-02 | 223:14393 | URBAN | Other | 932462 | 1 | 101.7833 | 101.7833 | 6.2149e-05 | 6.106e-05
2013-02-02 | 202:34254 | URBAN | Other | 932466 | 1 | 128.65 | 128.65 | 7.8554e-05 | 6.106e-05
2013-02-02 | ZN15002:PA6 | URBAN | Other | 932469 | 1 | 332.0167 | 332.0167 | 0.00020273 | 6.106e-05
2013-02-02 | ZN847:PA14 | URBAN | Vegetation | 932476 | 1 | 309.8833 | 309.8833 | 0.00018922 | 6.106e-05
2013-02-02 | 242:81541 | URBAN | Vegetation | 932497 | 1 | 165.0167 | 165.0167 | 0.00010076 | 6.106e-05
2013-02-02 | 509:48039 | LONG RURAL | Other | 932505 | 1 | 153.2333 | 153.2333 | 9.3565e-05 | 6.106e-05
2013-02-02 | ZN3672:PA26 | URBAN | Equipment Failure | 932512 | 1 | 377.3667 | 377.3667 | 0.00023042 | 6.106e-05
2013-02-02 | 232:11457 | URBAN | Other | 932537 | 1 | 207.5 | 207.5 | 0.0001267 | 6.106e-05
2013-02-02 | 235:2123 | URBAN | Other | 932544 | 1 | 103.8667 | 103.8667 | 6.3421e-05 | 6.106e-05
2013-02-02 | ZN12610:PA25 | SHORT RURAL | Animals | 932562 | 79 | 74 | 5846 | 0.0035696 | 0.0048238
2013-02-02 | 202:34259 | URBAN | Other | 932571 | 999 | 58 | 57942 | 0.03538 | 0.060999
2013-02-02 | ZN116:PA47 | URBAN | Other | 932578 | 5 | 243 | 1215 | 0.00074188 | 0.0003053
2013-02-02 | ZN2400:PA22 | URBAN | Other | 932579 | 1 | 164.4 | 164.4 | 0.00010038 | 6.106e-05
2013-02-02 | 256:80646 | URBAN | Other | 932581 | 1 | 308.65 | 308.65 | 0.00018846 | 6.106e-05
2013-02-02 | ZN9700:PA24 | URBAN | Equipment Failure | 932586 | 26 | 110.2667 | 2866.9333 | 0.0017506 | 0.0015876
2013-02-02 | ZN15012:PA8 | URBAN | Vegetation | 932596 | 1151 | 46 | 52946 | 0.032329 | 0.07028
2013-02-02 | 801:74122 | URBAN | Other | 932601 | 1 | 143.8167 | 143.8167 | 8.7815e-05 | 6.106e-05
2013-02-02 | 806:74080 | SHORT RURAL | Other | 932616 | 1 | 160.9167 | 160.9167 | 9.8256e-05 | 6.106e-05
2013-02-02 | 261:81864 | URBAN | Other | 932619 | 1 | 114.7 | 114.7 | 7.0036e-05 | 6.106e-05
2013-02-02 | ZN2473:PA15 | URBAN | Equipment Failure | 932621 | 447 | 67 | 25241 | 0.015412 | 0.027294
2013-02-02 | ZN384:PA33 | URBAN | Equipment Failure | 932626 | 1 | 110 | 110 | 6.7166e-05 | 6.106e-05
2013-02-02 | ZN180:PA21 | URBAN | Equipment Failure | 932630 | 37 | 1013.1333 | 37485.9333 | 0.022889 | 0.0022592
2013-02-02 | ZN9118:PA6 | URBAN | Equipment Failure | 932631 | 1 | 257.1667 | 257.1667 | 0.00015703 | 6.106e-05
2013-02-02 | 234:2001 | URBAN | Vegetation | 932637 | 133 | 32.2833 | 4293.6833 | 0.0026217 | 0.008121
2013-02-02 | ZN180:PA18 | URBAN | Equipment Failure | 932641 | 104 | 207 | 21528 | 0.013145 | 0.0063503
2013-02-02 | ZN180:PA31 | URBAN | Equipment Failure | 932641 | 17 | 207 | 3247 | 0.0019826 | 0.001038
2013-02-02 | 242:81539 | URBAN | Other | 932652 | 1 | 329.5667 | 329.5667 | 0.00020123 | 6.106e-05
2013-02-02 | ZN12610:PA13 | URBAN | Equipment Failure | 932653 | 1 | 156.9833 | 156.9833 | 9.5854e-05 | 6.106e-05
2013-02-02 | 208:56 | URBAN | Equipment Failure | 932657 | 344 | 264 | 60926 | 0.037202 | 0.021005
2013-02-02 | 509:48039 | LONG RURAL | Other | 932668 | 1 | 177.5333 | 177.5333 | 0.0001084 | 6.106e-05
2013-02-02 | ZN195:PA28 | URBAN | Vegetation | 932669 | 47 | 313 | 3744.3333 | 0.0022863 | 0.0028698
2013-02-02 | ZN2400:PA18 | SHORT RURAL | Other | 932687 | 398 | 201 | 69746 | 0.042587 | 0.024302
2013-02-02 | ZN9245:PA3 | URBAN | Vegetation | 932692 | 1 | 339.8333 | 339.8333 | 0.0002075 | 6.106e-05
2013-02-03 | ZN9550:PA6 | URBAN | Other | 932696 | 1 | 261.7333 | 261.7333 | 0.00015982 | 6.106e-05
2013-02-03 | ZN10990:PA2 | URBAN | Other | 932702 | 1 | 49.5 | 49.5 | 3.0225e-05 | 6.106e-05
2013-02-03 | ZN10990:PA2 | URBAN | Other | 932706 | 1 | 367.0167 | 367.0167 | 0.0002241 | 6.106e-05
2013-02-03 | ZN9118:PA21 | URBAN | Other | 932708 | 44 | 125.1 | 5504.4 | 0.003361 | 0.0026867
2013-02-03 | 801:74123 | SHORT RURAL | Other | 932709 | 54 | 160.2167 | 8651.7 | 0.0052828 | 0.0032973
2013-02-03 | ZN1788:PA15 | URBAN | Equipment Failure | 932728 | 1 | 1065.3333 | 1065.3333 | 0.0006505 | 6.106e-05
2013-02-03 | ZN9252:PA8 | URBAN | Other | 932737 | 1 | 697.1167 | 697.1167 | 0.00042566 | 6.106e-05
2013-02-03 | ZN36300:PA3 | URBAN | Equipment Failure | 932741 | 1 | 362.15 | 362.15 | 0.00022113 | 6.106e-05
2013-02-03 | 515:35197 | LONG RURAL | Equipment Failure | 932748 | 2 | 69 | 138 | 8.4263e-05 | 0.00012212
2013-02-03 | ZN4545:PA24 | URBAN | Vegetation | 932800 | 1 | 190.15 | 190.15 | 0.00011611 | 6.106e-05
2013-02-03 | 806:74080 | SHORT RURAL | Other | 932805 | 3 | 128.6 | 385.8 | 0.00023557 | 0.00018318
2013-02-03 | ZN187:PA20 | URBAN | Equipment Failure | 932807 | 1 | 363.2333 | 363.2333 | 0.00022179 | 6.106e-05
2013-02-03 | ZN12620:PA11 | SHORT RURAL | Equipment Failure | 932822 | 1 | 214.5167 | 214.5167 | 0.00013098 | 6.106e-05
2013-02-03 | ZN10999:PA10 | URBAN | Vegetation | 932823 | 1 | 333.3333 | 333.3333 | 0.00020353 | 6.106e-05
2013-02-03 | ZN10999:PA10 | URBAN | Vegetation | 932824 | 1 | 336.2833 | 336.2833 | 0.00020534 | 6.106e-05
2013-02-03 | ZN14144:PA1 | URBAN | Third Party Impacts | 932833 | 61 | 62 | 3782 | 0.0023093 | 0.0037247
2013-02-03 | ZN12640:PA13 | SHORT RURAL | Vegetation | 932834 | 1 | 292.7167 | 292.7167 | 0.00017873 | 6.106e-05
2013-02-03 | ZN180:PA18 | URBAN | Other | 932838 | 1 | 78.9833 | 78.9833 | 4.8227e-05 | 6.106e-05
2013-02-03 | 807:74180 | SHORT RURAL | Other | 932839 | 1 | 150 | 150 | 9.159e-05 | 6.106e-05
2013-02-03 | 512:48046 | SHORT RURAL | Other | 932843 | 1 | 294.7833 | 294.7833 | 0.00018 | 6.106e-05
2013-02-03 | ZN1164:PA3 | URBAN | Equipment Failure | 932850 | 1 | 1143.3 | 1143.3 | 0.0006981 | 6.106e-05
2013-02-03 | ZN1164:PA4 | URBAN | Other | 932861 | 1 | 332.1167 | 332.1167 | 0.00020279 | 6.106e-05
2013-02-03 | 524:33580 | SHORT RURAL | Equipment Failure | 932867 | 25 | 215.85 | 5396.25 | 0.003295 | 0.0015265
2013-02-03 | 514:18137 | SHORT RURAL | Other | 932875 | 10 | 35.3667 | 353.6667 | 0.00021595 | 0.0006106
2013-02-03 | 202:34260 | URBAN | Other | 932883 | 1 | 101.95 | 101.95 | 6.2251e-05 | 6.106e-05
2013-02-03 | 238:34144 | URBAN | Equipment Failure | 932886 | 1 | 395.6333 | 395.6333 | 0.00024157 | 6.106e-05
2013-02-03 | ZN1164:PA12 | URBAN | Equipment Failure | 932888 | 812 | 87 | 67544 | 0.041243 | 0.049581
2013-02-03 | ZN1164:PA22 | URBAN | Other | 932889 | 71 | 82 | 5822 | 0.0035549 | 0.0043353
2013-02-03 | ZN10999:PA12 | URBAN | Equipment Failure | 932895 | 31 | 55.2333 | 1712.2333 | 0.0010455 | 0.0018929
2013-02-04 | ZN1164:PA4 | URBAN | Other | 932900 | 1 | 201.4 | 201.4 | 0.00012298 | 6.106e-05
2013-02-04 | ZN12650:PA20 | URBAN | Equipment Failure | 932904 | 106 | 108.65 | 11516.9 | 0.0070323 | 0.0064724
2013-02-04 | 801:74121 | SHORT RURAL | Other | 932911 | 1 | 172.7167 | 172.7167 | 0.00010546 | 6.106e-05
2013-02-04 | 224:80337 | URBAN | Other | 932915 | 1 | 99 | 99 | 6.045e-05 | 6.106e-05
2013-02-04 | ZN3154:PA16 | URBAN | Other | 932932 | 1 | 151 | 151 | 9.2201e-05 | 6.106e-05
2013-02-04 | 810:74054 | LONG RURAL | Equipment Failure | 932936 | 1 | 368 | 368 | 0.0002247 | 6.106e-05
2013-01-30 | ZN1285:PA18 | URBAN | Equipment Failure | 932943 | 6 | 60 | 360 | 0.00021981 | 0.00036635
2013-02-01 | ZN9252:PA2 | URBAN | Other | 932948 | 1707 | 4 | 6828 | 0.0041692 | 0.10423
2013-02-04 | 511:29878 | SHORT RURAL | Other | 932986 | 1 | 74.4667 | 74.4667 | 4.547e-05 | 6.106e-05
2013-02-01 | ZN2568:PA40 | URBAN | Vegetation | 933015 | 1 | 1262 | 1262 | 0.00077058 | 6.106e-05
2013-02-03 | ZN15010:PA1 | URBAN | Equipment Failure | 933043 | 89 | 467 | 41563 | 0.025378 | 0.0054344
2013-02-04 | ZN9037:PA8 | URBAN | Equipment Failure | 933049 | 1 | 473.95 | 473.95 | 0.0002894 | 6.106e-05
2013-02-04 | ZN15010:PA1 | URBAN | Equipment Failure | 933054 | 89 | 305 | 27145 | 0.016575 | 0.0054344
2013-02-04 | ZN15010:PA9 | SHORT RURAL | Equipment Failure | 933054 | 1 | 305 | 305 | 0.00018623 | 6.106e-05
2013-02-04 | 524:33572 | SHORT RURAL | Equipment Failure | 933085 | 1 | 472 | 472 | 0.0002882 | 6.106e-05
2013-02-04 | ZN2835:PA9 | URBAN | Third Party Impacts | 933097 | 1 | 380.8667 | 380.8667 | 0.00023256 | 6.106e-05
2013-02-04 | ZN10993:PA12 | URBAN | Third Party Impacts | 933124 | 1 | 98.15 | 98.15 | 5.9931e-05 | 6.106e-05
2013-02-04 | ZN1164:PA20 | URBAN | Equipment Failure | 933126 | 1 | 376 | 195.3167 | 0.00011926 | 6.106e-05
2013-02-04 | ZN1164:PA3 | URBAN | Equipment Failure | 933126 | 20 | 376 | 6980 | 0.004262 | 0.0012212
2013-02-04 | ZN12570:PA25 | SHORT RURAL | Other | 933137 | 1 | 40.1667 | 40.1667 | 2.4526e-05 | 6.106e-05
2013-02-04 | 501:48115 | SHORT RURAL | Other | 933160 | 1 | 591.65 | 591.65 | 0.00036126 | 6.106e-05
2013-02-04 | 214:8667 | URBAN | Equipment Failure | 933177 | 2 | 45 | 90 | 5.4954e-05 | 0.00012212
2013-02-04 | 228:7487 | URBAN | Vegetation | 933265 | 1 | 143.0167 | 143.0167 | 8.7326e-05 | 6.106e-05
2013-02-04 | ZN340:PA21 | URBAN | Equipment Failure | 933275 | 1 | 253.1833 | 253.1833 | 0.00015459 | 6.106e-05
2013-02-04 | 238:34137 | URBAN | Other | 933294 | 1 | 147.75 | 147.75 | 9.0217e-05 | 6.106e-05
2013-02-04 | ZN12570:PA33 | SHORT RURAL | Equipment Failure | 933330 | 1 | 183.9833 | 183.9833 | 0.00011234 | 6.106e-05
2013-02-04 | 227:13015 | SHORT RURAL | Other | 933370 | 1 | 130.8167 | 130.8167 | 7.9877e-05 | 6.106e-05
2013-02-04 | ZN10996:PA10 | URBAN | Third Party Impacts | 933391 | 881 | 875 | 88070 | 0.053776 | 0.053794
2013-02-04 | ZN10996:PA8 | URBAN | Third Party Impacts | 933391 | 1 | 875 | 100 | 6.106e-05 | 6.106e-05
2013-02-04 | ZN2473:PA15 | URBAN | Other | 933395 | 1 | 146.9667 | 146.9667 | 8.9738e-05 | 6.106e-05
2013-02-04 | ZN14143:PA17 | SHORT RURAL | Third Party Impacts | 933398 | 750 | 91 | 59148 | 0.036116 | 0.045795
2013-02-05 | 232:11454 | SHORT RURAL | Other | 933417 | 1 | 989.9667 | 989.9667 | 0.00060449 | 6.1062e-05
2013-02-05 | ZN9118:PA20 | URBAN | Equipment Failure | 933418 | 1 | 206.2 | 206.2 | 0.00012591 | 6.1062e-05
2013-02-05 | ZN15009:PA5 | URBAN | Other | 933441 | 1 | 179.15 | 179.15 | 0.00010939 | 6.1062e-05
2013-02-05 | ZN15004:PA9 | URBAN | Animals | 933446 | 1 | 232.4667 | 232.4667 | 0.00014195 | 6.1062e-05
2013-02-02 | ZN180:PA21 | URBAN | Equipment Failure | 933496 | 42 | 999 | 41958 | 0.02562 | 0.0025645
2013-02-05 | ZN1788:PA17 | URBAN | Equipment Failure | 933553 | 1 | 191.3167 | 191.3167 | 0.00011682 | 6.1062e-05
2013-01-13 | 526:34635 | SHORT RURAL | Other | 933604 | 1 | 249 | 249 | 0.00015132 | 6.0773e-05
2013-02-05 | ZN3154:PA18 | URBAN | Equipment Failure | 933673 | 30 | 68.0333 | 2041 | 0.0012463 | 0.0018319
2013-02-05 | ZN9550:PA42 | URBAN | Third Party Impacts | 933676 | 39 | 530 | 20670 | 0.012622 | 0.0023814
2013-02-05 | ZN9118:PA11 | URBAN | Equipment Failure | 933689 | 1 | 214.1167 | 214.1167 | 0.00013074 | 6.1062e-05
2013-02-05 | 503:48012 | URBAN | Third Party Impacts | 933695 | 1 | 78.35 | 78.35 | 4.7842e-05 | 6.1062e-05
2013-02-05 | ZN195:PA4 | URBAN | Vegetation | 933734 | 17 | 77.3833 | 1315.5167 | 0.00080328 | 0.0010381
2013-02-05 | 232:33413 | SHORT RURAL | Other | 933765 | 1 | 173.4 | 173.4 | 0.00010588 | 6.1062e-05
2013-02-05 | 509:48040 | SHORT RURAL | Equipment Failure | 933768 | 100 | 302 | 19028 | 0.011619 | 0.0061062
2013-02-05 | ZN3154:PA18 | URBAN | Equipment Failure | 933775 | 30 | 800 | 24000 | 0.014655 | 0.0018319
2013-02-05 | 513:48059 | SHORT RURAL | Equipment Failure | 933828 | 3 | 152 | 456 | 0.00027844 | 0.00018319
2013-02-05 | ZN180:PA41 | URBAN | Other | 933836 | 1 | 334.05 | 334.05 | 0.00020398 | 6.1062e-05
2013-02-05 | ZN180:PA7 | URBAN | Equipment Failure | 933837 | 92 | 1449.6 | 133363.2 | 0.081434 | 0.0056177
2013-02-05 | ZN35800:PA16 | URBAN | Equipment Failure | 933838 | 323 | 603 | 48526 | 0.029631 | 0.019723
2013-02-06 | ZN12610:PA9 | SHORT RURAL | Animals | 933845 | 1153 | 54 | 62262 | 0.038019 | 0.070405
2013-02-06 | ZN35800:PA7 | URBAN | Equipment Failure | 933846 | 1 | 26.7333 | 26.7333 | 1.6324e-05 | 6.1063e-05
2013-02-06 | ZN15010:PA1 | URBAN | Other | 933855 | 1 | 303.35 | 303.35 | 0.00018523 | 6.1063e-05
2013-02-06 | ZN15009:PA1 | URBAN | Equipment Failure | 933862 | 85 | 240.4167 | 20435.4167 | 0.012478 | 0.0051903
2013-02-06 | 526:34640 | SHORT RURAL | Other | 933876 | 2 | 184 | 368 | 0.00022471 | 0.00012213
2013-01-12 | 514:18146 | SHORT RURAL | Equipment Failure | 933955 | 5 | 3092 | 6535 | 0.0039715 | 0.00030386
2013-02-06 | 256:80646 | URBAN | Vegetation | 934029 | 1 | 1223.8 | 1223.8 | 0.00074729 | 6.1063e-05
2013-02-06 | ZN10994:PA4 | URBAN | Other | 934060 | 48 | 90.7 | 4353.6 | 0.0026584 | 0.002931
2013-02-06 | ZN269:PA26 | URBAN | Equipment Failure | 934081 | 50 | 164.75 | 8237.5 | 0.00503 | 0.0030531
2013-02-06 | ZN12610:PA25 | SHORT RURAL | Equipment Failure | 934105 | 102 | 263 | 26826 | 0.016381 | 0.0062284
2013-02-06 | ZN180:PA23 | URBAN | Equipment Failure | 934129 | 74 | 230 | 17020 | 0.010393 | 0.0045186
2013-02-06 | ZN15005:PA10 | URBAN | Equipment Failure | 934140 | 769 | 141 | 45653 | 0.027877 | 0.046957
2013-02-06 | ZN15005:PA12 | URBAN | Equipment Failure | 934140 | 1 | 141 | 53 | 3.2363e-05 | 6.1063e-05
2013-02-06 | ZN15005:PA12 | URBAN | Equipment Failure | 934143 | 1 | 75.55 | 75.55 | 4.6133e-05 | 6.1063e-05
2013-02-06 | ZN340:PA27 | URBAN | Third Party Impacts | 934150 | 9 | 76 | 684 | 0.00041767 | 0.00054957
2013-02-06 | ZN1193:PA27 | URBAN | Vegetation | 934156 | 2 | 70 | 140 | 8.5488e-05 | 0.00012213
2013-02-06 | ZN1193:PA9 | URBAN | Vegetation | 934156 | 28 | 70 | 1960 | 0.0011968 | 0.0017098
2013-02-06 | ZN80:PA31 | URBAN | Equipment Failure | 934167 | 1 | 650.7667 | 650.7667 | 0.00039738 | 6.1063e-05
2013-02-06 | ZN15010:PA1 | URBAN | Vegetation | 934188 | 1 | 375.35 | 375.35 | 0.0002292 | 6.1063e-05
2013-02-06 | ZN2568:PA30 | URBAN | Other | 934196 | 1 | 398.5333 | 398.5333 | 0.00024336 | 6.1063e-05
2013-02-06 | ZN3425:PA12 | URBAN | Equipment Failure | 934203 | 34 | 45 | 1530 | 0.00093426 | 0.0020761
2013-02-06 | ZN1673:PA11 | URBAN | Vegetation | 934222 | 1 | 175.0333 | 175.0333 | 0.00010688 | 6.1063e-05
2013-02-06 | ZN3155:PA44 | URBAN | Equipment Failure | 934223 | 61 | 1486.8667 | 90698.8667 | 0.055383 | 0.0037248
2013-02-06 | 516:48067 | SHORT RURAL | Equipment Failure | 934231 | 1 | 175 | 175 | 0.00010686 | 6.1063e-05
2013-02-06 | ZN1193:PA6 | URBAN | Equipment Failure | 934244 | 256 | 65 | 16640 | 0.010161 | 0.015632
2013-02-06 | 507:80925 | SHORT RURAL | Other | 934248 | 18 | 68 | 1224 | 0.00074741 | 0.0010991
2013-02-06 | ZN180:PA7 | URBAN | Equipment Failure | 934255 | 109 | 15 | 1635 | 0.00099838 | 0.0066558
2013-02-07 | ZN1193:PA26 | URBAN | Other | 934262 | 1303 | 52.85 | 68863.55 | 0.042051 | 0.079566
2013-02-07 | ZN10994:PA11 | URBAN | Vegetation | 934264 | 1 | 292.6833 | 292.6833 | 0.00017872 | 6.1064e-05
2013-02-07 | ZN12570:PA29 | SHORT RURAL | Vegetation | 934266 | 58 | 80.6667 | 4678.6667 | 0.002857 | 0.0035417
2013-02-06 | ZN9118:PA3 | SHORT RURAL | Other | 934329 | 30 | 42 | 1260 | 0.00076939 | 0.0018319
2013-02-07 | ZN2602:PA21 | URBAN | Other | 934403 | 40 | 287 | 11480 | 0.0070101 | 0.0024425
2013-02-07 | 509:48039 | LONG RURAL | Other | 934444 | 2 | 106 | 212 | 0.00012946 | 0.00012213
2013-02-07 | ZN340:PA27 | URBAN | Third Party Impacts | 934483 | 1 | 314.5833 | 314.5833 | 0.0001921 | 6.1064e-05
2013-02-07 | 260:33353 | URBAN | Equipment Failure | 934549 | 150 | 61.2 | 8861.6 | 0.0054112 | 0.0091596
2013-02-07 | ZN3472:PA12 | URBAN | Equipment Failure | 934576 | 1 | 195.3833 | 195.3833 | 0.00011931 | 6.1064e-05
2013-02-07 | ZN12610:PA2 | URBAN | Equipment Failure | 934584 | 1 | 446.4 | 446.4 | 0.00027259 | 6.1064e-05
2013-02-07 | 807:74179 | SHORT RURAL | Other | 934595 | 1 | 39 | 39 | 2.3815e-05 | 6.1064e-05
2013-02-07 | 813:89061 | LONG RURAL | Other | 934601 | 26 | 126.4667 | 3288.1333 | 0.0020079 | 0.0015877
2013-02-07 | 806:74080 | SHORT RURAL | Other | 934631 | 6 | 855 | 5130 | 0.0031326 | 0.00036638
2013-02-07 | 806:74080 | SHORT RURAL | Other | 934639 | 6 | 855 | 5130 | 0.0031326 | 0.00036638
2013-02-07 | ZN3425:PA35 | URBAN | Vegetation | 934640 | 84 | 250 | 21000 | 0.012823 | 0.0051294
2013-02-07 | ZN342:PA24 | URBAN | Equipment Failure | 934644 | 1 | 831.35 | 831.35 | 0.00050765 | 6.1064e-05
2013-02-07 | ZN180:PA21 | URBAN | Equipment Failure | 934650 | 2 | 25.0333 | 50.0667 | 3.0573e-05 | 0.00012213
2013-02-07 | ZN12640:PA6 | URBAN | Vegetation | 934657 | 1 | 15.8 | 15.8 | 9.6481e-06 | 6.1064e-05
2013-02-07 | 507:80925 | SHORT RURAL | Other | 934664 | 18 | 125.2833 | 2255.1 | 0.001377 | 0.0010991
2013-02-08 | 261:81864 | URBAN | Other | 934668 | 1 | 152.7667 | 152.7667 | 9.3286e-05 | 6.1064e-05
2013-02-08 | ZN15001:PA18 | URBAN | Other | 934732 | 1 | 213.1 | 213.1 | 0.00013013 | 6.1064e-05
2013-02-08 | ZN3922:PA5 | URBAN | Other | 934741 | 95 | 94.1167 | 8941.0833 | 0.0054598 | 0.0058011
2013-02-08 | ZN2466:PA16 | URBAN | Weather | 934745 | 63 | 127.75 | 8048.25 | 0.0049146 | 0.0038471
2013-02-08 | ZN15004:PA5 | URBAN | Other | 934749 | 54 | 255 | 13770 | 0.0084086 | 0.0032975
2013-02-08 | 227:13020 | SHORT RURAL | Other | 934754 | 1 | 285.55 | 285.55 | 0.00017437 | 6.1064e-05
2013-02-08 | 225:13444 | URBAN | Other | 934765 | 1 | 92.8667 | 92.8667 | 5.6708e-05 | 6.1064e-05
2013-02-08 | 232:11457 | URBAN | Equipment Failure | 934772 | 43 | 96 | 4128 | 0.0025207 | 0.0026258
2013-02-08 | ZN14891:PA20 | SHORT RURAL | Other | 934782 | 1 | 91.9333 | 91.9333 | 5.6138e-05 | 6.1064e-05
2013-02-08 | 510:48164 | SHORT RURAL | Animals | 934793 | 1 | 91.9167 | 91.9167 | 5.6128e-05 | 6.1064e-05
2013-02-08 | 507:80925 | SHORT RURAL | Other | 934802 | 69 | 59.3833 | 4097.45 | 0.0025021 | 0.0042134
2013-02-08 | 260:33344 | URBAN | Other | 934847 | 1 | 116.1 | 116.1 | 7.0896e-05 | 6.1064e-05
2013-02-08 | ZN3425:PA22 | URBAN | Vegetation | 934864 | 1 | 559.5 | 559.5 | 0.00034165 | 6.1064e-05
2013-02-08 | 223:14394 | URBAN | Equipment Failure | 934873 | 191 | 131.9 | 22535.0333 | 0.013761 | 0.011663
2013-02-08 | ZN15006:PA13 | URBAN | Other | 934908 | 1 | 100.3833 | 100.3833 | 6.1298e-05 | 6.1064e-05
2013-02-08 | ZN342:PA24 | URBAN | Other | 934911 | 1 | 210.95 | 210.95 | 0.00012882 | 6.1064e-05
2013-02-08 | 507:80925 | SHORT RURAL | Equipment Failure | 934917 | 23 | 1555 | 5945 | 0.0036303 | 0.0014045
2013-02-08 | 511:29878 | SHORT RURAL | Equipment Failure | 934927 | 1 | 208.4667 | 208.4667 | 0.0001273 | 6.1064e-05
2013-02-08 | ZN4545:PA4 | URBAN | Other | 934928 | 44 | 52.7167 | 2319.5333 | 0.0014164 | 0.0026868
2013-02-08 | ZN1285:PA27 | URBAN | Equipment Failure | 934940 | 96 | 957 | 91872 | 0.056101 | 0.0058622
2013-02-08 | 214:8665 | URBAN | Other | 934942 | 1 | 43.4833 | 43.4833 | 2.6553e-05 | 6.1064e-05
2013-02-08 | 812:19066 | SHORT RURAL | Other | 934944 | 1706 | 110.4667 | 188456.1333 | 0.11508 | 0.10418
2013-02-08 | ZN10994:PA2 | URBAN | Equipment Failure | 934955 | 1 | 177.6 | 177.6 | 0.00010845 | 6.1064e-05
2013-02-08 | ZN262:PA19 | URBAN | Vegetation | 934963 | 148 | 149 | 22052 | 0.013466 | 0.0090375
2013-02-08 | 242:81541 | URBAN | Other | 934978 | 1 | 195.2333 | 195.2333 | 0.00011922 | 6.1064e-05
2013-02-09 | 224:80341 | URBAN | Other | 934985 | 1 | 100.5333 | 100.5333 | 6.139e-05 | 6.1064e-05
2013-02-09 | 264:81240 | SHORT RURAL | Other | 934987 | 1 | 80.7333 | 80.7333 | 4.9299e-05 | 6.1064e-05
2013-02-09 | 520:48172 | SHORT RURAL | Equipment Failure | 934988 | 1 | 154.1833 | 154.1833 | 9.4151e-05 | 6.1064e-05
2013-02-09 | ZN3155:PA23 | URBAN | Third Party Impacts | 934989 | 1 | 120.6167 | 120.6167 | 7.3654e-05 | 6.1064e-05
2013-02-09 | ZN15005:PA12 | URBAN | Vegetation | 934991 | 25 | 51 | 1275 | 0.00077857 | 0.0015266
2013-02-09 | ZN180:PA23 | URBAN | Other | 935010 | 74 | 68 | 5032 | 0.0030728 | 0.0045188
2013-02-09 | ZN269:PA16 | URBAN | Operational Error | 935019 | 133 | 110 | 14630 | 0.0089337 | 0.0081216
2013-02-09 | 513:48059 | SHORT RURAL | Other | 935022 | 1 | 38.3167 | 38.3167 | 2.3398e-05 | 6.1064e-05
2013-02-09 | ZN1290:PA4 | URBAN | Third Party Impacts | 935024 | 1 | 116.7333 | 116.7333 | 7.1282e-05 | 6.1064e-05
2013-02-09 | ZN35800:PA6 | URBAN | Equipment Failure | 935027 | 17 | 216 | 3672 | 0.0022423 | 0.0010381
2013-02-09 | 234:2001 | URBAN | Other | 935029 | 1 | 120.4 | 120.4 | 7.3521e-05 | 6.1064e-05
2013-02-09 | ZN1285:PA29 | URBAN | Equipment Failure | 935030 | 28 | 60 | 1680 | 0.0010259 | 0.0017098
2013-02-09 | ZN9118:PA21 | URBAN | Vegetation | 935070 | 26 | 178 | 4628 | 0.0028261 | 0.0015877
2013-02-09 | ZN12650:PA12 | URBAN | Equipment Failure | 935076 | 1235 | 53 | 65455 | 0.03997 | 0.075414
2013-02-09 | ZN2568:PA32 | URBAN | Other | 935112 | 1 | 187.65 | 187.65 | 0.00011459 | 6.1064e-05
2013-02-09 | 807:74180 | SHORT RURAL | Other | 935113 | 1 | 75 | 75 | 4.5798e-05 | 6.1064e-05
2013-02-09 | 242:81539 | URBAN | Other | 935116 | 1 | 157.1667 | 157.1667 | 9.5973e-05 | 6.1064e-05
2013-02-09 | 504:48026 | SHORT RURAL | Third Party Impacts | 935120 | 1260 | 146 | 102600 | 0.062652 | 0.076941
2013-02-10 | ZN35500:PA32 | URBAN | Animals | 935140 | 8 | 165 | 1320 | 0.00080605 | 0.00048851
2013-02-10 | 225:13444 | URBAN | Other | 935152 | 1 | 68.8 | 68.8 | 4.2012e-05 | 6.1064e-05
2013-02-10 | ZN15009:PA5 | URBAN | Equipment Failure | 935153 | 1 | 466.1167 | 466.1167 | 0.00028463 | 6.1064e-05
2013-02-10 | 501:48123 | SHORT RURAL | Equipment Failure | 935156 | 8 | 318 | 2544 | 0.0015535 | 0.00048851
2013-02-10 | 507:80931 | URBAN | Other | 935181 | 1 | 17.7333 | 17.7333 | 1.0829e-05 | 6.1064e-05
2013-02-10 | ZN2568:PA29 | URBAN | Equipment Failure | 935195 | 42 | 165.8333 | 6965 | 0.0042531 | 0.0025647
2013-02-10 | 526:34636 | SHORT RURAL | Other | 935198 | 1 | 75 | 75 | 4.5798e-05 | 6.1064e-05
2013-02-10 | ZN195:PA30 | URBAN | Equipment Failure | 935204 | 23 | 103 | 2369 | 0.0014466 | 0.0014045
2013-02-10 | ZN12600:PA9 | SHORT RURAL | Equipment Failure | 935212 | 40 | 42 | 1680 | 0.0010259 | 0.0024426
2013-02-10 | 202:34238 43 48 | URBAN | Other | 935217 | 1 | 143.8833 | 143.8833 | 8.7861e-05 | 6.1064e-05
2013-02-10 | ZN12640:PA10 | URBAN | Third Party Impacts | 935236 | 1 | 415.7333 | 415.7333 | 0.00025386 | 6.1064e-05
2013-02-10 | ZN9550:PA42 | URBAN | Other | 935239 | 1 | 327.7833 | 327.7833 | 0.00020016 | 6.1064e-05
2013-02-10 | 220:8687 | URBAN | Equipment Failure | 935240 | 26 | 79 | 2054 | 0.0012543 | 0.0015877
2013-02-10 | 258:80787 | URBAN | Vegetation | 935241 | 3 | 137 | 411 | 0.00025097 | 0.00018319
2013-02-10 | 515:35197 | LONG RURAL | Other | 935245 | 1 | 89.3167 | 89.3167 | 5.4541e-05 | 6.1064e-05
2013-02-10 | ZN9700:PA11 | URBAN | Other | 935249 | 1 | 305.4833 | 305.4833 | 0.00018654 | 6.1064e-05
2013-02-10 | ZN1287:PA15 | URBAN | Other | 935252 | 1 | 207.0833 | 207.0833 | 0.00012645 | 6.1064e-05
2013-02-10 | ZN340:PA3 | URBAN | Other | 935254 | 1 | 336.9 | 336.9 | 0.00020573 | 6.1064e-05
2013-02-10 | ZN9700:PA11 | URBAN | Other | 935255 | 1 | 275.4 | 275.4 | 0.00016817 | 6.1064e-05
2013-02-10 | ZN630:PA14 | SHORT RURAL | Other | 935257 | 1 | 329.35 | 329.35 | 0.00020112 | 6.1064e-05
2013-02-10 | 807:74184 | SHORT RURAL | Other | 935261 | 1 | 103.7333 | 103.7333 | 6.3344e-05 | 6.1064e-05
2013-02-10 | 516:48067 | SHORT RURAL | Other | 935263 | 3 | 92 | 276 | 0.00016854 | 0.00018319
2013-02-10 | 812:19072 | SHORT RURAL | Other | 935268 | 7 | 43 | 301 | 0.0001838 | 0.00042745
2013-02-10 | ZN342:PA28 | URBAN | Vegetation | 935275 | 1 | 235.0667 | 235.0667 | 0.00014354 | 6.1064e-05
2013-02-10 | ZN187:PA20 | URBAN | Equipment Failure | 935283 | 87 | 128.7833 | 11204.15 | 0.0068417 | 0.0053126
2013-02-10 | 812:19071 | SHORT RURAL | Other | 935286 | 1 | 61.45 | 61.45 | 3.7524e-05 | 6.1064e-05
2013-02-10 | 523:33501 | SHORT RURAL | Other | 935290 | 12 | 46.5333 | 558.4 | 0.00034098 | 0.00073277
2013-02-10 | ZN15006:PA1 | URBAN | Other | 935291 | 1 | 226.0667 | 226.0667 | 0.00013805 | 6.1064e-05
2013-02-10 | 813:89061 | LONG RURAL | Other | 935308 | 4 | 69.7333 | 245.7 | 0.00015003 | 0.00024426
2013-02-10 | 220:8687 | URBAN | Equipment Failure | 935314 | 26 | 30 | 780 | 0.0004763 | 0.0015877
2013-02-10 | 509:48040 | SHORT RURAL | Other | 935318 | 1 | 82 | 82 | 5.0073e-05 | 6.1064e-05
2013-02-10 | 810:74050 | SHORT RURAL | Other | 935319 | 1 | 72.85 | 72.85 | 4.4485e-05 | 6.1064e-05
2013-02-10 | ZN1788:PA6 | URBAN | Other | 935320 | 1 | 282.8667 | 282.8667 | 0.00017273 | 6.1064e-05
2013-02-10 | 509:48039 | LONG RURAL | Other | 935321 | 2 | 267 | 534 | 0.00032608 | 0.00012213
2013-02-10 | 516:48067 | SHORT RURAL | Other | 935325 | 44 | 97 | 4268 | 0.0026062 | 0.0026868
2013-02-10 | 515:35197 | LONG RURAL | Other | 935334 | 2 | 162 | 324 | 0.00019785 | 0.00012213
2013-02-10 | 512:48046 | SHORT RURAL | Other | 935336 | 5 | 328.3667 | 1641.8333 | 0.0010026 | 0.00030532
2013-02-10 | 526:34636 | SHORT RURAL | Other | 935337 | 4 | 168 | 672 | 0.00041035 | 0.00024426
2013-02-10 | 807:74184 | SHORT RURAL | Equipment Failure | 935338 | 2 | 123 | 246 | 0.00015022 | 0.00012213
2013-02-10 | 524:33572 | SHORT RURAL | Other | 935339 | 144 | 245 | 35280 | 0.021543 | 0.0087933
2013-02-10 | 504:48026 | SHORT RURAL | Equipment Failure | 935340 | 4 | 364.9167 | 1459.6667 | 0.00089134 | 0.00024426
2013-02-10 | 509:48039 | LONG RURAL | Other | 935341 | 1 | 302.0667 | 302.0667 | 0.00018445 | 6.1064e-05
2013-02-10 | 504:48033 | SHORT RURAL | Other | 935342 | 26 | 167.0833 | 4344.1667 | 0.0026527 | 0.0015877
2013-02-10 | 520:48172 | SHORT RURAL | Other | 935343 | 3 | 295 | 885 | 0.00054042 | 0.00018319
2013-02-10 | 513:48059 | SHORT RURAL | Other | 935344 | 1 | 184 | 184 | 0.00011236 | 6.1064e-05
2013-02-10 | 512:48046 | SHORT RURAL | Other | 935348 | 2 | 209 | 418 | 0.00025525 | 0.00012213
2013-02-10 | ZN12610:PA13 | URBAN | Other | 935352 | 1 | 211.7167 | 211.7167 | 0.00012928 | 6.1064e-05
2013-02-10 | 520:48172 | SHORT RURAL | Other | 935355 | 1 | 224.4333 | 224.4333 | 0.00013705 | 6.1064e-05
2013-02-10 | 512:48046 | SHORT RURAL | Other | 935358 | 11 | 207 | 2277 | 0.0013904 | 0.00067171
2013-02-10 | 523:33501 | SHORT RURAL | Other | 935360 | 24 | 306 | 7344 | 0.0044846 | 0.0014655
2013-02-10 | 260:33344 | URBAN | Equipment Failure | 935367 | 48 | 47.3833 | 2263.5 | 0.0013822 | 0.0029311
2013-02-10 | 261:81865 | URBAN | Other | 935371 | 1 | 92.1 | 92.1 | 5.624e-05 | 6.1064e-05
2013-02-10 | 261:81864 | URBAN | Equipment Failure | 935372 | 1 | 1045.8667 | 1045.8667 | 0.00063865 | 6.1064e-05
2013-02-10 | 224:80346 | URBAN | Other | 935373 | 1 | 187.4167 | 187.4167 | 0.00011444 | 6.1064e-05
2013-02-10 | 224:80346 | URBAN | Other | 935375 | 1 | 182.7333 | 182.7333 | 0.00011158 | 6.1064e-05
2013-02-10 | 258:80784 | URBAN | Other | 935376 | 1 | 185.2 | 185.2 | 0.00011309 | 6.1064e-05
2013-02-10 | 501:48115 | SHORT RURAL | Animals | 935378 | 43 | 309 | 13287 | 0.0081136 | 0.0026258
2013-02-10 | 515:35197 | LONG RURAL | Equipment Failure | 935380 | 1 | 158 | 158 | 9.6482e-05 | 6.1064e-05
2013-02-10 | 509:48039 | LONG RURAL | Vegetation | 935382 | 55 | 915.0333 | 39196.8333 | 0.023935 | 0.0033585
2013-02-11 | 813:89055 | SHORT RURAL | Other | 935388 | 8 | 75 | 600 | 0.00036639 | 0.00048851
2013-02-11 | ZN188:PA2 | URBAN | Other | 935389 | 1 | 541.6667 | 541.6667 | 0.00033076 | 6.1064e-05
2013-02-11 | 813:89061 | LONG RURAL | Other | 935393 | 1 | 123.9333 | 123.9333 | 7.5679e-05 | 6.1064e-05
2013-02-11 | 515:35197 | LONG RURAL | Other | 935394 | 8 | 272.7167 | 2181.7333 | 0.0013323 | 0.00048851
2013-02-11 | 524:33572 | SHORT RURAL | Equipment Failure | 935403 | 20 | 399 | 3136 | 0.001915 | 0.0012213
2013-02-11 | ZN80:PA32 | URBAN | Vegetation | 935405 | 1 | 247.4333 | 247.4333 | 0.00015109 | 6.1064e-05
2013-02-11 | 813:89061 | LONG RURAL | Other | 935407 | 10 | 225 | 2250 | 0.0013739 | 0.00061064
2013-02-11 | 504:48031 | SHORT RURAL | Other | 935409 | 63 | 227.2333 | 14315.7 | 0.0087418 | 0.0038471
2013-02-11 | ZN9550:PA43 | URBAN | Other | 935410 | 1 | 142.9 | 142.9 | 8.7261e-05 | 6.1064e-05
2013-02-11 | 526:34636 | SHORT RURAL | Equipment Failure | 935420 | 2 | 887 | 1774 | 0.0010833 | 0.00012213
2013-02-11 | 813:89055 | SHORT RURAL | Other | 935421 | 4 | 140 | 560 | 0.00034196 | 0.00024426
2013-02-11 | 512:48046 | SHORT RURAL | Other | 935423 | 7 | 398.9333 | 2792.5333 | 0.0017052 | 0.00042745
2013-02-11 | ZN1193:PA6 | URBAN | Vegetation | 935426 | 1 | 302.3667 | 302.3667 | 0.00018464 | 6.1064e-05
2013-02-11 | 515:35197 | LONG RURAL | Other | 935439 | 4 | 124 | 496 | 0.00030288 | 0.00024426
2013-02-11 | 242:81539 | URBAN | Equipment Failure | 935449 | 1 | 512.2167 | 512.2167 | 0.00031278 | 6.1064e-05
2013-02-11 | 504:48026 | SHORT RURAL | Other | 935450 | 3 | 392.7333 | 1178.2 | 0.00071946 | 0.00018319
2013-02-11 | 807:74184 | SHORT RURAL | Weather | 935452 | 1 | 222.8 | 222.8 | 0.00013605 | 6.1064e-05
2013-02-11 | 502:48010 | SHORT RURAL | Equipment Failure | 935456 | 9 | 425 | 3825 | 0.0023357 | 0.00054958
2013-02-10 | 807:74184 | SHORT RURAL | Other | 935457 | 3 | 840 | 2520 | 0.0015388 | 0.00018319
2013-02-11 | 814:82283 | SHORT RURAL | Other | 935464 | 1 | 300 | 300 | 0.00018319 | 6.1064e-05
2013-02-11 | ZN3472:PA18 | URBAN | Other | 935466 | 1 | 35.7833 | 35.7833 | 2.1851e-05 | 6.1064e-05
2013-02-11 | 801:74121 | SHORT RURAL | Other | 935481 | 1 | 250.1333 | 250.1333 | 0.00015274 | 6.1064e-05
2013-02-11 | 205:12213 | URBAN | Vegetation | 935545 | 1 | 79.7 | 79.7 | 4.8668e-05 | 6.1064e-05
2013-02-11 | 223:14394 | URBAN | Other | 935584 | 1 | 102.45 | 102.45 | 6.256e-05 | 6.1064e-05
2013-02-11 | ZN901:PA17 | URBAN | Third Party Impacts | 935607 | 1 | 156.6833 | 156.6833 | 9.5678e-05 | 6.1064e-05
2013-02-11 | 511:29878 | SHORT RURAL | Other | 935622 | 1 | 260 | 260 | 0.00015877 | 6.1064e-05
2013-02-11 | 511:29878 | SHORT RURAL | Other | 935624 | 5 | 120 | 600 | 0.00036639 | 0.00030532
2013-02-10 | 509:48040 | SHORT RURAL | Other | 935636 | 21 | 157 | 3297 | 0.0020133 | 0.0012824
2013-02-11 | 504:48026 | SHORT RURAL | Weather | 935649 | 1 | 166.1667 | 166.1667 | 0.00010147 | 6.1064e-05
2013-02-11 | 509:48040 | SHORT RURAL | Equipment Failure | 935660 | 6 | 389.3167 | 2335.9 | 0.0014264 | 0.00036639
2013-02-11 | ZN1788:PA30 | URBAN | Third Party Impacts | 935677 | 1 | 247.0667 | 247.0667 | 0.00015087 | 6.1064e-05
2013-02-11 | ZN9245:PA14 | URBAN | Vegetation | 935681 | 1 | 169.6667 | 169.6667 | 0.00010361 | 6.1064e-05
2013-02-11 | 511:29878 | SHORT RURAL | Equipment Failure | 935700 | 3 | 1579.0833 | 4737.25 | 0.0028928 | 0.00018319
2013-02-11 | ZN2602:PA36 | URBAN | Other | 935731 | 1 | 1191.6333 | 1191.6333 | 0.00072766 | 6.1064e-05
2013-02-11 | 235:2120 | SHORT RURAL | Other | 935777 | 1 | 60 | 60 | 3.6639e-05 | 6.1064e-05
2013-02-11 | 512:48046 | SHORT RURAL | Other | 935794 | 2 | 115 | 230 | 0.00014045 | 0.00012213
2013-02-11 | 223:14397 | URBAN | Other | 935813 | 1 | 90.7 | 90.7 | 5.5385e-05 | 6.1064e-05
2013-02-10 | 814:82283 | SHORT RURAL | Other | 935838 | 23 | 110 | 2530 | 0.0015449 | 0.0014045
2013-02-10 | 516:48067 | SHORT RURAL | Other | 935842 | 1 | 60 | 60 | 3.6639e-05 | 6.1064e-05
2013-02-10 | 812:19072 | SHORT RURAL | Other | 935854 | 2 | 101 | 202 | 0.00012335 | 0.00012213
2013-02-11 | 509:48039 | LONG RURAL | Other | 935861 | 1 | 251 | 251 | 0.00015327 | 6.1064e-05
2013-02-11 | 515:35197 | LONG RURAL | Animals | 935866 | 2 | 70 | 140 | 8.549e-05 | 0.00012213
2013-02-11 | 502:48010 | SHORT RURAL | Other | 935891 | 9 | 90 | 810 | 0.00049462 | 0.00054958
2013-02-11 | 813:89062 | SHORT RURAL | Other | 935899 | 2 | 305 | 610 | 0.00037249 | 0.00012213
2013-02-11 | ZN12690:PA8 | URBAN | Other | 935905 | 1 | 274.0667 | 274.0667 | 0.00016736 | 6.1064e-05
2013-02-11 | 813:89061 | LONG RURAL | Other | 935919 | 1 | 906 | 906 | 0.00055324 | 6.1064e-05
2013-02-11 | ZN1164:PA28 | URBAN | Equipment Failure | 935926 | 1 | 1123.35 | 1123.35 | 0.00068597 | 6.1064e-05
2013-02-11 | 504:48026 | SHORT RURAL | Other | 935934 | 1 | 96.0833 | 96.0833 | 5.8673e-05 | 6.1064e-05
2013-02-11 | ZN12610:PA2 | URBAN | Vegetation | 935936 | 1 | 145.4333 | 145.4333 | 8.8808e-05 | 6.1064e-05
2013-02-11 | ZN12610:PA25 | SHORT RURAL | Other | 935941 | 729 | 162 | 93480 | 0.057083 | 0.044516
2013-02-11 | ZN12610:PA9 | SHORT RURAL | Other | 935941 | 29 | 162 | 3567 | 0.0021782 | 0.0017709
2013-02-11 | ZN10996:PA20 | URBAN | Other | 935943 | 1 | 536.0833 | 536.0833 | 0.00032736 | 6.1064e-05
2013-02-12 | ZN3472:PA8 | URBAN | Equipment Failure | 935948 | 1 | 512.75 | 512.75 | 0.00031311 | 6.1066e-05
2013-02-12 | 227:13020 | SHORT RURAL | Equipment Failure | 935955 | 6 | 93 | 558 | 0.00034075 | 0.00036639
2013-02-12 | 511:29878 | SHORT RURAL | Weather | 935958 | 4 | 104 | 416 | 0.00025403 | 0.00024426
2013-02-12 | 206:34441 | URBAN | Other | 935963 | 1 | 58.9833 | 58.9833 | 3.6019e-05 | 6.1066e-05
2013-02-12 | ZN3425:PA28 | URBAN | Other | 935969 | 1 | 122.45 | 122.45 | 7.4775e-05 | 6.1066e-05
2013-02-08 | ZN2466:PA16 | URBAN | Equipment Failure | 935989 | 63 | 119 | 7497 | 0.004578 | 0.0038471
2013-02-10 | 515:35197 | LONG RURAL | Other | 936016 | 4 | 220 | 880 | 0.00053737 | 0.00024426
2013-02-10 | 515:35197 | LONG RURAL | Equipment Failure | 936024 | 20 | 83 | 1660 | 0.0010137 | 0.0012213
2013-02-11 | 813:89061 | LONG RURAL | Other | 936041 | 3 | 94 | 282 | 0.0001722 | 0.00018319
2013-02-12 | 512:48049 | SHORT RURAL | Animals | 936059 | 1 | 52.2667 | 52.2667 | 3.1917e-05 | 6.1066e-05
2013-02-11 | 243:80083 | SHORT RURAL | Other | 936067 | 228 | 7 | 1596 | 0.00097459 | 0.013923
2013-02-12 | ZN167:PA1 | URBAN | Equipment Failure | 936095 | 1 | 215 | 215 | 0.00013129 | 6.1066e-05
2013-02-12 | 220:8691 | URBAN | Other | 936109 | 1 | 59.2667 | 59.2667 | 3.6192e-05 | 6.1066e-05
2013-02-12 | ZN2400:PA18 | SHORT RURAL | Equipment Failure | 936124 | 1 | 614.6167 | 614.6167 | 0.00037532 | 6.1066e-05
2013-02-12 | ZN3154:PA12 | URBAN | Vegetation | 936126 | 30 | 59 | 1770 | 0.0010809 | 0.001832
2013-02-12 | ZN340:PA8 | URBAN | Equipment Failure | 936137 | 18 | 64.2 | 1155.6 | 0.00070568 | 0.0010992
2013-02-12 | ZN2310:PA38 | URBAN | Third Party Impacts | 936143 | 1 | 168.9833 | 168.9833 | 0.00010319 | 6.1066e-05
2013-02-12 | ZN12630:PA1 | SHORT RURAL | Equipment Failure | 936169 | 728 | 1578 | 33813 | 0.020648 | 0.044456
2013-02-12 | 232:33413 | SHORT RURAL | Other | 936198 | 1 | 229.1167 | 229.1167 | 0.00013991 | 6.1066e-05
2013-02-12 | ZN36300:PA11 | URBAN | Vegetation | 936203 | 1 | 165.85 | 165.85 | 0.00010128 | 6.1066e-05
2013-02-11 | 813:89061 | LONG RURAL | Other | 936218 | 5 | 250 | 1250 | 0.0007633 | 0.00030532
2013-02-12 | 260:33353 | URBAN | Other | 936222 | 1 | 288.6667 | 288.6667 | 0.00017628 | 6.1066e-05
2013-02-11 | 813:89055 | SHORT RURAL | Other | 936237 | 7 | 100 | 700 | 0.00042745 | 0.00042745
2013-02-11 | 520:48172 | SHORT RURAL | Other | 936255 | 1 | 50 | 50 | 3.0532e-05 | 6.1064e-05
2013-02-11 | 813:89055 | SHORT RURAL | Equipment Failure | 936257 | 1 | 255 | 255 | 0.00015571 | 6.1064e-05
2013-02-12 | 225:33676 | SHORT RURAL | Vegetation | 936276 | 1 | 181.2 | 181.2 | 0.00011065 | 6.1066e-05
2013-02-12 | ZN12610:PA25 | SHORT RURAL | Equipment Failure | 936297 | 728 | 179 | 104400 | 0.063753 | 0.044456
2013-02-12 | ZN12610:PA6 | URBAN | Equipment Failure | 936297 | 21 | 179 | 2961 | 0.0018082 | 0.0012824
2013-02-12 | ZN12610:PA9 | SHORT RURAL | Equipment Failure | 936297 | 29 | 179 | 3857 | 0.0023553 | 0.0017709
2013-02-12 | ZN965:PA43 | URBAN | Equipment Failure | 936333 | 1 | 446.0167 | 446.0167 | 0.00027236 | 6.1066e-05
2013-02-12 | 220:8688 | URBAN | Other | 936366 | 1 | 202.45 | 202.45 | 0.00012363 | 6.1066e-05
2013-02-12 | ZN36300:PA3 | URBAN | Vegetation | 936368 | 45 | 101.9 | 4585.5 | 0.0028002 | 0.002748
2013-02-12 | 806:74080 | SHORT RURAL | Other | 936380 | 1 | 214.1833 | 214.1833 | 0.00013079 | 6.1066e-05
2013-02-12 | 502:48010 | SHORT RURAL | Equipment Failure | 936390 | 18 | 70 | 1260 | 0.00076943 | 0.0010992
2013-02-12 | 513:48059 | SHORT RURAL | Other | 936404 | 1 | 57 | 57 | 3.4807e-05 | 6.1066e-05
2013-02-12 | 503:48017 | URBAN | Other | 936405 | 1 | 138.2167 | 138.2167 | 8.4403e-05 | 6.1066e-05
2013-02-12 | 224:80329 | SHORT RURAL | Other | 936408 | 1 | 105.3 | 105.3 | 6.4302e-05 | 6.1066e-05
2013-02-12 | 509:48039 | LONG RURAL | Equipment Failure | 936419 | 31 | 409.0167 | 12679.5167 | 0.0077428 | 0.001893
2013-02-13 | ZN36300:PA1 | URBAN | Other | 936428 | 1 | 69 | 69 | 4.2136e-05 | 6.1066e-05
2013-02-13 | ZN36300:PA19 | URBAN | Other | 936428 | 1838 | 69 | 126822 | 0.077445 | 0.11224
2013-02-13 | 509:48039 | LONG RURAL | Vegetation | 936430 | 40 | 586 | 16175 | 0.0098775 | 0.0024426
2013-02-13 | 801:74123 | SHORT RURAL | Weather | 936435 | 1 | 179.0833 | 179.0833 | 0.00010936 | 6.1066e-05
2013-02-13 | ZN1285:PA31 | URBAN | Equipment Failure | 936436 | 1877 | 145 | 161472 | 0.098605 | 0.11462
2013-02-13 | 225:33676 | SHORT RURAL | Equipment Failure | 936447 | 74 | 125.3667 | 9277.1333 | 0.0056652 | 0.0045189
2013-02-13 | 242:81535 | URBAN | Other | 936481 | 1 | 509.5667 | 509.5667 | 0.00031117 | 6.1066e-05
2013-02-13 | 526:34636 | SHORT RURAL | Other | 936489 | 1 | 50 | 50 | 3.0533e-05 | 6.1066e-05
2013-02-13 | 243:80080 | SHORT RURAL | Other | 936496 | 1 | 119.2 | 119.2 | 7.2791e-05 | 6.1066e-05
2013-02-13 | ZN2400:PA22 | URBAN | Equipment Failure | 936501 | 1 | 175.7167 | 175.7167 | 0.0001073 | 6.1066e-05
2013-02-13 | ZN14143:PA6 | URBAN | Equipment Failure | 936509 | 27 | 82 | 1550 | 0.00094653 | 0.0016488
2013-02-13 | 513:48051 | URBAN | Other | 936521 | 1 | 117.3333 | 117.3333 | 7.1651e-05 | 6.1066e-05
2013-02-13 | ZN195:PA25 | URBAN | Other | 936554 | 1 | 86.8833 | 86.8833 | 5.3056e-05 | 6.1066e-05
2013-02-13 | ZN195:PA25 | URBAN | Vegetation | 936562 | 33 | 48.0667 | 1586.2 | 0.00096863 | 0.0020152
2013-02-13 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 936608 | 5 | 372 | 1860 | 0.0011358 | 0.00030533
2013-02-13 | ZN262:PA6 | URBAN | Operational Error | 936680 | 52 | 71 | 3692 | 0.0022546 | 0.0031754
2013-02-13 | 261:81879 | URBAN | Other | 936720 | 1 | 90.4833 | 90.4833 | 5.5255e-05 | 6.1066e-05
2013-02-13 | ZN12630:PA5 | SHORT RURAL | Vegetation | 936741 | 283 | 524 | 34287 | 0.020938 | 0.017282
2013-02-13 | ZN13000:PA11 | URBAN | Third Party Impacts | 936752 | 6 | 152 | 912 | 0.00055692 | 0.0003664
2013-02-13 | ZN72:PA24 | SHORT RURAL | Third Party Impacts | 936762 | 1 | 171.6 | 171.6 | 0.00010479 | 6.1066e-05
2013-02-13 | 501:48122 | SHORT RURAL | Other | 936769 | 1 | 93 | 93 | 5.6792e-05 | 6.1066e-05
2013-02-13 | ZN1164:PA20 | URBAN | Other | 936787 | 88 | 62 | 5456 | 0.0033318 | 0.0053738
2013-02-13 | ZN129:PA27 | URBAN | Other | 936813 | 196 | 53 | 10388 | 0.0063436 | 0.011969
2013-02-13 | ZN129:PA9 | URBAN | Other | 936813 | 2 | 53 | 106 | 6.473e-05 | 0.00012213
2013-02-13 | ZN12640:PA18 | SHORT RURAL | Equipment Failure | 936814 | 112 | 134 | 14951.1667 | 0.0091301 | 0.0068394
2013-02-13 | 511:29878 | SHORT RURAL | Equipment Failure | 936822 | 1 | 116.5333 | 116.5333 | 7.1162e-05 | 6.1066e-05
2013-02-14 | ZN1193:PA28 | URBAN | Vegetation | 936833 | 1 | 194 | 194 | 0.00011847 | 6.1066e-05
2013-02-14 | ZN3155:PA15 | URBAN | Other | 936848 | 28 | 135 | 3780 | 0.0023083 | 0.0017099
2013-02-14 | 813:89062 | SHORT RURAL | Operational Error | 936850 | 1 | 164.1833 | 164.1833 | 0.00010026 | 6.1066e-05
2013-02-14 | ZN3472:PA12 | URBAN | Equipment Failure | 936948 | 46 | 723.1167 | 33263.3667 | 0.020313 | 0.0028091
2013-02-14 | ZN15013:PA4 | URBAN | Equipment Failure | 936967 | 1 | 533.0333 | 533.0333 | 0.0003255 | 6.1066e-05
2013-02-14 | 227:13018 | URBAN | Third Party Impacts | 936991 | 1 | 150.05 | 150.05 | 9.163e-05 | 6.1066e-05
2013-02-12 | 511:29878 | SHORT RURAL | Weather | 937055 | 3 | 180 | 540 | 0.00032976 | 0.0001832
2013-02-14 | 512:48049 | SHORT RURAL | Other | 937066 | 1 | 149.6 | 149.6 | 9.1355e-05 | 6.1066e-05
2013-02-14 | 504:48031 | SHORT RURAL | Other | 937077 | 7 | 86 | 602 | 0.00036762 | 0.00042746
2013-02-14 | 507:80917 | URBAN | Other | 937102 | 1 | 120 | 120 | 7.328e-05 | 6.1066e-05
2013-02-14 | ZN12600:PA13 | SHORT RURAL | Vegetation | 937133 | 5 | 207 | 345 | 0.00021068 | 0.00030533
2013-02-14 | ZN12650:PA1 | SHORT RURAL | Vegetation | 937133 | 8 | 207 | 552 | 0.00033709 | 0.00048853
2013-02-14 | ZN12690:PA24 | SHORT RURAL | Vegetation | 937133 | 894 | 207 | 54918 | 0.033536 | 0.054593
2013-02-14 | 205:12206 | URBAN | Vegetation | 937150 | 1 | 98.4 | 98.4 | 6.0089e-05 | 6.1066e-05
2013-02-14 | 504:48031 | SHORT RURAL | Animals | 937174 | 2 | 126 | 252 | 0.00015389 | 0.00012213
2013-02-14 | 261:81886 | URBAN | Equipment Failure | 937201 | 13 | 175 | 2275 | 0.0013893 | 0.00079386
2013-02-15 | ZN9245:PA15 | URBAN | Animals | 937207 | 36 | 106 | 3816 | 0.0023303 | 0.0021984
2013-02-15 | ZN15012:PA6 | URBAN | Other | 937287 | 1 | 176.4833 | 176.4833 | 0.00010777 | 6.1067e-05
2013-02-15 | ZN180:PA21 | URBAN | Equipment Failure | 937289 | 1 | 94 | 93.15 | 5.6884e-05 | 6.1067e-05
2013-02-15 | ZN180:PA7 | URBAN | Equipment Failure | 937289 | 67 | 94 | 6298 | 0.003846 | 0.0040915
2013-02-14 | 509:48040 | SHORT RURAL | Other | 937378 | 4 | 115 | 460 | 0.00028091 | 0.00024427
2013-02-15 | ZN4545:PA11 | URBAN | Third Party Impacts | 937397 | 1 | 57 | 57 | 3.4808e-05 | 6.1067e-05
2013-02-15 | ZN4545:PA26 | URBAN | Third Party Impacts | 937397 | 893 | 57 | 47921 | 0.029264 | 0.054532
2013-02-15 | ZN4545:PA21 | URBAN | Weather | 937401 | 78 | 167 | 13026 | 0.0079545 | 0.0047632
2013-02-13 | 801:74123 | SHORT RURAL | Animals | 937429 | 2 | 21 | 42 | 2.5648e-05 | 0.00012213
2013-02-13 | 514:18141 | SHORT RURAL | Other | 937431 | 1 | 110 | 110 | 6.7173e-05 | 6.1066e-05
2013-02-15 | ZN2602:PA27 | URBAN | Other | 937455 | 39 | 269.35 | 10504.65 | 0.0064148 | 0.0023816
2013-02-15 | ZN342:PA15 | URBAN | Equipment Failure | 937547 | 122 | 108 | 13176 | 0.0080461 | 0.0074501
2013-02-15 | 508:82578 | SHORT RURAL | Other | 937562 | 4 | 99 | 396 | 0.00024182 | 0.00024427
2013-02-15 | 217:33610 | URBAN | Vegetation | 937613 | 1 | 203.9667 | 203.9667 | 0.00012456 | 6.1067e-05
2013-02-15 | 217:33610 | URBAN | Vegetation | 937614 | 1 | 204.0167 | 204.0167 | 0.00012459 | 6.1067e-05
2013-02-15 | 258:80775 | URBAN | Other | 937617 | 1 | 41.1333 | 41.1333 | 2.5119e-05 | 6.1067e-05
2013-02-15 | ZN80:PA24 | URBAN | Equipment Failure | 937623 | 35 | 45 | 1575 | 0.0009618 | 0.0021373
2013-02-15 | ZN5868:PA28 | URBAN | Equipment Failure | 937628 | 43 | 35 | 1505 | 0.00091905 | 0.0026259
2013-02-16 | ZN14144:PA4 | URBAN | Vegetation | 937629 | 827 | 66 | 29974 | 0.018304 | 0.050502
2013-02-16 | ZN3922:PA22 | URBAN | Other | 937633 | 1 | 393.7167 | 393.7167 | 0.00024043 | 6.1067e-05
2013-02-16 | ZN1193:PA26 | URBAN | Vegetation | 937634 | 122 | 341.95 | 41717.9 | 0.025476 | 0.0074501
2013-02-16 | 504:48026 | SHORT RURAL | Equipment Failure | 937644 | 1 | 222.0167 | 222.0167 | 0.00013558 | 6.1067e-05
2013-02-16 | 509:48040 | SHORT RURAL | Equipment Failure | 937661 | 1 | 247 | 247 | 0.00015083 | 6.1067e-05
2013-02-16 | 264:81244 | URBAN | Other | 937665 | 1 | 55.75 | 55.75 | 3.4045e-05 | 6.1067e-05
2013-02-16 | ZN2466:PA20 | URBAN | Other | 937726 | 55 | 55.0833 | 3029.5833 | 0.0018501 | 0.0033587
2013-02-16 | ZN2310:PA10 | URBAN | Equipment Failure | 937737 | 1 | 46 | 46 | 2.8091e-05 | 6.1067e-05
2013-02-16 | ZN2310:PA22 | URBAN | Equipment Failure | 937737 | 34 | 46 | 1562.3 | 0.00095404 | 0.0020763
2013-02-16 | 242:81541 | URBAN | Other | 937738 | 101 | 151.8333 | 15335.1667 | 0.0093647 | 0.0061677
2013-02-16 | ZN269:PA16 | URBAN | Equipment Failure | 937753 | 92 | 84 | 7268 | 0.0044383 | 0.0056181
2013-02-16 | ZN269:PA19 | URBAN | Equipment Failure | 937753 | 122 | 84 | 3660 | 0.002235 | 0.0074501
2013-02-17 | ZN195:PA30 | URBAN | Vegetation | 937779 | 21 | 233.3833 | 4901.05 | 0.0029929 | 0.0012824
2013-02-17 | ZN3472:PA23 | URBAN | Third Party Impacts | 937789 | 137 | 123 | 16851 | 0.01029 | 0.0083661
2013-02-17 | 807:74184 | SHORT RURAL | Other | 937796 | 2 | 117 | 234 | 0.0001429 | 0.00012213
2013-02-17 | ZN2473:PA9 | URBAN | Equipment Failure | 937812 | 5 | 427 | 2135 | 0.0013038 | 0.00030533
2013-02-17 | ZN15013:PA8 | URBAN | Equipment Failure | 937836 | 15 | 380 | 5700 | 0.0034808 | 0.000916
2013-02-17 | ZN12630:PA1 | SHORT RURAL | Other | 937841 | 458 | 79 | 36088 | 0.022038 | 0.027968
2013-02-17 | ZN12630:PA4 | SHORT RURAL | Other | 937841 | 17 | 79 | 901 | 0.00055021 | 0.0010381
2013-02-17 | ZN2196:PA14 | URBAN | Vegetation | 937881 | 6 | 112 | 672 | 0.00041037 | 0.0003664
2013-02-17 | ZN12660:PA5 | SHORT RURAL | Equipment Failure | 937889 | 84 | 54.55 | 4582.2 | 0.0027982 | 0.0051296
2013-02-17 | ZN180:PA34 | URBAN | Other | 937895 | 40 | 94.2 | 3768 | 0.002301 | 0.0024427
2013-02-17 | ZN36300:PA11 | URBAN | Equipment Failure | 937900 | 1 | 223.6167 | 223.6167 | 0.00013656 | 6.1067e-05
2013-02-18 | 229:34983 | SHORT RURAL | Equipment Failure | 937914 | 1657 | 237 | 220834 | 0.13486 | 0.10119
2013-02-18 | 813:89063 | SHORT RURAL | Animals | 937916 | 1491 | 78 | 116298 | 0.071019 | 0.09105
2013-02-17 | ZN188:PA33 | URBAN | Equipment Failure | 937919 | 1 | 830 | 830 | 0.00050685 | 6.1067e-05
2013-02-18 | ZN9118:PA11 | URBAN | Equipment Failure | 937921 | 41 | 127 | 5207 | 0.0031797 | 0.0025037
2013-02-18 | ZN15005:PA6 | URBAN | Equipment Failure | 937932 | 11 | 102 | 1122 | 0.00068517 | 0.00067173
2013-02-18 | ZN12600:PA9 | SHORT RURAL | Other | 937945 | 1 | 53.5833 | 53.5833 | 3.2722e-05 | 6.1067e-05
2013-02-18 | 225:33670 | SHORT RURAL | Other | 937980 | 1 | 40.6333 | 40.6333 | 2.4813e-05 | 6.1067e-05
2013-02-16 | 242:81541 | URBAN | Other | 937987 | 101 | 60 | 6060 | 0.0037006 | 0.0061677
2013-02-18 | ZN15008:PA7 | URBAN | Equipment Failure | 937992 | 1 | 257.9 | 257.9 | 0.00015749 | 6.1067e-05
2013-02-18 | ZN2466:PA20 | URBAN | Third Party Impacts | 938008 | 37 | 255 | 9404.1667 | 0.0057428 | 0.0022595
2013-02-18 | ZN2466:PA41 | URBAN | Third Party Impacts | 938008 | 12 | 255 | 3060 | 0.0018686 | 0.0007328
2013-02-18 | ZN12640:PA2 | URBAN | Other | 938038 | 1 | 88.8167 | 88.8167 | 5.4237e-05 | 6.1067e-05
2013-02-18 | 229:34983 | SHORT RURAL | Other | 938083 | 11 | 35 | 385 | 0.00023511 | 0.00067173
2013-02-18 | 813:89055 | SHORT RURAL | Equipment Failure | 938217 | 1 | 62.35 | 62.35 | 3.8075e-05 | 6.1067e-05
2013-02-18 | 256:80652 | URBAN | Other | 938264 | 1 | 62.4667 | 62.4667 | 3.8146e-05 | 6.1067e-05
2013-02-18 | ZN15006:PA9 | URBAN | Third Party Impacts | 938281 | 67 | 57 | 3819 | 0.0023321 | 0.0040915
2013-01-18 | ZN690:PA5 | URBAN | Vegetation | 938291 | 45 | 393 | 17685 | 0.010811 | 0.002751
2013-02-18 | 524:33570 | SHORT RURAL | Other | 938301 | 1 | 81.8 | 81.8 | 4.9952e-05 | 6.1067e-05
2013-02-18 | ZN15002:PA6 | URBAN | Other | 938310 | 68 | 142.9667 | 9721.7333 | 0.0059367 | 0.0041525
2013-02-18 | 524:33572 | SHORT RURAL | Equipment Failure | 938318 | 1 | 189.7 | 189.7 | 0.00011584 | 6.1067e-05
2013-02-18 | 260:33347 | SHORT RURAL | Other | 938353 | 1 | 91.8667 | 91.8667 | 5.61e-05 | 6.1067e-05
2013-02-18 | ZN12650:PA9 | URBAN | Vegetation | 938367 | 1 | 159.5167 | 159.5167 | 9.7411e-05 | 6.1067e-05
2013-02-18 | ZN195:PA11 | URBAN | Vegetation | 938368 | 1 | 155.2167 | 155.2167 | 9.4786e-05 | 6.1067e-05
2013-02-18 | ZN12650:PA17 | URBAN | Other | 938370 | 1 | 238.5833 | 238.5833 | 0.00014569 | 6.1067e-05
2013-02-19 | ZN9900:PA8 | URBAN | Equipment Failure | 938391 | 43 | 70.4833 | 3030.7833 | 0.0018507 | 0.0026257
2013-02-19 | ZN965:PA42 | URBAN | Vegetation | 938400 | 29 | 107 | 3103 | 0.0018948 | 0.0017708
2013-02-19 | ZN35500:PA18 | SHORT RURAL | Third Party Impacts | 938409 | 51 | 133 | 6783 | 0.0041418 | 0.0031142
2013-02-19 | ZN10995:PA6 | URBAN | Equipment Failure | 938414 | 1 | 152.2833 | 152.2833 | 9.2987e-05 | 6.1062e-05
2013-02-19 | ZN15008:PA7 | URBAN | Third Party Impacts | 938486 | 2720 | 39 | 96270 | 0.058785 | 0.16609
2013-02-19 | ZN690:PA12 | URBAN | Other | 938591 | 80 | 86.5333 | 6922.6667 | 0.0042271 | 0.004885
2013-02-19 | ZN269:PA6 | URBAN | Equipment Failure | 938665 | 25 | 34.35 | 858.75 | 0.00052437 | 0.0015266
2013-02-19 | ZN180:PA41 | URBAN | Other | 938678 | 1 | 74.3333 | 74.3333 | 4.539e-05 | 6.1062e-05
2013-02-19 | ZN15004:PA9 | URBAN | Third Party Impacts | 938682 | 2 | 149.85 | 299.7 | 0.000183 | 0.00012212
2013-02-19 | ZN15005:PA12 | URBAN | Equipment Failure | 938684 | 1 | 365.0167 | 365.0167 | 0.00022289 | 6.1062e-05
2013-02-19 | ZN269:PA6 | URBAN | Equipment Failure | 938701 | 25 | 136.65 | 3416.25 | 0.002086 | 0.0015266
2013-02-19 | 524:33572 | SHORT RURAL | Other | 938702 | 1 | 135.9167 | 135.9167 | 8.2994e-05 | 6.1062e-05
2013-02-19 | ZN12610:PA18 | URBAN | Equipment Failure | 938709 | 1 | 188 | 48 | 2.931e-05 | 6.1062e-05
2013-02-19 | ZN12610:PA2 | URBAN | Equipment Failure | 938709 | 1521 | 188 | 71948 | 0.043933 | 0.092876
2013-02-19 | ZN965:PA33 | URBAN | Equipment Failure | 938739 | 14 | 320 | 4480 | 0.0027356 | 0.00085487
2013-02-19 | ZN3922:PA29 | URBAN | Equipment Failure | 938751 | 75 | 275 | 20622.5333 | 0.012593 | 0.0045797
2013-02-19 | ZN2602:PA34 | URBAN | Equipment Failure | 938752 | 1 | 94.85 | 94.85 | 5.7917e-05 | 6.1062e-05
2013-02-19 | ZN12600:PA13 | SHORT RURAL | Third Party Impacts | 938760 | 1 | 455.9833 | 448.0167 | 0.00027357 | 6.1062e-05
2013-02-19 | ZN12650:PA1 | SHORT RURAL | Third Party Impacts | 938760 | 56 | 455.9833 | 11492 | 0.0070173 | 0.0034195
2013-02-19 | ZN15002:PA6 | URBAN | Animals | 938769 | 1607 | 107 | 105703 | 0.064545 | 0.098127
2013-02-19 | ZN12600:PA1 | SHORT RURAL | Equipment Failure | 938792 | 46 | 61 | 2806 | 0.0017134 | 0.0028089
2013-02-19 | 224:80335 | SHORT RURAL | Other | 938797 | 1 | 58.3333 | 58.3333 | 3.562e-05 | 6.1062e-05
2013-02-19 | 264:81240 | SHORT RURAL | Operational Error | 938829 | 529 | 3 | 1587 | 0.00096906 | 0.032302
2013-02-20 | ZN2466:PA41 | URBAN | Equipment Failure | 938837 | 1 | 195.1667 | 195.1667 | 0.00011919 | 6.1071e-05
2013-02-19 | 502:48004 | URBAN | Third Party Impacts | 938862 | 18 | 315 | 2535 | 0.0015479 | 0.0010991
2013-02-20 | ZN12630:PA3 | SHORT RURAL | Equipment Failure | 938879 | 9 | 115 | 1035 | 0.00063209 | 0.00054964
2013-02-20 | 221:11894 | URBAN | Other | 938898 | 1 | 78.75 | 78.75 | 4.8094e-05 | 6.1071e-05
2013-02-20 | 258:80773 | URBAN | Equipment Failure | 938992 | 3 | 78 | 234 | 0.00014291 | 0.00018321
2013-02-07 | 806:74080 | SHORT RURAL | Other | 939001 | 3 | 810 | 2430 | 0.0014838 | 0.00018319
2013-02-20 | 227:13015 | SHORT RURAL | Vegetation | 939023 | 1 | 227.4833 | 227.4833 | 0.00013893 | 6.1071e-05
2013-02-20 | 258:80784 | URBAN | Other | 939083 | 1 | 85.7333 | 85.7333 | 5.2358e-05 | 6.1071e-05
2013-02-20 | ZN2568:PA28 | URBAN | Equipment Failure | 939110 | 301 | 36 | 10836 | 0.0066177 | 0.018382
2013-02-19 | ZN14892:PA6 | SHORT RURAL | Vegetation | 939127 | 3 | 15 | 45 | 2.7478e-05 | 0.00018319
2013-02-20 | 806:74076 | SHORT RURAL | Vegetation | 939168 | 40 | 298 | 11920 | 0.0072797 | 0.0024429
2013-02-20 | 806:74080 | SHORT RURAL | Vegetation | 939168 | 231 | 298 | 68838 | 0.04204 | 0.014107
2013-02-20 | 508:82578 | SHORT RURAL | Vegetation | 939180 | 1 | 108.0667 | 108.0667 | 6.5998e-05 | 6.1071e-05
2013-02-20 | 210:8682 | URBAN | Equipment Failure | 939192 | 67 | 42 | 2814 | 0.0017185 | 0.0040918
2013-02-20 | 225:33670 | SHORT RURAL | Other | 939201 | 1 | 182.7833 | 182.7833 | 0.00011163 | 6.1071e-05
2013-02-20 | 513:48059 | SHORT RURAL | Equipment Failure | 939206 | 5 | 122 | 610 | 0.00037254 | 0.00030536
2013-02-20 | ZN188:PA44 | URBAN | Other | 939211 | 31 | 1457 | 45167 | 0.027584 | 0.0018932
2013-02-20 | 243:80084 | SHORT RURAL | Vegetation | 939221 | 1 | 151.6667 | 151.6667 | 9.2625e-05 | 6.1071e-05
2013-02-21 | ZN3154:PA18 | URBAN | Vegetation | 939223 | 36 | 75.9167 | 2733 | 0.0016691 | 0.0021986
2013-02-21 | 523:33508 | SHORT RURAL | Other | 939226 | 1 | 177.0833 | 177.0833 | 0.00010815 | 6.1072e-05
2013-02-21 | ZN15011:PA2 | URBAN | Animals | 939227 | 53 | 116 | 6142.8 | 0.0037515 | 0.0032368
2013-02-21 | ZN269:PA26 | URBAN | Equipment Failure | 939235 | 78 | 96 | 7488 | 0.004573 | 0.0047636
2013-02-21 | ZN80:PA22 | URBAN | Vegetation | 939242 | 59 | 377 | 3953 | 0.0024142 | 0.0036032
2013-02-21 | ZN80:PA25 | URBAN | Vegetation | 939242 | 862 | 377 | 85072 | 0.051955 | 0.052644
2013-02-21 | 801:74123 | SHORT RURAL | Equipment Failure | 939250 | 10 | 114.35 | 1143.5 | 0.00069835 | 0.00061072
2013-02-21 | ZN269:PA26 | URBAN | Equipment Failure | 939261 | 1 | 719.0333 | 719.0333 | 0.00043913 | 6.1072e-05
2013-02-21 | ZN15012:PA2 | URBAN | Vegetation | 939322 | 61 | 65 | 3919 | 0.0023934 | 0.0037254
2013-02-21 | 515:35193 | SHORT RURAL | Other | 939344 | 7 | 50 | 350 | 0.00021375 | 0.0004275
2013-02-21 | 258:80787 | URBAN | Other | 939350 | 1 | 60.55 | 60.55 | 3.6979e-05 | 6.1072e-05
2013-02-20 | 508:82578 | SHORT RURAL | Other | 939352 | 41 | 10 | 410 | 0.00025039 | 0.0025039
2013-02-21 | ZN9035:PA11 | URBAN | Vegetation | 939358 | 24 | 39 | 936 | 0.00057163 | 0.0014657
2013-02-21 | ZN9037:PA10 | URBAN | Vegetation | 939358 | 1 | 39 | 39 | 2.3818e-05 | 6.1072e-05
2013-02-21 | ZN9118:PA15 | URBAN | Equipment Failure | 939368 | 1 | 154.1 | 154.1 | 9.4111e-05 | 6.1072e-05
2013-02-21 | 507:80926 | URBAN | Equipment Failure | 939376 | 86 | 620 | 6200 | 0.0037864 | 0.0052522
2013-02-21 | ZN1193:PA28 | URBAN | Weather | 939401 | 36 | 323 | 11628 | 0.0071014 | 0.0021986
2013-02-21 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 939410 | 1 | 35 | 35 | 2.1375e-05 | 6.1072e-05
2013-02-21 | ZN9700:PA11 | URBAN | Operational Error | 939493 | 1941 | 21 | 40761 | 0.024893 | 0.11854
2013-02-21 | ZN9700:PA12 | URBAN | Operational Error | 939493 | 1006 | 21 | 21126 | 0.012902 | 0.061438
2013-02-21 | ZN9700:PA16 | URBAN | Operational Error | 939493 | 786 | 21 | 16506 | 0.01008 | 0.048002
2013-02-21 | ZN9700:PA18 | URBAN | Operational Error | 939493 | 1168 | 21 | 24528 | 0.01498 | 0.071332
2013-02-21 | ZN9700:PA20 | URBAN | Operational Error | 939493 | 1 | 21 | 21 | 1.2825e-05 | 6.1072e-05
2013-02-21 | ZN9700:PA24 | URBAN | Operational Error | 939493 | 1397 | 21 | 29337 | 0.017917 | 0.085317
2013-02-21 | 813:89061 | LONG RURAL | Equipment Failure | 939539 | 2 | 77 | 154 | 9.405e-05 | 0.00012214
2013-02-21 | ZN180:PA7 | URBAN | Other | 939559 | 1 | 5629.05 | 5629.05 | 0.0034378 | 6.1072e-05
2013-02-21 | ZN1648:PA16 | URBAN | Third Party Impacts | 939568 | 114 | 175 | 19950 | 0.012184 | 0.0069622
2013-02-21 | 801:74121 | SHORT RURAL | Other | 939585 | 1 | 217 | 217 | 0.00013253 | 6.1072e-05
2013-02-21 | 258:80781 | SHORT RURAL | Vegetation | 939587 | 1 | 110.8667 | 110.8667 | 6.7708e-05 | 6.1072e-05
2013-02-21 | 812:19072 | SHORT RURAL | Other | 939588 | 1 | 184 | 184 | 0.00011237 | 6.1072e-05
2013-02-21 | ZN14891:PA16 | SHORT RURAL | Equipment Failure | 939608 | 1 | 186.2333 | 186.2333 | 0.00011374 | 6.1072e-05
2013-02-21 | 810:74054 | LONG RURAL | Other | 939617 | 1 | 146.0333 | 146.0333 | 8.9185e-05 | 6.1072e-05
2013-02-21 | 807:74184 | SHORT RURAL | Vegetation | 939618 | 1 | 55.5833 | 55.5833 | 3.3946e-05 | 6.1072e-05
2013-02-22 | ZN180:PA23 | URBAN | Other | 939652 | 74 | 209 | 15466 | 0.0094454 | 0.0045193
2013-02-21 | ZN180:PA21 | URBAN | Other | 939676 | 13 | 22 | 286 | 0.00017467 | 0.00079393
2013-02-22 | ZN9118:PA8 | URBAN | Vegetation | 939688 | 1 | 119.9833 | 119.9833 | 7.3276e-05 | 6.1072e-05
2013-02-22 | ZN12570:PA39 | URBAN | Equipment Failure | 939690 | 1 | 158.3 | 158.3 | 9.6677e-05 | 6.1072e-05
2013-02-22 | ZN1193:PA9 | URBAN | Third Party Impacts | 939691 | 1 | 212.15 | 212.15 | 0.00012956 | 6.1072e-05
2013-02-22 | 526:34640 | SHORT RURAL | Other | 939692 | 1 | 80 | 80 | 4.8858e-05 | 6.1072e-05
2013-02-22 | ZN9550:PA36 | URBAN | Vegetation | 939697 | 1 | 170.7333 | 170.7333 | 0.00010427 | 6.1072e-05
2013-02-22 | 812:19072 | SHORT RURAL | Other | 939713 | 1 | 324.7 | 324.7 | 0.0001983 | 6.1072e-05
2013-02-22 | ZN5868:PA14 | URBAN | Other | 939811 | 1 | 188.6167 | 188.6167 | 0.00011519 | 6.1072e-05
2013-02-22 | ZN12650:PA17 | URBAN | Other | 939819 | 1 | 175 | 175 | 0.00010688 | 6.1072e-05
2013-02-22 | ZN9550:PA36 | URBAN | Other | 939828 | 28 | 65.7333 | 1840.5333 | 0.0011241 | 0.00171
2013-02-22 | 501:48115 | SHORT RURAL | Vegetation | 939859 | 1 | 60.1833 | 60.1833 | 3.6755e-05 | 6.1072e-05
2013-02-22 | ZN188:PA13 | URBAN | Vegetation | 939868 | 1 | 313.8833 | 313.8833 | 0.0001917 | 6.1072e-05
2013-02-22 | ZN9252:PA4 | URBAN | Equipment Failure | 939887 | 58 | 19.1333 | 1109.7333 | 0.00067774 | 0.0035422
2013-02-22 | 511:29878 | SHORT RURAL | Equipment Failure | 939892 | 6 | 284.8167 | 1708.9 | 0.0010437 | 0.00036643
2013-02-22 | ZN1610:PA11 | URBAN | Vegetation | 939893 | 47 | 100.35 | 4716.45 | 0.0028804 | 0.0028704
2013-02-22 | 261:81879 | URBAN | Vegetation | 939902 | 1 | 168.9167 | 168.9167 | 0.00010316 | 6.1072e-05
2013-02-22 | ZN1193:PA28 | URBAN | Vegetation | 939910 | 602 | 236 | 89908 | 0.054909 | 0.036765
2013-02-22 | ZN80:PA32 | URBAN | Vegetation | 939910 | 2 | 236 | 256 | 0.00015634 | 0.00012214
2013-02-22 | 813:89063 | SHORT RURAL | Vegetation | 939943 | 23 | 190 | 4370 | 0.0026689 | 0.0014047
2013-02-22 | 242:81535 | URBAN | Other | 939947 | 1 | 268.5 | 268.5 | 0.00016398 | 6.1072e-05
2013-02-22 | 813:89061 | LONG RURAL | Equipment Failure | 939952 | 1 | 289.3833 | 289.3833 | 0.00017673 | 6.1072e-05
2013-02-22 | 513:48050 | SHORT RURAL | Vegetation | 939953 | 11 | 113.6667 | 1250.3333 | 0.00076361 | 0.00067179
2013-02-22 | ZN12640:PA8 | SHORT RURAL | Equipment Failure | 939963 | 1 | 1773.1833 | 1773.1833 | 0.0010829 | 6.1072e-05
2013-02-22 | ZN116:PA33 | URBAN | Vegetation | 939967 | 1 | 1129.25 | 1129.25 | 0.00068966 | 6.1072e-05
2013-02-22 | ZN847:PA23 | URBAN | Equipment Failure | 939973 | 25 | 282.8167 | 7070.4167 | 0.0043181 | 0.0015268
2013-02-22 | ZN3155:PA29 | URBAN | Equipment Failure | 939978 | 1 | 333.8333 | 333.8333 | 0.00020388 | 6.1072e-05
2013-02-22 | 235:2857 | SHORT RURAL | Equipment Failure | 939993 | 1 | 76 | 67 | 4.0918e-05 | 6.1072e-05
2013-02-22 | 238:34144 | URBAN | Equipment Failure | 939993 | 832 | 76 | 57145 | 0.0349 | 0.050812
2013-02-22 | 229:34983 | SHORT RURAL | Other | 939997 | 1 | 246.3667 | 246.3667 | 0.00015046 | 6.1072e-05
2013-02-22 | 501:48115 | SHORT RURAL | Other | 940001 | 1 | 157.0667 | 157.0667 | 9.5924e-05 | 6.1072e-05
2013-02-22 | 501:48115 | SHORT RURAL | Other | 940002 | 1 | 273.9667 | 273.9667 | 0.00016732 | 6.1072e-05
2013-02-22 | 223:14394 | URBAN | Other | 940004 | 1 | 72.5333 | 72.5333 | 4.4298e-05 | 6.1072e-05
2013-02-22 | ZN12640:PA16 | URBAN | Equipment Failure | 940011 | 1 | 428.1333 | 428.1333 | 0.00026147 | 6.1072e-05
2013-02-22 | ZN12660:PA14 | SHORT RURAL | Vegetation | 940025 | 109 | 342 | 37278 | 0.022766 | 0.0066569
2013-02-22 | 203:8086 | URBAN | Other | 940029 | 1 | 768.6 | 768.6 | 0.0004694 | 6.1072e-05
2013-02-22 | 503:48011 | SHORT RURAL | Other | 940033 | 1 | 174.05 | 174.05 | 0.0001063 | 6.1072e-05
2013-02-22 | 265:81651 | URBAN | Equipment Failure | 940036 | 18 | 323 | 5814 | 0.0035507 | 0.0010993
2013-02-22 | ZN12630:PA4 | SHORT RURAL | Vegetation | 940043 | 15 | 485 | 7275 | 0.004443 | 0.00091608
2013-02-22 | 509:48039 | LONG RURAL | Other | 940060 | 2 | 84 | 168 | 0.0001026 | 0.00012214
2013-02-22 | 261:81876 | URBAN | Other | 940071 | 1 | 65.3167 | 65.3167 | 3.989e-05 | 6.1072e-05
2013-02-22 | ZN15014:PA22 | URBAN | Equipment Failure | 940079 | 1 | 575.3 | 575.3 | 0.00035135 | 6.1072e-05
2013-02-22 | 238:34141 | SHORT RURAL | Other | 940082 | 1 | 245.0167 | 245.0167 | 0.00014964 | 6.1072e-05
2013-02-22 | 511:29877 | SHORT RURAL | Equipment Failure | 940083 | 1114 | 175 | 194950 | 0.11906 | 0.068034
2013-02-22 | 513:48059 | SHORT RURAL | Other | 940085 | 1 | 55.7 | 55.7 | 3.4017e-05 | 6.1072e-05
2013-02-23 | ZN12620:PA1 | SHORT RURAL | Third Party Impacts | 940093 | 1702 | 50 | 85100 | 0.051972 | 0.10394
2013-02-23 | ZN12620:PA8 | SHORT RURAL | Third Party Impacts | 940093 | 883 | 50 | 44150 | 0.026963 | 0.053927
2013-02-23 | ZN12570:PA24 | SHORT RURAL | Vegetation | 940096 | 1 | 114.25 | 114.25 | 6.9775e-05 | 6.1072e-05
2013-02-23 | ZN12610:PA9 | SHORT RURAL | Equipment Failure | 940099 | 1163 | 470 | 133286 | 0.081401 | 0.071027
2013-02-23 | 265:81651 | URBAN | Other | 940104 | 81 | 10.5167 | 851.85 | 0.00052024 | 0.0049468
2013-02-23 | ZN398:PA15 | URBAN | Other | 940108 | 1 | 509.4833 | 509.4833 | 0.00031115 | 6.1072e-05
2013-02-23 | ZN3472:PA17 | URBAN | Other | 940109 | 1 | 406.3833 | 406.3833 | 0.00024819 | 6.1072e-05
2013-02-23 | ZN12580:PA14 | URBAN | Equipment Failure | 940110 | 43 | 143.8333 | 6184.8333 | 0.0037772 | 0.0026261
2013-02-23 | ZN36300:PA3 | URBAN | Weather | 940111 | 49 | 294.2333 | 14417.4333 | 0.008805 | 0.0029925
2013-02-23 | ZN15010:PA7 | URBAN | Other | 940112 | 1 | 239.8667 | 239.8667 | 0.00014649 | 6.1072e-05
2013-02-23 | ZN12690:PA7 | SHORT RURAL | Equipment Failure | 940115 | 98 | 149 | 11368 | 0.0069427 | 0.0059851
2013-02-23 | ZN12630:PA4 | SHORT RURAL | Vegetation | 940116 | 17 | 62.2667 | 1058.5333 | 0.00064647 | 0.0010382
2013-02-23 | ZN2602:PA4 | URBAN | Other | 940121 | 1 | 339.4167 | 339.4167 | 0.00020729 | 6.1072e-05
2013-02-23 | ZN187:PA22 | URBAN | Vegetation | 940125 | 91 | 450 | 40950 | 0.025009 | 0.0055576
2013-02-23 | 502:48004 | URBAN | Other | 940126 | 1 | 147.25 | 147.25 | 8.9929e-05 | 6.1072e-05
2013-02-23 | 813:89061 | LONG RURAL | Other | 940131 | 1 | 384.6667 | 384.6667 | 0.00023492 | 6.1072e-05
2013-02-23 | ZN15006:PA15 | URBAN | Vegetation | 940133 | 34 | 365.5667 | 12429.2667 | 0.0075908 | 0.0020765
2013-02-23 | 227:13015 | SHORT RURAL | Other | 940135 | 2 | 84 | 168 | 0.0001026 | 0.00012214
2013-02-23 | ZN12640:PA18 | SHORT RURAL | Other | 940141 | 1 | 117.45 | 117.45 | 7.1729e-05 | 6.1072e-05
2013-02-23 | 511:29873 | SHORT RURAL | Equipment Failure | 940145 | 10 | 307.9 | 3079 | 0.0018804 | 0.00061072
2013-02-23 | ZN4545:PA36 | URBAN | Weather | 940151 | 82 | 141 | 11562 | 0.0070612 | 0.0050079
2013-02-23 | ZN1788:PA8 | URBAN | Other | 940163 | 1 | 537.5 | 537.5 | 0.00032826 | 6.1072e-05
2013-02-23 | ZN15004:PA5 | URBAN | Vegetation | 940166 | 1 | 382.5833 | 382.5833 | 0.00023365 | 6.1072e-05
2013-02-23 | ZN12650:PA9 | URBAN | Vegetation | 940167 | 1 | 186.3333 | 186.3333 | 0.0001138 | 6.1072e-05
2013-02-23 | ZN12620:PA3 | URBAN | Other | 940178 | 1 | 58.6833 | 58.6833 | 3.5839e-05 | 6.1072e-05
2013-02-23 | 224:80346 | URBAN | Other | 940179 | 1 | 179.9167 | 179.9167 | 0.00010988 | 6.1072e-05
2013-02-23 | ZN15006:PA12 | URBAN | Other | 940181 | 29 | 178 | 5162 | 0.0031525 | 0.0017711
2013-02-23 | ZN15014:PA11 | URBAN | Other | 940184 | 46 | 172 | 7912 | 0.004832 | 0.0028093
2013-02-23 | ZN10999:PA7 | URBAN | Equipment Failure | 940188 | 1 | 229.8333 | 229.8333 | 0.00014036 | 6.1072e-05
2013-02-23 | 221:11897 | URBAN | Other | 940200 | 1 | 881 | 881 | 0.00053805 | 6.1072e-05
2013-02-23 | 502:48004 | URBAN | Vegetation | 940203 | 1 | 622.65 | 622.65 | 0.00038027 | 6.1072e-05
2013-02-23 | ZN2602:PA15 | URBAN | Equipment Failure | 940209 | 55 | 223 | 12265 | 0.0074905 | 0.003359
2013-02-23 | ZN12570:PA24 | SHORT RURAL | Vegetation | 940214 | 1 | 344.4167 | 344.4167 | 0.00021034 | 6.1072e-05
2013-02-23 | ZN12570:PA33 | SHORT RURAL | Vegetation | 940218 | 36 | 361.3167 | 13007.4 | 0.0079439 | 0.0021986
2013-02-23 | ZN12610:PA20 | SHORT RURAL | Equipment Failure | 940221 | 223 | 234 | 16792 | 0.010255 | 0.013619
2013-02-23 | ZN262:PA6 | URBAN | Vegetation | 940234 | 58 | 178.4 | 10347.2 | 0.0063193 | 0.0035422
2013-02-23 | ZN12630:PA3 | SHORT RURAL | Vegetation | 940237 | 180 | 290 | 17339 | 0.010589 | 0.010993
2013-02-23 | ZN12630:PA4 | SHORT RURAL | Vegetation | 940237 | 272 | 290 | 27078 | 0.016537 | 0.016612
2013-02-23 | 504:48031 | SHORT RURAL | Vegetation | 940239 | 2 | 141 | 282 | 0.00017222 | 0.00012214
2013-02-23 | ZN1788:PA8 | URBAN | Other | 940241 | 1 | 444.1833 | 444.1833 | 0.00027127 | 6.1072e-05
2013-02-23 | 258:80779 | URBAN | Vegetation | 940248 | 1 | 654.1167 | 654.1167 | 0.00039948 | 6.1072e-05
2013-02-23 | ZN12620:PA1 | SHORT RURAL | Weather | 940249 | 72 | 445 | 32040 | 0.019568 | 0.0043972
2013-02-23 | 261:81865 | URBAN | Other | 940262 | 1 | 284.2833 | 284.2833 | 0.00017362 | 6.1072e-05
2013-02-23 | ZN3672:PA26 | URBAN | Equipment Failure | 940267 | 1 | 425.9 | 425.9 | 0.00026011 | 6.1072e-05
2013-02-23 | 264:81241 | SHORT RURAL | Other | 940270 | 1 | 99.5667 | 99.5667 | 6.0808e-05 | 6.1072e-05
2013-02-23 | ZN847:PA44 | URBAN | Vegetation | 940277 | 33 | 97 | 3201 | 0.0019549 | 0.0020154
2013-02-23 | ZN15005:PA6 | URBAN | Vegetation | 940288 | 10 | 382 | 3820 | 0.002333 | 0.00061072
2013-02-23 | ZN15005:PA8 | URBAN | Vegetation | 940288 | 39 | 382 | 14860.3 | 0.0090755 | 0.0023818
2013-02-23 | ZN12640:PA10 | URBAN | Other | 940312 | 1 | 145.65 | 145.65 | 8.8952e-05 | 6.1072e-05
2013-02-23 | ZN15010:PA7 | URBAN | Vegetation | 940313 | 1 | 190.25 | 190.25 | 0.00011619 | 6.1072e-05
2013-02-23 | ZN12570:PA33 | SHORT RURAL | Vegetation | 940314 | 4 | 2685 | 10740 | 0.0065592 | 0.00024429
2013-02-23 | ZN15014:PA16 | URBAN | Other | 940315 | 1 | 437.9 | 437.9 | 0.00026744 | 6.1072e-05
2013-02-23 | ZN2466:PA45 | URBAN | Other | 940321 | 1 | 563.55 | 563.55 | 0.00034417 | 6.1072e-05
2013-02-23 | ZN15010:PA7 | URBAN | Vegetation | 940337 | 1 | 159.1 | 159.1 | 9.7166e-05 | 6.1072e-05
2013-02-23 | ZN12660:PA14 | SHORT RURAL | Vegetation | 940342 | 1 | 343.4167 | 343.4167 | 0.00020973 | 6.1072e-05
2013-02-23 | ZN1673:PA7 | URBAN | Vegetation | 940353 | 52 | 338.9333 | 17624.5333 | 0.010764 | 0.0031758
2013-02-23 | ZN2602:PA27 | URBAN | Weather | 940355 | 57 | 100.3667 | 5720.9 | 0.0034939 | 0.0034811
2013-02-23 | 256:80640 | URBAN | Vegetation | 940358 | 33 | 131.4667 | 4338.4 | 0.0026496 | 0.0020154
2013-02-23 | 504:48033 | SHORT RURAL | Other | 940361 | 1 | 189.7833 | 189.7833 | 0.0001159 | 6.1072e-05
2013-02-23 | ZN12620:PA10 | SHORT RURAL | Equipment Failure | 940362 | 630 | 277 | 102950 | 0.062874 | 0.038475
2013-02-23 | ZN15010:PA7 | URBAN | Equipment Failure | 940388 | 1 | 139.15 | 139.15 | 8.4982e-05 | 6.1072e-05
2013-02-23 | ZN12660:PA14 | SHORT RURAL | Other | 940393 | 1 | 10.7333 | 10.7333 | 6.5551e-06 | 6.1072e-05
2013-02-23 | ZN14891:PA12 | SHORT RURAL | Vegetation | 940406 | 56 | 1922 | 63259 | 0.038634 | 0.00342
2013-02-23 | ZN9118:PA8 | URBAN | Equipment Failure | 940420 | 1 | 308.6333 | 308.6333 | 0.00018849 | 6.1072e-05
2013-02-23 | ZN965:PA26 | URBAN | Vegetation | 940421 | 913 | 136 | 84658 | 0.051703 | 0.055759
2013-02-23 | ZN12630:PA1 | SHORT RURAL | Vegetation | 940422 | 231 | 155 | 35703 | 0.021805 | 0.014108
2013-02-23 | ZN3154:PA18 | URBAN | Vegetation | 940433 | 1 | 1912.6 | 1912.6 | 0.0011681 | 6.1072e-05
2013-02-23 | ZN4545:PA40 | URBAN | Vegetation | 940444 | 1 | 1622.4667 | 1622.4667 | 0.00099088 | 6.1072e-05
2013-02-23 | ZN2310:PA27 | URBAN | Other | 940448 | 1 | 565.95 | 565.95 | 0.00034564 | 6.1072e-05
2013-02-23 | ZN180:PA22 | URBAN | Vegetation | 940453 | 99 | 171.5667 | 16985.1 | 0.010373 | 0.0060461
2013-02-23 | ZN5868:PA14 | URBAN | Vegetation | 940456 | 66 | 412.2833 | 27210.7 | 0.016618 | 0.0040308
2013-02-23 | 509:48039 | LONG RURAL | Vegetation | 940467 | 79 | 1518.9167 | 119994.4167 | 0.073283 | 0.0048247
2013-02-23 | 202:34260 | URBAN | Other | 940470 | 1 | 98.9333 | 98.9333 | 6.0421e-05 | 6.1072e-05
2013-02-23 | 222:2015 | SHORT RURAL | Other | 940481 | 1 | 228.9333 | 228.9333 | 0.00013981 | 6.1072e-05
2013-02-23 | ZN2568:PA32 | URBAN | Vegetation | 940485 | 80 | 149.7667 | 11981.3333 | 0.0073173 | 0.0048858
2013-02-23 | ZN12580:PA1 | URBAN | Equipment Failure | 940492 | 1 | 2904.5 | 2904.5 | 0.0017738 | 6.1072e-05
2013-02-23 | 225:13446 | URBAN | Vegetation | 940493 | 1 | 85.25 | 85.25 | 5.2064e-05 | 6.1072e-05
2013-02-23 | ZN187:PA20 | URBAN | Equipment Failure | 940495 | 592 | 109 | 62724 | 0.038307 | 0.036155
2013-02-23 | ZN187:PA8 | URBAN | Equipment Failure | 940495 | 1030 | 109 | 57680 | 0.035226 | 0.062904
2013-02-23 | 228:7490 | SHORT RURAL | Other | 940506 | 1 | 107.2667 | 107.2667 | 6.551e-05 | 6.1072e-05
2013-02-23 | ZN12650:PA6 | URBAN | Equipment Failure | 940528 | 246 | 107 | 26322 | 0.016075 | 0.015024
2013-02-23 | ZN80:PA32 | URBAN | Vegetation | 940530 | 43 | 106.6833 | 4587.3833 | 0.0028016 | 0.0026261
2013-02-23 | 227:13015 | SHORT RURAL | Other | 940535 | 1 | 113.3333 | 113.3333 | 6.9215e-05 | 6.1072e-05
2013-02-23 | 243:80084 | SHORT RURAL | Other | 940546 | 1 | 72.1 | 72.1 | 4.4033e-05 | 6.1072e-05
2013-02-23 | ZN1164:PA13 | URBAN | Third Party Impacts | 940549 | 49 | 320.15 | 15687.35 | 0.0095806 | 0.0029925
2013-02-23 | ZN2635:PA21 | URBAN | Vegetation | 940550 | 97 | 146 | 14162 | 0.008649 | 0.005924
2013-02-23 | ZN2466:PA16 | URBAN | Other | 940571 | 1 | 243 | 243 | 0.00014841 | 6.1072e-05
2013-02-23 | ZN847:PA22 | SHORT RURAL | Vegetation | 940579 | 1 | 360.95 | 360.95 | 0.00022044 | 6.1072e-05
2013-02-23 | ZN10996:PA14 | URBAN | Vegetation | 940584 | 1 | 1280.0667 | 1280.0667 | 0.00078176 | 6.1072e-05
2013-02-23 | ZN15005:PA6 | URBAN | Equipment Failure | 940588 | 1 | 94.4833 | 94.4833 | 5.7703e-05 | 6.1072e-05
2013-02-23 | 801:74122 | URBAN | Other | 940602 | 1 | 146.35 | 146.35 | 8.9379e-05 | 6.1072e-05
2013-02-23 | ZN10995:PA2 | URBAN | Other | 940617 | 13 | 51 | 663 | 0.00040491 | 0.00079394
2013-02-23 | ZN690:PA35 | URBAN | Vegetation | 940621 | 82 | 162.9833 | 13364.6333 | 0.0081621 | 0.0050079
2013-02-23 | ZN2568:PA22 | URBAN | Equipment Failure | 940634 | 1 | 1292.1333 | 1292.1333 | 0.00078913 | 6.1072e-05
2013-02-23 | ZN1164:PA21 | URBAN | Vegetation | 940638 | 1 | 403.4 | 403.4 | 0.00024637 | 6.1072e-05
2013-02-23 | ZN1164:PA21 | URBAN | Vegetation | 940641 | 1 | 402.2 | 402.2 | 0.00024563 | 6.1072e-05
2013-02-23 | ZN12570:PA35 | URBAN | Other | 940645 | 1 | 1404.65 | 1404.65 | 0.00085785 | 6.1072e-05
2013-02-23 | ZN12600:PA2 | SHORT RURAL | Vegetation | 940648 | 1 | 1703.0167 | 1703.0167 | 0.0010401 | 6.1072e-05
2013-02-23 | ZN12630:PA3 | SHORT RURAL | Vegetation | 940650 | 60 | 210 | 3250 | 0.0019848 | 0.0036643
2013-02-23 | ZN847:PA1 | URBAN | Other | 940654 | 56 | 160.6833 | 8998.2667 | 0.0054954 | 0.00342
2013-02-23 | ZN10997:PA2 | URBAN | Vegetation | 940660 | 66 | 102 | 6732 | 0.0041114 | 0.0040308
2013-02-23 | ZN15008:PA10 | URBAN | Other | 940669 | 1 | 326.95 | 326.95 | 0.00019968 | 6.1072e-05
2013-02-23 | 507:80931 | URBAN | Other | 940684 | 1 | 655.5167 | 655.5167 | 0.00040034 | 6.1072e-05
2013-02-23 | ZN1673:PA11 | URBAN | Vegetation | 940694 | 1 | 1756.6833 | 1756.6833 | 0.0010728 | 6.1072e-05
2013-02-23 | ZN15004:PA9 | URBAN | Vegetation | 940697 | 1 | 1153.2833 | 1153.2833 | 0.00070434 | 6.1072e-05
2013-02-23 | ZN9900:PA1 | URBAN | Other | 940704 | 1227 | 46 | 53607 | 0.032739 | 0.074936
2013-02-23 | 229:34983 | SHORT RURAL | Other | 940705 | 1 | 388.3167 | 388.3167 | 0.00023715 | 6.1072e-05
2013-02-23 | 229:34983 | SHORT RURAL | Vegetation | 940709 | 1 | 538.8167 | 538.8167 | 0.00032907 | 6.1072e-05
2013-02-23 | 501:48115 | SHORT RURAL | Other | 940717 | 1 | 478.9333 | 478.9333 | 0.0002925 | 6.1072e-05
2013-02-23 | ZN2602:PA17 | URBAN | Vegetation | 940722 | 123 | 80.1167 | 9854.35 | 0.0060183 | 0.0075119
2013-02-23 | 512:48046 | SHORT RURAL | Equipment Failure | 940724 | 3 | 162 | 486 | 0.00029681 | 0.00018322
2013-02-23 | ZN3154:PA6 | URBAN | Vegetation | 940727 | 1 | 443.8667 | 443.8667 | 0.00027108 | 6.1072e-05
2013-02-23 | ZN35370:PA2 | SHORT RURAL | Vegetation | 940730 | 16 | 1533.8333 | 24541.3333 | 0.014988 | 0.00097716
2013-02-23 | ZN15004:PA5 | URBAN | Other | 940741 | 1 | 127.2833 | 127.2833 | 7.7735e-05 | 6.1072e-05
2013-02-23 | 264:81236 | URBAN | Equipment Failure | 940749 | 1 | 999.2167 | 999.2167 | 0.00061024 | 6.1072e-05
2013-02-23 | ZN12570:PA40 | SHORT RURAL | Equipment Failure | 940752 | 835 | 139 | 83815 | 0.051188 | 0.050995
2013-02-23 | ZN847:PA21 | URBAN | Vegetation | 940753 | 1 | 1288.7 | 1288.7 | 0.00078704 | 6.1072e-05
2013-02-23 | ZN12600:PA2 | SHORT RURAL | Vegetation | 940761 | 60 | 148 | 8568 | 0.0052327 | 0.0036643
2013-02-23 | ZN35500:PA28 | URBAN | Vegetation | 940768 | 393 | 24 | 9432 | 0.0057603 | 0.024001
2013-02-23 | 504:48026 | SHORT RURAL | Vegetation | 940772 | 1 | 274.9333 | 274.9333 | 0.00016791 | 6.1072e-05
2013-02-23 | 235:2124 | URBAN | Vegetation | 940778 | 1 | 503.6333 | 503.6333 | 0.00030758 | 6.1072e-05
2013-02-23 | ZN847:PA22 | SHORT RURAL | Vegetation | 940780 | 1190 | 360 | 398894 | 0.24361 | 0.072676
2013-02-23 | 229:34989 | SHORT RURAL | Other | 940783 | 1 | 105.8167 | 105.8167 | 6.4625e-05 | 6.1072e-05
2013-02-23 | 229:34983 | SHORT RURAL | Other | 940786 | 1 | 199.4667 | 199.4667 | 0.00012182 | 6.1072e-05
2013-02-23 | 235:2124 | URBAN | Vegetation | 940789 | 1 | 498.1667 | 498.1667 | 0.00030424 | 6.1072e-05
2013-02-23 | 234:2001 | URBAN | Vegetation | 940795 | 1 | 377.8667 | 377.8667 | 0.00023077 | 6.1072e-05
2013-02-23 | ZN15004:PA9 | URBAN | Third Party Impacts | 940797 | 82 | 87.15 | 7146.3 | 0.0043644 | 0.0050079
2013-02-23 | ZN2635:PA21 | URBAN | Vegetation | 940807 | 1 | 661.6 | 661.6 | 0.00040405 | 6.1072e-05
2013-02-23 | 507:80917 | URBAN | Vegetation | 940808 | 1 | 407.0833 | 407.0833 | 0.00024861 | 6.1072e-05
2013-02-23 | 229:34989 | SHORT RURAL | Other | 940814 | 1 | 290.1333 | 290.1333 | 0.00017719 | 6.1072e-05
2013-02-23 | 504:48034 | URBAN | Other | 940816 | 1 | 574.5 | 574.5 | 0.00035086 | 6.1072e-05
2013-02-23 | 512:48046 | SHORT RURAL | Other | 940817 | 1 | 350 | 350 | 0.00021375 | 6.1072e-05
2013-02-23 | 258:80784 | URBAN | Other | 940818 | 1 | 755.7667 | 755.7667 | 0.00046156 | 6.1072e-05
2013-02-23 | 258:80784 | URBAN | Other | 940819 | 1 | 756.65 | 756.65 | 0.0004621 | 6.1072e-05
2013-02-23 | ZN35500:PA23 | URBAN | Vegetation | 940820 | 1 | 1183.9833 | 1183.9833 | 0.00072308 | 6.1072e-05
2013-02-23 | 205:12203 | URBAN | Vegetation | 940821 | 1 | 331.45 | 331.45 | 0.00020242 | 6.1072e-05
2013-02-23 | 214:8669 | URBAN | Weather | 940823 | 1447 | 437 | 623801.7 | 0.38097 | 0.088371
2013-02-23 | 258:80785 | URBAN | Weather | 940823 | 1479 | 437 | 126346 | 0.077162 | 0.090326
2013-02-23 | 258:80793 | SHORT RURAL | Weather | 940823 | 1223 | 437 | 274792 | 0.16782 | 0.074691
2013-02-23 | 229:34989 | SHORT RURAL | Other | 940826 | 1 | 444.7333 | 444.7333 | 0.00027161 | 6.1072e-05
2013-02-23 | 258:80791 | URBAN | Vegetation | 940830 | 1 | 258.3833 | 258.3833 | 0.0001578 | 6.1072e-05
2013-02-23 | 258:80784 | URBAN | Equipment Failure | 940834 | 63 | 579 | 36477 | 0.022277 | 0.0038475
2013-02-23 | 258:80784 | URBAN | Other | 940848 | 1 | 746.7833 | 746.7833 | 0.00045608 | 6.1072e-05
2013-02-23 | 504:48031 | SHORT RURAL | Equipment Failure | 940856 | 50 | 1059 | 35016 | 0.021385 | 0.0030536
2013-02-23 | 504:48031 | SHORT RURAL | Vegetation | 940867 | 1 | 1059.85 | 1059.85 | 0.00064727 | 6.1072e-05
2013-02-23 | ZN2400:PA21 | URBAN | Vegetation | 940874 | 646 | 330 | 118086 | 0.072118 | 0.039453
2013-02-23 | ZN14143:PA17 | SHORT RURAL | Vegetation | 940879 | 746 | 2765 | 1072188 | 0.65481 | 0.04556
2013-02-23 | 240:34835 | URBAN | Vegetation | 940880 | 1 | 271.2833 | 271.2833 | 0.00016568 | 6.1072e-05
2013-02-23 | ZN12630:PA3 | SHORT RURAL | Vegetation | 940887 | 427 | 4185 | 680713.1833 | 0.41573 | 0.026078
2013-02-23 | ZN3154:PA13 | URBAN | Vegetation | 940924 | 46 | 250.95 | 11543.7 | 0.00705 | 0.0028093
2013-02-23 | ZN12690:PA12 | SHORT RURAL | Vegetation | 940928 | 1 | 345.45 | 345.45 | 0.00021097 | 6.1072e-05
2013-02-23 | ZN3472:PA17 | URBAN | Other | 940929 | 1 | 727.25 | 727.25 | 0.00044415 | 6.1072e-05
2013-02-23 | ZN12620:PA3 | URBAN | Vegetation | 940932 | 1 | 342.6333 | 342.6333 | 0.00020925 | 6.1072e-05
2013-02-23 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 940949 | 17 | 1364 | 23188 | 0.014161 | 0.0010382
2013-02-23 | 504:48026 | SHORT RURAL | Vegetation | 940958 | 1 | 172.8833 | 172.8833 | 0.00010558 | 6.1072e-05
2013-02-23 | ZN3472:PA17 | URBAN | Other | 940962 | 1 | 709.3833 | 709.3833 | 0.00043324 | 6.1072e-05
2013-02-23 | ZN2400:PA15 | URBAN | Other | 940966 | 1216 | 170 | 190200 | 0.11616 | 0.074264
2013-02-23 | ZN2400:PA22 | URBAN | Vegetation | 940967 | 1 | 1419.5833 | 1419.5833 | 0.00086697 | 6.1072e-05
2013-02-23 | ZN2400:PA18 | SHORT RURAL | Vegetation | 940974 | 1253 | 478 | 209421 | 0.1279 | 0.076523
2013-02-23 | ZN847:PA44 | URBAN | Vegetation | 940976 | 1 | 1180.35 | 1180.35 | 0.00072087 | 6.1072e-05
2013-02-23 | 260:33347 | SHORT RURAL | Equipment Failure | 940983 | 47 | 571.5833 | 26864.4167 | 0.016407 | 0.0028704
2013-02-23 | ZN12630:PA5 | SHORT RURAL | Vegetation | 940993 | 257 | 1418 | 264224 | 0.16137 | 0.015696
2013-02-23 | 202:34256 | URBAN | Other | 940996 | 1 | 597.85 | 597.85 | 0.00036512 | 6.1072e-05
2013-02-23 | ZN12630:PA1 | SHORT RURAL | Vegetation | 941020 | 58 | 1110 | 64380 | 0.039318 | 0.0035422
2013-02-23 | ZN12630:PA4 | SHORT RURAL | Vegetation | 941026 | 272 | 1612 | 325698 | 0.19891 | 0.016612
2013-02-23 | ZN80:PA32 | URBAN | Vegetation | 941027 | 77 | 113 | 8701 | 0.0053139 | 0.0047026
2013-02-23 | ZN12630:PA1 | SHORT RURAL | Other | 941046 | 1 | 1073.1833 | 1073.1833 | 0.00065542 | 6.1072e-05
2013-02-23 | 202:34249 | URBAN | Other | 941058 | 1 | 376.45 | 376.45 | 0.00022991 | 6.1072e-05
2013-02-23 | ZN35500:PA23 | URBAN | Vegetation | 941059 | 43 | 135.1 | 5809.3 | 0.0035479 | 0.0026261
2013-02-23 | 258:80784 | URBAN | Other | 941084 | 1 | 263.9833 | 263.9833 | 0.00016122 | 6.1072e-05
2013-02-23 | 260:33347 | SHORT RURAL | Other | 941101 | 1 | 130.0167 | 130.0167 | 7.9404e-05 | 6.1072e-05
2013-02-23 | ZN847:PA18 | URBAN | Vegetation | 941104 | 45 | 881.1667 | 39652.5 | 0.024217 | 0.0027482
2013-02-23 | ZN3154:PA13 | URBAN | Vegetation | 941129 | 47 | 148.0833 | 6959.9167 | 0.0042506 | 0.0028704
2013-02-23 | ZN12570:PA22 | URBAN | Other | 941131 | 35 | 712.3167 | 24931.0833 | 0.015226 | 0.0021375
2013-02-23 | ZN847:PA5 | URBAN | Equipment Failure | 941132 | 39 | 856.55 | 33405.45 | 0.020401 | 0.0023818
2013-02-23 | ZN12660:PA10 | SHORT RURAL | Equipment Failure | 941155 | 48 | 544.4167 | 26132 | 0.015959 | 0.0029315
2013-02-23 | ZN12650:PA20 | URBAN | Other | 941157 | 1 | 698.5667 | 698.5667 | 0.00042663 | 6.1072e-05
2013-02-23 | ZN847:PA22 | SHORT RURAL | Vegetation | 941158 | 1 | 1232.8167 | 1232.8167 | 0.00075291 | 6.1072e-05
2013-02-23 | ZN4545:PA31 | URBAN | Equipment Failure | 941161 | 1 | 2397.4 | 2397.4 | 0.0014641 | 6.1072e-05
2013-02-23 | ZN3154:PA22 | URBAN | Vegetation | 941176 | 63 | 272 | 17110 | 0.010449 | 0.0038475
2013-02-23 | ZN1673:PA11 | URBAN | Other | 941181 | 52 | 703 | 36556 | 0.022326 | 0.0031758
2013-02-23 | ZN188:PA41 | URBAN | Equipment Failure | 941182 | 1 | 486.8667 | 486.8667 | 0.00029734 | 6.1072e-05
2013-02-24 | ZN965:PA33 | URBAN | Equipment Failure | 941185 | 31 | 333.4167 | 10335.9167 | 0.0063124 | 0.0018932
2013-02-23 | ZN269:PA2 | URBAN | Equipment Failure | 941189 | 1 | 723.9333 | 723.9333 | 0.00044212 | 6.1072e-05
2013-02-23 | ZN12640:PA8 | SHORT RURAL | Other | 941190 | 1 | 768.4167 | 768.4167 | 0.00046929 | 6.1072e-05
2013-02-23 | ZN15014:PA11 | URBAN | Vegetation | 941191 | 968 | 51 | 49368 | 0.03015 | 0.059118
2013-02-23 | ZN15014:PA20 | URBAN | Vegetation | 941191 | 1 | 51 | 51 | 3.1147e-05 | 6.1072e-05
2013-02-23 | ZN15010:PA5 | URBAN | Vegetation | 941198 | 79 | 736 | 58144 | 0.03551 | 0.0048247
2013-02-23 | ZN1673:PA7 | URBAN | Other | 941206 | 36 | 463 | 16668 | 0.01018 | 0.0021986
2013-02-23 | 234:2001 | URBAN | Vegetation | 941220 | 1 | 114.3833 | 114.3833 | 6.9856e-05 | 6.1072e-05
2013-02-23 | ZN847:PA15 | URBAN | Vegetation | 941224 | 1 | 2183.6167 | 2183.6167 | 0.0013336 | 6.1072e-05
2013-02-23 | ZN3472:PA21 | URBAN | Vegetation | 941229 | 74 | 271.2 | 20068.8 | 0.012256 | 0.0045193
2013-02-24 | ZN965:PA8 | URBAN | Vegetation | 941231 | 1 | 2007 | 2007 | 0.0012257 | 6.1072e-05
2013-02-23 | ZN15005:PA8 | URBAN | Other | 941232 | 39 | 646.4333 | 25210.9 | 0.015397 | 0.0023818
2013-02-23 | ZN3154:PA14 | URBAN | Vegetation | 941248 | 39 | 1154.1833 | 45013.15 | 0.027491 | 0.0023818
2013-02-23 | ZN2400:PA18 | SHORT RURAL | Vegetation | 941260 | 1 | 1143.6333 | 1143.6333 | 0.00069844 | 6.1072e-05
2013-02-23 | ZN195:PA25 | URBAN | Vegetation | 941262 | 1 | 1202.35 | 1202.35 | 0.0007343 | 6.1072e-05
2013-02-23 | ZN35500:PA23 | URBAN | Other | 941265 | 28 | 405 | 11340 | 0.0069256 | 0.00171
2013-02-23 | ZN3472:PA21 | URBAN | Vegetation | 941266 | 1 | 810.4833 | 810.4833 | 0.00049498 | 6.1072e-05
2013-02-24 | ZN35500:PA31 | URBAN | Other | 941267 | 12 | 449.55 | 5394.6 | 0.0032946 | 0.00073287
2013-02-23 | ZN15002:PA2 | SHORT RURAL | Other | 941284 | 275 | 153 | 41800 | 0.025528 | 0.016795
2013-02-23 | ZN15013:PA10 | SHORT RURAL | Other | 941284 | 151 | 153 | 23103 | 0.01411 | 0.0092219
2013-02-24 | ZN847:PA44 | URBAN | Vegetation | 941285 | 1 | 979.1167 | 979.1167 | 0.00059797 | 6.1072e-05
2013-02-23 | ZN35370:PA8 | SHORT RURAL | Vegetation | 941288 | 727 | 1058 | 237189 | 0.14486 | 0.044399
2013-02-23 | ZN15006:PA13 | URBAN | Vegetation | 941297 | 1314 | 711 | 666653 | 0.40714 | 0.080249
2013-02-24 | ZN1193:PA9 | URBAN | Vegetation | 941299 | 1 | 1241.05 | 1241.05 | 0.00075794 | 6.1072e-05
2013-02-24 | ZN35500:PA28 | URBAN | Vegetation | 941301 | 1 | 888.9 | 888.9 | 0.00054287 | 6.1072e-05
2013-02-24 | ZN15002:PA2 | SHORT RURAL | Other | 941309 | 97 | 472.65 | 45847.05 | 0.028 | 0.005924
2013-02-24 | ZN4545:PA31 | URBAN | Equipment Failure | 941310 | 1 | 1035.5833 | 1035.5833 | 0.00063245 | 6.1072e-05
2013-02-24 | 515:35197 | LONG RURAL | Equipment Failure | 941320 | 280 | 1108 | 77381 | 0.047258 | 0.0171
2013-02-24 | ZN1673:PA7 | URBAN | Vegetation | 941322 | 1 | 635.5333 | 635.5333 | 0.00038813 | 6.1072e-05
2013-02-24 | ZN15006:PA9 | URBAN | Vegetation | 941323 | 222 | 400 | 88800 | 0.054232 | 0.013558
2013-02-23 | ZN847:PA10 | URBAN | Other | 941327 | 27 | 646 | 17442 | 0.010652 | 0.0016489
2013-02-24 | ZN10999:PA12 | URBAN | Vegetation | 941328 | 31 | 167.6167 | 5196.1167 | 0.0031734 | 0.0018932
2013-02-24 | ZN1788:PA17 | URBAN | Equipment Failure | 941329 | 1 | 627.2667 | 627.2667 | 0.00038309 | 6.1072e-05
2013-02-24 | ZN12650:PA17 | URBAN | Vegetation | 941343 | 1 | 637.8167 | 637.8167 | 0.00038953 | 6.1072e-05
2013-02-24 | 225:13446 | URBAN | Other | 941345 | 81 | 372 | 30132 | 0.018402 | 0.0049468
2013-02-24 | ZN5868:PA14 | URBAN | Other | 941352 | 53 | 751.1167 | 39809.1833 | 0.024312 | 0.0032368
2013-02-24 | ZN3472:PA11 | URBAN | Equipment Failure | 941354 | 55 | 519.95 | 28597.25 | 0.017465 | 0.003359
2013-02-24 | ZN269:PA2 | URBAN | Vegetation | 941356 | 108 | 459.6333 | 49640.4 | 0.030316 | 0.0065958
2013-02-24 | ZN10996:PA20 | URBAN | Vegetation | 941357 | 279 | 60 | 16740 | 0.010223 | 0.017039
2013-02-24 | ZN1788:PA30 | URBAN | Vegetation | 941358 | 1 | 278.3833 | 278.3833 | 0.00017001 | 6.1072e-05
2013-02-24 | ZN262:PA29 | URBAN | Third Party Impacts | 941359 | 1 | 638.2333 | 638.2333 | 0.00038978 | 6.1072e-05
2013-02-24 | ZN398:PA10 | URBAN | Vegetation | 941361 | 1 | 968.0667 | 968.0667 | 0.00059122 | 6.1072e-05
2013-02-24 | ZN262:PA17 | URBAN | Vegetation | 941364 | 79 | 143.9 | 11368.1 | 0.0069427 | 0.0048247
2013-02-24 | ZN10993:PA2 | URBAN | Vegetation | 941367 | 2 | 726.1167 | 1436.15 | 0.00087709 | 0.00012214
2013-02-24 | ZN10999:PA24 | URBAN | Vegetation | 941367 | 1 | 726.1167 | 697.3667 | 0.0004259 | 6.1072e-05
2013-02-24 | ZN1788:PA30 | URBAN | Vegetation | 941371 | 148 | 739 | 109372 | 0.066796 | 0.0090387
2013-02-24 | ZN1788:PA30 | URBAN | Third Party Impacts | 941373 | 63 | 739 | 46557 | 0.028433 | 0.0038475
2013-02-24 | ZN35600:PA14 | URBAN | Other | 941379 | 105 | 327.3667 | 34373.5 | 0.020993 | 0.0064126
2013-02-24 | ZN1788:PA30 | URBAN | Vegetation | 941389 | 1 | 914.15 | 914.15 | 0.00055829 | 6.1072e-05
2013-02-24 | ZN2310:PA11 | URBAN | Other | 941395 | 1 | 3475.5667 | 3475.5667 | 0.0021226 | 6.1072e-05
2013-02-24 | ZN3155:PA19 | URBAN | Vegetation | 941397 | 11 | 716 | 7876 | 0.00481 | 0.00067179
2013-02-24 | ZN1788:PA30 | URBAN | Other | 941398 | 1 | 205.2 | 205.2 | 0.00012532 | 6.1072e-05
2013-02-24 | ZN2568:PA16 | URBAN | Weather | 941405 | 1 | 530.8833 | 530.8833 | 0.00032422 | 6.1072e-05
2013-02-24 | ZN36300:PA5 | URBAN | Vegetation | 941408 | 1 | 814.8833 | 814.8833 | 0.00049767 | 6.1072e-05
2013-02-24 | ZN9900:PA19 | URBAN | Vegetation | 941409 | 1 | 509.7833 | 509.7833 | 0.00031134 | 6.1072e-05
2013-02-24 | ZN12570:PA25 | SHORT RURAL | Other | 941412 | 1 | 483.8833 | 483.8833 | 0.00029552 | 6.1072e-05
2013-02-24 | ZN1290:PA12 | URBAN | Vegetation | 941414 | 199 | 812 | 161333.2 | 0.09853 | 0.012153
2013-02-24 | ZN9700:PA11 | URBAN | Other | 941416 | 1 | 647.2667 | 647.2667 | 0.0003953 | 6.1072e-05
2013-02-24 | ZN1287:PA5 | URBAN | Vegetation | 941419 | 63 | 1105 | 69615 | 0.042515 | 0.0038475
2013-02-24 | ZN1164:PA10 | URBAN | Vegetation | 941421 | 38 | 1054.2833 | 39102.2667 | 0.023881 | 0.0023207
2013-02-24 | ZN1164:PA27 | URBAN | Vegetation | 941421 | 16 | 1054.2833 | 15440 | 0.0094295 | 0.00097716
2013-02-24 | ZN35370:PA4 | URBAN | Vegetation | 941423 | 10 | 1215 | 12150 | 0.0074203 | 0.00061072
2013-02-24 | ZN188:PA18 | URBAN | Equipment Failure | 941425 | 87 | 933.6167 | 81224.65 | 0.049606 | 0.0053133
2013-02-24 | ZN1788:PA8 | URBAN | Other | 941428 | 1 | 191.8833 | 191.8833 | 0.00011719 | 6.1072e-05
2013-02-24 | ZN3154:PA13 | URBAN | Vegetation | 941430 | 1 | 1151.5167 | 1151.5167 | 0.00070326 | 6.1072e-05
2013-02-24 | ZN269:PA1 | URBAN | Vegetation | 941434 | 87 | 546 | 47282 | 0.028876 | 0.0053133
2013-02-24 | ZN2568:PA16 | URBAN | Weather | 941439 | 1 | 518.5167 | 518.5167 | 0.00031667 | 6.1072e-05
2013-02-24 | ZN1788:PA30 | URBAN | Vegetation | 941451 | 1 | 888.7167 | 888.7167 | 0.00054276 | 6.1072e-05
2013-02-24 | ZN1788:PA36 | URBAN | Vegetation | 941454 | 1 | 920.95 | 920.95 | 0.00056244 | 6.1072e-05
2013-02-24 | ZN1788:PA30 | URBAN | Vegetation | 941458 | 1 | 886.0333 | 886.0333 | 0.00054112 | 6.1072e-05
2013-02-24 | ZN10999:PA15 | URBAN | Vegetation | 941469 | 1 | 671.0167 | 671.0167 | 0.0004098 | 6.1072e-05
2013-02-24 | ZN2400:PA26 | URBAN | Equipment Failure | 941473 | 1 | 1127.25 | 1127.25 | 0.00068844 | 6.1072e-05
2013-02-24 | ZN262:PA31 | URBAN | Vegetation | 941478 | 1 | 861.85 | 861.85 | 0.00052635 | 6.1072e-05
2013-02-24 | ZN10991:PA5 | URBAN | Vegetation | 941480 | 1 | 591.0333 | 591.0333 | 0.00036096 | 6.1072e-05
2013-02-24 | ZN9900:PA8 | URBAN | Other | 941485 | 43 | 478.5 | 20575.5 | 0.012566 | 0.0026261
2013-02-24 | ZN9245:PA13 | URBAN | Vegetation | 941486 | 1 | 497.5167 | 497.5167 | 0.00030384 | 6.1072e-05
2013-02-23 | ZN12650:PA1 | SHORT RURAL | Vegetation | 941492 | 100 | 1202 | 69646 | 0.042534 | 0.0061072
2013-02-24 | ZN10993:PA2 | URBAN | Vegetation | 941501 | 1 | 668.1 | 668.1 | 0.00040802 | 6.1072e-05
2013-02-24 | ZN1788:PA8 | URBAN | Weather | 941510 | 43 | 1239.6167 | 53303.5167 | 0.032554 | 0.0026261
2013-02-24 | 258:80784 | URBAN | Other | 941513 | 1 | 358.1 | 358.1 | 0.0002187 | 6.1072e-05
2013-02-24 | ZN10993:PA2 | URBAN | Vegetation | 941525 | 64 | 693 | 44352 | 0.027087 | 0.0039086
2013-02-24 | ZN9550:PA9 | URBAN | Vegetation | 941531 | 51 | 515 | 26265 | 0.016041 | 0.0031147
2013-02-24 | ZN269:PA3 | URBAN | Vegetation | 941536 | 64 | 559.5 | 35808 | 0.021869 | 0.0039086
2013-02-24 | ZN15008:PA9 | URBAN | Vegetation | 941546 | 36 | 278.1167 | 10012.2 | 0.0061147 | 0.0021986
2013-02-24 | ZN1788:PA14 | URBAN | Vegetation | 941550 | 1 | 789.6 | 789.6 | 0.00048223 | 6.1072e-05
2013-02-24 | ZN2400:PA15 | URBAN | Vegetation | 941555 | 108 | 667 | 72036 | 0.043994 | 0.0065958
2013-02-24 | 258:80785 | URBAN | Other | 941557 | 45 | 159.7 | 7186.5 | 0.004389 | 0.0027482
2013-02-24 | ZN965:PA11 | URBAN | Vegetation | 941558 | 1 | 683.3833 | 683.3833 | 0.00041736 | 6.1072e-05
2013-02-24 | ZN2568:PA16 | URBAN | Vegetation | 941565 | 1 | 191.5333 | 191.5333 | 0.00011697 | 6.1072e-05
2013-02-24 | ZN847:PA18 | URBAN | Other | 941566 | 1 | 863.7333 | 863.7333 | 0.0005275 | 6.1072e-05
2013-02-24 | ZN9118:PA8 | URBAN | Vegetation | 941572 | 32 | 179.4833 | 5743.4667 | 0.0035077 | 0.0019543
2013-02-24 | ZN965:PA21 | URBAN | Equipment Failure | 941595 | 1 | 847.2 | 847.2 | 0.0005174 | 6.1072e-05
2013-02-24 | ZN12630:PA1 | SHORT RURAL | Vegetation | 941604 | 2 | 1884 | 3768 | 0.0023012 | 0.00012214
2013-02-24 | ZN10999:PA12 | URBAN | Equipment Failure | 941608 | 31 | 324.8 | 10068.8 | 0.0061492 | 0.0018932
2013-02-24 | ZN12690:PA24 | SHORT RURAL | Equipment Failure | 941617 | 74 | 702 | 24291 | 0.014835 | 0.0045193
2013-02-23 | ZN15010:PA7 | URBAN | Equipment Failure | 941628 | 1 | 544.1333 | 544.1333 | 0.00033231 | 6.1072e-05
2013-02-24 | 502:48001 | URBAN | Equipment Failure | 941631 | 1 | 192.7833 | 192.7833 | 0.00011774 | 6.1072e-05
2013-02-24 | ZN15004:PA3 | URBAN | Vegetation | 941649 | 45 | 616.8 | 25314.6333 | 0.01546 | 0.0027482
2013-02-24 | ZN15010:PA7 | URBAN | Other | 941651 | 63 | 348.9833 | 21985.95 | 0.013427 | 0.0038475
2013-02-24 | 258:80779 | URBAN | Other | 941660 | 1 | 167.9167 | 167.9167 | 0.00010255 | 6.1072e-05
2013-02-24 | ZN2568:PA16 | URBAN | Vegetation | 941664 | 1 | 926.85 | 926.85 | 0.00056605 | 6.1072e-05
2013-02-24 | ZN9550:PA33 | URBAN | Vegetation | 941674 | 31 | 392.2833 | 12160.7833 | 0.0074269 | 0.0018932
2013-02-24 | ZN36300:PA11 | URBAN | Vegetation | 941678 | 1 | 410.2333 | 410.2333 | 0.00025054 | 6.1072e-05
2013-02-24 | ZN35600:PA9 | URBAN | Equipment Failure | 941688 | 1 | 434.4833 | 434.4833 | 0.00026535 | 6.1072e-05
2013-02-24 | ZN12640:PA8 | SHORT RURAL | Other | 941691 | 25 | 502.9667 | 12574.1667 | 0.0076793 | 0.0015268
2013-02-24 | ZN2400:PA18 | SHORT RURAL | Vegetation | 941704 | 1 | 694.2833 | 694.2833 | 0.00042401 | 6.1072e-05
2013-02-24 | ZN15010:PA9 | SHORT RURAL | Vegetation | 941711 | 1 | 571.6 | 571.6 | 0.00034909 | 6.1072e-05
2013-02-24 | ZN269:PA3 | URBAN | Vegetation | 941713 | 1 | 256.0667 | 256.0667 | 0.00015639 | 6.1072e-05
2013-02-24 | ZN12570:PA39 | URBAN | Other | 941720 | 1 | 369.3333 | 369.3333 | 0.00022556 | 6.1072e-05
2013-02-24 | ZN12610:PA22 | URBAN | Other | 941742 | 1 | 74.35 | 74.35 | 4.5407e-05 | 6.1072e-05
2013-02-24 | ZN847:PA22 | SHORT RURAL | Other | 941743 | 1 | 527.2167 | 527.2167 | 0.00032198 | 6.1072e-05
2013-02-24 | ZN1164:PA21 | URBAN | Weather | 941751 | 74 | 448.05 | 33155.7 | 0.020249 | 0.0045193
2013-02-24 | 261:81879 | URBAN | Other | 941755 | 1 | 244.4833 | 244.4833 | 0.00014931 | 6.1072e-05
2013-02-24 | ZN195:PA29 | URBAN | Vegetation | 941767 | 1 | 929.3 | 929.3 | 0.00056754 | 6.1072e-05
2013-02-24 | ZN12630:PA3 | SHORT RURAL | Vegetation | 941775 | 1 | 1555.2167 | 1555.2167 | 0.00094981 | 6.1072e-05
2013-02-24 | ZN180:PA34 | URBAN | Other | 941783 | 1 | 1130.4167 | 1130.4167 | 0.00069037 | 6.1072e-05
2013-02-24 | 260:33353 | URBAN | Other | 941789 | 1 | 437.1333 | 437.1333 | 0.00026697 | 6.1072e-05
2013-02-24 | ZN12660:PA10 | SHORT RURAL | Vegetation | 941794 | 1 | 326.8167 | 326.8167 | 0.00019959 | 6.1072e-05
2013-02-24 | 243:80084 | SHORT RURAL | Other | 941801 | 1 | 123.3333 | 123.3333 | 7.5322e-05 | 6.1072e-05
2013-02-24 | ZN12650:PA1 | SHORT RURAL | Other | 941802 | 1 | 1722.7833 | 1722.7833 | 0.0010521 | 6.1072e-05
2013-02-24 | ZN847:PA18 | URBAN | Vegetation | 941820 | 26 | 445.8333 | 11591.6667 | 0.0070793 | 0.0015879
2013-02-24 | ZN965:PA33 | URBAN | Vegetation | 941828 | 1 | 743.1167 | 743.1167 | 0.00045384 | 6.1072e-05
2013-02-24 | ZN2400:PA15 | URBAN | Other | 941829 | 69 | 272.4333 | 18797.9 | 0.01148 | 0.004214
2013-02-24 | ZN269:PA3 | URBAN | Vegetation | 941835 | 72 | 194.4833 | 14002.8 | 0.0085518 | 0.0043972
2013-02-23 | ZN12650:PA13 | SHORT RURAL | Equipment Failure | 941836 | 1733 | 1255 | 591057 | 0.36097 | 0.10584
2013-02-24 | 224:80337 | URBAN | Vegetation | 941844 | 1 | 535.9 | 535.9 | 0.00032729 | 6.1072e-05
2013-02-24 | ZN15010:PA11 | URBAN | Equipment Failure | 941862 | 1 | 349.3 | 349.3 | 0.00021333 | 6.1072e-05
2013-02-24 | ZN1193:PA9 | URBAN | Vegetation | 941869 | 1 | 529.9667 | 529.9667 | 0.00032366 | 6.1072e-05
2013-02-24 | ZN847:PA46 | URBAN | Equipment Failure | 941870 | 1 | 447.5167 | 447.5167 | 0.00027331 | 6.1072e-05
2013-02-24 | ZN12600:PA13 | SHORT RURAL | Other | 941882 | 1 | 191.5833 | 191.5833 | 0.000117 | 6.1072e-05
2013-02-24 | ZN12660:PA14 | SHORT RURAL | Equipment Failure | 941884 | 1 | 1362 | 1362 | 0.0008318 | 6.1072e-05
2013-02-24 | ZN35600:PA1 | URBAN | Weather | 941901 | 38 | 836.5833 | 31790.1667 | 0.019415 | 0.0023207
2013-02-24 | 504:48026 | SHORT RURAL | Vegetation | 941907 | 1 | 285.8167 | 285.8167 | 0.00017455 | 6.1072e-05
2013-02-24 | ZN3922:PA26 | URBAN | Vegetation | 941917 | 1 | 597.5833 | 597.5833 | 0.00036496 | 6.1072e-05
2013-02-24 | 242:81539 | URBAN | Equipment Failure | 941928 | 1 | 604.0333 | 604.0333 | 0.0003689 | 6.1072e-05
2013-02-24 | ZN398:PA10 | URBAN | Vegetation | 941931 | 43 | 573 | 24639 | 0.015048 | 0.0026261
2013-02-24 | ZN9245:PA8 | SHORT RURAL | Vegetation | 941934 | 37 | 97.0667 | 3591.4667 | 0.0021934 | 0.0022597
2013-02-24 | ZN14143:PA17 | SHORT RURAL | Vegetation | 941952 | 1 | 308.3 | 308.3 | 0.00018829 | 6.1072e-05
2013-02-24 | ZN269:PA18 | URBAN | Equipment Failure | 941953 | 61 | 514.1333 | 31362.1333 | 0.019154 | 0.0037254
2013-02-24 | ZN2400:PA18 | SHORT RURAL | Vegetation | 941965 | 1 | 572.4 | 572.4 | 0.00034958 | 6.1072e-05
2013-02-24 | ZN14144:PA10 | SHORT RURAL | Vegetation | 941971 | 1 | 516.1 | 516.1 | 0.00031519 | 6.1072e-05
2013-02-24 | ZN3154:PA19 | URBAN | Vegetation | 941989 | 1 | 537.3833 | 537.3833 | 0.00032819 | 6.1072e-05
2013-02-24 | ZN14891:PA10 | SHORT RURAL | Other | 941994 | 1 | 727.25 | 727.25 | 0.00044415 | 6.1072e-05
2013-02-24 | ZN14143:PA17 | SHORT RURAL | Vegetation | 942023 | 1 | 1393.7833 | 1393.7833 | 0.00085121 | 6.1072e-05
2013-02-24 | ZN1164:PA4 | URBAN | Weather | 942040 | 33 | 349.9667 | 11548.9 | 0.0070532 | 0.0020154
2013-02-24 | ZN180:PA42 | URBAN | Vegetation | 942055 | 1 | 531.1333 | 531.1333 | 0.00032437 | 6.1072e-05
2013-02-24 | ZN3922:PA11 | URBAN | Other | 942061 | 56 | 323.4 | 18110.4 | 0.01106 | 0.00342
2013-02-24 | ZN874:PA12 | URBAN | Other | 942119 | 1 | 694.4 | 694.4 | 0.00042409 | 6.1072e-05
2013-02-24 | ZN2400:PA11 | SHORT RURAL | Vegetation | 942120 | 1 | 1410.45 | 1410.45 | 0.00086139 | 6.1072e-05
2013-02-23 | ZN14143:PA12 | SHORT RURAL | Vegetation | 942128 | 1 | 2299.4333 | 2299.4333 | 0.0014043 | 6.1072e-05
2013-02-24 | ZN14891:PA12 | SHORT RURAL | Other | 942132 | 1 | 206.7667 | 206.7667 | 0.00012628 | 6.1072e-05
2013-02-24 | ZN12570:PA33 | SHORT RURAL | Other | 942148 | 1 | 154.0333 | 154.0333 | 9.4072e-05 | 6.1072e-05
2013-02-24 | 227:13020 | SHORT RURAL | Other | 942155 | 1 | 271.5 | 271.5 | 0.00016581 | 6.1072e-05
2013-02-24 | ZN35370:PA2 | SHORT RURAL | Vegetation | 942165 | 17 | 990 | 16830 | 0.010278 | 0.0010382
2013-02-24 | 234:2001 | URBAN | Vegetation | 942166 | 1 | 161.5167 | 161.5167 | 9.8642e-05 | 6.1072e-05
2013-02-24 | ZN1850:PA13 | URBAN | Equipment Failure | 942167 | 1 | 431.2667 | 431.2667 | 0.00026338 | 6.1072e-05
2013-02-24 | 504:48033 | SHORT RURAL | Equipment Failure | 942190 | 4 | 120 | 480 | 0.00029315 | 0.00024429
2013-02-24 | ZN965:PA11 | URBAN | Other | 942200 | 26 | 47.0667 | 1223.7333 | 0.00074736 | 0.0015879
2013-02-24 | 208:58 | URBAN | Other | 942207 | 1 | 250.35 | 250.35 | 0.00015289 | 6.1072e-05
2013-02-24 | ZN12570:PA24 | SHORT RURAL | Other | 942222 | 1 | 369.15 | 369.15 | 0.00022545 | 6.1072e-05
2013-02-24 | ZN2400:PA15 | URBAN | Vegetation | 942237 | 23 | 143 | 3289 | 0.0020087 | 0.0014047
2013-02-24 | 260:33353 | URBAN | Other | 942244 | 1 | 427.5667 | 427.5667 | 0.00026112 | 6.1072e-05
2013-02-24 | ZN12690:PA12 | SHORT RURAL | Other | 942245 | 1 | 547.4833 | 547.4833 | 0.00033436 | 6.1072e-05
2013-02-24 | ZN2400:PA18 | SHORT RURAL | Vegetation | 942254 | 44 | 75 | 3300 | 0.0020154 | 0.0026872
2013-02-24 | ZN12570:PA41 | URBAN | Third Party Impacts | 942257 | 1 | 290.7333 | 290.7333 | 0.00017756 | 6.1072e-05
2013-02-24 | 227:13020 | SHORT RURAL | Vegetation | 942263 | 73 | 164 | 11972 | 0.0073116 | 0.0044583
2013-02-24 | 243:80080 | SHORT RURAL | Other | 942272 | 1 | 130.4833 | 130.4833 | 7.9689e-05 | 6.1072e-05
2013-02-24 | 229:34989 | SHORT RURAL | Equipment Failure | 942273 | 1 | 395.4667 | 395.4667 | 0.00024152 | 6.1072e-05
2013-02-24 | ZN12660:PA14 | SHORT RURAL | Vegetation | 942335 | 1 | 371.0167 | 371.0167 | 0.00022659 | 6.1072e-05
2013-02-24 | ZN847:PA2 | URBAN | Other | 942340 | 1 | 193.15 | 193.15 | 0.00011796 | 6.1072e-05
2013-02-24 | ZN9900:PA8 | URBAN | Equipment Failure | 942351 | 43 | 280.1 | 12044.3 | 0.0073557 | 0.0026261
2013-02-24 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 942365 | 1 | 1486.3167 | 1486.3167 | 0.00090773 | 6.1072e-05
2013-02-24 | ZN2400:PA26 | URBAN | Vegetation | 942383 | 1 | 1199.6667 | 1199.6667 | 0.00073266 | 6.1072e-05
2013-02-23 | ZN12630:PA1 | SHORT RURAL | Vegetation | 942390 | 12 | 2908 | 34896 | 0.021312 | 0.00073287
2013-02-24 | ZN12640:PA15 | URBAN | Vegetation | 942405 | 53 | 203 | 10759 | 0.0065708 | 0.0032368
2013-02-24 | ZN10996:PA8 | URBAN | Vegetation | 942417 | 1 | 35.9167 | 35.9167 | 2.1935e-05 | 6.1072e-05
2013-02-24 | 227:13015 | SHORT RURAL | Other | 942424 | 1 | 107.3 | 107.3 | 6.553e-05 | 6.1072e-05
2013-02-24 | ZN12570:PA37 | SHORT RURAL | Other | 942427 | 1 | 1728.9833 | 1728.9833 | 0.0010559 | 6.1072e-05
2013-02-24 | ZN965:PA6 | URBAN | Vegetation | 942443 | 34 | 35 | 1190 | 0.00072676 | 0.0020765
2013-02-24 | 220:8689 | URBAN | Other | 942449 | 1 | 500.4833 | 500.4833 | 0.00030566 | 6.1072e-05
2013-02-24 | 228:7490 | SHORT RURAL | Vegetation | 942454 | 1 | 376.0333 | 376.0333 | 0.00022965 | 6.1072e-05
2013-02-24 | ZN9900:PA3 | URBAN | Equipment Failure | 942462 | 1 | 1074.6667 | 1074.6667 | 0.00065632 | 6.1072e-05
2013-02-24 | ZN167:PA21 | URBAN | Equipment Failure | 942471 | 1 | 161.9 | 161.9 | 9.8876e-05 | 6.1072e-05
2013-02-24 | ZN965:PA47 | URBAN | Vegetation | 942475 | 51 | 249.35 | 12716.85 | 0.0077665 | 0.0031147
2013-02-24 | ZN2400:PA18 | SHORT RURAL | Other | 942477 | 1 | 182.6333 | 182.6333 | 0.00011154 | 6.1072e-05
2013-02-24 | 213:33774 | URBAN | Other | 942479 | 1 | 230.95 | 230.95 | 0.00014105 | 6.1072e-05
2013-02-24 | 513:48059 | SHORT RURAL | Other | 942499 | 1 | 369 | 369 | 0.00022536 | 6.1072e-05
2013-02-24 | ZN12630:PA1 | SHORT RURAL | Equipment Failure | 942504 | 1 | 1228.9667 | 1228.9667 | 0.00075056 | 6.1072e-05
2013-02-24 | ZN2400:PA18 | SHORT RURAL | Vegetation | 942506 | 1 | 232.7333 | 232.7333 | 0.00014214 | 6.1072e-05
2013-02-24 | ZN1164:PA9 | URBAN | Vegetation | 942513 | 32 | 115.9833 | 3711.4667 | 0.0022667 | 0.0019543
2013-02-24 | ZN2400:PA15 | URBAN | Vegetation | 942541 | 1 | 1317.4833 | 1317.4833 | 0.00080462 | 6.1072e-05
2013-02-24 | ZN2400:PA15 | URBAN | Other | 942543 | 1 | 251.3667 | 251.3667 | 0.00015352 | 6.1072e-05
2013-02-24 | ZN9700:PA23 | URBAN | Vegetation | 942546 | 1 | 123.9 | 123.9 | 7.5668e-05 | 6.1072e-05
2013-02-24 | ZN2568:PA26 | URBAN | Equipment Failure | 942547 | 1 | 78.9167 | 78.9167 | 4.8196e-05 | 6.1072e-05
2013-02-24 | ZN965:PA2 | URBAN | Vegetation | 942557 | 1 | 302.2833 | 302.2833 | 0.00018461 | 6.1072e-05
2013-02-24 | ZN3155:PA19 | URBAN | Vegetation | 942567 | 1 | 198.6833 | 198.6833 | 0.00012134 | 6.1072e-05
2013-02-24 | ZN3154:PA19 | URBAN | Vegetation | 942571 | 1 | 571.15 | 571.15 | 0.00034881 | 6.1072e-05
2013-02-24 | 203:8084 | URBAN | Vegetation | 942576 | 1 | 98.7167 | 98.7167 | 6.0288e-05 | 6.1072e-05
2013-02-24 | ZN3425:PA12 | URBAN | Vegetation | 942599 | 41 | 30 | 1230 | 0.00075119 | 0.002504
2013-02-24 | ZN12630:PA5 | SHORT RURAL | Other | 942605 | 1 | 1373.6667 | 1373.6667 | 0.00083893 | 6.1072e-05
2013-02-24 | 227:13020 | SHORT RURAL | Vegetation | 942633 | 58 | 96.4333 | 5593.1333 | 0.0034159 | 0.0035422
2013-02-24 | ZN14144:PA7 | SHORT RURAL | Vegetation | 942662 | 1 | 1414 | 1414 | 0.00086356 | 6.1072e-05
2013-02-24 | 243:80083 | SHORT RURAL | Other | 942672 | 4 | 98.8 | 395.2 | 0.00024136 | 0.00024429
2013-02-24 | 510:48164 | SHORT RURAL | Other | 942676 | 1 | 331.6333 | 331.6333 | 0.00020254 | 6.1072e-05
2013-02-24 | ZN15012:PA6 | URBAN | Vegetation | 942690 | 90 | 105 | 9450 | 0.0057713 | 0.0054965
2013-02-24 | ZN15012:PA6 | URBAN | Vegetation | 942695 | 28 | 105 | 2940 | 0.0017955 | 0.00171
2013-02-24 | ZN2400:PA22 | URBAN | Equipment Failure | 942696 | 1 | 125.7 | 125.7 | 7.6768e-05 | 6.1072e-05
2013-02-24 | 509:48039 | LONG RURAL | Other | 942705 | 40 | 223 | 8920 | 0.0054476 | 0.0024429
2013-02-24 | ZN2400:PA15 | URBAN | Vegetation | 942708 | 1 | 81.5667 | 81.5667 | 4.9815e-05 | 6.1072e-05
2013-02-24 | ZN12570:PA37 | SHORT RURAL | Vegetation | 942714 | 1 | 154.5167 | 154.5167 | 9.4367e-05 | 6.1072e-05
2013-02-24 | ZN965:PA11 | URBAN | Vegetation | 942722 | 1 | 114.5 | 114.5 | 6.9928e-05 | 6.1072e-05
2013-02-24 | ZN1164:PA4 | URBAN | Other | 942737 | 1 | 252.9833 | 252.9833 | 0.0001545 | 6.1072e-05
2013-02-24 | ZN9252:PA10 | URBAN | Equipment Failure | 942759 | 1 | 284.5333 | 284.5333 | 0.00017377 | 6.1072e-05
2013-02-24 | 812:19066 | SHORT RURAL | Other | 942760 | 1 | 122.8167 | 122.8167 | 7.5007e-05 | 6.1072e-05
2013-02-24 | 812:19066 | SHORT RURAL | Other | 942765 | 1 | 114.7167 | 114.7167 | 7.006e-05 | 6.1072e-05
2013-02-23 | ZN15001:PA2 | URBAN | Vegetation | 942803 | 18 | 35 | 630 | 0.00038475 | 0.0010993
2013-02-24 | ZN3154:PA19 | URBAN | Equipment Failure | 942818 | 1 | 692.7333 | 692.7333 | 0.00042307 | 6.1072e-05
2013-02-25 | ZN2602:PA30 | URBAN | Other | 942871 | 1 | 219.7167 | 219.7167 | 0.00013419 | 6.1072e-05
2013-02-25 | ZN2400:PA15 | URBAN | Equipment Failure | 942881 | 1 | 410.75 | 410.75 | 0.00025085 | 6.1072e-05
2013-02-25 | ZN2400:PA18 | SHORT RURAL | Vegetation | 942890 | 8 | 575 | 4600 | 0.0028093 | 0.00048858
2013-02-25 | ZN12630:PA1 | SHORT RURAL | Vegetation | 942896 | 1 | 320.0833 | 320.0833 | 0.00019548 | 6.1072e-05
2013-02-25 | ZN80:PA32 | URBAN | Equipment Failure | 942907 | 77 | 110.6667 | 8521.3333 | 0.0052042 | 0.0047026
2013-02-25 | ZN12630:PA3 | SHORT RURAL | Other | 942908 | 1 | 460.5667 | 460.5667 | 0.00028128 | 6.1072e-05
2013-02-25 | ZN965:PA37 | URBAN | Equipment Failure | 942933 | 15 | 55 | 825 | 0.00050385 | 0.00091608
2013-02-25 | ZN5868:PA14 | URBAN | Other | 942935 | 1 | 53.5667 | 53.5667 | 3.2714e-05 | 6.1072e-05
2013-02-25 | ZN847:PA22 | SHORT RURAL | Vegetation | 942944 | 1 | 127.3833 | 127.3833 | 7.7796e-05 | 6.1072e-05
2013-02-23 | 224:80346 | URBAN | Equipment Failure | 942973 | 62 | 255 | 5745 | 0.0035086 | 0.0037865
2013-02-25 | ZN9037:PA2 | URBAN | Vegetation | 942988 | 1 | 721.8333 | 721.8333 | 0.00044084 | 6.1072e-05
2013-02-25 | ZN14891:PA12 | SHORT RURAL | Vegetation | 942993 | 1 | 153.6333 | 153.6333 | 9.3827e-05 | 6.1072e-05
2013-02-25 | 526:34636 | SHORT RURAL | Other | 942995 | 4 | 423.0333 | 1692.1333 | 0.0010334 | 0.00024429
2013-02-25 | ZN10995:PA7 | URBAN | Other | 943003 | 1 | 77.0667 | 77.0667 | 4.7066e-05 | 6.1072e-05
2013-02-25 | ZN187:PA17 | URBAN | Vegetation | 943044 | 1 | 296.25 | 296.25 | 0.00018093 | 6.1072e-05
2013-02-24 | ZN2400:PA23 | URBAN | Vegetation | 943045 | 11 | 1347 | 14817 | 0.0090491 | 0.00067179
2013-02-25 | ZN12690:PA12 | SHORT RURAL | Other | 943047 | 1 | 262.0667 | 262.0667 | 0.00016005 | 6.1072e-05
2013-02-23 | ZN12630:PA4 | SHORT RURAL | Vegetation | 943063 | 1 | 2598.5 | 2598.5 | 0.001587 | 6.1072e-05
2013-02-25 | ZN384:PA41 | URBAN | Operational Error | 943092 | 5 | 219 | 1095 | 0.00066874 | 0.00030536
2013-02-23 | 230:81432 | URBAN | Equipment Failure | 943103 | 38 | 2436.4667 | 5700 | 0.0034811 | 0.0023207
2013-02-23 | 230:81434 | URBAN | Equipment Failure | 943103 | 1403 | 2436.4667 | 210450 | 0.12853 | 0.085684
2013-02-23 | 230:81438 | SHORT RURAL | Equipment Failure | 943103 | 305 | 2436.4667 | 45750 | 0.027941 | 0.018627
2013-02-23 | 230:81440 | URBAN | Equipment Failure | 943103 | 1586 | 2436.4667 | 363284 | 0.22187 | 0.096861
2013-02-23 | 231:8405 | SHORT RURAL | Equipment Failure | 943103 | 95 | 2436.4667 | 13965 | 0.0085287 | 0.0058019
2013-02-23 | 231:8415 | SHORT RURAL | Equipment Failure | 943103 | 815 | 2436.4667 | 119805 | 0.073168 | 0.049774
2013-02-25 | ZN10999:PA1 | URBAN | Equipment Failure | 943117 | 59 | 61.05 | 3601.95 | 0.0021998 | 0.0036033
2013-02-25 | ZN1068:PA11 | URBAN | Other | 943121 | 1 | 79.1 | 79.1 | 4.8308e-05 | 6.1072e-05
2013-02-24 | ZN35500:PA34 | URBAN | Vegetation | 943133 | 100 | 32 | 3200 | 0.0019543 | 0.0061072
2013-02-24 | ZN12640:PA18 | SHORT RURAL | Vegetation | 943172 | 1 | 1451 | 1451 | 0.00088616 | 6.1072e-05
2013-02-25 | ZN5868:PA14 | URBAN | Equipment Failure | 943191 | 17 | 84 | 1156 | 0.00070599 | 0.0010382
2013-02-25 | ZN80:PA22 | URBAN | Equipment Failure | 943191 | 20 | 84 | 1680 | 0.001026 | 0.0012214
2013-02-25 | ZN80:PA24 | URBAN | Equipment Failure | 943191 | 1430 | 84 | 106752 | 0.065196 | 0.087333
2013-02-22 | 526:34640 | SHORT RURAL | Other | 943214 | 2 | 52 | 104 | 6.3515e-05 | 0.00012214
2013-02-25 | ZN5868:PA14 | URBAN | Equipment Failure | 943221 | 11 | 60 | 660 | 0.00040308 | 0.00067179
2013-02-25 | ZN15004:PA9 | URBAN | Equipment Failure | 943257 | 1 | 133.35 | 133.35 | 8.144e-05 | 6.1072e-05
2013-02-25 | ZN15008:PA5 | URBAN | Equipment Failure | 943266 | 1 | 93.5667 | 93.5667 | 5.7143e-05 | 6.1072e-05
2013-02-25 | ZN14143:PA12 | SHORT RURAL | Vegetation | 943273 | 1 | 306.5 | 306.5 | 0.00018719 | 6.1072e-05
2013-02-25 | ZN1068:PA11 | URBAN | Other | 943304 | 1 | 225.85 | 225.85 | 0.00013793 | 6.1072e-05
2013-02-25 | ZN12570:PA25 | SHORT RURAL | Other | 943318 | 1 | 132.5833 | 132.5833 | 8.0972e-05 | 6.1072e-05
2013-02-25 | ZN12610:PA13 | URBAN | Equipment Failure | 943337 | 2 | 276.7333 | 553.4667 | 0.00033801 | 0.00012214
2013-02-25 | ZN4990:PA51 52KLM | CBD | Other | 943339 | 5 | 51 | 255 | 0.00015573 | 0.00030536
2013-02-25 | ZN4990:PA55 56GHJ | CBD | Other | 943339 | 1396 | 51 | 71196 | 0.043481 | 0.085257
2013-02-25 | 232:11457 | URBAN | Vegetation | 943348 | 1 | 152.0333 | 152.0333 | 9.285e-05 | 6.1072e-05
2013-02-25 | ZN3155:PA18 | URBAN | Equipment Failure | 943387 | 77 | 123 | 9471 | 0.0057841 | 0.0047026
2013-02-25 | 507:80923 | SHORT RURAL | Other | 943389 | 1 | 204.2167 | 204.2167 | 0.00012472 | 6.1072e-05
2013-02-24 | 258:80791 | URBAN | Equipment Failure | 943399 | 792 | 1157 | 63029 | 0.038493 | 0.048369
2013-02-25 | ZN3154:PA19 | URBAN | Vegetation | 943408 | 44 | 80 | 3520 | 0.0021497 | 0.0026872
2013-02-25 | ZN14892:PA21 | URBAN | Equipment Failure | 943419 | 1 | 245.9667 | 245.9667 | 0.00015022 | 6.1072e-05
2013-02-25 | 228:7491 | URBAN | Other | 943420 | 1 | 122.2 | 122.2 | 7.463e-05 | 6.1072e-05
2013-02-24 | ZN12650:PA17 | URBAN | Vegetation | 943421 | 1 | 1544.1167 | 1544.1167 | 0.00094303 | 6.1072e-05
2013-02-25 | ZN1287:PA5 | URBAN | Other | 943429 | 97 | 60 | 5820 | 0.0035544 | 0.005924
2013-02-25 | ZN12570:PA29 | SHORT RURAL | Vegetation | 943441 | 1 | 267.85 | 267.85 | 0.00016358 | 6.1072e-05
2013-02-24 | 238:34141 | SHORT RURAL | Operational Error | 943456 | 1132 | 2 | 2264 | 0.0013827 | 0.069134
2013-02-25 | ZN2473:PA25 | URBAN | Equipment Failure | 943465 | 1305 | 51 | 66555 | 0.040647 | 0.079699
2013-02-25 | ZN12570:PA33 | SHORT RURAL | Other | 943466 | 71 | 261.95 | 18598.45 | 0.011358 | 0.0043361
2013-02-25 | ZN12630:PA1 | SHORT RURAL | Vegetation | 943487 | 364 | 43 | 15652 | 0.009559 | 0.02223
2013-02-25 | ZN10999:PA1 | URBAN | Equipment Failure | 943505 | 59 | 109 | 6431 | 0.0039276 | 0.0036033
2013-02-25 | ZN10999:PA4 | URBAN | Equipment Failure | 943505 | 1 | 109 | 108.9667 | 6.6548e-05 | 6.1072e-05
2013-02-25 | ZN965:PA20 | URBAN | Other | 943521 | 54 | 120 | 6480 | 0.0039575 | 0.0032979
2013-02-25 | ZN80:PA24 | URBAN | Equipment Failure | 943767 | 421 | 142 | 32417 | 0.019798 | 0.025711
2013-02-25 | ZN80:PA37 | URBAN | Equipment Failure | 943767 | 1 | 142 | 77 | 4.7026e-05 | 6.1072e-05
2013-02-25 | ZN80:PA40 | URBAN | Equipment Failure | 943767 | 2500 | 142 | 206280 | 0.12598 | 0.15268
2013-02-25 | ZN2473:PA32 | URBAN | Other | 943773 | 23 | 103.9167 | 2390.0833 | 0.0014597 | 0.0014047
2013-02-25 | 260:33353 | URBAN | Equipment Failure | 943775 | 95 | 128.55 | 10259.1167 | 0.0062655 | 0.0058019
2013-02-25 | ZN80:PA37 | URBAN | Other | 943781 | 1 | 83.85 | 83.85 | 5.1209e-05 | 6.1072e-05
2013-02-25 | ZN14143:PA17 | SHORT RURAL | Other | 943782 | 1 | 655.5 | 655.5 | 0.00040033 | 6.1072e-05
2013-02-26 | ZN14891:PA12 | SHORT RURAL | Vegetation | 943789 | 1 | 485.55 | 485.55 | 0.00029654 | 6.1073e-05
2013-02-26 | ZN1673:PA11 | URBAN | Vegetation | 943792 | 47 | 329.8167 | 15501.3833 | 0.0094672 | 0.0028704
2013-02-26 | ZN10999:PA17 | URBAN | Vegetation | 943795 | 1 | 141.5833 | 141.5833 | 8.6469e-05 | 6.1073e-05
2013-02-26 | ZN4545:PA31 | URBAN | Animals | 943815 | 1183 | 83 | 98189 | 0.059967 | 0.07225
2013-02-26 | ZN3155:PA18 | URBAN | Third Party Impacts | 943853 | 1 | 387.6667 | 387.6667 | 0.00023676 | 6.1073e-05
2013-02-26 | ZN2196:PA11 | URBAN | Other | 943882 | 1 | 113.4 | 113.4 | 6.9257e-05 | 6.1073e-05
2013-02-23 | 504:48031 | SHORT RURAL | Vegetation | 943892 | 133 | 1033 | 50738 | 0.030987 | 0.0081226
2013-02-26 | 810:74054 | LONG RURAL | Equipment Failure | 943903 | 1 | 150 | 150 | 9.161e-05 | 6.1073e-05
2013-02-26 | ZN12570:PA37 | SHORT RURAL | Other | 943919 | 1 | 140.5833 | 140.5833 | 8.5859e-05 | 6.1073e-05
2013-02-24 | ZN2400:PA18 | SHORT RURAL | Other | 943930 | 1 | 164 | 164 | 0.00010016 | 6.1072e-05
2013-02-23 | ZN12630:PA1 | SHORT RURAL | Vegetation | 943952 | 129 | 1937 | 235342 | 0.14373 | 0.0078783
2013-02-26 | ZN15002:PA6 | URBAN | Other | 943973 | 1 | 170.4667 | 170.4667 | 0.00010411 | 6.1073e-05
2013-02-26 | ZN12630:PA1 | SHORT RURAL | Equipment Failure | 943975 | 12 | 360 | 4320 | 0.0026384 | 0.00073288
2013-02-23 | 235:2120 | SHORT RURAL | Equipment Failure | 943976 | 1540 | 847 | 194960 | 0.11907 | 0.094051
2013-02-24 | ZN1850:PA10 | URBAN | Third Party Impacts | 943984 | 18 | 114 | 2052 | 0.0012532 | 0.0010993
2013-02-26 | ZN12610:PA13 | URBAN | Equipment Failure | 944000 | 1 | 394.85 | 394.85 | 0.00024115 | 6.1073e-05
2013-02-26 | ZN3472:PA32 | SHORT RURAL | Other | 944005 | 1 | 250 | 250 | 0.00015268 | 6.1073e-05
2013-02-26 | ZN12630:PA2 | SHORT RURAL | Vegetation | 944006 | 110 | 110 | 12100 | 0.0073899 | 0.0067181
2013-02-24 | ZN3472:PA30 | URBAN | Operational Error | 944029 | 30 | 20 | 600 | 0.00036643 | 0.0018322
2013-02-26 | ZN195:PA22 | URBAN | Vegetation | 944040 | 34 | 402 | 13668 | 0.0083475 | 0.0020765
2013-02-23 | 509:48039 | LONG RURAL | Equipment Failure | 944042 | 55 | 2502 | 137340 | 0.083877 | 0.003359
2013-02-26 | ZN15006:PA9 | URBAN | Equipment Failure | 944046 | 1 | 212.1 | 212.1 | 0.00012954 | 6.1073e-05
2013-02-26 | ZN847:PA1 | URBAN | Third Party Impacts | 944051 | 1 | 208.2 | 208.2 | 0.00012715 | 6.1073e-05
2013-02-26 | ZN3154:PA19 | URBAN | Equipment Failure | 944053 | 1 | 500.3167 | 500.3167 | 0.00030556 | 6.1073e-05
2013-02-24 | ZN3922:PA26 | URBAN | Vegetation | 944166 | 62 | 15 | 930 | 0.00056797 | 0.0037865
2013-02-24 | ZN9900:PA8 | URBAN | Equipment Failure | 944176 | 43 | 45 | 1735 | 0.0010596 | 0.0026261
2013-02-23 | 235:2857 | SHORT RURAL | Operational Error | 944208 | 1 | 2 | 2 | 1.2214e-06 | 6.1072e-05
2013-02-23 | 238:34144 | URBAN | Operational Error | 944208 | 832 | 2 | 1664 | 0.0010162 | 0.050812
2013-02-26 | ZN15013:PA10 | SHORT RURAL | Equipment Failure | 944222 | 488 | 31 | 14534 | 0.0088764 | 0.029804
2013-02-22 | 813:89061 | LONG RURAL | Equipment Failure | 944270 | 1 | 271 | 271 | 0.00016551 | 6.1072e-05
2013-02-26 | ZN965:PA8 | URBAN | Vegetation | 944291 | 1 | 154.1667 | 154.1667 | 9.4155e-05 | 6.1073e-05
2013-02-26 | ZN2473:PA32 | URBAN | Equipment Failure | 944300 | 23 | 130.4 | 2999.2 | 0.0018317 | 0.0014047
2013-02-26 | ZN15001:PA15 | URBAN | Equipment Failure | 944322 | 1 | 151.0833 | 151.0833 | 9.2271e-05 | 6.1073e-05
2013-02-26 | 214:8669 | URBAN | Vegetation | 944326 | 1 | 96.75 | 96.75 | 5.9088e-05 | 6.1073e-05
2013-02-26 | ZN9037:PA9 | URBAN | Vegetation | 944389 | 1 | 175.1167 | 175.1167 | 0.00010695 | 6.1073e-05
2013-02-26 | ZN9037:PA9 | URBAN | Vegetation | 944393 | 1 | 169.25 | 169.25 | 0.00010337 | 6.1073e-05
2013-02-26 | ZN195:PA28 | URBAN | Vegetation | 944405 | 1 | 342.2167 | 342.2167 | 0.000209 | 6.1073e-05
2013-02-26 | ZN2473:PA32 | URBAN | Equipment Failure | 944415 | 23 | 209 | 4807 | 0.0029358 | 0.0014047
2013-02-26 | ZN80:PA40 | URBAN | Vegetation | 944420 | 25 | 3 | 75 | 4.5805e-05 | 0.0015268
2013-02-26 | ZN1850:PA11 | URBAN | Vegetation | 944421 | 1 | 379.6 | 379.6 | 0.00023183 | 6.1073e-05
2013-02-26 | ZN12630:PA3 | SHORT RURAL | Vegetation | 944434 | 1 | 156.5333 | 156.5333 | 9.56e-05 | 6.1073e-05
2013-02-26 | 235:2120 | SHORT RURAL | Other | 944436 | 1 | 117.6 | 117.6 | 7.1822e-05 | 6.1073e-05
2013-02-26 | ZN1285:PA33 | URBAN | Other | 944442 | 1 | 198.2 | 198.2 | 0.00012105 | 6.1073e-05
2013-02-26 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 944445 | 5 | 132.2167 | 661.0833 | 0.00040374 | 0.00030537
2013-02-26 | ZN2400:PA22 | URBAN | Vegetation | 944459 | 36 | 111 | 3996 | 0.0024405 | 0.0021986
2013-02-27 | ZN12580:PA14 | URBAN | Animals | 944479 | 1 | 194.8 | 194.8 | 0.00011897 | 6.1074e-05
2013-02-27 | ZN35600:PA1 | URBAN | Vegetation | 944481 | 38 | 20 | 760 | 0.00046416 | 0.0023208
2013-02-27 | ZN10999:PA1 | URBAN | Equipment Failure | 944486 | 60 | 590.0167 | 32466 | 0.019828 | 0.0036644
2013-02-27 | ZN10999:PA4 | URBAN | Equipment Failure | 944486 | 1 | 590.0167 | 325.1667 | 0.00019859 | 6.1074e-05
2013-02-27 | ZN14892:PA14 | SHORT RURAL | Other | 944489 | 1 | 499.7333 | 499.7333 | 0.00030521 | 6.1074e-05
2013-02-27 | 810:74050 | SHORT RURAL | Other | 944499 | 1 | 277.1333 | 277.1333 | 0.00016926 | 6.1074e-05
2013-02-27 | ZN35500:PA31 | URBAN | Third Party Impacts | 944518 | 65 | 69.6167 | 4525.0833 | 0.0027636 | 0.0039698
2013-02-27 | ZN1193:PA9 | URBAN | Other | 944539 | 24 | 67.6167 | 1622.8 | 0.00099111 | 0.0014658
2013-02-27 | ZN4545:PA4 | URBAN | Equipment Failure | 944579 | 1 | 203.6333 | 203.6333 | 0.00012437 | 6.1074e-05
2013-02-27 | 240:34846 | URBAN | Equipment Failure | 944585 | 1 | 89.4167 | 89.4167 | 5.461e-05 | 6.1074e-05
2013-02-27 | 515:35197 | LONG RURAL | Other | 944586 | 1 | 253.7333 | 253.7333 | 0.00015496 | 6.1074e-05
2013-02-25 | 232:11453 | SHORT RURAL | Operational Error | 944592 | 1276 | 5 | 6380 | 0.0038964 | 0.077928
2013-02-26 | 222:2014 | URBAN | Equipment Failure | 944608 | 1 | 210 | 210 | 0.00012825 | 6.1073e-05
2013-02-26 | 511:29877 | SHORT RURAL | Other | 944614 | 30 | 180 | 5400 | 0.003298 | 0.0018322
2013-02-27 | 813:89063 | SHORT RURAL | Other | 944676 | 1 | 122.7 | 122.7 | 7.4938e-05 | 6.1074e-05
2013-02-27 | ZN1285:PA31 | URBAN | Equipment Failure | 944786 | 246 | 51 | 12546 | 0.0076623 | 0.015024
2013-02-27 | 813:89062 | SHORT RURAL | Other | 944808 | 1 | 82.8 | 82.8 | 5.0569e-05 | 6.1074e-05
2013-02-27 | ZN9900:PA13 | URBAN | Equipment Failure | 944810 | 35 | 65.05 | 2276.75 | 0.0013905 | 0.0021376
2013-02-27 | ZN3154:PA23 | URBAN | Other | 944852 | 1 | 83.4833 | 83.4833 | 5.0987e-05 | 6.1074e-05
2013-02-27 | ZN342:PA26 | URBAN | Third Party Impacts | 944881 | 1 | 267.5833 | 267.5833 | 0.00016342 | 6.1074e-05
2013-02-27 | ZN3154:PA24 | URBAN | Vegetation | 944898 | 55 | 126.2667 | 6944.6667 | 0.0042414 | 0.0033591
2013-02-27 | ZN116:PA47 | URBAN | Other | 944972 | 1 | 319.8667 | 319.8667 | 0.00019536 | 6.1074e-05
2013-02-27 | 507:80923 | SHORT RURAL | Equipment Failure | 944987 | 1 | 284 | 284 | 0.00017345 | 6.1074e-05
2013-02-27 | 256:80644 | URBAN | Other | 945000 | 1 | 144.1333 | 144.1333 | 8.8028e-05 | 6.1074e-05
2013-02-27 | ZN1285:PA27 | URBAN | Equipment Failure | 945015 | 2366 | 132 | 307854 | 0.18802 | 0.1445
2013-02-27 | ZN1285:PA31 | URBAN | Equipment Failure | 945015 | 246 | 132 | 32472 | 0.019832 | 0.015024
2013-02-27 | ZN9118:PA20 | URBAN | Third Party Impacts | 945017 | 1 | 271.9 | 271.9 | 0.00016606 | 6.1074e-05
2013-02-27 | ZN1788:PA2 | URBAN | Vegetation | 945024 | 1 | 112.7333 | 112.7333 | 6.8851e-05 | 6.1074e-05
2013-02-27 | ZN342:PA18 | URBAN | Operational Error | 945037 | 31 | 305 | 9455 | 0.0057745 | 0.0018933
2013-02-27 | ZN2310:PA38 | URBAN | Other | 945058 | 22 | 135 | 2970 | 0.0018139 | 0.0013436
2013-02-27 | ZN1164:PA9 | URBAN | Vegetation | 945064 | 32 | 244 | 7808 | 0.0047687 | 0.0019544
2013-02-28 | ZN3154:PA17 | URBAN | Animals | 945067 | 32 | 64 | 2048 | 0.0012508 | 0.0019544
2013-02-28 | ZN2473:PA9 | URBAN | Equipment Failure | 945069 | 49 | 46 | 2254 | 0.0013766 | 0.0029926
2013-02-27 | 523:33501 | SHORT RURAL | Other | 945096 | 2 | 90 | 180 | 0.00010993 | 0.00012215
2013-02-28 | ZN690:PA25 | URBAN | Equipment Failure | 945114 | 1 | 1584.6 | 1584.6 | 0.00096778 | 6.1074e-05
2013-02-28 | 256:80640 | URBAN | Third Party Impacts | 945132 | 106 | 100 | 10600 | 0.0064739 | 0.0064739
2013-02-28 | ZN398:PA24 | URBAN | Equipment Failure | 945153 | 1 | 104.7333 | 104.7333 | 6.3965e-05 | 6.1074e-05
2013-02-28 | ZN1673:PA1 | URBAN | Third Party Impacts | 945203 | 1 | 148.3 | 148.3 | 9.0573e-05 | 6.1074e-05
2013-02-28 | 214:8665 | URBAN | Other | 945221 | 1 | 38.55 | 38.55 | 2.3544e-05 | 6.1074e-05
2013-02-28 | ZN15013:PA2 | URBAN | Equipment Failure | 945251 | 69 | 87 | 5319 | 0.0032485 | 0.0042141
2013-02-28 | 507:80923 | SHORT RURAL | Other | 945254 | 2 | 54.0167 | 108.0333 | 6.5981e-05 | 0.00012215
2013-01-27 | 240:34852 | URBAN | Equipment Failure | 945260 | 34 | 370 | 12580 | 0.0076908 | 0.0020786
2013-02-28 | 258:80784 | URBAN | Equipment Failure | 945269 | 63 | 117 | 7371 | 0.0045018 | 0.0038477
2013-02-28 | ZN9252:PA12 | URBAN | Vegetation | 945309 | 45 | 82.65 | 3719.25 | 0.0022715 | 0.0027483
2013-02-28 | ZN12600:PA2 | SHORT RURAL | Equipment Failure | 945353 | 8 | 106.1833 | 849.4667 | 0.00051881 | 0.00048859
2013-02-28 | 205:12206 | URBAN | Other | 945366 | 1 | 97.25 | 97.25 | 5.9395e-05 | 6.1074e-05
2013-02-23 | ZN12630:PA3 | SHORT RURAL | Other | 945374 | 2 | 6480 | 12960 | 0.007915 | 0.00012214
2013-02-24 | ZN12640:PA16 | URBAN | Weather | 945384 | 47 | 685 | 32195 | 0.019662 | 0.0028704
2013-02-28 | ZN12600:PA13 | SHORT RURAL | Vegetation | 945418 | 1 | 114.8333 | 114.8333 | 7.0134e-05 | 6.1074e-05
2013-02-28 | ZN35600:PA19 | URBAN | Vegetation | 945434 | 2 | 109.8167 | 204.8833 | 0.00012513 | 0.00012215
2013-02-28 | ZN12690:PA8 | URBAN | Other | 945436 | 1 | 97.7333 | 97.7333 | 5.969e-05 | 6.1074e-05
2013-02-28 | ZN9118:PA3 | SHORT RURAL | Other | 945445 | 1 | 109.3167 | 109.3167 | 6.6764e-05 | 6.1074e-05
2013-02-28 | ZN9118:PA3 | SHORT RURAL | Other | 945450 | 1 | 105.5667 | 105.5667 | 6.4474e-05 | 6.1074e-05
2013-02-28 | 232:11457 | URBAN | Other | 945472 | 1 | 150.2333 | 150.2333 | 9.1754e-05 | 6.1074e-05
2013-02-25 | ZN12630:PA1 | SHORT RURAL | Vegetation | 945474 | 9 | 20 | 180 | 0.00010993 | 0.00054965
2013-02-28 | ZN1788:PA16 | URBAN | Other | 945496 | 2 | 124 | 248 | 0.00015146 | 0.00012215
2013-02-28 | 813:89055 | SHORT RURAL | Operational Error | 945500 | 7 | 90 | 630 | 0.00038477 | 0.00042752
2013-02-28 | ZN15013:PA2 | URBAN | Equipment Failure | 945502 | 69 | 63 | 3336 | 0.0020374 | 0.0042141
2013-02-28 | ZN2602:PA9 | URBAN | Other | 945518 | 1 | 372.5167 | 372.5167 | 0.00022751 | 6.1074e-05
2013-02-28 | ZN2473:PA31 | URBAN | Other | 945534 | 1 | 222.4 | 222.4 | 0.00013583 | 6.1074e-05
2013-02-28 | ZN12570:PA35 | URBAN | Vegetation | 945543 | 1 | 114.9 | 114.9 | 7.0174e-05 | 6.1074e-05
2013-02-28 | ZN10997:PA8 | URBAN | Weather | 945544 | 35 | 78 | 2730 | 0.0016673 | 0.0021376
2013-02-28 | 210:8682 | URBAN | Other | 945551 | 1 | 65.9833 | 65.9833 | 4.0299e-05 | 6.1074e-05
2013-02-28 | ZN15010:PA1 | URBAN | Other | 945553 | 1 | 1150.35 | 1150.35 | 0.00070257 | 6.1074e-05
2013-02-28 | ZN14891:PA10 | SHORT RURAL | Other | 945557 | 1 | 218.6667 | 218.6667 | 0.00013355 | 6.1074e-05
2013-02-28 | ZN14144:PA4 | URBAN | Vegetation | 945559 | 828 | 49 | 40572 | 0.024779 | 0.05057
2013-02-28 | ZN3672:PA13 | URBAN | Equipment Failure | 945563 | 1 | 125.2167 | 125.2167 | 7.6475e-05 | 6.1074e-05
2013-02-28 | 513:48056 | SHORT RURAL | Animals | 945565 | 1 | 111.6 | 111.6 | 6.8159e-05 | 6.1074e-05
2013-02-28 | ZN36300:PA17 | URBAN | Animals | 945578 | 1395 | 343 | 168918 | 0.10317 | 0.085199
2013-02-28 | 516:48065 | SHORT RURAL | Other | 945584 | 7 | 353 | 2471 | 0.0015091 | 0.00042752
2013-02-28 | ZN269:PA3 | URBAN | Vegetation | 945594 | 1 | 838.85 | 838.85 | 0.00051232 | 6.1074e-05
2013-02-28 | ZN12640:PA16 | URBAN | Other | 945597 | 1 | 756.3667 | 756.3667 | 0.00046195 | 6.1074e-05
2013-02-28 | ZN36300:PA17 | URBAN | Animals | 945601 | 1 | 141.0667 | 141.0667 | 8.6155e-05 | 6.1074e-05
2013-02-28 | ZN14144:PA5 | SHORT RURAL | Vegetation | 945605 | 15 | 98 | 1470 | 0.00089779 | 0.00091611
2013-02-28 | ZN340:PA24 | URBAN | Other | 945608 | 1 | 481.0333 | 481.0333 | 0.00029379 | 6.1074e-05
2013-02-28 | ZN35600:PA9 | URBAN | Other | 945610 | 1 | 171.85 | 171.85 | 0.00010496 | 6.1074e-05
2013-02-28 | ZN35600:PA12 | SHORT RURAL | Other | 945613 | 1 | 109.0333 | 109.0333 | 6.6591e-05 | 6.1074e-05
2013-02-28 | ZN1193:PA7 | URBAN | Equipment Failure | 945620 | 1 | 109.45 | 109.45 | 6.6846e-05 | 6.1074e-05
2013-02-28 | ZN1850:PA3 | URBAN | Animals | 945622 | 1006 | 74 | 67892 | 0.041465 | 0.061441
2013-03-01 | ZN14143:PA17 | SHORT RURAL | Third Party Impacts | 945624 | 505 | 83 | 41915 | 0.0256 | 0.030843
2013-03-01 | ZN35500:PA23 | URBAN | Vegetation | 945633 | 4 | 54 | 216 | 0.00013192 | 0.0002443
2013-03-01 | ZN35500:PA31 | URBAN | Vegetation | 945633 | 12 | 54 | 648 | 0.00039577 | 0.0007329
2013-03-01 | ZN7900:PA23 | URBAN | Vegetation | 945639 | 26 | 34 | 884 | 0.0005399 | 0.0015879
2013-03-01 | ZN12630:PA1 | SHORT RURAL | Vegetation | 945641 | 94 | 830 | 16078 | 0.0098196 | 0.005741
2013-03-01 | ZN14143:PA17 | SHORT RURAL | Vegetation | 945641 | 1 | 830 | 146 | 8.9169e-05 | 6.1075e-05
2013-03-01 | ZN14891:PA21 | SHORT RURAL | Equipment Failure | 945644 | 846 | 193 | 163228 | 0.099691 | 0.051669
2013-03-01 | 232:11457 | URBAN | Equipment Failure | 945645 | 1 | 283.35 | 283.35 | 0.00017306 | 6.1075e-05
2013-03-01 | ZN35600:PA3 | URBAN | Other | 945651 | 1 | 84.3167 | 84.3167 | 5.1496e-05 | 6.1075e-05
2013-03-01 | ZN14144:PA1 | URBAN | Vegetation | 945657 | 1181 | 18 | 21258 | 0.012983 | 0.072129
2013-03-01 | ZN14144:PA10 | SHORT RURAL | Vegetation | 945657 | 667 | 18 | 12006 | 0.0073327 | 0.040737
2013-03-01 | ZN14144:PA2 | SHORT RURAL | Vegetation | 945657 | 1004 | 18 | 18072 | 0.011037 | 0.061319
2013-03-01 | ZN14144:PA4 | URBAN | Vegetation | 945657 | 827 | 18 | 14886 | 0.0090916 | 0.050509
2013-03-01 | ZN14144:PA5 | SHORT RURAL | Vegetation | 945657 | 278 | 18 | 5004 | 0.0030562 | 0.016979
2013-03-01 | ZN14144:PA7 | SHORT RURAL | Vegetation | 945657 | 1030 | 18 | 18540 | 0.011323 | 0.062907
2013-03-01 | ZN14144:PA8 | URBAN | Vegetation | 945657 | 482 | 18 | 8676 | 0.0052989 | 0.029438
2013-03-01 | ZN269:PA6 | URBAN | Equipment Failure | 945661 | 25 | 131.95 | 3298.75 | 0.0020147 | 0.0015269
2013-03-01 | 232:11457 | URBAN | Equipment Failure | 945663 | 1 | 151.4333 | 151.4333 | 9.2488e-05 | 6.1075e-05
2013-03-01 | ZN35600:PA9 | URBAN | Other | 945665 | 1 | 170.65 | 170.65 | 0.00010422 | 6.1075e-05
2013-03-01 | 509:48040 | SHORT RURAL | Vegetation | 945674 | 828 | 202 | 85452 | 0.05219 | 0.05057
2013-03-01 | 258:80775 | URBAN | Vegetation | 945681 | 1 | 43 | 43 | 2.6262e-05 | 6.1075e-05
2013-03-01 | ZN3672:PA13 | URBAN | Weather | 945682 | 32 | 507.4333 | 16237.8667 | 0.0099173 | 0.0019544
2013-03-01 | 202:34245 | URBAN | Other | 945683 | 1 | 377.5333 | 196.9833 | 0.00012031 | 6.1075e-05
2013-03-01 | 202:34250 | URBAN | Other | 945683 | 43 | 377.5333 | 13416 | 0.0081938 | 0.0026262
2013-03-01 | 202:34253 | URBAN | Other | 945683 | 20 | 377.5333 | 6240 | 0.0038111 | 0.0012215
2013-03-01 | 202:34254 | URBAN | Other | 945683 | 21 | 377.5333 | 6543.6 | 0.0039965 | 0.0012826
2013-03-01 | 202:34260 | URBAN | Other | 945683 | 100 | 377.5333 | 30968.5833 | 0.018914 | 0.0061075
2013-03-01 | ZN10994:PA7 | URBAN | Vegetation | 945684 | 1 | 155.55 | 155.55 | 9.5002e-05 | 6.1075e-05
2013-03-01 | ZN3154:PA14 | URBAN | Vegetation | 945685 | 1 | 219.85 | 219.85 | 0.00013427 | 6.1075e-05
2013-03-01 | 232:11457 | URBAN | Equipment Failure | 945689 | 1 | 96.5 | 96.5 | 5.8937e-05 | 6.1075e-05
2013-03-01 | ZN9252:PA12 | URBAN | Other | 945700 | 1 | 133.4 | 133.4 | 8.1474e-05 | 6.1075e-05
2013-03-01 | 261:81886 | URBAN | Vegetation | 945704 | 1 | 128.7333 | 128.7333 | 7.8624e-05 | 6.1075e-05
2013-03-01 | 261:81886 | URBAN | Vegetation | 945708 | 1 | 125.1333 | 125.1333 | 7.6425e-05 | 6.1075e-05
2013-03-01 | 230:81434 | URBAN | Vegetation | 945736 | 681 | 200 | 49680 | 0.030342 | 0.041592
2013-03-01 | 806:74080 | SHORT RURAL | Equipment Failure | 945789 | 3 | 127 | 381 | 0.0002327 | 0.00018322
2013-03-01 | 232:11454 | SHORT RURAL | Vegetation | 945795 | 1 | 301.2667 | 301.2667 | 0.000184 | 6.1075e-05
2013-03-01 | 224:80332 | URBAN | Equipment Failure | 945817 | 1 | 447.1667 | 447.1667 | 0.00027311 | 6.1075e-05
2013-03-01 | ZN12650:PA1 | SHORT RURAL | Vegetation | 945842 | 29 | 175 | 5075 | 0.0030996 | 0.0017712
2013-03-01 | 235:2123 | URBAN | Other | 945853 | 1 | 254.15 | 254.15 | 0.00015522 | 6.1075e-05
2013-03-01 | ZN398:PA25 | URBAN | Vegetation | 945856 | 70 | 65 | 4550 | 0.0027789 | 0.0042752
2013-03-01 | 229:34983 | SHORT RURAL | Vegetation | 945896 | 1 | 254.5833 | 254.5833 | 0.00015549 | 6.1075e-05
2013-03-01 | ZN35370:PA4 | URBAN | Vegetation | 945913 | 164 | 92.4167 | 15156.3333 | 0.0092567 | 0.010016
2013-03-01 | ZN12570:PA41 | URBAN | Equipment Failure | 945915 | 772 | 392 | 90104 | 0.055031 | 0.04715
2013-03-01 | 223:14394 | URBAN | Other | 945925 | 1 | 401.6167 | 401.6167 | 0.00024529 | 6.1075e-05
2013-03-01 | ZN14144:PA4 | URBAN | Other | 945926 | 1 | 384.85 | 384.85 | 0.00023505 | 6.1075e-05
2013-03-01 | ZN180:PA23 | URBAN | Equipment Failure | 945947 | 74 | 439.3667 | 32513.1333 | 0.019857 | 0.0045195
2013-03-01 | 503:48017 | URBAN | Other | 945957 | 25 | 102 | 2550 | 0.0015574 | 0.0015269
2013-03-01 | ZN12570:PA40 | SHORT RURAL | Other | 945963 | 12 | 269.5167 | 3234.2 | 0.0019753 | 0.0007329
2013-03-01 | ZN965:PA47 | URBAN | Other | 945971 | 42 | 292 | 12264 | 0.0074902 | 0.0025651
2013-03-01 | ZN9035:PA4 | URBAN | Other | 945979 | 1 | 63.7333 | 63.7333 | 3.8925e-05 | 6.1075e-05
2013-03-01 | ZN3472:PA7 | SHORT RURAL | Other | 945984 | 29 | 118.6 | 3439.4 | 0.0021006 | 0.0017712
2013-03-01 | 504:48031 | SHORT RURAL | Vegetation | 945990 | 533 | 135 | 69001 | 0.042142 | 0.032553
2013-03-01 | ZN12570:PA35 | URBAN | Vegetation | 945998 | 1 | 1364.85 | 1364.85 | 0.00083358 | 6.1075e-05
2013-03-01 | 230:81440 | URBAN | Vegetation | 946000 | 1 | 110.9333 | 110.9333 | 6.7752e-05 | 6.1075e-05
2013-03-01 | ZN12610:PA16 | URBAN | Other | 946023 | 1 | 414.2167 | 414.2167 | 0.00025298 | 6.1075e-05
2013-03-01 | 220:8689 | URBAN | Other | 946025 | 1 | 151.7167 | 151.7167 | 9.2661e-05 | 6.1075e-05
2013-03-01 | ZN116:PA47 | URBAN | Equipment Failure | 946041 | 175 | 311 | 54425 | 0.03324 | 0.010688
2013-03-01 | ZN14891:PA9 | URBAN | Third Party Impacts | 946052 | 48 | 198.6 | 9532.8 | 0.0058222 | 0.0029316
2013-03-01 | ZN269:PA19 | URBAN | Other | 946061 | 2 | 518.45 | 1036.9 | 0.00063329 | 0.00012215
2013-03-01 | ZN9245:PA10 | URBAN | Other | 946077 | 1 | 80.5 | 80.5 | 4.9165e-05 | 6.1075e-05
2013-03-01 | 502:48010 | SHORT RURAL | Equipment Failure | 946088 | 13 | 1306 | 4328 | 0.0026433 | 0.00079397
2013-03-01 | ZN1850:PA12 | URBAN | Other | 946103 | 1 | 521.5167 | 521.5167 | 0.00031852 | 6.1075e-05
2013-03-01 | ZN116:PA47 | URBAN | Equipment Failure | 946108 | 5 | 728 | 3640 | 0.0022231 | 0.00030537
2013-03-01 | ZN12660:PA8 | URBAN | Vegetation | 946112 | 28 | 46 | 1288 | 0.00078665 | 0.0017101
2013-03-01 | ZN1164:PA15 | URBAN | Equipment Failure | 946114 | 1 | 378.7667 | 378.7667 | 0.00023133 | 6.1075e-05
2013-03-01 | ZN10990:PA2 | URBAN | Other | 946135 | 1 | 354.2167 | 354.2167 | 0.00021634 | 6.1075e-05
2013-03-01 | ZN1285:PA24 | URBAN | Other | 946136 | 1 | 153.1667 | 153.1667 | 9.3546e-05 | 6.1075e-05
2013-03-01 | ZN35600:PA1 | URBAN | Other | 946139 | 1 | 388.5 | 388.5 | 0.00023728 | 6.1075e-05
2013-03-01 | ZN129:PA19 | URBAN | Vegetation | 946143 | 4 | 319 | 1276 | 0.00077932 | 0.0002443
2013-03-01 | 232:11454 | SHORT RURAL | Other | 946148 | 1 | 289.6833 | 289.6833 | 0.00017692 | 6.1075e-05
2013-03-01 | ZN13000:PA2 | URBAN | Vegetation | 946158 | 1 | 428.2833 | 428.2833 | 0.00026157 | 6.1075e-05
2013-03-01 | 526:34640 | SHORT RURAL | Other | 946163 | 19 | 202.8833 | 3854.7833 | 0.0023543 | 0.0011604
2013-03-01 | 256:80650 | URBAN | Other | 946171 | 1 | 352.2833 | 352.2833 | 0.00021516 | 6.1075e-05
2013-03-01 | ZN12630:PA1 | SHORT RURAL | Vegetation | 946173 | 364 | 7.2333 | 2632.9333 | 0.0016081 | 0.022231
2013-03-01 | 526:34640 | SHORT RURAL | Other | 946180 | 1 | 222.8333 | 222.8333 | 0.0001361 | 6.1075e-05
2013-03-01 | 526:34636 | SHORT RURAL | Other | 946184 | 1 | 219.8833 | 219.8833 | 0.00013429 | 6.1075e-05
2013-03-01 | ZN847:PA47 | SHORT RURAL | Equipment Failure | 946200 | 259 | 333 | 35941 | 0.021951 | 0.015818
2013-03-01 | 261:81864 | URBAN | Other | 946202 | 1 | 60.45 | 60.45 | 3.692e-05 | 6.1075e-05
2013-03-01 | 219:1740 | SHORT RURAL | Other | 946221 | 1 | 90.45 | 90.45 | 5.5242e-05 | 6.1075e-05
2013-03-01 | ZN3472:PA11 | URBAN | Vegetation | 946227 | 1 | 195.4667 | 195.4667 | 0.00011938 | 6.1075e-05
2013-03-01 | ZN15006:PA8 | URBAN | Vegetation | 946228 | 1 | 259.3833 | 259.3833 | 0.00015842 | 6.1075e-05
2013-03-01 | ZN12570:PA29 | SHORT RURAL | Vegetation | 946236 | 771 | 71 | 54741 | 0.033433 | 0.047089
2013-03-01 | ZN2400:PA18 | SHORT RURAL | Third Party Impacts | 946254 | 1 | 155.25 | 155.25 | 9.4819e-05 | 6.1075e-05
2013-03-01 | 813:89061 | LONG RURAL | Other | 946266 | 1 | 213.7167 | 213.7167 | 0.00013053 | 6.1075e-05
2013-03-01 | 509:48039 | LONG RURAL | Equipment Failure | 946270 | 10 | 140.45 | 1404.5 | 0.0008578 | 0.00061075
2013-03-01 | ZN35600:PA9 | URBAN | Other | 946273 | 1 | 740.5333 | 740.5333 | 0.00045228 | 6.1075e-05
2013-03-01 | 526:34640 | SHORT RURAL | Other | 946275 | 1 | 46.3 | 46.3 | 2.8278e-05 | 6.1075e-05
2013-03-01 | 507:80932 | SHORT RURAL | Other | 946284 | 1 | 1101.5 | 1101.5 | 0.00067274 | 6.1075e-05
2013-03-01 | 238:34144 | URBAN | Other | 946285 | 1 | 934.0667 | 934.0667 | 0.00057048 | 6.1075e-05
2013-03-01 | ZN3472:PA7 | SHORT RURAL | Equipment Failure | 946287 | 1 | 1350.35 | 1350.35 | 0.00082473 | 6.1075e-05
2013-03-01 | ZN15014:PA18 | URBAN | Equipment Failure | 946302 | 2 | 1011.4667 | 1954.4 | 0.0011936 | 0.00012215
2013-03-01 | ZN180:PA23 | URBAN | Equipment Failure | 946305 | 74 | 210.0667 | 15544.9333 | 0.0094941 | 0.0045195
2013-03-01 | ZN3154:PA22 | URBAN | Third Party Impacts | 946310 | 722 | 1097 | 104399 | 0.063762 | 0.044096
2013-03-02 | ZN3154:PA22 | URBAN | Third Party Impacts | 946311 | 25 | 999.2 | 24980 | 0.015257 | 0.0015269
2013-03-01 | 222:2018 | URBAN | Equipment Failure | 946327 | 76 | 196 | 14896 | 0.0090977 | 0.0046417
2013-03-01 | 235:2120 | SHORT RURAL | Vegetation | 946328 | 263 | 792 | 41557 | 0.025381 | 0.016063
2013-03-02 | ZN15002:PA6 | URBAN | Animals | 946331 | 1 | 87 | 71 | 4.3363e-05 | 6.1075e-05
2013-03-02 | ZN15002:PA8 | URBAN | Animals | 946331 | 814 | 87 | 43858 | 0.026786 | 0.049715
2013-03-02 | 206:34438 | SHORT RURAL | Vegetation | 946335 | 32 | 425 | 13600 | 0.0083062 | 0.0019544
2013-03-02 | ZN15008:PA7 | URBAN | Other | 946339 | 1 | 400.9667 | 400.9667 | 0.00024489 | 6.1075e-05
2013-03-02 | ZN12600:PA1 | SHORT RURAL | Equipment Failure | 946341 | 192 | 276 | 31680 | 0.019349 | 0.011726
2013-03-02 | ZN12600:PA13 | SHORT RURAL | Equipment Failure | 946341 | 851 | 276 | 151406 | 0.092471 | 0.051975
2013-03-02 | 229:34983 | SHORT RURAL | Other | 946345 | 26 | 491 | 12766 | 0.0077968 | 0.0015879
2013-03-02 | ZN15004:PA9 | URBAN | Other | 946349 | 1 | 328.4333 | 328.4333 | 0.00020059 | 6.1075e-05
2013-03-02 | 229:34989 | SHORT RURAL | Vegetation | 946350 | 1 | 240.8667 | 240.8667 | 0.00014711 | 6.1075e-05
2013-03-02 | ZN180:PA23 | URBAN | Equipment Failure | 946352 | 74 | 705.9667 | 52241.5333 | 0.031906 | 0.0045195
2013-03-02 | 256:80646 | URBAN | Other | 946353 | 1 | 534.5 | 534.5 | 0.00032645 | 6.1075e-05
2013-03-02 | ZN1673:PA7 | URBAN | Equipment Failure | 946359 | 36 | 646.4833 | 23273.4 | 0.014214 | 0.0021987
2013-03-02 | 258:80775 | URBAN | Other | 946366 | 1 | 485.3333 | 485.3333 | 0.00029642 | 6.1075e-05
2013-03-02 | ZN847:PA44 | URBAN | Other | 946374 | 1 | 368.2 | 368.2 | 0.00022488 | 6.1075e-05
2013-03-02 | 208:53 | URBAN | Other | 946376 | 1 | 467.4167 | 467.4167 | 0.00028547 | 6.1075e-05
2013-03-02 | ZN15010:PA5 | URBAN | Other | 946378 | 1 | 330.7167 | 330.7167 | 0.00020198 | 6.1075e-05
2013-03-02 | 242:81541 | URBAN | Vegetation | 946383 | 1526 | 169 | 230741 | 0.14092 | 0.0932
2013-03-02 | ZN1287:PA21 | URBAN | Other | 946401 | 1 | 341.7167 | 341.7167 | 0.0002087 | 6.1075e-05
2013-03-02 | ZN12580:PA4 | URBAN | Vegetation | 946410 | 1 | 288.0167 | 288.0167 | 0.00017591 | 6.1075e-05
2013-03-02 | 512:48048 | SHORT RURAL | Vegetation | 946414 | 1 | 280.55 | 280.55 | 0.00017135 | 6.1075e-05
2013-03-02 | 512:48048 | SHORT RURAL | Vegetation | 946415 | 1 | 271.9 | 271.9 | 0.00016606 | 6.1075e-05
2013-03-02 | 504:48026 | SHORT RURAL | Other | 946422 | 1 | 363.9 | 363.9 | 0.00022225 | 6.1075e-05
2013-03-02 | ZN3922:PA22 | URBAN | Equipment Failure | 946430 | 1 | 528.9 | 528.9 | 0.00032303 | 6.1075e-05
2013-03-02 | 261:81882 | URBAN | Equipment Failure | 946432 | 24 | 420 | 10080 | 0.0061564 | 0.0014658
2013-03-02 | ZN3672:PA13 | URBAN | Other | 946433 | 1 | 87.1 | 87.1 | 5.3196e-05 | 6.1075e-05
2013-03-02 | 221:11900 | URBAN | Vegetation | 946454 | 1 | 93.0833 | 93.0833 | 5.6851e-05 | 6.1075e-05
2013-03-02 | 512:48048 | SHORT RURAL | Vegetation | 946455 | 1 | 205.4 | 205.4 | 0.00012545 | 6.1075e-05
2013-03-02 | 232:11457 | URBAN | Other | 946460 | 1 | 181.6 | 181.6 | 0.00011091 | 6.1075e-05
2013-03-02 | ZN12620:PA1 | SHORT RURAL | Other | 946466 | 1 | 781.3333 | 781.3333 | 0.0004772 | 6.1075e-05
2013-03-02 | ZN15012:PA8 | URBAN | Other | 946472 | 1 | 351.4667 | 351.4667 | 0.00021466 | 6.1075e-05
2013-03-02 | 523:33501 | SHORT RURAL | Other | 946485 | 61 | 7476 | 90557 | 0.055308 | 0.0037256
2013-03-02 | ZN1673:PA9 | URBAN | Other | 946490 | 1 | 548.9833 | 548.9833 | 0.00033529 | 6.1075e-05
2013-03-02 | 256:80647 | URBAN | Equipment Failure | 946507 | 164 | 121 | 19844 | 0.01212 | 0.010016
2013-03-02 | 261:81870 | URBAN | Other | 946515 | 1 | 213.8667 | 213.8667 | 0.00013062 | 6.1075e-05
2013-03-02 | ZN72:PA16 | URBAN | Other | 946524 | 1 | 373.6333 | 373.6333 | 0.0002282 | 6.1075e-05
2013-03-02 | ZN2835:PA23 | URBAN | Other | 946537 | 1 | 335.9667 | 335.9667 | 0.00020519 | 6.1075e-05
2013-03-02 | 205:12206 | URBAN | Other | 946540 | 2 | 159.75 | 319.5 | 0.00019513 | 0.00012215
2013-03-02 | ZN965:PA8 | URBAN | Equipment Failure | 946542 | 28 | 454.1833 | 12717.1333 | 0.007767 | 0.0017101
2013-03-02 | ZN9252:PA7 | URBAN | Other | 946544 | 1 | 472.0333 | 472.0333 | 0.00028829 | 6.1075e-05
2013-03-02 | 801:74121 | SHORT RURAL | Equipment Failure | 946550 | 475 | 176 | 52636 | 0.032147 | 0.029011
2013-03-02 | 501:48115 | SHORT RURAL | Other | 946570 | 1 | 143.8833 | 143.8833 | 8.7877e-05 | 6.1075e-05
2013-03-02 | ZN10999:PA4 | URBAN | Third Party Impacts | 946573 | 74 | 30 | 2220 | 0.0013559 | 0.0045195
2013-03-02 | ZN187:PA30 | URBAN | Vegetation | 946576 | 88 | 17 | 1496 | 0.00091368 | 0.0053746
2013-03-02 | 256:80647 | URBAN | Other | 946580 | 1 | 60.2667 | 60.2667 | 3.6808e-05 | 6.1075e-05
2013-03-02 | ZN1285:PA20 | URBAN | Other | 946584 | 1 | 591.1667 | 591.1667 | 0.00036105 | 6.1075e-05
2013-03-01 | 509:48040 | SHORT RURAL | Other | 946602 | 105 | 1196 | 7595 | 0.0046386 | 0.0064129
2013-03-02 | ZN965:PA28 | URBAN | Other | 946606 | 1 | 143.95 | 143.95 | 8.7917e-05 | 6.1075e-05
2013-03-02 | 503:48017 | URBAN | Equipment Failure | 946609 | 25 | 204.2167 | 5105.4167 | 0.0031181 | 0.0015269
2013-03-02 | 801:74122 | URBAN | Equipment Failure | 946616 | 1 | 129.5667 | 129.5667 | 7.9133e-05 | 6.1075e-05
2013-03-02 | 223:14398 | URBAN | Equipment Failure | 946619 | 853 | 4191 | 52755 | 0.03222 | 0.052097
2013-03-02 | 238:34141 | SHORT RURAL | Other | 946620 | 1 | 202.0667 | 202.0667 | 0.00012341 | 6.1075e-05
2013-03-02 | 238:34141 | SHORT RURAL | Other | 946622 | 1 | 200.15 | 200.15 | 0.00012224 | 6.1075e-05
2013-03-02 | 507:80925 | SHORT RURAL | Other | 946640 | 31 | 121.4833 | 3765.9833 | 0.0023001 | 0.0018933
2013-03-02 | ZN15010:PA7 | URBAN | Other | 946659 | 1 | 254.2 | 254.2 | 0.00015525 | 6.1075e-05
2013-03-02 | ZN1673:PA7 | URBAN | Other | 946682 | 1 | 80.7833 | 80.7833 | 4.9338e-05 | 6.1075e-05
2013-03-03 | ZN14144:PA8 | URBAN | Vegetation | 946691 | 1 | 555.65 | 555.65 | 0.00033936 | 6.1075e-05
2013-03-03 | 510:48164 | SHORT RURAL | Other | 946692 | 2 | 481.2167 | 962.4333 | 0.00058781 | 0.00012215
2013-03-03 | ZN12690:PA24 | SHORT RURAL | Vegetation | 946693 | 1 | 162.6333 | 162.6333 | 9.9328e-05 | 6.1075e-05
2013-03-03 | ZN690:PA12 | URBAN | Equipment Failure | 946694 | 1 | 567.1833 | 567.1833 | 0.00034641 | 6.1075e-05
2013-03-03 | ZN12620:PA11 | SHORT RURAL | Equipment Failure | 946696 | 562 | 170 | 77521 | 0.047346 | 0.034324
2013-03-03 | ZN9037:PA7 | URBAN | Equipment Failure | 946697 | 641 | 134 | 78424 | 0.047897 | 0.039149
2013-03-03 | ZN15012:PA6 | URBAN | Other | 946702 | 1 | 678.75 | 678.75 | 0.00041455 | 6.1075e-05
2013-03-03 | 214:8669 | URBAN | Vegetation | 946710 | 1 | 216.3333 | 216.3333 | 0.00013213 | 6.1075e-05
2013-03-03 | ZN4545:PA19 | URBAN | Vegetation | 946720 | 44 | 121 | 5324 | 0.0032516 | 0.0026873
2013-03-03 | 206:34434 | URBAN | Other | 946722 | 1 | 86.45 | 86.45 | 5.2799e-05 | 6.1075e-05
2013-03-03 | ZN15002:PA6 | URBAN | Equipment Failure | 946742 | 89 | 132.9833 | 11835.5167 | 0.0072285 | 0.0054357
2013-03-03 | ZN2602:PA4 | URBAN | Equipment Failure | 946750 | 1 | 144.1 | 144.1 | 8.8009e-05 | 6.1075e-05
2013-03-03 | 501:48115 | SHORT RURAL | Other | 946757 | 10 | 73.0333 | 730.3333 | 0.00044605 | 0.00061075
2013-03-03 | 214:8667 | URBAN | Vegetation | 946788 | 1 | 46.5333 | 46.5333 | 2.842e-05 | 6.1075e-05
2013-03-03 | ZN12690:PA8 | URBAN | Equipment Failure | 946802 | 57 | 312.75 | 17826.75 | 0.010888 | 0.0034813
2013-03-03 | 813:89055 | SHORT RURAL | Other | 946804 | 1 | 157.9333 | 157.9333 | 9.6458e-05 | 6.1075e-05
2013-03-03 | ZN12610:PA10 | SHORT RURAL | Equipment Failure | 946807 | 1824 | 232 | 62027 | 0.037883 | 0.1114
2013-03-03 | 232:11454 | SHORT RURAL | Other | 946818 | 1 | 170.1167 | 170.1167 | 0.0001039 | 6.1075e-05
2013-03-03 | ZN10999:PA22 | URBAN | Equipment Failure | 946822 | 70 | 71 | 4970 | 0.0030354 | 0.0042752
2013-03-03 | ZN1193:PA25 | URBAN | Vegetation | 946840 | 1 | 394.2833 | 394.2833 | 0.00024081 | 6.1075e-05
2013-03-03 | ZN15008:PA10 | URBAN | Other | 946841 | 1 | 170.8833 | 170.8833 | 0.00010437 | 6.1075e-05
2013-03-03 | ZN12630:PA2 | SHORT RURAL | Other | 946844 | 1 | 251.2333 | 251.2333 | 0.00015344 | 6.1075e-05
2013-03-03 | ZN35600:PA1 | URBAN | Vegetation | 946845 | 1 | 169 | 169 | 0.00010322 | 6.1075e-05
2013-03-03 | 220:8687 | URBAN | Other | 946850 | 1 | 277.5 | 277.5 | 0.00016948 | 6.1075e-05
2013-03-03 | 205:12213 | URBAN | Other | 946851 | 1 | 108.15 | 108.15 | 6.6053e-05 | 6.1075e-05
2013-03-03 | ZN1648:PA20 | URBAN | Vegetation | 946869 | 46 | 89 | 4094 | 0.0025004 | 0.0028094
2013-03-03 | ZN690:PA25 | URBAN | Vegetation | 946869 | 2 | 89 | 178 | 0.00010871 | 0.00012215
2013-03-03 | ZN4545:PA40 | URBAN | Third Party Impacts | 946880 | 4 | 165 | 660 | 0.00040309 | 0.0002443
2013-03-03 | ZN2635:PA10 | URBAN | Vegetation | 946886 | 1 | 295.0833 | 295.0833 | 0.00018022 | 6.1075e-05
2013-03-03 | 202:34260 | URBAN | Other | 946888 | 1 | 109.1167 | 109.1167 | 6.6643e-05 | 6.1075e-05
2013-03-03 | 202:34260 | URBAN | Other | 946889 | 1 | 106.3833 | 106.3833 | 6.4974e-05 | 6.1075e-05
2013-03-03 | 202:34260 | URBAN | Other | 946890 | 1 | 90.1167 | 90.1167 | 5.5039e-05 | 6.1075e-05
2013-03-03 | ZN12630:PA2 | SHORT RURAL | Equipment Failure | 946891 | 529 | 1349 | 66368 | 0.040534 | 0.032309
2013-03-03 | 261:81870 | URBAN | Other | 946897 | 1 | 143.4667 | 143.4667 | 8.7622e-05 | 6.1075e-05
2013-03-03 | ZN2602:PA4 | URBAN | Equipment Failure | 946904 | 1791 | 51 | 75563 | 0.04615 | 0.10939
2013-03-03 | ZN35600:PA19 | URBAN | Equipment Failure | 946904 | 37 | 51 | 1517 | 0.00092651 | 0.0022598
2013-03-03 | ZN12650:PA17 | URBAN | Other | 946908 | 1 | 998.4 | 998.4 | 0.00060977 | 6.1075e-05
2013-03-03 | ZN3472:PA40 | URBAN | Other | 946911 | 24 | 37.6 | 902.4 | 0.00055114 | 0.0014658
2013-03-03 | ZN1164:PA15 | URBAN | Other | 946934 | 1 | 651.2 | 651.2 | 0.00039772 | 6.1075e-05
2013-03-03 | 520:48172 | SHORT RURAL | Other | 946938 | 2 | 54 | 108 | 6.5961e-05 | 0.00012215
2013-03-04 | ZN195:PA30 | URBAN | Vegetation | 946941 | 21 | 189 | 3969 | 0.0024241 | 0.0012826
2013-03-04 | 813:89055 | SHORT RURAL | Other | 946945 | 37 | 600 | 22200 | 0.013559 | 0.0022598
2013-03-04 | ZN2473:PA42 | URBAN | Equipment Failure | 946946 | 78 | 276.9 | 21598.2 | 0.013191 | 0.0047638
2013-03-04 | ZN1610:PA11 | URBAN | Equipment Failure | 946947 | 1 | 288.3167 | 288.3167 | 0.00017609 | 6.1075e-05
2013-03-04 | ZN3672:PA35 | URBAN | Other | 946948 | 1 | 239.4 | 239.4 | 0.00014621 | 6.1075e-05
2013-03-04 | ZN9252:PA2 | URBAN | Other | 946963 | 1 | 61.7667 | 61.7667 | 3.7724e-05 | 6.1075e-05
2013-03-04 | 258:80787 | URBAN | Other | 947019 | 135 | 113.9667 | 15385.5 | 0.0093967 | 0.0082451
2013-03-04 | ZN2310:PA38 | URBAN | Other | 947024 | 1 | 118.45 | 118.45 | 7.2343e-05 | 6.1075e-05
2013-03-04 | 228:7487 | URBAN | Other | 947034 | 1 | 124.7 | 124.7 | 7.616e-05 | 6.1075e-05
2013-03-04 | ZN3472:PA28 | URBAN | Other | 947064 | 1 | 143.9 | 143.9 | 8.7887e-05 | 6.1075e-05
2013-03-04 | ZN965:PA28 | URBAN | Equipment Failure | 947070 | 27 | 89.3667 | 2412.9 | 0.0014737 | 0.001649
2013-03-02 | 225:13446 | URBAN | Vegetation | 947112 | 1520 | 317 | 91871 | 0.05611 | 0.092834
2013-03-04 | 222:2015 | SHORT RURAL | Other | 947151 | 1 | 130.9167 | 130.9167 | 7.9957e-05 | 6.1075e-05
2013-03-04 | 813:89055 | SHORT RURAL | Equipment Failure | 947190 | 2 | 171 | 342 | 0.00020888 | 0.00012215
2013-03-04 | ZN14144:PA8 | URBAN | Vegetation | 947226 | 1 | 42.2833 | 42.2833 | 2.5825e-05 | 6.1075e-05
2013-02-14 | ZN1164:PA20 | URBAN | Equipment Failure | 947240 | 90 | 1664 | 68270 | 0.04169 | 0.005496
2013-03-04 | ZN36300:PA13 | URBAN | Vegetation | 947246 | 1 | 447.3667 | 447.3667 | 0.00027323 | 6.1075e-05
2013-03-04 | 524:33572 | SHORT RURAL | Other | 947267 | 1 | 342 | 342 | 0.00020888 | 6.1075e-05
2013-03-04 | ZN180:PA21 | URBAN | Equipment Failure | 947303 | 1963 | 83 | 147865 | 0.090308 | 0.11989
2013-03-01 | 504:48031 | SHORT RURAL | Vegetation | 947316 | 533 | 199 | 31829 | 0.01944 | 0.032553
2013-03-04 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 947329 | 94 | 150 | 14100 | 0.0086116 | 0.005741
2013-03-04 | ZN14891:PA12 | SHORT RURAL | Other | 947355 | 1 | 565.45 | 565.45 | 0.00034535 | 6.1075e-05
2013-03-04 | ZN2196:PA17 | URBAN | Equipment Failure | 947382 | 23 | 316 | 7268 | 0.0044389 | 0.0014047
2013-03-04 | 501:48115 | SHORT RURAL | Other | 947402 | 1 | 175.3333 | 175.3333 | 0.00010708 | 6.1075e-05
2013-03-04 | ZN116:PA36 | URBAN | Third Party Impacts | 947407 | 1 | 339.1833 | 339.1833 | 0.00020716 | 6.1075e-05
2013-03-04 | ZN12630:PA1 | SHORT RURAL | Other | 947412 | 1 | 443.35 | 443.35 | 0.00027078 | 6.1075e-05
2013-03-04 | 502:48004 | URBAN | Other | 947419 | 1 | 232.2667 | 232.2667 | 0.00014186 | 6.1075e-05
2013-03-04 | 513:48050 | SHORT RURAL | Other | 947432 | 1 | 41.9667 | 41.9667 | 2.5631e-05 | 6.1075e-05
2013-03-04 | ZN14892:PA19 | URBAN | Equipment Failure | 947437 | 1722 | 154 | 123322 | 0.075319 | 0.10517
2013-03-04 | ZN12570:PA24 | SHORT RURAL | Equipment Failure | 947443 | 440 | 76.9333 | 33850.6667 | 0.020674 | 0.026873
2013-03-04 | ZN263:PA33 34KLM | CBD | Equipment Failure | 947454 | 38 | 3919 | 126372 | 0.077182 | 0.0023208
2013-03-04 | 206:34441 | URBAN | Other | 947491 | 1 | 222.3333 | 222.3333 | 0.00013579 | 6.1075e-05
2013-03-04 | ZN14892:PA19 | URBAN | Other | 947500 | 1 | 22.2333 | 22.2333 | 1.3579e-05 | 6.1075e-05
2013-03-04 | ZN14892:PA19 | URBAN | Equipment Failure | 947505 | 27 | 90 | 2430 | 0.0014841 | 0.001649
2013-03-04 | ZN2310:PA10 | URBAN | Equipment Failure | 947508 | 1 | 156.45 | 156.45 | 9.5552e-05 | 6.1075e-05
2013-03-05 | ZN4545:PA41 | URBAN | Equipment Failure | 947515 | 154 | 123.1667 | 18967.6667 | 0.011578 | 0.0094005
2013-03-05 | ZN263:PA33 34DEF | CBD | Other | 947531 | 1 | 249.2833 | 249.2833 | 0.00015217 | 6.1042e-05
2013-03-05 | ZN342:PA18 | URBAN | Equipment Failure | 947532 | 39 | 231.4333 | 9025.9 | 0.0055096 | 0.0023806
2013-03-05 | ZN180:PA41 | URBAN | Equipment Failure | 947548 | 1 | 233.4167 | 233.4167 | 0.00014248 | 6.1042e-05
2013-03-05 | 501:48115 | SHORT RURAL | Other | 947549 | 1 | 172.9667 | 172.9667 | 0.00010558 | 6.1042e-05
2013-03-05 | 813:89055 | SHORT RURAL | Other | 947550 | 1 | 137.5833 | 137.5833 | 8.3984e-05 | 6.1042e-05
2013-03-02 | 512:48048 | SHORT RURAL | Vegetation | 947551 | 487 | 117 | 34418 | 0.021021 | 0.029743
2013-03-05 | ZN12610:PA10 | SHORT RURAL | Other | 947584 | 1 | 324.8833 | 324.8833 | 0.00019832 | 6.1042e-05
2013-03-01 | ZN188:PA1 | URBAN | Third Party Impacts | 947596 | 15 | 20 | 300 | 0.00018322 | 0.00091612
2013-03-05 | ZN12580:PA12 | SHORT RURAL | Third Party Impacts | 947644 | 1 | 225.3667 | 225.3667 | 0.00013757 | 6.1042e-05
2013-03-02 | ZN14891:PA12 | SHORT RURAL | Vegetation | 947661 | 3 | 17 | 51 | 3.1148e-05 | 0.00018322
2013-03-04 | 810:74050 | SHORT RURAL | Vegetation | 947719 | 47 | 364 | 8936 | 0.0054577 | 0.0028705
2013-03-05 | ZN3922:PA26 | URBAN | Other | 947735 | 1 | 73.3333 | 73.3333 | 4.4764e-05 | 6.1042e-05
2013-03-05 | 510:48164 | SHORT RURAL | Equipment Failure | 947849 | 371 | 322 | 25482 | 0.015555 | 0.022647
2013-03-05 | ZN2310:PA20 | URBAN | Equipment Failure | 947855 | 1 | 446.85 | 446.85 | 0.00027277 | 6.1042e-05
2013-03-05 | 515:35193 | SHORT RURAL | Equipment Failure | 947884 | 150 | 503 | 26402 | 0.016116 | 0.0091563
2013-03-05 | ZN4545:PA17 | URBAN | Equipment Failure | 947913 | 1 | 452.2833 | 452.2833 | 0.00027608 | 6.1042e-05
2013-03-05 | ZN72:PA10 | URBAN | Vegetation | 947916 | 103 | 76.7167 | 7901.8167 | 0.0048234 | 0.0062873
2013-03-05 | 261:81879 | URBAN | Other | 947941 | 1 | 143.75 | 143.75 | 8.7748e-05 | 6.1042e-05
2013-03-05 | 232:11457 | URBAN | Other | 947979 | 1 | 310.7167 | 310.7167 | 0.00018967 | 6.1042e-05
2013-03-05 | 509:48039 | LONG RURAL | Vegetation | 947993 | 30 | 956.4667 | 28694 | 0.017515 | 0.0018313
2013-03-05 | 509:48039 | LONG RURAL | Equipment Failure | 947998 | 1 | 1009.7 | 1009.7 | 0.00061634 | 6.1042e-05
2013-03-06 | ZN188:PA41 | URBAN | Other | 948019 | 58 | 228.9667 | 13280.0667 | 0.0081065 | 0.0035405
2013-03-05 | 232:11457 | URBAN | Equipment Failure | 948028 | 1 | 95 | 95 | 5.799e-05 | 6.1042e-05
2013-03-06 | 512:48049 | SHORT RURAL | Other | 948077 | 7 | 114 | 798 | 0.00048712 | 0.0004273
2013-03-06 | ZN262:PA34 | URBAN | Third Party Impacts | 948084 | 12 | 562 | 6744 | 0.0041167 | 0.00073251
2013-03-06 | ZN3154:PA17 | URBAN | Vegetation | 948121 | 20 | 25 | 500 | 0.00030521 | 0.0012208
2013-03-06 | 242:81539 | URBAN | Other | 948217 | 1 | 216.1333 | 216.1333 | 0.00013193 | 6.1042e-05
2013-03-06 | ZN80:PA25 | URBAN | Vegetation | 948258 | 1 | 299.4333 | 299.4333 | 0.00018278 | 6.1042e-05
2013-03-06 | 510:48164 | SHORT RURAL | Other | 948263 | 13 | 166 | 2158 | 0.0013173 | 0.00079355
2013-03-06 | 243:80080 | SHORT RURAL | Other | 948272 | 1 | 37.1667 | 37.1667 | 2.2687e-05 | 6.1042e-05
2013-03-06 | ZN14891:PA12 | SHORT RURAL | Vegetation | 948284 | 1 | 117.5833 | 117.5833 | 7.1776e-05 | 6.1042e-05
2013-03-06 | ZN15005:PA6 | URBAN | Equipment Failure | 948309 | 956 | 146 | 139576 | 0.085201 | 0.058357
2013-03-06 | ZN847:PA18 | URBAN | Equipment Failure | 948376 | 42 | 85 | 3570 | 0.0021792 | 0.0025638
2013-03-06 | ZN15006:PA9 | URBAN | Equipment Failure | 948406 | 1 | 141.3333 | 141.3333 | 8.6273e-05 | 6.1042e-05
2013-03-06 | 227:13015 | SHORT RURAL | Other | 948415 | 10 | 394.6333 | 3946.3333 | 0.0024089 | 0.00061042
2013-03-07 | ZN12660:PA14 | SHORT RURAL | Equipment Failure | 948417 | 54 | 219.1 | 11831.4 | 0.0072222 | 0.0032963
2013-03-07 | ZN15014:PA19 | URBAN | Equipment Failure | 948425 | 1 | 268.2 | 268.2 | 0.00016372 | 6.1043e-05
2013-03-07 | ZN690:PA14 | URBAN | Third Party Impacts | 948427 | 7 | 265 | 1855 | 0.0011323 | 0.0004273
2013-03-07 | ZN13000:PA11 | URBAN | Vegetation | 948428 | 1 | 226.0667 | 226.0667 | 0.000138 | 6.1043e-05
2013-03-07 | ZN10997:PA1 | URBAN | Equipment Failure | 948442 | 2 | 110 | 220 | 0.00013429 | 0.00012209
2013-03-07 | ZN10997:PA7 | URBAN | Equipment Failure | 948442 | 91 | 110 | 9975.1167 | 0.0060891 | 0.0055549
2013-03-07 | 509:48040 | SHORT RURAL | Equipment Failure | 948477 | 66 | 70 | 4620 | 0.0028202 | 0.0040288
2013-03-07 | ZN262:PA6 | URBAN | Third Party Impacts | 948554 | 57 | 120 | 6840 | 0.0041753 | 0.0034794
2013-03-07 | ZN12620:PA7 | URBAN | Equipment Failure | 948637 | 1 | 98.2667 | 98.2667 | 5.9985e-05 | 6.1043e-05
2013-03-07 | ZN14144:PA7 | SHORT RURAL | Other | 948669 | 1 | 18.2833 | 18.2833 | 1.1161e-05 | 6.1043e-05
2013-02-24 | 243:80083 | SHORT RURAL | Equipment Failure | 948692 | 1 | 1165 | 1165 | 0.00071149 | 6.1072e-05
2013-03-07 | ZN1164:PA3 | URBAN | Other | 948720 | 131 | 96.4667 | 12637.1333 | 0.007714 | 0.0079966
2013-03-07 | ZN12650:PA12 | URBAN | Vegetation | 948726 | 1 | 212.75 | 212.75 | 0.00012987 | 6.1043e-05
2013-03-07 | ZN8700:PA61 62KLM | CBD | Equipment Failure | 948727 | 1 | 293.5167 | 293.5167 | 0.00017917 | 6.1043e-05
2013-03-07 | ZN965:PA47 | URBAN | Animals | 948796 | 1 | 17.5167 | 17.5167 | 1.0693e-05 | 6.1043e-05
2013-03-07 | ZN965:PA47 | URBAN | Third Party Impacts | 948811 | 18 | 64 | 1152 | 0.00070321 | 0.0010988
2013-03-07 | ZN116:PA35 | URBAN | Other | 948846 | 1 | 262.5833 | 262.5833 | 0.00016029 | 6.1043e-05
2013-03-07 | 504:48026 | SHORT RURAL | Other | 948855 | 83 | 50.3833 | 4181.8167 | 0.0025527 | 0.0050665
2013-03-07 | ZN1164:PA12 | URBAN | Equipment Failure | 948869 | 808 | 67 | 49184 | 0.030023 | 0.049322
2013-03-07 | ZN1164:PA15 | URBAN | Equipment Failure | 948869 | 1 | 67 | 67 | 4.0899e-05 | 6.1043e-05
2013-03-07 | ZN13000:PA5 | SHORT RURAL | Equipment Failure | 948880 | 47 | 91.8167 | 4315.3833 | 0.0026342 | 0.002869
2013-03-07 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 948883 | 209 | 637 | 27472 | 0.01677 | 0.012758
2013-03-08 | ZN1788:PA11 | URBAN | Equipment Failure | 948895 | 486 | 173 | 81023 | 0.04946 | 0.029667
2013-03-08 | ZN1788:PA14 | URBAN | Equipment Failure | 948895 | 1092 | 173 | 41496 | 0.025331 | 0.06666
2013-03-08 | ZN2835:PA35 | URBAN | Equipment Failure | 948897 | 58 | 157.8333 | 9154.3333 | 0.0055882 | 0.0035405
2013-03-08 | ZN12570:PA37 | SHORT RURAL | Equipment Failure | 948901 | 22 | 250 | 5500 | 0.0033574 | 0.001343
2013-03-08 | ZN10996:PA19 | URBAN | Equipment Failure | 949045 | 1 | 431.3333 | 431.3333 | 0.0002633 | 6.1044e-05
2013-03-08 | 224:80346 | URBAN | Other | 949123 | 1 | 97.05 | 97.05 | 5.9243e-05 | 6.1044e-05
2013-03-08 | ZN35500:PA28 | URBAN | Other | 949138 | 1 | 108.4167 | 108.4167 | 6.6182e-05 | 6.1044e-05
2013-03-08 | 511:29880 | URBAN | Other | 949139 | 1 | 114.75 | 114.75 | 7.0048e-05 | 6.1044e-05
2013-03-08 | 224:80341 | URBAN | Other | 949143 | 1 | 181.0333 | 181.0333 | 0.00011051 | 6.1044e-05
2013-03-08 | 225:33679 | URBAN | Third Party Impacts | 949157 | 1 | 123.95 | 123.95 | 7.5664e-05 | 6.1044e-05
2013-03-08 | 813:89055 | SHORT RURAL | Other | 949197 | 2 | 31 | 62 | 3.7847e-05 | 0.00012209
2013-03-08 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 949201 | 1 | 320.45 | 320.45 | 0.00019561 | 6.1044e-05
2013-03-08 | ZN12650:PA1 | SHORT RURAL | Other | 949221 | 13 | 142.3333 | 1850.3333 | 0.0011295 | 0.00079357
2013-03-09 | ZN9700:PA23 | URBAN | Other | 949225 | 49 | 144.1833 | 7064.9833 | 0.0043127 | 0.0029911
2013-03-09 | ZN965:PA8 | URBAN | Equipment Failure | 949238 | 30 | 560.0667 | 7917.55 | 0.0048332 | 0.0018313
2013-03-09 | ZN965:PA24 | SHORT RURAL | Other | 949246 | 25 | 116 | 2900 | 0.0017703 | 0.0015261
2013-03-09 | ZN965:PA20 | URBAN | Other | 949262 | 1 | 133.55 | 133.55 | 8.1524e-05 | 6.1044e-05
2013-03-09 | ZN180:PA19 | URBAN | Other | 949264 | 1 | 74.35 | 74.35 | 4.5386e-05 | 6.1044e-05
2013-03-09 | ZN12650:PA6 | URBAN | Other | 949276 | 1 | 249.3 | 249.3 | 0.00015218 | 6.1044e-05
2013-03-09 | ZN12610:PA2 | URBAN | Vegetation | 949293 | 1 | 50.95 | 50.95 | 3.1102e-05 | 6.1044e-05
2013-03-09 | 243:80084 | SHORT RURAL | Other | 949296 | 1 | 95.3667 | 95.3667 | 5.8215e-05 | 6.1044e-05
2013-03-09 | 512:48049 | SHORT RURAL | Other | 949315 | 1 | 76.75 | 76.75 | 4.6851e-05 | 6.1044e-05
2013-03-09 | ZN3472:PA21 | URBAN | Third Party Impacts | 949319 | 74 | 59.25 | 4384.5 | 0.0026765 | 0.0045172
2013-03-09 | ZN12630:PA1 | SHORT RURAL | Equipment Failure | 949324 | 3 | 205 | 615 | 0.00037542 | 0.00018313
2013-03-09 | ZN10990:PA1 | URBAN | Equipment Failure | 949340 | 1 | 535.7333 | 535.7333 | 0.00032703 | 6.1044e-05
2013-03-09 | ZN35370:PA8 | SHORT RURAL | Equipment Failure | 949356 | 13 | 66 | 858 | 0.00052376 | 0.00079357
2013-03-09 | ZN8000:PA25 | URBAN | Equipment Failure | 949363 | 1 | 180.6667 | 180.6667 | 0.00011029 | 6.1044e-05
2013-03-09 | 812:19066 | SHORT RURAL | Equipment Failure | 949365 | 1 | 149.9167 | 149.9167 | 9.1515e-05 | 6.1044e-05
2013-03-09 | ZN269:PA18 | URBAN | Equipment Failure | 949369 | 32 | 132 | 4224 | 0.0025785 | 0.0019534
2013-03-10 | 234:2001 | URBAN | Other | 949373 | 1 | 270 | 270 | 0.00016482 | 6.1044e-05
2013-03-10 | ZN15012:PA2 | URBAN | Animals | 949374 | 1319 | 41 | 54079 | 0.033012 | 0.080517
2013-03-10 | ZN15012:PA4 | URBAN | Animals | 949374 | 1186 | 41 | 48626 | 0.029683 | 0.072398
2013-03-10 | ZN15012:PA6 | URBAN | Animals | 949374 | 1387 | 41 | 56867 | 0.034714 | 0.084668
2013-03-10 | ZN15012:PA8 | URBAN | Animals | 949374 | 1149 | 41 | 47109 | 0.028757 | 0.070139
2013-03-10 | 504:48033 | SHORT RURAL | Other | 949378 | 1 | 113.4 | 113.4 | 6.9224e-05 | 6.1044e-05
2013-03-10 | ZN14892:PA16 | URBAN | Other | 949399 | 1 | 166.6833 | 166.6833 | 0.00010175 | 6.1044e-05
2013-03-10 | ZN2835:PA35 | URBAN | Equipment Failure | 949412 | 94 | 263 | 24706.5333 | 0.015082 | 0.0057381
2013-03-10 | 234:2001 | URBAN | Other | 949416 | 134 | 59.65 | 7993.1 | 0.0048793 | 0.0081799
2013-03-10 | ZN2568:PA32 | URBAN | Equipment Failure | 949427 | 2338 | 62 | 85703 | 0.052316 | 0.14272
2013-03-10 | 515:35197 | LONG RURAL | Other | 949438 | 5 | 120 | 600 | 0.00036626 | 0.00030522
2013-03-10 | ZN3472:PA33 | URBAN | Other | 949440 | 1 | 310.4833 | 310.4833 | 0.00018953 | 6.1044e-05
2013-03-10 | 801:74123 | SHORT RURAL | Equipment Failure | 949442 | 2 | 135 | 270 | 0.00016482 | 0.00012209
2013-03-10 | 523:33501 | SHORT RURAL | Equipment Failure | 949462 | 1 | 218 | 218 | 0.00013308 | 6.1044e-05
2013-03-10 | ZN2466:PA45 | URBAN | Other | 949465 | 1 | 353.95 | 353.95 | 0.00021606 | 6.1044e-05
2013-03-11 | 511:29876 | SHORT RURAL | Equipment Failure | 949478 | 1 | 272.4 | 272.4 | 0.00016628 | 6.1044e-05
2013-03-11 | 216:10723 | URBAN | Other | 949517 | 1 | 36.1 | 36.1 | 2.2037e-05 | 6.1044e-05
2013-03-07 | 526:34636 | SHORT RURAL | Other | 949544 | 64 | 61 | 3904 | 0.0023831 | 0.0039067
2013-03-11 | ZN35500:PA14 | URBAN | Equipment Failure | 949608 | 16 | 76 | 1216 | 0.00074229 | 0.0009767
2013-03-11 | ZN35500:PA32 | URBAN | Equipment Failure | 949608 | 534 | 76 | 33312 | 0.020335 | 0.032597
2013-03-07 | 238:34144 | URBAN | Equipment Failure | 949624 | 143 | 60 | 7885 | 0.0048132 | 0.0087291
2013-03-11 | ZN8000:PA19 | URBAN | Other | 949628 | 1 | 86.3667 | 86.3667 | 5.2721e-05 | 6.1044e-05
2013-03-11 | ZN12640:PA7 | URBAN | Equipment Failure | 949716 | 120 | 104.9333 | 12592 | 0.0076866 | 0.0073253
2013-03-11 | ZN15014:PA11 | URBAN | Third Party Impacts | 949722 | 1 | 120.1333 | 120.1333 | 7.3334e-05 | 6.1044e-05
2013-03-11 | ZN15014:PA11 | URBAN | Third Party Impacts | 949735 | 22 | 20 | 440 | 0.00026859 | 0.001343
2013-03-11 | 503:48011 | SHORT RURAL | Other | 949793 | 1 | 83.9667 | 83.9667 | 5.1256e-05 | 6.1044e-05
2013-03-11 | 222:2014 | URBAN | Other | 949828 | 1 | 485 | 485 | 0.00029606 | 6.1044e-05
2013-03-11 | ZN342:PA24 | URBAN | Equipment Failure | 949885 | 36 | 130 | 4680 | 0.0028568 | 0.0021976
2013-03-11 | 229:34995 | SHORT RURAL | Other | 949887 | 18 | 64 | 1152 | 0.00070322 | 0.0010988
2013-03-12 | ZN35370:PA10 | SHORT RURAL | Other | 949889 | 188 | 100 | 12922 | 0.0078863 | 0.011474
2013-03-12 | ZN1287:PA18 | URBAN | Equipment Failure | 949892 | 1 | 142.5167 | 142.5167 | 8.6978e-05 | 6.103e-05
2013-03-12 | ZN3425:PA35 | URBAN | Other | 949893 | 1 | 536.1333 | 536.1333 | 0.0003272 | 6.103e-05
2013-03-12 | 229:34983 | SHORT RURAL | Equipment Failure | 949895 | 31 | 145.1167 | 3090.6667 | 0.0018862 | 0.0018919
2013-03-12 | 510:48164 | SHORT RURAL | Equipment Failure | 949915 | 1 | 214.4 | 214.4 | 0.00013085 | 6.103e-05
2013-03-12 | 501:48123 | SHORT RURAL | Other | 949952 | 20 | 217.9833 | 4359.6667 | 0.0026607 | 0.0012206
2013-03-12 | ZN180:PA42 | URBAN | Equipment Failure | 949980 | 1 | 382.3167 | 382.3167 | 0.00023333 | 6.103e-05
2013-03-11 | 526:34640 | SHORT RURAL | Equipment Failure | 949992 | 6 | 30 | 180 | 0.00010988 | 0.00036626
2013-03-12 | ZN342:PA23 | URBAN | Equipment Failure | 950003 | 1 | 464 | 461.7833 | 0.00028183 | 6.103e-05
2013-03-12 | ZN342:PA24 | URBAN | Equipment Failure | 950003 | 35 | 464 | 13760 | 0.0083977 | 0.002136
2013-03-12 | 219:1785 | URBAN | Vegetation | 950018 | 1 | 352.45 | 352.45 | 0.0002151 | 6.103e-05
2013-03-12 | 206:34434 | URBAN | Other | 950034 | 27 | 49.9 | 1347.3 | 0.00082225 | 0.0016478
2013-03-12 | ZN9550:PA11 | URBAN | Equipment Failure | 950096 | 17 | 56.7667 | 965.0333 | 0.00058896 | 0.0010375
2013-03-12 | 801:74123 | SHORT RURAL | Other | 950121 | 4 | 86 | 344 | 0.00020994 | 0.00024412
2013-03-12 | ZN1193:PA17 | URBAN | Equipment Failure | 950141 | 53 | 253 | 12667 | 0.0077306 | 0.0032346
2013-03-12 | ZN1193:PA28 | URBAN | Equipment Failure | 950141 | 604 | 253 | 78748 | 0.04806 | 0.036862
2013-03-12 | ZN35500:PA14 | URBAN | Equipment Failure | 950141 | 25 | 253 | 3175 | 0.0019377 | 0.0015257
2013-03-12 | ZN35500:PA32 | URBAN | Equipment Failure | 950141 | 130 | 253 | 16510 | 0.010076 | 0.0079339
2013-03-12 | ZN398:PA15 | URBAN | Equipment Failure | 950147 | 1 | 461.95 | 461.95 | 0.00028193 | 6.103e-05
2013-03-12 | ZN1193:PA28 | URBAN | Equipment Failure | 950148 | 710 | 239 | 169690 | 0.10356 | 0.043331
2013-03-12 | ZN3425:PA43 | URBAN | Equipment Failure | 950168 | 1294 | 74 | 87550 | 0.053432 | 0.078973
2013-03-12 | ZN129:PA4 | URBAN | Equipment Failure | 950177 | 1 | 346 | 346 | 0.00021116 | 6.103e-05
2013-03-12 | ZN965:PA43 | URBAN | Vegetation | 950202 | 1 | 241.1667 | 241.1667 | 0.00014718 | 6.103e-05
2013-03-12 | ZN80:PA31 | URBAN | Vegetation | 950208 | 789 | 72 | 56808 | 0.03467 | 0.048153
2013-03-12 | ZN80:PA32 | URBAN | Vegetation | 950212 | 104 | 453 | 47112 | 0.028752 | 0.0063471
2013-03-12 | 222:2017 | URBAN | Other | 950224 | 1 | 90.4833 | 90.4833 | 5.5222e-05 | 6.103e-05
2013-03-12 | 524:33576 | SHORT RURAL | Other | 950229 | 1 | 145.4667 | 145.4667 | 8.8778e-05 | 6.103e-05
2013-03-12 | 219:1783 | SHORT RURAL | Equipment Failure | 950264 | 1270 | 73 | 92710 | 0.056581 | 0.077508
2013-03-12 | ZN4545:PA31 | URBAN | Other | 950283 | 96 | 145 | 13890.3333 | 0.0084772 | 0.0058589
2013-03-12 | 509:48039 | LONG RURAL | Equipment Failure | 950292 | 56 | 100 | 5600 | 0.0034177 | 0.0034177
2013-03-12 | 243:80075 | SHORT RURAL | Other | 950299 | 1 | 224.6667 | 224.6667 | 0.00013711 | 6.103e-05
2013-03-12 | 216:10729 | URBAN | Other | 950319 | 1 | 126.15 | 126.15 | 7.6989e-05 | 6.103e-05
2013-03-12 | ZN2196:PA18 | URBAN | Equipment Failure | 950331 | 930 | 103 | 87326 | 0.053295 | 0.056758
2013-03-12 | ZN35800:PA1 | URBAN | Equipment Failure | 950331 | 93 | 103 | 8091 | 0.0049379 | 0.0056758
2013-03-12 | 513:48059 | SHORT RURAL | Animals | 950334 | 1 | 119 | 119 | 7.2625e-05 | 6.103e-05
2013-03-12 | 203:8088 | URBAN | Other | 950335 | 57 | 52 | 2964 | 0.0018089 | 0.0034787
2013-03-13 | 214:8665 | URBAN | Other | 950337 | 1 | 203.7 | 203.7 | 0.00012432 | 6.1031e-05
2013-03-13 | ZN3472:PA31 | URBAN | Equipment Failure | 950338 | 1 | 551.8333 | 551.8333 | 0.00033679 | 6.1031e-05
2013-03-13 | 523:33508 | SHORT RURAL | Other | 950345 | 1 | 93.7167 | 93.7167 | 5.7196e-05 | 6.1031e-05
2013-03-13 | ZN129:PA19 | URBAN | Equipment Failure | 950362 | 1 | 140.4 | 140.4 | 8.5687e-05 | 6.1031e-05
2013-03-13 | 203:8088 | URBAN | Other | 950407 | 1 | 258.1833 | 258.1833 | 0.00015757 | 6.1031e-05
2013-03-12 | 243:80074 | URBAN | Third Party Impacts | 950477 | 6 | 161 | 966 | 0.00058955 | 0.00036618
2013-03-13 | ZN340:PA2 | URBAN | Operational Error | 950509 | 1 | 402.0833 | 402.0833 | 0.00024539 | 6.1031e-05
2013-03-13 | 208:58 | URBAN | Other | 950543 | 1 | 54.3167 | 54.3167 | 3.315e-05 | 6.1031e-05
2013-03-13 | ZN15005:PA2 | URBAN | Vegetation | 950569 | 1 | 238.4333 | 238.4333 | 0.00014552 | 6.1031e-05
2013-03-13 | 810:74054 | LONG RURAL | Other | 950579 | 1 | 129.4167 | 129.4167 | 7.8984e-05 | 6.1031e-05
2013-03-13 | 227:13019 | SHORT RURAL | Other | 950586 | 1 | 118.3667 | 118.3667 | 7.224e-05 | 6.1031e-05
2013-03-03 | 510:48164 | SHORT RURAL | Other | 950593 | 2 | 1918 | 3836 | 0.0023428 | 0.00012215
2012-08-10 | 203:8083 | SHORT RURAL | Equipment Failure | 950614 | 135 | 114 | 15390 | 0.0094031 | 0.0082483
2012-08-10 | 203:8089 | URBAN | Equipment Failure | 950614 | 2 | 114 | 228 | 0.0001393 | 0.0001222
2013-03-13 | ZN690:PA17 | URBAN | Vegetation | 950627 | 1 | 165.3833 | 165.3833 | 0.00010093 | 6.1031e-05
2013-03-13 | ZN2635:PA17 | URBAN | Other | 950667 | 38 | 187 | 7106 | 0.0043368 | 0.0023192
2013-03-13 | ZN398:PA24 | URBAN | Vegetation | 950671 | 31 | 96 | 2974.5 | 0.0018154 | 0.001892
2013-03-13 | ZN1673:PA9 | URBAN | Vegetation | 950690 | 1 | 243.9667 | 243.9667 | 0.00014889 | 6.1031e-05
2013-03-13 | 511:29877 | SHORT RURAL | Other | 950707 | 1 | 164.2167 | 164.2167 | 0.00010022 | 6.1031e-05
2013-03-13 | ZN1788:PA14 | URBAN | Other | 950711 | 1 | 1203.8 | 1203.8 | 0.00073469 | 6.1031e-05
2013-03-14 | ZN2602:PA29 | URBAN | Equipment Failure | 950744 | 101 | 1100.9833 | 111199.3167 | 0.067866 | 0.0061641
2013-03-14 | 516:48066 | SHORT RURAL | Other | 950749 | 1 | 197.2 | 197.2 | 0.00012035 | 6.1031e-05
2013-03-14 | ZN12620:PA1 | SHORT RURAL | Other | 950752 | 28 | 413.3333 | 11573.3333 | 0.0070633 | 0.0017089
2013-03-14 | 507:80920 | SHORT RURAL | Third Party Impacts | 950753 | 9 | 105 | 945 | 0.00057674 | 0.00054928
2013-03-14 | 501:48125 | URBAN | Other | 950765 | 1 | 121.0167 | 121.0167 | 7.3858e-05 | 6.1031e-05
2013-03-14 | 803:74016 | SHORT RURAL | Animals | 950774 | 1 | 110.05 | 110.05 | 6.7165e-05 | 6.1031e-05
2013-03-14 | 231:8405 | SHORT RURAL | Third Party Impacts | 950786 | 1 | 426.5167 | 426.5167 | 0.00026031 | 6.1031e-05
2013-03-14 | 814:82283 | SHORT RURAL | Other | 950807 | 1 | 103.2167 | 103.2167 | 6.2994e-05 | 6.1031e-05
2013-03-13 | 510:48164 | SHORT RURAL | Equipment Failure | 950819 | 1 | 30 | 30 | 1.8309e-05 | 6.1031e-05
2013-03-14 | ZN12570:PA40 | SHORT RURAL | Vegetation | 950822 | 1 | 56.9167 | 56.9167 | 3.4737e-05 | 6.1031e-05
2013-03-14 | ZN1285:PA24 | URBAN | Equipment Failure | 950837 | 74 | 237.8667 | 17602.1333 | 0.010743 | 0.0045163
2013-03-14 | ZN9118:PA12 | URBAN | Vegetation | 950860 | 24 | 57.5833 | 1382 | 0.00084345 | 0.0014647
2013-03-14 | 221:11900 | URBAN | Other | 950911 | 1 | 30.8833 | 30.8833 | 1.8848e-05 | 6.1031e-05
2013-03-14 | 513:48056 | SHORT RURAL | Vegetation | 950925 | 3 | 1780 | 5340 | 0.0032591 | 0.00018309
2012-10-31 | 210:8675 | URBAN | Other | 950959 | 53 | 202 | 10706 | 0.0065156 | 0.0032255
2013-03-14 | 507:80920 | SHORT RURAL | Third Party Impacts | 950970 | 1 | 58.9 | 58.9 | 3.5947e-05 | 6.1031e-05
2012-11-27 | 512:48049 | SHORT RURAL | Vegetation | 950978 | 4 | 50 | 200 | 0.00012167 | 0.00024335
2012-12-02 | 232:11454 | SHORT RURAL | Vegetation | 950987 | 79 | 350 | 27650 | 0.016821 | 0.0048061
2013-03-14 | 216:10723 | URBAN | Other | 950988 | 1 | 130.75 | 130.75 | 7.9798e-05 | 6.1031e-05
2013-03-14 | ZN10999:PA39 | URBAN | Third Party Impacts | 950989 | 1 | 86.0167 | 86.0167 | 5.2497e-05 | 6.1031e-05
2013-03-14 | 224:80340 | SHORT RURAL | Equipment Failure | 951016 | 1 | 143.05 | 143.05 | 8.7305e-05 | 6.1031e-05
2013-03-14 | ZN3425:PA12 | URBAN | Vegetation | 951098 | 42 | 10 | 420 | 0.00025633 | 0.0025633
2013-03-14 | 801:74118 | URBAN | Other | 951101 | 1 | 833.9167 | 833.9167 | 0.00050895 | 6.1031e-05
2013-03-14 | ZN1164:PA13 | URBAN | Other | 951121 | 75 | 55.5 | 4162.5 | 0.0025404 | 0.0045773
2013-03-15 | ZN1788:PA30 | URBAN | Third Party Impacts | 951130 | 60 | 76.0833 | 4565 | 0.0027861 | 0.0036619
2013-03-14 | 217:33612 | URBAN | Vegetation | 951133 | 69 | 86 | 5934 | 0.0036216 | 0.0042112
2013-03-15 | ZN3922:PA29 | URBAN | Other | 951149 | 1 | 587 | 587 | 0.00035826 | 6.1032e-05
2013-03-15 | ZN342:PA24 | URBAN | Equipment Failure | 951150 | 27 | 794 | 21438 | 0.013084 | 0.0016479
2013-03-15 | ZN931:PA18 | URBAN | Equipment Failure | 951150 | 2 | 794 | 1588 | 0.00096918 | 0.00012206
2013-03-15 | ZN931:PA26 | URBAN | Equipment Failure | 951150 | 20 | 794 | 580 | 0.00035398 | 0.0012206
2013-03-15 | ZN14144:PA7 | SHORT RURAL | Vegetation | 951152 | 1029 | 698 | 119202 | 0.072751 | 0.062802
2013-03-15 | ZN9037:PA9 | URBAN | Other | 951154 | 1 | 307.65 | 307.65 | 0.00018776 | 6.1032e-05
2013-03-15 | ZN15005:PA4 | URBAN | Animals | 951155 | 53 | 88.6833 | 4700.2167 | 0.0028686 | 0.0032347
2013-03-15 | 228:7490 | SHORT RURAL | Equipment Failure | 951158 | 2 | 69 | 138 | 8.4224e-05 | 0.00012206
2013-03-15 | ZN15004:PA3 | URBAN | Other | 951161 | 1 | 532.2167 | 532.2167 | 0.00032482 | 6.1032e-05
2013-03-15 | ZN3922:PA29 | URBAN | Other | 951178 | 1 | 267.4 | 267.4 | 0.0001632 | 6.1032e-05
2013-03-15 | ZN35500:PA35 | URBAN | Equipment Failure | 951193 | 9 | 184.4333 | 1659.9 | 0.0010131 | 0.00054929
2013-03-15 | 258:80785 | URBAN | Other | 951245 | 1 | 58.1667 | 58.1667 | 3.55e-05 | 6.1032e-05
2013-03-15 | 260:33347 | SHORT RURAL | Other | 951249 | 1 | 75.4833 | 75.4833 | 4.6069e-05 | 6.1032e-05
2013-03-15 | ZN12610:PA22 | URBAN | Other | 951269 | 1 | 204.8667 | 204.8667 | 0.00012503 | 6.1032e-05
2013-03-15 | 502:48010 | SHORT RURAL | Equipment Failure | 951286 | 1 | 221.5833 | 221.5833 | 0.00013524 | 6.1032e-05
2013-03-15 | 206:34441 | URBAN | Other | 951303 | 1 | 45.85 | 45.85 | 2.7983e-05 | 6.1032e-05
2013-03-15 | 511:29878 | SHORT RURAL | Equipment Failure | 951316 | 8 | 453 | 3624 | 0.0022118 | 0.00048825
2013-03-15 | ZN1164:PA9 | URBAN | Third Party Impacts | 951321 | 25 | 69.9833 | 1749.5833 | 0.0010678 | 0.0015258
2013-03-15 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 951346 | 1 | 1404.1833 | 1404.1833 | 0.000857 | 6.1032e-05
2013-03-15 | ZN12600:PA2 | SHORT RURAL | Equipment Failure | 951348 | 777 | 209 | 64418 | 0.039315 | 0.047422
2013-03-15 | 256:80640 | URBAN | Other | 951375 | 1 | 42.4 | 42.4 | 2.5877e-05 | 6.1032e-05
2013-03-15 | 202:34260 | URBAN | Equipment Failure | 951411 | 1 | 64.45 | 64.45 | 3.9335e-05 | 6.1032e-05
2013-03-15 | ZN14891:PA21 | SHORT RURAL | Equipment Failure | 951422 | 1 | 1479 | 1479 | 0.00090266 | 6.1032e-05
2013-03-15 | ZN9700:PA17 | URBAN | Vegetation | 951425 | 1 | 382.2667 | 382.2667 | 0.0002333 | 6.1032e-05
2013-03-15 | ZN12570:PA22 | URBAN | Vegetation | 951441 | 667 | 42 | 28014 | 0.017097 | 0.040708
2013-03-15 | ZN12600:PA2 | SHORT RURAL | Other | 951461 | 1 | 241.4167 | 241.4167 | 0.00014734 | 6.1032e-05
2013-03-15 | ZN1610:PA18 | URBAN | Equipment Failure | 951483 | 196 | 58 | 11368 | 0.0069381 | 0.011962
2013-03-15 | ZN9252:PA2 | URBAN | Other | 951508 | 1 | 247.8 | 247.8 | 0.00015124 | 6.1032e-05
2013-03-15 | 523:33501 | SHORT RURAL | Other | 951511 | 2 | 99 | 198 | 0.00012084 | 0.00012206
2013-03-15 | 261:81879 | URBAN | Other | 951513 | 1 | 51.05 | 51.05 | 3.1157e-05 | 6.1032e-05
2013-03-15 | ZN2400:PA26 | URBAN | Other | 951529 | 874 | 93 | 80796 | 0.049311 | 0.053342
2013-03-16 | ZN180:PA10 | URBAN | Equipment Failure | 951534 | 1329 | 82 | 102234 | 0.062395 | 0.081111
2013-03-16 | ZN15006:PA2 | URBAN | Other | 951564 | 1 | 265.4667 | 265.4667 | 0.00016202 | 6.1032e-05
2013-03-16 | ZN12640:PA15 | URBAN | Equipment Failure | 951568 | 2 | 439.6667 | 879.3333 | 0.00053667 | 0.00012206
2013-03-16 | ZN2835:PA9 | URBAN | Vegetation | 951579 | 1 | 264.9833 | 264.9833 | 0.00016172 | 6.1032e-05
2013-03-16 | 801:74123 | SHORT RURAL | Other | 951580 | 1 | 45 | 45 | 2.7464e-05 | 6.1032e-05
2013-03-16 | ZN180:PA24 | URBAN | Other | 951585 | 1 | 646.4667 | 646.4667 | 0.00039455 | 6.1032e-05
2013-03-16 | ZN8000:PA6 | URBAN | Other | 951587 | 1 | 633.9833 | 633.9833 | 0.00038693 | 6.1032e-05
2013-03-16 | ZN35800:PA4 | URBAN | Third Party Impacts | 951593 | 1 | 159.8667 | 159.8667 | 9.7569e-05 | 6.1032e-05
2013-03-16 | ZN4545:PA40 | URBAN | Other | 951602 | 1 | 452.45 | 452.45 | 0.00027614 | 6.1032e-05
2013-03-16 | 227:13015 | SHORT RURAL | Equipment Failure | 951613 | 315 | 318 | 81252 | 0.049589 | 0.019225
2013-03-16 | ZN116:PA50 | URBAN | Equipment Failure | 951631 | 45 | 80 | 3600 | 0.0021971 | 0.0027464
2013-03-16 | 234:14291 | URBAN | Other | 951647 | 1 | 63.9833 | 63.9833 | 3.905e-05 | 6.1032e-05
2013-03-16 | 234:14291 | URBAN | Other | 951648 | 1 | 57.9667 | 57.9667 | 3.5378e-05 | 6.1032e-05
2013-03-16 | ZN9118:PA26 | URBAN | Other | 951657 | 1 | 65.7833 | 65.7833 | 4.0149e-05 | 6.1032e-05
2013-03-17 | ZN9037:PA16 | URBAN | Other | 951662 | 1 | 710.25 | 710.25 | 0.00043348 | 6.1032e-05
2013-03-17 | ZN4545:PA41 | URBAN | Animals | 951665 | 76 | 45 | 3420 | 0.0020873 | 0.0046384
2013-03-17 | ZN2635:PA1 | URBAN | Vegetation | 951672 | 52 | 272.4 | 14117.1333 | 0.0086159 | 0.0031736
2013-03-17 | ZN965:PA35 | URBAN | Vegetation | 951672 | 7 | 272.4 | 1750 | 0.0010681 | 0.00042722
2013-03-17 | ZN262:PA20 | URBAN | Other | 951674 | 8 | 235 | 1880 | 0.0011474 | 0.00048825
2013-03-17 | ZN340:PA28 | SHORT RURAL | Vegetation | 951680 | 15 | 146 | 2190 | 0.0013366 | 0.00091548
2013-03-17 | ZN3288:PA41 42KLM | CBD | Equipment Failure | 951683 | 28 | 206 | 5768 | 0.0035203 | 0.0017089
2013-03-17 | ZN2310:PA25 | URBAN | Other | 951687 | 85 | 56 | 4698.4 | 0.0028675 | 0.0051877
2013-03-17 | 232:11460 | URBAN | Other | 951711 | 1 | 90 | 90 | 5.4929e-05 | 6.1032e-05
2013-03-17 | ZN12610:PA22 | URBAN | Equipment Failure | 951714 | 1 | 272.35 | 272.35 | 0.00016622 | 6.1032e-05
2013-03-17 | ZN15014:PA18 | URBAN | Vegetation | 951724 | 37 | 180 | 6660 | 0.0040647 | 0.0022582
2013-03-17 | ZN12620:PA3 | URBAN | Other | 951740 | 1 | 74.8167 | 74.8167 | 4.5662e-05 | 6.1032e-05
2013-03-17 | ZN12690:PA7 | SHORT RURAL | Other | 951752 | 1 | 110.3667 | 110.3667 | 6.7359e-05 | 6.1032e-05
2013-03-17 | 205:12205 | URBAN | Equipment Failure | 951757 | 1198 | 45 | 33410 | 0.020391 | 0.073116
2013-03-17 | ZN12570:PA34 | SHORT RURAL | Vegetation | 951758 | 776 | 145 | 32132 | 0.019611 | 0.047361
2013-03-17 | ZN847:PA7 | URBAN | Equipment Failure | 951771 | 24 | 86.8 | 2083.2 | 0.0012714 | 0.0014648
2013-03-17 | ZN2568:PA14 | URBAN | Vegetation | 951790 | 3 | 25 | 75 | 4.5774e-05 | 0.0001831
2013-03-17 | 238:34151 | URBAN | Equipment Failure | 951802 | 1 | 99.1667 | 99.1667 | 6.0523e-05 | 6.1032e-05
2013-03-17 | ZN1068:PA27 | URBAN | Equipment Failure | 951810 | 3 | 103 | 309 | 0.00018859 | 0.0001831
2013-03-18 | ZN342:PA26 | URBAN | Equipment Failure | 951813 | 2536 | 69 | 170506 | 0.10406 | 0.15478
2013-03-18 | ZN15004:PA3 | URBAN | Equipment Failure | 951839 | 1 | 293.9333 | 293.9333 | 0.00017939 | 6.1032e-05
2013-03-18 | ZN116:PA32 | URBAN | Other | 951842 | 94 | 782 | 73508 | 0.044863 | 0.005737
2013-03-18 | 801:74123 | SHORT RURAL | Other | 951949 | 1 | 48.6 | 48.6 | 2.9661e-05 | 6.1032e-05
2013-03-18 | 807:74179 | SHORT RURAL | Equipment Failure | 952042 | 5 | 120 | 600 | 0.00036619 | 0.00030516
2013-03-18 | ZN10999:PA22 | URBAN | Vegetation | 952056 | 1 | 55.2833 | 55.2833 | 3.374e-05 | 6.1032e-05
2013-03-18 | 225:33673 | SHORT RURAL | Third Party Impacts | 952080 | 38 | 89 | 3382 | 0.0020641 | 0.0023192
2013-03-18 | ZN1164:PA15 | URBAN | Equipment Failure | 952111 | 1 | 388.3 | 388.3 | 0.00023699 | 6.1032e-05
2013-03-18 | 238:34137 | URBAN | Equipment Failure | 952142 | 1 | 166.9833 | 166.9833 | 0.00010191 | 6.1032e-05
2013-03-18 | 807:74184 | SHORT RURAL | Weather | 952169 | 1 | 1571.3833 | 1571.3833 | 0.00095904 | 6.1032e-05
2013-03-18 | ZN1673:PA7 | URBAN | Other | 952210 | 1 | 90.0167 | 90.0167 | 5.4939e-05 | 6.1032e-05
2013-03-18 | ZN15001:PA2 | URBAN | Other | 952248 | 1 | 598.2333 | 598.2333 | 0.00036511 | 6.1032e-05
2013-03-19 | ZN36300:PA17 | URBAN | Other | 952249 | 1 | 482.6 | 482.6 | 0.00029454 | 6.1033e-05
2013-03-19 | 256:80653 | URBAN | Third Party Impacts | 952250 | 2 | 71.8167 | 143.6333 | 8.7663e-05 | 0.00012207
2013-03-19 | ZN10994:PA4 | URBAN | Equipment Failure | 952259 | 1684 | 162 | 250569 | 0.15293 | 0.10278
2013-03-19 | ZN10995:PA2 | URBAN | Other | 952261 | 1 | 210.8333 | 210.8333 | 0.00012868 | 6.1033e-05
2013-03-18 | ZN2568:PA25 | URBAN | Vegetation | 952263 | 1 | 50 | 50 | 3.0516e-05 | 6.1032e-05
2013-03-19 | 813:89062 | SHORT RURAL | Other | 952270 | 58 | 58.5833 | 3397.8333 | 0.0020738 | 0.0035399
2013-03-19 | ZN10999:PA24 | URBAN | Other | 952302 | 1 | 57.4333 | 57.4333 | 3.5053e-05 | 6.1033e-05
2013-03-19 | 243:80075 | SHORT RURAL | Equipment Failure | 952309 | 171 | 564 | 10089 | 0.0061576 | 0.010437
2013-03-19 | 243:80080 | SHORT RURAL | Equipment Failure | 952309 | 1153 | 564 | 71977 | 0.04393 | 0.070371
2013-03-19 | 225:33673 | SHORT RURAL | Other | 952413 | 1 | 117.6 | 117.6 | 7.1774e-05 | 6.1033e-05
2013-03-19 | ZN15014:PA5 | URBAN | Equipment Failure | 952469 | 79 | 258.0833 | 20388.5833 | 0.012444 | 0.0048216
2013-03-19 | ZN1673:PA18 | URBAN | Vegetation | 952471 | 16 | 40 | 640 | 0.00039061 | 0.00097652
2013-03-19 | ZN12690:PA24 | SHORT RURAL | Vegetation | 952486 | 1 | 111.2667 | 111.2667 | 6.7909e-05 | 6.1033e-05
2013-03-19 | ZN12690:PA24 | SHORT RURAL | Vegetation | 952487 | 1 | 107.1667 | 107.1667 | 6.5407e-05 | 6.1033e-05
2013-03-19 | 501:48123 | SHORT RURAL | Equipment Failure | 952526 | 20 | 226.9667 | 4539.3333 | 0.0027705 | 0.0012207
2013-03-19 | 813:89061 | LONG RURAL | Equipment Failure | 952586 | 1 | 333 | 333 | 0.00020324 | 6.1033e-05
2013-03-19 | ZN2568:PA32 | URBAN | Equipment Failure | 952589 | 145 | 179.1 | 25969.5 | 0.01585 | 0.0088497
2013-03-20 | ZN3425:PA28 | URBAN | Equipment Failure | 952617 | 1 | 1243.2667 | 1243.2667 | 0.00075881 | 6.1033e-05
2013-03-19 | ZN9550:PA1 | URBAN | Third Party Impacts | 952618 | 28 | 70 | 1960 | 0.0011962 | 0.0017089
2013-03-20 | ZN690:PA5 | URBAN | Equipment Failure | 952712 | 1 | 625 | 625 | 0.00038146 | 6.1033e-05
2013-03-20 | 512:48046 | SHORT RURAL | Third Party Impacts | 952727 | 1 | 196.0833 | 196.0833 | 0.00011968 | 6.1033e-05
2013-03-20 | ZN1788:PA30 | URBAN | Other | 952771 | 73 | 56.4667 | 4122.0667 | 0.0025158 | 0.0044554
2013-03-20 | ZN12570:PA37 | SHORT RURAL | Equipment Failure | 952803 | 2027 | 216 | 279027 | 0.1703 | 0.12371
2013-03-20 | ZN4545:PA4 | URBAN | Other | 952913 | 40 | 455 | 18200 | 0.011108 | 0.0024413
2013-03-20 | 503:48011 | SHORT RURAL | Other | 952924 | 1 | 136.2167 | 136.2167 | 8.3138e-05 | 6.1033e-05
2013-03-13 | ZN1673:PA1 | URBAN | Other | 952925 | 36 | 70 | 2520 | 0.001538 | 0.0021971
2013-03-20 | ZN12600:PA3 | URBAN | Equipment Failure | 952930 | 34 | 120 | 4080 | 0.0024902 | 0.0020751
2013-03-20 | ZN12650:PA13 | SHORT RURAL | Equipment Failure | 952966 | 117 | 212.85 | 16188.8 | 0.0098806 | 0.0071409
2013-03-20 | ZN14891:PA1 | SHORT RURAL | Equipment Failure | 952986 | 1 | 53 | 53 | 3.2348e-05 | 6.1033e-05
2013-03-20 | 509:48040 | SHORT RURAL | Other | 952990 | 1 | 137.7 | 137.7 | 8.4043e-05 | 6.1033e-05
2013-03-20 | 812:19071 | SHORT RURAL | Other | 953009 | 1 | 93.9167 | 93.9167 | 5.7321e-05 | 6.1033e-05
2013-03-20 | 806:82656 | LONG RURAL | Equipment Failure | 953038 | 6 | 30 | 180 | 0.00010986 | 0.0003662
2013-03-20 | ZN129:PA18 | URBAN | Equipment Failure | 953057 | 45 | 99 | 4455 | 0.002719 | 0.0027465
2013-03-20 | ZN129:PA5 | URBAN | Equipment Failure | 953057 | 5 | 99 | 495 | 0.00030212 | 0.00030517
2013-03-20 | 502:48002 | URBAN | Other | 953062 | 1 | 140.85 | 140.85 | 8.5966e-05 | 6.1033e-05
2013-03-21 | ZN35370:PA10 | SHORT RURAL | Third Party Impacts | 953111 | 1 | 123.2167 | 123.2167 | 7.5204e-05 | 6.1034e-05
2013-03-21 | 514:18137 | SHORT RURAL | Animals | 953117 | 45 | 374 | 6572 | 0.0040111 | 0.0027465
2013-03-21 | ZN15004:PA9 | URBAN | Equipment Failure | 953139 | 1 | 145.45 | 145.45 | 8.8774e-05 | 6.1034e-05
2013-03-21 | 223:14394 | URBAN | Equipment Failure | 953148 | 1 | 91.95 | 91.95 | 5.6121e-05 | 6.1034e-05
2013-03-21 | 225:13444 | URBAN | Other | 953174 | 1 | 70.4833 | 70.4833 | 4.3019e-05 | 6.1034e-05
2013-03-21 | ZN12610:PA13 | URBAN | Other | 953224 | 1 | 322.0167 | 322.0167 | 0.00019654 | 6.1034e-05
2013-03-21 | ZN9252:PA2 | URBAN | Equipment Failure | 953230 | 28 | 178.9333 | 5010.1333 | 0.0030579 | 0.0017089
2013-03-21 | ZN15004:PA5 | URBAN | Other | 953239 | 35 | 125.6 | 4396 | 0.002683 | 0.0021362
2013-03-21 | 806:82656 | LONG RURAL | Equipment Failure | 953244 | 1 | 180.0667 | 180.0667 | 0.0001099 | 6.1034e-05
2013-03-21 | ZN10996:PA20 | URBAN | Other | 953281 | 1 | 91.5833 | 91.5833 | 5.5897e-05 | 6.1034e-05
2013-03-21 | 810:74062 | SHORT RURAL | Equipment Failure | 953328 | 48 | 34.5333 | 1657.6 | 0.0010117 | 0.0029296
2013-03-21 | 810:74062 | SHORT RURAL | Equipment Failure | 953330 | 1 | 33.9333 | 33.9333 | 2.0711e-05 | 6.1034e-05
2013-03-21 | ZN10997:PA2 | URBAN | Third Party Impacts | 953366 | 45 | 20 | 900 | 0.0005493 | 0.0027465
2013-03-21 | ZN12640:PA8 | SHORT RURAL | Equipment Failure | 953398 | 966 | 127 | 67871 | 0.041424 | 0.058959
2013-03-21 | ZN4545:PA2 | URBAN | Equipment Failure | 953414 | 888 | 118 | 57354 | 0.035005 | 0.054198
2013-03-21 | ZN4545:PA21 | URBAN | Equipment Failure | 953414 | 48 | 118 | 5664 | 0.003457 | 0.0029296
2013-03-21 | ZN10996:PA20 | URBAN | Equipment Failure | 953420 | 8 | 80 | 640 | 0.00039062 | 0.00048827
2013-03-21 | ZN35370:PA2 | SHORT RURAL | Other | 953421 | 1 | 142.7833 | 142.7833 | 8.7146e-05 | 6.1034e-05
2013-03-21 | ZN12630:PA1 | SHORT RURAL | Equipment Failure | 953429 | 9 | 80 | 720 | 0.00043944 | 0.0005493
2013-03-21 | 512:48049 | SHORT RURAL | Other | 953448 | 1 | 141.9833 | 141.9833 | 8.6658e-05 | 6.1034e-05
2013-03-21 | 523:33501 | SHORT RURAL | Other | 953451 | 1 | 59.5333 | 59.5333 | 3.6335e-05 | 6.1034e-05
2013-03-22 | ZN80:PA24 | URBAN | Other | 953482 | 1 | 103.65 | 103.65 | 6.3262e-05 | 6.1034e-05
2013-03-22 | ZN1673:PA1 | URBAN | Vegetation | 953515 | 50 | 100.7 | 5035 | 0.0030731 | 0.0030517
2013-03-22 | ZN80:PA24 | URBAN | Other | 953542 | 1 | 47.4833 | 47.4833 | 2.8981e-05 | 6.1034e-05
2013-03-22 | ZN15008:PA1 | URBAN | Vegetation | 953555 | 2285 | 46 | 105110 | 0.064153 | 0.13946
2013-03-22 | 806:82656 | LONG RURAL | Other | 953570 | 1 | 120 | 120 | 7.3241e-05 | 6.1034e-05
2013-03-22 | 225:33676 | SHORT RURAL | Other | 953573 | 1 | 87.85 | 87.85 | 5.3619e-05 | 6.1034e-05
2013-03-22 | 225:13446 | URBAN | Other | 953601 | 1 | 87.6 | 87.6 | 5.3466e-05 | 6.1034e-05
2013-03-22 | 264:81236 | URBAN | Equipment Failure | 953612 | 1 | 445.5833 | 445.5833 | 0.00027196 | 6.1034e-05
2013-03-22 | ZN4545:PA17 | URBAN | Vegetation | 953641 | 997 | 825 | 122438 | 0.074729 | 0.060851
2013-03-22 | 507:80922 | SHORT RURAL | Equipment Failure | 953661 | 1 | 113.95 | 113.95 | 6.9548e-05 | 6.1034e-05
2013-03-22 | ZN15012:PA6 | URBAN | Vegetation | 953670 | 4 | 167 | 668 | 0.00040771 | 0.00024414
2013-03-22 | ZN12620:PA11 | SHORT RURAL | Equipment Failure | 953683 | 14 | 154.4833 | 2162.7667 | 0.00132 | 0.00085448
2013-03-22 | ZN4545:PA19 | URBAN | Vegetation | 953691 | 64 | 707.1667 | 45258.6667 | 0.027623 | 0.0039062
2013-03-22 | ZN3672:PA9 | URBAN | Other | 953727 | 1 | 139.75 | 139.75 | 8.5295e-05 | 6.1034e-05
2013-03-22 | ZN9118:PA8 | URBAN | Vegetation | 953746 | 1 | 157.6 | 157.6 | 9.619e-05 | 6.1034e-05
2013-03-22 | ZN3922:PA12 | URBAN | Equipment Failure | 953806 | 2 | 300.55 | 600.4 | 0.00036645 | 0.00012207
2013-03-22 | ZN14891:PA12 | SHORT RURAL | Vegetation | 953807 | 1 | 162.8 | 162.8 | 9.9364e-05 | 6.1034e-05
2013-03-22 | ZN1788:PA15 | URBAN | Other | 953814 | 1 | 283.6833 | 283.6833 | 0.00017314 | 6.1034e-05
2013-03-22 | ZN1788:PA15 | URBAN | Other | 953815 | 1 | 99.4 | 99.4 | 6.0668e-05 | 6.1034e-05
2013-03-22 | 225:33679 | URBAN | Vegetation | 953845 | 1 | 62.1 | 62.1 | 3.7902e-05 | 6.1034e-05
2013-03-22 | ZN10994:PA11 | URBAN | Vegetation | 953854 | 1 | 180.9333 | 180.9333 | 0.00011043 | 6.1034e-05
2013-03-23 | ZN965:PA2 | URBAN | Vegetation | 953855 | 37 | 25 | 925 | 0.00056457 | 0.0022583
2013-03-22 | 803:74016 | SHORT RURAL | Other | 953869 | 2 | 66.9333 | 133.8667 | 8.1704e-05 | 0.00012207
2013-03-22 | ZN965:PA15 | URBAN | Weather | 953875 | 68 | 12 | 816 | 0.00049804 | 0.0041503
2013-03-23 | ZN14892:PA6 | SHORT RURAL | Equipment Failure | 953893 | 1 | 527.3333 | 527.3333 | 0.00032185 | 6.1034e-05
2013-03-23 | 801:74122 | URBAN | Other | 953905 | 1 | 127.0167 | 127.0167 | 7.7524e-05 | 6.1034e-05
2013-03-23 | ZN2400:PA22 | URBAN | Vegetation | 953906 | 1341 | 75 | 100575 | 0.061385 | 0.081847
2013-03-23 | ZN8000:PA6 | URBAN | Other | 953907 | 1 | 708.8167 | 708.8167 | 0.00043262 | 6.1034e-05
2013-03-23 | ZN12660:PA14 | SHORT RURAL | Other | 953928 | 1 | 225.8667 | 225.8667 | 0.00013786 | 6.1034e-05
2013-03-23 | ZN15010:PA5 | URBAN | Vegetation | 953934 | 1 | 299.8 | 299.8 | 0.00018298 | 6.1034e-05
2013-03-23 | 812:19066 | SHORT RURAL | Equipment Failure | 953954 | 1 | 168.7333 | 168.7333 | 0.00010299 | 6.1034e-05
2013-03-23 | ZN12630:PA3 | SHORT RURAL | Other | 953955 | 1 | 72.9333 | 72.9333 | 4.4514e-05 | 6.1034e-05
2013-03-23 | ZN12630:PA3 | SHORT RURAL | Vegetation | 953957 | 153 | 204 | 9071 | 0.0055364 | 0.0093382
2013-03-23 | ZN195:PA25 | URBAN | Third Party Impacts | 953963 | 33 | 58 | 1914 | 0.0011682 | 0.0020141
2013-03-23 | ZN10994:PA11 | URBAN | Vegetation | 953964 | 1 | 196.7333 | 196.7333 | 0.00012007 | 6.1034e-05
2013-03-23 | 206:34432 | URBAN | Other | 953981 | 1 | 88.8 | 88.8 | 5.4198e-05 | 6.1034e-05
2013-03-23 | ZN3425:PA15 | URBAN | Other | 953996 | 1 | 389.3167 | 389.3167 | 0.00023762 | 6.1034e-05
2013-03-23 | ZN2602:PA42 | URBAN | Other | 954010 | 3 | 124 | 372 | 0.00022705 | 0.0001831
2013-03-23 | 523:33503 | URBAN | Other | 954012 | 1 | 113.95 | 113.95 | 6.9548e-05 | 6.1034e-05
2013-03-23 | ZN1287:PA21 | URBAN | Equipment Failure | 954026 | 109 | 83 | 9047 | 0.0055218 | 0.0066527
2013-03-24 | ZN3472:PA31 | URBAN | Equipment Failure | 954030 | 1 | 132.4333 | 132.4333 | 8.083e-05 | 6.1034e-05
2013-03-24 | 515:35192 | SHORT RURAL | Equipment Failure | 954053 | 337 | 178 | 14084 | 0.0085961 | 0.020569
2013-03-24 | ZN14892:PA6 | SHORT RURAL | Other | 954070 | 1 | 129.4 | 129.4 | 7.8978e-05 | 6.1034e-05
2013-03-24 | ZN3288:PA41 42KLM | CBD | Other | 954078 | 5 | 727 | 3635 | 0.0022186 | 0.00030517
2013-03-24 | 526:34636 | SHORT RURAL | Equipment Failure | 954089 | 1 | 1765 | 1765 | 0.0010773 | 6.1034e-05
2013-03-24 | ZN12610:PA2 | URBAN | Equipment Failure | 954096 | 54 | 67 | 3617.65 | 0.002208 | 0.0032958
2013-03-24 | ZN15013:PA4 | URBAN | Equipment Failure | 954109 | 5 | 448 | 2240 | 0.0013672 | 0.00030517
2013-03-24 | 222:2015 | SHORT RURAL | Equipment Failure | 954113 | 1 | 83.6 | 83.6 | 5.1025e-05 | 6.1034e-05
2013-03-24 | 260:33347 | SHORT RURAL | Equipment Failure | 954121 | 1 | 126.3333 | 126.3333 | 7.7107e-05 | 6.1034e-05
2013-03-24 | ZN1287:PA12 | URBAN | Vegetation | 954128 | 1 | 520.1333 | 520.1333 | 0.00031746 | 6.1034e-05
2013-03-24 | 520:48172 | SHORT RURAL | Equipment Failure | 954143 | 1 | 87.9333 | 87.9333 | 5.3669e-05 | 6.1034e-05
2013-03-24 | ZN2466:PA16 | URBAN | Equipment Failure | 954153 | 43 | 120.75 | 5192.25 | 0.003169 | 0.0026245
2013-03-24 | 224:80346 | URBAN | Other | 954157 | 1 | 80.5 | 80.5 | 4.9133e-05 | 6.1034e-05
2013-03-24 | ZN965:PA38 | URBAN | Other | 954158 | 31 | 75.75 | 2348.25 | 0.0014332 | 0.0018921
2013-03-25 | ZN4545:PA36 | URBAN | Third Party Impacts | 954168 | 1 | 996.8667 | 996.8667 | 0.00060843 | 6.1034e-05
2013-03-25 | 812:19072 | SHORT RURAL | Other | 954193 | 1 | 255.25 | 255.25 | 0.00015579 | 6.1034e-05
2013-03-25 | 256:80640 | URBAN | Third Party Impacts | 954247 | 106 | 77 | 8162 | 0.0049816 | 0.0064696
2013-03-25 | ZN1164:PA4 | URBAN | Other | 954257 | 1 | 216.5833 | 216.5833 | 0.00013219 | 6.1034e-05
2013-03-25 | ZN1068:PA27 | URBAN | Equipment Failure | 954259 | 1 | 153.9 | 153.9 | 9.3932e-05 | 6.1034e-05
2013-03-25 | ZN269:PA7 | URBAN | Third Party Impacts | 954264 | 1 | 115.3667 | 115.3667 | 7.0413e-05 | 6.1034e-05
2013-03-23 | 523:33501 | SHORT RURAL | Other | 954297 | 339 | 202 | 56378 | 0.03441 | 0.020691
2013-03-25 | ZN2473:PA32 | URBAN | Other | 954317 | 70 | 51.75 | 3622.5 | 0.002211 | 0.0042724
2013-03-20 | ZN965:PA6 | URBAN | Other | 954327 | 12 | 250 | 3000 | 0.001831 | 0.0007324
2013-03-25 | 507:80923 | SHORT RURAL | Other | 954462 | 1 | 109 | 109 | 6.6527e-05 | 6.1034e-05
2013-03-25 | ZN342:PA24 | URBAN | Third Party Impacts | 954469 | 1 | 269.7167 | 269.7167 | 0.00016462 | 6.1034e-05
2013-03-25 | 520:48172 | SHORT RURAL | Equipment Failure | 954482 | 1 | 70 | 70 | 4.2724e-05 | 6.1034e-05
2013-03-25 | 812:19072 | SHORT RURAL | Other | 954511 | 3 | 102 | 306 | 0.00018676 | 0.0001831
2013-03-25 | ZN12610:PA10 | SHORT RURAL | Other | 954521 | 1 | 251.4667 | 251.4667 | 0.00015348 | 6.1034e-05
2013-03-25 | ZN15014:PA14 | SHORT RURAL | Vegetation | 954547 | 36 | 4.8667 | 175.2 | 0.00010693 | 0.0021972
2013-03-25 | ZN35500:PA34 | URBAN | Other | 954555 | 154 | 127.0667 | 19568.2667 | 0.011943 | 0.0093993
2013-03-25 | 502:48004 | URBAN | Other | 954560 | 1 | 150.3 | 150.3 | 9.1734e-05 | 6.1034e-05
2013-03-25 | ZN3154:PA5 | URBAN | Other | 954562 | 1 | 351.1333 | 351.1333 | 0.00021431 | 6.1034e-05
2013-03-25 | 227:13015 | SHORT RURAL | Other | 954567 | 8 | 143.6 | 1148.8 | 0.00070116 | 0.00048827
2013-03-26 | ZN3154:PA18 | URBAN | Vegetation | 954569 | 1 | 480.5667 | 480.5667 | 0.00029315 | 6.1e-05
2013-03-25 | ZN3154:PA18 | URBAN | Vegetation | 954572 | 56 | 107 | 5992 | 0.0036572 | 0.0034179
2013-03-25 | ZN3154:PA18 | URBAN | Vegetation | 954576 | 27 | 88 | 2376 | 0.0014502 | 0.0016479
2013-03-26 | ZN2635:PA1 | URBAN | Other | 954577 | 47 | 351.3333 | 16512.6667 | 0.010073 | 0.002867
2013-03-26 | ZN9700:PA12 | URBAN | Equipment Failure | 954580 | 57 | 224.5667 | 12800.3 | 0.0078082 | 0.003477
2013-03-26 | ZN180:PA20 | URBAN | Equipment Failure | 954709 | 1 | 448 | 448 | 0.00027328 | 6.1e-05
2013-03-26 | ZN180:PA33 | URBAN | Equipment Failure | 954709 | 252 | 448 | 112844.6667 | 0.068836 | 0.015372
2013-03-26 | ZN9700:PA12 | URBAN | Third Party Impacts | 954738 | 11 | 634.85 | 6983.35 | 0.0042599 | 0.00067101
2013-03-26 | 513:48050 | SHORT RURAL | Animals | 954755 | 3 | 45 | 135 | 8.2351e-05 | 0.000183
2013-03-26 | ZN9700:PA12 | URBAN | Third Party Impacts | 954795 | 2 | 324.5167 | 649.0333 | 0.00039591 | 0.000122
2013-03-26 | ZN180:PA10 | URBAN | Other | 954819 | 48 | 71 | 3408 | 0.0020789 | 0.002928
2013-03-26 | ZN180:PA17 | URBAN | Other | 954819 | 22 | 71 | 1562 | 0.00095283 | 0.001342
2013-03-26 | ZN965:PA3 | URBAN | Vegetation | 954873 | 26 | 75.5 | 1963 | 0.0011974 | 0.001586
2013-03-26 | 231:8415 | SHORT RURAL | Other | 954939 | 1 | 85.5333 | 85.5333 | 5.2176e-05 | 6.1e-05
2013-03-26 | 502:48008 | URBAN | Other | 954944 | 1 | 85.15 | 85.15 | 5.1942e-05 | 6.1e-05
2013-03-26 | ZN3472:PA34 | URBAN | Equipment Failure | 954972 | 1 | 382.6 | 382.6 | 0.00023339 | 6.1e-05
2013-03-26 | 224:80332 | URBAN | Other | 954980 | 1 | 177.6833 | 177.6833 | 0.00010839 | 6.1e-05
2013-03-26 | 511:29878 | SHORT RURAL | Other | 954985 | 1 | 111.0833 | 111.0833 | 6.7761e-05 | 6.1e-05
2013-03-26 | 234:14291 | URBAN | Other | 954995 | 1 | 123.9333 | 123.9333 | 7.56e-05 | 6.1e-05
2013-03-26 | 206:34438 | SHORT RURAL | Animals | 954998 | 589 | 48 | 28272 | 0.017246 | 0.035929
2013-03-26 | 229:34989 | SHORT RURAL | Equipment Failure | 955011 | 2008 | 554 | 324012 | 0.19765 | 0.12249
2013-03-27 | 240:34852 | URBAN | Third Party Impacts | 955024 | 53 | 381 | 20193 | 0.012318 | 0.0032331
2013-03-27 | ZN965:PA8 | URBAN | Other | 955026 | 46 | 48.5167 | 2231.7667 | 0.0013614 | 0.002806
2013-03-27 | ZN9118:PA11 | URBAN | Other | 955028 | 1 | 342.6 | 342.6 | 0.00020899 | 6.1001e-05
2013-03-27 | ZN965:PA8 | URBAN | Equipment Failure | 955036 | 46 | 722.8333 | 33250.3333 | 0.020283 | 0.002806
2013-03-27 | ZN12620:PA2 | SHORT RURAL | Animals | 955045 | 51 | 62 | 3162 | 0.0019289 | 0.0031111
2013-03-27 | ZN847:PA19 | URBAN | Other | 955083 | 1 | 373.7333 | 373.7333 | 0.00022798 | 6.1001e-05
2013-03-27 | ZN15012:PA4 | URBAN | Other | 955090 | 105 | 46 | 4590 | 0.0027999 | 0.0064051
2013-03-27 | ZN15010:PA5 | URBAN | Other | 955113 | 1 | 138.4833 | 138.4833 | 8.4476e-05 | 6.1001e-05
2013-03-27 | ZN2310:PA28 | URBAN | Equipment Failure | 955178 | 1 | 208.9333 | 208.9333 | 0.00012745 | 6.1001e-05
2013-03-27 | 503:48078 | URBAN | Other | 955244 | 36 | 57.4833 | 2069.4 | 0.0012624 | 0.002196
2013-03-27 | ZN9118:PA11 | URBAN | Other | 955254 | 1 | 281.5667 | 281.5667 | 0.00017176 | 6.1001e-05
2013-03-27 | ZN874:PA12 | URBAN | Third Party Impacts | 955274 | 1 | 162.6333 | 162.6333 | 9.9208e-05 | 6.1001e-05
2013-03-27 | 503:48011 | SHORT RURAL | Equipment Failure | 955280 | 14 | 44.7167 | 626.0333 | 0.00038189 | 0.00085401
2013-03-27 | ZN129:PA12 | URBAN | Equipment Failure | 955300 | 15 | 1177 | 17655 | 0.01077 | 0.00091502
2013-03-27 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 955335 | 6 | 209 | 1254 | 0.00076495 | 0.00036601
2013-03-25 | ZN35500:PA23 | URBAN | Other | 955339 | 1 | 216 | 96 | 5.8593e-05 | 6.1034e-05
2013-03-25 | ZN35500:PA28 | URBAN | Other | 955339 | 3061 | 216 | 430706 | 0.26288 | 0.18683
2013-03-27 | ZN1193:PA26 | URBAN | Other | 955351 | 1 | 526.45 | 526.45 | 0.00032114 | 6.1001e-05
2013-03-27 | ZN3154:PA18 | URBAN | Vegetation | 955362 | 42 | 112.0167 | 4704.7 | 0.0028699 | 0.002562
2013-03-27 | 240:34852 | URBAN | Third Party Impacts | 955372 | 468 | 235 | 42864 | 0.026147 | 0.028548
2013-03-27 | 230:81434 | URBAN | Equipment Failure | 955407 | 1 | 47.2667 | 47.2667 | 2.8833e-05 | 6.1001e-05
2013-03-27 | ZN262:PA5 | URBAN | Other | 955408 | 62 | 5 | 310 | 0.0001891 | 0.0037821
2013-03-27 | ZN1850:PA11 | URBAN | Equipment Failure | 955432 | 1 | 198.05 | 198.05 | 0.00012081 | 6.1001e-05
2013-03-27 | ZN847:PA1 | URBAN | Vegetation | 955444 | 27 | 106.4667 | 2874.6 | 0.0017535 | 0.001647
2013-03-27 | ZN2602:PA21 | URBAN | Vegetation | 955456 | 1 | 217.0833 | 217.0833 | 0.00013242 | 6.1001e-05
2013-03-27 | ZN2602:PA21 | URBAN | Vegetation | 955460 | 1 | 200.4167 | 200.4167 | 0.00012226 | 6.1001e-05
2013-03-27 | ZN15009:PA3 | URBAN | Other | 955462 | 1 | 183.3833 | 183.3833 | 0.00011187 | 6.1001e-05
2013-03-28 | 801:74119 | URBAN | Other | 955469 | 616 | 93 | 30184 | 0.018413 | 0.037577
2013-03-28 | 801:74121 | SHORT RURAL | Other | 955469 | 179 | 93 | 13556 | 0.0082694 | 0.010919
2013-03-25 | 232:11457 | URBAN | Third Party Impacts | 955495 | 104 | 20 | 2080 | 0.0012695 | 0.0063476
2013-03-28 | 807:74179 | SHORT RURAL | Other | 955498 | 1 | 111.2167 | 111.2167 | 6.7844e-05 | 6.1002e-05
2013-03-28 | ZN1164:PA13 | URBAN | Other | 955500 | 75 | 56.2 | 4215 | 0.0025712 | 0.0045751
2013-03-28 | ZN1164:PA13 | URBAN | Equipment Failure | 955559 | 75 | 86.1667 | 6462.5 | 0.0039422 | 0.0045751
2013-03-27 | ZN14144:PA1 | URBAN | Other | 955580 | 32 | 20 | 640 | 0.00039041 | 0.001952
2013-03-27 | 232:11455 | URBAN | Other | 955606 | 1 | 35 | 35 | 2.135e-05 | 6.1001e-05
2013-03-28 | 511:29880 | URBAN | Other | 955627 | 1 | 237 | 237 | 0.00014457 | 6.1002e-05
2013-03-28 | ZN12600:PA1 | SHORT RURAL | Equipment Failure | 955687 | 617 | 38 | 23446 | 0.014302 | 0.037638
2013-03-28 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 955687 | 179 | 38 | 6802 | 0.0041493 | 0.010919
2013-03-28 | 515:35198 | SHORT RURAL | Vegetation | 955742 | 1 | 343.4667 | 343.4667 | 0.00020952 | 6.1002e-05
2013-03-28 | 261:81879 | URBAN | Equipment Failure | 955821 | 3645 | 151 | 129915 | 0.07925 | 0.22235
2013-03-28 | ZN3154:PA18 | URBAN | Vegetation | 955830 | 1 | 433.55 | 433.55 | 0.00026447 | 6.1002e-05
2013-03-28 | 225:13446 | URBAN | Equipment Failure | 955842 | 1542 | 1463 | 65421 | 0.039908 | 0.094065
2013-03-28 | ZN187:PA8 | URBAN | Other | 955845 | 69 | 54.3667 | 3751.3 | 0.0022884 | 0.0042091
2013-03-28 | 225:13446 | URBAN | Equipment Failure | 955860 | 238 | 20 | 4760 | 0.0029037 | 0.014518
2013-03-28 | 225:33679 | URBAN | Equipment Failure | 955860 | 689 | 20 | 8957 | 0.0054639 | 0.04203
2013-03-28 | 507:80932 | SHORT RURAL | Other | 955875 | 1 | 104.8333 | 104.8333 | 6.395e-05 | 6.1002e-05
2013-03-28 | ZN2310:PA27 | URBAN | Third Party Impacts | 955887 | 65 | 43.15 | 2804.75 | 0.0017109 | 0.0039651
2013-03-28 | 513:48050 | SHORT RURAL | Other | 955890 | 7 | 262 | 1834 | 0.0011188 | 0.00042701
2013-03-28 | ZN3288:PA43 44GHJ | CBD | Other | 955903 | 21 | 140.5167 | 2950.85 | 0.0018001 | 0.001281
2013-03-28 | ZN1673:PA11 | URBAN | Other | 955912 | 19 | 145 | 2755 | 0.0016806 | 0.001159
2013-03-28 | ZN1290:PA1 | URBAN | Other | 955920 | 1 | 66.6833 | 66.6833 | 4.0678e-05 | 6.1002e-05
2013-03-29 | ZN9118:PA11 | URBAN | Other | 955930 | 1 | 166.2333 | 166.2333 | 0.00010141 | 6.1002e-05
2013-03-28 | ZN14891:PA6 | URBAN | Other | 955937 | 1 | 186.4 | 186.4 | 0.00011371 | 6.1002e-05
2013-03-28 | ZN9037:PA16 | URBAN | Other | 955938 | 1 | 228.95 | 228.95 | 0.00013966 | 6.1002e-05
2013-03-28 | 214:8669 | URBAN | Other | 955943 | 1 | 135.1333 | 135.1333 | 8.2434e-05 | 6.1002e-05
2013-03-28 | 217:33612 | URBAN | Other | 955949 | 1 | 311.25 | 311.25 | 0.00018987 | 6.1002e-05
2013-03-28 | 261:81870 | URBAN | Other | 955951 | 1 | 232.8167 | 232.8167 | 0.00014202 | 6.1002e-05
2013-03-28 | 217:33612 | URBAN | Other | 955952 | 1 | 298.4667 | 298.4667 | 0.00018207 | 6.1002e-05
2013-03-28 | ZN35600:PA14 | URBAN | Equipment Failure | 955953 | 1 | 976.95 | 976.95 | 0.00059596 | 6.1002e-05
2013-03-28 | ZN9245:PA14 | URBAN | Other | 955954 | 1 | 70.3333 | 70.3333 | 4.2905e-05 | 6.1002e-05
2013-03-28 | 238:34140 | URBAN | Third Party Impacts | 955957 | 101 | 64.5333 | 6517.8667 | 0.003976 | 0.0061612
2013-03-28 | ZN3472:PA33 | URBAN | Equipment Failure | 955966 | 114 | 303.2667 | 34572.4 | 0.02109 | 0.0069542
2013-03-29 | ZN35600:PA2 | URBAN | Other | 955969 | 1 | 744.3833 | 744.3833 | 0.00045409 | 6.1002e-05
2013-03-29 | ZN1850:PA11 | URBAN | Equipment Failure | 955973 | 1 | 504.9667 | 504.9667 | 0.00030804 | 6.1002e-05
2013-03-29 | ZN15013:PA6 | SHORT RURAL | Equipment Failure | 955976 | 222 | 137.7667 | 30584.2 | 0.018657 | 0.013542
2013-03-29 | ZN12650:PA14 | URBAN | Other | 955977 | 471 | 73 | 32052 | 0.019552 | 0.028732
2013-03-29 | 261:81879 | URBAN | Other | 955980 | 1 | 201.75 | 201.75 | 0.00012307 | 6.1002e-05
2013-03-29 | 229:34995 | SHORT RURAL | Equipment Failure | 955983 | 62 | 200 | 12400 | 0.0075642 | 0.0037821
2013-03-29 | ZN8700:PA61 62GHJ | CBD | Other | 955986 | 4 | 879 | 3516 | 0.0021448 | 0.00024401
2013-03-29 | 238:34147 | URBAN | Other | 955996 | 1 | 67 | 67 | 4.0871e-05 | 6.1002e-05
2013-03-29 | ZN965:PA8 | URBAN | Other | 956005 | 5 | 612 | 3060 | 0.0018667 | 0.00030501
2013-03-29 | ZN195:PA11 | URBAN | Equipment Failure | 956009 | 21 | 185.8167 | 3902.15 | 0.0023804 | 0.001281
2013-03-29 | 509:48039 | LONG RURAL | Other | 956016 | 1 | 179.05 | 179.05 | 0.00010922 | 6.1002e-05
2013-03-29 | 222:2014 | URBAN | Other | 956027 | 1 | 54 | 54 | 3.2941e-05 | 6.1002e-05
2013-03-29 | ZN2196:PA25 | URBAN | Vegetation | 956032 | 57 | 153.8333 | 8768.5 | 0.005349 | 0.0034771
2013-03-29 | 523:33501 | SHORT RURAL | Equipment Failure | 956052 | 4 | 97 | 388 | 0.00023669 | 0.00024401
2013-03-29 | ZN965:PA15 | URBAN | Other | 956063 | 19 | 157 | 2983 | 0.0018197 | 0.001159
2013-03-29 | 238:34136 | URBAN | Other | 956067 | 1 | 208.35 | 208.35 | 0.0001271 | 6.1002e-05
2013-03-29 | ZN847:PA15 | URBAN | Other | 956070 | 18 | 165 | 2970 | 0.0018118 | 0.001098
2013-03-29 | ZN342:PA24 | URBAN | Other | 956074 | 1 | 36.1167 | 36.1167 | 2.2032e-05 | 6.1002e-05
2013-03-29 | 807:74184 | SHORT RURAL | Other | 956081 | 1 | 129.9833 | 129.9833 | 7.9292e-05 | 6.1002e-05
2013-03-29 | ZN262:PA15 | URBAN | Equipment Failure | 956082 | 40 | 1391.6833 | 55667.3333 | 0.033958 | 0.0024401
2013-03-30 | 238:34147 | URBAN | Equipment Failure | 956089 | 1 | 49.1 | 49.1 | 2.9952e-05 | 6.1002e-05
2013-03-30 | ZN14143:PA12 | SHORT RURAL | Equipment Failure | 956091 | 39 | 461 | 17979 | 0.010968 | 0.0023791
2013-03-30 | ZN15005:PA2 | URBAN | Equipment Failure | 956093 | 1902 | 60 | 101997 | 0.06222 | 0.11603
2013-03-30 | ZN15011:PA6 | URBAN | Equipment Failure | 956093 | 3 | 60 | 153 | 9.3333e-05 | 0.00018301
2013-03-30 | ZN15006:PA6 | URBAN | Other | 956098 | 30 | 15 | 450 | 0.00027451 | 0.0018301
2013-03-30 | 238:34147 | URBAN | Other | 956100 | 1 | 32 | 32 | 1.9521e-05 | 6.1002e-05
2013-03-30 | 238:34147 | URBAN | Other | 956101 | 1 | 115.85 | 115.85 | 7.0671e-05 | 6.1002e-05
2013-03-30 | 232:11460 | URBAN | Equipment Failure | 956102 | 12 | 143.2833 | 1719.4 | 0.0010489 | 0.00073202
2013-03-30 | 501:48124 | URBAN | Other | 956109 | 1 | 227.5667 | 227.5667 | 0.00013882 | 6.1002e-05
2013-03-30 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 956117 | 93 | 341 | 31713 | 0.019346 | 0.0056732
2013-03-30 | ZN965:PA38 | URBAN | Equipment Failure | 956140 | 44 | 85.1167 | 3745.1333 | 0.0022846 | 0.0026841
2013-03-30 | ZN9118:PA21 | URBAN | Vegetation | 956152 | 44 | 109 | 4796 | 0.0029257 | 0.0026841
2013-03-30 | ZN1673:PA9 | URBAN | Third Party Impacts | 956155 | 1 | 353.3833 | 353.3833 | 0.00021557 | 6.1002e-05
2013-03-30 | 217:33610 | URBAN | Other | 956164 | 1 | 42.3167 | 42.3167 | 2.5814e-05 | 6.1002e-05
2013-03-30 | ZN269:PA2 | URBAN | Equipment Failure | 956177 | 60 | 370 | 22150 | 0.013512 | 0.0036601
2013-03-30 | ZN269:PA9 | URBAN | Equipment Failure | 956177 | 4 | 370 | 1480 | 0.00090283 | 0.00024401
2013-03-30 | ZN14143:PA12 | SHORT RURAL | Equipment Failure | 956183 | 1 | 445.0667 | 445.0667 | 0.0002715 | 6.1002e-05
2013-03-30 | ZN630:PA14 | SHORT RURAL | Equipment Failure | 956186 | 64 | 494 | 31616 | 0.019286 | 0.0039041
2013-03-30 | 513:48056 | SHORT RURAL | Animals | 956193 | 11 | 67 | 737 | 0.00044958 | 0.00067102
2013-03-30 | ZN847:PA23 | URBAN | Other | 956200 | 1 | 99.9833 | 99.9833 | 6.0992e-05 | 6.1002e-05
2013-03-30 | ZN12630:PA2 | SHORT RURAL | Vegetation | 956214 | 194 | 810 | 56107 | 0.034226 | 0.011834
2013-03-31 | ZN3922:PA2 | SHORT RURAL | Vegetation | 956247 | 65 | 169 | 10985 | 0.0067011 | 0.0039651
2013-03-31 | 258:80779 | URBAN | Third Party Impacts | 956256 | 1 | 107.0333 | 107.0333 | 6.5292e-05 | 6.1002e-05
2013-03-31 | 216:10723 | URBAN | Other | 956263 | 56 | 171.35 | 9595.6 | 0.0058535 | 0.0034161
2013-03-31 | ZN847:PA28 | URBAN | Other | 956309 | 114 | 51.9 | 5916.6 | 0.0036092 | 0.0069542
2013-04-01 | ZN965:PA38 | URBAN | Other | 956323 | 31 | 126.8667 | 3932.8667 | 0.0023991 | 0.0018911
2013-04-01 | 515:35193 | SHORT RURAL | Other | 956327 | 17 | 128 | 2176 | 0.0013274 | 0.001037
2013-04-01 | ZN342:PA28 | URBAN | Other | 956336 | 1 | 351.7167 | 351.7167 | 0.00021455 | 6.1002e-05
2013-04-01 | 202:34261 | SHORT RURAL | Other | 956394 | 45 | 38 | 1710 | 0.0010431 | 0.0027451
2013-04-01 | ZN9037:PA9 | URBAN | Other | 956412 | 1 | 796.6667 | 796.6667 | 0.00048598 | 6.1002e-05
2013-04-01 | ZN12570:PA34 | SHORT RURAL | Other | 956413 | 1 | 306.0333 | 306.0333 | 0.00018669 | 6.1002e-05
2013-03-29 | ZN36300:PA11 | URBAN | Animals | 956423 | 34 | 55 | 1870 | 0.0011407 | 0.0020741
2013-04-02 | ZN35500:PA28 | URBAN | Third Party Impacts | 956439 | 70 | 137 | 9590 | 0.0058509 | 0.0042708
2013-04-02 | 513:48050 | SHORT RURAL | Other | 956466 | 1 | 399.1667 | 399.1667 | 0.00024354 | 6.1011e-05
2013-04-02 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 956468 | 5 | 417 | 2085 | 0.0012721 | 0.00030505
2013-04-02 | ZN4545:PA31 | URBAN | Other | 956501 | 1 | 383.6667 | 383.6667 | 0.00023408 | 6.1011e-05
2013-03-31 | ZN12630:PA2 | SHORT RURAL | Other | 956516 | 160 | 15 | 2146 | 0.0013091 | 0.0097603
2013-04-02 | 807:74179 | SHORT RURAL | Other | 956517 | 5 | 172 | 860 | 0.00052469 | 0.00030505
2013-04-02 | ZN12630:PA4 | SHORT RURAL | Other | 956528 | 1 | 374.3167 | 374.3167 | 0.00022837 | 6.1011e-05
2013-04-02 | ZN12610:PA13 | URBAN | Other | 956575 | 1 | 303.6833 | 303.6833 | 0.00018528 | 6.1011e-05
2013-04-02 | 513:48058 | URBAN | Equipment Failure | 956577 | 56 | 22 | 1232 | 0.00075165 | 0.0034166
2013-04-02 | 803:74010 | SHORT RURAL | Other | 956606 | 1 | 276.7 | 276.7 | 0.00016882 | 6.1011e-05
2013-04-02 | ZN1788:PA8 | URBAN | Equipment Failure | 956624 | 1106 | 160 | 112283 | 0.068505 | 0.067478
2013-04-02 | 513:48058 | URBAN | Other | 956682 | 1 | 38.7833 | 38.7833 | 2.3662e-05 | 6.1011e-05
2013-04-02 | 511:29877 | SHORT RURAL | Other | 956684 | 1 | 111 | 111 | 6.7722e-05 | 6.1011e-05
2013-04-02 | ZN35800:PA21 | URBAN | Other | 956685 | 1 | 97.7833 | 97.7833 | 5.9658e-05 | 6.1011e-05
2013-04-02 | ZN14891:PA5 | SHORT RURAL | Other | 956695 | 5 | 122 | 610 | 0.00037217 | 0.00030505
2013-04-02 | 261:81879 | URBAN | Third Party Impacts | 956714 | 201 | 40 | 8040 | 0.0049053 | 0.012263
2013-03-30 | 238:34147 | URBAN | Other | 956722 | 1 | 50 | 50 | 3.0501e-05 | 6.1002e-05
2013-03-31 | 238:34147 | URBAN | Operational Error | 956743 | 1167 | 2 | 2334 | 0.0014238 | 0.071189
2013-04-02 | ZN12570:PA24 | SHORT RURAL | Vegetation | 956785 | 1 | 195.5167 | 195.5167 | 0.00011929 | 6.1011e-05
2013-04-02 | 515:35197 | LONG RURAL | Equipment Failure | 956798 | 2 | 90 | 180 | 0.00010982 | 0.00012202
2013-04-02 | ZN72:PA30 | URBAN | Equipment Failure | 956809 | 32 | 63.4833 | 2031.4667 | 0.0012394 | 0.0019523
2013-04-02 | 238:34147 | URBAN | Other | 956812 | 1 | 76.5333 | 76.5333 | 4.6694e-05 | 6.1011e-05
2013-04-02 | 221:11893 | URBAN | Other | 956817 | 1 | 106.1333 | 106.1333 | 6.4753e-05 | 6.1011e-05
2013-04-03 | ZN2568:PA30 | URBAN | Weather | 956892 | 3 | 316 | 948 | 0.00057839 | 0.00018303
2013-04-03 | 213:33774 | URBAN | Other | 956895 | 43 | 115.9667 | 4986.5667 | 0.0030424 | 0.0026235
2013-04-03 | ZN15008:PA9 | URBAN | Other | 956897 | 1 | 270.2667 | 270.2667 | 0.00016489 | 6.1011e-05
2013-04-03 | 502:48010 | SHORT RURAL | Third Party Impacts | 956909 | 1 | 462.1333 | 462.1333 | 0.00028195 | 6.1011e-05
2013-04-03 | ZN1850:PA13 | URBAN | Other | 956917 | 1 | 164.7 | 164.7 | 0.00010049 | 6.1011e-05
2013-04-03 | 512:48049 | SHORT RURAL | Other | 956920 | 1 | 132.9333 | 132.9333 | 8.1104e-05 | 6.1011e-05
2013-04-03 | ZN931:PA12 | URBAN | Other | 956940 | 1 | 270.15 | 270.15 | 0.00016482 | 6.1011e-05
2013-04-02 | 807:74179 | SHORT RURAL | Other | 956942 | 1 | 137 | 137 | 8.3585e-05 | 6.1011e-05
2013-04-03 | ZN2310:PA4 | URBAN | Third Party Impacts | 956945 | 90 | 72.5167 | 6526.5 | 0.0039819 | 0.005491
2013-04-03 | ZN965:PA38 | URBAN | Equipment Failure | 957035 | 31 | 92.5333 | 2868.5333 | 0.0017501 | 0.0018913
2013-04-03 | ZN12690:PA24 | SHORT RURAL | Other | 957071 | 15 | 80.25 | 1203.75 | 0.00073442 | 0.00091517
2013-04-03 | ZN14892:PA10 | SHORT RURAL | Other | 957135 | 1 | 199.4167 | 199.4167 | 0.00012167 | 6.1011e-05
2013-04-03 | ZN3425:PA28 | URBAN | Vegetation | 957194 | 1 | 484.45 | 484.45 | 0.00029557 | 6.1011e-05
2013-04-03 | 243:80084 | SHORT RURAL | Other | 957200 | 1 | 157.25 | 157.25 | 9.594e-05 | 6.1011e-05
2013-03-24 | ZN847:PA1 | URBAN | Vegetation | 957201 | 57 | 704 | 22368 | 0.013652 | 0.0034789
2012-07-29 | ZN262:PA5 | URBAN | Other | 957211 | 108 | 93 | 10044 | 0.0061366 | 0.0065985
2013-04-03 | 217:33611 | URBAN | Other | 957213 | 1 | 89.2 | 89.2 | 5.4422e-05 | 6.1011e-05
2013-04-03 | ZN1788:PA8 | URBAN | Other | 957219 | 1 | 372.0667 | 372.0667 | 0.000227 | 6.1011e-05
2013-04-03 | ZN12640:PA18 | SHORT RURAL | Vegetation | 957223 | 1 | 179.1 | 179.1 | 0.00010927 | 6.1011e-05
2013-04-03 | ZN12600:PA2 | SHORT RURAL | Third Party Impacts | 957224 | 15 | 150 | 2250 | 0.0013728 | 0.00091517
2013-04-03 | 222:2014 | URBAN | Equipment Failure | 957276 | 45 | 147.0667 | 4230 | 0.0025808 | 0.0027455
2013-04-03 | 222:2017 | URBAN | Equipment Failure | 957276 | 1 | 147.0667 | 87.05 | 5.311e-05 | 6.1011e-05
2013-04-03 | ZN4545:PA41 | URBAN | Other | 957284 | 381 | 12 | 3322 | 0.0020268 | 0.023245
2013-04-03 | ZN262:PA7 | URBAN | Other | 957294 | 1 | 302.05 | 302.05 | 0.00018428 | 6.1011e-05
2013-04-03 | ZN80:PA40 | URBAN | Other | 957321 | 1 | 243.0667 | 243.0667 | 0.0001483 | 6.1011e-05
2013-04-03 | ZN2835:PA30 | URBAN | Other | 957323 | 1 | 202.7167 | 202.7167 | 0.00012368 | 6.1011e-05
2013-04-04 | ZN9245:PA13 | URBAN | Other | 957348 | 2 | 188.4167 | 374.3167 | 0.00022838 | 0.00012202
2013-04-04 | ZN180:PA34 | URBAN | Equipment Failure | 957357 | 40 | 114.3833 | 4575.3333 | 0.0027915 | 0.0024405
2013-04-04 | ZN12600:PA1 | SHORT RURAL | Other | 957360 | 30 | 290 | 8700 | 0.0053081 | 0.0018304
2013-04-04 | ZN4545:PA40 | URBAN | Other | 957387 | 1 | 262.7333 | 262.7333 | 0.0001603 | 6.1012e-05
2013-04-03 | 512:48049 | SHORT RURAL | Other | 957394 | 2 | 75 | 150 | 9.1517e-05 | 0.00012202
2013-04-03 | 802:82220 | SHORT RURAL | Equipment Failure | 957397 | 6 | 62 | 372 | 0.00022696 | 0.00036607
2013-04-04 | ZN12570:PA24 | SHORT RURAL | Vegetation | 957415 | 1 | 189.0833 | 189.0833 | 0.00011536 | 6.1012e-05
2013-04-04 | ZN3155:PA24 | URBAN | Other | 957422 | 1 | 124.3667 | 124.3667 | 7.5879e-05 | 6.1012e-05
2013-04-04 | ZN10990:PA7 | URBAN | Equipment Failure | 957457 | 1 | 98.1833 | 98.1833 | 5.9904e-05 | 6.1012e-05
2013-04-04 | ZN10990:PA7 | URBAN | Equipment Failure | 957460 | 1 | 94.65 | 94.65 | 5.7748e-05 | 6.1012e-05
2013-04-04 | ZN72:PA10 | URBAN | Equipment Failure | 957494 | 1 | 66 | 54.6667 | 3.3353e-05 | 6.1012e-05
2013-04-04 | ZN72:PA16 | URBAN | Equipment Failure | 957494 | 1356 | 66 | 89496 | 0.054604 | 0.082733
2013-04-04 | ZN72:PA34 | URBAN | Equipment Failure | 957494 | 1085 | 66 | 71610 | 0.043691 | 0.066198
2013-04-04 | ZN9700:PA24 | URBAN | Other | 957513 | 1 | 65.4833 | 65.4833 | 3.9953e-05 | 6.1012e-05
2013-04-04 | ZN9700:PA24 | URBAN | Other | 957524 | 1 | 60.4833 | 60.4833 | 3.6902e-05 | 6.1012e-05
2013-04-04 | ZN15008:PA10 | URBAN | Third Party Impacts | 957605 | 1 | 190.25 | 190.25 | 0.00011608 | 6.1012e-05
2013-04-04 | ZN15010:PA1 | URBAN | Vegetation | 957641 | 1 | 334.5833 | 334.5833 | 0.00020414 | 6.1012e-05
2013-04-04 | ZN2568:PA14 | URBAN | Equipment Failure | 957695 | 66 | 271 | 17877.2 | 0.010907 | 0.0040268
2013-04-04 | ZN2568:PA9 | URBAN | Equipment Failure | 957695 | 1 | 271 | 271 | 0.00016534 | 6.1012e-05
2013-04-04 | ZN2568:PA9 | URBAN | Equipment Failure | 957711 | 168 | 264 | 44352 | 0.02706 | 0.01025
2013-04-04 | ZN12640:PA16 | URBAN | Animals | 957766 | 1 | 105.1833 | 105.1833 | 6.4175e-05 | 6.1012e-05
2013-04-04 | ZN3922:PA17 | SHORT RURAL | Other | 957780 | 1 | 254.9667 | 254.9667 | 0.00015556 | 6.1012e-05
2013-04-04 | 227:13015 | SHORT RURAL | Other | 957784 | 1 | 126.6833 | 126.6833 | 7.7292e-05 | 6.1012e-05
2013-04-04 | ZN12690:PA3 | SHORT RURAL | Other | 957793 | 2 | 142 | 284 | 0.00017328 | 0.00012202
2013-04-04 | ZN12600:PA2 | SHORT RURAL | Third Party Impacts | 957799 | 1 | 31 | 31 | 1.8914e-05 | 6.1012e-05
2013-04-04 | ZN116:PA45 | URBAN | Equipment Failure | 957805 | 63 | 87 | 5073 | 0.0030952 | 0.0038438
2013-04-04 | ZN2568:PA9 | URBAN | Equipment Failure | 957817 | 89 | 87.3833 | 7777.1167 | 0.004745 | 0.0054301
2013-04-04 | 511:29878 | SHORT RURAL | Other | 957836 | 1 | 168.5833 | 168.5833 | 0.00010286 | 6.1012e-05
2013-04-04 | ZN9900:PA19 | URBAN | Equipment Failure | 957838 | 1 | 192.95 | 192.95 | 0.00011772 | 6.1012e-05
2013-04-04 | ZN10997:PA2 | URBAN | Other | 957857 | 1 | 336.5667 | 336.5667 | 0.00020535 | 6.1012e-05
2013-04-04 | ZN269:PA18 | URBAN | Equipment Failure | 957860 | 32 | 2188 | 33568 | 0.020481 | 0.0019524
2013-04-04 | ZN269:PA7 | URBAN | Equipment Failure | 957860 | 64 | 2188 | 3136 | 0.0019133 | 0.0039048
2013-04-04 | ZN12600:PA13 | SHORT RURAL | Other | 957869 | 852 | 120 | 81145 | 0.049508 | 0.051983
2013-04-04 | ZN12600:PA2 | SHORT RURAL | Other | 957869 | 441 | 120 | 35242 | 0.021502 | 0.026906
2013-04-05 | ZN188:PA1 | URBAN | Vegetation | 957870 | 1 | 50 | 50 | 3.0506e-05 | 6.1013e-05
2013-04-04 | ZN3154:PA19 | URBAN | Vegetation | 957871 | 15 | 43 | 645 | 0.00039353 | 0.00091518
2013-04-04 | ZN690:PA11 | URBAN | Third Party Impacts | 957872 | 1 | 69.25 | 69.25 | 4.2251e-05 | 6.1012e-05
2013-04-05 | ZN4990:PA55 56KLM | CBD | Other | 957901 | 56 | 158 | 8848 | 0.0053984 | 0.0034167
2013-04-04 | 807:74180 | SHORT RURAL | Equipment Failure | 957916 | 1 | 250 | 250 | 0.00015253 | 6.1012e-05
2013-04-05 | ZN35370:PA8 | SHORT RURAL | Other | 957933 | 1 | 82.0333 | 82.0333 | 5.0051e-05 | 6.1013e-05
2013-04-05 | 264:81240 | SHORT RURAL | Other | 958032 | 7 | 4 | 28 | 1.7084e-05 | 0.00042709
2013-04-05 | ZN2310:PA11 | URBAN | Third Party Impacts | 958044 | 1 | 168.25 | 168.25 | 0.00010265 | 6.1013e-05
2013-04-05 | ZN269:PA7 | URBAN | Equipment Failure | 958086 | 64 | 123 | 7872 | 0.0048029 | 0.0039048
2013-04-05 | ZN269:PA14 | URBAN | Equipment Failure | 958102 | 1 | 111.5667 | 111.5667 | 6.807e-05 | 6.1013e-05
2013-04-05 | ZN9118:PA17 | URBAN | Other | 958202 | 1 | 295.4333 | 295.4333 | 0.00018025 | 6.1013e-05
2013-04-05 | 504:48033 | SHORT RURAL | Other | 958203 | 1 | 144.5 | 144.5 | 8.8164e-05 | 6.1013e-05
2013-04-05 | ZN262:PA33 | URBAN | Other | 958204 | 1 | 319.8333 | 319.8333 | 0.00019514 | 6.1013e-05
2013-04-05 | ZN269:PA7 | URBAN | Other | 958211 | 1 | 72.45 | 72.45 | 4.4204e-05 | 6.1013e-05
2013-04-05 | ZN80:PA22 | URBAN | Other | 958251 | 59 | 31 | 1829 | 0.0011159 | 0.0035998
2013-04-05 | ZN80:PA25 | URBAN | Other | 958251 | 62 | 31 | 1922 | 0.0011727 | 0.0037828
2013-04-05 | ZN9118:PA8 | URBAN | Equipment Failure | 958259 | 31 | 79 | 2421.5 | 0.0014774 | 0.0018914
2013-04-06 | 512:48046 | SHORT RURAL | Equipment Failure | 958266 | 30 | 30 | 900 | 0.00054912 | 0.0018304
2013-04-06 | ZN3472:PA7 | SHORT RURAL | Equipment Failure | 958286 | 1 | 269.9667 | 269.9667 | 0.00016471 | 6.1013e-05
2013-04-05 | ZN269:PA18 | URBAN | Equipment Failure | 958289 | 115 | 1604 | 24445.4 | 0.014915 | 0.0070165
2013-04-06 | ZN3472:PA33 | URBAN | Equipment Failure | 958305 | 1 | 302.6833 | 302.6833 | 0.00018468 | 6.1013e-05
2013-04-06 | ZN35370:PA2 | SHORT RURAL | Third Party Impacts | 958309 | 1 | 468.0333 | 468.0333 | 0.00028556 | 6.1013e-05
2013-04-06 | ZN2635:PA4 | URBAN | Vegetation | 958312 | 1 | 189 | 189 | 0.00011531 | 6.1013e-05
2013-04-06 | 513:48050 | SHORT RURAL | Other | 958333 | 7 | 217.9833 | 1525.8833 | 0.00093099 | 0.00042709
2013-04-06 | 501:48123 | SHORT RURAL | Equipment Failure | 958360 | 1 | 151.4667 | 151.4667 | 9.2414e-05 | 6.1013e-05
2013-04-06 | 513:48050 | SHORT RURAL | Other | 958365 | 7 | 59.15 | 414.05 | 0.00025262 | 0.00042709
2013-04-06 | ZN340:PA27 | URBAN | Other | 958371 | 1 | 191.9667 | 191.9667 | 0.00011712 | 6.1013e-05
2013-04-06 | 219:1785 | URBAN | Animals | 958382 | 46 | 52 | 2392 | 0.0014594 | 0.0028066
2013-04-07 | 511:29880 | URBAN | Equipment Failure | 958410 | 1 | 91 | 91 | 5.5522e-05 | 6.1013e-05
2013-04-07 | 261:81882 | URBAN | Other | 958435 | 1 | 77.4833 | 77.4833 | 4.7275e-05 | 6.1013e-05
2013-04-07 | 513:48051 | URBAN | Equipment Failure | 958450 | 27 | 41 | 1107 | 0.00067541 | 0.0016473
2013-04-07 | 515:35197 | LONG RURAL | Other | 958458 | 1 | 209.0167 | 209.0167 | 0.00012753 | 6.1013e-05
2013-04-07 | ZN262:PA26 | URBAN | Third Party Impacts | 958463 | 37 | 196 | 7252 | 0.0044247 | 0.0022575
2013-04-07 | ZN12610:PA2 | URBAN | Equipment Failure | 958464 | 58 | 69 | 4002 | 0.0024417 | 0.0035387
2013-04-07 | 511:29880 | URBAN | Other | 958480 | 1 | 43.0167 | 43.0167 | 2.6246e-05 | 6.1013e-05
2013-04-08 | ZN3155:PA16 | URBAN | Equipment Failure | 958504 | 32 | 566 | 17467 | 0.010657 | 0.0019524
2013-04-08 | ZN9550:PA43 | URBAN | Animals | 958520 | 1 | 131.6833 | 131.6833 | 8.0344e-05 | 6.1013e-05
2013-04-08 | ZN3154:PA18 | URBAN | Third Party Impacts | 958539 | 1 | 202.3 | 202.3 | 0.00012343 | 6.1013e-05
2013-04-04 | ZN2473:PA9 | URBAN | Equipment Failure | 958556 | 49 | 537 | 26313 | 0.016054 | 0.0029896
2013-04-08 | ZN14892:PA16 | URBAN | Other | 958577 | 1 | 219.85 | 219.85 | 0.00013414 | 6.1013e-05
2013-04-08 | 507:80923 | SHORT RURAL | Equipment Failure | 958639 | 1 | 115 | 115 | 7.0165e-05 | 6.1013e-05
2013-04-08 | ZN2473:PA9 | URBAN | Other | 958724 | 1 | 60.2833 | 60.2833 | 3.6781e-05 | 6.1013e-05
2013-04-08 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 958731 | 1 | 137.2667 | 137.2667 | 8.375e-05 | 6.1013e-05
2013-04-08 | ZN9301:PA13 | SHORT RURAL | Equipment Failure | 958737 | 4 | 150 | 600 | 0.00036608 | 0.00024405
2013-04-08 | 515:35197 | LONG RURAL | Other | 958750 | 2 | 161 | 322 | 0.00019646 | 0.00012203
2013-04-08 | 504:48034 | URBAN | Other | 958819 | 1 | 79.1167 | 79.1167 | 4.8271e-05 | 6.1013e-05
2013-04-08 | 501:48115 | SHORT RURAL | Vegetation | 958829 | 1 | 89.2 | 89.2 | 5.4423e-05 | 6.1013e-05
2013-04-08 | ZN12630:PA2 | SHORT RURAL | Other | 958860 | 1 | 79.4 | 79.4 | 4.8444e-05 | 6.1013e-05
2013-04-08 | 513:48051 | URBAN | Other | 958881 | 2 | 190.75 | 381.2 | 0.00023258 | 0.00012203
2013-04-08 | ZN12660:PA14 | SHORT RURAL | Third Party Impacts | 958883 | 57 | 87 | 4959 | 0.0030256 | 0.0034777
2013-04-08 | ZN14891:PA20 | SHORT RURAL | Animals | 958892 | 515 | 76 | 39140 | 0.02388 | 0.031422
2013-04-09 | ZN195:PA11 | URBAN | Third Party Impacts | 958895 | 22 | 645 | 14190 | 0.0086539 | 0.0013417
2013-04-09 | ZN8700:PA61 62GHJ | CBD | Equipment Failure | 958896 | 2 | 36 | 72 | 4.391e-05 | 0.00012197
2013-04-09 | 510:48164 | SHORT RURAL | Equipment Failure | 958897 | 2 | 341 | 682 | 0.00041593 | 0.00012197
2013-04-09 | 810:74050 | SHORT RURAL | Other | 958971 | 1 | 148.7 | 148.7 | 9.0687e-05 | 6.0986e-05
2013-04-09 | 511:29878 | SHORT RURAL | Equipment Failure | 958979 | 1 | 43 | 43 | 2.6224e-05 | 6.0986e-05
2013-04-09 | 812:19072 | SHORT RURAL | Other | 959040 | 1 | 123 | 123 | 7.5013e-05 | 6.0986e-05
2013-04-09 | ZN2635:PA17 | URBAN | Third Party Impacts | 959070 | 36 | 108 | 3888 | 0.0023711 | 0.0021955
2013-04-09 | ZN35600:PA9 | URBAN | Equipment Failure | 959077 | 27 | 16.4833 | 445.05 | 0.00027142 | 0.0016466
2013-04-09 | 511:29878 | SHORT RURAL | Third Party Impacts | 959153 | 3 | 51.2333 | 153.7 | 9.3736e-05 | 0.00018296
2013-04-09 | ZN2835:PA23 | URBAN | Other | 959154 | 1 | 937.5833 | 937.5833 | 0.0005718 | 6.0986e-05
2013-04-09 | ZN2310:PA20 | URBAN | Equipment Failure | 959158 | 1 | 74.6167 | 74.6167 | 4.5506e-05 | 6.0986e-05
2013-04-09 | 504:48028 | URBAN | Vegetation | 959180 | 1 | 69 | 69 | 4.2081e-05 | 6.0986e-05
2013-04-09 | ZN1193:PA26 | URBAN | Equipment Failure | 959181 | 1301 | 127 | 126038 | 0.076866 | 0.079343
2013-04-09 | 242:81541 | URBAN | Equipment Failure | 959204 | 120 | 49 | 5880 | 0.003586 | 0.0073183
2013-04-09 | ZN36300:PA19 | URBAN | Third Party Impacts | 959236 | 78 | 74.7 | 5826.6 | 0.0035534 | 0.0047569
2013-04-09 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 959273 | 334 | 6 | 2004 | 0.0012222 | 0.020369
2013-04-10 | 217:33610 | URBAN | Animals | 959303 | 59 | 49 | 2891 | 0.0017631 | 0.0035982
2013-04-10 | ZN9118:PA20 | URBAN | Equipment Failure | 959305 | 35 | 305 | 10675 | 0.0065103 | 0.0021345
2013-04-10 | ZN2602:PA15 | URBAN | Equipment Failure | 959319 | 2 | 408.5167 | 817.0333 | 0.00049828 | 0.00012197
2013-04-10 | 515:35200 | URBAN | Other | 959322 | 1 | 39.3833 | 39.3833 | 2.4019e-05 | 6.0987e-05
2013-04-10 | 802:82225 | SHORT RURAL | Other | 959348 | 2 | 357 | 714 | 0.00043545 | 0.00012197
2013-04-10 | ZN12570:PA37 | SHORT RURAL | Equipment Failure | 959357 | 23 | 422 | 9705.0167 | 0.0059188 | 0.0014027
2013-04-10 | ZN2602:PA15 | URBAN | Equipment Failure | 959363 | 1 | 331.7833 | 331.7833 | 0.00020234 | 6.0987e-05
2013-04-09 | 810:74054 | LONG RURAL | Other | 959376 | 1 | 40 | 40 | 2.4394e-05 | 6.0986e-05
2013-04-10 | ZN12640:PA13 | SHORT RURAL | Equipment Failure | 959384 | 28 | 286 | 8008 | 0.0048838 | 0.0017076
2013-04-10 | ZN14144:PA8 | URBAN | Equipment Failure | 959464 | 1 | 359.1667 | 359.1667 | 0.00021904 | 6.0987e-05
2013-04-10 | ZN965:PA38 | URBAN | Equipment Failure | 959492 | 31 | 187 | 5797 | 0.0035354 | 0.0018906
2013-04-10 | 502:48010 | SHORT RURAL | Equipment Failure | 959512 | 1 | 97.7 | 97.7 | 5.9584e-05 | 6.0987e-05
2013-04-10 | ZN1068:PA18 | URBAN | Vegetation | 959536 | 95 | 133.4333 | 12676.1667 | 0.0077308 | 0.0057937
2013-04-10 | 235:2124 | URBAN | Vegetation | 959558 | 934 | 222 | 72988 | 0.044513 | 0.056962
2013-04-10 | 227:13014 | SHORT RURAL | Operational Error | 959596 | 57 | 14 | 798 | 0.00048667 | 0.0034762
2013-04-10 | 227:13015 | SHORT RURAL | Operational Error | 959596 | 1511 | 14 | 21154 | 0.012901 | 0.092151
2013-04-10 | 227:13016 | SHORT RURAL | Operational Error | 959596 | 145 | 14 | 2030 | 0.001238 | 0.0088431
2013-04-10 | 227:13018 | URBAN | Operational Error | 959596 | 558 | 14 | 7812 | 0.0047643 | 0.034031
2013-04-10 | 227:13019 | SHORT RURAL | Operational Error | 959596 | 120 | 14 | 1680 | 0.0010246 | 0.0073184
2013-04-10 | 227:13020 | SHORT RURAL | Operational Error | 959596 | 1740 | 14 | 24360 | 0.014856 | 0.10612
2013-04-09 | ZN1673:PA11 | URBAN | Third Party Impacts | 959664 | 31 | 70 | 2170 | 0.0013234 | 0.0018906
2013-04-10 | ZN9252:PA4 | URBAN | Third Party Impacts | 959677 | 1 | 314.2167 | 314.2167 | 0.00019163 | 6.0987e-05
2013-04-10 | ZN3155:PA21 | URBAN | Third Party Impacts | 959681 | 62 | 25 | 1550 | 0.0009453 | 0.0037812
2013-04-11 | 501:48122 | SHORT RURAL | Third Party Impacts | 959702 | 26 | 150 | 3900 | 0.0023785 | 0.0015857
2013-04-10 | 217:33611 | URBAN | Other | 959733 | 1 | 49.5 | 49.5 | 3.0188e-05 | 6.0987e-05
2013-04-11 | 801:74122 | URBAN | Equipment Failure | 959737 | 1 | 272.9 | 272.9 | 0.00016643 | 6.0987e-05
2013-04-11 | ZN3672:PA6 | URBAN | Third Party Impacts | 959741 | 11 | 95 | 1045 | 0.00063731 | 0.00067086
2013-04-11 | ZN1164:PA23 | URBAN | Equipment Failure | 959746 | 1 | 208.0667 | 208.0667 | 0.00012689 | 6.0987e-05
2013-04-11 | ZN1193:PA26 | URBAN | Other | 959863 | 57 | 169 | 9633 | 0.0058749 | 0.0034763
2013-04-11 | 235:8684 | SHORT RURAL | Third Party Impacts | 959904 | 2 | 285 | 570 | 0.00034763 | 0.00012197
2013-04-11 | 509:48039 | LONG RURAL | Other | 959953 | 2 | 213 | 426 | 0.0002598 | 0.00012197
2013-04-11 | 229:34995 | SHORT RURAL | Other | 959973 | 12 | 64.1 | 769.2 | 0.00046911 | 0.00073184
2013-04-11 | ZN398:PA3 | URBAN | Third Party Impacts | 960038 | 1 | 167.9167 | 167.9167 | 0.00010241 | 6.0987e-05
2013-04-11 | 234:2001 | URBAN | Other | 960060 | 1 | 68.95 | 68.95 | 4.2051e-05 | 6.0987e-05
2013-04-11 | 235:2123 | URBAN | Other | 960062 | 1 | 98.0667 | 98.0667 | 5.9808e-05 | 6.0987e-05
2013-04-11 | 264:81236 | URBAN | Other | 960076 | 1 | 50.4333 | 50.4333 | 3.0758e-05 | 6.0987e-05
2013-04-11 | ZN3154:PA10 | URBAN | Animals | 960098 | 936 | 46 | 43056 | 0.026259 | 0.057084
2013-04-11 | 242:81539 | URBAN | Vegetation | 960117 | 1 | 187 | 187 | 0.00011405 | 6.0987e-05
2013-04-11 | 224:80332 | URBAN | Animals | 960124 | 84 | 69 | 5796 | 0.0035348 | 0.0051229
2013-04-12 | 812:19072 | SHORT RURAL | Third Party Impacts | 960145 | 1 | 76.2667 | 76.2667 | 4.6513e-05 | 6.0987e-05
2013-04-12 | 523:33508 | SHORT RURAL | Other | 960169 | 5 | 62 | 310 | 0.00018906 | 0.00030494
2013-04-12 | 210:8681 | URBAN | Other | 960210 | 1 | 64 | 64 | 3.9032e-05 | 6.0987e-05
2013-04-12 | ZN2602:PA36 | URBAN | Third Party Impacts | 960236 | 6 | 68 | 408 | 0.00024883 | 0.00036592
2013-04-12 | ZN2602:PA41 | URBAN | Third Party Impacts | 960236 | 3 | 68 | 204 | 0.00012441 | 0.00018296
2013-04-12 | 229:34995 | SHORT RURAL | Other | 960310 | 1 | 45.85 | 45.85 | 2.7963e-05 | 6.0987e-05
2013-04-12 | ZN8000:PA4 | URBAN | Other | 960358 | 1 | 212.3 | 212.3 | 0.00012948 | 6.0987e-05
2013-04-12 | 511:29878 | SHORT RURAL | Other | 960363 | 84 | 21 | 1764 | 0.0010758 | 0.0051229
2013-04-10 | 803:74016 | SHORT RURAL | Weather | 960369 | 1 | 40 | 40 | 2.4395e-05 | 6.0987e-05
2013-04-11 | 513:48059 | SHORT RURAL | Other | 960370 | 1 | 30 | 30 | 1.8296e-05 | 6.0987e-05
2013-04-12 | 813:89061 | LONG RURAL | Equipment Failure | 960403 | 1 | 206 | 206 | 0.00012563 | 6.0987e-05
2013-04-12 | 261:81882 | URBAN | Other | 960440 | 1 | 31.3333 | 31.3333 | 1.9109e-05 | 6.0987e-05
2013-04-12 | ZN9301:PA13 | SHORT RURAL | Third Party Impacts | 960471 | 21 | 1145 | 8580 | 0.0052327 | 0.0012807
2013-04-12 | ZN9301:PA8 | URBAN | Equipment Failure | 960474 | 1 | 23.5333 | 23.5333 | 1.4352e-05 | 6.0987e-05
2013-04-12 | ZN2568:PA40 | URBAN | Other | 960475 | 6 | 93 | 558 | 0.00034031 | 0.00036592
2013-04-12 | ZN690:PA5 | URBAN | Equipment Failure | 960482 | 538 | 769 | 57970 | 0.035354 | 0.032811
2013-04-13 | ZN180:PA24 | URBAN | Third Party Impacts | 960492 | 138 | 358 | 49404 | 0.03013 | 0.0084162
2013-04-13 | ZN12630:PA3 | SHORT RURAL | Other | 960495 | 1 | 152.7333 | 152.7333 | 9.3148e-05 | 6.0987e-05
2013-04-13 | ZN690:PA5 | URBAN | Equipment Failure | 960500 | 1 | 277.3333 | 277.3333 | 0.00016914 | 6.0987e-05
2013-04-13 | 507:80925 | SHORT RURAL | Other | 960501 | 1 | 109.8333 | 109.8333 | 6.6984e-05 | 6.0987e-05
2013-04-13 | 511:29878 | SHORT RURAL | Vegetation | 960544 | 30 | 182.55 | 5476.5 | 0.00334 | 0.0018296
2013-04-13 | ZN12630:PA3 | SHORT RURAL | Other | 960551 | 3 | 236.2333 | 704.1667 | 0.00042945 | 0.00018296
2013-04-13 | ZN2568:PA39 | URBAN | Equipment Failure | 960555 | 1 | 336.2167 | 336.2167 | 0.00020505 | 6.0987e-05
2013-04-13 | 232:33413 | SHORT RURAL | Other | 960556 | 1 | 152.5833 | 152.5833 | 9.3056e-05 | 6.0987e-05
2013-04-13 | ZN187:PA10 | URBAN | Equipment Failure | 960560 | 1 | 276.0667 | 276.0667 | 0.00016837 | 6.0987e-05
2013-04-13 | ZN1673:PA9 | URBAN | Vegetation | 960571 | 1 | 153.3833 | 69 | 4.2081e-05 | 6.0987e-05
2013-04-13 | ZN847:PA39 | URBAN | Vegetation | 960571 | 61 | 153.3833 | 5981.4333 | 0.0036479 | 0.0037202
2013-04-13 | 210:8681 | URBAN | Other | 960590 | 1 | 39.6833 | 39.6833 | 2.4202e-05 | 6.0987e-05
2013-04-14 | ZN262:PA34 | URBAN | Third Party Impacts | 960607 | 17 | 349 | 5933 | 0.0036184 | 0.0010368
2013-04-14 | 261:81870 | URBAN | Animals | 960611 | 59 | 119.1833 | 7031.8167 | 0.0042885 | 0.0035982
2013-04-14 | ZN12690:PA26 | URBAN | Equipment Failure | 960614 | 1 | 115 | 115 | 7.0135e-05 | 6.0987e-05
2013-04-14 | ZN1290:PA12 | URBAN | Vegetation | 960615 | 167 | 99.25 | 16574.75 | 0.010108 | 0.010185
2013-04-14 | ZN36300:PA11 | URBAN | Vegetation | 960629 | 3555 | 94 | 233615 | 0.14248 | 0.21681
2013-04-14 | ZN36300:PA3 | URBAN | Vegetation | 960629 | 1 | 94 | 59 | 3.5982e-05 | 6.0987e-05
2013-04-14 | ZN1673:PA11 | URBAN | Equipment Failure | 960656 | 56 | 50 | 2800 | 0.0017076 | 0.0034153
2013-04-14 | 221:11894 | URBAN | Equipment Failure | 960676 | 1 | 64.9833 | 64.9833 | 3.9632e-05 | 6.0987e-05
2013-04-14 | ZN965:PA46 | URBAN | Other | 960679 | 1 | 1051.4167 | 1051.4167 | 0.00064123 | 6.0987e-05
2013-04-14 | ZN2310:PA31 | URBAN | Equipment Failure | 960681 | 1 | 263.3333 | 263.3333 | 0.0001606 | 6.0987e-05
2013-04-14 | ZN262:PA17 | URBAN | Equipment Failure | 960683 | 1601 | 73 | 111569 | 0.068043 | 0.097641
2013-04-15 | ZN2400:PA18 | SHORT RURAL | Other | 960705 | 46 | 73.8 | 3394.8 | 0.0020704 | 0.0028054
2013-04-15 | 511:29878 | SHORT RURAL | Other | 960707 | 6 | 143.5167 | 861.1 | 0.00052516 | 0.00036592
2013-04-15 | ZN3154:PA17 | URBAN | Other | 960758 | 1 | 38.4 | 6.3667 | 3.8829e-06 | 6.0987e-05
2013-04-15 | ZN3154:PA23 | URBAN | Other | 960758 | 48 | 38.4 | 1843.2 | 0.0011241 | 0.0029274
2013-04-15 | 238:34147 | URBAN | Third Party Impacts | 960813 | 31 | 60 | 1860 | 0.0011344 | 0.0018906
2013-04-15 | ZN2568:PA8 | URBAN | Equipment Failure | 960815 | 3 | 77 | 231 | 0.00014088 | 0.00018296
2013-04-15 | 515:35192 | SHORT RURAL | Other | 960842 | 1 | 20.1333 | 20.1333 | 1.2279e-05 | 6.0987e-05
2013-04-15 | 214:8665 | URBAN | Other | 960856 | 1 | 221.2 | 221.2 | 0.0001349 | 6.0987e-05
2013-04-15 | ZN15012:PA8 | URBAN | Third Party Impacts | 960891 | 1 | 1133.1833 | 1133.1833 | 0.0006911 | 6.0987e-05
2013-04-15 | 214:8666 | URBAN | Other | 960945 | 1 | 132.3167 | 132.3167 | 8.0696e-05 | 6.0987e-05
2013-04-12 | ZN15005:PA8 | URBAN | Equipment Failure | 960959 | 1310 | 446 | 144131 | 0.087902 | 0.079893
2013-04-15 | ZN342:PA26 | URBAN | Vegetation | 960987 | 89 | 106 | 9434 | 0.0057535 | 0.0054279
2013-04-15 | ZN12650:PA6 | URBAN | Equipment Failure | 961000 | 1 | 719.1667 | 719.1667 | 0.0004386 | 6.0987e-05
2013-04-15 | 242:81539 | URBAN | Other | 961004 | 1 | 161.9333 | 161.9333 | 9.8759e-05 | 6.0987e-05
2013-04-15 | ZN7481:PA20 | URBAN | Vegetation | 961005 | 1 | 446.75 | 446.75 | 0.00027246 | 6.0987e-05
2013-04-15 | 242:81539 | URBAN | Other | 961012 | 1 | 170.4 | 170.4 | 0.00010392 | 6.0987e-05
2013-04-15 | 222:2015 | SHORT RURAL | Equipment Failure | 961050 | 1 | 802.5667 | 802.5667 | 0.00048946 | 6.0987e-05
2013-04-15 | ZN3472:PA34 | URBAN | Equipment Failure | 961051 | 1 | 135.8167 | 135.8167 | 8.2831e-05 | 6.0987e-05
2013-04-15 | ZN3154:PA16 | URBAN | Vegetation | 961055 | 33 | 181 | 5966.6 | 0.0036389 | 0.0020126
2013-04-15 | ZN9700:PA17 | URBAN | Other | 961061 | 1 | 188.2667 | 188.2667 | 0.00011482 | 6.0987e-05
2013-04-15 | 807:74184 | SHORT RURAL | Equipment Failure | 961063 | 202 | 75 | 14830 | 0.0090444 | 0.012319
2013-04-15 | ZN14143:PA10 | SHORT RURAL | Vegetation | 961067 | 298 | 132 | 32108 | 0.019582 | 0.018174
2013-04-15 | ZN2466:PA16 | URBAN | Equipment Failure | 961072 | 2 | 2184.3833 | 4368.7667 | 0.0026644 | 0.00012197
2013-04-15 | ZN12640:PA13 | SHORT RURAL | Equipment Failure | 961073 | 56 | 77.2667 | 4326.9333 | 0.0026389 | 0.0034153
2013-04-15 | ZN14892:PA3 | SHORT RURAL | Other | 961082 | 1 | 24.1833 | 24.1833 | 1.4749e-05 | 6.0987e-05
2013-04-15 | ZN1850:PA3 | URBAN | Weather | 961086 | 1006 | 124 | 70218 | 0.042824 | 0.061353
2013-04-15 | 512:48049 | SHORT RURAL | Other | 961087 | 908 | 43 | 39044 | 0.023812 | 0.055376
2013-04-15 | ZN1850:PA10 | URBAN | Weather | 961091 | 1 | 107.7667 | 107.7667 | 6.5724e-05 | 6.0987e-05
2013-04-15 | 216:10728 | URBAN | Other | 961093 | 795 | 28 | 22260 | 0.013576 | 0.048485
2013-04-15 | 515:35198 | SHORT RURAL | Other | 961095 | 1 | 43.2333 | 43.2333 | 2.6367e-05 | 6.0987e-05
2013-04-15 | 507:80932 | SHORT RURAL | Other | 961097 | 3 | 58 | 174 | 0.00010612 | 0.00018296
2013-04-15 | 507:80932 | SHORT RURAL | Other | 961100 | 2 | 85 | 170 | 0.00010368 | 0.00012197
2013-04-16 | ZN36300:PA9 | URBAN | Other | 961106 | 1 | 293.15 | 293.15 | 0.00017878 | 6.0985e-05
2013-04-16 | ZN9252:PA10 | URBAN | Vegetation | 961108 | 1 | 135.3333 | 135.3333 | 8.2533e-05 | 6.0985e-05
2013-04-16 | ZN12690:PA24 | SHORT RURAL | Equipment Failure | 961111 | 3 | 78.0333 | 234.1 | 0.00014277 | 0.00018295
2013-04-16 | ZN9252:PA10 | URBAN | Vegetation | 961117 | 1 | 140.3833 | 140.3833 | 8.5612e-05 | 6.0985e-05
2013-04-16 | ZN14144:PA10 | SHORT RURAL | Other | 961120 | 1 | 257.9 | 257.9 | 0.00015728 | 6.0985e-05
2013-04-16 | ZN9252:PA10 | URBAN | Vegetation | 961127 | 1 | 102.2833 | 102.2833 | 6.2377e-05 | 6.0985e-05
2013-04-16 | ZN12570:PA24 | SHORT RURAL | Vegetation | 961138 | 8 | 295 | 2360 | 0.0014392 | 0.00048788
2013-04-16 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 961151 | 1 | 56 | 56 | 3.4151e-05 | 6.0985e-05
2013-04-16 | 507:80932 | SHORT RURAL | Equipment Failure | 961161 | 1 | 87 | 87 | 5.3057e-05 | 6.0985e-05
2013-04-16 | ZN72:PA23 | URBAN | Other | 961174 | 5 | 232 | 1160 | 0.00070742 | 0.00030492
2013-04-16 | ZN72:PA34 | URBAN | Other | 961174 | 79 | 232 | 18328 | 0.011177 | 0.0048178
2013-04-16 | ZN8700:PA61 62GHJ | CBD | Other | 961206 | 1 | 88.2167 | 88.2167 | 5.3799e-05 | 6.0985e-05
2013-04-16 | ZN1193:PA16 | URBAN | Third Party Impacts | 961221 | 1 | 232.1167 | 232.1167 | 0.00014156 | 6.0985e-05
2013-04-16 | 503:48012 | URBAN | Equipment Failure | 961226 | 1 | 249.5833 | 249.5833 | 0.00015221 | 6.0985e-05
2013-04-16 | 202:34231 37 42 | URBAN | Other | 961233 | 1 | 87.2667 | 86.5167 | 5.2762e-05 | 6.0985e-05
2013-04-16 | 202:34261 | SHORT RURAL | Other | 961233 | 45 | 87.2667 | 945 | 0.00057631 | 0.0027443
2013-04-16 | ZN12640:PA19 | URBAN | Other | 961251 | 1 | 241.9833 | 241.9833 | 0.00014757 | 6.0985e-05
2013-04-16 | 205:12208 | URBAN | Other | 961261 | 1 | 162.1667 | 162.1667 | 9.8897e-05 | 6.0985e-05
2013-04-16 | ZN4545:PA41 | URBAN | Other | 961320 | 49 | 55.35 | 2712.15 | 0.001654 | 0.0029883
2013-04-16 | 227:13018 | URBAN | Vegetation | 961356 | 1 | 236.35 | 236.35 | 0.00014414 | 6.0985e-05
2013-04-16 | 803:74016 | SHORT RURAL | Equipment Failure | 961386 | 1 | 66.6167 | 66.6167 | 4.0626e-05 | 6.0985e-05
2013-04-16 | 810:74050 | SHORT RURAL | Other | 961388 | 1 | 118.0167 | 118.0167 | 7.1972e-05 | 6.0985e-05
2013-04-16 | 810:74054 | LONG RURAL | Equipment Failure | 961440 | 21 | 331 | 3411 | 0.0020802 | 0.0012807
2013-04-16 | ZN1285:PA27 | URBAN | Third Party Impacts | 961446 | 33 | 135 | 4455 | 0.0027169 | 0.0020125
2013-04-17 | ZN8000:PA20 | URBAN | Third Party Impacts | 961537 | 24 | 173.0667 | 4153.6 | 0.0025331 | 0.0014636
2013-04-17 | ZN14892:PA8 | URBAN | Other | 961588 | 3 | 86 | 258 | 0.00015734 | 0.00018296
2013-04-17 | ZN262:PA34 | URBAN | Weather | 961591 | 79 | 95.2833 | 7527.3833 | 0.0045906 | 0.0048178
2013-04-17 | ZN3472:PA22 | URBAN | Equipment Failure | 961594 | 2 | 262.2167 | 439.0167 | 0.00026774 | 0.00012197
2013-04-17 | ZN14891:PA16 | SHORT RURAL | Equipment Failure | 961606 | 94 | 75.95 | 7139.3 | 0.0043539 | 0.0057326
2013-04-17 | ZN14892:PA3 | SHORT RURAL | Vegetation | 961728 | 1 | 169.7333 | 169.7333 | 0.00010351 | 6.0985e-05
2013-04-14 | ZN10999:PA4 | URBAN | Equipment Failure | 961762 | 1 | 105 | 105 | 6.4037e-05 | 6.0987e-05
2013-04-17 | ZN847:PA39 | URBAN | Third Party Impacts | 961775 | 1 | 385.05 | 385.05 | 0.00023482 | 6.0985e-05
2013-04-17 | ZN8000:PA20 | URBAN | Third Party Impacts | 961811 | 16 | 350.2 | 5603.2 | 0.0034171 | 0.00097577
2013-04-17 | ZN12600:PA9 | SHORT RURAL | Third Party Impacts | 961847 | 33 | 71 | 2343 | 0.0014289 | 0.0020125
2013-04-17 | ZN35800:PA14 | URBAN | Third Party Impacts | 961867 | 1 | 262.4833 | 262.4833 | 0.00016008 | 6.0985e-05
2013-04-18 | ZN9037:PA4 | URBAN | Equipment Failure | 961936 | 1 | 76 | 76 | 4.635e-05 | 6.0986e-05
2013-04-18 | ZN9037:PA8 | URBAN | Equipment Failure | 961936 | 65 | 76 | 4940 | 0.0030127 | 0.0039641
2013-04-18 | ZN9037:PA9 | URBAN | Equipment Failure | 961936 | 2 | 76 | 152 | 9.2699e-05 | 0.00012197
2013-04-18 | 224:80340 | SHORT RURAL | Other | 961941 | 1 | 391.8333 | 391.8333 | 0.00023897 | 6.0986e-05
2013-04-18 | ZN3472:PA12 | URBAN | Other | 961964 | 46 | 20 | 920 | 0.00056107 | 0.0028054
2013-04-18 | 813:89061 | LONG RURAL | Equipment Failure | 962009 | 5 | 255 | 1275 | 0.00077758 | 0.00030493
2013-04-18 | 240:34846 | URBAN | Other | 962022 | 25 | 75.3 | 1882.5 | 0.0011481 | 0.0015247
2013-04-18 | 507:80917 | URBAN | Third Party Impacts | 962069 | 1 | 75.9333 | 75.9333 | 4.6309e-05 | 6.0986e-05
2013-04-18 | 208:74 | URBAN | Third Party Impacts | 962134 | 1 | 72.1667 | 72.1667 | 4.4012e-05 | 6.0986e-05
2013-04-05 | ZN180:PA23 | URBAN | Equipment Failure | 962141 | 57 | 1050 | 59850 | 0.036516 | 0.0034777
2013-04-05 | ZN180:PA23 | URBAN | Other | 962148 | 35 | 1050 | 36750 | 0.022422 | 0.0021355
2013-04-18 | ZN15014:PA5 | URBAN | Vegetation | 962174 | 35 | 130 | 4550 | 0.0027749 | 0.0021345
2013-04-18 | ZN1285:PA18 | URBAN | Equipment Failure | 962256 | 1 | 84 | 68 | 4.1471e-05 | 6.0986e-05
2013-04-18 | ZN3472:PA15 | URBAN | Equipment Failure | 962256 | 952 | 84 | 65562 | 0.039984 | 0.058059
2013-04-18 | ZN3472:PA21 | URBAN | Equipment Failure | 962256 | 1 | 84 | 68 | 4.1471e-05 | 6.0986e-05
2013-04-18 | ZN3472:PA40 | URBAN | Equipment Failure | 962256 | 1 | 84 | 68 | 4.1471e-05 | 6.0986e-05
2013-04-18 | 240:34846 | URBAN | Equipment Failure | 962274 | 1 | 558 | 558 | 0.0003403 | 6.0986e-05
2013-04-18 | ZN36300:PA17 | URBAN | Third Party Impacts | 962278 | 1 | 185.75 | 185.75 | 0.00011328 | 6.0986e-05
2013-04-18 | ZN3472:PA31 | URBAN | Other | 962280 | 1 | 50.3333 | 50.3333 | 3.0696e-05 | 6.0986e-05
2013-04-19 | ZN9252:PA9 | URBAN | Equipment Failure | 962306 | 45 | 162 | 7290 | 0.0044459 | 0.0027444
2013-04-19 | 217:33611 | URBAN | Other | 962308 | 13 | 93 | 1209 | 0.00073733 | 0.00079283
2013-04-19 | 232:11460 | URBAN | Equipment Failure | 962318 | 1 | 292 | 292 | 0.00017808 | 6.0987e-05
2013-04-19 | 240:34843 | URBAN | Other | 962321 | 1 | 162 | 162 | 9.8798e-05 | 6.0987e-05
2013-04-16 | 216:10728 | URBAN | Equipment Failure | 962347 | 1 | 75 | 75 | 4.5739e-05 | 6.0985e-05
2013-04-18 | 229:34989 | SHORT RURAL | Equipment Failure | 962391 | 1225 | 804 | 165020 | 0.10064 | 0.074708
2013-04-16 | 807:74183 | SHORT RURAL | Other | 962421 | 96 | 88 | 8395 | 0.0051197 | 0.0058545
2013-04-19 | ZN12650:PA1 | SHORT RURAL | Vegetation | 962457 | 1 | 161.5833 | 161.5833 | 9.8544e-05 | 6.0987e-05
2013-04-19 | ZN15004:PA9 | URBAN | Third Party Impacts | 962504 | 1 | 82 | 82 | 5.0009e-05 | 6.0987e-05
2013-04-19 | ZN14144:PA10 | SHORT RURAL | Other | 962515 | 185 | 378 | 35622 | 0.021725 | 0.011283
2013-04-19 | ZN1164:PA27 | URBAN | Equipment Failure | 962536 | 21 | 20 | 420 | 0.00025614 | 0.0012807
2013-04-19 | 238:34140 | URBAN | Other | 962548 | 2 | 55 | 110 | 6.7085e-05 | 0.00012197
2013-04-19 | ZN2310:PA33 | URBAN | Third Party Impacts | 962586 | 1 | 144.05 | 144.05 | 8.7851e-05 | 6.0987e-05
2013-04-16 | ZN1285:PA30 | URBAN | Other | 962612 | 1 | 25 | 25 | 1.5246e-05 | 6.0985e-05
2013-04-19 | 202:34254 | URBAN | Other | 962618 | 1 | 148.3333 | 148.3333 | 9.0464e-05 | 6.0987e-05
2013-04-19 | ZN2196:PA5 | URBAN | Equipment Failure | 962623 | 1 | 392.4 | 392.4 | 0.00023931 | 6.0987e-05
2013-04-19 | ZN1673:PA2 | URBAN | Vegetation | 962627 | 1 | 475.15 | 475.15 | 0.00028978 | 6.0987e-05
2013-04-19 | ZN1673:PA9 | URBAN | Equipment Failure | 962637 | 58 | 153 | 8874 | 0.005412 | 0.0035372
2013-04-19 | ZN80:PA32 | URBAN | Vegetation | 962650 | 182 | 184 | 32758 | 0.019978 | 0.0111
2013-04-19 | ZN711:PA32 | URBAN | Weather | 962662 | 58 | 134.7333 | 7814.5333 | 0.0047658 | 0.0035372
2013-04-19 | ZN2602:PA4 | URBAN | Other | 962663 | 1 | 426.9667 | 426.9667 | 0.00026039 | 6.0987e-05
2013-04-19 | ZN3472:PA28 | URBAN | Equipment Failure | 962695 | 1 | 366 | 366 | 0.00022321 | 6.0987e-05
2013-04-19 | 258:80784 | URBAN | Other | 962710 | 82 | 46.4333 | 2299.3667 | 0.0014023 | 0.0050009
2013-04-19 | ZN15006:PA9 | URBAN | Equipment Failure | 962717 | 1 | 170.3833 | 170.3833 | 0.00010391 | 6.0987e-05
2013-04-20 | ZN9037:PA7 | URBAN | Equipment Failure | 962750 | 641 | 297 | 63837 | 0.038932 | 0.039092
2013-04-20 | ZN188:PA26 | URBAN | Vegetation | 962762 | 67 | 306.3833 | 20527.6833 | 0.012519 | 0.0040861
2013-04-20 | ZN3154:PA19 | URBAN | Equipment Failure | 962770 | 43 | 236.5667 | 10172.3667 | 0.0062038 | 0.0026224
2013-04-20 | ZN12600:PA2 | SHORT RURAL | Vegetation | 962783 | 1 | 173.4833 | 173.4833 | 0.0001058 | 6.0987e-05
2013-04-20 | ZN188:PA9 | URBAN | Equipment Failure | 962799 | 29 | 602 | 17458 | 0.010647 | 0.0017686
2013-04-20 | ZN1788:PA1 | URBAN | Equipment Failure | 962802 | 1 | 849 | 849 | 0.00051778 | 6.0987e-05
2013-04-20 | 813:89062 | SHORT RURAL | Equipment Failure | 962809 | 585 | 205 | 22423 | 0.013675 | 0.035677
2013-04-20 | ZN340:PA19 | SHORT RURAL | Equipment Failure | 962813 | 1 | 1028.7 | 1028.7 | 0.00062737 | 6.0987e-05
2013-04-20 | ZN2602:PA31 | URBAN | Vegetation | 962815 | 55 | 15 | 825 | 0.00050314 | 0.0033543
2013-04-20 | ZN15014:PA14 | SHORT RURAL | Vegetation | 962843 | 327 | 64 | 20928 | 0.012763 | 0.019943
2013-04-20 | ZN1788:PA30 | URBAN | Equipment Failure | 962848 | 1 | 722.3 | 722.3 | 0.00044051 | 6.0987e-05
2013-04-20 | ZN901:PA13 | URBAN | Other | 962871 | 297 | 58.1667 | 17275.5 | 0.010536 | 0.018113
2013-04-20 | ZN12620:PA8 | SHORT RURAL | Vegetation | 962883 | 1 | 243.7833 | 243.7833 | 0.00014868 | 6.0987e-05
2013-04-20 | 217:33610 | URBAN | Animals | 962889 | 59 | 48 | 2832 | 0.0017271 | 0.0035982
2013-04-20 | ZN3922:PA23 | URBAN | Other | 962893 | 2 | 631 | 1262 | 0.00076965 | 0.00012197
2013-04-20 | ZN35500:PA24 | URBAN | Vegetation | 962921 | 1 | 101 | 79 | 4.8179e-05 | 6.0987e-05
2013-04-20 | ZN35500:PA28 | URBAN | Vegetation | 962921 | 3123 | 101 | 243297 | 0.14838 | 0.19046
2013-04-20 | ZN10990:PA7 | URBAN | Other | 962931 | 1 | 695 | 695 | 0.00042386 | 6.0987e-05
2013-04-20 | ZN690:PA17 | URBAN | Vegetation | 962936 | 27 | 840 | 22680 | 0.013832 | 0.0016466
2013-04-20 | 206:34441 | URBAN | Vegetation | 962937 | 1393 | 29 | 40397 | 0.024637 | 0.084954
2013-04-20 | ZN195:PA23 | URBAN | Vegetation | 962943 | 64 | 160 | 10240 | 0.006245 | 0.0039031
2013-04-20 | 230:81434 | URBAN | Other | 962944 | 1 | 58.4667 | 58.4667 | 3.5657e-05 | 6.0987e-05
2013-04-20 | ZN187:PA16 | URBAN | Vegetation | 962946 | 55 | 65 | 3575 | 0.0021803 | 0.0033543
2013-04-20 | 235:2121 | URBAN | Other | 962951 | 1 | 122 | 122 | 7.4404e-05 | 6.0987e-05
2013-04-20 | ZN711:PA32 | URBAN | Vegetation | 962962 | 58 | 93 | 5394 | 0.0032896 | 0.0035372
2013-04-20 | ZN15012:PA2 | URBAN | Vegetation | 962988 | 1 | 129.95 | 129.95 | 7.9252e-05 | 6.0987e-05
2013-04-20 | ZN12570:PA22 | URBAN | Vegetation | 962998 | 1 | 147.3333 | 147.3333 | 8.9854e-05 | 6.0987e-05
2013-04-21 | ZN2635:PA12 | SHORT RURAL | Equipment Failure | 963028 | 32 | 299.5 | 9584 | 0.005845 | 0.0019516
2013-04-21 | ZN129:PA18 | URBAN | Equipment Failure | 963030 | 45 | 263 | 11835 | 0.0072178 | 0.0027444
2013-04-21 | ZN129:PA5 | URBAN | Equipment Failure | 963030 | 4 | 263 | 1052 | 0.00064158 | 0.00024395
2013-04-21 | ZN847:PA22 | SHORT RURAL | Other | 963061 | 1 | 84.6833 | 84.6833 | 5.1646e-05 | 6.0987e-05
2013-04-21 | ZN180:PA16 | URBAN | Equipment Failure | 963064 | 49 | 56.6 | 2773.4 | 0.0016914 | 0.0029883
2013-04-21 | 261:81865 | URBAN | Other | 963079 | 1 | 31.4833 | 31.4833 | 1.9201e-05 | 6.0987e-05
2013-04-21 | ZN2602:PA42 | URBAN | Equipment Failure | 963106 | 1 | 308.1833 | 308.1833 | 0.00018795 | 6.0987e-05
2013-04-21 | ZN180:PA34 | URBAN | Equipment Failure | 963114 | 40 | 83 | 3320 | 0.0020248 | 0.0024395
2013-04-21 | 801:74123 | SHORT RURAL | Other | 963122 | 1 | 78 | 78 | 4.757e-05 | 6.0987e-05
2013-04-21 | 501:48123 | SHORT RURAL | Vegetation | 963129 | 22 | 118 | 2596 | 0.0015832 | 0.0013417
2013-04-21 | ZN3472:PA12 | URBAN | Other | 963141 | 46 | 134 | 6164 | 0.0037592 | 0.0028054
2013-04-21 | ZN180:PA16 | URBAN | Equipment Failure | 963146 | 49 | 912 | 44688 | 0.027254 | 0.0029883
2013-04-21 | ZN180:PA21 | URBAN | Equipment Failure | 963146 | 1 | 912 | 902 | 0.0005501 | 6.0987e-05
2013-04-21 | 509:48039 | LONG RURAL | Other | 963155 | 3 | 234.3 | 647.7 | 0.00039501 | 0.00018296
2013-04-21 | ZN180:PA43 | URBAN | Equipment Failure | 963175 | 1 | 234.25 | 234.25 | 0.00014286 | 6.0987e-05
2013-04-22 | ZN4990:PA51 52ABC | CBD | Equipment Failure | 963241 | 16 | 188 | 3008 | 0.0018345 | 0.00097579
2013-04-22 | 220:8689 | URBAN | Other | 963244 | 1 | 254.5 | 254.5 | 0.00015521 | 6.0987e-05
2013-04-22 | ZN10993:PA2 | URBAN | Equipment Failure | 963247 | 1 | 72.2667 | 72.2667 | 4.4073e-05 | 6.0987e-05
2013-04-22 | ZN35600:PA9 | URBAN | Equipment Failure | 963255 | 1 | 453.2833 | 453.2833 | 0.00027644 | 6.0987e-05
2013-04-20 | ZN15014:PA14 | SHORT RURAL | Equipment Failure | 963297 | 27 | 144 | 3888 | 0.0023712 | 0.0016466
2013-04-22 | ZN847:PA22 | SHORT RURAL | Vegetation | 963300 | 1 | 366.9167 | 366.9167 | 0.00022377 | 6.0987e-05
2013-04-22 | ZN15005:PA8 | URBAN | Equipment Failure | 963325 | 1 | 614.2833 | 614.2833 | 0.00037463 | 6.0987e-05
2013-04-19 | ZN2466:PA45 | URBAN | Third Party Impacts | 963355 | 41 | 40 | 1640 | 0.0010002 | 0.0025005
2013-04-22 | 813:89061 | LONG RURAL | Third Party Impacts | 963438 | 112 | 176 | 4172 | 0.0025444 | 0.0068305
2013-04-22 | ZN3425:PA16 | URBAN | Equipment Failure | 963463 | 1 | 239.4833 | 239.4833 | 0.00014605 | 6.0987e-05
2013-04-22 | ZN9118:PA20 | URBAN | Other | 963508 | 1 | 376.6 | 376.6 | 0.00022968 | 6.0987e-05
2013-04-22 | ZN2602:PA18 | URBAN | Equipment Failure | 963541 | 2 | 246.85 | 493.7 | 0.00030109 | 0.00012197
2013-04-22 | ZN3472:PA28 | URBAN | Other | 963544 | 1 | 935 | 935 | 0.00057023 | 6.0987e-05
2013-04-22 | ZN901:PA14 | URBAN | Equipment Failure | 963574 | 47 | 118 | 5546 | 0.0033823 | 0.0028664
2013-04-22 | ZN901:PA32 | URBAN | Equipment Failure | 963574 | 61 | 118 | 7198 | 0.0043898 | 0.0037202
2013-04-22 | ZN9037:PA4 | URBAN | Animals | 963589 | 2 | 80 | 66 | 4.0251e-05 | 0.00012197
2013-04-22 | ZN9037:PA8 | URBAN | Animals | 963589 | 2 | 80 | 90 | 5.4888e-05 | 0.00012197
2013-04-22 | ZN9700:PA16 | URBAN | Animals | 963589 | 1 | 80 | 45 | 2.7444e-05 | 6.0987e-05
2013-04-22 | ZN9700:PA23 | URBAN | Animals | 963589 | 1684 | 80 | 69439 | 0.042349 | 0.1027
2013-04-22 | ZN342:PA35 | URBAN | Equipment Failure | 963614 | 782 | 75 | 58650 | 0.035769 | 0.047692
2013-04-23 | ZN12630:PA1 | SHORT RURAL | Vegetation | 963616 | 97 | 444 | 12885 | 0.0079009 | 0.0059479
2013-04-23 | ZN12570:PA24 | SHORT RURAL | Equipment Failure | 963619 | 8 | 226 | 1808 | 0.0011086 | 0.00049055
2013-04-23 | 502:48010 | SHORT RURAL | Other | 963621 | 1558 | 184 | 286032 | 0.17539 | 0.095534
2013-04-23 | 512:48049 | SHORT RURAL | Equipment Failure | 963623 | 56 | 366 | 10458 | 0.0064127 | 0.0034338
2013-04-23 | ZN35370:PA8 | SHORT RURAL | Equipment Failure | 963630 | 25 | 111.7333 | 2793.3333 | 0.0017128 | 0.001533
2013-04-23 | ZN12640:PA2 | URBAN | Third Party Impacts | 963648 | 130 | 337 | 43810 | 0.026864 | 0.0079714
2013-04-23 | 217:33612 | URBAN | Other | 963660 | 1 | 27.3333 | 27.3333 | 1.676e-05 | 6.1319e-05
2013-04-23 | ZN12640:PA6 | URBAN | Other | 963662 | 1 | 61.0333 | 61.0333 | 3.7425e-05 | 6.1319e-05
2013-04-23 | ZN14892:PA16 | URBAN | Other | 963727 | 1 | 194.0167 | 194.0167 | 0.00011897 | 6.1319e-05
2013-04-23 | 232:11454 | SHORT RURAL | Equipment Failure | 963782 | 86 | 136 | 11696 | 0.0071718 | 0.0052734
2013-04-23 | 202:34231 37 42 | URBAN | Other | 963810 | 6 | 72.9667 | 433.9 | 0.00026606 | 0.00036791
2013-04-23 | 202:34261 | SHORT RURAL | Other | 963810 | 45 | 72.9667 | 2565 | 0.0015728 | 0.0027593
2013-04-23 | ZN180:PA34 | URBAN | Third Party Impacts | 963825 | 1 | 488.8333 | 488.8333 | 0.00029975 | 6.1319e-05
2013-04-23 | ZN1850:PA13 | URBAN | Third Party Impacts | 963848 | 53 | 83.7333 | 4437.8667 | 0.0027212 | 0.0032499
2013-04-23 | ZN36300:PA9 | URBAN | Third Party Impacts | 963889 | 114 | 73.6833 | 8399.9 | 0.0051507 | 0.0069903
2013-04-23 | ZN15006:PA13 | URBAN | Equipment Failure | 963895 | 1 | 176.5667 | 176.5667 | 0.00010827 | 6.1319e-05
2013-04-23 | ZN3155:PA23 | URBAN | Other | 963948 | 1 | 163.7167 | 163.7167 | 0.00010039 | 6.1319e-05
2013-04-23 | ZN2835:PA36 | URBAN | Other | 963951 | 20 | 86.45 | 1729 | 0.0010602 | 0.0012264
2013-04-23 | ZN36300:PA13 | URBAN | Vegetation | 963961 | 1 | 107 | 58 | 3.5565e-05 | 6.1319e-05
2013-04-23 | ZN36300:PA17 | URBAN | Vegetation | 963961 | 1398 | 107 | 128146 | 0.078577 | 0.085723
2013-04-23 | ZN9037:PA16 | URBAN | Equipment Failure | 963982 | 1 | 133.0333 | 133.0333 | 8.1574e-05 | 6.1319e-05
2013-04-24 | 511:29878 | SHORT RURAL | Equipment Failure | 963989 | 126 | 445 | 33968 | 0.020704 | 0.0076799
2013-04-24 | ZN3472:PA34 | URBAN | Equipment Failure | 963993 | 1 | 409 | 409 | 0.00024929 | 6.0951e-05
2013-04-24 | ZN3154:PA13 | URBAN | Vegetation | 963996 | 605 | 39 | 23595 | 0.014381 | 0.036876
2013-04-23 | 509:48039 | LONG RURAL | Equipment Failure | 964027 | 12 | 246 | 2952 | 0.0018101 | 0.00073582
2013-04-24 | 810:74050 | SHORT RURAL | Equipment Failure | 964135 | 1 | 294.05 | 294.05 | 0.00017923 | 6.0951e-05
2013-04-24 | ZN180:PA15 | URBAN | Equipment Failure | 964202 | 1 | 518.25 | 518.25 | 0.00031588 | 6.0951e-05
2013-04-24 | 221:11899 | URBAN | Other | 964297 | 1 | 103.7 | 103.7 | 6.3207e-05 | 6.0951e-05
2013-04-24 | ZN2310:PA3 | URBAN | Equipment Failure | 964301 | 1 | 264.3833 | 264.3833 | 0.00016115 | 6.0951e-05
2013-04-24 | ZN13000:PA11 | URBAN | Vegetation | 964338 | 46 | 91.3333 | 4201.3333 | 0.0025608 | 0.0028038
2013-04-24 | 238:34137 | URBAN | Equipment Failure | 964353 | 7 | 70 | 490 | 0.00029866 | 0.00042666
2013-04-24 | 238:34137 | URBAN | Equipment Failure | 964356 | 11 | 77 | 847 | 0.00051626 | 0.00067046
2013-04-24 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 964358 | 8 | 54 | 432 | 0.00026331 | 0.00048761
2013-04-24 | 208:71 | URBAN | Equipment Failure | 964359 | 192 | 53.9167 | 7266 | 0.0044287 | 0.011703
2013-04-24 | 258:80781 | SHORT RURAL | Equipment Failure | 964359 | 2 | 53.9167 | 69.85 | 4.2574e-05 | 0.0001219
2013-04-25 | ZN1788:PA17 | URBAN | Equipment Failure | 964366 | 130 | 151 | 19630 | 0.011965 | 0.0079238
2013-04-25 | ZN12660:PA5 | SHORT RURAL | Equipment Failure | 964380 | 1 | 212.1833 | 212.1833 | 0.00012933 | 6.0952e-05
2013-04-25 | ZN12610:PA7 | URBAN | Other | 964382 | 1 | 165.45 | 165.45 | 0.00010085 | 6.0952e-05
2013-04-25 | ZN1287:PA22 | URBAN | Equipment Failure | 964430 | 1 | 302.4167 | 302.4167 | 0.00018433 | 6.0952e-05
2013-04-25 | ZN1285:PA18 | URBAN | Third Party Impacts | 964443 | 14 | 145 | 2030 | 0.0012373 | 0.00085333
2013-04-25 | ZN3472:PA31 | URBAN | Third Party Impacts | 964443 | 1 | 145 | 144.0167 | 8.7781e-05 | 6.0952e-05
2013-04-26 | ZN35500:PA31 | URBAN | Other | 964455 | 1 | 460.8333 | 460.8333 | 0.00028089 | 6.0952e-05
2013-04-26 | ZN12570:PA41 | URBAN | Other | 964463 | 1 | 741.8833 | 741.8833 | 0.00045219 | 6.0952e-05
2013-04-24 | 224:80331 | URBAN | Equipment Failure | 964519 | 23 | 25 | 575 | 0.00035047 | 0.0014019
2013-04-26 | 523:33501 | SHORT RURAL | Animals | 964522 | 1 | 47.8167 | 47.8167 | 2.9145e-05 | 6.0952e-05
2013-04-26 | 240:34840 | URBAN | Third Party Impacts | 964617 | 1587 | 176 | 60428 | 0.036832 | 0.096731
2013-04-26 | ZN116:PA50 | URBAN | Operational Error | 964628 | 1729 | 4 | 6916 | 0.0042154 | 0.10539
2013-04-26 | ZN7481:PA20 | URBAN | Operational Error | 964628 | 803 | 4 | 3212 | 0.0019578 | 0.048945
2013-04-26 | 203:8084 | URBAN | Vegetation | 964630 | 1 | 154.7333 | 154.7333 | 9.4313e-05 | 6.0952e-05
2013-04-26 | ZN116:PA42 | URBAN | Vegetation | 964644 | 1 | 167.7 | 167.7 | 0.00010222 | 6.0952e-05
2013-04-26 | ZN965:PA43 | URBAN | Equipment Failure | 964666 | 1023 | 140 | 102117 | 0.062242 | 0.062354
2013-04-26 | ZN35500:PA27 | URBAN | Other | 964672 | 1 | 275.05 | 275.05 | 0.00016765 | 6.0952e-05
2013-04-26 | ZN2400:PA15 | URBAN | Other | 964698 | 1 | 121.7667 | 121.7667 | 7.4219e-05 | 6.0952e-05
2013-04-26 | ZN12650:PA20 | URBAN | Vegetation | 964723 | 1 | 346.4167 | 346.4167 | 0.00021115 | 6.0952e-05
2013-04-26 | ZN9118:PA12 | URBAN | Equipment Failure | 964735 | 34 | 39 | 1326 | 0.00080822 | 0.0020724
2013-04-26 | ZN13000:PA5 | SHORT RURAL | Equipment Failure | 964761 | 8 | 152 | 1216 | 0.00074118 | 0.00048762
2013-04-26 | ZN15010:PA11 | URBAN | Third Party Impacts | 964770 | 1 | 315.1667 | 315.1667 | 0.0001921 | 6.0952e-05
2013-04-26 | 501:48122 | SHORT RURAL | Equipment Failure | 964781 | 1 | 75 | 75 | 4.5714e-05 | 6.0952e-05
2013-04-26 | ZN12570:PA25 | SHORT RURAL | Vegetation | 964783 | 71 | 363.75 | 25826.25 | 0.015742 | 0.0043276
2013-04-26 | ZN12570:PA25 | SHORT RURAL | Other | 964784 | 1 | 57.7667 | 57.7667 | 3.521e-05 | 6.0952e-05
2013-04-26 | ZN847:PA23 | URBAN | Other | 964785 | 35 | 217 | 7595 | 0.0046293 | 0.0021333
2013-04-27 | ZN10995:PA1 | URBAN | Equipment Failure | 964805 | 127 | 93.7667 | 11908.3667 | 0.0072584 | 0.0077409
2013-04-27 | 220:8687 | URBAN | Equipment Failure | 964808 | 69 | 357.45 | 24664.05 | 0.015033 | 0.0042057
2013-04-27 | ZN2602:PA30 | URBAN | Equipment Failure | 964812 | 1 | 310.6333 | 310.6333 | 0.00018934 | 6.0952e-05
2013-04-27 | 507:80923 | SHORT RURAL | Other | 964813 | 28 | 76.1167 | 2131.2667 | 0.0012991 | 0.0017067
2013-04-27 | ZN2602:PA21 | URBAN | Other | 964820 | 1 | 408.8333 | 408.8333 | 0.00024919 | 6.0952e-05
2013-04-27 | ZN12640:PA18 | SHORT RURAL | Equipment Failure | 964824 | 54 | 153.35 | 8280.9 | 0.0050474 | 0.0032914
2013-04-27 | ZN12600:PA9 | SHORT RURAL | Third Party Impacts | 964854 | 1 | 287.7833 | 287.7833 | 0.00017541 | 6.0952e-05
2013-04-27 | ZN9550:PA36 | URBAN | Equipment Failure | 964870 | 53 | 116 | 6148 | 0.0037473 | 0.0032305
2013-04-27 | ZN12660:PA14 | SHORT RURAL | Equipment Failure | 964918 | 54 | 59.35 | 3204.9 | 0.0019535 | 0.0032914
2013-04-27 | ZN12580:PA1 | URBAN | Vegetation | 964922 | 1 | 195.9 | 195.9 | 0.00011941 | 6.0952e-05
2013-04-27 | ZN35335:PA14 | URBAN | Equipment Failure | 964933 | 205 | 84 | 17165 | 0.010462 | 0.012495
2013-04-27 | ZN80:PA32 | URBAN | Equipment Failure | 964934 | 17 | 46 | 782 | 0.00047665 | 0.0010362
2013-04-27 | ZN1193:PA21 | URBAN | Other | 964940 | 1 | 37.8 | 37.8 | 2.304e-05 | 6.0952e-05
2013-04-27 | ZN12580:PA16 | URBAN | Equipment Failure | 964945 | 79 | 46 | 3634 | 0.002215 | 0.0048152
2013-04-28 | ZN35800:PA1 | URBAN | Equipment Failure | 964952 | 1 | 530.65 | 530.65 | 0.00032344 | 6.0952e-05
2013-04-28 | ZN1788:PA17 | URBAN | Equipment Failure | 964955 | 130 | 207.3333 | 26953.3333 | 0.016429 | 0.0079238
2013-04-28 | ZN12650:PA17 | URBAN | Equipment Failure | 964957 | 100 | 245 | 24500 | 0.014933 | 0.0060952
2013-04-28 | ZN15015:PA15 | URBAN | Vegetation | 964958 | 20 | 151 | 3020 | 0.0018408 | 0.001219
2013-04-28 | ZN35800:PA1 | URBAN | Equipment Failure | 964960 | 2 | 203.6 | 407.2 | 0.0002482 | 0.0001219
2013-04-28 | ZN12620:PA11 | SHORT RURAL | Equipment Failure | 965002 | 1 | 237.5833 | 237.5833 | 0.00014481 | 6.0952e-05
2013-04-28 | ZN965:PA8 | URBAN | Equipment Failure | 965003 | 1 | 302.4667 | 302.4667 | 0.00018436 | 6.0952e-05
2013-04-28 | 202:34261 | SHORT RURAL | Other | 965009 | 45 | 33 | 1485 | 0.00090514 | 0.0027428
2013-04-28 | ZN3154:PA10 | URBAN | Vegetation | 965014 | 47 | 73 | 3431 | 0.0020913 | 0.0028647
2013-04-28 | 520:48172 | SHORT RURAL | Other | 965025 | 3 | 74.8333 | 224.5 | 0.00013684 | 0.00018286
2013-04-28 | ZN10999:PA4 | URBAN | Equipment Failure | 965031 | 1666 | 52 | 78638 | 0.047931 | 0.10155
2013-04-28 | ZN15006:PA8 | URBAN | Other | 965047 | 1 | 59.95 | 59.95 | 3.6541e-05 | 6.0952e-05
2013-04-28 | ZN14891:PA20 | SHORT RURAL | Animals | 965064 | 514 | 51.7167 | 26582.3667 | 0.016203 | 0.031329
2013-04-29 | ZN1193:PA27 | URBAN | Vegetation | 965130 | 1 | 162.1667 | 162.1667 | 9.8844e-05 | 6.0952e-05
2013-04-26 | 231:8415 | SHORT RURAL | Animals | 965132 | 817 | 139 | 95564 | 0.058248 | 0.049798
2013-04-29 | 801:74119 | URBAN | Equipment Failure | 965146 | 1 | 84.1167 | 84.1167 | 5.1271e-05 | 6.0952e-05
2013-04-29 | ZN10994:PA4 | URBAN | Equipment Failure | 965198 | 44 | 64.0167 | 2816.7333 | 0.0017169 | 0.0026819
2013-04-27 | 507:80932 | SHORT RURAL | Other | 965207 | 1117 | 84 | 84935 | 0.05177 | 0.068083
2013-04-29 | 813:89062 | SHORT RURAL | Vegetation | 965283 | 1 | 452.8167 | 452.8167 | 0.000276 | 6.0952e-05
2013-04-29 | 213:33771 | URBAN | Vegetation | 965292 | 1 | 186.3833 | 186.3833 | 0.0001136 | 6.0952e-05
2013-04-29 | ZN9252:PA3 | URBAN | Equipment Failure | 965305 | 660 | 101 | 38742 | 0.023614 | 0.040228
2013-04-29 | ZN80:PA32 | URBAN | Other | 965429 | 109 | 18.9667 | 2067.3667 | 0.0012601 | 0.0066438
2013-04-29 | ZN10995:PA2 | URBAN | Third Party Impacts | 965461 | 35 | 90 | 3150 | 0.00192 | 0.0021333
2013-04-29 | 214:8669 | URBAN | Other | 965462 | 1 | 81 | 81 | 4.9371e-05 | 6.0952e-05
2013-04-29 | 813:89062 | SHORT RURAL | Equipment Failure | 965464 | 33 | 477 | 10335 | 0.0062994 | 0.0020114
2013-04-29 | ZN12620:PA7 | URBAN | Equipment Failure | 965470 | 67 | 57 | 3819 | 0.0023278 | 0.0040838
2013-04-29 | ZN384:PA9 | URBAN | Equipment Failure | 965487 | 6 | 285 | 1710 | 0.0010423 | 0.00036571
2013-04-30 | 220:8689 | URBAN | Other | 965517 | 1 | 142.3333 | 142.3333 | 8.6731e-05 | 6.0935e-05
2013-04-30 | ZN12570:PA37 | SHORT RURAL | Third Party Impacts | 965544 | 2028 | 80 | 156353 | 0.095274 | 0.12358
2013-04-30 | ZN129:PA18 | URBAN | Equipment Failure | 965566 | 45 | 250.8833 | 11289.75 | 0.0068795 | 0.0027421
2013-04-30 | ZN129:PA5 | URBAN | Equipment Failure | 965566 | 4 | 250.8833 | 1003.5333 | 0.00061151 | 0.00024374
2013-04-21 | ZN3472:PA15 | URBAN | Other | 965628 | 46 | 300 | 13800 | 0.0084162 | 0.0028054
2013-04-30 | 232:11457 | URBAN | Vegetation | 965676 | 1 | 320.4167 | 320.4167 | 0.00019525 | 6.0935e-05
2013-04-30 | ZN2310:PA4 | URBAN | Third Party Impacts | 965736 | 1 | 105.0333 | 105.0333 | 6.4003e-05 | 6.0935e-05
2013-04-30 | 206:34434 | URBAN | Other | 965835 | 1 | 101.2 | 101.2 | 6.1667e-05 | 6.0935e-05
2013-04-30 | 801:74121 | SHORT RURAL | Equipment Failure | 965868 | 9 | 65 | 585 | 0.00035647 | 0.00054842
2013-04-30 | 205:12203 | URBAN | Equipment Failure | 965902 | 3 | 474 | 1422 | 0.0008665 | 0.00018281
2013-04-30 | 806:82662 | SHORT RURAL | Other | 965908 | 2 | 124 | 248 | 0.00015112 | 0.00012187
2013-04-30 | 202:34245 | URBAN | Other | 965911 | 1 | 111.4667 | 111.4667 | 6.7923e-05 | 6.0935e-05
2013-05-01 | 810:74054 | LONG RURAL | Other | 965918 | 1 | 4.1167 | 4.1167 | 2.5085e-06 | 6.0936e-05
2013-05-01 | 230:81440 | URBAN | Other | 965920 | 1 | 239.5667 | 239.5667 | 0.00014598 | 6.0936e-05
2013-05-01 | ZN14891:PA5 | SHORT RURAL | Other | 965955 | 1 | 109.7833 | 109.7833 | 6.6897e-05 | 6.0936e-05
2013-05-01 | ZN195:PA9 | URBAN | Third Party Impacts | 965984 | 1 | 304.4167 | 304.4167 | 0.0001855 | 6.0936e-05
2013-05-01 | 239:82128 | SHORT RURAL | Other | 965998 | 87 | 120 | 10440 | 0.0063617 | 0.0053014
2013-05-01 | 812:19066 | SHORT RURAL | Third Party Impacts | 966112 | 1 | 28.3333 | 28.3333 | 1.7265e-05 | 6.0936e-05
2013-05-01 | 261:81864 | URBAN | Other | 966120 | 1 | 115.35 | 115.35 | 7.029e-05 | 6.0936e-05
2013-05-01 | ZN9245:PA14 | URBAN | Third Party Impacts | 966142 | 1 | 13 | 13 | 7.9217e-06 | 6.0936e-05
2013-04-26 | 813:89063 | SHORT RURAL | Equipment Failure | 966161 | 4 | 145 | 580 | 0.00035352 | 0.00024381
2013-04-26 | 813:89063 | SHORT RURAL | Equipment Failure | 966162 | 4 | 135 | 540 | 0.00032914 | 0.00024381
2013-05-01 | ZN12610:PA11 | URBAN | Equipment Failure | 966164 | 32 | 93 | 2976 | 0.0018135 | 0.0019499
2013-05-01 | ZN12650:PA19 | SHORT RURAL | Third Party Impacts | 966216 | 1 | 362.3833 | 362.3833 | 0.00022082 | 6.0936e-05
2013-05-01 | 242:81535 | URBAN | Other | 966239 | 1 | 198.15 | 198.15 | 0.00012074 | 6.0936e-05
2013-05-01 | ZN15010:PA5 | URBAN | Other | 966272 | 1 | 361.0833 | 361.0833 | 0.00022003 | 6.0936e-05
2013-05-01 | ZN10993:PA2 | URBAN | Third Party Impacts | 966335 | 1 | 389.2833 | 389.2833 | 0.00023721 | 6.0936e-05
2013-05-01 | 503:48011 | SHORT RURAL | Equipment Failure | 966348 | 14 | 294 | 4116 | 0.0025081 | 0.0008531
2013-05-01 | 504:48033 | SHORT RURAL | Other | 966372 | 4 | 209.5667 | 838.2667 | 0.00051081 | 0.00024374
2013-05-01 | ZN12660:PA6 | SHORT RURAL | Vegetation | 966500 | 39 | 284 | 11076 | 0.0067493 | 0.0023765
2013-05-01 | ZN187:PA13 | URBAN | Vegetation | 966504 | 91 | 158 | 14378 | 0.0087614 | 0.0055452
2013-05-02 | ZN965:PA3 | URBAN | Vegetation | 966507 | 28 | 158 | 4424 | 0.0026958 | 0.0017062
2013-05-02 | ZN7900:PA24 | URBAN | Other | 966522 | 11 | 206 | 2266 | 0.0013808 | 0.0006703
2013-05-02 | ZN901:PA24 | URBAN | Other | 966522 | 73 | 206 | 15038 | 0.0091636 | 0.0044484
2013-05-02 | 813:89062 | SHORT RURAL | Other | 966577 | 1 | 75.8 | 75.8 | 4.619e-05 | 6.0936e-05
2013-05-02 | ZN180:PA10 | URBAN | Third Party Impacts | 966645 | 1 | 318.3667 | 318.3667 | 0.000194 | 6.0936e-05
2013-05-02 | ZN12580:PA4 | URBAN | Third Party Impacts | 966767 | 1 | 147.7 | 147.7 | 9.0003e-05 | 6.0936e-05
2013-05-02 | 230:81434 | URBAN | Equipment Failure | 966903 | 17 | 80 | 1360 | 0.00082873 | 0.0010359
2013-05-02 | ZN2602:PA30 | URBAN | Equipment Failure | 966933 | 171 | 1404.5667 | 240180.9 | 0.14636 | 0.01042
2013-05-02 | 261:81864 | URBAN | Other | 966951 | 1 | 81.7167 | 81.7167 | 4.9795e-05 | 6.0936e-05
2013-05-03 | 512:48046 | SHORT RURAL | Equipment Failure | 966966 | 1 | 477.35 | 477.35 | 0.00029088 | 6.0937e-05
2013-05-03 | 812:19071 | SHORT RURAL | Equipment Failure | 967058 | 61 | 240 | 14640 | 0.0089211 | 0.0037171
2013-05-03 | ZN12610:PA18 | URBAN | Other | 967077 | 1 | 225.1833 | 225.1833 | 0.00013722 | 6.0937e-05
2013-05-03 | 811:74234 | SHORT RURAL | Equipment Failure | 967091 | 1 | 79.3667 | 79.3667 | 4.8363e-05 | 6.0937e-05
2013-05-03 | 224:80337 | URBAN | Other | 967093 | 1 | 300.7667 | 300.7667 | 0.00018328 | 6.0937e-05
2013-05-03 | 813:89061 | LONG RURAL | Equipment Failure | 967099 | 2 | 195 | 390 | 0.00023765 | 0.00012187
2013-05-03 | 812:19071 | SHORT RURAL | Other | 967133 | 1 | 29.8167 | 29.8167 | 1.8169e-05 | 6.0937e-05
2013-05-03 | ZN1648:PA20 | URBAN | Third Party Impacts | 967144 | 1 | 96.7833 | 96.7833 | 5.8977e-05 | 6.0937e-05
2013-05-03 | ZN12610:PA17 | URBAN | Equipment Failure | 967162 | 1191 | 138 | 120940 | 0.073697 | 0.072576
2013-05-03 | 243:80074 | URBAN | Other | 967166 | 1 | 187.3333 | 187.3333 | 0.00011415 | 6.0937e-05
2013-05-03 | ZN15014:PA19 | URBAN | Third Party Impacts | 967189 | 1 | 267.8333 | 267.8333 | 0.00016321 | 6.0937e-05
2013-05-03 | 258:80785 | URBAN | Other | 967210 | 1 | 46.8667 | 46.8667 | 2.8559e-05 | 6.0937e-05
2013-05-03 | 203:8089 | URBAN | Equipment Failure | 967220 | 466 | 340 | 73316 | 0.044676 | 0.028397
2013-05-03 | ZN15010:PA1 | URBAN | Equipment Failure | 967222 | 1 | 247.4667 | 247.4667 | 0.0001508 | 6.0937e-05
2013-05-03 | 523:33501 | SHORT RURAL | Other | 967235 | 1 | 88.8667 | 88.8667 | 5.4152e-05 | 6.0937e-05
2013-05-03 | 513:48059 | SHORT RURAL | Equipment Failure | 967261 | 1 | 56 | 56 | 3.4125e-05 | 6.0937e-05
2013-05-04 | 807:74183 | SHORT RURAL | Other | 967271 | 1 | 163.4833 | 163.4833 | 9.9621e-05 | 6.0937e-05
2013-05-04 | 511:29878 | SHORT RURAL | Other | 967297 | 1 | 155.1833 | 155.1833 | 9.4564e-05 | 6.0937e-05
2013-05-04 | ZN12690:PA12 | SHORT RURAL | Equipment Failure | 967316 | 1 | 316.25 | 316.25 | 0.00019271 | 6.0937e-05
2013-05-04 | 515:35197 | LONG RURAL | Third Party Impacts | 967329 | 2 | 163 | 326 | 0.00019865 | 0.00012187
2013-05-04 | ZN2310:PA10 | URBAN | Equipment Failure | 967346 | 1 | 264.2 | 264.2 | 0.00016099 | 6.0937e-05
2013-05-04 | ZN12580:PA16 | URBAN | Animals | 967357 | 2 | 37.6 | 75.2 | 4.5824e-05 | 0.00012187
2013-05-05 | 238:34144 | URBAN | Vegetation | 967366 | 1 | 56.6667 | 56.6667 | 3.4531e-05 | 6.0937e-05
2013-05-05 | ZN14144:PA10 | SHORT RURAL | Animals | 967368 | 10 | 581 | 5810 | 0.0035404 | 0.00060937
2013-05-05 | ZN10990:PA7 | URBAN | Equipment Failure | 967384 | 25 | 86 | 2150 | 0.0013101 | 0.0015234
2013-05-05 | 502:48004 | URBAN | Equipment Failure | 967403 | 1 | 352.4333 | 352.4333 | 0.00021476 | 6.0937e-05
2013-05-05 | ZN15005:PA10 | URBAN | Equipment Failure | 967439 | 83 | 17 | 1411 | 0.00085982 | 0.0050578
2013-05-05 | 812:19072 | SHORT RURAL | Other | 967448 | 1 | 140.3333 | 140.3333 | 8.5515e-05 | 6.0937e-05
2013-05-05 | ZN12610:PA10 | SHORT RURAL | Equipment Failure | 967455 | 1 | 145.3 | 145.3 | 8.8541e-05 | 6.0937e-05
2013-05-05 | ZN15014:PA12 | SHORT RURAL | Equipment Failure | 967458 | 1 | 1217.8667 | 1217.8667 | 0.00074213 | 6.0937e-05
2013-05-05 | 243:80074 | URBAN | Other | 967470 | 1 | 87.4333 | 87.4333 | 5.3279e-05 | 6.0937e-05
2013-05-05 | ZN15009:PA11 | URBAN | Equipment Failure | 967472 | 77 | 146 | 11242 | 0.0068505 | 0.0046921
2013-05-05 | ZN116:PA36 | URBAN | Equipment Failure | 967477 | 92 | 192.3667 | 17697.7333 | 0.010784 | 0.0056062
2013-05-05 | ZN80:PA22 | URBAN | Equipment Failure | 967484 | 54 | 43 | 2322 | 0.001415 | 0.0032906
2013-05-05 | ZN80:PA27 | URBAN | Equipment Failure | 967484 | 724 | 43 | 31132 | 0.018971 | 0.044118
2013-05-06 | ZN1287:PA3 | URBAN | Equipment Failure | 967490 | 63 | 35.4833 | 2235.45 | 0.0013622 | 0.003839
2013-05-06 | ZN398:PA16 | URBAN | Equipment Failure | 967495 | 2049 | 111 | 180086 | 0.10974 | 0.12486
2013-05-06 | 508:82578 | SHORT RURAL | Equipment Failure | 967511 | 7 | 574.3667 | 4020.5667 | 0.00245 | 0.00042656
2013-05-06 | 813:89055 | SHORT RURAL | Equipment Failure | 967537 | 4 | 145 | 580 | 0.00035343 | 0.00024375
2013-05-06 | ZN12650:PA20 | URBAN | Equipment Failure | 967549 | 60 | 179 | 10740 | 0.0065446 | 0.0036562
2013-05-02 | 806:82667 | SHORT RURAL | Other | 967616 | 2 | 115 | 230 | 0.00014015 | 0.00012187
2013-05-06 | 502:48010 | SHORT RURAL | Equipment Failure | 967662 | 9 | 523 | 4707 | 0.0028683 | 0.00054843
2013-04-28 | ZN965:PA20 | URBAN | Equipment Failure | 967677 | 32 | 202 | 2217 | 0.0013513 | 0.0019505
2013-05-06 | ZN965:PA24 | SHORT RURAL | Equipment Failure | 967692 | 30 | 97 | 2908.0667 | 0.0017721 | 0.0018281
2013-05-06 | 802:82225 | SHORT RURAL | Other | 967700 | 2 | 35 | 70 | 4.2656e-05 | 0.00012187
2013-05-02 | 216:10724 | SHORT RURAL | Weather | 967817 | 2 | 445 | 890 | 0.00054233 | 0.00012187
2013-05-06 | 221:11895 | URBAN | Other | 967880 | 1 | 44.4 | 44.4 | 2.7056e-05 | 6.0937e-05
2013-05-06 | 512:48049 | SHORT RURAL | Equipment Failure | 967896 | 2 | 35 | 70 | 4.2656e-05 | 0.00012187
2013-05-06 | 803:74016 | SHORT RURAL | Animals | 967933 | 1 | 30 | 30 | 1.8281e-05 | 6.0937e-05
2013-05-06 | ZN12640:PA7 | URBAN | Other | 967936 | 1 | 116.2667 | 116.2667 | 7.0849e-05 | 6.0937e-05
2013-05-06 | 243:80084 | SHORT RURAL | Equipment Failure | 967956 | 1 | 315.2833 | 315.2833 | 0.00019212 | 6.0937e-05
2013-05-06 | ZN1600:PA23ABC | CBD | Other | 967957 | 14 | 110 | 1540 | 0.00093843 | 0.00085311
2013-05-06 | ZN4990:PA55 56GHJ | CBD | Other | 967957 | 1 | 110 | 110 | 6.703e-05 | 6.0937e-05
2013-05-07 | ZN262:PA20 | URBAN | Other | 967978 | 1 | 157.75 | 157.75 | 9.6103e-05 | 6.0921e-05
2013-05-07 | ZN690:PA3 | URBAN | Vegetation | 967981 | 39 | 234 | 9126 | 0.0055597 | 0.0023759
2013-05-07 | 229:34983 | SHORT RURAL | Equipment Failure | 968017 | 1 | 179.85 | 179.85 | 0.00010957 | 6.0921e-05
2013-05-07 | ZN187:PA17 | URBAN | Third Party Impacts | 968043 | 133 | 113.7 | 8028.1667 | 0.0048909 | 0.0081025
2013-05-07 | ZN187:PA19 | URBAN | Third Party Impacts | 968043 | 78 | 113.7 | 4680 | 0.0028511 | 0.0047519
2013-05-07 | ZN3154:PA23 | URBAN | Third Party Impacts | 968074 | 50 | 77 | 3850 | 0.0023455 | 0.0030461
2013-05-07 | 810:74054 | LONG RURAL | Equipment Failure | 968105 | 1 | 333.75 | 333.75 | 0.00020332 | 6.0921e-05
2013-05-07 | ZN14144:PA7 | SHORT RURAL | Equipment Failure | 968179 | 1 | 240.3 | 240.3 | 0.00014639 | 6.0921e-05
2013-05-07 | 216:10726 | URBAN | Other | 968241 | 1 | 98.75 | 98.75 | 6.016e-05 | 6.0921e-05
2013-05-07 | ZN711:PA15 | URBAN | Equipment Failure | 968368 | 441 | 50 | 20763 | 0.012649 | 0.026866
2013-05-07 | 216:10727 | URBAN | Other | 968411 | 1 | 117.1833 | 117.1833 | 7.1389e-05 | 6.0921e-05
2013-05-07 | 515:35200 | URBAN | Third Party Impacts | 968419 | 73 | 56 | 4088 | 0.0024905 | 0.0044472
2013-05-08 | ZN269:PA1 | URBAN | Other | 968423 | 1 | 274.2 | 274.2 | 0.00016705 | 6.0922e-05
2013-05-08 | ZN180:PA32 | URBAN | Equipment Failure | 968425 | 1 | 819.4333 | 819.4333 | 0.00049922 | 6.0922e-05
2013-05-08 | 224:80340 | SHORT RURAL | Third Party Impacts | 968433 | 122 | 510 | 62220 | 0.037906 | 0.0074325
2013-05-08 | ZN12570:PA35 | URBAN | Equipment Failure | 968438 | 10 | 197.5667 | 1975.6667 | 0.0012036 | 0.00060922
2013-05-08 | ZN10999:PA4 | URBAN | Equipment Failure | 968441 | 1 | 148.8 | 148.8 | 9.0653e-05 | 6.0922e-05
2013-05-08 | ZN12570:PA37 | SHORT RURAL | Other | 968447 | 1 | 164.5 | 164.5 | 0.00010022 | 6.0922e-05
2013-05-08 | ZN1850:PA14 | URBAN | Other | 968464 | 27 | 196.8167 | 5314.05 | 0.0032375 | 0.0016449
2013-05-08 | 503:48078 | URBAN | Equipment Failure | 968471 | 1 | 187.7 | 187.7 | 0.00011435 | 6.0922e-05
2013-05-08 | ZN690:PA10 | URBAN | Third Party Impacts | 968572 | 75 | 74 | 5550 | 0.0033812 | 0.0045692
2013-05-08 | ZN2400:PA21 | URBAN | Other | 968578 | 1 | 182.3333 | 182.3333 | 0.00011108 | 6.0922e-05
2013-05-08 | 509:48039 | LONG RURAL | Equipment Failure | 968618 | 18 | 50 | 900 | 0.0005483 | 0.0010966
2013-05-08 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 968706 | 1 | 313.6667 | 313.6667 | 0.00019109 | 6.0922e-05
2013-05-08 | 239:82132 | URBAN | Vegetation | 968713 | 1 | 164.65 | 164.65 | 0.00010031 | 6.0922e-05
2013-05-08 | ZN15002:PA8 | URBAN | Other | 968761 | 22 | 100.2833 | 2206.2333 | 0.0013441 | 0.0013403
2013-05-08 | 229:34995 | SHORT RURAL | Other | 968803 | 1 | 128.65 | 128.65 | 7.8377e-05 | 6.0922e-05
2013-05-08 | 206:34441 | URBAN | Other | 968882 | 1 | 137.55 | 137.55 | 8.3799e-05 | 6.0922e-05
2013-05-08 | 216:10727 | URBAN | Other | 968883 | 1 | 205.3 | 205.3 | 0.00012507 | 6.0922e-05
2013-05-08 | ZN180:PA21 | URBAN | Equipment Failure | 968886 | 1 | 1746.7333 | 1746.7333 | 0.0010642 | 6.0922e-05
2013-05-08 | 503:48016 | URBAN | Equipment Failure | 968888 | 1 | 123.4167 | 123.4167 | 7.5189e-05 | 6.0922e-05
2013-05-09 | ZN269:PA1 | URBAN | Other | 968890 | 1 | 45.6833 | 45.6833 | 2.7832e-05 | 6.0923e-05
2013-05-09 | ZN269:PA1 | URBAN | Other | 968891 | 1 | 43.6 | 43.6 | 2.6562e-05 | 6.0923e-05
2013-05-09 | ZN9252:PA10 | URBAN | Other | 968893 | 1 | 194.8667 | 194.8667 | 0.00011872 | 6.0923e-05
2013-05-09 | ZN1850:PA12 | URBAN | Other | 968894 | 1 | 197.5333 | 197.5333 | 0.00012034 | 6.0923e-05
2013-05-09 | 524:33570 | SHORT RURAL | Equipment Failure | 968897 | 1 | 138 | 138 | 8.4074e-05 | 6.0923e-05
2013-05-09 | ZN116:PA34 | URBAN | Other | 968899 | 1 | 219.45 | 219.45 | 0.0001337 | 6.0923e-05
2013-05-09 | ZN1850:PA12 | URBAN | Other | 968900 | 1 | 151.9333 | 151.9333 | 9.2563e-05 | 6.0923e-05
2013-05-09 | ZN1850:PA12 | URBAN | Other | 968901 | 1 | 150.7 | 150.7 | 9.1811e-05 | 6.0923e-05
2013-05-09 | ZN35500:PA24 | URBAN | Other | 968902 | 1 | 242.45 | 242.45 | 0.00014771 | 6.0923e-05
2013-05-09 | ZN1287:PA17 | URBAN | Other | 968906 | 1 | 244.9 | 244.9 | 0.0001492 | 6.0923e-05
2013-05-09 | ZN12660:PA16 | URBAN | Equipment Failure | 968918 | 851 | 76 | 48866 | 0.029771 | 0.051846
2013-05-06 | ZN398:PA15 | URBAN | Other | 968940 | 70 | 168 | 11760 | 0.0071662 | 0.0042656
2013-05-09 | 504:48031 | SHORT RURAL | Other | 968943 | 535 | 64 | 33610 | 0.020476 | 0.032594
2013-05-09 | 504:48033 | SHORT RURAL | Other | 968943 | 1151 | 64 | 71228 | 0.043394 | 0.070123
2013-05-06 | ZN9550:PA43 | URBAN | Animals | 968955 | 1052 | 42 | 34544 | 0.02105 | 0.064105
2013-05-09 | 503:48017 | URBAN | Equipment Failure | 968976 | 1 | 195.95 | 195.95 | 0.00011938 | 6.0923e-05
2013-05-01 | ZN9245:PA14 | URBAN | Third Party Impacts | 968983 | 46 | 13 | 598 | 0.0003644 | 0.0028031
2013-05-01 | ZN9245:PA14 | URBAN | Third Party Impacts | 968984 | 3 | 13 | 39 | 2.3765e-05 | 0.00018281
2013-05-01 | ZN9245:PA14 | URBAN | Third Party Impacts | 968989 | 42 | 13 | 546 | 0.00033271 | 0.0025593
2013-05-09 | 801:74121 | SHORT RURAL | Third Party Impacts | 969000 | 1 | 111.3 | 111.3 | 6.7807e-05 | 6.0923e-05
2013-05-09 | 511:29877 | SHORT RURAL | Other | 969149 | 1 | 233.45 | 233.45 | 0.00014223 | 6.0923e-05
2013-05-09 | 222:2018 | URBAN | Other | 969174 | 1 | 190.8333 | 190.8333 | 0.00011626 | 6.0923e-05
2013-05-09 | ZN2196:PA18 | URBAN | Vegetation | 969207 | 932 | 76 | 70832 | 0.043153 | 0.05678
2013-05-09 | ZN3922:PA12 | URBAN | Other | 969212 | 1 | 237.8333 | 237.8333 | 0.0001449 | 6.0923e-05
2013-05-09 | ZN10995:PA7 | URBAN | Third Party Impacts | 969233 | 1 | 482.25 | 482.25 | 0.0002938 | 6.0923e-05
2013-05-09 | 202:34261 | SHORT RURAL | Other | 969234 | 51 | 52 | 2652 | 0.0016157 | 0.0031071
2013-05-09 | ZN269:PA19 | URBAN | Equipment Failure | 969290 | 72 | 100 | 7200 | 0.0043865 | 0.0043865
2013-05-09 | ZN2568:PA29 | URBAN | Equipment Failure | 969303 | 1 | 668.0667 | 668.0667 | 0.00040701 | 6.0923e-05
2013-05-09 | 224:80346 | URBAN | Other | 969307 | 1 | 128.7333 | 128.7333 | 7.8428e-05 | 6.0923e-05
2013-05-10 | 265:81648 | URBAN | Equipment Failure | 969308 | 1 | 256.35 | 256.35 | 0.00015618 | 6.0923e-05
2013-05-10 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 969309 | 19 | 159 | 3021 | 0.0018405 | 0.0011575
2013-05-10 | ZN1850:PA10 | URBAN | Other | 969313 | 1 | 483.1167 | 483.1167 | 0.00029433 | 6.0923e-05
2013-05-10 | ZN1287:PA11 | URBAN | Other | 969315 | 1 | 482.95 | 482.95 | 0.00029423 | 6.0923e-05
2013-05-10 | ZN1193:PA16 | URBAN | Other | 969317 | 1 | 298.6833 | 298.6833 | 0.00018197 | 6.0923e-05
2013-05-10 | 512:48048 | SHORT RURAL | Other | 969347 | 1 | 427.7167 | 427.7167 | 0.00026058 | 6.0923e-05
2013-05-10 | 214:8669 | URBAN | Other | 969353 | 1 | 134.8333 | 134.8333 | 8.2145e-05 | 6.0923e-05
2013-05-10 | ZN14891:PA5 | SHORT RURAL | Other | 969363 | 1 | 135.6833 | 135.6833 | 8.2663e-05 | 6.0923e-05
2013-05-09 | 807:74180 | SHORT RURAL | Other | 969373 | 2 | 30 | 60 | 3.6554e-05 | 0.00012185
2013-05-10 | 514:18137 | SHORT RURAL | Equipment Failure | 969377 | 3 | 110 | 330 | 0.00020105 | 0.00018277
2013-05-10 | 806:82662 | SHORT RURAL | Other | 969381 | 1 | 174.75 | 174.75 | 0.00010646 | 6.0923e-05
2013-05-10 | ZN35600:PA25 | URBAN | Other | 969383 | 1 | 379.6333 | 379.6333 | 0.00023129 | 6.0923e-05
2013-05-10 | 214:8669 | URBAN | Other | 969393 | 1 | 196.0333 | 196.0333 | 0.00011943 | 6.0923e-05
2013-05-10 | ZN9245:PA10 | URBAN | Third Party Impacts | 969408 | 68 | 92 | 6256 | 0.0038114 | 0.0041428
2013-05-10 | 232:11457 | URBAN | Other | 969416 | 1 | 154.05 | 154.05 | 9.3853e-05 | 6.0923e-05
2013-05-10 | ZN15006:PA9 | URBAN | Other | 969417 | 1 | 389.4667 | 389.4667 | 0.00023728 | 6.0923e-05
2013-05-10 | ZN3472:PA8 | URBAN | Other | 969421 | 1 | 146.4667 | 146.4667 | 8.9232e-05 | 6.0923e-05
2013-05-10 | ZN12610:PA11 | URBAN | Other | 969451 | 1 | 161.5667 | 161.5667 | 9.8432e-05 | 6.0923e-05
2013-05-10 | 234:2001 | URBAN | Other | 969493 | 1 | 61.5833 | 61.5833 | 3.7519e-05 | 6.0923e-05
2013-05-10 | ZN1164:PA3 | URBAN | Equipment Failure | 969541 | 131 | 147.2833 | 19294.1167 | 0.011755 | 0.007981
2013-05-10 | 511:29877 | SHORT RURAL | Other | 969556 | 1 | 181.0333 | 181.0333 | 0.00011029 | 6.0923e-05
2013-05-10 | 801:74119 | URBAN | Other | 969584 | 1 | 99.3167 | 99.3167 | 6.0507e-05 | 6.0923e-05
2013-05-10 | 224:80332 | URBAN | Other | 969609 | 1 | 121.1167 | 121.1167 | 7.3788e-05 | 6.0923e-05
2013-05-10 | ZN269:PA1 | URBAN | Equipment Failure | 969614 | 108 | 129 | 13932 | 0.0084879 | 0.0065797
2013-05-10 | 512:48049 | SHORT RURAL | Other | 969620 | 1 | 219.1 | 219.1 | 0.00013348 | 6.0923e-05
2013-05-10 | 806:82667 | SHORT RURAL | Other | 969622 | 1 | 202 | 202 | 0.00012307 | 6.0923e-05
2013-05-10 | ZN9118:PA21 | URBAN | Equipment Failure | 969628 | 1 | 193.2833 | 193.2833 | 0.00011775 | 6.0923e-05
2013-05-10 | ZN9037:PA10 | URBAN | Equipment Failure | 969635 | 1 | 463.4667 | 463.4667 | 0.00028236 | 6.0923e-05
2013-05-10 | ZN1068:PA27 | URBAN | Other | 969639 | 1 | 202.5667 | 202.5667 | 0.00012341 | 6.0923e-05
2013-05-10 | ZN9550:PA11 | URBAN | Third Party Impacts | 969643 | 1 | 137.3667 | 137.3667 | 8.3688e-05 | 6.0923e-05
2013-05-11 | ZN1287:PA15 | URBAN | Other | 969645 | 1 | 659.0833 | 659.0833 | 0.00040154 | 6.0923e-05
2013-05-11 | ZN10994:PA2 | URBAN | Other | 969646 | 1 | 497.2167 | 497.2167 | 0.00030292 | 6.0923e-05
2013-05-11 | ZN1287:PA4 | URBAN | Other | 969647 | 1 | 254.85 | 254.85 | 0.00015526 | 6.0923e-05
2013-05-11 | ZN965:PA21 | URBAN | Equipment Failure | 969648 | 71 | 235.0333 | 16687.3667 | 0.010167 | 0.0043256
2013-05-11 | 502:48004 | URBAN | Equipment Failure | 969651 | 1 | 289.7 | 289.7 | 0.0001765 | 6.0923e-05
2013-05-11 | ZN9550:PA42 | URBAN | Other | 969656 | 1 | 891.2833 | 891.2833 | 0.000543 | 6.0923e-05
2013-05-11 | ZN10994:PA12 | URBAN | Other | 969659 | 1 | 298.0667 | 298.0667 | 0.00018159 | 6.0923e-05
2013-05-11 | ZN9037:PA7 | URBAN | Equipment Failure | 969661 | 1 | 476.9833 | 476.9833 | 0.00029059 | 6.0923e-05
2013-05-11 | ZN398:PA2 | URBAN | Other | 969662 | 1 | 376.05 | 376.05 | 0.0002291 | 6.0923e-05
2013-05-11 | ZN12580:PA4 | URBAN | Equipment Failure | 969663 | 1 | 204.5833 | 204.5833 | 0.00012464 | 6.0923e-05
2013-05-11 | ZN35500:PA28 | URBAN | Equipment Failure | 969675 | 1 | 237.8333 | 237.8333 | 0.0001449 | 6.0923e-05
2013-05-11 | 239:82129 | SHORT RURAL | Other | 969687 | 1 | 101.8833 | 101.8833 | 6.2071e-05 | 6.0923e-05
2013-05-11 | ZN2310:PA25 | URBAN | Third Party Impacts | 969688 | 1 | 520.6833 | 520.6833 | 0.00031722 | 6.0923e-05
2013-05-11 | 202:34254 | URBAN | Other | 969697 | 1 | 76.3 | 76.3 | 4.6485e-05 | 6.0923e-05
2013-05-11 | 806:82662 | SHORT RURAL | Other | 969698 | 1 | 330.4667 | 330.4667 | 0.00020133 | 6.0923e-05
2013-05-11 | ZN9245:PA10 | URBAN | Equipment Failure | 969707 | 1 | 491.2167 | 491.2167 | 0.00029927 | 6.0923e-05
2013-05-11 | ZN180:PA41 | URBAN | Operational Error | 969741 | 2125 | 76 | 156169 | 0.095143 | 0.12946
2013-05-11 | 208:59 | URBAN | Vegetation | 969750 | 1 | 122.5167 | 122.5167 | 7.4641e-05 | 6.0923e-05
2013-05-11 | 264:81240 | SHORT RURAL | Other | 969758 | 1 | 112.2 | 112.2 | 6.8356e-05 | 6.0923e-05
2013-05-11 | 512:48049 | SHORT RURAL | Other | 969760 | 1 | 284.8333 | 284.8333 | 0.00017353 | 6.0923e-05
2013-05-11 | ZN1610:PA11 | URBAN | Other | 969773 | 1 | 365.8833 | 365.8833 | 0.00022291 | 6.0923e-05
2013-05-11 | ZN1648:PA20 | URBAN | Other | 969782 | 1 | 301.8333 | 301.8333 | 0.00018389 | 6.0923e-05
2013-05-11 | ZN10996:PA10 | URBAN | Other | 969801 | 1 | 244 | 244 | 0.00014865 | 6.0923e-05
2013-05-11 | ZN4545:PA32 | URBAN | Other | 969804 | 1 | 254.9333 | 254.9333 | 0.00015531 | 6.0923e-05
2013-05-11 | ZN36300:PA19 | URBAN | Other | 969807 | 1 | 224.8333 | 224.8333 | 0.00013698 | 6.0923e-05
2013-05-12 | ZN1287:PA6 | URBAN | Other | 969812 | 1 | 331.4167 | 331.4167 | 0.00020191 | 6.0923e-05
2013-05-12 | ZN965:PA38 | URBAN | Equipment Failure | 969813 | 47 | 975 | 45825 | 0.027918 | 0.0028634
2013-05-12 | ZN1285:PA19 | URBAN | Equipment Failure | 969819 | 1 | 236.8833 | 236.8833 | 0.00014432 | 6.0923e-05
2013-05-12 | ZN35600:PA25 | URBAN | Third Party Impacts | 969820 | 43 | 400 | 17200 | 0.010479 | 0.0026197
2013-05-12 | ZN9118:PA21 | URBAN | Other | 969821 | 1 | 178.9333 | 178.9333 | 0.00010901 | 6.0923e-05
2013-05-12 | ZN3472:PA17 | URBAN | Equipment Failure | 969825 | 1 | 547.8833 | 547.8833 | 0.00033379 | 6.0923e-05
2013-05-12 | ZN35500:PA27 | URBAN | Equipment Failure | 969826 | 1 | 352.7 | 352.7 | 0.00021488 | 6.0923e-05
2013-05-12 | ZN10995:PA2 | URBAN | Other | 969838 | 1 | 483.8167 | 483.8167 | 0.00029476 | 6.0923e-05
2013-05-12 | ZN195:PA9 | URBAN | Other | 969844 | 1 | 193.9333 | 193.9333 | 0.00011815 | 6.0923e-05
2013-05-12 | ZN1287:PA12 | URBAN | Equipment Failure | 969853 | 1 | 276.4 | 276.4 | 0.00016839 | 6.0923e-05
2013-05-12 | ZN10994:PA12 | URBAN | Equipment Failure | 969854 | 1 | 411.0833 | 411.0833 | 0.00025045 | 6.0923e-05
2013-05-12 | ZN690:PA28 | URBAN | Other | 969858 | 1 | 554.75 | 554.75 | 0.00033797 | 6.0923e-05
2013-05-12 | ZN690:PA28 | URBAN | Other | 969859 | 1 | 554.75 | 554.75 | 0.00033797 | 6.0923e-05
2013-05-12 | ZN10994:PA8 | URBAN | Other | 969863 | 1 | 386.3167 | 386.3167 | 0.00023536 | 6.0923e-05
2013-05-12 | ZN10994:PA8 | URBAN | Other | 969866 | 1 | 374.7333 | 374.7333 | 0.0002283 | 6.0923e-05
2013-05-12 | ZN9037:PA8 | URBAN | Other | 969869 | 1 | 355.1833 | 355.1833 | 0.00021639 | 6.0923e-05
2013-05-12 | ZN9037:PA8 | URBAN | Other | 969872 | 1 | 351.25 | 351.25 | 0.00021399 | 6.0923e-05
2013-05-12 | ZN15005:PA8 | URBAN | Other | 969874 | 1 | 338.25 | 338.25 | 0.00020607 | 6.0923e-05
2013-05-12 | ZN1193:PA21 | URBAN | Other | 969877 | 1 | 331.7 | 331.7 | 0.00020208 | 6.0923e-05
2013-05-12 | ZN129:PA5 | URBAN | Equipment Failure | 969881 | 1 | 147.2 | 147.2 | 8.9679e-05 | 6.0923e-05
2013-05-12 | ZN1287:PA11 | URBAN | Other | 969883 | 1 | 748.25 | 748.25 | 0.00045586 | 6.0923e-05
2013-05-12 | ZN72:PA26 | URBAN | Third Party Impacts | 969885 | 51 | 118.25 | 6030.75 | 0.0036741 | 0.0031071
2013-05-12 | ZN262:PA40 | URBAN | Other | 969890 | 1 | 183.5167 | 183.5167 | 0.0001118 | 6.0923e-05
2013-05-12 | ZN15009:PA9 | URBAN | Equipment Failure | 969891 | 23 | 2009.55 | 46219.65 | 0.028159 | 0.0014012
2013-05-12 | ZN690:PA14 | URBAN | Other | 969893 | 1 | 606.9833 | 606.9833 | 0.00036979 | 6.0923e-05
2013-05-12 | 243:80084 | SHORT RURAL | Equipment Failure | 969915 | 64 | 68.8333 | 4405.3333 | 0.0026839 | 0.0038991
2013-05-12 | ZN1285:PA24 | URBAN | Other | 969922 | 1 | 686.9333 | 686.9333 | 0.0004185 | 6.0923e-05
2013-05-12 | ZN3472:PA34 | URBAN | Other | 969941 | 1 | 391.85 | 391.85 | 0.00023873 | 6.0923e-05
2013-05-12 | ZN10995:PA1 | URBAN | Other | 969942 | 1 | 298.9833 | 298.9833 | 0.00018215 | 6.0923e-05
2013-05-12 | ZN1287:PA15 | URBAN | Other | 969945 | 1 | 494.7 | 494.7 | 0.00030139 | 6.0923e-05
2013-05-12 | ZN262:PA31 | URBAN | Equipment Failure | 969946 | 1 | 223.3833 | 223.3833 | 0.00013609 | 6.0923e-05
2013-05-12 | 220:8687 | URBAN | Other | 969947 | 1 | 167.3667 | 167.3667 | 0.00010197 | 6.0923e-05
2013-05-12 | ZN2835:PA30 | URBAN | Other | 969954 | 1 | 689.1833 | 689.1833 | 0.00041987 | 6.0923e-05
2013-05-12 | 220:8688 | URBAN | Other | 969955 | 1 | 69.75 | 69.75 | 4.2494e-05 | 6.0923e-05
2013-05-12 | ZN15012:PA6 | URBAN | Other | 969957 | 1 | 860.2 | 860.2 | 0.00052406 | 6.0923e-05
2013-05-12 | 507:80917 | URBAN | Other | 969959 | 1 | 107.6833 | 107.6833 | 6.5604e-05 | 6.0923e-05
2013-05-12 | ZN2602:PA18 | URBAN | Equipment Failure | 969962 | 1213 | 122 | 112598 | 0.068599 | 0.0739
2013-05-13 | 523:33503 | URBAN | Equipment Failure | 969963 | 1 | 101.9833 | 101.9833 | 6.2132e-05 | 6.0923e-05
2013-05-13 | ZN3472:PA21 | URBAN | Other | 969965 | 1 | 440.6 | 440.6 | 0.00026843 | 6.0923e-05
2013-05-13 | 502:48004 | URBAN | Equipment Failure | 969967 | 1 | 135.0167 | 135.0167 | 8.2257e-05 | 6.0923e-05
2013-05-13 | 507:80925 | SHORT RURAL | Equipment Failure | 969969 | 1 | 112.1 | 112.1 | 6.8295e-05 | 6.0923e-05
2013-05-13 | ZN180:PA28 | URBAN | Other | 969971 | 1 | 445.4167 | 445.4167 | 0.00027136 | 6.0923e-05
2013-05-13 | ZN3672:PA9 | URBAN | Other | 969974 | 1 | 230.4 | 230.4 | 0.00014037 | 6.0923e-05
2013-05-13 | ZN10990:PA11 | URBAN | Equipment Failure | 969983 | 1 | 160.5833 | 160.5833 | 9.7833e-05 | 6.0923e-05
2013-05-13 | ZN116:PA42 | URBAN | Other | 969986 | 1 | 224.1 | 224.1 | 0.00013653 | 6.0923e-05
2013-05-13 | ZN3425:PA43 | URBAN | Other | 969987 | 1 | 252.5 | 252.5 | 0.00015383 | 6.0923e-05
2013-05-13 | ZN874:PA18 | SHORT RURAL | Other | 969991 | 1 | 446.0333 | 446.0333 | 0.00027174 | 6.0923e-05
2013-05-13 | ZN72:PA17 | URBAN | Other | 969992 | 1 | 287.35 | 287.35 | 0.00017506 | 6.0923e-05
2013-05-13 | 213:33770 | URBAN | Other | 970001 | 33 | 537.35 | 17732.55 | 0.010803 | 0.0020105
2013-05-13 | 807:74180 | SHORT RURAL | Equipment Failure | 970022 | 1 | 316.5167 | 316.5167 | 0.00019283 | 6.0923e-05
2013-05-13 | ZN2602:PA41 | URBAN | Operational Error | 970034 | 1446 | 20 | 28920 | 0.017619 | 0.088095
2013-05-13 | ZN1285:PA18 | URBAN | Third Party Impacts | 970043 | 14 | 114 | 1596 | 0.00097234 | 0.00085293
2013-05-13 | 810:74050 | SHORT RURAL | Equipment Failure | 970052 | 1 | 464.2667 | 464.2667 | 0.00028285 | 6.0923e-05
2013-05-13 | 812:19065 | SHORT RURAL | Equipment Failure | 970069 | 1 | 51.7833 | 51.7833 | 3.1548e-05 | 6.0923e-05
2013-05-13 | ZN2835:PA23 | URBAN | Other | 970098 | 1 | 14.85 | 14.85 | 9.0471e-06 | 6.0923e-05
2013-05-13 | ZN2835:PA15 | URBAN | Other | 970129 | 1 | 251.75 | 251.75 | 0.00015337 | 6.0923e-05
2013-05-13 | ZN340:PA2 | URBAN | Third Party Impacts | 970144 | 39 | 329 | 10906 | 0.0066443 | 0.002376
2013-05-13 | ZN2835:PA31 | URBAN | Other | 970223 | 1 | 1241.4 | 1241.4 | 0.0007563 | 6.0923e-05
2013-05-13 | ZN72:PA25 | URBAN | Other | 970225 | 1 | 218.6167 | 218.6167 | 0.00013319 | 6.0923e-05
2013-05-13 | 515:35197 | LONG RURAL | Equipment Failure | 970227 | 1 | 109.7333 | 109.7333 | 6.6853e-05 | 6.0923e-05
2013-05-13 | ZN690:PA27 | URBAN | Equipment Failure | 970307 | 173 | 144 | 14326 | 0.0087279 | 0.01054
2013-05-13 | 503:48011 | SHORT RURAL | Other | 970342 | 1 | 375.2167 | 375.2167 | 0.00022859 | 6.0923e-05
2013-05-13 | 503:48012 | URBAN | Other | 970346 | 1 | 192.3333 | 192.3333 | 0.00011718 | 6.0923e-05
2013-05-13 | 812:19071 | SHORT RURAL | Other | 970403 | 1 | 121.1667 | 121.1667 | 7.3819e-05 | 6.0923e-05
2013-05-13 | ZN9700:PA11 | URBAN | Vegetation | 970405 | 1 | 129.1 | 129.1 | 7.8652e-05 | 6.0923e-05
2013-05-13 | ZN9700:PA15 | URBAN | Vegetation | 970421 | 1 | 209.4667 | 209.4667 | 0.00012761 | 6.0923e-05
2013-05-14 | 503:48016 | URBAN | Other | 970428 | 1 | 358.9 | 358.9 | 0.00021863 | 6.0918e-05
2013-05-14 | 503:48016 | URBAN | Other | 970430 | 1 | 146.7833 | 146.7833 | 8.9417e-05 | 6.0918e-05
2013-05-14 | 507:80926 | URBAN | Equipment Failure | 970434 | 1 | 244.2833 | 244.2833 | 0.00014881 | 6.0918e-05
2013-05-14 | ZN9550:PA6 | URBAN | Other | 970439 | 1 | 195.25 | 195.25 | 0.00011894 | 6.0918e-05
2013-05-14 | ZN2310:PA3 | URBAN | Other | 970448 | 1 | 163.0167 | 163.0167 | 9.9306e-05 | 6.0918e-05
2013-05-14 | 507:80926 | URBAN | Other | 970451 | 1 | 191.1167 | 191.1167 | 0.00011642 | 6.0918e-05
2013-05-14 | 523:33508 | SHORT RURAL | Equipment Failure | 970453 | 1 | 59.6833 | 59.6833 | 3.6358e-05 | 6.0918e-05
2013-05-14 | ZN2473:PA26 | URBAN | Other | 970456 | 1 | 907.1833 | 907.1833 | 0.00055264 | 6.0918e-05
2013-05-14 | ZN12650:PA13 | SHORT RURAL | Vegetation | 970458 | 1733 | 178 | 102804 | 0.062626 | 0.10557
2013-05-14 | 507:80923 | SHORT RURAL | Equipment Failure | 970468 | 6 | 392.3167 | 2353.9 | 0.0014339 | 0.00036551
2013-05-14 | 229:34983 | SHORT RURAL | Equipment Failure | 970472 | 1 | 377.0833 | 377.0833 | 0.00022971 | 6.0918e-05
2013-05-14 | ZN1287:PA23 | URBAN | Equipment Failure | 970477 | 1 | 417.2333 | 417.2333 | 0.00025417 | 6.0918e-05
2013-05-14 | 220:8687 | URBAN | Other | 970491 | 1 | 95.9667 | 95.9667 | 5.8461e-05 | 6.0918e-05
2013-05-14 | 224:80340 | SHORT RURAL | Other | 970504 | 1 | 121.7167 | 121.7167 | 7.4147e-05 | 6.0918e-05
2013-05-14 | ZN3922:PA7 | URBAN | Other | 970517 | 1 | 121.2667 | 121.2667 | 7.3873e-05 | 6.0918e-05
2013-05-14 | 224:80332 | URBAN | Other | 970541 | 1 | 259.9667 | 259.9667 | 0.00015837 | 6.0918e-05
2013-05-13 | ZN12570:PA22 | URBAN | Equipment Failure | 970546 | 30 | 55 | 1650 | 0.0010052 | 0.0018277
2013-05-14 | 240:34852 | URBAN | Other | 970547 | 1 | 80 | 80 | 4.8734e-05 | 6.0918e-05
2013-05-14 | ZN2310:PA17 | URBAN | Third Party Impacts | 970558 | 1 | 663.5333 | 663.5333 | 0.00040421 | 6.0918e-05
2013-05-14 | ZN12610:PA13 | URBAN | Other | 970560 | 1 | 91.3333 | 91.3333 | 5.5638e-05 | 6.0918e-05
2013-05-14 | 523:33501 | SHORT RURAL | Equipment Failure | 970575 | 1 | 67.6667 | 67.6667 | 4.1221e-05 | 6.0918e-05
2013-05-14 | 258:80791 | URBAN | Other | 970647 | 1 | 21.4667 | 21.4667 | 1.3077e-05 | 6.0918e-05
2013-05-14 | 812:19072 | SHORT RURAL | Other | 970669 | 1 | 45 | 45 | 2.7413e-05 | 6.0918e-05
2013-05-14 | ZN180:PA41 | URBAN | Other | 970671 | 1 | 183.1333 | 183.1333 | 0.00011156 | 6.0918e-05
2013-05-14 | ZN1287:PA4 | URBAN | Other | 970696 | 1 | 84.5333 | 84.5333 | 5.1496e-05 | 6.0918e-05
2013-05-14 | ZN3154:PA23 | URBAN | Equipment Failure | 970700 | 35 | 840 | 29400 | 0.01791 | 0.0021321
2013-05-14 | ZN1287:PA6 | URBAN | Third Party Impacts | 970737 | 32 | 331.7833 | 10617.0667 | 0.0064677 | 0.0019494
2013-05-14 | ZN847:PA23 | URBAN | Third Party Impacts | 970775 | 1 | 301.55 | 301.55 | 0.0001837 | 6.0918e-05
2013-05-14 | ZN262:PA16 | URBAN | Equipment Failure | 970808 | 1 | 211.7333 | 211.7333 | 0.00012898 | 6.0918e-05
2013-05-14 | ZN4545:PA24 | URBAN | Equipment Failure | 970821 | 48 | 113.3333 | 5440 | 0.0033139 | 0.0029241
2013-05-14 | 509:48039 | LONG RURAL | Other | 970826 | 1 | 269.3167 | 269.3167 | 0.00016406 | 6.0918e-05
2013-05-14 | ZN690:PA36 | URBAN | Other | 970865 | 1 | 653.4333 | 653.4333 | 0.00039806 | 6.0918e-05
2013-05-15 | 227:13019 | SHORT RURAL | Other | 970871 | 1 | 87.5333 | 87.5333 | 5.3325e-05 | 6.0919e-05
2013-05-15 | ZN12630:PA3 | SHORT RURAL | Equipment Failure | 970874 | 8 | 380.5833 | 3044.6667 | 0.0018548 | 0.00048735
2013-05-15 | ZN12660:PA10 | SHORT RURAL | Other | 970894 | 1 | 134.1833 | 134.1833 | 8.1743e-05 | 6.0919e-05
2013-05-15 | ZN167:PA12 | URBAN | Third Party Impacts | 970901 | 1 | 161.75 | 161.75 | 9.8537e-05 | 6.0919e-05
2013-05-15 | ZN10993:PA5 | URBAN | Other | 970915 | 1 | 173.55 | 173.55 | 0.00010573 | 6.0919e-05
2013-05-15 | ZN2602:PA31 | URBAN | Vegetation | 970960 | 73 | 481 | 29638 | 0.018055 | 0.0044471
2013-05-15 | ZN2602:PA34 | URBAN | Vegetation | 970960 | 114 | 481 | 41724 | 0.025418 | 0.0069448
2013-05-15 | ZN2602:PA41 | URBAN | Vegetation | 970960 | 30 | 481 | 14430 | 0.0087906 | 0.0018276
2013-05-15 | ZN10999:PA24 | URBAN | Equipment Failure | 970961 | 1 | 84.7667 | 84.7667 | 5.1639e-05 | 6.0919e-05
2013-05-15 | ZN35500:PA27 | URBAN | Other | 970991 | 1 | 212.15 | 212.15 | 0.00012924 | 6.0919e-05
2013-05-15 | 516:48066 | SHORT RURAL | Other | 971055 | 1 | 42.35 | 42.35 | 2.5799e-05 | 6.0919e-05
2013-05-15 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 971058 | 1 | 60 | 60 | 3.6552e-05 | 6.0919e-05
2013-05-15 | ZN1068:PA18 | URBAN | Other | 971101 | 96 | 130.9333 | 12569.6 | 0.0076573 | 0.0058482
2013-05-15 | 264:81244 | URBAN | Other | 971137 | 1 | 102.7167 | 102.7167 | 6.2574e-05 | 6.0919e-05
2013-05-15 | ZN12570:PA25 | SHORT RURAL | Equipment Failure | 971149 | 1 | 369.3 | 369.3 | 0.00022497 | 6.0919e-05
2013-05-15 | ZN10991:PA12 | URBAN | Equipment Failure | 971154 | 1 | 333.3167 | 333.3167 | 0.00020305 | 6.0919e-05
2013-05-15 | 512:48049 | SHORT RURAL | Other | 971170 | 1 | 170.0333 | 170.0333 | 0.00010358 | 6.0919e-05
2013-05-15 | 510:48164 | SHORT RURAL | Other | 971197 | 2 | 336 | 672 | 0.00040938 | 0.00012184
2013-05-15 | ZN269:PA9 | URBAN | Equipment Failure | 971222 | 233 | 36 | 8368.95 | 0.0050983 | 0.014194
2013-05-15 | ZN15001:PA18 | URBAN | Equipment Failure | 971225 | 799 | 198 | 62960 | 0.038355 | 0.048674
2013-05-15 | ZN15011:PA6 | URBAN | Equipment Failure | 971225 | 534 | 198 | 49662 | 0.030254 | 0.032531
2013-05-15 | ZN2835:PA19 | URBAN | Other | 971243 | 1 | 248.7833 | 248.7833 | 0.00015156 | 6.0919e-05
2013-05-15 | ZN180:PA43 | URBAN | Other | 971254 | 1 | 351.4333 | 351.4333 | 0.00021409 | 6.0919e-05
2013-05-15 | ZN262:PA6 | URBAN | Third Party Impacts | 971260 | 64 | 496 | 31744 | 0.019338 | 0.0038988
2013-05-16 | 507:80917 | URBAN | Other | 971264 | 1 | 115.3167 | 115.3167 | 7.0251e-05 | 6.092e-05
2013-05-16 | ZN4545:PA21 | URBAN | Equipment Failure | 971268 | 1 | 223.8833 | 223.8833 | 0.00013639 | 6.092e-05
2013-05-16 | ZN10994:PA7 | URBAN | Other | 971272 | 1 | 179.7667 | 179.7667 | 0.00010951 | 6.092e-05
2013-05-16 | ZN15008:PA9 | URBAN | Other | 971294 | 1 | 138.2333 | 138.2333 | 8.4212e-05 | 6.092e-05
2013-05-16 | ZN180:PA21 | URBAN | Other | 971336 | 1 | 50.7167 | 50.7167 | 3.0897e-05 | 6.092e-05
2013-05-16 | 221:11899 | URBAN | Vegetation | 971344 | 1 | 109.2333 | 109.2333 | 6.6545e-05 | 6.092e-05
2013-05-16 | 523:33501 | SHORT RURAL | Equipment Failure | 971427 | 12 | 17.3833 | 208.6 | 0.00012708 | 0.00073104
2013-05-16 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 971574 | 1 | 45.2833 | 45.2833 | 2.7587e-05 | 6.092e-05
2013-05-16 | 813:89063 | SHORT RURAL | Equipment Failure | 971590 | 25 | 119.7667 | 2994.1667 | 0.001824 | 0.001523
2013-05-16 | ZN12580:PA14 | URBAN | Other | 971596 | 1 | 184.2 | 184.2 | 0.00011221 | 6.092e-05
2013-05-16 | ZN2310:PA26 | URBAN | Equipment Failure | 971598 | 65 | 97.3667 | 6328.8333 | 0.0038555 | 0.0039598
2013-05-16 | 503:48011 | SHORT RURAL | Other | 971604 | 1 | 141.5167 | 141.5167 | 8.6212e-05 | 6.092e-05
2013-05-16 | 227:13015 | SHORT RURAL | Other | 971616 | 10 | 183.8833 | 1838.8333 | 0.0011202 | 0.0006092
2013-05-17 | ZN14891:PA20 | SHORT RURAL | Other | 971622 | 515 | 76 | 39140 | 0.023845 | 0.031374
2013-05-17 | ZN12690:PA7 | SHORT RURAL | Equipment Failure | 971625 | 25 | 179.0833 | 4477.0833 | 0.0027275 | 0.001523
2013-05-17 | ZN80:PA28 | URBAN | Other | 971675 | 1 | 358.6 | 358.6 | 0.00021846 | 6.0921e-05
2013-05-17 | 210:8676 | URBAN | Other | 971704 | 1 | 54 | 54 | 3.2897e-05 | 6.0921e-05
2013-05-17 | ZN9245:PA10 | URBAN | Equipment Failure | 971736 | 1 | 132.3667 | 132.3667 | 8.0639e-05 | 6.0921e-05
2013-05-17 | 225:33670 | SHORT RURAL | Other | 971763 | 2 | 76 | 152 | 9.26e-05 | 0.00012184
2013-05-17 | ZN965:PA4 | URBAN | Vegetation | 971778 | 777 | 73 | 53001 | 0.032289 | 0.047336
2013-05-17 | 813:89055 | SHORT RURAL | Other | 971788 | 8 | 126 | 1008 | 0.00061409 | 0.00048737
2013-05-17 | ZN35800:PA1 | URBAN | Other | 971807 | 56 | 125.9667 | 7054.1333 | 0.0042975 | 0.0034116
2013-05-17 | 807:74180 | SHORT RURAL | Equipment Failure | 971828 | 1 | 119.2167 | 119.2167 | 7.2628e-05 | 6.0921e-05
2013-05-17 | 242:81539 | URBAN | Vegetation | 971855 | 1984 | 97 | 192448 | 0.11724 | 0.12087
2013-05-17 | 507:80925 | SHORT RURAL | Other | 971873 | 70 | 101.1667 | 7081.6667 | 0.0043142 | 0.0042645
2013-05-17 | ZN14892:PA8 | URBAN | Other | 971904 | 1 | 117.9833 | 117.9833 | 7.1877e-05 | 6.0921e-05
2013-05-17 | 242:81539 | URBAN | Other | 971954 | 1 | 157.9833 | 157.9833 | 9.6245e-05 | 6.0921e-05
2013-05-17 | ZN2635:PA17 | URBAN | Equipment Failure | 971961 | 1 | 156 | 156 | 9.5037e-05 | 6.0921e-05
2013-05-17 | ZN15011:PA10 | URBAN | Other | 971970 | 34 | 67.8 | 2305.2 | 0.0014044 | 0.0020713
2013-05-17 | ZN10994:PA13 | URBAN | Equipment Failure | 971975 | 1 | 195.9667 | 195.9667 | 0.00011939 | 6.0921e-05
2013-05-17 | 520:48172 | SHORT RURAL | Other | 971979 | 3 | 66 | 198 | 0.00012062 | 0.00018276
2013-05-17 | ZN342:PA15 | URBAN | Equipment Failure | 971983 | 81 | 608 | 49248 | 0.030002 | 0.0049346
2013-05-17 | 523:33501 | SHORT RURAL | Other | 971985 | 1 | 698.4167 | 698.4167 | 0.00042548 | 6.0921e-05
2013-05-18 | ZN15012:PA4 | URBAN | Other | 971989 | 1 | 381.8333 | 381.8333 | 0.00023262 | 6.0921e-05
2013-05-18 | 230:81440 | URBAN | Other | 971990 | 1 | 205.45 | 205.45 | 0.00012516 | 6.0921e-05
2013-05-18 | ZN36300:PA5 | URBAN | Other | 971996 | 1 | 325.25 | 325.25 | 0.00019815 | 6.0921e-05
2013-05-18 | 203:8086 | URBAN | Other | 972008 | 1 | 110.95 | 110.95 | 6.7592e-05 | 6.0921e-05
2013-05-18 | ZN12570:PA40 | SHORT RURAL | Third Party Impacts | 972068 | 29 | 71 | 2059 | 0.0012544 | 0.0017667
2013-05-18 | 812:19066 | SHORT RURAL | Third Party Impacts | 972071 | 3 | 64 | 192 | 0.00011697 | 0.00018276
2013-05-18 | ZN1285:PA24 | URBAN | Equipment Failure | 972073 | 1 | 285.8667 | 285.8667 | 0.00017415 | 6.0921e-05
2013-05-18 | ZN15009:PA1 | URBAN | Equipment Failure | 972080 | 38 | 209 | 7942 | 0.0048384 | 0.002315
2013-05-18 | ZN10996:PA10 | URBAN | Equipment Failure | 972089 | 1 | 1578.6167 | 1578.6167 | 0.00096171 | 6.0921e-05
2013-05-18 | ZN12640:PA13 | SHORT RURAL | Equipment Failure | 972095 | 2 | 66 | 132 | 8.0416e-05 | 0.00012184
2013-05-18 | ZN12640:PA16 | URBAN | Equipment Failure | 972095 | 123 | 66 | 8019.6 | 0.0048856 | 0.0074933
2013-05-19 | ZN9550:PA1 | URBAN | Equipment Failure | 972113 | 121 | 72.0167 | 8714.0167 | 0.0053087 | 0.0073715
2013-05-19 | 511:29877 | SHORT RURAL | Other | 972114 | 40 | 186 | 7440 | 0.0045325 | 0.0024368
2013-05-19 | 813:89055 | SHORT RURAL | Animals | 972124 | 2 | 71 | 142 | 8.6508e-05 | 0.00012184
2013-05-19 | ZN9550:PA1 | URBAN | Equipment Failure | 972153 | 121 | 256.1 | 30988.1 | 0.018878 | 0.0073715
2013-05-19 | ZN9035:PA4 | URBAN | Equipment Failure | 972155 | 1 | 395.85 | 395.85 | 0.00024116 | 6.0921e-05
2013-05-19 | ZN15002:PA6 | URBAN | Vegetation | 972168 | 1 | 160.9667 | 160.9667 | 9.8063e-05 | 6.0921e-05
2013-05-19 | 507:80932 | SHORT RURAL | Equipment Failure | 972200 | 2 | 130.2167 | 260.4333 | 0.00015866 | 0.00012184
2013-05-19 | 801:74122 | URBAN | Equipment Failure | 972212 | 71 | 50 | 3550 | 0.0021627 | 0.0043254
2013-05-19 | ZN1290:PA10 | URBAN | Equipment Failure | 972222 | 34 | 114 | 3676 | 0.0022395 | 0.0020713
2013-05-20 | ZN14143:PA21 | URBAN | Animals | 972228 | 36 | 79 | 2481 | 0.0015115 | 0.0021932
2013-05-20 | ZN2196:PA18 | URBAN | Equipment Failure | 972233 | 39 | 124.4667 | 4854.2 | 0.0029572 | 0.0023759
2013-05-15 | ZN167:PA12 | URBAN | Third Party Impacts | 972281 | 1 | 15 | 15 | 9.1379e-06 | 6.0919e-05
2013-05-20 | 238:34147 | URBAN | Other | 972308 | 1 | 111 | 111 | 6.7622e-05 | 6.0921e-05
2013-05-17 | 504:48033 | SHORT RURAL | Other | 972317 | 1 | 244 | 244 | 0.00014865 | 6.0921e-05
2013-05-19 | 511:29877 | SHORT RURAL | Other | 972334 | 40 | 30 | 1200 | 0.00073105 | 0.0024368
2013-05-20 | 206:34440 | URBAN | Equipment Failure | 972342 | 1 | 113.5833 | 113.5833 | 6.9196e-05 | 6.0921e-05
2013-05-17 | 512:48049 | SHORT RURAL | Equipment Failure | 972352 | 11 | 25 | 275 | 0.00016753 | 0.00067013
2013-05-20 | ZN3425:PA43 | URBAN | Equipment Failure | 972357 | 1 | 211.1833 | 211.1833 | 0.00012866 | 6.0921e-05
2013-05-20 | ZN35800:PA18 | URBAN | Vegetation | 972386 | 1 | 185.4667 | 185.4667 | 0.00011299 | 6.0921e-05
2013-05-20 | 526:34636 | SHORT RURAL | Equipment Failure | 972676 | 3 | 196 | 588 | 0.00035822 | 0.00018276
2013-05-20 | 501:48125 | URBAN | Other | 972684 | 1 | 212.2833 | 212.2833 | 0.00012933 | 6.0921e-05
2013-05-20 | ZN9037:PA2 | URBAN | Animals | 972687 | 109 | 53.7333 | 5856.9333 | 0.0035681 | 0.0066404
2013-05-20 | ZN4545:PA24 | URBAN | Animals | 972693 | 559 | 35 | 19565 | 0.011919 | 0.034055
2013-05-21 | 520:48172 | SHORT RURAL | Other | 972706 | 1 | 274.3333 | 274.3333 | 0.00016713 | 6.0922e-05
2013-05-21 | 520:48172 | SHORT RURAL | Other | 972710 | 1 | 111.2667 | 111.2667 | 6.7786e-05 | 6.0922e-05
2013-05-21 | ZN12650:PA13 | SHORT RURAL | Other | 972760 | 1 | 44 | 44 | 2.6806e-05 | 6.0922e-05
2013-05-21 | ZN9037:PA10 | URBAN | Equipment Failure | 972765 | 1619 | 116 | 146228 | 0.089086 | 0.098634
2013-05-21 | ZN187:PA17 | URBAN | Third Party Impacts | 972769 | 1483 | 76 | 106732 | 0.065024 | 0.090348
2013-05-09 | ZN10990:PA8 | URBAN | Other | 972774 | 4 | 90 | 360 | 0.00021932 | 0.00024369
2013-05-21 | 812:19066 | SHORT RURAL | Equipment Failure | 972787 | 1 | 253.85 | 253.85 | 0.00015465 | 6.0922e-05
2013-05-21 | ZN12580:PA7 | URBAN | Equipment Failure | 972792 | 170 | 110 | 18300 | 0.011149 | 0.010357
2013-05-21 | ZN7900:PA7 | URBAN | Equipment Failure | 972816 | 1 | 760.65 | 760.65 | 0.00046341 | 6.0922e-05
2013-05-21 | ZN13000:PA10 | URBAN | Equipment Failure | 972858 | 3 | 164 | 492 | 0.00029974 | 0.00018277
2013-05-21 | 223:14394 | URBAN | Vegetation | 972923 | 1 | 197.15 | 197.15 | 0.00012011 | 6.0922e-05
2013-05-19 | ZN14891:PA10 | SHORT RURAL | Operational Error | 973004 | 252 | 2 | 504 | 0.00030704 | 0.015352
2013-05-21 | 206:34441 | URBAN | Other | 973005 | 1 | 49.4 | 49.4 | 3.0096e-05 | 6.0922e-05
2013-05-21 | 812:19071 | SHORT RURAL | Other | 973055 | 1 | 66.55 | 66.55 | 4.0544e-05 | 6.0922e-05
2013-05-21 | ZN9037:PA10 | URBAN | Equipment Failure | 973060 | 1 | 292.0333 | 292.0333 | 0.00017791 | 6.0922e-05
2013-05-21 | ZN9037:PA10 | URBAN | Equipment Failure | 973078 | 1 | 252.9333 | 252.9333 | 0.00015409 | 6.0922e-05
2013-05-21 | 235:8684 | SHORT RURAL | Third Party Impacts | 973102 | 117 | 487 | 9018 | 0.005494 | 0.0071279
2013-05-21 | ZN35600:PA3 | URBAN | Third Party Impacts | 973104 | 44 | 61.6 | 2710.4 | 0.0016512 | 0.0026806
2013-05-21 | ZN847:PA28 | URBAN | Equipment Failure | 973129 | 33 | 112.8 | 3722.4 | 0.0022678 | 0.0020104
2013-05-21 | 512:48049 | SHORT RURAL | Equipment Failure | 973146 | 1 | 283.9333 | 283.9333 | 0.00017298 | 6.0922e-05
2013-05-21 | ZN10990:PA2 | URBAN | Other | 973156 | 70 | 50.35 | 3524.5 | 0.0021472 | 0.0042646
2013-05-22 | ZN9118:PA15 | URBAN | Third Party Impacts | 973183 | 1 | 73.5167 | 73.5167 | 4.4789e-05 | 6.0923e-05
2013-05-20 | ZN2310:PA33 | URBAN | Vegetation | 973261 | 74 | 32 | 2368 | 0.0014426 | 0.0045082
2013-05-22 | ZN15005:PA6 | URBAN | Other | 973275 | 1 | 108.75 | 108.75 | 6.6254e-05 | 6.0923e-05
2013-05-22 | 223:14393 | URBAN | Vegetation | 973302 | 1 | 388.8667 | 388.8667 | 0.00023691 | 6.0923e-05
2013-05-22 | ZN12570:PA35 | URBAN | Other | 973316 | 1 | 528.2667 | 528.2667 | 0.00032184 | 6.0923e-05
2013-05-22 | 243:80083 | SHORT RURAL | Other | 973324 | 1 | 218.9667 | 218.9667 | 0.0001334 | 6.0923e-05
2013-05-22 | ZN180:PA23 | URBAN | Third Party Impacts | 973335 | 1 | 72.6833 | 72.6833 | 4.4281e-05 | 6.0923e-05
2013-05-22 | ZN10999:PA11 | URBAN | Other | 973362 | 1 | 45.9 | 45.9 | 2.7964e-05 | 6.0923e-05
2013-05-22 | ZN10999:PA11 | URBAN | Other | 973368 | 1 | 57.8 | 57.8 | 3.5214e-05 | 6.0923e-05
2013-05-22 | 512:48049 | SHORT RURAL | Other | 973384 | 1 | 124.4 | 124.4 | 7.5789e-05 | 6.0923e-05
2013-05-22 | ZN690:PA11 | URBAN | Other | 973426 | 1 | 102.3667 | 102.3667 | 6.2365e-05 | 6.0923e-05
2013-05-22 | ZN4545:PA11 | URBAN | Equipment Failure | 973470 | 1 | 140.8 | 140.8 | 8.578e-05 | 6.0923e-05
2013-05-22 | ZN2310:PA22 | URBAN | Other | 973495 | 1 | 557.75 | 557.75 | 0.0003398 | 6.0923e-05
2013-05-22 | ZN3922:PA7 | URBAN | Other | 973503 | 1 | 311.85 | 311.85 | 0.00018999 | 6.0923e-05
2013-05-22 | ZN3472:PA28 | URBAN | Other | 973512 | 1 | 216.3833 | 216.3833 | 0.00013183 | 6.0923e-05
2013-05-22 | ZN2568:PA29 | URBAN | Other | 973517 | 1 | 135.1667 | 135.1667 | 8.2348e-05 | 6.0923e-05
2013-05-22 | ZN2568:PA29 | URBAN | Other | 973520 | 1 | 130.85 | 130.85 | 7.9718e-05 | 6.0923e-05
2013-05-22 | ZN2568:PA29 | URBAN | Other | 973522 | 1 | 129.5167 | 129.5167 | 7.8906e-05 | 6.0923e-05
2013-05-22 | ZN2835:PA32 | SHORT RURAL | Other | 973524 | 1 | 193.45 | 193.45 | 0.00011786 | 6.0923e-05
2013-05-22 | ZN1164:PA10 | URBAN | Other | 973526 | 1 | 238 | 238 | 0.000145 | 6.0923e-05
2013-05-22 | ZN35500:PA24 | URBAN | Equipment Failure | 973529 | 1 | 327.1167 | 327.1167 | 0.00019929 | 6.0923e-05
2013-05-22 | ZN1648:PA10 | URBAN | Other | 973531 | 1 | 126.8333 | 126.8333 | 7.7271e-05 | 6.0923e-05
2013-05-22 | ZN129:PA18 | URBAN | Equipment Failure | 973534 | 1 | 353.7167 | 353.7167 | 0.0002155 | 6.0923e-05
2013-05-22 | ZN690:PA34 | URBAN | Other | 973535 | 1 | 697.5 | 697.5 | 0.00042494 | 6.0923e-05
2013-05-22 | 523:33503 | URBAN | Other | 973541 | 1 | 262.3833 | 262.3833 | 0.00015985 | 6.0923e-05
2013-05-22 | ZN1648:PA11 | URBAN | Other | 973543 | 1 | 521.2167 | 521.2167 | 0.00031754 | 6.0923e-05
2013-05-22 | ZN2635:PA17 | URBAN | Other | 973544 | 1 | 398.2167 | 398.2167 | 0.00024261 | 6.0923e-05
2013-05-22 | ZN10999:PA4 | URBAN | Equipment Failure | 973564 | 1 | 1038.75 | 1038.75 | 0.00063284 | 6.0923e-05
2013-05-22 | 812:19072 | SHORT RURAL | Equipment Failure | 973565 | 119 | 498 | 23658 | 0.014413 | 0.0072499
2013-05-22 | 503:48012 | URBAN | Other | 973567 | 1 | 150.65 | 150.65 | 9.1781e-05 | 6.0923e-05
2013-05-22 | 504:48033 | SHORT RURAL | Other | 973569 | 1 | 77.5333 | 77.5333 | 4.7236e-05 | 6.0923e-05
2013-05-22 | ZN9252:PA4 | URBAN | Vegetation | 973589 | 1284 | 62 | 79608 | 0.0485 | 0.078226
2013-05-22 | ZN12600:PA3 | URBAN | Equipment Failure | 973599 | 92 | 64.0333 | 5891.0667 | 0.003589 | 0.0056049
2013-05-22 | ZN1287:PA15 | URBAN | Other | 973600 | 1 | 498.7167 | 498.7167 | 0.00030383 | 6.0923e-05
2013-05-22 | 507:80922 | SHORT RURAL | Other | 973609 | 88 | 78.9333 | 6946.1333 | 0.0042318 | 0.0053613
2013-05-22 | ZN1287:PA11 | URBAN | Other | 973622 | 63 | 804.6833 | 50695.05 | 0.030885 | 0.0038382
2013-05-22 | ZN12570:PA39 | URBAN | Other | 973624 | 57 | 187.7333 | 10700.8 | 0.0065193 | 0.0034726
2013-05-22 | ZN3922:PA13 | URBAN | Equipment Failure | 973634 | 172 | 104 | 17844 | 0.010871 | 0.010479
2013-05-22 | ZN3922:PA17 | SHORT RURAL | Equipment Failure | 973634 | 78 | 104 | 7254 | 0.0044194 | 0.004752
2013-05-22 | ZN3922:PA2 | SHORT RURAL | Equipment Failure | 973634 | 78 | 104 | 7254 | 0.0044194 | 0.004752
2013-05-22 | ZN3922:PA29 | URBAN | Equipment Failure | 973634 | 2865 | 104 | 272968 | 0.1663 | 0.17455
2013-05-22 | ZN3922:PA5 | URBAN | Equipment Failure | 973634 | 98 | 104 | 9114 | 0.0055526 | 0.0059705
2013-05-23 | ZN10999:PA16 | URBAN | Other | 973650 | 52 | 96 | 4992 | 0.0030413 | 0.003168
2013-05-22 | ZN3472:PA33 | URBAN | Other | 973654 | 1 | 310.8 | 310.8 | 0.00018935 | 6.0923e-05
2013-05-23 | 231:8415 | SHORT RURAL | Equipment Failure | 973657 | 816 | 369 | 171146 | 0.10427 | 0.049714
2013-05-23 | ZN12570:PA29 | SHORT RURAL | Other | 973659 | 772 | 80 | 61305 | 0.037349 | 0.047033
2013-05-23 | ZN15004:PA3 | URBAN | Vegetation | 973660 | 1 | 407.65 | 407.65 | 0.00024836 | 6.0924e-05
2013-05-23 | ZN3155:PA19 | URBAN | Equipment Failure | 973662 | 1 | 304.75 | 304.75 | 0.00018567 | 6.0924e-05
2013-05-23 | 503:48011 | SHORT RURAL | Other | 973663 | 1 | 202.2 | 202.2 | 0.00012319 | 6.0924e-05
2013-05-23 | 801:74123 | SHORT RURAL | Equipment Failure | 973665 | 1 | 219.0667 | 219.0667 | 0.00013346 | 6.0924e-05
2013-05-23 | 217:33611 | URBAN | Other | 973677 | 1 | 424.4333 | 424.4333 | 0.00025858 | 6.0924e-05
2013-05-22 | 264:81244 | URBAN | Third Party Impacts | 973691 | 3 | 20 | 60 | 3.6554e-05 | 0.00018277
2013-05-23 | 221:11899 | URBAN | Equipment Failure | 973721 | 1 | 128.3333 | 128.3333 | 7.8186e-05 | 6.0924e-05
2013-05-23 | 230:81440 | URBAN | Equipment Failure | 973724 | 1 | 232.2333 | 232.2333 | 0.00014149 | 6.0924e-05
2013-05-22 | ZN2473:PA32 | URBAN | Other | 973762 | 36 | 2 | 72 | 4.3865e-05 | 0.0021932
2013-05-23 | ZN9245:PA13 | URBAN | Other | 973782 | 1 | 152.2833 | 152.2833 | 9.2777e-05 | 6.0924e-05
2013-05-23 | ZN12650:PA12 | URBAN | Vegetation | 973785 | 36 | 240 | 8640 | 0.0052638 | 0.0021933
2013-05-23 | ZN690:PA4 | URBAN | Other | 973804 | 1 | 293.5 | 293.5 | 0.00017881 | 6.0924e-05
2013-05-23 | ZN9252:PA2 | URBAN | Vegetation | 973823 | 1 | 67.8333 | 67.8333 | 4.1327e-05 | 6.0924e-05
2013-05-23 | ZN269:PA3 | URBAN | Vegetation | 973857 | 1 | 559.9333 | 559.9333 | 0.00034113 | 6.0924e-05
2013-05-23 | 507:80920 | SHORT RURAL | Other | 973869 | 1 | 123.9833 | 123.9833 | 7.5535e-05 | 6.0924e-05
2013-05-23 | 515:35192 | SHORT RURAL | Other | 973871 | 3 | 10 | 30 | 1.8277e-05 | 0.00018277
2013-05-23 | ZN7900:PA12 | URBAN | Other | 973883 | 1 | 170.8167 | 170.8167 | 0.00010407 | 6.0924e-05
2013-05-23 | ZN12640:PA2 | URBAN | Other | 973889 | 1 | 383.5833 | 383.5833 | 0.00023369 | 6.0924e-05
2013-05-23 | ZN195:PA29 | URBAN | Other | 973896 | 1 | 155.65 | 155.65 | 9.4828e-05 | 6.0924e-05
2013-05-23 | ZN167:PA12 | URBAN | Equipment Failure | 973920 | 1 | 212.4333 | 212.4333 | 0.00012942 | 6.0924e-05
2013-05-23 | ZN15011:PA2 | URBAN | Animals | 973929 | 1599 | 33 | 51729 | 0.031515 | 0.097417
2013-05-23 | 813:89062 | SHORT RURAL | Equipment Failure | 973978 | 1 | 277.0167 | 277.0167 | 0.00016877 | 6.0924e-05
2013-05-23 | 813:89061 | LONG RURAL | Equipment Failure | 974003 | 93 | 377 | 35061 | 0.021361 | 0.0056659
2013-05-23 | ZN15004:PA3 | URBAN | Vegetation | 974027 | 60 | 7 | 420 | 0.00025588 | 0.0036554
2013-05-23 | 223:14393 | URBAN | Equipment Failure | 974028 | 1 | 108.5167 | 108.5167 | 6.6113e-05 | 6.0924e-05
2013-05-23 | 235:2120 | SHORT RURAL | Operational Error | 974042 | 1 | 48 | 48 | 2.9243e-05 | 6.0924e-05
2013-05-23 | 223:14393 | URBAN | Equipment Failure | 974051 | 1 | 30.45 | 30.45 | 1.8551e-05 | 6.0924e-05
2013-05-23 | ZN15012:PA4 | URBAN | Other | 974075 | 1 | 190.6667 | 190.6667 | 0.00011616 | 6.0924e-05
2013-05-23 | 223:14393 | URBAN | Equipment Failure | 974127 | 114 | 37 | 4218 | 0.0025698 | 0.0069453
2013-05-23 | ZN14891:PA9 | URBAN | Other | 974128 | 1 | 175.7333 | 175.7333 | 0.00010706 | 6.0924e-05
2013-05-23 | ZN690:PA35 | URBAN | Third Party Impacts | 974144 | 1 | 276.4167 | 276.4167 | 0.0001684 | 6.0924e-05
2013-05-23 | 230:81434 | URBAN | Other | 974148 | 85 | 109.1833 | 9280.5833 | 0.0056541 | 0.0051785
2013-05-23 | ZN15009:PA11 | URBAN | Equipment Failure | 974155 | 1 | 385.7167 | 385.7167 | 0.00023499 | 6.0924e-05
2013-05-23 | ZN269:PA19 | URBAN | Equipment Failure | 974159 | 1 | 2403.0667 | 2403.0667 | 0.001464 | 6.0924e-05
2013-05-23 | 258:80790 | URBAN | Other | 974160 | 1 | 180.85 | 180.85 | 0.00011018 | 6.0924e-05
2013-05-23 | ZN12570:PA25 | SHORT RURAL | Other | 974169 | 1 | 635.0833 | 635.0833 | 0.00038692 | 6.0924e-05
2013-05-23 | ZN15004:PA9 | URBAN | Equipment Failure | 974177 | 43 | 161.4 | 6940.2 | 0.0042282 | 0.0026197
2013-05-23 | ZN72:PA22 | URBAN | Third Party Impacts | 974192 | 78 | 433 | 33774 | 0.020576 | 0.0047521
2013-05-24 | ZN14144:PA5 | SHORT RURAL | Equipment Failure | 974195 | 11 | 66 | 726 | 0.00044231 | 0.00067017
2013-05-23 | ZN116:PA42 | URBAN | Equipment Failure | 974196 | 14 | 855 | 11970 | 0.0072926 | 0.00085293
2013-05-23 | ZN72:PA34 | URBAN | Third Party Impacts | 974201 | 79 | 438 | 34602 | 0.021081 | 0.004813
2013-05-24 | ZN9118:PA12 | URBAN | Vegetation | 974210 | 1 | 125.5333 | 125.5333 | 7.648e-05 | 6.0924e-05
2013-05-24 | ZN14144:PA5 | SHORT RURAL | Vegetation | 974212 | 19 | 178 | 3382 | 0.0020605 | 0.0011576
2013-05-24 | ZN12570:PA37 | SHORT RURAL | Equipment Failure | 974222 | 1 | 312.0333 | 312.0333 | 0.0001901 | 6.0924e-05
2013-05-23 | ZN7900:PA12 | URBAN | Other | 974244 | 7 | 311 | 2177 | 0.0013263 | 0.00042647
2013-05-24 | ZN12640:PA7 | URBAN | Equipment Failure | 974288 | 41 | 312.8167 | 12825.4833 | 0.0078138 | 0.0024979
2013-05-24 | 813:89055 | SHORT RURAL | Equipment Failure | 974306 | 3 | 187 | 561 | 0.00034179 | 0.00018277
2013-05-24 | ZN10990:PA1 | URBAN | Vegetation | 974313 | 9 | 89 | 801 | 0.000488 | 0.00054832
2013-05-24 | ZN12610:PA16 | URBAN | Other | 974353 | 1 | 72.0167 | 72.0167 | 4.3876e-05 | 6.0924e-05
2013-05-24 | 512:48049 | SHORT RURAL | Other | 974355 | 1 | 152.0833 | 152.0833 | 9.2656e-05 | 6.0924e-05
2013-05-24 | ZN5868:PA27 | URBAN | Weather | 974357 | 44 | 88 | 3872 | 0.002359 | 0.0026807
2013-05-24 | ZN1164:PA26 | URBAN | Other | 974446 | 1 | 242.7167 | 242.7167 | 0.00014787 | 6.0924e-05
2013-05-24 | ZN1164:PA26 | URBAN | Other | 974502 | 1 | 135.7167 | 135.7167 | 8.2684e-05 | 6.0924e-05
2013-05-24 | ZN1164:PA10 | URBAN | Vegetation | 974534 | 31 | 25 | 775 | 0.00047216 | 0.0018887
2013-05-24 | ZN15011:PA2 | URBAN | Vegetation | 974574 | 1 | 1020.9333 | 1020.9333 | 0.000622 | 6.0924e-05
2013-05-24 | ZN129:PA3 | URBAN | Vegetation | 974577 | 828 | 352 | 88596 | 0.053976 | 0.050445
2013-05-24 | ZN129:PA8 | URBAN | Vegetation | 974577 | 1071 | 352 | 72023 | 0.043879 | 0.06525
2013-05-24 | ZN9037:PA10 | URBAN | Other | 974587 | 1 | 175.45 | 175.45 | 0.00010689 | 6.0924e-05
2013-05-24 | ZN9252:PA12 | URBAN | Equipment Failure | 974605 | 1 | 278.1333 | 278.1333 | 0.00016945 | 6.0924e-05
2013-05-24 | ZN9252:PA12 | URBAN | Other | 974612 | 1 | 231.6167 | 231.6167 | 0.00014111 | 6.0924e-05
2013-05-24 | ZN9252:PA12 | URBAN | Other | 974614 | 1 | 221.9833 | 221.9833 | 0.00013524 | 6.0924e-05
2013-05-24 | ZN3155:PA30 | URBAN | Equipment Failure | 974618 | 4 | 234 | 936 | 0.00057025 | 0.0002437
2013-05-24 | 504:48034 | URBAN | Equipment Failure | 974624 | 1 | 107.7167 | 107.7167 | 6.5626e-05 | 6.0924e-05
2013-05-24 | ZN5868:PA30 | URBAN | Other | 974625 | 1 | 797.5333 | 797.5333 | 0.00048589 | 6.0924e-05
2013-05-24 | ZN15014:PA12 | SHORT RURAL | Other | 974626 | 1 | 723.0667 | 723.0667 | 0.00044052 | 6.0924e-05
2013-05-25 | 208:58 | URBAN | Equipment Failure | 974632 | 73 | 358 | 26134 | 0.015922 | 0.0044475
2013-05-25 | 256:80647 | URBAN | Third Party Impacts | 974633 | 1790 | 82 | 104289 | 0.063537 | 0.10905
2013-05-25 | ZN195:PA30 | URBAN | Animals | 974634 | 43 | 333.9833 | 14361.2833 | 0.0087495 | 0.0026197
2013-05-25 | ZN398:PA9 | URBAN | Other | 974642 | 1 | 244.0833 | 244.0833 | 0.00014871 | 6.0924e-05
2013-05-25 | 504:48029 | URBAN | Equipment Failure | 974652 | 243 | 253 | 61479 | 0.037456 | 0.014805
2013-05-25 | 256:80647 | URBAN | Equipment Failure | 974679 | 132 | 80.9833 | 10576.95 | 0.0064439 | 0.008042
2013-05-25 | ZN195:PA30 | URBAN | Equipment Failure | 974680 | 1 | 477.3667 | 477.3667 | 0.00029083 | 6.0924e-05
2013-05-25 | ZN3922:PA29 | URBAN | Other | 974709 | 79 | 278 | 21962 | 0.01338 | 0.004813
2013-05-25 | ZN3155:PA30 | URBAN | Equipment Failure | 974712 | 4 | 188 | 752 | 0.00045815 | 0.0002437
2013-05-25 | ZN2835:PA31 | URBAN | Third Party Impacts | 974716 | 52 | 62.6 | 3255.2 | 0.0019832 | 0.0031681
2013-05-25 | 258:80787 | URBAN | Other | 974729 | 1 | 118.9333 | 118.9333 | 7.2459e-05 | 6.0924e-05
2013-05-25 | 232:11454 | SHORT RURAL | Other | 974737 | 1 | 168.9167 | 168.9167 | 0.00010291 | 6.0924e-05
2013-05-25 | ZN129:PA21 | URBAN | Equipment Failure | 974765 | 30 | 34 | 1020 | 0.00062143 | 0.0018277
2013-05-25 | ZN10999:PA17 | URBAN | Equipment Failure | 974772 | 70 | 53 | 3710 | 0.0022603 | 0.0042647
2013-05-25 | ZN10999:PA32 | URBAN | Equipment Failure | 974772 | 1 | 53 | 53 | 3.229e-05 | 6.0924e-05
2013-05-25 | ZN2400:PA11 | SHORT RURAL | Equipment Failure | 974786 | 1 | 888.0167 | 888.0167 | 0.00054102 | 6.0924e-05
2013-05-26 | ZN12660:PA14 | SHORT RURAL | Other | 974793 | 2495 | 135 | 336825 | 0.20521 | 0.15201
2013-05-26 | ZN12660:PA16 | URBAN | Other | 974793 | 263 | 135 | 35505 | 0.021631 | 0.016023
2013-05-26 | 803:74007 | SHORT RURAL | Other | 974821 | 396 | 101 | 22572 | 0.013752 | 0.024126
2013-05-26 | 803:74010 | SHORT RURAL | Other | 974821 | 685 | 101 | 39045 | 0.023788 | 0.041733
2013-05-26 | 803:74016 | SHORT RURAL | Other | 974821 | 152 | 101 | 8664 | 0.0052785 | 0.0092605
2013-05-26 | 806:82662 | SHORT RURAL | Other | 974821 | 230 | 101 | 23230 | 0.014153 | 0.014013
2013-05-26 | 806:82667 | SHORT RURAL | Other | 974821 | 40 | 101 | 4040 | 0.0024613 | 0.002437
2013-05-26 | 811:74234 | SHORT RURAL | Other | 974821 | 258 | 101 | 26058 | 0.015876 | 0.015718
2013-05-26 | 510:48164 | SHORT RURAL | Equipment Failure | 974841 | 1 | 321.4833 | 321.4833 | 0.00019586 | 6.0924e-05
2013-05-26 | ZN14892:PA10 | SHORT RURAL | Other | 974845 | 1 | 270.3667 | 270.3667 | 0.00016472 | 6.0924e-05
2013-05-26 | 813:89061 | LONG RURAL | Equipment Failure | 974857 | 1 | 122.2167 | 122.2167 | 7.446e-05 | 6.0924e-05
2013-05-26 | 513:48052 | URBAN | Other | 974870 | 1 | 53.2333 | 53.2333 | 3.2432e-05 | 6.0924e-05
2013-05-26 | ZN9550:PA1 | URBAN | Other | 974871 | 41 | 193 | 7913 | 0.0048209 | 0.0024979
2013-05-26 | ZN9550:PA28 | URBAN | Other | 974871 | 2 | 193 | 386 | 0.00023517 | 0.00012185
2013-05-26 | ZN72:PA25 | URBAN | Other | 974881 | 47 | 225.2 | 10584.4 | 0.0064485 | 0.0028634
2013-05-26 | 503:48011 | SHORT RURAL | Other | 974887 | 1 | 124.0833 | 124.0833 | 7.5597e-05 | 6.0924e-05
2013-05-26 | 503:48017 | URBAN | Other | 974899 | 1 | 93.5667 | 93.5667 | 5.7005e-05 | 6.0924e-05
2013-05-26 | ZN901:PA20 | URBAN | Equipment Failure | 974900 | 110 | 31.9833 | 3518.1667 | 0.0021434 | 0.0067017
2013-05-26 | ZN14892:PA8 | URBAN | Other | 974910 | 1 | 222.1833 | 222.1833 | 0.00013536 | 6.0924e-05
2013-05-26 | ZN36300:PA11 | URBAN | Equipment Failure | 974919 | 63 | 88 | 5544 | 0.0033776 | 0.0038382
2013-05-26 | ZN36300:PA3 | URBAN | Equipment Failure | 974919 | 32 | 88 | 2816 | 0.0017156 | 0.0019496
2013-05-26 | ZN13000:PA10 | URBAN | Equipment Failure | 974944 | 423 | 213 | 48244 | 0.029392 | 0.025771
2013-05-27 | ZN3154:PA17 | URBAN | Other | 974946 | 19 | 271 | 5149 | 0.003137 | 0.0011576
2013-05-27 | 202:34232 | URBAN | Vegetation | 974952 | 110 | 183.3667 | 12452 | 0.0075863 | 0.0067017
2013-05-27 | 256:80647 | URBAN | Vegetation | 974952 | 1 | 183.3667 | 109.3167 | 6.66e-05 | 6.0924e-05
2013-05-27 | ZN3472:PA34 | URBAN | Other | 974956 | 5 | 109 | 545 | 0.00033204 | 0.00030462
2013-05-27 | 234:14291 | URBAN | Equipment Failure | 974987 | 1 | 58.4167 | 58.4167 | 3.559e-05 | 6.0924e-05
2013-05-27 | 238:34147 | URBAN | Third Party Impacts | 975004 | 1 | 547.5667 | 547.5667 | 0.0003336 | 6.0924e-05
2013-05-27 | 807:74179 | SHORT RURAL | Other | 975159 | 1 | 259.9833 | 259.9833 | 0.00015839 | 6.0924e-05
2013-05-27 | ZN3425:PA15 | URBAN | Other | 975174 | 56 | 36 | 1904 | 0.00116 | 0.0034118
2013-05-27 | ZN3425:PA27 | URBAN | Other | 975174 | 262 | 36 | 8908 | 0.0054271 | 0.015962
2013-05-27 | ZN3425:PA28 | URBAN | Other | 975174 | 743 | 36 | 26005 | 0.015843 | 0.045267
2013-05-27 | ZN3425:PA30 | URBAN | Other | 975174 | 364 | 36 | 12376 | 0.00754 | 0.022176
2013-05-27 | ZN3425:PA32 | URBAN | Other | 975174 | 168 | 36 | 5712 | 0.00348 | 0.010235
2013-05-27 | ZN3425:PA33 | URBAN | Other | 975174 | 457 | 36 | 15995 | 0.0097448 | 0.027842
2013-05-27 | ZN3425:PA34 | URBAN | Other | 975174 | 586 | 36 | 19924 | 0.012139 | 0.035702
2013-05-27 | ZN3425:PA35 | URBAN | Other | 975174 | 852 | 36 | 29820 | 0.018168 | 0.051907
2013-05-27 | ZN3425:PA36 | URBAN | Other | 975174 | 4 | 36 | 136 | 8.2857e-05 | 0.0002437
2013-05-27 | ZN3425:PA39 | URBAN | Other | 975174 | 685 | 36 | 23975 | 0.014607 | 0.041733
2013-05-27 | ZN3425:PA43 | URBAN | Other | 975174 | 1296 | 36 | 45360 | 0.027635 | 0.078958
2013-05-27 | ZN3425:PA44 | URBAN | Other | 975174 | 923 | 36 | 33228 | 0.020244 | 0.056233
2013-05-27 | ZN3425:PA46 | URBAN | Other | 975174 | 302 | 36 | 10872 | 0.0066237 | 0.018399
2013-05-27 | ZN80:PA37 | URBAN | Other | 975174 | 20 | 36 | 680 | 0.00041429 | 0.0012185
2013-05-27 | ZN14892:PA17 | URBAN | Equipment Failure | 975199 | 10 | 40 | 400 | 0.0002437 | 0.00060924
2013-05-27 | ZN9037:PA2 | URBAN | Equipment Failure | 975203 | 109 | 376 | 40984 | 0.024969 | 0.0066407
2013-05-08 | ZN5868:PA30 | URBAN | Equipment Failure | 975214 | 1684 | 378 | 170414 | 0.10382 | 0.10259
2013-05-27 | ZN7900:PA12 | URBAN | Equipment Failure | 975238 | 163 | 213.1167 | 34738.0167 | 0.021164 | 0.0099307
2013-05-25 | ZN3922:PA2 | SHORT RURAL | Other | 975301 | 78 | 271 | 21138 | 0.012878 | 0.0047521
2013-05-27 | 503:48011 | SHORT RURAL | Third Party Impacts | 975305 | 1 | 101.5833 | 101.5833 | 6.1889e-05 | 6.0924e-05
2013-05-27 | ZN12610:PA22 | URBAN | Equipment Failure | 975377 | 1895 | 186 | 86872 | 0.052926 | 0.11545
2013-05-27 | ZN3154:PA17 | URBAN | Equipment Failure | 975415 | 23 | 1520 | 27460 | 0.01673 | 0.0014013
2013-05-27 | ZN1164:PA3 | URBAN | Other | 975434 | 100 | 27 | 2700 | 0.001645 | 0.0060924
2013-05-27 | ZN269:PA19 | URBAN | Other | 975434 | 12 | 27 | 324 | 0.00019739 | 0.00073109
2013-05-27 | ZN12630:PA2 | SHORT RURAL | Equipment Failure | 975449 | 1 | 129.6667 | 129.6667 | 7.8998e-05 | 6.0924e-05
2013-05-27 | 507:80917 | URBAN | Other | 975455 | 1 | 243.1833 | 243.1833 | 0.00014816 | 6.0924e-05
2013-05-28 | ZN2310:PA37 | URBAN | Third Party Impacts | 975466 | 1 | 172.6167 | 172.6167 | 0.00010512 | 6.0897e-05
2013-05-28 | ZN10993:PA2 | URBAN | Other | 975496 | 1 | 319.4667 | 319.4667 | 0.00019455 | 6.0897e-05
2013-05-28 | ZN12630:PA1 | SHORT RURAL | Other | 975521 | 1 | 73.05 | 73.05 | 4.4485e-05 | 6.0897e-05
2013-05-28 | 811:74234 | SHORT RURAL | Equipment Failure | 975531 | 1 | 242.0833 | 242.0833 | 0.00014742 | 6.0897e-05
2013-05-28 | ZN35600:PA22 | URBAN | Other | 975537 | 1 | 327.5333 | 327.5333 | 0.00019946 | 6.0897e-05
2013-05-28 | ZN35600:PA22 | URBAN | Other | 975592 | 1 | 247.4167 | 247.4167 | 0.00015067 | 6.0897e-05
2013-05-28 | ZN1648:PA11 | URBAN | Other | 975619 | 1 | 180.2667 | 180.2667 | 0.00010978 | 6.0897e-05
2013-05-28 | ZN12630:PA2 | SHORT RURAL | Other | 975640 | 1 | 174.1833 | 174.1833 | 0.00010607 | 6.0897e-05
2013-05-28 | ZN35500:PA14 | URBAN | Operational Error | 975641 | 74 | 45 | 2838 | 0.0017283 | 0.0045064
2013-05-28 | ZN35500:PA32 | URBAN | Operational Error | 975641 | 131 | 45 | 5895 | 0.0035899 | 0.0079775
2013-05-28 | ZN14891:PA9 | URBAN | Third Party Impacts | 975643 | 9 | 35.6 | 320.4 | 0.00019511 | 0.00054807
2013-05-28 | 508:82578 | SHORT RURAL | Other | 975806 | 1 | 67.9667 | 67.9667 | 4.139e-05 | 6.0897e-05
2013-05-28 | ZN3922:PA5 | URBAN | Other | 975814 | 1 | 229.0167 | 229.0167 | 0.00013946 | 6.0897e-05
2013-05-28 | ZN3922:PA5 | URBAN | Other | 975840 | 1 | 171.8167 | 171.8167 | 0.00010463 | 6.0897e-05
2013-05-28 | ZN3922:PA5 | URBAN | Other | 975842 | 1 | 166.7667 | 166.7667 | 0.00010156 | 6.0897e-05
2013-05-28 | 516:48067 | SHORT RURAL | Equipment Failure | 975848 | 8 | 92 | 736 | 0.0004482 | 0.00048718
2013-05-28 | 258:80778 | URBAN | Equipment Failure | 975851 | 1 | 155.1 | 155.1 | 9.4451e-05 | 6.0897e-05
2013-05-28 | 508:82578 | SHORT RURAL | Equipment Failure | 975870 | 27 | 175 | 4725 | 0.0028774 | 0.0016442
2013-05-28 | ZN398:PA25 | URBAN | Other | 975872 | 1 | 385.9833 | 385.9833 | 0.00023505 | 6.0897e-05
2013-05-28 | ZN10991:PA8 | URBAN | Other | 975876 | 1 | 495.9667 | 495.9667 | 0.00030203 | 6.0897e-05
2013-05-28 | ZN72:PA26 | URBAN | Third Party Impacts | 975878 | 61 | 194 | 11834 | 0.0072066 | 0.0037147
2013-05-22 | ZN187:PA17 | URBAN | Equipment Failure | 975894 | 995 | 2 | 1990 | 0.0012124 | 0.060619
2013-05-29 | ZN2635:PA16 | URBAN | Equipment Failure | 975915 | 28 | 219.6667 | 3968.5333 | 0.0024167 | 0.0017051
2013-05-29 | ZN965:PA15 | URBAN | Equipment Failure | 975915 | 1 | 219.6667 | 217.35 | 0.00013236 | 6.0898e-05
2013-05-29 | ZN7481:PA17 | URBAN | Equipment Failure | 976002 | 1 | 688.9 | 688.9 | 0.00041952 | 6.0898e-05
2013-05-29 | 223:14397 | URBAN | Equipment Failure | 976021 | 1 | 143.6167 | 143.6167 | 8.7459e-05 | 6.0898e-05
2013-05-29 | 813:89063 | SHORT RURAL | Third Party Impacts | 976047 | 1 | 53.9333 | 53.9333 | 3.2844e-05 | 6.0898e-05
2013-05-29 | ZN2400:PA11 | SHORT RURAL | Third Party Impacts | 976052 | 1 | 84.6833 | 84.6833 | 5.157e-05 | 6.0898e-05
2013-05-29 | 214:8669 | URBAN | Other | 976057 | 1 | 56.7333 | 56.7333 | 3.4549e-05 | 6.0898e-05
2013-05-27 | ZN7900:PA12 | URBAN | Equipment Failure | 976113 | 163 | 1688 | 275144 | 0.16763 | 0.0099307
2013-05-29 | ZN35600:PA19 | URBAN | Third Party Impacts | 976128 | 47 | 339.6 | 15961.2 | 0.00972 | 0.0028622
2013-05-29 | ZN35600:PA19 | URBAN | Weather | 976165 | 12 | 51 | 612 | 0.00037269 | 0.00073077
2013-05-29 | ZN12690:PA12 | SHORT RURAL | Equipment Failure | 976225 | 35 | 58 | 2030 | 0.0012362 | 0.0021314
2013-05-29 | ZN12650:PA20 | URBAN | Equipment Failure | 976245 | 1 | 80.35 | 80.35 | 4.8931e-05 | 6.0898e-05
2013-05-29 | ZN12650:PA20 | URBAN | Equipment Failure | 976247 | 1 | 67.0167 | 67.0167 | 4.0812e-05 | 6.0898e-05
2013-05-30 | 264:81240 | SHORT RURAL | Other | 976248 | 43 | 112.5333 | 4838.9333 | 0.0029469 | 0.0026187
2013-05-30 | 243:80074 | URBAN | Equipment Failure | 976251 | 146 | 690 | 100740 | 0.06135 | 0.0088913
2013-05-30 | ZN12610:PA22 | URBAN | Other | 976254 | 81 | 97 | 7857 | 0.0047849 | 0.0049329
2013-05-30 | ZN80:PA28 | URBAN | Equipment Failure | 976259 | 438 | 86 | 36534 | 0.022249 | 0.026674
2013-05-30 | 503:48012 | URBAN | Other | 976286 | 1 | 383.4333 | 383.4333 | 0.00023351 | 6.0899e-05
2013-05-30 | ZN14891:PA5 | SHORT RURAL | Operational Error | 976306 | 2 | 20.9667 | 41.9333 | 2.5537e-05 | 0.0001218
2013-05-28 | 503:48017 | URBAN | Equipment Failure | 976317 | 16 | 25 | 400 | 0.00024359 | 0.00097435
2013-05-30 | ZN9245:PA10 | URBAN | Other | 976326 | 46 | 72.6167 | 3340.3667 | 0.0020343 | 0.0028014
2013-05-30 | 232:11455 | URBAN | Equipment Failure | 976366 | 4 | 534.8 | 684.8 | 0.00041704 | 0.0002436
2013-05-30 | 509:48039 | LONG RURAL | Equipment Failure | 976406 | 4 | 128.75 | 515 | 0.00031363 | 0.0002436
2013-05-30 | 258:80787 | URBAN | Other | 976474 | 1 | 90.65 | 90.65 | 5.5205e-05 | 6.0899e-05
2013-05-30 | 256:80646 | URBAN | Vegetation | 976777 | 1 | 49.9167 | 49.9167 | 3.0399e-05 | 6.0899e-05
2013-05-30 | 234:14291 | URBAN | Other | 976840 | 1 | 151.6333 | 151.6333 | 9.2344e-05 | 6.0899e-05
2013-05-30 | 507:80923 | SHORT RURAL | Other | 976884 | 6 | 169 | 1014 | 0.00061752 | 0.0003654
2013-05-30 | 221:11900 | URBAN | Third Party Impacts | 976909 | 1199 | 388 | 193460 | 0.11782 | 0.073018
2013-05-31 | ZN12570:PA24 | SHORT RURAL | Equipment Failure | 976924 | 75 | 91 | 6825 | 0.0041564 | 0.0045675
2013-05-31 | 213:33775 | URBAN | Equipment Failure | 976953 | 1 | 85.2833 | 85.2833 | 5.1937e-05 | 6.09e-05
2013-05-29 | ZN12650:PA20 | URBAN | Equipment Failure | 976992 | 686 | 2 | 1372 | 0.00083552 | 0.041776
2013-05-31 | 811:74234 | SHORT RURAL | Equipment Failure | 977022 | 2 | 90 | 180 | 0.00010962 | 0.0001218
2013-05-31 | 511:29878 | SHORT RURAL | Other | 977041 | 15 | 139.0333 | 2085.5 | 0.0012701 | 0.0009135
2013-05-31 | 509:48039 | LONG RURAL | Other | 977104 | 3 | 105 | 315 | 0.00019183 | 0.0001827
2013-05-31 | ZN3472:PA28 | URBAN | Other | 977120 | 1 | 232.2833 | 232.2833 | 0.00014146 | 6.09e-05
2013-05-31 | 258:80787 | URBAN | Third Party Impacts | 977167 | 102 | 151.65 | 15468.3 | 0.0094201 | 0.0062118
2013-05-31 | ZN12620:PA8 | SHORT RURAL | Other | 977236 | 1 | 78.1833 | 78.1833 | 4.7613e-05 | 6.09e-05
2013-05-31 | ZN12690:PA24 | SHORT RURAL | Vegetation | 977237 | 1 | 226.0667 | 226.0667 | 0.00013767 | 6.09e-05
2013-05-31 | ZN3154:PA5 | URBAN | Other | 977242 | 1 | 324 | 324 | 0.00019732 | 6.09e-05
2013-05-31 | ZN3154:PA5 | URBAN | Other | 977278 | 37 | 55 | 2035 | 0.0012393 | 0.0022533
2013-06-01 | 512:48049 | SHORT RURAL | Equipment Failure | 977287 | 3 | 137 | 411 | 0.0002503 | 0.0001827
2013-06-01 | ZN116:PA41 | URBAN | Vegetation | 977293 | 48 | 109 | 5232 | 0.0031863 | 0.0029232
2013-06-01 | ZN116:PA42 | URBAN | Vegetation | 977293 | 70 | 109 | 7624.1667 | 0.0046431 | 0.004263
2013-06-01 | ZN262:PA19 | URBAN | Other | 977300 | 1 | 81.3167 | 81.3167 | 4.9522e-05 | 6.09e-05
2013-06-01 | 261:81865 | URBAN | Other | 977318 | 1 | 86.3667 | 86.3667 | 5.2597e-05 | 6.09e-05
2013-06-01 | 810:74062 | SHORT RURAL | Other | 977321 | 47 | 59.1167 | 2637.3833 | 0.0016062 | 0.0028623
2013-06-01 | ZN690:PA4 | URBAN | Vegetation | 977341 | 1 | 92.4667 | 92.4667 | 5.6312e-05 | 6.09e-05
2013-06-01 | 258:80787 | URBAN | Other | 977349 | 1 | 100.2 | 100.2 | 6.1022e-05 | 6.09e-05
2013-06-01 | ZN847:PA19 | URBAN | Other | 977370 | 44 | 137 | 6028 | 0.003671 | 0.0026796
2013-06-01 | 509:48039 | LONG RURAL | Other | 977372 | 2 | 122 | 244 | 0.0001486 | 0.0001218
2013-06-01 | 512:48046 | SHORT RURAL | Equipment Failure | 977387 | 1 | 150 | 150 | 9.135e-05 | 6.09e-05
2013-06-01 | ZN1193:PA21 | URBAN | Equipment Failure | 977393 | 1 | 326.6833 | 326.6833 | 0.00019895 | 6.09e-05
2013-06-01 | ZN12640:PA19 | URBAN | Third Party Impacts | 977399 | 77 | 194.65 | 14988.05 | 0.0091277 | 0.0046893
2013-06-01 | ZN116:PA36 | URBAN | Other | 977409 | 1 | 77.2 | 77.2 | 4.7015e-05 | 6.09e-05
2013-06-01 | ZN14891:PA20 | SHORT RURAL | Equipment Failure | 977418 | 18 | 106 | 1908 | 0.001162 | 0.0010962
2013-06-02 | ZN4990:PA53 54KLM | CBD | Equipment Failure | 977429 | 21 | 1679 | 35259 | 0.021473 | 0.0012789
2013-06-02 | ZN9118:PA26 | URBAN | Other | 977430 | 1 | 492.2167 | 492.2167 | 0.00029976 | 6.09e-05
2013-06-02 | 803:74016 | SHORT RURAL | Equipment Failure | 977431 | 5 | 235 | 1175 | 0.00071557 | 0.0003045
2013-06-02 | ZN10990:PA5 | URBAN | Equipment Failure | 977460 | 1 | 746 | 746 | 0.00045431 | 6.09e-05
2013-06-02 | ZN9900:PA2 | URBAN | Other | 977465 | 1 | 135.3333 | 135.3333 | 8.2418e-05 | 6.09e-05
2013-06-02 | ZN690:PA14 | URBAN | Vegetation | 977467 | 54 | 40.2667 | 2174.4 | 0.0013242 | 0.0032886
2013-06-02 | ZN398:PA29 | URBAN | Other | 977469 | 1 | 367.9667 | 367.9667 | 0.00022409 | 6.09e-05
2013-06-02 | ZN15012:PA8 | URBAN | Vegetation | 977475 | 1144 | 68 | 77792 | 0.047375 | 0.069669
2013-06-02 | ZN1673:PA9 | URBAN | Equipment Failure | 977498 | 487 | 103 | 43957 | 0.02677 | 0.029658
2013-06-02 | ZN9252:PA2 | URBAN | Vegetation | 977510 | 1 | 652.1167 | 652.1167 | 0.00039714 | 6.09e-05
2013-06-02 | ZN14892:PA6 | SHORT RURAL | Other | 977518 | 1 | 57.2667 | 57.2667 | 3.4875e-05 | 6.09e-05
2013-06-02 | ZN9550:PA43 | URBAN | Equipment Failure | 977523 | 1 | 632.6833 | 632.6833 | 0.0003853 | 6.09e-05
2013-06-02 | ZN2835:PA29 | URBAN | Equipment Failure | 977526 | 13 | 553 | 7189 | 0.0043781 | 0.0007917
2013-06-02 | ZN9118:PA22 | URBAN | Vegetation | 977527 | 1 | 431.8167 | 431.8167 | 0.00026298 | 6.09e-05
2013-06-02 | ZN1164:PA26 | URBAN | Vegetation | 977538 | 38 | 270.9333 | 10295.4667 | 0.0062699 | 0.0023142
2013-06-02 | ZN1788:PA1 | URBAN | Weather | 977546 | 204 | 202 | 41208 | 0.025096 | 0.012424
2013-06-02 | ZN14891:PA12 | SHORT RURAL | Other | 977549 | 333 | 165 | 51420 | 0.031315 | 0.02028
2013-06-02 | ZN14891:PA1 | SHORT RURAL | Other | 977555 | 312 | 130 | 33085 | 0.020149 | 0.019001
2013-06-02 | ZN14891:PA16 | SHORT RURAL | Other | 977555 | 179 | 130 | 18795 | 0.011446 | 0.010901
2013-06-02 | 234:2001 | URBAN | Other | 977569 | 1 | 64 | 64 | 3.8976e-05 | 6.09e-05
2013-06-02 | ZN15002:PA8 | URBAN | Vegetation | 977571 | 1 | 596.3333 | 596.3333 | 0.00036317 | 6.09e-05
2013-06-02 | ZN398:PA29 | URBAN | Other | 977586 | 1 | 248.4833 | 248.4833 | 0.00015133 | 6.09e-05
2013-06-02 | ZN12610:PA18 | URBAN | Other | 977599 | 1 | 202.4333 | 202.4333 | 0.00012328 | 6.09e-05
2013-06-02 | ZN14891:PA20 | SHORT RURAL | Other | 977601 | 1 | 128.55 | 128.55 | 7.8287e-05 | 6.09e-05
2013-06-02 | ZN1673:PA1 | URBAN | Other | 977607 | 1 | 92.2167 | 92.2167 | 5.616e-05 | 6.09e-05
2013-06-02 | ZN14892:PA3 | SHORT RURAL | Vegetation | 977612 | 102 | 18 | 1836 | 0.0011181 | 0.0062118
2013-06-02 | 214:8669 | URBAN | Other | 977616 | 1 | 74.25 | 74.25 | 4.5218e-05 | 6.09e-05
2013-06-02 | ZN2602:PA15 | URBAN | Other | 977629 | 1 | 92.6 | 92.6 | 5.6393e-05 | 6.09e-05
2013-06-02 | 220:8689 | URBAN | Other | 977630 | 1 | 76.1167 | 76.1167 | 4.6355e-05 | 6.09e-05
2013-06-02 | ZN116:PA35 | URBAN | Vegetation | 977634 | 52 | 75 | 3894.1667 | 0.0023715 | 0.0031668
2013-06-02 | ZN12690:PA16 | SHORT RURAL | Vegetation | 977650 | 25 | 192 | 4800 | 0.0029232 | 0.0015225
2013-06-02 | ZN15002:PA6 | URBAN | Equipment Failure | 977658 | 1 | 518.4167 | 518.4167 | 0.00031571 | 6.09e-05
2013-06-02 | 243:80084 | SHORT RURAL | Other | 977676 | 1 | 123.9167 | 123.9167 | 7.5465e-05 | 6.09e-05
2013-06-02 | ZN1673:PA2 | URBAN | Other | 977678 | 13 | 158.8 | 2064.4 | 0.0012572 | 0.0007917
2013-06-02 | ZN12640:PA18 | SHORT RURAL | Other | 977679 | 1 | 77.9667 | 77.9667 | 4.7481e-05 | 6.09e-05
2013-06-02 | ZN14891:PA20 | SHORT RURAL | Other | 977681 | 1 | 146.8167 | 146.8167 | 8.9411e-05 | 6.09e-05
2013-06-02 | ZN12690:PA24 | SHORT RURAL | Vegetation | 977683 | 1 | 385.3667 | 385.3667 | 0.00023469 | 6.09e-05
2013-06-02 | ZN116:PA36 | URBAN | Other | 977685 | 1 | 16.0333 | 16.0333 | 9.7643e-06 | 6.09e-05
2013-06-02 | ZN9118:PA20 | URBAN | Equipment Failure | 977691 | 1 | 651.7833 | 651.7833 | 0.00039693 | 6.09e-05
2013-06-02 | ZN129:PA9 | URBAN | Equipment Failure | 977702 | 25 | 64 | 1600 | 0.0009744 | 0.0015225
2013-06-02 | ZN12640:PA15 | URBAN | Other | 977710 | 1 | 365.9833 | 365.9833 | 0.00022288 | 6.09e-05
2013-06-02 | ZN12690:PA24 | SHORT RURAL | Vegetation | 977714 | 26 | 24 | 624 | 0.00038001 | 0.0015834
2013-06-02 | ZN9301:PA8 | URBAN | Other | 977729 | 1 | 498.2 | 498.2 | 0.0003034 | 6.09e-05
2013-06-02 | ZN15006:PA12 | URBAN | Other | 977735 | 1 | 93.5833 | 93.5833 | 5.6992e-05 | 6.09e-05
2013-06-02 | ZN129:PA24 | URBAN | Other | 977744 | 168 | 129 | 21672 | 0.013198 | 0.010231
2013-06-02 | ZN129:PA9 | URBAN | Other | 977744 | 25 | 129 | 3225 | 0.001964 | 0.0015225
2013-06-02 | ZN15012:PA8 | URBAN | Vegetation | 977765 | 1 | 415.7333 | 415.7333 | 0.00025318 | 6.09e-05
2013-06-02 | 240:34852 | URBAN | Other | 977783 | 1 | 755.7667 | 755.7667 | 0.00046026 | 6.09e-05
2013-06-02 | ZN12620:PA11 | SHORT RURAL | Equipment Failure | 977790 | 41 | 96.6 | 3960.6 | 0.002412 | 0.0024969
2013-06-02 | 242:81538 | URBAN | Animals | 977794 | 206 | 577 | 60976 | 0.037134 | 0.012545
2013-06-02 | 242:81539 | URBAN | Animals | 977794 | 1984 | 577 | 400457 | 0.24388 | 0.12083
2013-06-02 | ZN15004:PA5 | URBAN | Vegetation | 977799 | 1 | 234.4667 | 234.4667 | 0.00014279 | 6.09e-05
2013-06-03 | 507:80925 | SHORT RURAL | Equipment Failure | 977826 | 1 | 399.1167 | 399.1167 | 0.00024306 | 6.09e-05
2013-06-02 | ZN10999:PA4 | URBAN | Third Party Impacts | 977862 | 1 | 190 | 190 | 0.00011571 | 6.09e-05
2013-06-03 | 229:34995 | SHORT RURAL | Equipment Failure | 977876 | 1 | 212.1833 | 212.1833 | 0.00012922 | 6.09e-05
2013-06-03 | 507:80932 | SHORT RURAL | Equipment Failure | 977885 | 4 | 184 | 736 | 0.00044822 | 0.0002436
2013-06-03 | 205:12206 | URBAN | Other | 977890 | 1 | 226.1667 | 226.1667 | 0.00013773 | 6.09e-05
2013-06-01 | 265:81651 | URBAN | Equipment Failure | 977911 | 2 | 105 | 210 | 0.00012789 | 0.0001218
2013-06-03 | 526:34640 | SHORT RURAL | Equipment Failure | 977918 | 2 | 160 | 320 | 0.00019488 | 0.0001218
2013-06-03 | ZN9700:PA17 | URBAN | Equipment Failure | 977934 | 1 | 70.8667 | 70.8667 | 4.3158e-05 | 6.09e-05
2013-06-03 | ZN3472:PA34 | URBAN | Equipment Failure | 977935 | 7 | 396 | 2772 | 0.0016881 | 0.0004263
2013-06-03 | 220:8689 | URBAN | Other | 977951 | 1 | 164.9667 | 164.9667 | 0.00010046 | 6.09e-05
2013-06-03 | 224:80332 | URBAN | Other | 977976 | 1 | 110.2833 | 110.2833 | 6.7162e-05 | 6.09e-05
2013-06-03 | ZN3425:PA16 | URBAN | Equipment Failure | 977993 | 17 | 138 | 2346 | 0.0014287 | 0.0010353
2013-06-03 | 261:81879 | URBAN | Equipment Failure | 977998 | 105 | 54.3167 | 5703.25 | 0.0034733 | 0.0063945
2013-06-03 | ZN10990:PA6 | URBAN | Vegetation | 978031 | 1 | 487.5333 | 487.5333 | 0.00029691 | 6.09e-05
2013-06-03 | ZN80:PA25 | URBAN | Equipment Failure | 978082 | 915 | 132 | 120780 | 0.073555 | 0.055723
2013-06-02 | ZN15008:PA9 | URBAN | Other | 978085 | 1001 | 4 | 4004 | 0.0024384 | 0.060961
2013-06-02 | ZN15011:PA2 | URBAN | Other | 978085 | 859 | 4 | 3436 | 0.0020925 | 0.052313
2013-06-03 | ZN10995:PA12 | URBAN | Other | 978134 | 1 | 1173.9833 | 1173.9833 | 0.00071495 | 6.09e-05
2013-06-03 | ZN2835:PA31 | URBAN | Other | 978146 | 1 | 318.1833 | 318.1833 | 0.00019377 | 6.09e-05
2013-06-03 | ZN129:PA5 | URBAN | Equipment Failure | 978240 | 1 | 2200.65 | 2200.65 | 0.0013402 | 6.09e-05
2013-06-03 | ZN9118:PA20 | URBAN | Equipment Failure | 978245 | 1 | 272.4333 | 272.4333 | 0.00016591 | 6.09e-05
2013-06-03 | ZN1648:PA16 | URBAN | Other | 978256 | 70 | 129 | 9030 | 0.0054992 | 0.004263
2013-06-03 | ZN13000:PA2 | URBAN | Equipment Failure | 978261 | 294 | 24 | 7056 | 0.0042971 | 0.017905
2013-06-03 | ZN13000:PA1 | URBAN | Other | 978270 | 1 | 17.4833 | 17.4833 | 1.0647e-05 | 6.09e-05
2013-06-03 | ZN1285:PA19 | URBAN | Other | 978271 | 70 | 25 | 1750 | 0.0010657 | 0.004263
2013-06-03 | ZN12600:PA9 | SHORT RURAL | Equipment Failure | 978278 | 5 | 90 | 450 | 0.00027405 | 0.0003045
2013-06-03 | ZN3472:PA31 | URBAN | Equipment Failure | 978285 | 61 | 65 | 3965 | 0.0024147 | 0.0037149
2013-06-03 | ZN2835:PA9 | URBAN | Third Party Impacts | 978302 | 124 | 328 | 40672 | 0.024769 | 0.0075516
2013-06-04 | ZN116:PA50 | URBAN | Third Party Impacts | 978307 | 1 | 619.3167 | 619.3167 | 0.00037694 | 6.0864e-05
2013-06-04 | ZN10994:PA9 | URBAN | Equipment Failure | 978310 | 69 | 93 | 6417 | 0.0039057 | 0.0041996
2013-06-04 | ZN187:PA26 | URBAN | Other | 978318 | 21 | 116 | 2436 | 0.0014827 | 0.0012782
2013-06-04 | 513:48056 | SHORT RURAL | Equipment Failure | 978321 | 2 | 93 | 186 | 0.00011321 | 0.00012173
2013-06-04 | ZN14892:PA9 | URBAN | Other | 978328 | 1 | 158.4333 | 158.4333 | 9.6429e-05 | 6.0864e-05
2013-06-04 | 810:74062 | SHORT RURAL | Other | 978332 | 1 | 37.1 | 37.1 | 2.2581e-05 | 6.0864e-05
2013-06-04 | ZN711:PA33 | URBAN | Equipment Failure | 978342 | 126 | 868 | 32949 | 0.020054 | 0.0076689
2013-06-04 | ZN116:PA50 | URBAN | Third Party Impacts | 978347 | 1 | 145.0833 | 145.0833 | 8.8304e-05 | 6.0864e-05
2013-06-03 | 239:82132 | URBAN | Other | 978357 | 212 | 25 | 5300 | 0.0032277 | 0.012911
2013-06-04 | ZN180:PA27 | URBAN | Other | 978386 | 1 | 10457.55 | 10457.55 | 0.0063649 | 6.0864e-05
2013-06-04 | 225:13446 | URBAN | Other | 978398 | 1 | 76.3333 | 76.3333 | 4.646e-05 | 6.0864e-05
2013-06-04 | 802:82225 | SHORT RURAL | Other | 978408 | 1 | 89 | 89 | 5.4169e-05 | 6.0864e-05
2013-06-04 | ZN2473:PA41 | URBAN | Other | 978439 | 1 | 193.3333 | 193.3333 | 0.00011767 | 6.0864e-05
2013-06-04 | ZN4545:PA24 | URBAN | Equipment Failure | 978501 | 91 | 130.8667 | 11908.8667 | 0.0072482 | 0.0055387
2013-06-04 | 238:34137 | URBAN | Equipment Failure | 978508 | 1 | 106.9167 | 106.9167 | 6.5074e-05 | 6.0864e-05
2013-06-04 | ZN2835:PA16 | URBAN | Third Party Impacts | 978558 | 1460 | 62 | 86152 | 0.052436 | 0.088862
2013-06-04 | ZN398:PA2 | URBAN | Third Party Impacts | 978578 | 1 | 456.6 | 456.6 | 0.00027791 | 6.0864e-05
2013-06-04 | ZN398:PA2 | URBAN | Third Party Impacts | 978586 | 149 | 90.55 | 13491.95 | 0.0082118 | 0.0090688
2013-06-04 | ZN14891:PA5 | SHORT RURAL | Equipment Failure | 978652 | 356 | 64 | 22784 | 0.013867 | 0.021668
2013-05-30 | ZN10995:PA8 | URBAN | Third Party Impacts | 978685 | 699 | 836 | 100666 | 0.061305 | 0.042569
2013-06-04 | ZN180:PA27 | URBAN | Third Party Impacts | 978699 | 1 | 150.9667 | 150.9667 | 9.1885e-05 | 6.0864e-05
2013-05-30 | ZN10995:PA2 | URBAN | Other | 978705 | 64 | 112 | 7168 | 0.0043653 | 0.0038976
2013-06-04 | ZN12580:PA16 | URBAN | Equipment Failure | 978746 | 6 | 262 | 1572 | 0.00095679 | 0.00036519
2013-06-04 | 810:74054 | LONG RURAL | Animals | 978751 | 2 | 172.4167 | 299.9667 | 0.00018257 | 0.00012173
2013-06-04 | ZN4545:PA27 | URBAN | Equipment Failure | 978766 | 1 | 209.7333 | 209.7333 | 0.00012765 | 6.0864e-05
2013-06-04 | ZN15009:PA9 | URBAN | Equipment Failure | 978810 | 1 | 46.4167 | 46.4167 | 2.8251e-05 | 6.0864e-05
2013-06-04 | ZN398:PA2 | URBAN | Other | 978830 | 14 | 155.8833 | 2182.3667 | 0.0013283 | 0.0008521
2013-06-04 | 813:89062 | SHORT RURAL | Equipment Failure | 978833 | 1 | 40.2167 | 40.2167 | 2.4478e-05 | 6.0864e-05
2013-06-04 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 978866 | 1 | 815.6333 | 815.6333 | 0.00049643 | 6.0864e-05
2013-06-04 | ZN3472:PA29 | URBAN | Third Party Impacts | 978867 | 34 | 738.2833 | 25101.6333 | 0.015278 | 0.0020694
2013-06-05 | ZN2835:PA29 | URBAN | Third Party Impacts | 978874 | 139 | 74 | 10286 | 0.0062606 | 0.0084602
2013-06-05 | 229:34995 | SHORT RURAL | Other | 978876 | 1 | 80.7667 | 80.7667 | 4.9159e-05 | 6.0865e-05
2013-06-05 | ZN2835:PA29 | URBAN | Third Party Impacts | 978879 | 1 | 394.95 | 394.95 | 0.00024039 | 6.0865e-05
2013-06-05 | ZN965:PA47 | URBAN | Equipment Failure | 978901 | 1 | 93.1167 | 93.1167 | 5.6675e-05 | 6.0865e-05
2013-06-05 | ZN847:PA10 | URBAN | Third Party Impacts | 978902 | 27 | 102.75 | 2774.25 | 0.0016885 | 0.0016434
2013-06-05 | ZN2835:PA29 | URBAN | Third Party Impacts | 978909 | 1 | 70.2333 | 70.2333 | 4.2747e-05 | 6.0865e-05
2013-06-05 | 229:34995 | SHORT RURAL | Third Party Impacts | 978949 | 16 | 110 | 1760 | 0.0010712 | 0.00097384
2013-06-05 | ZN12650:PA1 | SHORT RURAL | Equipment Failure | 979012 | 1 | 11.8167 | 11.8167 | 7.1922e-06 | 6.0865e-05
2013-06-05 | ZN3672:PA13 | URBAN | Third Party Impacts | 979017 | 1 | 267.2833 | 267.2833 | 0.00016268 | 6.0865e-05
2013-06-06 | ZN10996:PA9 | URBAN | Equipment Failure | 979037 | 93 | 499 | 46407 | 0.028246 | 0.0056605
2013-06-05 | ZN3672:PA13 | URBAN | Third Party Impacts | 979042 | 1 | 209.1167 | 209.1167 | 0.00012728 | 6.0865e-05
2013-06-05 | ZN12610:PA10 | SHORT RURAL | Other | 979043 | 1 | 359.6833 | 359.6833 | 0.00021892 | 6.0865e-05
2013-06-05 | ZN10996:PA11 | URBAN | Equipment Failure | 979053 | 96 | 65.5167 | 6289.6 | 0.0038282 | 0.005843
2013-06-05 | 813:89062 | SHORT RURAL | Third Party Impacts | 979069 | 34 | 77.15 | 2623.1 | 0.0015965 | 0.0020694
2013-06-05 | ZN116:PA33 | URBAN | Equipment Failure | 979182 | 66 | 102 | 6732 | 0.0040974 | 0.0040171
2013-06-05 | 513:48057 | URBAN | Other | 979203 | 1 | 180.6167 | 180.6167 | 0.00010993 | 6.0865e-05
2013-06-05 | ZN15014:PA20 | URBAN | Equipment Failure | 979224 | 46 | 139.1667 | 6401.6667 | 0.0038964 | 0.0027998
2013-06-05 | ZN12600:PA3 | URBAN | Equipment Failure | 979231 | 1 | 156.9667 | 156.9667 | 9.5538e-05 | 6.0865e-05
2013-06-05 | 238:34137 | URBAN | Equipment Failure | 979271 | 13 | 567.2667 | 7374.4667 | 0.0044885 | 0.00079124
2013-06-06 | 223:14393 | URBAN | Third Party Impacts | 979276 | 1 | 622.4333 | 622.4333 | 0.00037885 | 6.0866e-05
2013-06-06 | ZN12690:PA16 | SHORT RURAL | Vegetation | 979282 | 1 | 18.2833 | 18.2833 | 1.1128e-05 | 6.0866e-05
2013-06-05 | 814:82283 | SHORT RURAL | Other | 979302 | 1 | 15 | 15 | 9.1297e-06 | 6.0865e-05
2013-06-05 | 814:82283 | SHORT RURAL | Equipment Failure | 979304 | 1 | 105 | 105 | 6.3908e-05 | 6.0865e-05
2013-06-02 | ZN384:PA1 | URBAN | Equipment Failure | 979349 | 415 | 4900.8833 | 1245 | 0.0007582 | 0.025273
2013-06-02 | ZN384:PA2 | URBAN | Equipment Failure | 979349 | 35 | 4900.8833 | 105 | 6.3945e-05 | 0.0021315
2013-06-02 | ZN384:PA4 | URBAN | Equipment Failure | 979349 | 87 | 4900.8833 | 261 | 0.00015895 | 0.0052983
2013-06-02 | ZN384:PA9 | URBAN | Equipment Failure | 979349 | 829 | 4900.8833 | 2487 | 0.0015146 | 0.050486
2013-06-04 | ZN1788:PA11 | URBAN | Third Party Impacts | 979406 | 1 | 376 | 376 | 0.00022885 | 6.0864e-05
2013-06-06 | 205:12210 | URBAN | Other | 979414 | 1 | 75.2167 | 75.2167 | 4.5781e-05 | 6.0866e-05
2013-06-04 | ZN2635:PA10 | URBAN | Equipment Failure | 979430 | 2288 | 89 | 199433 | 0.12138 | 0.13926
2013-06-06 | 523:33501 | SHORT RURAL | Equipment Failure | 979438 | 339 | 45 | 15255 | 0.009285 | 0.020633
2013-06-06 | ZN167:PA21 | URBAN | Third Party Impacts | 979499 | 1 | 360.5333 | 360.5333 | 0.00021944 | 6.0866e-05
2013-06-06 | ZN167:PA21 | URBAN | Third Party Impacts | 979505 | 1 | 348.75 | 348.75 | 0.00021227 | 6.0866e-05
2013-06-06 | 238:34147 | URBAN | Other | 979517 | 31 | 116 | 3596 | 0.0021887 | 0.0018868
2013-06-06 | ZN14144:PA10 | SHORT RURAL | Other | 979566 | 1 | 229.4333 | 229.4333 | 0.00013965 | 6.0866e-05
2013-06-06 | 235:2120 | SHORT RURAL | Equipment Failure | 979593 | 791 | 109.7167 | 66143 | 0.040258 | 0.048145
2013-06-06 | 238:34144 | URBAN | Equipment Failure | 979593 | 1 | 109.7167 | 109.7167 | 6.678e-05 | 6.0866e-05
2013-06-06 | ZN1287:PA24 | URBAN | Operational Error | 979610 | 66 | 120 | 7920 | 0.0048206 | 0.0040171
2013-06-06 | 264:81232 | URBAN | Other | 979658 | 1 | 183.1 | 183.1 | 0.00011144 | 6.0866e-05
2013-06-06 | ZN3672:PA37 | URBAN | Other | 979692 | 1 | 318.2 | 318.2 | 0.00019367 | 6.0866e-05
2013-06-07 | ZN1673:PA7 | URBAN | Equipment Failure | 979705 | 23 | 436 | 5768 | 0.0035108 | 0.0013999
2013-06-07 | ZN4545:PA42 | URBAN | Other | 979712 | 1 | 72.2333 | 72.2333 | 4.3966e-05 | 6.0866e-05
2013-06-07 | ZN3154:PA22 | URBAN | Equipment Failure | 979713 | 723 | 224 | 91922 | 0.055949 | 0.044006
2013-06-07 | 232:33413 | SHORT RURAL | Equipment Failure | 979714 | 1 | 324.0167 | 324.0167 | 0.00019722 | 6.0866e-05
2013-06-07 | 232:33413 | SHORT RURAL | Equipment Failure | 979719 | 1 | 319.3 | 319.3 | 0.00019435 | 6.0866e-05
2013-06-07 | 812:19066 | SHORT RURAL | Equipment Failure | 979730 | 39 | 115 | 4485 | 0.0027298 | 0.0023738
2013-06-07 | 214:8671 | URBAN | Other | 979792 | 1 | 56.0333 | 56.0333 | 3.4105e-05 | 6.0866e-05
2013-06-07 | 513:48056 | SHORT RURAL | Equipment Failure | 979797 | 5 | 107 | 535 | 0.00032563 | 0.00030433
2013-06-07 | 513:48059 | SHORT RURAL | Third Party Impacts | 979808 | 65 | 180 | 7710 | 0.0046928 | 0.0039563
2013-06-07 | ZN14144:PA1 | URBAN | Third Party Impacts | 979824 | 1 | 327.7 | 327.7 | 0.00019946 | 6.0866e-05
2013-06-07 | 202:34261 | SHORT RURAL | Other | 979945 | 51 | 46 | 2346 | 0.0014279 | 0.0031042
2013-06-07 | 812:19066 | SHORT RURAL | Other | 979947 | 6 | 85 | 510 | 0.00031042 | 0.0003652
2013-06-07 | 801:74120 | SHORT RURAL | Equipment Failure | 979951 | 1 | 230 | 230 | 0.00013999 | 6.0866e-05
2013-06-07 | 503:48011 | SHORT RURAL | Other | 979975 | 1 | 83.5833 | 83.5833 | 5.0874e-05 | 6.0866e-05
2013-06-07 | ZN847:PA2 | URBAN | Equipment Failure | 980020 | 1 | 391.1333 | 391.1333 | 0.00023807 | 6.0866e-05
2013-06-07 | 264:81236 | URBAN | Other | 980035 | 1 | 68.4333 | 68.4333 | 4.1653e-05 | 6.0866e-05
2013-06-07 | ZN12690:PA12 | SHORT RURAL | Other | 980060 | 1 | 875.4333 | 875.4333 | 0.00053284 | 6.0866e-05
2013-06-08 | 208:62 | URBAN | Equipment Failure | 980116 | 1 | 149.6833 | 149.6833 | 9.1106e-05 | 6.0866e-05
2013-06-08 | ZN2466:PA16 | URBAN | Equipment Failure | 981007 | 43 | 541 | 23263 | 0.014159 | 0.0026172
2013-06-08 | 513:48059 | SHORT RURAL | Equipment Failure | 981011 | 5 | 131 | 655 | 0.00039867 | 0.00030433
2013-06-08 | 258:80778 | URBAN | Other | 981013 | 1 | 857 | 857 | 0.00052162 | 6.0866e-05
2013-06-08 | ZN3472:PA31 | URBAN | Other | 981026 | 75 | 83.6 | 6270 | 0.0038163 | 0.004565
2013-06-09 | ZN847:PA10 | URBAN | Vegetation | 981028 | 1 | 144.2333 | 144.2333 | 8.7789e-05 | 6.0866e-05
2013-06-09 | ZN12610:PA16 | URBAN | Third Party Impacts | 981031 | 238 | 475 | 69115 | 0.042068 | 0.014486
2013-06-09 | 511:29878 | SHORT RURAL | Equipment Failure | 981038 | 4 | 269.5167 | 1078.0667 | 0.00065618 | 0.00024346
2013-06-08 | ZN4545:PA21 | URBAN | Equipment Failure | 981059 | 133 | 41 | 5453 | 0.003319 | 0.0080952
2013-06-08 | ZN965:PA38 | URBAN | Other | 981063 | 44 | 49 | 2156 | 0.0013123 | 0.0026781
2013-06-08 | 220:8687 | URBAN | Equipment Failure | 981068 | 59 | 256 | 15104 | 0.0091932 | 0.0035911
2013-06-07 | 238:34144 | URBAN | Equipment Failure | 981118 | 278 | 56 | 3336 | 0.0020305 | 0.016921
2013-06-09 | ZN3154:PA22 | URBAN | Equipment Failure | 981252 | 26 | 199.7667 | 5188.7667 | 0.0031582 | 0.0015825
2013-06-09 | 503:48017 | URBAN | Equipment Failure | 981264 | 21 | 60.0333 | 1011.6833 | 0.00061577 | 0.0012782
2013-06-09 | 256:80641 | URBAN | Other | 981282 | 1 | 54.2667 | 54.2667 | 3.303e-05 | 6.0866e-05
2013-06-09 | 256:80641 | URBAN | Other | 981287 | 1 | 67.15 | 67.15 | 4.0872e-05 | 6.0866e-05
2013-06-10 | ZN10995:PA6 | URBAN | Equipment Failure | 981299 | 68 | 71 | 4828 | 0.0029386 | 0.0041389
2013-06-10 | ZN1285:PA27 | URBAN | Equipment Failure | 981302 | 14 | 318 | 4452 | 0.0027098 | 0.00085213
2013-06-10 | ZN262:PA27 | URBAN | Equipment Failure | 981315 | 17 | 128.9 | 2191.3 | 0.0013338 | 0.0010347
2013-06-10 | 806:82662 | SHORT RURAL | Other | 981325 | 1 | 116 | 116 | 7.0605e-05 | 6.0866e-05
2013-06-10 | ZN965:PA20 | URBAN | Equipment Failure | 981327 | 905 | 13 | 11765 | 0.0071609 | 0.055084
2013-06-10 | ZN965:PA21 | URBAN | Equipment Failure | 981327 | 678 | 13 | 8814 | 0.0053647 | 0.041267
2013-06-10 | ZN965:PA22 | URBAN | Equipment Failure | 981327 | 570 | 13 | 7410 | 0.0045102 | 0.034694
2013-06-10 | ZN965:PA24 | SHORT RURAL | Equipment Failure | 981327 | 951 | 13 | 12363 | 0.0075249 | 0.057884
2013-06-10 | ZN965:PA26 | URBAN | Equipment Failure | 981327 | 907 | 13 | 11791 | 0.0071767 | 0.055206
2013-06-10 | 801:74121 | SHORT RURAL | Other | 981360 | 1 | 114.35 | 114.35 | 6.96e-05 | 6.0866e-05
2013-06-10 | 220:8689 | URBAN | Other | 981368 | 1 | 118.7167 | 118.7167 | 7.2258e-05 | 6.0866e-05
2013-06-10 | 222:2015 | SHORT RURAL | Equipment Failure | 981396 | 1 | 1296.8667 | 1296.8667 | 0.00078935 | 6.0866e-05
2013-06-10 | 526:34637 | SHORT RURAL | Equipment Failure | 981398 | 3 | 55.5333 | 166.6 | 0.0001014 | 0.0001826
2013-06-10 | ZN12690:PA12 | SHORT RURAL | Equipment Failure | 981405 | 1 | 316.4667 | 316.4667 | 0.00019262 | 6.0866e-05
2013-06-10 | 504:48033 | SHORT RURAL | Equipment Failure | 981407 | 1152 | 292 | 166650 | 0.10143 | 0.070118
2013-06-10 | ZN187:PA20 | URBAN | Other | 981413 | 1 | 205.8333 | 205.8333 | 0.00012528 | 6.0866e-05
2013-06-10 | ZN262:PA42 | URBAN | Other | 981416 | 1 | 263.8667 | 263.8667 | 0.00016061 | 6.0866e-05
2013-06-10 | ZN2466:PA25 | URBAN | Other | 981462 | 1 | 575.3 | 575.3 | 0.00035016 | 6.0866e-05
2013-06-11 | 235:2123 | URBAN | Other | 981466 | 1 | 375.9833 | 375.9833 | 0.00022885 | 6.0866e-05
2013-06-11 | ZN180:PA28 | URBAN | Other | 981469 | 118 | 317 | 37406 | 0.022768 | 0.0071822
2013-06-11 | ZN180:PA29 | URBAN | Other | 981469 | 2 | 317 | 634 | 0.00038589 | 0.00012173
2013-06-11 | ZN180:PA31 | URBAN | Other | 981469 | 2 | 317 | 634 | 0.00038589 | 0.00012173
2013-06-11 | 812:19065 | SHORT RURAL | Other | 981470 | 1 | 288.6667 | 288.6667 | 0.0001757 | 6.0866e-05
2013-06-11 | ZN342:PA24 | URBAN | Equipment Failure | 981490 | 1 | 326.5167 | 1631.1667 | 0.00099283 | 6.0866e-05
2013-06-11 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 981499 | 10 | 142 | 1420 | 0.0008643 | 0.00060866
2013-06-11 | 504:48026 | SHORT RURAL | Equipment Failure | 981549 | 1 | 146.0333 | 146.0333 | 8.8885e-05 | 6.0866e-05
2013-06-08 | 813:89061 | LONG RURAL | Equipment Failure | 981632 | 6 | 226 | 1210 | 0.00073648 | 0.0003652
2013-06-11 | ZN12690:PA22 | URBAN | Other | 981637 | 1 | 94.4833 | 94.4833 | 5.7508e-05 | 6.0866e-05
2013-06-11 | ZN129:PA19 | URBAN | Other | 981648 | 1 | 63.3833 | 63.3833 | 3.8579e-05 | 6.0866e-05
2013-06-11 | ZN1285:PA24 | URBAN | Vegetation | 981739 | 1 | 1433.7833 | 1433.7833 | 0.00087269 | 6.0866e-05
2013-06-11 | 511:29878 | SHORT RURAL | Equipment Failure | 981853 | 20 | 199 | 3980 | 0.0024225 | 0.0012173
2013-06-12 | ZN14891:PA8 | SHORT RURAL | Equipment Failure | 981914 | 1321 | 103 | 127974 | 0.077893 | 0.080404
2013-06-12 | 213:33771 | URBAN | Third Party Impacts | 981917 | 1 | 248.95 | 248.95 | 0.00015153 | 6.0866e-05
2013-06-12 | ZN9118:PA26 | URBAN | Other | 982064 | 1 | 266.1833 | 266.1833 | 0.00016202 | 6.0866e-05
2013-06-12 | 515:35192 | SHORT RURAL | Equipment Failure | 982086 | 158 | 1341 | 10998 | 0.0066941 | 0.0096168
2013-06-11 | ZN12660:PA14 | SHORT RURAL | Equipment Failure | 982102 | 10 | 60 | 600 | 0.0003652 | 0.00060866
2013-06-12 | 261:81885 | URBAN | Other | 982116 | 1 | 170.8833 | 170.8833 | 0.00010401 | 6.0866e-05
2013-06-12 | 801:74121 | SHORT RURAL | Other | 982153 | 8 | 126 | 903 | 0.00054962 | 0.00048693
2013-06-12 | ZN12630:PA2 | SHORT RURAL | Equipment Failure | 982155 | 1 | 266.2667 | 266.2667 | 0.00016207 | 6.0866e-05
2013-06-12 | ZN1164:PA26 | URBAN | Other | 982274 | 60 | 51.5167 | 3091 | 0.0018814 | 0.003652
2013-06-12 | 812:19072 | SHORT RURAL | Equipment Failure | 982278 | 1 | 969.4667 | 969.4667 | 0.00059008 | 6.0866e-05
2013-06-12 | 806:82662 | SHORT RURAL | Other | 982283 | 19 | 133 | 2527 | 0.0015381 | 0.0011565
2013-06-12 | ZN12630:PA2 | SHORT RURAL | Equipment Failure | 982296 | 1 | 163.7833 | 163.7833 | 9.9689e-05 | 6.0866e-05
2013-06-12 | ZN14144:PA5 | SHORT RURAL | Other | 982301 | 1 | 476.7667 | 476.7667 | 0.00029019 | 6.0866e-05
2013-06-12 | 801:74121 | SHORT RURAL | Other | 982334 | 1 | 77.9333 | 77.9333 | 4.7435e-05 | 6.0866e-05
2013-06-12 | ZN35600:PA22 | URBAN | Equipment Failure | 982360 | 82 | 71.5333 | 5865.7333 | 0.0035702 | 0.004991
2013-06-12 | ZN1287:PA21 | URBAN | Equipment Failure | 982364 | 1 | 280.6833 | 280.6833 | 0.00017084 | 6.0866e-05
2013-06-12 | 511:29878 | SHORT RURAL | Animals | 982367 | 348 | 556 | 60142 | 0.036606 | 0.021181
2013-06-12 | ZN12580:PA10 | URBAN | Animals | 982400 | 1501 | 68 | 102068 | 0.062125 | 0.09136
2013-06-13 | ZN3155:PA19 | URBAN | Equipment Failure | 982404 | 917 | 91 | 83447 | 0.050791 | 0.055814
2013-06-13 | ZN690:PA34 | URBAN | Equipment Failure | 982410 | 49 | 158.6333 | 7773.0333 | 0.0047311 | 0.0029824
2013-06-13 | ZN10990:PA1 | URBAN | Third Party Impacts | 982412 | 1 | 1467.3333 | 1467.3333 | 0.00089311 | 6.0866e-05
2013-06-12 | 806:82662 | SHORT RURAL | Equipment Failure | 982471 | 16 | 310 | 2760 | 0.0016799 | 0.00097386
2013-06-13 | ZN129:PA8 | URBAN | Equipment Failure | 982552 | 1 | 176.3 | 176.3 | 0.00010731 | 6.0866e-05
2013-06-13 | 807:74184 | SHORT RURAL | Other | 982558 | 1 | 130 | 130 | 7.9126e-05 | 6.0866e-05
2013-06-13 | ZN5868:PA2 | URBAN | Other | 982581 | 17 | 60 | 1020 | 0.00062083 | 0.0010347
2013-06-13 | ZN10991:PA5 | URBAN | Other | 982596 | 1 | 123.8667 | 123.8667 | 7.5393e-05 | 6.0866e-05
2013-06-13 | ZN5868:PA2 | URBAN | Other | 982609 | 1 | 38.1167 | 38.1167 | 2.32e-05 | 6.0866e-05
2013-06-13 | ZN188:PA25 | URBAN | Equipment Failure | 982617 | 275 | 49 | 12045 | 0.0073313 | 0.016738
2013-06-13 | ZN13000:PA1 | URBAN | Other | 982642 | 1 | 28.3 | 28.3 | 1.7225e-05 | 6.0866e-05
2013-06-13 | 807:74184 | SHORT RURAL | Equipment Failure | 982684 | 1 | 79.5 | 79.5 | 4.8389e-05 | 6.0866e-05
2013-06-13 | ZN187:PA28 | URBAN | Other | 982712 | 12 | 80 | 954 | 0.00058066 | 0.00073039
2013-06-13 | ZN2196:PA4 | URBAN | Third Party Impacts | 982718 | 1 | 1186.2167 | 1186.2167 | 0.000722 | 6.0866e-05
2013-06-13 | ZN2196:PA4 | URBAN | Third Party Impacts | 982733 | 1 | 1173.9667 | 1173.9667 | 0.00071455 | 6.0866e-05
2013-06-13 | 813:89062 | SHORT RURAL | Equipment Failure | 982736 | 1 | 2181 | 8439 | 0.0051365 | 6.0866e-05
2013-06-13 | 261:81882 | URBAN | Equipment Failure | 982756 | 1 | 102.4333 | 102.4333 | 6.2347e-05 | 6.0866e-05
2013-06-13 | 214:8666 | URBAN | Other | 982758 | 1 | 68.6167 | 68.6167 | 4.1764e-05 | 6.0866e-05
2013-06-13 | ZN9900:PA19 | URBAN | Vegetation | 982820 | 705 | 433 | 88048 | 0.053591 | 0.042911
2013-06-13 | ZN847:PA18 | URBAN | Vegetation | 982836 | 42 | 371.5 | 15603 | 0.0094969 | 0.0025564
2013-06-13 | 239:82129 | SHORT RURAL | Other | 982842 | 98 | 81.9167 | 8027.8333 | 0.0048862 | 0.0059649
2013-06-14 | ZN10991:PA12 | URBAN | Equipment Failure | 982863 | 37 | 123.15 | 4556.55 | 0.0027734 | 0.002252
2013-06-08 | ZN690:PA35 | URBAN | Equipment Failure | 982872 | 86 | 78 | 6708 | 0.0040829 | 0.0052345
2013-06-14 | ZN10999:PA36 | URBAN | Equipment Failure | 982954 | 1 | 317.8167 | 317.8167 | 0.00019344 | 6.0866e-05
2013-06-14 | ZN1164:PA27 | URBAN | Equipment Failure | 982963 | 8 | 181.85 | 1454.8 | 0.00088548 | 0.00048693
2013-06-14 | ZN35370:PA8 | SHORT RURAL | Equipment Failure | 982989 | 1 | 231.8 | 231.8 | 0.00014109 | 6.0866e-05
2013-06-14 | 512:48046 | SHORT RURAL | Equipment Failure | 982990 | 5 | 501.9667 | 2509.8333 | 0.0015276 | 0.00030433
2013-06-14 | ZN12610:PA2 | URBAN | Equipment Failure | 983021 | 1 | 4063.6667 | 4063.6667 | 0.0024734 | 6.0866e-05
2013-06-14 | ZN12630:PA1 | SHORT RURAL | Vegetation | 983024 | 368 | 24.2 | 8905.6 | 0.0054205 | 0.022399
2013-06-14 | ZN14143:PA17 | SHORT RURAL | Vegetation | 983067 | 1 | 121.1667 | 121.1667 | 7.3749e-05 | 6.0866e-05
2013-06-14 | ZN2568:PA29 | URBAN | Equipment Failure | 983106 | 19 | 82 | 1558 | 0.00094829 | 0.0011565
2013-06-14 | ZN384:PA37 | URBAN | Equipment Failure | 983106 | 167 | 82 | 13694 | 0.008335 | 0.010165
2013-06-14 | ZN1164:PA27 | URBAN | Equipment Failure | 983107 | 8 | 94.5 | 756 | 0.00046015 | 0.00048693
2013-06-14 | ZN12630:PA4 | SHORT RURAL | Equipment Failure | 983193 | 6 | 112 | 672 | 0.00040902 | 0.0003652
2013-06-15 | 807:74184 | SHORT RURAL | Equipment Failure | 983222 | 63 | 193 | 6281 | 0.003823 | 0.0038346
2013-06-15 | ZN15012:PA8 | URBAN | Vegetation | 983271 | 40 | 143.55 | 5742 | 0.0034949 | 0.0024346
2013-06-15 | 258:80793 | SHORT RURAL | Other | 983294 | 1 | 93.9667 | 93.9667 | 5.7194e-05 | 6.0866e-05
2013-06-15 | ZN12610:PA10 | SHORT RURAL | Equipment Failure | 983329 | 1841 | 70 | 126893 | 0.077235 | 0.11205
2013-06-15 | ZN12610:PA18 | URBAN | Equipment Failure | 983329 | 90 | 70 | 6030 | 0.0036702 | 0.0054779
2013-06-16 | 224:80344 | URBAN | Other | 983335 | 1 | 117.8833 | 117.8833 | 7.1751e-05 | 6.0866e-05
2013-06-16 | ZN116:PA32 | URBAN | Equipment Failure | 983337 | 60 | 415.8 | 24851.8333 | 0.015126 | 0.003652
2013-06-16 | 526:34636 | SHORT RURAL | Equipment Failure | 983377 | 1 | 70.1667 | 70.1667 | 4.2708e-05 | 6.0866e-05
2013-06-16 | ZN12570:PA39 | URBAN | Equipment Failure | 983378 | 1 | 253.6333 | 253.6333 | 0.00015438 | 6.0866e-05
2013-06-16 | ZN12690:PA19 | URBAN | Other | 983393 | 1 | 49.7 | 49.7 | 3.025e-05 | 6.0866e-05
2013-06-16 | ZN12630:PA2 | SHORT RURAL | Vegetation | 983397 | 1 | 323.6 | 323.6 | 0.00019696 | 6.0866e-05
2013-06-16 | ZN12640:PA2 | URBAN | Other | 983403 | 1 | 44.8333 | 44.8333 | 2.7288e-05 | 6.0866e-05
2013-06-16 | ZN12690:PA8 | URBAN | Equipment Failure | 983409 | 1 | 217.4333 | 217.4333 | 0.00013234 | 6.0866e-05
2013-06-16 | ZN14144:PA1 | URBAN | Other | 983412 | 1 | 473.1333 | 473.1333 | 0.00028798 | 6.0866e-05
2013-06-16 | ZN2835:PA9 | URBAN | Equipment Failure | 983415 | 124 | 83.75 | 10385 | 0.0063209 | 0.0075474
2013-06-16 | 208:56 | URBAN | Equipment Failure | 983422 | 145 | 71.4833 | 10365.0833 | 0.0063088 | 0.0088256
2013-06-16 | 803:74007 | SHORT RURAL | Equipment Failure | 983430 | 1 | 922.5333 | 922.5333 | 0.00056151 | 6.0866e-05
2013-06-16 | ZN2602:PA31 | URBAN | Equipment Failure | 983442 | 97 | 171.6667 | 16325.3333 | 0.0099366 | 0.005904
2013-06-17 | 512:48046 | SHORT RURAL | Equipment Failure | 983471 | 105 | 76.6667 | 8050 | 0.0048997 | 0.0063909
2013-06-17 | 228:7487 | URBAN | Vegetation | 983481 | 1 | 83.2833 | 83.2833 | 5.0691e-05 | 6.0866e-05
2013-06-13 | 801:74123 | SHORT RURAL | Equipment Failure | 983493 | 2 | 95 | 190 | 0.00011565 | 0.00012173
2013-06-17 | ZN2635:PA21 | URBAN | Third Party Impacts | 983519 | 1 | 185.65 | 185.65 | 0.000113 | 6.0866e-05
2013-06-17 | ZN2635:PA17 | URBAN | Vegetation | 983521 | 54 | 57 | 3078 | 0.0018735 | 0.0032868
2013-06-17 | ZN630:PA32 | URBAN | Equipment Failure | 983538 | 212 | 76 | 15813 | 0.0096248 | 0.012904
2013-06-17 | ZN3288:PA41 42KLM | CBD | Other | 983544 | 28 | 56.5333 | 1582.9333 | 0.00096347 | 0.0017043
2013-06-17 | ZN14892:PA13 | URBAN | Other | 983600 | 1 | 1264.0167 | 1264.0167 | 0.00076936 | 6.0866e-05
2013-06-17 | 256:80646 | URBAN | Other | 983658 | 1 | 253.8667 | 253.8667 | 0.00015452 | 6.0866e-05
2013-06-17 | 512:48049 | SHORT RURAL | Equipment Failure | 983760 | 4 | 158 | 632 | 0.00038467 | 0.00024346
2013-06-17 | ZN15008:PA7 | URBAN | Equipment Failure | 983858 | 73 | 59.1 | 4314.3 | 0.0026259 | 0.0044432
2013-06-17 | 813:89059 | URBAN | Other | 983865 | 1 | 924.45 | 924.45 | 0.00056268 | 6.0866e-05
2013-06-17 | ZN1290:PA4 | URBAN | Other | 983875 | 30 | 125.6667 | 3770 | 0.0022947 | 0.001826
2013-06-18 | 511:29878 | SHORT RURAL | Vegetation | 983945 | 2 | 253 | 506 | 0.00030798 | 0.00012173
2013-06-18 | ZN12640:PA13 | SHORT RURAL | Other | 983960 | 1 | 240.6667 | 240.6667 | 0.00014648 | 6.0866e-05
2013-06-18 | 213:33775 | URBAN | Equipment Failure | 984005 | 26 | 57.1833 | 1486.7667 | 0.00090494 | 0.0015825
2013-06-18 | ZN1850:PA14 | URBAN | Equipment Failure | 984059 | 1 | 179.6333 | 179.6333 | 0.00010934 | 6.0866e-05
2013-06-18 | ZN129:PA24 | URBAN | Equipment Failure | 984114 | 1 | 503.5667 | 503.5667 | 0.0003065 | 6.0866e-05
2013-06-18 | ZN1193:PA28 | URBAN | Other | 984133 | 1 | 362.5 | 362.5 | 0.00022064 | 6.0866e-05
2013-06-18 | ZN342:PA21 | URBAN | Equipment Failure | 984143 | 1 | 106 | 58 | 3.5302e-05 | 6.0866e-05
2013-06-18 | ZN342:PA26 | URBAN | Equipment Failure | 984143 | 4547 | 106 | 162795 | 0.099087 | 0.27676
2013-06-18 | ZN965:PA47 | URBAN | Weather | 984155 | 23 | 189.5 | 4358.5 | 0.0026528 | 0.0013999
2013-06-19 | ZN35370:PA10 | SHORT RURAL | Equipment Failure | 984247 | 1 | 112 | 112 | 6.817e-05 | 6.0866e-05
2013-06-18 | 235:2124 | URBAN | Other | 984266 | 1 | 137.9333 | 137.9333 | 8.3955e-05 | 6.0866e-05
2013-06-18 | ZN12600:PA2 | SHORT RURAL | Equipment Failure | 984270 | 11 | 42.9 | 471.9 | 0.00028723 | 0.00066953
2013-06-18 | ZN262:PA16 | URBAN | Other | 984272 | 1 | 68.1333 | 68.1333 | 4.147e-05 | 6.0866e-05
2013-06-18 | 232:33413 | SHORT RURAL | Other | 984279 | 155 | 109.4 | 16957 | 0.010321 | 0.0094342
2013-06-18 | 223:14397 | URBAN | Third Party Impacts | 984283 | 21 | 10 | 210 | 0.00012782 | 0.0012782
2013-06-18 | 227:13015 | SHORT RURAL | Other | 984293 | 10 | 87.5167 | 875.1667 | 0.00053268 | 0.00060866
2013-06-18 | 240:34843 | URBAN | Other | 984297 | 1 | 85.95 | 85.95 | 5.2314e-05 | 6.0866e-05
2013-06-19 | 225:33670 | SHORT RURAL | Animals | 984305 | 61 | 56 | 3416 | 0.0020792 | 0.0037128
2013-06-19 | ZN262:PA17 | URBAN | Weather | 984307 | 83 | 373.4667 | 30997.7333 | 0.018867 | 0.0050519
2013-06-19 | ZN2310:PA27 | URBAN | Equipment Failure | 984308 | 1 | 1724.9 | 1724.9 | 0.0010499 | 6.0866e-05
2013-06-19 | ZN2835:PA19 | URBAN | Other | 984338 | 1 | 238.4 | 238.4 | 0.0001451 | 6.0866e-05
2013-06-19 | ZN384:PA4 | URBAN | Equipment Failure | 984342 | 87 | 78 | 6786 | 0.0041304 | 0.0052953
2013-06-19 | ZN384:PA9 | URBAN | Equipment Failure | 984342 | 2 | 78 | 156 | 9.4951e-05 | 0.00012173
2013-06-19 | ZN12650:PA9 | URBAN | Equipment Failure | 984361 | 78 | 108.4667 | 8460.4 | 0.0051495 | 0.0047476
2013-06-19 | ZN35500:PA16 | URBAN | Vegetation | 984394 | 354 | 94 | 23718 | 0.014436 | 0.021547
2013-06-19 | ZN4545:PA24 | URBAN | Vegetation | 984394 | 535 | 94 | 50290 | 0.03061 | 0.032563
2013-06-19 | ZN12650:PA1 | SHORT RURAL | Vegetation | 984432 | 44 | 303 | 11715 | 0.0071305 | 0.0026781
2013-06-19 | ZN80:PA30 | URBAN | Equipment Failure | 984529 | 1 | 4194.6667 | 4194.6667 | 0.0025531 | 6.0866e-05
2013-06-19 | 513:48059 | SHORT RURAL | Equipment Failure | 984534 | 1 | 99.1333 | 99.1333 | 6.0339e-05 | 6.0866e-05
2013-06-19 | 238:34141 | SHORT RURAL | Equipment Failure | 984550 | 13 | 358.2333 | 4657.0333 | 0.0028346 | 0.00079126
2013-06-19 | ZN3472:PA33 | URBAN | Equipment Failure | 984555 | 1 | 163.6 | 163.6 | 9.9577e-05 | 6.0866e-05
2013-06-19 | ZN15006:PA15 | URBAN | Equipment Failure | 984695 | 113 | 110.3833 | 12473.3167 | 0.007592 | 0.0068779
2013-06-20 | ZN12610:PA18 | URBAN | Other | 984707 | 28 | 60.2167 | 1686.0667 | 0.0010262 | 0.0017043
2013-06-20 | ZN80:PA27 | URBAN | Vegetation | 984710 | 1 | 130.2167 | 130.2167 | 7.9258e-05 | 6.0866e-05
2013-06-20 | ZN384:PA42 | URBAN | Equipment Failure | 984716 | 2 | 104 | 208 | 0.0001266 | 0.00012173
2013-06-20 | ZN5868:PA2 | URBAN | Other | 984732 | 6 | 136 | 816 | 0.00049667 | 0.0003652
2013-06-19 | 216:10723 | URBAN | Other | 984752 | 704 | 30 | 21120 | 0.012855 | 0.04285
2013-06-19 | 216:10724 | SHORT RURAL | Other | 984752 | 792 | 30 | 23760 | 0.014462 | 0.048206
2013-06-19 | 216:10726 | URBAN | Other | 984752 | 761 | 30 | 22830 | 0.013896 | 0.046319
2013-06-19 | 216:10727 | URBAN | Other | 984752 | 1492 | 30 | 44760 | 0.027244 | 0.090812
2013-06-19 | 216:10728 | URBAN | Other | 984752 | 793 | 30 | 23790 | 0.01448 | 0.048267
2013-06-19 | 216:10729 | URBAN | Other | 984752 | 1018 | 30 | 30540 | 0.018589 | 0.061962
2013-06-20 | ZN35500:PA22 | URBAN | Equipment Failure | 984838 | 1 | 195.7 | 195.7 | 0.00011911 | 6.0866e-05
2013-06-20 | ZN15014:PA19 | URBAN | Equipment Failure | 984842 | 1 | 668.2667 | 668.2667 | 0.00040675 | 6.0866e-05
2013-06-20 | 238:34141 | SHORT RURAL | Equipment Failure | 984924 | 29 | 260 | 7540 | 0.0045893 | 0.0017651
2013-06-20 | ZN14144:PA10 | SHORT RURAL | Other | 984995 | 1 | 127.9833 | 127.9833 | 7.7898e-05 | 6.0866e-05
2013-06-20 | 510:48164 | SHORT RURAL | Equipment Failure | 985011 | 1 | 177 | 177 | 0.00010773 | 6.0866e-05
2013-06-20 | 507:80922 | SHORT RURAL | Third Party Impacts | 985016 | 1 | 65 | 65 | 3.9563e-05 | 6.0866e-05
2013-06-20 | 509:48040 | SHORT RURAL | Equipment Failure | 985034 | 1 | 275 | 275 | 0.00016738 | 6.0866e-05
2013-06-20 | ZN269:PA7 | URBAN | Vegetation | 985046 | 1 | 240.8833 | 240.8833 | 0.00014662 | 6.0866e-05
2013-06-21 | ZN965:PA46 | URBAN | Other | 985069 | 51 | 61 | 3111 | 0.0018935 | 0.0031042
2013-06-21 | ZN15008:PA7 | URBAN | Equipment Failure | 985085 | 61 | 136 | 8254 | 0.0050239 | 0.0037128
2013-06-21 | ZN690:PA27 | URBAN | Equipment Failure | 985091 | 15 | 523 | 7803 | 0.0047494 | 0.00091299
2013-06-21 | ZN690:PA5 | URBAN | Equipment Failure | 985091 | 538 | 523 | 29610 | 0.018022 | 0.032746
2013-06-17 | ZN12630:PA4 | SHORT RURAL | Equipment Failure | 985157 | 1 | 50 | 50 | 3.0433e-05 | 6.0866e-05
2013-06-21 | 801:74122 | URBAN | Other | 985213 | 1 | 62.25 | 62.25 | 3.7889e-05 | 6.0866e-05
2013-06-21 | ZN3922:PA13 | URBAN | Equipment Failure | 985273 | 1 | 4434.2 | 4434.2 | 0.0026989 | 6.0866e-05
2013-06-21 | ZN3472:PA29 | URBAN | Third Party Impacts | 985351 | 1 | 413.35 | 413.35 | 0.00025159 | 6.0866e-05
2013-06-21 | ZN187:PA17 | URBAN | Vegetation | 985359 | 30 | 10 | 9734 | 0.0059247 | 0.001826
2013-06-21 | ZN1850:PA10 | URBAN | Equipment Failure | 985401 | 1 | 457.0333 | 457.0333 | 0.00027818 | 6.0866e-05
2013-06-21 | 243:80084 | SHORT RURAL | Other | 985405 | 1 | 137.1 | 137.1 | 8.3447e-05 | 6.0866e-05
2013-06-21 | 227:13015 | SHORT RURAL | Other | 985413 | 1 | 517 | 517 | 0.00031468 | 6.0866e-05
2013-06-22 | 507:80932 | SHORT RURAL | Other | 985436 | 20 | 93 | 1860 | 0.0011321 | 0.0012173
2013-06-21 | ZN931:PA3 | URBAN | Equipment Failure | 985441 | 87 | 511 | 44457 | 0.027059 | 0.0052953
2013-06-22 | ZN931:PA3 | URBAN | Equipment Failure | 985443 | 87 | 310 | 26970 | 0.016416 | 0.0052953
2013-06-22 | ZN1164:PA26 | URBAN | Equipment Failure | 985452 | 60 | 846.3333 | 50780 | 0.030908 | 0.003652
2013-06-22 | 510:48164 | SHORT RURAL | Equipment Failure | 985463 | 1 | 381.2167 | 381.2167 | 0.00023203 | 6.0866e-05
2013-06-22 | 501:48122 | SHORT RURAL | Other | 985482 | 1 | 85 | 85 | 5.1736e-05 | 6.0866e-05
2013-06-22 | 515:35192 | SHORT RURAL | Equipment Failure | 985513 | 1 | 159 | 159 | 9.6777e-05 | 6.0866e-05
2013-06-22 | ZN9252:PA10 | URBAN | Other | 985554 | 1 | 262.0833 | 262.0833 | 0.00015952 | 6.0866e-05
2013-06-22 | ZN3154:PA11 | URBAN | Other | 985564 | 46 | 62.3167 | 570350.9333 | 0.34715 | 0.0027998
2013-06-22 | 205:12210 | URBAN | Other | 985568 | 114 | 31.5167 | 3592.9 | 0.0021869 | 0.0069387
2013-06-22 | ZN12620:PA11 | SHORT RURAL | Equipment Failure | 985583 | 15 | 125 | 1875 | 0.0011412 | 0.00091299
2013-06-22 | ZN2602:PA34 | URBAN | Other | 985584 | 2 | 85 | 170 | 0.00010347 | 0.00012173
2013-06-22 | ZN7481:PA1 | URBAN | Equipment Failure | 985588 | 1 | 1111.0667 | 1111.0667 | 0.00067626 | 6.0866e-05
2013-06-22 | ZN116:PA35 | URBAN | Other | 985594 | 53 | 67 | 3551 | 0.0021614 | 0.0032259
2013-06-23 | ZN116:PA35 | URBAN | Equipment Failure | 985601 | 53 | 93 | 4929 | 0.0030001 | 0.0032259
2013-06-23 | ZN9252:PA4 | URBAN | Vegetation | 985605 | 54 | 212 | 11448 | 0.0069679 | 0.0032868
2013-06-23 | ZN14892:PA6 | SHORT RURAL | Equipment Failure | 985614 | 16 | 61.4333 | 982.9333 | 0.00059827 | 0.00097386
2013-06-23 | ZN195:PA9 | URBAN | Other | 985625 | 1 | 229.8 | 229.8 | 0.00013987 | 6.0866e-05
2013-06-23 | ZN14891:PA12 | SHORT RURAL | Other | 985642 | 10 | 68 | 680 | 0.00041389 | 0.00060866
2013-06-23 | 810:74058 | SHORT RURAL | Other | 985648 | 2 | 78 | 156 | 9.4951e-05 | 0.00012173
2013-06-23 | ZN9245:PA10 | URBAN | Equipment Failure | 985650 | 1 | 3126.6833 | 3126.6833 | 0.0019031 | 6.0866e-05
2013-06-23 | ZN14891:PA12 | SHORT RURAL | Other | 985651 | 1 | 130.2833 | 130.2833 | 7.9298e-05 | 6.0866e-05
2013-06-23 | ZN187:PA24 | URBAN | Other | 985670 | 20 | 175 | 3500 | 0.0021303 | 0.0012173
2013-06-23 | 513:48052 | URBAN | Equipment Failure | 985674 | 525 | 265.5 | 67767 | 0.041247 | 0.031955
2013-06-23 | 513:48058 | URBAN | Equipment Failure | 985674 | 1 | 265.5 | 242.5 | 0.0001476 | 6.0866e-05
2013-06-23 | ZN3922:PA5 | URBAN | Equipment Failure | 985694 | 2319 | 144 | 278539 | 0.16954 | 0.14115
2013-06-23 | 258:80773 | URBAN | Other | 985702 | 1 | 159.3667 | 159.3667 | 9.7e-05 | 6.0866e-05
2013-06-23 | 807:74184 | SHORT RURAL | Animals | 985704 | 1 | 149 | 149 | 9.069e-05 | 6.0866e-05
2013-06-23 | ZN187:PA28 | URBAN | Equipment Failure | 985705 | 2 | 963 | 1926 | 0.0011723 | 0.00012173
2013-06-23 | 230:81440 | URBAN | Vegetation | 985711 | 1 | 168.2667 | 168.2667 | 0.00010242 | 6.0866e-05
2013-06-23 | 213:33771 | URBAN | Equipment Failure | 985715 | 1504 | 256 | 209229 | 0.12735 | 0.091543
2013-06-23 | ZN35370:PA8 | SHORT RURAL | Equipment Failure | 985722 | 1 | 1394.25 | 1394.25 | 0.00084863 | 6.0866e-05
2013-06-23 | ZN901:PA13 | URBAN | Equipment Failure | 985723 | 1691 | 33 | 55803 | 0.033965 | 0.10292
2013-06-23 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 985728 | 1 | 321.9833 | 321.9833 | 0.00019598 | 6.0866e-05
2013-06-23 | ZN1068:PA26 | URBAN | Other | 985733 | 1 | 188.3833 | 188.3833 | 0.00011466 | 6.0866e-05
2013-06-23 | 515:35197 | LONG RURAL | Equipment Failure | 985759 | 2 | 111 | 222 | 0.00013512 | 0.00012173
2013-06-23 | ZN2568:PA39 | URBAN | Other | 985766 | 1 | 64.6167 | 64.6167 | 3.933e-05 | 6.0866e-05
2013-06-23 | ZN12620:PA11 | SHORT RURAL | Equipment Failure | 985767 | 59 | 280.0333 | 16521.9667 | 0.010056 | 0.0035911
2013-06-23 | ZN15011:PA2 | URBAN | Equipment Failure | 985777 | 747 | 36 | 26892 | 0.016368 | 0.045467
2013-06-23 | ZN10999:PA24 | URBAN | Vegetation | 985781 | 76 | 273.45 | 20782.2 | 0.012649 | 0.0046258
2013-06-23 | ZN5868:PA30 | URBAN | Equipment Failure | 985784 | 99 | 40 | 3960 | 0.0024103 | 0.0060257
2013-06-23 | ZN129:PA28 | URBAN | Equipment Failure | 985800 | 1 | 1110.85 | 1110.85 | 0.00067613 | 6.0866e-05
2013-06-23 | ZN1164:PA15 | URBAN | Other | 985809 | 4 | 95 | 380 | 0.00023129 | 0.00024346
2013-06-23 | ZN1164:PA4 | URBAN | Other | 985809 | 206 | 95 | 19570 | 0.011911 | 0.012538
2013-06-23 | ZN180:PA35 | URBAN | Equipment Failure | 985812 | 99 | 83.9833 | 8314.35 | 0.0050606 | 0.0060257
2013-06-23 | ZN1285:PA22 | URBAN | Equipment Failure | 985815 | 55 | 147 | 8085 | 0.004921 | 0.0033476
2013-06-23 | ZN187:PA13 | URBAN | Equipment Failure | 985822 | 159 | 76 | 12084 | 0.0073551 | 0.0096777
2013-06-23 | ZN1648:PA16 | URBAN | Equipment Failure | 985844 | 74 | 74.55 | 5516.7 | 0.0033578 | 0.0045041
2013-06-23 | ZN1850:PA14 | URBAN | Equipment Failure | 985851 | 27 | 162.9333 | 4291.6667 | 0.0026122 | 0.0016434
2013-06-23 | ZN965:PA38 | URBAN | Equipment Failure | 985854 | 44 | 94.2333 | 4146.2667 | 0.0025237 | 0.0026781
2013-06-24 | ZN116:PA50 | URBAN | Other | 985862 | 1 | 3281.5333 | 3281.5333 | 0.0019973 | 6.0866e-05
2013-06-24 | ZN965:PA38 | URBAN | Equipment Failure | 985864 | 44 | 831.3167 | 36577.9333 | 0.022264 | 0.0026781
2013-06-24 | ZN180:PA19 | URBAN | Equipment Failure | 985867 | 1 | 994.7333 | 157 | 9.556e-05 | 6.0866e-05
2013-06-24 | ZN180:PA23 | URBAN | Equipment Failure | 985867 | 34 | 994.7333 | 26866.8 | 0.016353 | 0.0020694
2013-06-24 | ZN180:PA27 | URBAN | Equipment Failure | 985867 | 77 | 994.7333 | 34750.1 | 0.021151 | 0.0046867
2013-06-24 | ZN180:PA29 | URBAN | Equipment Failure | 985867 | 43 | 994.7333 | 10869.6833 | 0.006616 | 0.0026172
2013-06-24 | ZN9700:PA11 | URBAN | Equipment Failure | 985870 | 1934 | 76 | 111796 | 0.068046 | 0.11772
2013-06-24 | ZN2602:PA27 | URBAN | Equipment Failure | 985874 | 39 | 225.0167 | 8775.65 | 0.0053414 | 0.0023738
2013-06-24 | ZN10999:PA24 | URBAN | Equipment Failure | 985875 | 97 | 143.65 | 13934.05 | 0.0084811 | 0.005904
2013-06-24 | ZN2602:PA15 | URBAN | Other | 985887 | 50 | 105.1 | 5255 | 0.0031985 | 0.0030433
2013-06-24 | ZN72:PA14 | URBAN | Vegetation | 985898 | 1 | 200.4333 | 200.4333 | 0.000122 | 6.0866e-05
2013-06-24 | ZN1850:PA14 | URBAN | Equipment Failure | 985914 | 27 | 125 | 3366.3333 | 0.002049 | 0.0016434
2013-06-21 | ZN12690:PA7 | SHORT RURAL | Equipment Failure | 985930 | 8 | 47 | 376 | 0.00022886 | 0.00048693
2013-06-24 | ZN1287:PA6 | URBAN | Equipment Failure | 985952 | 1 | 152.0167 | 152.0167 | 9.2527e-05 | 6.0866e-05
2013-06-22 | ZN931:PA3 | URBAN | Equipment Failure | 985997 | 87 | 195 | 16965 | 0.010326 | 0.0052953
2013-06-24 | ZN2602:PA27 | URBAN | Equipment Failure | 986045 | 39 | 480.6833 | 18746.65 | 0.01141 | 0.0023738
2013-06-21 | 807:74180 | SHORT RURAL | Other | 986059 | 2 | 60 | 120 | 7.3039e-05 | 0.00012173
2013-06-24 | ZN129:PA5 | URBAN | Other | 986143 | 1 | 9968.15 | 9968.15 | 0.0060672 | 6.0866e-05
2013-06-24 | ZN12660:PA10 | SHORT RURAL | Equipment Failure | 986150 | 1 | 525.9333 | 525.9333 | 0.00032012 | 6.0866e-05
2013-06-24 | ZN1648:PA16 | URBAN | Other | 986164 | 74 | 74.6667 | 5525.3333 | 0.0033631 | 0.0045041
2013-06-24 | ZN4545:PA41 | URBAN | Equipment Failure | 986187 | 2370 | 148 | 309703 | 0.1885 | 0.14425
2013-06-24 | 516:48066 | SHORT RURAL | Equipment Failure | 986190 | 1 | 73.2 | 73.2 | 4.4554e-05 | 6.0866e-05
2013-06-24 | ZN15012:PA2 | URBAN | Equipment Failure | 986214 | 42 | 145 | 6090 | 0.0037067 | 0.0025564
2013-06-24 | ZN15010:PA9 | SHORT RURAL | Vegetation | 986276 | 8 | 200.2167 | 1601.7333 | 0.00097491 | 0.00048693
2013-06-24 | ZN1850:PA14 | URBAN | Equipment Failure | 986322 | 27 | 74.15 | 1966.5 | 0.0011969 | 0.0016434
2013-06-24 | ZN2196:PA21 | URBAN | Equipment Failure | 986332 | 46 | 86 | 3956 | 0.0024079 | 0.0027998
2013-06-24 | ZN398:PA16 | URBAN | Other | 986389 | 59 | 107.0833 | 6317.9167 | 0.0038455 | 0.0035911
2013-06-24 | ZN711:PA21 | URBAN | Other | 986400 | 1137 | 38 | 35128 | 0.021381 | 0.069205
2013-06-24 | ZN3154:PA5 | URBAN | Vegetation | 986415 | 38 | 60.4333 | 2296.4667 | 0.0013978 | 0.0023129
2013-06-24 | ZN847:PA1 | URBAN | Vegetation | 986417 | 20 | 140 | 2800 | 0.0017043 | 0.0012173
2013-06-24 | 513:48059 | SHORT RURAL | Other | 986426 | 5 | 84 | 420 | 0.00025564 | 0.00030433
2013-06-24 | ZN35800:PA16 | URBAN | Equipment Failure | 986428 | 1 | 284 | 284 | 0.00017286 | 6.0866e-05
2013-06-24 | ZN35800:PA2 | URBAN | Equipment Failure | 986428 | 14 | 284 | 3976 | 0.00242 | 0.00085213
2013-06-25 | ZN9037:PA16 | URBAN | Vegetation | 986432 | 166 | 197 | 6142 | 0.0037384 | 0.010104
2013-06-25 | ZN9037:PA8 | URBAN | Vegetation | 986432 | 1642 | 197 | 71474 | 0.043503 | 0.099942
2013-06-25 | ZN10994:PA4 | URBAN | Equipment Failure | 986440 | 1682 | 299 | 365823 | 0.22266 | 0.10238
2013-06-25 | 502:48010 | SHORT RURAL | Third Party Impacts | 986444 | 24 | 130 | 3120 | 0.001899 | 0.0014608
2013-06-25 | ZN10994:PA20 | URBAN | Other | 986448 | 106 | 186.6333 | 19783.1333 | 0.012041 | 0.0064518
2013-06-25 | ZN5868:PA2 | URBAN | Equipment Failure | 986449 | 6 | 184 | 1104 | 0.00067196 | 0.0003652
2013-06-25 | ZN3155:PA44 | URBAN | Equipment Failure | 986459 | 1 | 195.1167 | 195.1167 | 0.00011876 | 6.0866e-05
2013-06-25 | 813:89061 | LONG RURAL | Equipment Failure | 986481 | 1 | 175.3 | 175.3 | 0.0001067 | 6.0866e-05
2013-06-25 | ZN12640:PA2 | URBAN | Other | 986487 | 1 | 108.3333 | 108.3333 | 6.5938e-05 | 6.0866e-05
2013-06-25 | ZN2196:PA25 | URBAN | Other | 986530 | 1715 | 79 | 107237 | 0.065271 | 0.10439
2013-06-23 | ZN15008:PA9 | URBAN | Equipment Failure | 986561 | 1192 | 5 | 5960 | 0.0036276 | 0.072552
2013-06-24 | ZN398:PA24 | URBAN | Operational Error | 986566 | 1931 | 2 | 3862 | 0.0023506 | 0.11753
2013-06-24 | ZN398:PA26 | URBAN | Operational Error | 986566 | 1081 | 2 | 2162 | 0.0013159 | 0.065796
2013-06-24 | ZN398:PA29 | URBAN | Operational Error | 986566 | 769 | 2 | 1538 | 0.00093612 | 0.046806
2013-06-24 | ZN398:PA30 | URBAN | Operational Error | 986566 | 1419 | 2 | 2838 | 0.0017274 | 0.086369
2013-06-24 | ZN398:PA31 | URBAN | Operational Error | 986566 | 651 | 2 | 1302 | 0.00079248 | 0.039624
2013-06-24 | 202:34231 37 42 | URBAN | Other | 986632 | 5 | 913 | 4565 | 0.0027785 | 0.00030433
2013-06-25 | ZN180:PA35 | URBAN | Third Party Impacts | 986650 | 1 | 1316.1667 | 1316.1667 | 0.0008011 | 6.0866e-05
2013-06-25 | ZN35600:PA9 | URBAN | Other | 986659 | 1 | 474.7333 | 474.7333 | 0.00028895 | 6.0866e-05
2013-06-25 | 242:81538 | URBAN | Other | 986674 | 1 | 132 | 132 | 8.0343e-05 | 6.0866e-05
2013-06-25 | ZN9301:PA13 | SHORT RURAL | Third Party Impacts | 986685 | 21 | 57 | 1197 | 0.00072857 | 0.0012782
2013-06-25 | ZN12580:PA4 | URBAN | Equipment Failure | 986709 | 1636 | 57 | 60849 | 0.037036 | 0.099577
2013-06-25 | ZN847:PA5 | URBAN | Vegetation | 986750 | 42 | 117 | 4914 | 0.002991 | 0.0025564
2013-06-25 | ZN129:PA5 | URBAN | Other | 986799 | 1 | 137.0167 | 137.0167 | 8.3397e-05 | 6.0866e-05
2013-06-25 | ZN116:PA35 | URBAN | Operational Error | 986847 | 50 | 2 | 100 | 6.0866e-05 | 0.0030433
2013-06-25 | ZN1788:PA8 | URBAN | Other | 986852 | 85 | 10 | 850 | 0.00051736 | 0.0051736
2013-06-25 | ZN965:PA47 | URBAN | Other | 986904 | 86 | 163 | 14018 | 0.0085322 | 0.0052345
2013-06-25 | ZN9900:PA6 | URBAN | Equipment Failure | 986939 | 5 | 1380.1667 | 6900.8333 | 0.0042003 | 0.00030433
2013-06-25 | ZN15014:PA19 | URBAN | Equipment Failure | 986953 | 32 | 150.4167 | 4813.3333 | 0.0029297 | 0.0019477
2013-06-25 | 812:19072 | SHORT RURAL | Other | 986955 | 1 | 186.2333 | 186.2333 | 0.00011335 | 6.0866e-05
2013-06-25 | 206:34432 | URBAN | Equipment Failure | 986962 | 21 | 316.0667 | 6637.4 | 0.0040399 | 0.0012782
2013-06-25 | 242:81541 | URBAN | Other | 986970 | 119 | 40.6333 | 4835.3667 | 0.0029431 | 0.0072431
2013-06-25 | ZN180:PA42 | URBAN | Other | 986971 | 257 | 855.1 | 219022.75 | 0.13331 | 0.015643
2013-06-25 | ZN9252:PA8 | URBAN | Vegetation | 986984 | 49 | 105 | 5145 | 0.0031316 | 0.0029824
2013-06-25 | 217:33610 | URBAN | Other | 986991 | 62 | 42 | 2604 | 0.001585 | 0.0037737
2013-06-26 | ZN14892:PA9 | URBAN | Third Party Impacts | 987023 | 1 | 112.15 | 112.15 | 6.8261e-05 | 6.0866e-05
2013-06-26 | ZN10994:PA2 | URBAN | Equipment Failure | 987034 | 2268 | 213 | 218471 | 0.13297 | 0.13804
2013-06-26 | ZN10994:PA4 | URBAN | Equipment Failure | 987034 | 790 | 213 | 83740 | 0.050969 | 0.048084
2013-06-25 | 238:34141 | SHORT RURAL | Other | 987050 | 8 | 170 | 1360 | 0.00082778 | 0.00048693
2013-06-26 | ZN965:PA24 | SHORT RURAL | Equipment Failure | 987068 | 29 | 199.5667 | 5787.4333 | 0.0035226 | 0.0017651
2013-06-26 | ZN1648:PA16 | URBAN | Equipment Failure | 987083 | 74 | 164.5333 | 12175.4667 | 0.0074107 | 0.0045041
2013-06-26 | ZN12660:PA14 | SHORT RURAL | Other | 987171 | 1 | 129.1 | 129.1 | 7.8578e-05 | 6.0866e-05
2013-06-26 | ZN35370:PA8 | SHORT RURAL | Other | 987174 | 1 | 126.9833 | 126.9833 | 7.729e-05 | 6.0866e-05
2013-06-26 | ZN35370:PA8 | SHORT RURAL | Other | 987216 | 1 | 80.95 | 80.95 | 4.9271e-05 | 6.0866e-05
2013-06-26 | ZN10993:PA12 | URBAN | Equipment Failure | 987258 | 65 | 116.7833 | 6630 | 0.0040354 | 0.0039563
2013-06-26 | ZN10993:PA13 | URBAN | Equipment Failure | 987258 | 1 | 116.7833 | 82.0667 | 4.9951e-05 | 6.0866e-05
2013-06-28 | 206:34438 | SHORT RURAL | Other | 987260 | 10 | 199.8 | 1998 | 0.0012161 | 0.00060866
2013-06-26 | ZN398:PA15 | URBAN | Equipment Failure | 987283 | 1 | 251.9167 | 251.9167 | 0.00015333 | 6.0866e-05
2013-06-26 | ZN2835:PA28 | URBAN | Other | 987339 | 1 | 1216.3833 | 1216.3833 | 0.00074036 | 6.0866e-05
2013-06-26 | ZN8000:PA6 | URBAN | Equipment Failure | 987367 | 708 | 112 | 67167 | 0.040882 | 0.043093
2013-06-26 | ZN14144:PA10 | SHORT RURAL | Equipment Failure | 987400 | 1 | 174.05 | 174.05 | 0.00010594 | 6.0866e-05
2013-06-26 | 502:48010 | SHORT RURAL | Equipment Failure | 987407 | 2 | 281 | 562 | 0.00034207 | 0.00012173
2013-06-26 | ZN262:PA40 | URBAN | Equipment Failure | 987413 | 90 | 87.75 | 7897.5 | 0.0048069 | 0.0054779
2013-06-26 | ZN3672:PA46 | URBAN | Equipment Failure | 987452 | 79 | 67 | 5293 | 0.0032216 | 0.0048084
2013-06-26 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 987460 | 10 | 72 | 720 | 0.00043824 | 0.00060866
2013-06-26 | ZN188:PA32 | URBAN | Other | 987463 | 59 | 107 | 6313 | 0.0038425 | 0.0035911
2013-06-26 | ZN3672:PA46 | URBAN | Equipment Failure | 987475 | 51 | 101.1 | 5156.1 | 0.0031383 | 0.0031042
2013-06-26 | ZN965:PA35 | URBAN | Vegetation | 987485 | 85 | 312 | 76551 | 0.046594 | 0.0051736
2013-06-26 | 202:34260 | URBAN | Other | 987488 | 1 | 284.4667 | 284.4667 | 0.00017314 | 6.0866e-05
2013-06-27 | ZN5868:PA14 | URBAN | Vegetation | 987510 | 1 | 1832.6833 | 1832.6833 | 0.0011155 | 6.0866e-05
2013-06-27 | ZN2196:PA5 | URBAN | Equipment Failure | 987531 | 1 | 450.35 | 450.35 | 0.00027411 | 6.0866e-05
2013-06-27 | ZN2196:PA5 | URBAN | Equipment Failure | 987533 | 31 | 143.45 | 4446.95 | 0.0027067 | 0.0018868
2013-06-27 | ZN2196:PA5 | URBAN | Equipment Failure | 987545 | 1 | 439.1833 | 439.1833 | 0.00026731 | 6.0866e-05
2013-06-27 | ZN4545:PA40 | URBAN | Equipment Failure | 987562 | 1 | 1458.5667 | 1458.5667 | 0.00088777 | 6.0866e-05
2013-06-27 | ZN2196:PA5 | URBAN | Equipment Failure | 987566 | 1 | 412.85 | 412.85 | 0.00025129 | 6.0866e-05
2013-06-27 | 217:33611 | URBAN | Other | 987629 | 13 | 78 | 1014 | 0.00061718 | 0.00079126
2013-06-27 | 214:8669 | URBAN | Other | 987633 | 1 | 1406.0667 | 1406.0667 | 0.00085582 | 6.0866e-05
2013-06-27 | 217:33611 | URBAN | Other | 987643 | 1 | 5681.0667 | 5681.0667 | 0.0034578 | 6.0866e-05
2013-06-27 | ZN1164:PA8 | URBAN | Other | 987646 | 1 | 169.15 | 169.15 | 0.00010295 | 6.0866e-05
2013-05-31 | ZN14891:PA12 | SHORT RURAL | Other | 987740 | 10 | 85 | 850 | 0.00051765 | 0.000609
2013-05-31 | ZN14891:PA12 | SHORT RURAL | Other | 987741 | 364 | 2 | 728 | 0.00044335 | 0.022167
2013-06-27 | ZN3425:PA24 | URBAN | Third Party Impacts | 987792 | 1 | 1418.8333 | 1418.8333 | 0.00086359 | 6.0866e-05
2013-06-27 | ZN15011:PA6 | URBAN | Equipment Failure | 987886 | 1 | 281.6333 | 281.6333 | 0.00017142 | 6.0866e-05
2013-06-27 | ZN12580:PA1 | URBAN | Equipment Failure | 987895 | 1 | 192.7 | 192.7 | 0.00011729 | 6.0866e-05
2013-06-27 | 507:80923 | SHORT RURAL | Other | 987905 | 6 | 194.5 | 1167 | 0.00071031 | 0.0003652
2013-06-27 | ZN15010:PA9 | SHORT RURAL | Vegetation | 987921 | 1 | 1038.2833 | 1038.2833 | 0.00063196 | 6.0866e-05
2013-06-27 | ZN398:PA30 | URBAN | Equipment Failure | 987927 | 98 | 39.0167 | 3823.6333 | 0.0023273 | 0.0059649
2013-06-27 | ZN262:PA42 | URBAN | Equipment Failure | 987929 | 46 | 172.0167 | 7912.7667 | 0.0048162 | 0.0027998
2013-06-27 | 801:74121 | SHORT RURAL | Equipment Failure | 987944 | 1 | 173.6167 | 173.6167 | 0.00010567 | 6.0866e-05
2013-06-28 | ZN12610:PA10 | SHORT RURAL | Equipment Failure | 987949 | 1182 | 138 | 111108 | 0.067627 | 0.071944
2013-06-28 | ZN12610:PA24 | SHORT RURAL | Equipment Failure | 987949 | 1187 | 138 | 113465 | 0.069062 | 0.072248
2013-06-28 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 987959 | 10 | 239 | 2390 | 0.0014547 | 0.00060866
2013-06-28 | ZN2196:PA21 | URBAN | Equipment Failure | 987974 | 1 | 224.75 | 224.75 | 0.0001368 | 6.0866e-05
2013-06-28 | ZN35800:PA14 | URBAN | Other | 987980 | 1 | 120.95 | 120.95 | 7.3618e-05 | 6.0866e-05
2013-06-28 | ZN1193:PA15 | URBAN | Equipment Failure | 987989 | 1038 | 76 | 78888 | 0.048016 | 0.063179
2013-06-28 | ZN1193:PA26 | URBAN | Equipment Failure | 987989 | 395 | 76 | 30020 | 0.018272 | 0.024042
2013-06-28 | ZN1193:PA26 | URBAN | Other | 987999 | 1 | 4294.2667 | 4294.2667 | 0.0026138 | 6.0866e-05
2013-06-28 | ZN3922:PA14 | URBAN | Other | 988002 | 1 | 4453.3333 | 4453.3333 | 0.0027106 | 6.0866e-05
2013-06-28 | 217:33611 | URBAN | Equipment Failure | 988008 | 13 | 164.7667 | 2141.9667 | 0.0013037 | 0.00079126
2013-06-28 | ZN3472:PA31 | URBAN | Third Party Impacts | 988054 | 1 | 160.1833 | 160.1833 | 9.7497e-05 | 6.0866e-05
2013-06-28 | ZN180:PA15 | URBAN | Equipment Failure | 988058 | 1 | 4155.0167 | 4155.0167 | 0.002529 | 6.0866e-05
2013-06-28 | ZN2196:PA25 | URBAN | Equipment Failure | 988146 | 865 | 163 | 125270 | 0.076247 | 0.052649
2013-06-28 | 507:80923 | SHORT RURAL | Other | 988300 | 1 | 112 | 112 | 6.817e-05 | 6.0866e-05
2013-06-28 | ZN262:PA31 | URBAN | Third Party Impacts | 988315 | 1 | 334.3333 | 334.3333 | 0.0002035 | 6.0866e-05
2013-06-28 | ZN9700:PA20 | URBAN | Equipment Failure | 988345 | 2 | 229 | 243 | 0.0001479 | 0.00012173
2013-06-28 | ZN180:PA34 | URBAN | Equipment Failure | 988349 | 39 | 85 | 3315 | 0.0020177 | 0.0023738
2013-06-28 | ZN2602:PA15 | URBAN | Equipment Failure | 988385 | 1 | 774.8833 | 774.8833 | 0.00047164 | 6.0866e-05
2013-06-29 | ZN2310:PA23 | URBAN | Equipment Failure | 988397 | 2 | 55 | 110 | 6.6953e-05 | 0.00012173
2013-06-29 | ZN2196:PA6 | URBAN | Third Party Impacts | 988447 | 3 | 91 | 273 | 0.00016616 | 0.0001826
2013-06-29 | ZN965:PA46 | URBAN | Equipment Failure | 988468 | 1 | 1610.9333 | 1610.9333 | 0.00098051 | 6.0866e-05
2013-06-29 | 224:80337 | URBAN | Equipment Failure | 988496 | 1 | 108.65 | 108.65 | 6.6131e-05 | 6.0866e-05
2013-06-29 | ZN12650:PA13 | SHORT RURAL | Equipment Failure | 988497 | 2149 | 102.0167 | 200738 | 0.12218 | 0.1308
2013-06-29 | ZN8700:PA65 66K | CBD | Other | 988515 | 10 | 73 | 730 | 0.00044432 | 0.00060866
2013-06-29 | ZN3472:PA8 | URBAN | Vegetation | 988539 | 2 | 454.4 | 609.0833 | 0.00037073 | 0.00012173
2013-06-29 | 813:89055 | SHORT RURAL | Animals | 988569 | 1 | 153 | 153 | 9.3125e-05 | 6.0866e-05
2013-06-29 | 210:8682 | URBAN | Other | 988575 | 1 | 61.9167 | 61.9167 | 3.7686e-05 | 6.0866e-05
2013-06-29 | 217:33612 | URBAN | Equipment Failure | 988614 | 21 | 243.85 | 5014.85 | 0.0030523 | 0.0012782
2013-06-30 | ZN3288:PA41 42KLM | CBD | Other | 988652 | 28 | 201 | 5628 | 0.0034255 | 0.0017043
2013-06-30 | 813:89062 | SHORT RURAL | Animals | 988678 | 1 | 90 | 90 | 5.4779e-05 | 6.0866e-05
2013-06-30 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 988707 | 10 | 53.15 | 531.5 | 0.0003235 | 0.00060866
2013-06-30 | ZN10999:PA11 | URBAN | Equipment Failure | 988712 | 32 | 207 | 6624 | 0.0040318 | 0.0019477
2013-06-30 | ZN9245:PA11 | URBAN | Equipment Failure | 988717 | 1 | 501.65 | 501.65 | 0.00030533 | 6.0866e-05
2013-06-30 | ZN269:PA14 | URBAN | Other | 988720 | 81 | 170.6 | 13818.6 | 0.0084108 | 0.0049302
2013-06-30 | ZN9118:PA17 | URBAN | Vegetation | 988729 | 1 | 273.7667 | 273.7667 | 0.00016663 | 6.0866e-05
2013-06-30 | ZN9900:PA19 | URBAN | Equipment Failure | 988737 | 36 | 282 | 10152 | 0.0061791 | 0.0021912
2013-06-30 | ZN9118:PA20 | URBAN | Equipment Failure | 988738 | 33 | 120.9333 | 3990.8 | 0.002429 | 0.0020086
2013-06-30 | 261:81879 | URBAN | Equipment Failure | 988747 | 2107 | 56 | 114176 | 0.069494 | 0.12824
2013-06-30 | ZN14891:PA12 | SHORT RURAL | Equipment Failure | 988754 | 10 | 98.4 | 984 | 0.00059892 | 0.00060866
2013-06-30 | ZN2835:PA9 | URBAN | Third Party Impacts | 988760 | 1 | 307.1333 | 307.1333 | 0.00018694 | 6.0866e-05
2013-06-30 | ZN180:PA24 | URBAN | Other | 988766 | 1 | 391.0333 | 391.0333 | 0.00023801 | 6.0866e-05
2013-06-30 | 509:48039 | LONG RURAL | Other | 988769 | 2 | 147.2167 | 294.4333 | 0.00017921 | 0.00012173
2013-06-30 | 221:11895 | URBAN | Equipment Failure | 988778 | 78 | 55.4333 | 4323.8 | 0.0026317 | 0.0047476
2013-06-30 | ZN3288:PA43 44KLM | CBD | Equipment Failure | 988787 | 6 | 1582 | 9492 | 0.0057774 | 0.0003652
2013-06-30 | 238:34137 | URBAN | Vegetation | 988800 | 3 | 436 | 1308 | 0.00079613 | 0.0001826
2013-06-30 | 806:82662 | SHORT RURAL | Other | 988805 | 1 | 113.2667 | 113.2667 | 6.8941e-05 | 6.0866e-05
2013-06-30 | 503:48017 | URBAN | Other | 988819 | 4 | 187.4833 | 749.9333 | 0.00045646 | 0.00024346
2013-06-30 | ZN129:PA3 | URBAN | Other | 988847 | 33 | 38.7333 | 1278.2 | 0.00077799 | 0.0020086
2013-06-30 | ZN9900:PA19 | URBAN | Equipment Failure | 988853 | 1 | 2165.2 | 2165.2 | 0.0013179 | 6.0866e-05
2013-06-30 | ZN129:PA3 | URBAN | Equipment Failure | 988858 | 33 | 86.3667 | 2850.1 | 0.0017347 | 0.0020086
2013-06-30 | 258:80785 | URBAN | Other | 988864 | 1 | 99.9333 | 99.9333 | 6.0826e-05 | 6.0866e-05
2013-06-29 | ZN180:PA28 | URBAN | Equipment Failure | 988903 | 97 | 85 | 8245 | 0.0050184 | 0.005904
2013-06-29 | ZN180:PA28 | URBAN | Other | 988925 | 47 | 15 | 705 | 0.00042911 | 0.0028607
2013-06-29 | ZN180:PA28 | URBAN | Other | 988926 | 21 | 15 | 315 | 0.00019173 | 0.0012782
2013-06-28 | 813:89061 | LONG RURAL | Equipment Failure | 989029 | 3 | 35 | 105 | 6.3909e-05 | 0.0001826
2013-06-27 | ZN1193:PA26 | URBAN | Equipment Failure | 990291 | 36 | 30 | 1080 | 0.00065735 | 0.0021912
Table 2: Planned Outages
Date (DD/MM/YYYY) | Feeder ID / name | Feeder classification | Cause of event | Event ID | Number of customers interrupted | Duration of interruption (Mins) | Total planned customer minutes off supply (Mins) | Planned SAIDI impact | Planned SAIFI impact
2012-07-01 | 224:80332 | URBAN | Planned Outage | 843180 | 1 | 160 | 160 | 9.7747e-05 | 6.1092e-05
2012-07-01 | 511:29880 | URBAN | Planned Outage | 843208 | 1 | 600 | 600 | 0.00036655 | 6.1092e-05
2012-07-01 | 511:29872 | URBAN | Planned Outage | 843273 | 20 | 470 | 9400 | 0.0057426 | 0.0012218
2012-07-03 | 507:80925 | SHORT RURAL | Planned Outage | 843530 | 108 | 430 | 46440 | 0.028371 | 0.0065979
2012-07-02 | 227:13019 | SHORT RURAL | Planned Outage | 843624 | 7 | 435 | 3045 | 0.0018602 | 0.00042764
2012-07-02 | 228:7490 | SHORT RURAL | Planned Outage | 843626 | 5 | 70 | 350 | 0.00021382 | 0.00030546
2012-07-02 | 202:34256 | URBAN | Planned Outage | 843635 | 102 | 240 | 24480 | 0.014955 | 0.0062314
2012-07-03 | 509:48039 | LONG RURAL | Planned Outage | 843652 | 19 | 165 | 3135 | 0.0019152 | 0.0011607
2012-07-06 | 264:81240 | SHORT RURAL | Planned Outage | 845010 | 31 | 170 | 5270 | 0.0032196 | 0.0018939
2012-07-08 | 507:80922 | SHORT RURAL | Planned Outage | 845651 | 100 | 350 | 35000 | 0.021382 | 0.0061092
2012-07-08 | 512:48049 | SHORT RURAL | Planned Outage | 845654 | 24 | 305 | 7320 | 0.0044719 | 0.0014662
2012-07-03 | 243:80084 | SHORT RURAL | Planned Outage | 846374 | 20 | 245 | 4900 | 0.0029935 | 0.0012218
2012-07-01 | ZN12650:PA6 | URBAN | Planned Outage | 846391 | 39 | 480 | 18720 | 0.011436 | 0.0023826
2012-07-01 | ZN180:PA7 | URBAN | Planned Outage | 846394 | 12 | 420 | 5040 | 0.003079 | 0.0007331
2012-07-04 | 214:8670 | URBAN | Planned Outage | 846403 | 54 | 150 | 8100 | 0.0049484 | 0.003299
2012-07-05 | 812:19072 | SHORT RURAL | Planned Outage | 846417 | 5 | 225 | 1125 | 0.00068729 | 0.00030546
2012-07-02 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 846424 | 92 | 480 | 43320 | 0.026465 | 0.0056205
2012-07-02 | ZN901:PA18 | URBAN | Planned Outage | 846433 | 86 | 420 | 36120 | 0.022066 | 0.0052539
2012-07-02 | ZN12610:PA18 | URBAN | Planned Outage | 846434 | 84 | 420 | 35280 | 0.021553 | 0.0051317
2012-07-02 | ZN12690:PA16 | SHORT RURAL | Planned Outage | 846437 | 12 | 480 | 5760 | 0.0035189 | 0.0007331
2012-07-02 | ZN12640:PA7 | URBAN | Planned Outage | 846439 | 88 | 480 | 42240 | 0.025805 | 0.0053761
2012-07-02 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 846442 | 34 | 480 | 16320 | 0.0099702 | 0.0020771
2012-07-02 | ZN12640:PA18 | SHORT RURAL | Planned Outage | 846458 | 171 | 480 | 82080 | 0.050144 | 0.010447
2012-07-03 | ZN12690:PA16 | SHORT RURAL | Planned Outage | 846467 | 12 | 480 | 5760 | 0.0035189 | 0.0007331
2012-07-02 | ZN15001:PA15 | URBAN | Planned Outage | 846473 | 61 | 480 | 29280 | 0.017888 | 0.0037266
2012-07-02 | ZN9118:PA6 | URBAN | Planned Outage | 846478 | 26 | 360 | 9360 | 0.0057182 | 0.0015884
2012-07-02 | ZN3155:PA11 | URBAN | Planned Outage | 846480 | 1 | 720 | 720 | 0.00043986 | 6.1092e-05
2012-07-03 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 846485 | 2 | 510 | 1020 | 0.00062314 | 0.00012218
2012-07-03 | ZN3922:PA11 | URBAN | Planned Outage | 846490 | 66 | 270 | 17820 | 0.010887 | 0.0040321
2012-07-04 | ZN12570:PA18 | URBAN | Planned Outage | 846492 | 49 | 480 | 23520 | 0.014369 | 0.0029935
2012-07-04 | ZN12660:PA10 | SHORT RURAL | Planned Outage | 846496 | 115 | 480 | 55200 | 0.033723 | 0.0070256
2012-07-04 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 846502 | 4 | 450 | 1800 | 0.0010997 | 0.00024437
2012-07-04 | ZN3155:PA21 | URBAN | Planned Outage | 846505 | 44 | 360 | 15840 | 0.009677 | 0.002688
2012-07-04 | ZN12570:PA18 | URBAN | Planned Outage | 846507 | 95 | 360 | 34200 | 0.020893 | 0.0058037
2012-07-04 | ZN2400:PA15 | URBAN | Planned Outage | 846522 | 6 | 270 | 1620 | 0.00098969 | 0.00036655
2012-07-04 | ZN3155:PA21 | URBAN | Planned Outage | 846523 | 47 | 330 | 15510 | 0.0094754 | 0.0028713
2012-07-05 | 524:33572 | SHORT RURAL | Planned Outage | 846536 | 308 | 260 | 80080 | 0.048923 | 0.018816
2012-07-03 | 240:34846 | URBAN | Planned Outage | 846563 | 47 | 165 | 7755 | 0.0047377 | 0.0028713
2012-07-03 | 229:34995 | SHORT RURAL | Planned Outage | 846568 | 8 | 355 | 2840 | 0.001735 | 0.00048874
2012-07-04 | 232:33413 | SHORT RURAL | Planned Outage | 846570 | 26 | 160 | 4160 | 0.0025414 | 0.0015884
2012-07-04 | 213:33775 | URBAN | Planned Outage | 846573 | 30 | 365 | 10950 | 0.0066896 | 0.0018328
2012-07-05 | 232:11459 | SHORT RURAL | Planned Outage | 846575 | 48 | 195 | 9360 | 0.0057182 | 0.0029324
2012-07-05 | 232:33413 | SHORT RURAL | Planned Outage | 846577 | 2 | 165 | 330 | 0.0002016 | 0.00012218
2012-07-06 | 227:13018 | URBAN | Planned Outage | 846578 | 155 | 480 | 74400 | 0.045453 | 0.0094693
2012-07-05 | ZN12640:PA19 | URBAN | Planned Outage | 846611 | 304 | 540 | 159420 | 0.097393 | 0.018572
2012-07-05 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 846616 | 50 | 540 | 27000 | 0.016495 | 0.0030546
2012-07-05 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 846617 | 14 | 480 | 6720 | 0.0041054 | 0.00085529
2012-07-05 | ZN14143:PA10 | SHORT RURAL | Planned Outage | 846617 | 21 | 480 | 6660 | 0.0040687 | 0.0012829
2012-07-05 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 846625 | 15 | 480 | 7200 | 0.0043986 | 0.00091638
2012-07-05 | ZN187:PA4 | URBAN | Planned Outage | 846630 | 225 | 480 | 108000 | 0.06598 | 0.013746
2012-07-05 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 846631 | 3 | 480 | 1440 | 0.00087973 | 0.00018328
2012-07-05 | ZN12570:PA12 | SHORT RURAL | Planned Outage | 846639 | 38 | 480 | 18240 | 0.011143 | 0.0023215
2012-07-05 | ZN1287:PA4 | URBAN | Planned Outage | 846642 | 160 | 540 | 86400 | 0.052784 | 0.0097747
2012-07-08 | 224:80329 | SHORT RURAL | Planned Outage | 846649 | 1 | 395 | 395 | 0.00024131 | 6.1092e-05
2012-07-05 | ZN12690:PA16 | SHORT RURAL | Planned Outage | 846658 | 11 | 360 | 3960 | 0.0024192 | 0.00067201
2012-07-05 | ZN12570:PA19 | URBAN | Planned Outage | 846661 | 52 | 1080 | 56160 | 0.034309 | 0.0031768
2012-07-06 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 846662 | 27 | 480 | 12960 | 0.0079175 | 0.0016495
2012-07-06 | ZN9118:PA24 | URBAN | Planned Outage | 846665 | 108 | 390 | 42120 | 0.025732 | 0.006598
2012-07-07 | ZN3288:PA41 42ABC | CBD | Planned Outage | 846670 | 10 | 420 | 4200 | 0.0025659 | 0.00061092
2012-07-03 | 524:33576 | SHORT RURAL | Planned Outage | 846673 | 17 | 380 | 6460 | 0.0039465 | 0.0010386
2012-07-08 | ZN3288:PA45 46ABC | CBD | Planned Outage | 846674 | 62 | 330 | 20460 | 0.012499 | 0.0037877
2012-07-04 | 238:34143 | URBAN | Planned Outage | 846677 | 75 | 50 | 3750 | 0.0022909 | 0.0045819
2012-07-04 | 526:34636 | SHORT RURAL | Planned Outage | 846681 | 14 | 315 | 4410 | 0.0026942 | 0.00085529
2012-07-08 | ZN12650:PA20 | URBAN | Planned Outage | 846684 | 844 | 480 | 304200 | 0.18584 | 0.051562
2012-07-04 | 503:48012 | URBAN | Planned Outage | 846685 | 101 | 125 | 12625 | 0.0077129 | 0.0061703
2012-07-04 | 504:48031 | SHORT RURAL | Planned Outage | 846687 | 29 | 50 | 1450 | 0.00088583 | 0.0017717
2012-07-04 | 504:48031 | SHORT RURAL | Planned Outage | 846690 | 2 | 200 | 400 | 0.00024437 | 0.00012218
2012-07-04 | 512:48047 | SHORT RURAL | Planned Outage | 846691 | 42 | 165 | 6930 | 0.0042337 | 0.0025659
2012-07-04 | 526:34641 | SHORT RURAL | Planned Outage | 846693 | 6 | 265 | 1590 | 0.00097136 | 0.00036655
2012-07-05 | 524:33580 | SHORT RURAL | Planned Outage | 846695 | 1 | 55 | 55 | 3.3601e-05 | 6.1092e-05
2012-07-05 | 507:80923 | SHORT RURAL | Planned Outage | 846718 | 4 | 135 | 540 | 0.0003299 | 0.00024437
2012-07-06 | 509:48040 | SHORT RURAL | Planned Outage | 846739 | 1 | 210 | 210 | 0.00012829 | 6.1092e-05
2012-07-06 | 238:34141 | SHORT RURAL | Planned Outage | 846743 | 72 | 515 | 37080 | 0.022653 | 0.0043986
2012-07-06 | 238:34141 | SHORT RURAL | Planned Outage | 846754 | 28 | 140 | 3920 | 0.0023948 | 0.0017106
2012-07-09 | 243:80083 | SHORT RURAL | Planned Outage | 846784 | 7 | 270 | 1890 | 0.0011546 | 0.00042765
2012-07-09 | 227:13019 | SHORT RURAL | Planned Outage | 846786 | 12 | 355 | 4260 | 0.0026025 | 0.00073311
2012-07-03 | 813:89055 | SHORT RURAL | Planned Outage | 846790 | 1 | 125 | 125 | 7.6365e-05 | 6.1092e-05
2012-07-03 | 520:48172 | SHORT RURAL | Planned Outage | 846795 | 51 | 495 | 25245 | 0.015423 | 0.0031157
2012-07-03 | 514:18137 | SHORT RURAL | Planned Outage | 846798 | 1 | 80 | 80 | 4.8874e-05 | 6.1092e-05
2012-07-03 | 813:89061 | LONG RURAL | Planned Outage | 846906 | 1 | 10 | 10 | 6.1092e-06 | 6.1092e-05
2012-07-04 | 801:74121 | SHORT RURAL | Planned Outage | 846909 | 1 | 112 | 112 | 6.8423e-05 | 6.1092e-05
2012-07-04 | 802:82225 | SHORT RURAL | Planned Outage | 846915 | 59 | 280 | 16520 | 0.010092 | 0.0036044
2012-07-04 | 523:33501 | SHORT RURAL | Planned Outage | 846921 | 93 | 345 | 32085 | 0.019601 | 0.0056815
2012-07-05 | 523:33508 | SHORT RURAL | Planned Outage | 846925 | 13 | 200 | 2600 | 0.0015884 | 0.0007942
2012-07-05 | 801:74121 | SHORT RURAL | Planned Outage | 846927 | 6 | 215 | 1290 | 0.00078809 | 0.00036655
2012-07-06 | 513:48058 | URBAN | Planned Outage | 846941 | 52 | 100 | 5200 | 0.0031768 | 0.0031768
2012-07-06 | 513:48059 | SHORT RURAL | Planned Outage | 846946 | 4 | 300 | 1200 | 0.00073311 | 0.00024437
2012-07-11 | 507:80923 | SHORT RURAL | Planned Outage | 846962 | 388 | 375 | 145500 | 0.088892 | 0.023705
2012-07-07 | 807:74183 | SHORT RURAL | Planned Outage | 846985 | 4 | 230 | 920 | 0.00056205 | 0.00024437
2012-07-07 | 803:74013 | SHORT RURAL | Planned Outage | 846990 | 1 | 195 | 195 | 0.00011913 | 6.1092e-05
2012-07-08 | 810:74054 | LONG RURAL | Planned Outage | 846994 | 1 | 40 | 40 | 2.4437e-05 | 6.1092e-05
2012-07-08 | 810:74054 | LONG RURAL | Planned Outage | 847005 | 1 | 50 | 50 | 3.0546e-05 | 6.1092e-05
2012-07-08 | 810:74054 | LONG RURAL | Planned Outage | 847007 | 1 | 55 | 55 | 3.3601e-05 | 6.1092e-05
2012-07-08 | 810:74054 | LONG RURAL | Planned Outage | 847013 | 1 | 70 | 70 | 4.2765e-05 | 6.1092e-05
2012-07-10 | 232:33413 | SHORT RURAL | Planned Outage | 847049 | 65 | 250 | 16250 | 0.0099278 | 0.0039711
2012-07-09 | ZN14891:PA10 | SHORT RURAL | Planned Outage | 847055 | 182 | 480 | 24360 | 0.014882 | 0.011119
2012-07-11 | 526:34637 | SHORT RURAL | Planned Outage | 847063 | 8 | 256 | 2048 | 0.0012512 | 0.00048875
2012-07-09 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 847066 | 13 | 480 | 6240 | 0.0038122 | 0.0007942
2012-07-10 | 260:33353 | URBAN | Planned Outage | 847067 | 87 | 420 | 36540 | 0.022324 | 0.0053152
2012-07-09 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 847069 | 11 | 420 | 4620 | 0.0028225 | 0.00067201
2012-07-09 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 847071 | 7 | 360 | 2520 | 0.0015395 | 0.00042765
2012-07-10 | 227:13020 | SHORT RURAL | Planned Outage | 847072 | 14 | 265 | 3710 | 0.0022666 | 0.00085531
2012-07-09 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 847079 | 17 | 360 | 6120 | 0.0037388 | 0.0010386
2012-07-09 | ZN9037:PA15 | URBAN | Planned Outage | 847153 | 57 | 540 | 30780 | 0.018804 | 0.0034823
2012-07-09 | ZN1068:PA27 | URBAN | Planned Outage | 847170 | 25 | 450 | 11250 | 0.0068729 | 0.0015273
2012-07-10 | ZN12660:PA11 | URBAN | Planned Outage | 847173 | 96 | 510 | 48960 | 0.029912 | 0.005865
2012-07-10 | ZN965:PA33 | URBAN | Planned Outage | 847180 | 1 | 420 | 420 | 0.00025659 | 6.1094e-05
2012-07-10 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 847185 | 104 | 540 | 52920 | 0.032331 | 0.0063538
2012-07-10 | 526:34636 | SHORT RURAL | Planned Outage | 847187 | 8 | 180 | 1440 | 0.00087975 | 0.00048875
2012-07-10 | 524:33576 | SHORT RURAL | Planned Outage | 847195 | 8 | 55 | 440 | 0.00026881 | 0.00048875
2012-07-10 | 503:48078 | URBAN | Planned Outage | 847203 | 1 | 275 | 275 | 0.00016801 | 6.1094e-05
2012-07-10 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 847204 | 22 | 480 | 10560 | 0.0064515 | 0.0013441
2012-07-10 | 238:34141 | SHORT RURAL | Planned Outage | 847205 | 5 | 350 | 1750 | 0.0010691 | 0.00030547
2012-07-11 | 526:34640 | SHORT RURAL | Planned Outage | 847216 | 4 | 270 | 1080 | 0.00065982 | 0.00024438
2012-07-11 | 526:34635 | SHORT RURAL | Planned Outage | 847222 | 30 | 256 | 7680 | 0.004692 | 0.0018328
2012-07-11 | ZN15001:PA15 | URBAN | Planned Outage | 847521 | 61 | 480 | 29280 | 0.017888 | 0.0037267
2012-07-11 | ZN9700:PA23 | URBAN | Planned Outage | 847530 | 31 | 510 | 15810 | 0.009659 | 0.0018939
2012-07-11 | 223:14394 | URBAN | Planned Outage | 847622 | 2 | 475 | 950 | 0.00058039 | 0.00012219
2012-07-11 | 232:11457 | URBAN | Planned Outage | 847624 | 43 | 285 | 12255 | 0.0074871 | 0.002627
2012-07-11 | 507:80923 | SHORT RURAL | Planned Outage | 847660 | 17 | 280 | 4760 | 0.0029081 | 0.0010386
2012-07-12 | 227:13019 | SHORT RURAL | Planned Outage | 847864 | 12 | 260 | 3120 | 0.0019062 | 0.00073316
2012-07-12 | 260:33353 | URBAN | Planned Outage | 847867 | 1 | 450 | 450 | 0.00027493 | 6.1097e-05
2012-07-12 | 232:11457 | URBAN | Planned Outage | 847869 | 164 | 430 | 70520 | 0.043085 | 0.01002
2012-07-12 | 238:34143 | URBAN | Planned Outage | 847934 | 75 | 34 | 2550 | 0.001558 | 0.0045822
2012-07-12 | ZN12690:PA6 | URBAN | Planned Outage | 848809 | 1 | 15 | 15 | 9.1645e-06 | 6.1097e-05
2012-07-12 | ZN12690:PA16 | SHORT RURAL | Planned Outage | 848816 | 12 | 60 | 720 | 0.0004399 | 0.00073316
2012-07-12 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 848819 | 86 | 480 | 41280 | 0.025221 | 0.0052543
2012-07-12 | ZN3155:PA24 | URBAN | Planned Outage | 848822 | 20 | 630 | 12600 | 0.0076982 | 0.0012219
2012-07-12 | ZN3155:PA11 | URBAN | Planned Outage | 848823 | 1 | 630 | 630 | 0.00038491 | 6.1097e-05
2012-07-13 | ZN12610:PA11 | URBAN | Planned Outage | 848825 | 120 | 480 | 57600 | 0.035192 | 0.0073316
2012-07-13 | ZN12610:PA10 | SHORT RURAL | Planned Outage | 848827 | 39 | 480 | 18720 | 0.011437 | 0.0023828
2012-07-13 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 848830 | 2 | 480 | 960 | 0.00058653 | 0.00012219
2012-07-13 | ZN14892:PA13 | URBAN | Planned Outage | 848835 | 100 | 480 | 48000 | 0.029326 | 0.0061097
2012-07-13 | ZN3288:PA43 44KLM | CBD | Planned Outage | 848837 | 7 | 3960 | 27720 | 0.016936 | 0.00042768
2012-07-14 | ZN2635:PA19 | URBAN | Planned Outage | 848840 | 1 | 60 | 60 | 3.6658e-05 | 6.1097e-05
2012-07-14 | ZN2635:PA19 | URBAN | Planned Outage | 848841 | 28 | 420 | 11760 | 0.007185 | 0.0017107
2012-07-14 | ZN2473:PA26 | URBAN | Planned Outage | 848844 | 129 | 600 | 77400 | 0.047289 | 0.0078815
2012-07-14 | ZN3288:PA41 42ABC | CBD | Planned Outage | 848850 | 169 | 420 | 70980 | 0.043366 | 0.010325
2012-07-14 | ZN2473:PA1 | URBAN | Planned Outage | 848853 | 37 | 420 | 15540 | 0.0094944 | 0.0022606
2012-07-14 | ZN3288:PA45 46ABC | CBD | Planned Outage | 848856 | 67 | 510 | 34170 | 0.020877 | 0.0040935
2012-07-16 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 849078 | 4 | 510 | 120 | 7.3316e-05 | 0.00024439
2012-07-16 | ZN3472:PA21 | URBAN | Planned Outage | 849086 | 1 | 240 | 240 | 0.00014663 | 6.1097e-05
2012-07-16 | ZN10993:PA8 | URBAN | Planned Outage | 849094 | 1 | 450 | 450 | 0.00027493 | 6.1097e-05
2012-07-16 | ZN15015:PA15 | URBAN | Planned Outage | 849102 | 13 | 480 | 6240 | 0.0038124 | 0.00079426
2012-07-16 | ZN12570:PA19 | URBAN | Planned Outage | 849105 | 2 | 480 | 960 | 0.00058653 | 0.00012219
2012-07-16 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 849118 | 19 | 480 | 9120 | 0.005572 | 0.0011608
2012-07-17 | 512:48046 | SHORT RURAL | Planned Outage | 849130 | 60 | 220 | 13200 | 0.0080647 | 0.0036658
2012-07-16 | ZN12600:PA11 | URBAN | Planned Outage | 849138 | 145 | 480 | 69600 | 0.042523 | 0.008859
2012-07-16 | ZN12650:PA6 | URBAN | Planned Outage | 849138 | 89 | 480 | 42720 | 0.0261 | 0.0054376
2012-07-16 | ZN12640:PA2 | URBAN | Planned Outage | 849148 | 105 | 480 | 50400 | 0.030793 | 0.0064151
2012-07-16 | ZN12580:PA16 | URBAN | Planned Outage | 849152 | 69 | 480 | 33120 | 0.020235 | 0.0042157
2012-07-16 | ZN14144:PA2 | SHORT RURAL | Planned Outage | 849161 | 44 | 480 | 21120 | 0.012904 | 0.0026882
2012-07-16 | ZN12610:PA20 | SHORT RURAL | Planned Outage | 849177 | 89 | 480 | 42720 | 0.0261 | 0.0054376
2012-07-16 | ZN1164:PA21 | URBAN | Planned Outage | 849180 | 105 | 150 | 15750 | 0.0096227 | 0.0064151
2012-07-16 | ZN4545:PA33 | SHORT RURAL | Planned Outage | 849186 | 163 | 300 | 48900 | 0.029876 | 0.0099587
2012-07-16 | ZN874:PA8 | URBAN | Planned Outage | 849187 | 150 | 298 | 44700 | 0.02731 | 0.0091645
2012-07-16 | ZN35370:PA4 | URBAN | Planned Outage | 849196 | 6 | 30 | 180 | 0.00010997 | 0.00036658
2012-07-16 | 258:80784 | URBAN | Planned Outage | 849277 | 98 | 360 | 35280 | 0.021555 | 0.0059875
2012-07-16 | 227:13019 | SHORT RURAL | Planned Outage | 849319 | 12 | 430 | 5160 | 0.0031526 | 0.00073316
2012-07-16 | 264:81240 | SHORT RURAL | Planned Outage | 849334 | 2 | 160 | 320 | 0.00019551 | 0.00012219
2012-07-16 | 504:48026 | SHORT RURAL | Planned Outage | 849335 | 62 | 385 | 23870 | 0.014584 | 0.003788
2012-07-16 | 512:48049 | SHORT RURAL | Planned Outage | 849339 | 3 | 300 | 900 | 0.00054987 | 0.00018329
2012-07-17 | 524:33572 | SHORT RURAL | Planned Outage | 849470 | 35 | 5 | 175 | 0.00010692 | 0.0021384
2012-07-17 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 849545 | 2 | 540 | 1080 | 0.00065984 | 0.00012219
2012-07-17 | ZN1285:PA33 | URBAN | Planned Outage | 849546 | 87 | 450 | 39150 | 0.023919 | 0.0053154
2012-07-17 | ZN14891:PA16 | SHORT RURAL | Planned Outage | 849563 | 51 | 480 | 24480 | 0.014956 | 0.0031159
2012-07-17 | ZN12570:PA16 | SHORT RURAL | Planned Outage | 849569 | 68 | 300 | 20400 | 0.012464 | 0.0041546
2012-07-18 | ZN12570:PA16 | SHORT RURAL | Planned Outage | 849572 | 8 | 480 | 3840 | 0.0023461 | 0.00048877
2012-07-18 | 232:11459 | SHORT RURAL | Planned Outage | 849681 | 7 | 350 | 2450 | 0.0014969 | 0.00042767
2012-07-17 | 264:81236 | URBAN | Planned Outage | 849698 | 7 | 310 | 2170 | 0.0013258 | 0.00042767
2012-07-17 | 229:34995 | SHORT RURAL | Planned Outage | 849703 | 198 | 559 | 110682 | 0.067623 | 0.012097
2012-07-17 | 258:80784 | URBAN | Planned Outage | 849708 | 128 | 335 | 42880 | 0.026198 | 0.0078203
2012-07-17 | 510:48164 | SHORT RURAL | Planned Outage | 849735 | 10 | 145 | 1450 | 0.0008859 | 0.00061096
2012-07-17 | 524:33572 | SHORT RURAL | Planned Outage | 849759 | 24 | 675 | 16200 | 0.0098976 | 0.0014663
2012-07-17 | 512:48049 | SHORT RURAL | Planned Outage | 849764 | 1 | 65 | 65 | 3.9713e-05 | 6.1096e-05
2012-07-18 | ZN12610:PA20 | SHORT RURAL | Planned Outage | 850048 | 3 | 480 | 1440 | 0.00087979 | 0.00018329
2012-07-18 | ZN12570:PA12 | SHORT RURAL | Planned Outage | 850053 | 59 | 480 | 28320 | 0.017302 | 0.0036047
2012-07-18 | ZN14892:PA13 | URBAN | Planned Outage | 850055 | 100 | 480 | 48000 | 0.029326 | 0.0061096
2012-07-18 | ZN9700:PA23 | URBAN | Planned Outage | 850056 | 31 | 510 | 15810 | 0.0096593 | 0.001894
2012-07-18 | ZN1068:PA27 | URBAN | Planned Outage | 850057 | 12 | 1320 | 15840 | 0.0096777 | 0.00073316
2012-07-18 | ZN1068:PA18 | URBAN | Planned Outage | 850060 | 11 | 540 | 5940 | 0.0036291 | 0.00067206
2012-07-19 | ZN12620:PA1 | SHORT RURAL | Planned Outage | 850096 | 62 | 480 | 29760 | 0.018182 | 0.003788
2012-07-19 | 232:11459 | SHORT RURAL | Planned Outage | 850099 | 93 | 450 | 41850 | 0.025569 | 0.005682
2012-07-18 | 264:81240 | SHORT RURAL | Planned Outage | 850169 | 11 | 420 | 4620 | 0.0028227 | 0.00067206
2012-07-18 | 243:80083 | SHORT RURAL | Planned Outage | 850221 | 30 | 405 | 12150 | 0.0074232 | 0.0018329
2012-07-18 | 258:80785 | URBAN | Planned Outage | 850222 | 1 | 120 | 120 | 7.3316e-05 | 6.1096e-05
2012-07-18 | 232:11454 | SHORT RURAL | Planned Outage | 850224 | 110 | 45 | 4950 | 0.0030243 | 0.0067206
2012-07-18 | 232:11454 | SHORT RURAL | Planned Outage | 850225 | 1 | 400 | 400 | 0.00024439 | 6.1096e-05
2012-07-19 | 202:34253 | URBAN | Planned Outage | 850236 | 30 | 145 | 4350 | 0.0026577 | 0.0018329
2012-07-18 | 264:81240 | SHORT RURAL | Planned Outage | 850238 | 16 | 430 | 6880 | 0.0042034 | 0.00097754
2012-07-18 | 513:48059 | SHORT RURAL | Planned Outage | 850247 | 12 | 358 | 4296 | 0.0026247 | 0.00073316
2012-07-18 | 803:74007 | SHORT RURAL | Planned Outage | 850249 | 14 | 295 | 4130 | 0.0025233 | 0.00085535
2012-07-19 | ZN12580:PA2 | URBAN | Planned Outage | 850568 | 11 | 315 | 1245 | 0.00076065 | 0.00067206
2012-07-19 | ZN931:PA31 | URBAN | Planned Outage | 850602 | 2 | 120 | 240 | 0.00014663 | 0.00012219
2012-07-19 | ZN931:PA13 | URBAN | Planned Outage | 850621 | 1 | 120 | 120 | 7.3316e-05 | 6.1096e-05
2012-07-19 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 850625 | 3 | 480 | 1440 | 0.00087979 | 0.00018329
2012-07-19 | ZN12570:PA8 | SHORT RURAL | Planned Outage | 850630 | 2 | 480 | 960 | 0.00058653 | 0.00012219
2012-07-19 | ZN180:PA10 | URBAN | Planned Outage | 850631 | 88 | 420 | 36960 | 0.022581 | 0.0053765
2012-07-20 | ZN12580:PA2 | URBAN | Planned Outage | 850632 | 273 | 300 | 27300 | 0.016679 | 0.016679
2012-07-21 | 507:80923 | SHORT RURAL | Planned Outage | 850851 | 40 | 345 | 13800 | 0.0084313 | 0.0024439
2012-07-20 | ZN12640:PA10 | URBAN | Planned Outage | 851412 | 250 | 510 | 127500 | 0.077898 | 0.015274
2012-07-20 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 851414 | 6 | 480 | 2880 | 0.0017596 | 0.00036658
2012-07-20 | ZN14892:PA13 | URBAN | Planned Outage | 851416 | 153 | 480 | 73440 | 0.044869 | 0.0093478
2012-07-20 | ZN2835:PA41 | URBAN | Planned Outage | 851427 | 28 | 330 | 9240 | 0.0056453 | 0.0017107
2012-07-21 | ZN342:PA18 | URBAN | Planned Outage | 851431 | 1 | 20 | 20 | 1.2219e-05 | 6.1097e-05
2012-07-21 | ZN2635:PA14 | URBAN | Planned Outage | 851436 | 8 | 510 | 4080 | 0.0024927 | 0.00048877
2012-07-21 | ZN3288:PA41 42ABC | CBD | Planned Outage | 851438 | 4 | 360 | 1440 | 0.00087979 | 0.00024439
2012-07-21 | ZN2473:PA20 | URBAN | Planned Outage | 851447 | 45 | 90 | 4050 | 0.0024744 | 0.0027493
2012-07-22 | ZN2466:PA26 | URBAN | Planned Outage | 851451 | 1 | 510 | 510 | 0.00031159 | 6.1097e-05
2012-07-22 | ZN180:PA7 | URBAN | Planned Outage | 851457 | 12 | 420 | 5040 | 0.0030793 | 0.00073316
2012-07-19 | 511:29878 | SHORT RURAL | Planned Outage | 851579 | 91 | 165 | 15015 | 0.0091736 | 0.0055598
2012-07-19 | 232:11459 | SHORT RURAL | Planned Outage | 851588 | 179 | 450 | 80550 | 0.049213 | 0.010936
2012-07-22 | 515:35200 | URBAN | Planned Outage | 851614 | 8 | 390 | 3120 | 0.0019062 | 0.00048877
2012-07-19 | 258:80784 | URBAN | Planned Outage | 851621 | 124 | 150 | 18600 | 0.011364 | 0.007576
2012-07-20 | 264:81240 | SHORT RURAL | Planned Outage | 851634 | 20 | 230 | 4600 | 0.0028104 | 0.0012219
2012-07-20 | 227:13019 | SHORT RURAL | Planned Outage | 851637 | 12 | 280 | 3360 | 0.0020528 | 0.00073316
2012-07-20 | 227:13020 | SHORT RURAL | Planned Outage | 851653 | 16 | 90 | 1440 | 0.00087979 | 0.00097755
2012-07-22 | 202:34232 | URBAN | Planned Outage | 851656 | 99 | 390 | 38610 | 0.023589 | 0.0060486
2012-07-22 | 258:80776 | URBAN | Planned Outage | 851658 | 1 | 790 | 790 | 0.00048266 | 6.1097e-05
2012-07-19 | 510:48164 | SHORT RURAL | Planned Outage | 851663 | 37 | 295 | 10915 | 0.0066687 | 0.0022606
2012-07-19 | 509:48039 | LONG RURAL | Planned Outage | 851664 | 12 | 330 | 3960 | 0.0024194 | 0.00073316
2012-07-21 | 507:80923 | SHORT RURAL | Planned Outage | 851665 | 106 | 495 | 52470 | 0.032057 | 0.0064762
2012-07-19 | 513:48058 | URBAN | Planned Outage | 851666 | 52 | 405 | 21060 | 0.012867 | 0.003177
2012-07-20 | 806:74080 | SHORT RURAL | Planned Outage | 851669 | 1 | 290 | 290 | 0.00017718 | 6.1097e-05
2012-07-22 | 810:74054 | LONG RURAL | Planned Outage | 851671 | 1 | 85 | 85 | 5.1932e-05 | 6.1097e-05
2012-07-22 | 810:74054 | LONG RURAL | Planned Outage | 851675 | 1 | 60 | 60 | 3.6658e-05 | 6.1097e-05
2012-07-22 | 810:74054 | LONG RURAL | Planned Outage | 851676 | 1 | 75 | 75 | 4.5822e-05 | 6.1097e-05
2012-07-22 | 810:74054 | LONG RURAL | Planned Outage | 851678 | 1 | 55 | 55 | 3.3603e-05 | 6.1097e-05
2012-07-23 | 227:13019 | SHORT RURAL | Planned Outage | 851969 | 12 | 270 | 3240 | 0.0019795 | 0.00073316
2012-07-23 | 213:33773 | SHORT RURAL | Planned Outage | 851970 | 3 | 320 | 960 | 0.00058653 | 0.00018329
2012-07-23 | 227:13015 | SHORT RURAL | Planned Outage | 851971 | 14 | 355 | 4970 | 0.0030365 | 0.00085535
2012-07-24 | 232:33411 | SHORT RURAL | Planned Outage | 852015 | 1 | 465 | 465 | 0.0002841 | 6.1097e-05
2012-07-25 | 238:34141 | SHORT RURAL | Planned Outage | 852397 | 10 | 360 | 3600 | 0.0021995 | 0.00061097
2012-07-24 | 243:80081 | URBAN | Planned Outage | 852425 | 1 | 80 | 80 | 4.8877e-05 | 6.1097e-05
2012-07-24 | 264:81240 | SHORT RURAL | Planned Outage | 852426 | 42 | 353 | 14826 | 0.0090582 | 0.0025661
2012-07-24 | 218:7482 | URBAN | Planned Outage | 852428 | 68 | 295 | 20060 | 0.012256 | 0.0041546
2012-07-24 | 203:8085 | URBAN | Planned Outage | 852437 | 96 | 480 | 46080 | 0.028153 | 0.0058653
2012-07-24 | 509:48040 | SHORT RURAL | Planned Outage | 852441 | 2 | 115 | 230 | 0.00014052 | 0.00012219
2012-07-24 | 509:48040 | SHORT RURAL | Planned Outage | 852444 | 2 | 115 | 230 | 0.00014052 | 0.00012219
2012-07-24 | 512:48049 | SHORT RURAL | Planned Outage | 852450 | 2 | 78 | 156 | 9.5311e-05 | 0.00012219
2012-07-24 | 514:18137 | SHORT RURAL | Planned Outage | 852458 | 2 | 460 | 920 | 0.00056209 | 0.00012219
2012-07-24 | 813:89062 | SHORT RURAL | Planned Outage | 852491 | 1 | 56 | 56 | 3.4214e-05 | 6.1097e-05
2012-07-25 | 258:80793 | SHORT RURAL | Planned Outage | 852672 | 82 | 300 | 24600 | 0.01503 | 0.0050099
2012-07-25 | 228:7490 | SHORT RURAL | Planned Outage | 853133 | 30 | 420 | 12600 | 0.0076982 | 0.0018329
2012-07-25 | 243:80083 | SHORT RURAL | Planned Outage | 853135 | 30 | 495 | 14850 | 0.0090729 | 0.0018329
2012-07-25 | 524:33580 | SHORT RURAL | Planned Outage | 853151 | 49 | 60 | 2940 | 0.0017962 | 0.0029937
2012-07-25 | 810:74054 | LONG RURAL | Planned Outage | 853167 | 10 | 135 | 1350 | 0.00082481 | 0.00061097
2012-07-25 | 807:74183 | SHORT RURAL | Planned Outage | 853172 | 8 | 180 | 1440 | 0.00087979 | 0.00048877
2012-07-27 | ZN269:PA16 | URBAN | Planned Outage | 853520 | 101 | 480 | 48480 | 0.02962 | 0.0061708
2012-07-27 | 238:34141 | SHORT RURAL | Planned Outage | 853570 | 86 | 450 | 38700 | 0.023645 | 0.0052543
2012-07-26 | 234:2001 | URBAN | Planned Outage | 853611 | 138 | 120 | 16560 | 0.010118 | 0.0084314
2012-07-26 | 511:29878 | SHORT RURAL | Planned Outage | 853616 | 4 | 400 | 1600 | 0.00097755 | 0.00024439
2012-07-26 | 502:48010 | SHORT RURAL | Planned Outage | 853619 | 27 | 55 | 1485 | 0.00090729 | 0.0016496
2012-07-26 | 807:74184 | SHORT RURAL | Planned Outage | 853620 | 1 | 47 | 47 | 2.8716e-05 | 6.1097e-05
2012-07-26 | 810:74054 | LONG RURAL | Planned Outage | 853621 | 1 | 70 | 70 | 4.2768e-05 | 6.1097e-05
2012-07-28 | ZN15005:PA12 | URBAN | Planned Outage | 853975 | 233 | 439.05 | 102298.65 | 0.062501 | 0.014236
2012-07-29 | 513:48050 | SHORT RURAL | Planned Outage | 854342 | 108 | 420 | 45360 | 0.027714 | 0.0065985
2012-07-29 | 507:80923 | SHORT RURAL | Planned Outage | 854345 | 114 | 420 | 47880 | 0.029253 | 0.0069651
2012-07-27 | 224:80337 | URBAN | Planned Outage | 854356 | 1 | 260 | 260 | 0.00015885 | 6.1097e-05
2012-07-27 | 503:48012 | URBAN | Planned Outage | 854368 | 137 | 345 | 47265 | 0.028878 | 0.0083703
2012-07-27 | 509:48039 | LONG RURAL | Planned Outage | 854370 | 2 | 180 | 360 | 0.00021995 | 0.00012219
2012-07-22 | ZN263:PA35 37KLM | CBD | Planned Outage | 854381 | 155 | 2160 | 334800 | 0.20455 | 0.00947
2012-07-27 | 810:74054 | LONG RURAL | Planned Outage | 854415 | 2 | 145 | 290 | 0.00017718 | 0.00012219
2012-07-29 | 523:33508 | SHORT RURAL | Planned Outage | 854416 | 5 | 555 | 2775 | 0.0016954 | 0.00030549
2012-07-23 | ZN15013:PA4 | URBAN | Planned Outage | 854525 | 5 | 480 | 2400 | 0.0014663 | 0.00030548
2012-07-23 | ZN12620:PA8 | SHORT RURAL | Planned Outage | 854526 | 1 | 3360 | 3360 | 0.0020528 | 6.1097e-05
2012-07-23 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 854551 | 45 | 495 | 22275 | 0.013609 | 0.0027493
2012-07-23 | ZN12570:PA12 | SHORT RURAL | Planned Outage | 854559 | 3 | 480 | 1440 | 0.00087979 | 0.00018329
2012-07-23 | ZN12570:PA19 | URBAN | Planned Outage | 854562 | 52 | 480 | 24960 | 0.01525 | 0.003177
2012-07-23 | ZN14892:PA13 | URBAN | Planned Outage | 854563 | 53 | 480 | 25440 | 0.015543 | 0.0032381
2012-07-23 | ZN12640:PA8 | SHORT RURAL | Planned Outage | 854564 | 38 | 360 | 13680 | 0.008358 | 0.0023217
2012-07-24 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 854578 | 304 | 510 | 143400 | 0.087613 | 0.018573
2012-07-24 | ZN15001:PA15 | URBAN | Planned Outage | 854595 | 61 | 480 | 29280 | 0.017889 | 0.0037269
2012-07-25 | ZN12620:PA13 | SHORT RURAL | Planned Outage | 854597 | 154 | 480 | 9240 | 0.0056453 | 0.0094089
2012-07-25 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 854601 | 3 | 480 | 1440 | 0.00087979 | 0.00018329
2012-07-25 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 854603 | 9 | 480 | 4320 | 0.0026394 | 0.00054987
2012-07-25 | ZN12610:PA20 | SHORT RURAL | Planned Outage | 854606 | 90 | 480 | 43200 | 0.026394 | 0.0054987
2012-07-25 | ZN14892:PA13 | URBAN | Planned Outage | 854608 | 153 | 480 | 73440 | 0.04487 | 0.0093478
2012-07-25 | ZN384:PA22 | URBAN | Planned Outage | 854610 | 2 | 540 | 1080 | 0.00065985 | 0.00012219
2012-07-25 | ZN9700:PA23 | URBAN | Planned Outage | 854806 | 31 | 450 | 13950 | 0.008523 | 0.001894
2012-07-25 | ZN1068:PA27 | URBAN | Planned Outage | 854808 | 11 | 540 | 5940 | 0.0036292 | 0.00067207
2012-07-25 | ZN1068:PA18 | URBAN | Planned Outage | 854809 | 15 | 540 | 8100 | 0.0049488 | 0.00091645
2012-07-26 | ZN188:PA9 | URBAN | Planned Outage | 854812 | 2 | 19 | 38 | 2.3217e-05 | 0.00012219
2012-07-26 | ZN188:PA9 | URBAN | Planned Outage | 854815 | 5 | 20 | 100 | 6.1097e-05 | 0.00030549
2012-07-26 | ZN14892:PA13 | URBAN | Planned Outage | 854816 | 153 | 480 | 73440 | 0.04487 | 0.0093478
2012-07-26 | ZN188:PA4 | URBAN | Planned Outage | 854819 | 1 | 330 | 330 | 0.00020162 | 6.1097e-05
2012-07-26 | ZN15001:PA2 | URBAN | Planned Outage | 854822 | 27 | 60 | 1620 | 0.00098977 | 0.0016496
2012-07-27 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 854825 | 48 | 510 | 2880 | 0.0017596 | 0.0029327
2012-07-27 | ZN12650:PA6 | URBAN | Planned Outage | 854836 | 89 | 480 | 42720 | 0.026101 | 0.0054376
2012-07-27 | ZN2473:PA20 | URBAN | Planned Outage | 854837 | 45 | 270 | 12150 | 0.0074233 | 0.0027494
2012-07-27 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 854843 | 20 | 420 | 8400 | 0.0051321 | 0.0012219
2012-07-28 | ZN2473:PA1 | URBAN | Planned Outage | 854863 | 37 | 420 | 15540 | 0.0094945 | 0.0022606
2012-07-29 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 854870 | 4 | 600 | 240 | 0.00014663 | 0.00024439
2012-07-30 | ZN4990:PA51 52ABC | CBD | Planned Outage | 854877 | 1 | 300 | 300 | 0.00018329 | 6.1097e-05
2012-07-30 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 854881 | 4 | 600 | 240 | 0.00014663 | 0.00024439
2012-07-30 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 854884 | 23 | 480 | 11040 | 0.0067451 | 0.0014052
2012-07-30 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 854890 | 6 | 480 | 2880 | 0.0017596 | 0.00036658
2012-07-30 | ZN180:PA10 | URBAN | Planned Outage | 854892 | 255 | 420 | 107100 | 0.065435 | 0.01558
2012-07-30 | ZN9900:PA1 | URBAN | Planned Outage | 854897 | 2 | 300 | 600 | 0.00036658 | 0.00012219
2012-07-30 | 232:33413 | SHORT RURAL | Planned Outage | 855010 | 3 | 365 | 1095 | 0.00066901 | 0.00018329
2012-07-30 | 232:11459 | SHORT RURAL | Planned Outage | 855013 | 316 | 555 | 175380 | 0.10715 | 0.019307
2012-07-30 | 227:13015 | SHORT RURAL | Planned Outage | 855024 | 110 | 360 | 39600 | 0.024194 | 0.0067207
2012-07-30 | 208:59 | URBAN | Planned Outage | 855033 | 52 | 285 | 14820 | 0.0090546 | 0.003177
2012-07-30 | 524:33572 | SHORT RURAL | Planned Outage | 855035 | 7 | 30 | 210 | 0.0001283 | 0.00042768
2012-07-30 | 513:48059 | SHORT RURAL | Planned Outage | 855042 | 23 | 210 | 4830 | 0.002951 | 0.0014052
2012-07-31 | 807:74180 | SHORT RURAL | Planned Outage | 855290 | 20 | 165 | 3300 | 0.0020162 | 0.001222
2012-07-31 | 227:13020 | SHORT RURAL | Planned Outage | 855293 | 27 | 220 | 5940 | 0.0036292 | 0.0016496
2012-07-31 | 232:33413 | SHORT RURAL | Planned Outage | 855306 | 39 | 313 | 12207 | 0.0074582 | 0.0023828
2012-07-31 | 511:29878 | SHORT RURAL | Planned Outage | 855308 | 1 | 115 | 115 | 7.0262e-05 | 6.1098e-05
2012-07-31 | 509:48039 | LONG RURAL | Planned Outage | 855309 | 1 | 120 | 120 | 7.3317e-05 | 6.1098e-05
2012-07-31 | 511:29876 | SHORT RURAL | Planned Outage | 855310 | 12 | 335 | 4020 | 0.0024561 | 0.00073317
2012-07-31 | 523:33508 | SHORT RURAL | Planned Outage | 855312 | 4 | 95 | 380 | 0.00023217 | 0.00024439
2012-07-31 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 855314 | 66 | 540 | 17820 | 0.010888 | 0.0040324
2012-07-31 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 855320 | 59 | 480 | 11220 | 0.0068551 | 0.0036048
2012-07-31 | ZN12640:PA10 | URBAN | Planned Outage | 855326 | 115 | 480 | 55200 | 0.033726 | 0.0070262
2012-07-31 | ZN12570:PA12 | SHORT RURAL | Planned Outage | 855328 | 38 | 480 | 18240 | 0.011144 | 0.0023217
2012-07-31 | ZN12650:PA6 | URBAN | Planned Outage | 855331 | 11 | 480 | 5280 | 0.003226 | 0.00067207
2012-07-31 | ZN14892:PA13 | URBAN | Planned Outage | 855804 | 306 | 1920 | 146880 | 0.08974 | 0.018696
2012-08-02 | 232:11453 | SHORT RURAL | Planned Outage | 855819 | 76 | 540 | 41040 | 0.025075 | 0.0046435
2012-08-02 | 232:33411 | SHORT RURAL | Planned Outage | 855819 | 315 | 540 | 170100 | 0.10393 | 0.019246
2012-08-02 | 810:74058 | SHORT RURAL | Planned Outage | 855841 | 47 | 315 | 14805 | 0.0090456 | 0.0028716
2012-08-01 | ZN12570:PA2 | SHORT RURAL | Planned Outage | 855847 | 208 | 480 | 99840 | 0.061 | 0.012708
2012-08-01 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 855847 | 89 | 480 | 42720 | 0.026101 | 0.0054377
2012-08-01 | ZN12580:PA16 | URBAN | Planned Outage | 855857 | 10 | 480 | 4800 | 0.0029327 | 0.00061098
2012-08-01 | ZN3155:PA21 | URBAN | Planned Outage | 855858 | 132 | 420 | 55440 | 0.033873 | 0.0080649
2012-08-01 | ZN15001:PA15 | URBAN | Planned Outage | 855866 | 61 | 480 | 29280 | 0.017889 | 0.003727
2012-08-01 | ZN14891:PA10 | SHORT RURAL | Planned Outage | 855870 | 75 | 780 | 33060 | 0.020199 | 0.0045823
2012-08-02 | ZN12650:PA6 | URBAN | Planned Outage | 855885 | 26 | 570 | 2340 | 0.0014297 | 0.0015886
2012-08-01 | 232:33413 | SHORT RURAL | Planned Outage | 855886 | 39 | 390 | 15210 | 0.009293 | 0.0023828
2012-08-02 | ZN195:PA30 | URBAN | Planned Outage | 855888 | 22 | 60 | 1320 | 0.0008065 | 0.0013442
2012-08-01 | 238:34141 | SHORT RURAL | Planned Outage | 855895 | 28 | 375 | 10500 | 0.0064153 | 0.0017107
2012-08-01 | 510:48164 | SHORT RURAL | Planned Outage | 855900 | 2 | 190 | 380 | 0.00023217 | 0.0001222
2012-08-01 | 509:48039 | LONG RURAL | Planned Outage | 855903 | 4 | 30 | 120 | 7.3318e-05 | 0.00024439
2012-08-01 | 510:48164 | SHORT RURAL | Planned Outage | 855904 | 1 | 45 | 45 | 2.7494e-05 | 6.1098e-05
2012-08-01 | 813:89061 | LONG RURAL | Planned Outage | 855905 | 19 | 200 | 3800 | 0.0023217 | 0.0011609
2012-08-01 | 515:35197 | LONG RURAL | Planned Outage | 855907 | 4 | 290 | 1160 | 0.00070874 | 0.00024439
2012-08-01 | 512:48049 | SHORT RURAL | Planned Outage | 855909 | 2 | 275 | 550 | 0.00033604 | 0.0001222
2012-08-02 | 501:48115 | SHORT RURAL | Planned Outage | 856260 | 133 | 520 | 69160 | 0.042256 | 0.0081261
2012-08-02 | 813:89055 | SHORT RURAL | Planned Outage | 856263 | 1 | 78 | 78 | 4.7657e-05 | 6.1098e-05
2012-08-02 | 513:48059 | SHORT RURAL | Planned Outage | 856268 | 12 | 310 | 3720 | 0.0022729 | 0.00073318
2012-08-02 | 810:74050 | SHORT RURAL | Planned Outage | 856270 | 3 | 280 | 840 | 0.00051323 | 0.0001833
2012-08-02 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 856274 | 6 | 600 | 3600 | 0.0021995 | 0.00036659
2012-08-02 | ZN931:PA8 | URBAN | Planned Outage | 856276 | 67 | 300 | 20100 | 0.012281 | 0.0040936
2012-08-02 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 856277 | 13 | 450 | 5850 | 0.0035743 | 0.00079428
2012-08-02 | ZN14892:PA13 | URBAN | Planned Outage | 856281 | 154 | 480 | 73920 | 0.045164 | 0.0094092
2012-08-02 | ZN195:PA28 | URBAN | Planned Outage | 856283 | 32 | 360 | 11520 | 0.0070385 | 0.0019551
2012-08-02 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 856288 | 10 | 300 | 3000 | 0.001833 | 0.00061098
2012-07-19 | 232:11459 | SHORT RURAL | Planned Outage | 856393 | 7 | 420 | 2940 | 0.0017962 | 0.00042767
2012-07-20 | 232:11459 | SHORT RURAL | Planned Outage | 856395 | 7 | 395 | 2765 | 0.0016893 | 0.00042768
2012-07-23 | 232:11459 | SHORT RURAL | Planned Outage | 856396 | 7 | 485 | 3395 | 0.0020742 | 0.00042768
2012-07-24 | 232:11459 | SHORT RURAL | Planned Outage | 856397 | 7 | 420 | 2940 | 0.0017962 | 0.00042768
2012-07-25 | 232:11459 | SHORT RURAL | Planned Outage | 856398 | 7 | 480 | 3360 | 0.0020529 | 0.00042768
2012-07-26 | 232:11459 | SHORT RURAL | Planned Outage | 856401 | 7 | 495 | 3465 | 0.002117 | 0.00042768
2012-07-27 | 232:11459 | SHORT RURAL | Planned Outage | 856402 | 7 | 400 | 2800 | 0.0017107 | 0.00042768
2012-07-30 | 232:11459 | SHORT RURAL | Planned Outage | 856404 | 7 | 380 | 2660 | 0.0016252 | 0.00042768
2012-08-01 | 232:11459 | SHORT RURAL | Planned Outage | 856406 | 7 | 395 | 2765 | 0.0016894 | 0.00042769
2012-08-02 | 232:11459 | SHORT RURAL | Planned Outage | 856407 | 7 | 345 | 2415 | 0.0014755 | 0.00042769
2012-08-05 | 225:33676 | SHORT RURAL | Planned Outage | 856826 | 104 | 647 | 67288 | 0.041112 | 0.0063542
2012-08-05 | 225:33670 | SHORT RURAL | Planned Outage | 856827 | 31 | 660 | 20460 | 0.012501 | 0.0018941
2012-08-03 | ZN129:PA5 | URBAN | Planned Outage | 856910 | 8 | 630 | 5040 | 0.0030794 | 0.00048879
2012-08-03 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 856916 | 60 | 480 | 17880 | 0.010924 | 0.0036659
2012-08-03 | ZN12570:PA12 | SHORT RURAL | Planned Outage | 856927 | 2 | 420 | 840 | 0.00051323 | 0.0001222
2012-08-03 | ZN36300:PA17 | URBAN | Planned Outage | 856934 | 30 | 540 | 16200 | 0.0098979 | 0.001833
2012-08-04 | ZN14143:PA10 | SHORT RURAL | Planned Outage | 856941 | 1 | 450 | 450 | 0.00027494 | 6.1098e-05
2012-08-04 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 856941 | 2 | 450 | 900 | 0.00054989 | 0.0001222
2012-08-04 | ZN2568:PA21 | URBAN | Planned Outage | 856943 | 2 | 240 | 480 | 0.00029327 | 0.0001222
2012-08-03 | 227:13020 | SHORT RURAL | Planned Outage | 856979 | 2 | 210 | 420 | 0.00025661 | 0.0001222
2012-08-03 | 213:33771 | URBAN | Planned Outage | 856981 | 3 | 375 | 1125 | 0.00068736 | 0.0001833
2012-08-04 | 232:33413 | SHORT RURAL | Planned Outage | 856985 | 209 | 365 | 76285 | 0.046609 | 0.01277
2012-08-06 | ZN3155:PA20 | URBAN | Planned Outage | 857000 | 76 | 390 | 18709.9333 | 0.011431 | 0.0046435
2012-08-06 | ZN3155:PA34 | SHORT RURAL | Planned Outage | 857000 | 119 | 390 | 46410 | 0.028356 | 0.0072707
2012-08-05 | 240:34843 | URBAN | Planned Outage | 857037 | 2 | 345 | 690 | 0.00042158 | 0.0001222
2012-08-05 | 203:8088 | URBAN | Planned Outage | 857046 | 48 | 440 | 21120 | 0.012904 | 0.0029327
2012-08-05 | 205:12206 | URBAN | Planned Outage | 857049 | 2 | 320 | 640 | 0.00039103 | 0.0001222
2012-08-05 | 258:80787 | URBAN | Planned Outage | 857059 | 1 | 366 | 366 | 0.00022362 | 6.1098e-05
2012-08-03 | 235:2120 | SHORT RURAL | Planned Outage | 857076 | 9 | 480 | 4320 | 0.0026395 | 0.00054989
2012-08-03 | 238:34144 | URBAN | Planned Outage | 857078 | 13 | 530 | 6890 | 0.0042097 | 0.00079428
2012-08-04 | 524:33580 | SHORT RURAL | Planned Outage | 857082 | 1 | 563 | 563 | 0.00034398 | 6.1098e-05
2012-08-04 | 511:29877 | SHORT RURAL | Planned Outage | 857090 | 5 | 345 | 1725 | 0.0010539 | 0.00030549
2012-08-04 | 509:48040 | SHORT RURAL | Planned Outage | 857095 | 9 | 320 | 2880 | 0.0017596 | 0.00054989
2012-08-04 | 512:48047 | SHORT RURAL | Planned Outage | 857096 | 6 | 320 | 1920 | 0.0011731 | 0.00036659
2012-08-05 | 525:34586 | SHORT RURAL | Planned Outage | 857108 | 3 | 446 | 1338 | 0.0008175 | 0.0001833
2012-08-05 | 525:34589 | URBAN | Planned Outage | 857108 | 1 | 446 | 446 | 0.0002725 | 6.1098e-05
2012-08-03 | 514:18141 | SHORT RURAL | Planned Outage | 857112 | 5 | 320 | 1600 | 0.00097757 | 0.00030549
2012-08-03 | 806:74076 | SHORT RURAL | Planned Outage | 857151 | 2 | 225 | 450 | 0.00027494 | 0.0001222
2012-08-03 | 811:74234 | SHORT RURAL | Planned Outage | 857155 | 1 | 435 | 435 | 0.00026578 | 6.1098e-05
2012-08-04 | 811:74234 | SHORT RURAL | Planned Outage | 857159 | 109 | 310 | 33790 | 0.020645 | 0.0066597
2012-08-05 | 812:19065 | SHORT RURAL | Planned Outage | 857168 | 14 | 38 | 532 | 0.00032504 | 0.00085538
2012-08-05 | 523:33501 | SHORT RURAL | Planned Outage | 857169 | 3 | 315 | 945 | 0.00057738 | 0.0001833
2012-08-06 | ZN1285:PA29 | URBAN | Planned Outage | 857456 | 11 | 420 | 4620 | 0.0028227 | 0.00067208
2012-08-06 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 857462 | 6 | 480 | 2880 | 0.0017596 | 0.00036659
2012-08-06 | ZN12570:PA12 | SHORT RURAL | Planned Outage | 857465 | 66 | 420 | 27720 | 0.016936 | 0.0040325
2012-08-06 | ZN965:PA24 | SHORT RURAL | Planned Outage | 857468 | 48 | 300 | 14400 | 0.0087982 | 0.0029327
2012-08-07 | ZN12610:PA10 | SHORT RURAL | Planned Outage | 857845 | 39 | 480 | 18720 | 0.011438 | 0.0023828
2012-08-07 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 857849 | 16 | 480 | 7680 | 0.0046924 | 0.00097758
2012-08-07 | ZN12610:PA24 | SHORT RURAL | Planned Outage | 857856 | 75 | 480 | 36000 | 0.021995 | 0.0045824
2012-08-07 | ZN9900:PA5 | URBAN | Planned Outage | 857857 | 73 | 360 | 26280 | 0.016057 | 0.0044602
2012-08-07 | ZN12590:PA3 | SHORT RURAL | Planned Outage | 857860 | 64 | 270 | 17280 | 0.010558 | 0.0039103
2012-08-08 | 810:74058 | SHORT RURAL | Planned Outage | 857880 | 18 | 235 | 4230 | 0.0025909 | 0.0011025
2012-08-07 | 256:80632 | URBAN | Planned Outage | 857926 | 107 | 420 | 44940 | 0.027458 | 0.0065375
2012-08-07 | 231:8415 | SHORT RURAL | Planned Outage | 857927 | 1 | 320 | 320 | 0.00019552 | 6.1099e-05
2012-08-08 | 232:11459 | SHORT RURAL | Planned Outage | 857964 | 305 | 315 | 96075 | 0.058846 | 0.018681
2012-08-07 | 238:34141 | SHORT RURAL | Planned Outage | 857997 | 8 | 340 | 2720 | 0.0016619 | 0.00048879
2012-08-07 | 801:74121 | SHORT RURAL | Planned Outage | 857998 | 5 | 270 | 1350 | 0.00082483 | 0.00030549
2012-08-07 | 523:33501 | SHORT RURAL | Planned Outage | 858000 | 1 | 163 | 163 | 9.9591e-05 | 6.1099e-05
2012-08-07 | 801:74121 | SHORT RURAL | Planned Outage | 858003 | 12 | 315 | 3780 | 0.0023095 | 0.00073318
2012-08-07 | 514:18137 | SHORT RURAL | Planned Outage | 858025 | 2 | 210 | 420 | 0.00025661 | 0.0001222
2012-08-08 | 264:81240 | SHORT RURAL | Planned Outage | 858408 | 11 | 360 | 3960 | 0.0024255 | 0.00067376
2012-08-08 | 232:33413 | SHORT RURAL | Planned Outage | 858421 | 39 | 450 | 17550 | 0.010749 | 0.0023888
2012-08-08 | 221:11898 | URBAN | Planned Outage | 858452 | 3 | 190 | 570 | 0.00034913 | 0.00018375
2012-08-08 | 512:48049 | SHORT RURAL | Planned Outage | 858454 | 3 | 160 | 480 | 0.000294 | 0.00018375
2012-08-08 | 810:74054 | LONG RURAL | Planned Outage | 858459 | 6 | 200 | 1200 | 0.00073501 | 0.0003675
2012-08-08 | ZN3154:PA22 | URBAN | Planned Outage | 858615 | 4 | 540 | 120 | 7.3501e-05 | 0.000245
2012-08-08 | ZN12640:PA18 | SHORT RURAL | Planned Outage | 858636 | 279 | 480 | 88560 | 0.054244 | 0.017089
2012-08-08 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 858670 | 23 | 570 | 13110 | 0.0080299 | 0.0014088
2012-08-08 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 858696 | 49 | 480 | 23520 | 0.014406 | 0.0030013
2012-08-13 | 509:48039 | LONG RURAL | Planned Outage | 862209 | 10 | 405 | 4050 | 0.0024745 | 0.00061099
2012-08-08 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 862234 | 13 | 480 | 6240 | 0.003822 | 0.00079626
2012-08-08 | ZN12640:PA19 | URBAN | Planned Outage | 862253 | 145 | 450 | 65250 | 0.039966 | 0.0088813
2012-08-08 | ZN14891:PA10 | SHORT RURAL | Planned Outage | 862290 | 75 | 300 | 22500 | 0.013781 | 0.0045938
2012-08-08 | ZN3155:PA34 | SHORT RURAL | Planned Outage | 862771 | 58 | 390 | 22620 | 0.013855 | 0.0035525
2012-08-08 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 862781 | 5 | 480 | 2400 | 0.00147 | 0.00030625
2012-08-13 | ZN188:PA3 | URBAN | Planned Outage | 862852 | 2 | 510 | 1020 | 0.00062321 | 0.0001222
2012-08-14 | 514:18137 | SHORT RURAL | Planned Outage | 862926 | 77 | 300 | 23100 | 0.014114 | 0.0047046
2012-08-13 | ZN10993:PA8 | URBAN | Planned Outage | 863004 | 1 | 330 | 330 | 0.00020163 | 6.1099e-05
2012-08-13 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 863015 | 12 | 450 | 5400 | 0.0032993 | 0.00073318
2012-08-13 | ZN14891:PA1 | SHORT RURAL | Planned Outage | 863017 | 12 | 480 | 5760 | 0.0035193 | 0.00073318
2012-08-13 | ZN12570:PA16 | SHORT RURAL | Planned Outage | 863019 | 11 | 480 | 5280 | 0.003226 | 0.00067208
2012-08-13 | ZN12570:PA19 | URBAN | Planned Outage | 863020 | 94 | 1200 | 112800 | 0.068919 | 0.0057433
2012-08-14 | ZN12650:PA10 | URBAN | Planned Outage | 863025 | 1 | 30 | 30 | 1.833e-05 | 6.1099e-05
2012-08-14 | ZN3472:PA21 | URBAN | Planned Outage | 863026 | 1 | 270 | 270 | 0.00016497 | 6.1099e-05
2012-08-09 | 511:29877 | SHORT RURAL | Planned Outage | 863052 | 27 | 422 | 11394 | 0.0069886 | 0.0016561
2012-08-09 | 216:10723 | URBAN | Planned Outage | 863055 | 223 | 150 | 33450 | 0.020517 | 0.013678
2012-08-09 | 516:48065 | SHORT RURAL | Planned Outage | 863061 | 8 | 370 | 2960 | 0.0018155 | 0.00049069
2012-08-10 | 524:33572 | SHORT RURAL | Planned Outage | 863088 | 308 | 320 | 98560 | 0.060219 | 0.018818
2012-08-10 | 234:14291 | URBAN | Planned Outage | 863090 | 141 | 277 | 39057 | 0.023863 | 0.0086149
2012-08-12 | 203:8089 | URBAN | Planned Outage | 863093 | 7 | 155 | 1085 | 0.00066292 | 0.00042769
2012-08-09 | 501:48123 | SHORT RURAL | Planned Outage | 863097 | 20 | 540 | 10800 | 0.0066243 | 0.0012267
2012-08-10 | 503:48012 | URBAN | Planned Outage | 863102 | 107 | 230 | 24610 | 0.015036 | 0.0065376
2012-08-10 | 511:29876 | SHORT RURAL | Planned Outage | 863104 | 12 | 390 | 4680 | 0.0028594 | 0.00073318
2012-08-12 | 504:48033 | SHORT RURAL | Planned Outage | 863106 | 1 | 455 | 455 | 0.000278 | 6.1099e-05
2012-08-09 | 807:74184 | SHORT RURAL | Planned Outage | 863112 | 7 | 300 | 2100 | 0.0012881 | 0.00042935
2012-08-10 | 512:48049 | SHORT RURAL | Planned Outage | 863113 | 1 | 145 | 145 | 8.8593e-05 | 6.1099e-05
2012-08-10 | 810:74054 | LONG RURAL | Planned Outage | 863117 | 9 | 135 | 1215 | 0.00074235 | 0.00054989
2012-08-13 | 807:74180 | SHORT RURAL | Planned Outage | 863120 | 8 | 170 | 1360 | 0.00083094 | 0.00048879
2012-08-14 | ZN4545:PA4 | URBAN | Planned Outage | 863345 | 66 | 450 | 29700 | 0.018146 | 0.0040325
2012-08-14 | ZN12660:PA14 | SHORT RURAL | Planned Outage | 863347 | 38 | 480 | 18240 | 0.011144 | 0.0023217
2012-08-14 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 863397 | 12 | 480 | 5760 | 0.0035193 | 0.00073318
2012-08-14 | ZN12640:PA19 | URBAN | Planned Outage | 863403 | 145 | 480 | 69600 | 0.042525 | 0.0088593
2012-08-14 | ZN14144:PA1 | URBAN | Planned Outage | 863404 | 51 | 420 | 21420 | 0.013087 | 0.003116
2012-08-14 | ZN15001:PA17 | URBAN | Planned Outage | 863405 | 3 | 480 | 1440 | 0.00087982 | 0.0001833
2012-08-14 | 216:10729 | URBAN | Planned Outage | 863528 | 55 | 780 | 42900 | 0.026211 | 0.0033604
2012-08-15 | ZN12650:PA6 | URBAN | Planned Outage | 863556 | 215 | 480 | 103200 | 0.063054 | 0.013136
2012-08-14 | 235:2120 | SHORT RURAL | Planned Outage | 863570 | 9 | 500 | 4500 | 0.0027494 | 0.00054989
2012-08-14 | 502:48009 | URBAN | Planned Outage | 863577 | 42 | 140 | 5880 | 0.0035926 | 0.0025661
2012-08-14 | 807:74179 | SHORT RURAL | Planned Outage | 863579 | 1 | 120 | 120 | 7.3318e-05 | 6.1099e-05
2012-08-15 | 232:11459 | SHORT RURAL | Planned Outage | 863920 | 7 | 510 | 3570 | 0.0021812 | 0.00042769
2012-08-15 | 232:11457 | URBAN | Planned Outage | 863922 | 43 | 200 | 8600 | 0.0052545 | 0.0026272
2012-08-15 | 502:48004 | URBAN | Planned Outage | 863929 | 51 | 510 | 26010 | 0.015892 | 0.003116
2012-08-15 | 813:89061 | LONG RURAL | Planned Outage | 863932 | 18 | 255 | 4590 | 0.0028044 | 0.0010998
2012-08-15 | 516:48066 | SHORT RURAL | Planned Outage | 863935 | 14 | 330 | 4620 | 0.0028228 | 0.00085538
2012-08-15 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 863977 | 7 | 480 | 3360 | 0.0020529 | 0.00042769
2012-08-15 | ZN12570:PA2 | SHORT RURAL | Planned Outage | 864070 | 209 | 480 | 100320 | 0.061294 | 0.01277
2012-08-15 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 864070 | 89 | 480 | 42720 | 0.026101 | 0.0054378
2012-08-15 | ZN2602:PA21 | URBAN | Planned Outage | 864079 | 1 | 360 | 360 | 0.00021996 | 6.1099e-05
2012-08-16 | ZN15013:PA10 | SHORT RURAL | Planned Outage | 864358 | 1 | 480 | 480 | 0.00029327 | 6.1099e-05
2012-08-16 | ZN12570:PA19 | URBAN | Planned Outage | 864360 | 2 | 510 | 1020 | 0.00062321 | 0.0001222
2012-08-16 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 864365 | 51 | 540 | 27540 | 0.016827 | 0.003116
2012-08-16 | ZN10990:PA8 | URBAN | Planned Outage | 864374 | 13 | 540 | 7020 | 0.0042891 | 0.00079428
2012-08-16 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 864377 | 2 | 480 | 960 | 0.00058655 | 0.0001222
2012-08-16 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 864380 | 17 | 480 | 8160 | 0.0049856 | 0.0010387
2012-08-16 | 232:11459 | SHORT RURAL | Planned Outage | 864398 | 7 | 500 | 3500 | 0.0021385 | 0.00042769
2012-08-16 | 227:13019 | SHORT RURAL | Planned Outage | 864401 | 12 | 385 | 4620 | 0.0028228 | 0.00073318
2012-08-16 | 208:59 | URBAN | Planned Outage | 864405 | 51 | 310 | 15810 | 0.0096597 | 0.003116
2012-08-16 | 801:74121 | SHORT RURAL | Planned Outage | 864411 | 13 | 250 | 3250 | 0.0019857 | 0.00079428
2012-08-16 | 523:33508 | SHORT RURAL | Planned Outage | 864428 | 22 | 335 | 7370 | 0.004503 | 0.0013442
2012-08-06 | 232:11459 | SHORT RURAL | Planned Outage | 864435 | 7 | 500 | 3500 | 0.0021384 | 0.00042769
2012-08-16 | ZN14892:PA13 | URBAN | Planned Outage | 864510 | 153 | 480 | 73440 | 0.044871 | 0.0093481
2012-08-16 | ZN12610:PA22 | URBAN | Planned Outage | 864515 | 70 | 480 | 33600 | 0.020529 | 0.0042769
2012-08-16 | ZN35370:PA10 | SHORT RURAL | Planned Outage | 864517 | 64 | 420 | 26880 | 0.016423 | 0.0039103
2012-08-16 | ZN2635:PA17 | URBAN | Planned Outage | 864526 | 28 | 420 | 11760 | 0.0071852 | 0.0017108
2012-08-17 | ZN269:PA18 | URBAN | Planned Outage | 864534 | 165 | 60 | 9900 | 0.0060488 | 0.010081
2012-08-19 | ZN9301:PA13 | SHORT RURAL | Planned Outage | 865286 | 5 | 480 | 2400 | 0.0014664 | 0.00030549
2012-08-17 | ZN9700:PA12 | URBAN | Planned Outage | 865464 | 69 | 510 | 35190 | 0.021501 | 0.0042158
2012-08-17 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 865469 | 8 | 480 | 3840 | 0.0023462 | 0.00048879
2012-08-17 | ZN12570:PA12 | SHORT RURAL | Planned Outage | 865474 | 38 | 480 | 18240 | 0.011144 | 0.0023217
2012-08-17 | ZN9700:PA22 | URBAN | Planned Outage | 865476 | 35 | 420 | 14700 | 0.0089815 | 0.0021385
2012-08-17 | ZN8700:PA63 64DEF | CBD | Planned Outage | 865478 | 23 | 3540 | 81420 | 0.049747 | 0.0014053
2012-08-17 | ZN342:PA28 | URBAN | Planned Outage | 865484 | 1 | 60 | 60 | 3.6659e-05 | 6.1099e-05
2012-08-17 | ZN342:PA28 | URBAN | Planned Outage | 865494 | 1 | 2220 | 2220 | 0.0013564 | 6.1099e-05
2012-08-18 | ZN342:PA28 | URBAN | Planned Outage | 865496 | 1 | 810 | 810 | 0.0004949 | 6.1099e-05
2012-08-18 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 865502 | 2 | 30 | 60 | 3.6659e-05 | 0.0001222
2012-08-18 | ZN263:PA31 32GHJ | CBD | Planned Outage | 865505 | 167 | 15 | 2505 | 0.0015305 | 0.010203
2012-08-19 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 865508 | 27 | 600 | 2160 | 0.0013197 | 0.0016497
2012-08-19 | ZN1673:PA18 | URBAN | Planned Outage | 865520 | 1 | 480 | 480 | 0.00029327 | 6.1099e-05
2012-08-19 | ZN116:PA41 | URBAN | Planned Outage | 865534 | 37 | 420 | 15540 | 0.0094947 | 0.0022606
2012-08-19 | ZN2602:PA32 | URBAN | Planned Outage | 865537 | 2 | 120 | 240 | 0.00014664 | 0.0001222
2012-08-17 | 511:29878 | SHORT RURAL | Planned Outage | 865755 | 44 | 550 | 24200 | 0.014786 | 0.0026883
2012-08-18 | 507:80923 | SHORT RURAL | Planned Outage | 865759 | 2 | 420 | 840 | 0.00051323 | 0.0001222
2012-08-17 | 229:34983 | SHORT RURAL | Planned Outage | 865761 | 112 | 300 | 33600 | 0.020529 | 0.006843
2012-08-17 | 232:11459 | SHORT RURAL | Planned Outage | 865764 | 7 | 510 | 3570 | 0.0021812 | 0.00042769
2012-08-17 | 243:80083 | SHORT RURAL | Planned Outage | 865770 | 6 | 4613.3667 | 27680.2 | 0.016912 | 0.00036659
2012-08-18 | 232:11455 | URBAN | Planned Outage | 865772 | 76 | 105 | 7980 | 0.0048757 | 0.0046435
2012-08-18 | 232:11460 | URBAN | Planned Outage | 865775 | 15 | 210 | 3150 | 0.0019246 | 0.00091648
2012-08-17 | 511:29878 | SHORT RURAL | Planned Outage | 865779 | 204 | 550 | 112200 | 0.068553 | 0.012464
2012-08-17 | 238:34136 | URBAN | Planned Outage | 865784 | 104 | 105 | 10920 | 0.006672 | 0.0063543
2012-08-18 | 238:34144 | URBAN | Planned Outage | 865790 | 19 | 270 | 5130 | 0.0031344 | 0.0011609
2012-08-18 | 501:48125 | URBAN | Planned Outage | 865792 | 75 | 315 | 23625 | 0.014435 | 0.0045824
2012-08-17 | 523:33501 | SHORT RURAL | Planned Outage | 865800 | 1 | 90 | 90 | 5.4989e-05 | 6.1099e-05
2012-08-17 | 810:74054 | LONG RURAL | Planned Outage | 865801 | 9 | 255 | 2295 | 0.0014022 | 0.00054989
2012-08-18 | 514:18137 | SHORT RURAL | Planned Outage | 865802 | 9 | 250 | 2250 | 0.0013747 | 0.00054989
2012-08-20 | ZN12650:PA6 | URBAN | Planned Outage | 865990 | 13 | 90 | 1170 | 0.00071485 | 0.00079428
2012-08-20 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 865992 | 6 | 480 | 2880 | 0.0017596 | 0.00036659
2012-08-20 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 866001 | 5 | 480 | 2400 | 0.0014664 | 0.00030549
2012-08-20 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 866008 | 17 | 480 | 8160 | 0.0049856 | 0.0010387
2012-08-20 | ZN14892:PA13 | URBAN | Planned Outage | 866016 | 125 | 480 | 60000 | 0.036659 | 0.0076373
2012-08-20 | ZN12650:PA6 | URBAN | Planned Outage | 866018 | 13 | 90 | 1170 | 0.00071485 | 0.00079428
2012-08-20 | ZN10993:PA6 | URBAN | Planned Outage | 866021 | 46 | 150 | 6900 | 0.0042158 | 0.0028105
2012-08-20 | 511:29877 | SHORT RURAL | Planned Outage | 866238 | 27 | 373 | 10071 | 0.0061532 | 0.0016497
2012-08-20 | 232:11459 | SHORT RURAL | Planned Outage | 866244 | 7 | 445 | 3115 | 0.0019032 | 0.00042769
2012-08-20 | 213:33777 | SHORT RURAL | Planned Outage | 866246 | 4 | 205 | 820 | 0.00050101 | 0.00024439
2012-08-20 | 515:35198 | SHORT RURAL | Planned Outage | 866254 | 9 | 210 | 1890 | 0.0011548 | 0.00054989
2012-08-21 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 866533 | 66 | 540 | 20760 | 0.012684 | 0.0040325
2012-08-22 | ZN12610:PA24 | SHORT RURAL | Planned Outage | 866537 | 74 | 480 | 35520 | 0.021702 | 0.0045213
2012-08-21 | ZN12610:PA24 | SHORT RURAL | Planned Outage | 866554 | 116 | 420 | 48720 | 0.029767 | 0.0070874
2012-08-21 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 866558 | 3 | 480 | 1440 | 0.00087982 | 0.0001833
2012-08-22 | 806:74080 | SHORT RURAL | Planned Outage | 866569 | 230 | 199 | 45770 | 0.027965 | 0.014053
2012-08-21 | 264:81240 | SHORT RURAL | Planned Outage | 866586 | 52 | 360 | 18720 | 0.011438 | 0.0031771
2012-08-21 | 227:13014 | SHORT RURAL | Planned Outage | 866596 | 46 | 340 | 15640 | 0.0095558 | 0.0028105
2012-08-21 | 243:80083 | SHORT RURAL | Planned Outage | 866600 | 15 | 415 | 6225 | 0.0038034 | 0.00091648
2012-08-21 | 243:80083 | SHORT RURAL | Planned Outage | 866606 | 3 | 415 | 1245 | 0.00076068 | 0.0001833
2012-08-21 | 232:33413 | SHORT RURAL | Planned Outage | 866610 | 99 | 165 | 16335 | 0.0099805 | 0.0060488
2012-08-21 | 232:11459 | SHORT RURAL | Planned Outage | 866612 | 7 | 405 | 2835 | 0.0017321 | 0.00042769
2012-08-21 | 232:11460 | URBAN | Planned Outage | 866624 | 317 | 575 | 182275 | 0.11137 | 0.019368
2012-08-21 | 511:29878 | SHORT RURAL | Planned Outage | 866626 | 84 | 450 | 37800 | 0.023095 | 0.0051323
2012-08-21 | 509:48039 | LONG RURAL | Planned Outage | 866631 | 1 | 150 | 150 | 9.1648e-05 | 6.1099e-05
2012-08-21 | 509:48039 | LONG RURAL | Planned Outage | 866634 | 1 | 50 | 50 | 3.0549e-05 | 6.1099e-05
2012-08-21 | 515:35192 | SHORT RURAL | Planned Outage | 866636 | 17 | 310 | 5270 | 0.0032199 | 0.0010387
2012-08-22 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 867027 | 2 | 480 | 960 | 0.00058655 | 0.0001222
2012-08-22 | ZN12570:PA1 | SHORT RURAL | Planned Outage | 867031 | 51 | 480 | 24480 | 0.014957 | 0.003116
2012-08-23 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 867032 | 8 | 480 | 3840 | 0.0023462 | 0.00048879
2012-08-22 | ZN12570:PA12 | SHORT RURAL | Planned Outage | 867033 | 97 | 480 | 46560 | 0.028448 | 0.0059266
2012-08-22 | ZN12650:PA12 | URBAN | Planned Outage | 867037 | 43 | 180 | 7740 | 0.004729 | 0.0026272
2012-08-22 | ZN3154:PA12 | URBAN | Planned Outage | 867042 | 1 | 240 | 240 | 0.00014664 | 6.1099e-05
2012-08-22 | 512:48049 | SHORT RURAL | Planned Outage | 867201 | 1 | 200 | 200 | 0.0001222 | 6.1099e-05
2012-08-22 | 216:10727 | URBAN | Planned Outage | 867246 | 120 | 143 | 17160 | 0.010485 | 0.0073318
2012-08-22 | 232:33413 | SHORT RURAL | Planned Outage | 867251 | 33 | 240 | 7920 | 0.004839 | 0.0020163
2012-08-22 | 243:80077 | URBAN | Planned Outage | 867392 | 110 | 940 | 12650 | 0.007729 | 0.0067208
2012-08-22 | 232:11457 | URBAN | Planned Outage | 867420 | 1 | 300 | 300 | 0.0001833 | 6.1099e-05
2012-08-22 | 205:12203 | URBAN | Planned Outage | 867560 | 40 | 30 | 1200 | 0.00073318 | 0.0024439
2012-08-22 | 202:34249 | URBAN | Planned Outage | 867569 | 53 | 135 | 7155 | 0.0043716 | 0.0032382
2012-08-23 | 213:33773 | SHORT RURAL | Planned Outage | 868436 | 2 | 290 | 580 | 0.00035437 | 0.0001222
2012-08-23 | 234:33444 | SHORT RURAL | Planned Outage | 868438 | 1 | 270 | 270 | 0.00016497 | 6.1099e-05
2012-08-23 | 258:80775 | URBAN | Planned Outage | 868442 | 62 | 450 | 27900 | 0.017047 | 0.0037881
2012-08-23 | 510:48164 | SHORT RURAL | Planned Outage | 868445 | 9 | 265 | 2385 | 0.0014572 | 0.00054989
2012-08-23 | 523:33501 | SHORT RURAL | Planned Outage | 868449 | 2 | 280 | 560 | 0.00034215 | 0.0001222
2012-08-27 | 512:48047 | SHORT RURAL | Planned Outage | 869169 | 42 | 300 | 12600 | 0.0076984 | 0.0025661
2012-08-23 | ZN3472:PA21 | URBAN | Planned Outage | 869172 | 6 | 450 | 2700 | 0.0016497 | 0.00036659
2012-08-23 | ZN3472:PA21 | URBAN | Planned Outage | 869174 | 3 | 450 | 1350 | 0.00082483 | 0.0001833
2012-08-23 | ZN14891:PA1 | SHORT RURAL | Planned Outage | 869177 | 64 | 480 | 8160 | 0.0049856 | 0.0039103
2012-08-23 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 869183 | 6 | 480 | 2880 | 0.0017596 | 0.00036659
2012-08-23 | ZN12600:PA11 | URBAN | Planned Outage | 869186 | 221 | 480 | 106080 | 0.064813 | 0.013503
2012-08-23 | ZN3472:PA32 | SHORT RURAL | Planned Outage | 869199 | 12 | 510 | 6120 | 0.0037392 | 0.00073318
2012-08-23 | ZN874:PA8 | URBAN | Planned Outage | 869201 | 1 | 540 | 540 | 0.00032993 | 6.1099e-05
2012-08-23 | ZN874:PA8 | URBAN | Planned Outage | 869204 | 149 | 120 | 17880 | 0.010924 | 0.0091037
2012-08-24 | ZN12650:PA6 | URBAN | Planned Outage | 869206 | 89 | 510 | 45390 | 0.027733 | 0.0054378
2012-08-24 | ZN14892:PA13 | URBAN | Planned Outage | 869215 | 100 | 480 | 48000 | 0.029327 | 0.0061099
2012-08-24 | 513:48059 | SHORT RURAL | Planned Outage | 869229 | 8 | 370 | 2960 | 0.0018085 | 0.00048879
2012-08-24 | ZN12570:PA18 | URBAN | Planned Outage | 869241 | 130 | 360 | 46800 | 0.028594 | 0.0079428
2012-08-25 | 813:89062 | SHORT RURAL | Planned Outage | 869253 | 11 | 280 | 3080 | 0.0018818 | 0.00067208
2012-08-26 | 514:18137 | SHORT RURAL | Planned Outage | 869257 | 50 | 318 | 15900 | 0.0097147 | 0.0030549
2012-08-25 | 221:11899 | URBAN | Planned Outage | 869259 | 1 | 540 | 540 | 0.00032993 | 6.1099e-05
2012-08-26 | 213:33775 | URBAN | Planned Outage | 869265 | 66 | 60 | 3960 | 0.0024195 | 0.0040325
2012-08-26 | 240:34843 | URBAN | Planned Outage | 869267 | 2 | 190 | 380 | 0.00023217 | 0.0001222
2012-08-26 | 258:80785 | URBAN | Planned Outage | 869274 | 1 | 495 | 495 | 0.00030244 | 6.1099e-05
2012-08-26 | 203:8088 | URBAN | Planned Outage | 869279 | 3 | 320 | 960 | 0.00058655 | 0.0001833
2012-08-25 | ZN15015:PA5 | URBAN | Planned Outage | 869280 | 3 | 510 | 1530 | 0.00093481 | 0.0001833
2012-08-24 | 507:80923 | SHORT RURAL | Planned Outage | 869282 | 6 | 330 | 1980 | 0.0012098 | 0.00036659
2012-08-25 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 869287 | 31 | 480 | 14880 | 0.0090915 | 0.0018941
2012-08-24 | 504:48031 | SHORT RURAL | Planned Outage | 869288 | 31 | 290 | 8990 | 0.0054928 | 0.0018941
2012-08-26 | ZN2196:PA18 | URBAN | Planned Outage | 869295 | 13 | 629 | 8177 | 0.004996 | 0.00079428
2012-08-24 | 509:48039 | LONG RURAL | Planned Outage | 869296 | 1 | 115 | 115 | 7.0263e-05 | 6.1099e-05
2012-08-24 | 509:48039 | LONG RURAL | Planned Outage | 869306 | 1 | 180 | 180 | 0.00010998 | 6.1099e-05
2012-08-24 | 264:81240 | SHORT RURAL | Planned Outage | 869312 | 27 | 380 | 10260 | 0.0062687 | 0.0016497
2012-08-25 | 511:29878 | SHORT RURAL | Planned Outage | 869317 | 9 | 430 | 3870 | 0.0023645 | 0.00054989
2012-08-25 | 526:34641 | SHORT RURAL | Planned Outage | 869351 | 5 | 315 | 1575 | 0.0009623 | 0.00030549
2012-08-26 | 511:29872 | URBAN | Planned Outage | 869352 | 24 | 128 | 3072 | 0.0018769 | 0.0014664
2012-08-24 | 512:48049 | SHORT RURAL | Planned Outage | 869356 | 5 | 60 | 300 | 0.0001833 | 0.00030549
2012-08-24 | 512:48049 | SHORT RURAL | Planned Outage | 869358 | 5 | 78 | 390 | 0.00023828 | 0.00030549
2012-08-25 | 813:89062 | SHORT RURAL | Planned Outage | 869361 | 1 | 415 | 415 | 0.00025356 | 6.1099e-05
2012-08-28 | 801:74121 | SHORT RURAL | Planned Outage | 869695 | 130 | 330 | 42900 | 0.026211 | 0.0079428
2012-08-27 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 869962 | 22 | 540 | 8040 | 0.0049123 | 0.0013442
2012-08-27 | ZN2635:PA20 | URBAN | Planned Outage | 869968 | 142 | 450 | 63900 | 0.039042 | 0.008676
2012-08-27 | ZN12570:PA16 | SHORT RURAL | Planned Outage | 869971 | 5 | 480 | 2400 | 0.0014664 | 0.00030549
2012-08-27 | ZN711:PA26 | URBAN | Planned Outage | 869972 | 197 | 60 | 11820 | 0.0072219 | 0.012036
2012-08-27 | 206:34432 | URBAN | Planned Outage | 870003 | 17 | 280 | 4760 | 0.0029083 | 0.0010387
2012-08-27 | 227:13020 | SHORT RURAL | Planned Outage | 870008 | 44 | 30 | 1320 | 0.0008065 | 0.0026883
2012-08-27 | 238:34141 | SHORT RURAL | Planned Outage | 870010 | 1 | 155 | 155 | 9.4703e-05 | 6.1099e-05
2012-08-27 | 524:33572 | SHORT RURAL | Planned Outage | 870012 | 2 | 155 | 310 | 0.00018941 | 0.0001222
2012-08-27 | 509:48039 | LONG RURAL | Planned Outage | 870017 | 1 | 55 | 55 | 3.3604e-05 | 6.1099e-05
2012-08-27 | 509:48039 | LONG RURAL | Planned Outage | 870021 | 2 | 75 | 150 | 9.1648e-05 | 0.0001222
2012-08-27 | 807:74179 | SHORT RURAL | Planned Outage | 870025 | 6 | 105 | 630 | 0.00038492 | 0.00036659
2012-08-28 | 501:48115 | SHORT RURAL | Planned Outage | 870239 | 4 | 240 | 960 | 0.00058655 | 0.00024439
2012-08-28 | 224:80332 | URBAN | Planned Outage | 870249 | 48 | 10 | 480 | 0.00029327 | 0.0029327
2012-08-28 | 232:33411 | SHORT RURAL | Planned Outage | 870252 | 183 | 300 | 54900 | 0.033543 | 0.011181
2012-08-28 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 870255 | 66 | 540 | 17820 | 0.010888 | 0.0040325
2012-08-28 | 243:80083 | SHORT RURAL | Planned Outage | 870258 | 15 | 445 | 6675 | 0.0040783 | 0.00091648
2012-08-28 | 526:34636 | SHORT RURAL | Planned Outage | 870260 | 24 | 520 | 12480 | 0.0076251 | 0.0014664
2012-08-28 | ZN129:PA5 | URBAN | Planned Outage | 870262 | 8 | 630 | 5040 | 0.0030794 | 0.00048879
2012-08-28 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 870264 | 5 | 480 | 2400 | 0.0014664 | 0.00030549
2012-08-28 | 509:48040 | SHORT RURAL | Planned Outage | 870268 | 3 | 155 | 465 | 0.00028411 | 0.0001833
2012-08-28 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 870275 | 13 | 480 | 6240 | 0.0038126 | 0.00079428
2012-08-28 | 509:48039 | LONG RURAL | Planned Outage | 870283 | 28 | 80 | 2240 | 0.0013686 | 0.0017108
2012-08-29 | 216:10729 | URBAN | Planned Outage | 870288 | 152 | 228 | 34656 | 0.021174 | 0.009287
2012-08-28 | 509:48039 | LONG RURAL | Planned Outage | 870292 | 1 | 90 | 90 | 5.4989e-05 | 6.1099e-05
2012-08-28 | 509:48039 | LONG RURAL | Planned Outage | 870294 | 1 | 195 | 195 | 0.00011914 | 6.1099e-05
2012-08-28 | ZN1287:PA4 | URBAN | Planned Outage | 870372 | 3 | 1560 | 4680 | 0.0028594 | 0.0001833
2012-08-28 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 870394 | 304 | 360 | 107640 | 0.065767 | 0.018574
2012-08-28 | ZN14892:PA5 | URBAN | Planned Outage | 870419 | 2 | 210 | 420 | 0.00025661 | 0.0001222
2012-08-28 | ZN14892:PA5 | URBAN | Planned Outage | 870420 | 17 | 210 | 3570 | 0.0021812 | 0.0010387
2012-08-29 | ZN14892:PA14 | SHORT RURAL | Planned Outage | 870749 | 109 | 600 | 42420 | 0.025918 | 0.0066598
2012-08-29 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 870762 | 17 | 540 | 9180 | 0.0056089 | 0.0010387
2012-08-29 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 870764 | 5 | 480 | 2400 | 0.0014664 | 0.00030549
2012-08-29 | ZN12610:PA24 | SHORT RURAL | Planned Outage | 870766 | 149 | 480 | 71520 | 0.043698 | 0.0091037
2012-08-29 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 870791 | 3 | 420 | 1260 | 0.00076984 | 0.0001833
2012-08-29 | ZN12650:PA13 | SHORT RURAL | Planned Outage | 870795 | 116 | 450 | 52200 | 0.031893 | 0.0070874
2012-08-29 | ZN2466:PA41 | URBAN | Planned Outage | 870805 | 91 | 390 | 35490 | 0.021684 | 0.00556
2012-08-29 | ZN2466:PA41 | URBAN | Planned Outage | 870807 | 35 | 90 | 3150 | 0.0019246 | 0.0021385
2012-08-29 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 870809 | 52 | 180 | 9360 | 0.0057188 | 0.0031771
2012-08-29 | 523:33508 | SHORT RURAL | Planned Outage | 870825 | 5 | 355 | 1775 | 0.0010845 | 0.00030549
2012-08-29 | 801:74121 | SHORT RURAL | Planned Outage | 870827 | 22 | 210 | 4620 | 0.0028228 | 0.0013442
2012-08-29 | 243:80077 | URBAN | Planned Outage | 870829 | 13 | 92 | 1196 | 0.00073074 | 0.00079428
2012-08-29 | 243:80077 | URBAN | Planned Outage | 870830 | 9 | 92 | 828 | 0.0005059 | 0.00054989
2012-08-29 | 264:81240 | SHORT RURAL | Planned Outage | 870886 | 6 | 345 | 2070 | 0.0012647 | 0.00036659
2012-08-29 | 503:48011 | SHORT RURAL | Planned Outage | 870889 | 14 | 354 | 4956 | 0.003028 | 0.00085538
2012-08-29 | 813:89061 | LONG RURAL | Planned Outage | 870891 | 2 | 280 | 560 | 0.00034215 | 0.0001222
2012-08-29 | 812:19066 | SHORT RURAL | Planned Outage | 870892 | 4 | 355 | 1420 | 0.0008676 | 0.00024439
2012-08-30 | 511:29877 | SHORT RURAL | Planned Outage | 871110 | 27 | 395 | 10665 | 0.0065162 | 0.0016497
2012-08-30 | 264:81240 | SHORT RURAL | Planned Outage | 871112 | 2 | 170 | 340 | 0.00020774 | 0.0001222
2012-08-30 | 229:34995 | SHORT RURAL | Planned Outage | 871117 | 1 | 160 | 160 | 9.7758e-05 | 6.1099e-05
2012-08-30 | 232:11453 | SHORT RURAL | Planned Outage | 871123 | 2 | 400 | 800 | 0.00048879 | 0.0001222
2012-08-30 | 511:29876 | SHORT RURAL | Planned Outage | 871157 | 2 | 495 | 990 | 0.00060488 | 0.0001222
2012-08-30 | 501:48115 | SHORT RURAL | Planned Outage | 871160 | 5 | 90 | 450 | 0.00027494 | 0.00030549
2012-08-30 | 514:18137 | SHORT RURAL | Planned Outage | 871190 | 5 | 200 | 1000 | 0.00061099 | 0.00030549
2012-08-30 | 813:89061 | LONG RURAL | Planned Outage | 871192 | 22 | 402 | 8844 | 0.0054036 | 0.0013442
2012-08-30 | ZN4545:PA4 | URBAN | Planned Outage | 871368 | 43 | 600 | 25800 | 0.015763 | 0.0026272
2012-08-30 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 871371 | 18 | 480 | 8640 | 0.0052789 | 0.0010998
2012-08-30 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 871378 | 38 | 480 | 18240 | 0.011144 | 0.0023217
2012-08-31 | ZN12610:PA10 | SHORT RURAL | Planned Outage | 871849 | 46 | 540 | 24840 | 0.015177 | 0.0028105
2012-08-31 | ZN874:PA8 | URBAN | Planned Outage | 871857 | 1 | 450 | 450 | 0.00027494 | 6.1099e-05
2012-08-31 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 871858 | 2 | 360 | 720 | 0.00043991 | 0.0001222
2012-08-31 | ZN874:PA8 | URBAN | Planned Outage | 871861 | 150 | 120 | 18000 | 0.010998 | 0.0091648
2012-08-31 | ZN15006:PA12 | URBAN | Planned Outage | 871865 | 12 | 225 | 2700 | 0.0016497 | 0.00073318
2012-09-01 | ZN8700:PA61 62ABC | CBD | Planned Outage | 871871 | 45 | 330 | 14850 | 0.0090732 | 0.0027494
2012-09-01 | ZN12610:PA18 | URBAN | Planned Outage | 871880 | 2 | 360 | 720 | 0.00043991 | 0.0001222
2012-09-02 | 523:33508 | SHORT RURAL | Planned Outage | 871948 | 51 | 190 | 9690 | 0.0059205 | 0.003116
2012-08-31 | 258:80787 | URBAN | Planned Outage | 871958 | 2 | 60 | 120 | 7.3318e-05 | 0.0001222
2012-08-31 | 243:80077 | URBAN | Planned Outage | 871962 | 1 | 345 | 345 | 0.00021079 | 6.1099e-05
2012-08-31 | 232:11454 | SHORT RURAL | Planned Outage | 871975 | 2 | 507 | 1014 | 0.00061954 | 0.0001222
2012-08-31 | 504:48034 | URBAN | Planned Outage | 872002 | 188 | 60 | 11280 | 0.0068919 | 0.011487
2012-09-01 | 510:48164 | SHORT RURAL | Planned Outage | 872017 | 20 | 360 | 7200 | 0.0043991 | 0.001222
2012-08-31 | 523:33501 | SHORT RURAL | Planned Outage | 872024 | 21 | 318 | 6678 | 0.0040802 | 0.0012831
2012-08-31 | 807:74184 | SHORT RURAL | Planned Outage | 872028 | 1 | 50 | 50 | 3.0549e-05 | 6.1099e-05
2012-09-03 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 872416 | 36 | 480 | 17280 | 0.010558 | 0.0021996
2012-09-03 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 872434 | 38 | 480 | 18240 | 0.011144 | 0.0023217
2012-09-03 | 214:8669 | URBAN | Planned Outage | 872456 | 3 | 230 | 690 | 0.00042158 | 0.0001833
2012-09-03 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 872459 | 43 | 480 | 20640 | 0.012611 | 0.0026272
2012-09-03 | ZN12590:PA1 | SHORT RURAL | Planned Outage | 872466 | 77 | 480 | 36960 | 0.022582 | 0.0047046
2012-09-03 | ZN12580:PA16 | URBAN | Planned Outage | 872469 | 10 | 480 | 4800 | 0.0029327 | 0.00061099
2012-09-03 | ZN12660:PA14 | SHORT RURAL | Planned Outage | 872470 | 117 | 480 | 56160 | 0.034313 | 0.0071485
2012-09-03 | 260:33353 | URBAN | Planned Outage | 872486 | 1 | 310 | 310 | 0.00018941 | 6.1099e-05
2012-09-03 | 264:81240 | SHORT RURAL | Planned Outage | 872490 | 27 | 375 | 10125 | 0.0061862 | 0.0016497
2012-09-04 | ZN9900:PA6 | URBAN | Planned Outage | 872861 | 11 | 540 | 5940 | 0.0036293 | 0.00067209
2012-09-04 | 813:89062 | SHORT RURAL | Planned Outage | 872868 | 11 | 445 | 4895 | 0.0029908 | 0.00067209
2012-09-04 | 260:33347 | SHORT RURAL | Planned Outage | 872873 | 3 | 255 | 765 | 0.0004674 | 0.0001833
2012-09-04 | 232:33413 | SHORT RURAL | Planned Outage | 872880 | 39 | 305 | 11895 | 0.0072677 | 0.0023828
2012-09-04 | ZN12650:PA20 | URBAN | Planned Outage | 872881 | 527 | 510 | 155520 | 0.095021 | 0.032199
2012-09-04 | 243:80077 | URBAN | Planned Outage | 872890 | 9 | 585 | 5265 | 0.0032168 | 0.00054989
2012-09-04 | 203:8085 | URBAN | Planned Outage | 872893 | 78 | 360 | 28080 | 0.017157 | 0.0047657
2012-09-04 | 812:19066 | SHORT RURAL | Planned Outage | 872900 | 4 | 295 | 1180 | 0.00072096 | 0.00024439
2012-09-04 | 514:18137 | SHORT RURAL | Planned Outage | 872903 | 12 | 185 | 2220 | 0.0013564 | 0.00073318
2012-09-04 | 813:89062 | SHORT RURAL | Planned Outage | 872904 | 1 | 350 | 350 | 0.00021385 | 6.1099e-05
2012-09-04 | ZN12570:PA15 | SHORT RURAL | Planned Outage | 872908 | 57 | 540 | 30780 | 0.018806 | 0.0034826
2012-09-04 | ZN711:PA26 | URBAN | Planned Outage | 872913 | 217 | 90 | 19530 | 0.011933 | 0.013258
2012-09-04 | 811:74234 | SHORT RURAL | Planned Outage | 872927 | 6 | 175 | 1050 | 0.00064154 | 0.00036659
2012-09-04 | 511:29878 | SHORT RURAL | Planned Outage | 872929 | 3 | 15 | 45 | 2.7494e-05 | 0.0001833
2012-09-04 | 511:29878 | SHORT RURAL | Planned Outage | 872935 | 2 | 20 | 40 | 2.4439e-05 | 0.0001222
2012-09-04 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 872940 | 3 | 450 | 1350 | 0.00082483 | 0.0001833
2012-09-04 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 872964 | 16 | 480 | 7680 | 0.0046924 | 0.00097758
2012-09-04 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 873042 | 13 | 480 | 6240 | 0.0038126 | 0.00079428
2012-09-04 | ZN12600:PA11 | URBAN | Planned Outage | 873050 | 169 | 480 | 81120 | 0.049563 | 0.010326
2012-09-04 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 873055 | 5 | 480 | 2400 | 0.0014664 | 0.00030549
2012-09-04 | ZN965:PA38 | URBAN | Planned Outage | 873060 | 31 | 480 | 14880 | 0.0090915 | 0.0018941
2012-09-04 | ZN14892:PA13 | URBAN | Planned Outage | 873063 | 53 | 480 | 25440 | 0.015544 | 0.0032382
2012-09-04 | ZN12660:PA10 | SHORT RURAL | Planned Outage | 873070 | 45 | 180 | 8100 | 0.004949 | 0.0027494
2012-09-05 | ZN12590:PA1 | SHORT RURAL | Planned Outage | 873418 | 3 | 480 | 600 | 0.00036659 | 0.0001833
2012-09-05 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 873430 | 24 | 480 | 1440 | 0.00087982 | 0.0014664
2012-09-05 | ZN1610:PA13 | URBAN | Planned Outage | 873436 | 73 | 420 | 30660 | 0.018733 | 0.0044602
2012-09-05 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 873441 | 28 | 420 | 11760 | 0.0071852 | 0.0017108
2012-09-05 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 873443 | 8 | 120 | 960 | 0.00058655 | 0.00048879
2012-09-05 | 813:89062 | SHORT RURAL | Planned Outage | 873510 | 11 | 329 | 3619 | 0.0022112 | 0.00067209
2012-09-05 | 243:80077 | URBAN | Planned Outage | 873517 | 1 | 420 | 420 | 0.00025661 | 6.1099e-05
2012-09-05 | 240:34852 | URBAN | Planned Outage | 873518 | 2 | 370 | 740 | 0.00045213 | 0.0001222
2012-09-05 | 501:48118 | SHORT RURAL | Planned Outage | 873559 | 17 | 62 | 1054 | 0.00064398 | 0.0010387
2012-09-05 | 509:48040 | SHORT RURAL | Planned Outage | 873560 | 51 | 370 | 18870 | 0.011529 | 0.003116
2012-09-05 | 509:48039 | LONG RURAL | Planned Outage | 873567 | 1 | 180 | 180 | 0.00010998 | 6.1099e-05
2012-09-05 | 807:74180 | SHORT RURAL | Planned Outage | 873571 | 2 | 80 | 160 | 9.7758e-05 | 0.0001222
2012-09-05 | 813:89062 | SHORT RURAL | Planned Outage | 873573 | 1 | 435 | 435 | 0.00026578 | 6.1099e-05
2012-09-05 | 509:48039 | LONG RURAL | Planned Outage | 873579 | 1 | 170 | 170 | 0.00010387 | 6.1099e-05
2012-09-07 | ZN12650:PA13 | SHORT RURAL | Planned Outage | 874013 | 116 | 570 | 66120 | 0.040398 | 0.0070874
2012-09-06 | ZN12640:PA18 | SHORT RURAL | Planned Outage | 874880 | 317 | 480 | 152160 | 0.092968 | 0.019368
2012-09-06 | ZN1285:PA20 | URBAN | Planned Outage | 874959 | 179 | 480 | 85920 | 0.052496 | 0.010937
2012-09-06 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 874968 | 66 | 480 | 18240 | 0.011144 | 0.0040325
2012-09-06 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 875135 | 11 | 480 | 5280 | 0.003226 | 0.00067209
2012-09-06 | ZN12600:PA11 | URBAN | Planned Outage | 875154 | 11 | 480 | 5280 | 0.003226 | 0.00067209
2012-09-06 | ZN12600:PA3 | URBAN | Planned Outage | 875169 | 58 | 480 | 27840 | 0.01701 | 0.0035437
2012-09-06 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 875171 | 13 | 480 | 6240 | 0.0038126 | 0.00079428
2012-09-06 | ZN15005:PA4 | URBAN | Planned Outage | 875183 | 52 | 420 | 21840 | 0.013344 | 0.0031771
2012-09-07 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 875354 | 3 | 480 | 1440 | 0.00087982 | 0.0001833
2012-09-07 | ZN12580:PA1 | URBAN | Planned Outage | 875360 | 70 | 480 | 33600 | 0.020529 | 0.0042769
2012-09-07 | ZN12600:PA11 | URBAN | Planned Outage | 875365 | 7 | 420 | 2940 | 0.0017963 | 0.00042769
2012-09-07 | ZN2400:PA11 | SHORT RURAL | Planned Outage | 875376 | 43 | 300 | 12900 | 0.0078817 | 0.0026272
2012-09-07 | ZN342:PA28 | URBAN | Planned Outage | 875382 | 1 | 2220 | 2220 | 0.0013564 | 6.1099e-05
2012-09-08 | ZN129:PA21 | URBAN | Planned Outage | 875425 | 1 | 480 | 480 | 0.00029327 | 6.1099e-05
2012-09-08 | ZN2196:PA17 | URBAN | Planned Outage | 875428 | 8 | 480 | 3840 | 0.0023462 | 0.00048879
2012-09-08 | ZN12660:PA11 | URBAN | Planned Outage | 875435 | 220 | 540 | 118800 | 0.072585 | 0.013442
2012-09-06 | 228:7490 | SHORT RURAL | Planned Outage | 875446 | 1 | 50 | 50 | 3.0549e-05 | 6.1099e-05
2012-09-09 | ZN12690:PA17 | URBAN | Planned Outage | 875454 | 5 | 420 | 2100 | 0.0012831 | 0.00030549
2012-09-09 | 507:80926 | URBAN | Planned Outage | 875455 | 22 | 400 | 8800 | 0.0053767 | 0.0013442
2012-09-06 | 232:11453 | SHORT RURAL | Planned Outage | 875462 | 2 | 500 | 1000 | 0.00061099 | 0.0001222
2012-09-09 | ZN14892:PA14 | SHORT RURAL | Planned Outage | 875464 | 1 | 480 | 480 | 0.00029327 | 6.1099e-05
2012-09-06 | 243:80083 | SHORT RURAL | Planned Outage | 875465 | 15 | 380 | 5700 | 0.0034826 | 0.00091648
2012-09-07 | 232:11459 | SHORT RURAL | Planned Outage | 875468 | 9 | 310 | 2790 | 0.0017047 | 0.00054989
2012-09-09 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 875471 | 19 | 540 | 10260 | 0.0062687 | 0.0011609
2012-09-09 | ZN3472:PA34 | URBAN | Planned Outage | 875478 | 4 | 660 | 2640 | 0.001613 | 0.00024439
2012-09-11 | 260:33347 | SHORT RURAL | Planned Outage | 875482 | 3 | 125 | 375 | 0.00022912 | 0.0001833
2012-09-10 | ZN9550:PA43 | URBAN | Planned Outage | 875483 | 52 | 510 | 26520 | 0.016203 | 0.0031771
2012-09-10 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 875485 | 10 | 480 | 4800 | 0.0029327 | 0.00061099
2012-09-08 | 203:8083 | SHORT RURAL | Planned Outage | 875488 | 2 | 140 | 280 | 0.00017108 | 0.0001222
2012-09-09 | 224:80337 | URBAN | Planned Outage | 875496 | 126 | 140 | 17640 | 0.010778 | 0.0076984
2012-09-09 | 202:34256 | URBAN | Planned Outage | 875499 | 42 | 305 | 12810 | 0.0078267 | 0.0025661
2012-09-10 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 875518 | 30 | 510 | 15300 | 0.0093481 | 0.001833
2012-09-09 | 208:56 | URBAN | Planned Outage | 875522 | 107 | 500 | 53500 | 0.032688 | 0.0065376
2012-09-06 | 510:48164 | SHORT RURAL | Planned Outage | 875536 | 6 | 265 | 1590 | 0.00097147 | 0.00036659
2012-09-06 | 509:48039 | LONG RURAL | Planned Outage | 875539 | 1 | 165 | 165 | 0.00010081 | 6.1099e-05
2012-09-07 | 503:48011 | SHORT RURAL | Planned Outage | 875540 | 99 | 320 | 31680 | 0.019356 | 0.0060488
2012-09-07 | 264:81240 | SHORT RURAL | Planned Outage | 875548 | 12 | 340 | 4080 | 0.0024928 | 0.00073318
2012-09-07 | 512:48046 | SHORT RURAL | Planned Outage | 875553 | 21 | 220 | 4620 | 0.0028228 | 0.0012831
2012-09-07 | 509:48039 | LONG RURAL | Planned Outage | 875554 | 1 | 150 | 150 | 9.1648e-05 | 6.1099e-05
2012-09-09 | 232:33413 | SHORT RURAL | Planned Outage | 875560 | 142 | 385 | 54670 | 0.033403 | 0.008676
2012-09-07 | 515:35192 | SHORT RURAL | Planned Outage | 875564 | 7 | 290 | 2030 | 0.0012403 | 0.00042769
2012-09-08 | 806:74076 | SHORT RURAL | Planned Outage | 875566 | 2 | 130 | 260 | 0.00015886 | 0.0001222
2012-09-09 | 513:48059 | SHORT RURAL | Planned Outage | 875568 | 8 | 345 | 2760 | 0.0016863 | 0.00048879
2012-09-10 | 224:80332 | URBAN | Planned Outage | 875594 | 202 | 375 | 75750 | 0.046282 | 0.012342
2012-09-10 | 260:33350 | SHORT RURAL | Planned Outage | 875597 | 5 | 320 | 1600 | 0.00097758 | 0.00030549
2012-09-10 | 232:33413 | SHORT RURAL | Planned Outage | 875598 | 3 | 155 | 465 | 0.00028411 | 0.0001833
2012-09-10 | 229:34983 | SHORT RURAL | Planned Outage | 875601 | 39 | 440 | 17160 | 0.010485 | 0.0023828
2012-09-10 | 504:48026 | SHORT RURAL | Planned Outage | 875633 | 25 | 134 | 3350 | 0.0020468 | 0.0015275
2012-09-10 | 235:2120 | SHORT RURAL | Planned Outage | 875635 | 2 | 145 | 290 | 0.00017719 | 0.0001222
2012-09-11 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 875904 | 101 | 510 | 51510 | 0.031472 | 0.006171
2012-09-11 | ZN9252:PA10 | URBAN | Planned Outage | 875945 | 139 | 480 | 66720 | 0.040765 | 0.0084927
2012-09-11 | ZN12600:PA11 | URBAN | Planned Outage | 875947 | 16 | 90 | 1440 | 0.00087982 | 0.00097758
2012-09-11 | ZN12600:PA11 | URBAN | Planned Outage | 875951 | 25 | 90 | 2250 | 0.0013747 | 0.0015275
2012-09-11 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 876000 | 13 | 480 | 6240 | 0.0038126 | 0.00079428
2012-09-11 | ZN12600:PA11 | URBAN | Planned Outage | 876007 | 16 | 390 | 6240 | 0.0038126 | 0.00097758
2012-09-11 | ZN1290:PA2 | URBAN | Planned Outage | 876011 | 4 | 120 | 480 | 0.00029327 | 0.00024439
2012-09-11 | ZN1290:PA17 | URBAN | Planned Outage | 876013 | 1 | 150 | 150 | 9.1648e-05 | 6.1099e-05
2012-09-12 | ZN3155:PA36 | URBAN | Planned Outage | 876014 | 70 | 20 | 1400 | 0.00085538 | 0.0042769
2012-09-12 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 876265 | 52 | 480 | 24960 | 0.01525 | 0.0031771
2012-09-12 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 876276 | 32 | 480 | 15360 | 0.0093848 | 0.0019552
2012-09-12 | ZN12570:PA16 | SHORT RURAL | Planned Outage | 876294 | 17 | 390 | 6630 | 0.0040508 | 0.0010387
2012-09-11 | 807:74184 | SHORT RURAL | Planned Outage | 876374 | 10 | 185 | 1850 | 0.0011303 | 0.00061099
2012-09-11 | 232:33413 | SHORT RURAL | Planned Outage | 876387 | 19 | 370 | 7030 | 0.0042952 | 0.0011609
2012-09-11 | 526:34637 | SHORT RURAL | Planned Outage | 876389 | 5 | 95 | 475 | 0.00029022 | 0.00030549
2012-09-11 | 515:35192 | SHORT RURAL | Planned Outage | 876404 | 15 | 320 | 4800 | 0.0029327 | 0.00091648
2012-09-11 | 220:8691 | URBAN | Planned Outage | 876408 | 1 | 550 | 550 | 0.00033604 | 6.1099e-05
2012-09-11 | 217:33612 | URBAN | Planned Outage | 876409 | 8 | 315 | 2520 | 0.0015397 | 0.00048879
2012-09-11 | 232:11459 | SHORT RURAL | Planned Outage | 876413 | 68 | 380 | 25840 | 0.015788 | 0.0041547
2012-09-11 | 501:48123 | SHORT RURAL | Planned Outage | 876418 | 3 | 345 | 1035 | 0.00063237 | 0.0001833
2012-09-11 | 507:80917 | URBAN | Planned Outage | 876420 | 85 | 415 | 35275 | 0.021553 | 0.0051934
2012-09-11 | 526:34636 | SHORT RURAL | Planned Outage | 876423 | 2 | 140 | 280 | 0.00017108 | 0.0001222
2012-09-11 | 231:8415 | SHORT RURAL | Planned Outage | 876433 | 3 | 55 | 165 | 0.00010081 | 0.0001833
2012-09-11 | 509:48039 | LONG RURAL | Planned Outage | 876435 | 1 | 85 | 85 | 5.1934e-05 | 6.1099e-05
2012-09-13 | 513:48059 | SHORT RURAL | Planned Outage | 876438 | 7 | 65 | 455 | 0.00027765 | 0.00042716
2012-09-11 | 509:48039 | LONG RURAL | Planned Outage | 876446 | 1 | 90 | 90 | 5.4989e-05 | 6.1099e-05
2012-09-12 | 512:48046 | SHORT RURAL | Planned Outage | 876448 | 21 | 380 | 7980 | 0.0048757 | 0.0012831
2012-09-12 | 511:29878 | SHORT RURAL | Planned Outage | 876478 | 2 | 105 | 210 | 0.00012831 | 0.0001222
2012-09-12 | 507:80926 | URBAN | Planned Outage | 876482 | 1 | 75 | 75 | 4.5824e-05 | 6.1099e-05
2012-09-12 | 526:34640 | SHORT RURAL | Planned Outage | 876495 | 2 | 150 | 300 | 0.0001833 | 0.0001222
2012-09-12 | 523:33508 | SHORT RURAL | Planned Outage | 876510 | 6 | 200 | 1200 | 0.00073318 | 0.00036659
2012-09-12 | 807:74184 | SHORT RURAL | Planned Outage | 876512 | 12 | 330 | 3960 | 0.0024195 | 0.00073318
2012-09-12 | 810:74054 | LONG RURAL | Planned Outage | 876514 | 3 | 75 | 225 | 0.00013747 | 0.0001833
2012-09-12 | 810:74054 | LONG RURAL | Planned Outage | 876520 | 1 | 45 | 45 | 2.7494e-05 | 6.1099e-05
2012-09-13 | 231:8405 | SHORT RURAL | Planned Outage | 877013 | 39 | 305 | 11895 | 0.0072587 | 0.0023799
2012-09-13 | 243:80083 | SHORT RURAL | Planned Outage | 877014 | 78 | 445 | 34710 | 0.021181 | 0.0047598
2012-09-13 | 510:48164 | SHORT RURAL | Planned Outage | 877015 | 1 | 60 | 60 | 3.6614e-05 | 6.1023e-05
2012-09-13 | 523:33501 | SHORT RURAL | Planned Outage | 877017 | 1 | 75 | 75 | 4.5767e-05 | 6.1023e-05
2012-09-13 | 513:48059 | SHORT RURAL | Planned Outage | 877018 | 9 | 180 | 1620 | 0.00098857 | 0.00054921
2012-09-13 | 801:74121 | SHORT RURAL | Planned Outage | 877020 | 2 | 305 | 610 | 0.00037224 | 0.00012205
2012-09-13 | 801:74123 | SHORT RURAL | Planned Outage | 877029 | 9 | 180 | 1620 | 0.00098857 | 0.00054921
2012-09-12 | 264:81240 | SHORT RURAL | Planned Outage | 877034 | 26 | 285 | 7410 | 0.0045274 | 0.0015886
2012-09-14 | 514:18137 | SHORT RURAL | Planned Outage | 877469 | 2 | 515 | 1030 | 0.00062815 | 0.00012197
2012-09-14 | 513:48059 | SHORT RURAL | Planned Outage | 877479 | 45 | 375 | 16875 | 0.010291 | 0.0027444
2012-09-16 | 235:2121 | URBAN | Planned Outage | 877483 | 13 | 270 | 3510 | 0.0021406 | 0.00079281
2012-09-16 | 514:18137 | SHORT RURAL | Planned Outage | 877490 | 2 | 385 | 770 | 0.00046959 | 0.00012197
2012-09-14 | 260:33350 | SHORT RURAL | Planned Outage | 877500 | 5 | 365 | 1825 | 0.001113 | 0.00030493
2012-09-13 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 877509 | 6 | 480 | 2880 | 0.0017575 | 0.00036614
2012-09-13 | ZN12660:PA14 | SHORT RURAL | Planned Outage | 877514 | 118 | 480 | 56640 | 0.034563 | 0.0072007
2012-09-13 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 877527 | 13 | 480 | 6240 | 0.0038078 | 0.0007933
2012-09-14 | 232:11453 | SHORT RURAL | Planned Outage | 877532 | 38 | 255 | 9690 | 0.0059095 | 0.0023175
2012-09-14 | 227:13019 | SHORT RURAL | Planned Outage | 877535 | 4 | 25 | 100 | 6.0986e-05 | 0.00024394
2012-09-16 | 203:8082 | URBAN | Planned Outage | 877542 | 4 | 350 | 1400 | 0.0008538 | 0.00024394
2012-09-16 | 258:80784 | URBAN | Planned Outage | 877549 | 96 | 285 | 27360 | 0.016686 | 0.0058546
2012-09-13 | ZN12600:PA11 | URBAN | Planned Outage | 877566 | 41 | 480 | 19680 | 0.012009 | 0.0025019
2012-09-13 | ZN12570:PA2 | SHORT RURAL | Planned Outage | 877568 | 2 | 300 | 600 | 0.00036614 | 0.00012205
2012-09-14 | ZN15012:PA6 | URBAN | Planned Outage | 877571 | 5 | 420 | 2100 | 0.0012807 | 0.00030493
2012-09-14 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 877576 | 22 | 480 | 10560 | 0.0064401 | 0.0013417
2012-09-14 | ZN12610:PA20 | SHORT RURAL | Planned Outage | 877585 | 21 | 480 | 10080 | 0.0061474 | 0.0012807
2012-09-14 | ZN2635:PA17 | URBAN | Planned Outage | 877587 | 79 | 360 | 28440 | 0.017344 | 0.0048179
2012-09-16 | 232:11460 | URBAN | Planned Outage | 877591 | 20 | 325 | 6500 | 0.0039641 | 0.0012197
2012-09-14 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 877597 | 2 | 150 | 300 | 0.00018296 | 0.00012197
2012-09-14 | ZN342:PA28 | URBAN | Planned Outage | 877598 | 2 | 2250 | 4440 | 0.0027078 | 0.00012197
2012-09-15 | ZN342:PA28 | URBAN | Planned Outage | 877615 | 49 | 480 | 23520 | 0.014344 | 0.0029883
2012-09-15 | ZN342:PA28 | URBAN | Planned Outage | 877618 | 2 | 480 | 960 | 0.00058546 | 0.00012197
2012-09-14 | 810:74054 | LONG RURAL | Planned Outage | 877622 | 23 | 182 | 4186 | 0.0025529 | 0.0014027
2012-09-15 | ZN10993:PA8 | URBAN | Planned Outage | 877634 | 1 | 270 | 270 | 0.00016466 | 6.0986e-05
2012-09-15 | ZN384:PA41 | URBAN | Planned Outage | 877636 | 22 | 570 | 12540 | 0.0076476 | 0.0013417
2012-09-15 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 877638 | 23 | 360 | 8280 | 0.0050496 | 0.0014027
2012-09-15 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 877644 | 3 | 480 | 1440 | 0.00087819 | 0.00018296
2012-09-16 | ZN3472:PA34 | URBAN | Planned Outage | 877651 | 6 | 660 | 3960 | 0.002415 | 0.00036591
2012-09-18 | 801:74121 | SHORT RURAL | Planned Outage | 878042 | 156 | 320 | 49920 | 0.03043 | 0.0095095
2012-09-18 | 509:48039 | LONG RURAL | Planned Outage | 878056 | 84 | 330 | 27720 | 0.016898 | 0.0051205
2012-09-17 | 501:48123 | SHORT RURAL | Planned Outage | 878319 | 75 | 482 | 36150 | 0.022046 | 0.0045739
2012-09-17 | 507:80923 | SHORT RURAL | Planned Outage | 878331 | 2 | 270 | 540 | 0.00032932 | 0.00012197
2012-09-18 | 264:81240 | SHORT RURAL | Planned Outage | 878842 | 11 | 400 | 4400 | 0.0026822 | 0.00067054
2012-09-18 | 258:80785 | URBAN | Planned Outage | 878845 | 1 | 415 | 415 | 0.00025298 | 6.0958e-05
2012-09-18 | 256:80632 | URBAN | Planned Outage | 878847 | 107 | 180 | 19260 | 0.011741 | 0.0065225
2012-09-18 | 510:48164 | SHORT RURAL | Planned Outage | 878851 | 16 | 400 | 6400 | 0.0039013 | 0.00097533
2012-09-18 | 501:48123 | SHORT RURAL | Planned Outage | 878857 | 8 | 285 | 2280 | 0.0013898 | 0.00048767
2012-09-18 | 235:2120 | SHORT RURAL | Planned Outage | 878879 | 10 | 435 | 4350 | 0.0026517 | 0.00060958
2012-09-18 | 811:74234 | SHORT RURAL | Planned Outage | 878883 | 3 | 255 | 765 | 0.00046633 | 0.00018287
2012-09-18 | 516:48067 | SHORT RURAL | Planned Outage | 878886 | 2 | 80 | 160 | 9.7533e-05 | 0.00012192
2012-09-19 | ZN14892:PA5 | URBAN | Planned Outage | 879186 | 10 | 480 | 4800 | 0.002926 | 0.00060958
2012-09-19 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 879189 | 1 | 480 | 480 | 0.0002926 | 6.0958e-05
2012-09-19 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 879191 | 2 | 480 | 960 | 0.0005852 | 0.00012192
2012-09-19 | ZN12610:PA24 | SHORT RURAL | Planned Outage | 879193 | 75 | 480 | 36000 | 0.021945 | 0.0045719
2012-09-19 | 232:11453 | SHORT RURAL | Planned Outage | 879272 | 108 | 355 | 38340 | 0.023371 | 0.0065835
2012-09-19 | 260:33350 | SHORT RURAL | Planned Outage | 879275 | 5 | 487 | 2435 | 0.0014843 | 0.00030479
2012-09-19 | 229:34995 | SHORT RURAL | Planned Outage | 879280 | 4 | 230 | 920 | 0.00056082 | 0.00024383
2012-09-19 | 264:81240 | SHORT RURAL | Planned Outage | 879283 | 10 | 390 | 3900 | 0.0023774 | 0.00060958
2012-09-19 | 214:8669 | URBAN | Planned Outage | 879287 | 3 | 345 | 1035 | 0.00063092 | 0.00018287
2012-09-19 | 232:11460 | URBAN | Planned Outage | 879289 | 1 | 385 | 385 | 0.00023469 | 6.0958e-05
2012-09-19 | 803:74013 | SHORT RURAL | Planned Outage | 879291 | 2 | 135 | 270 | 0.00016459 | 0.00012192
2012-09-20 | 258:80775 | URBAN | Planned Outage | 879477 | 319 | 555 | 177045 | 0.10793 | 0.019446
2012-09-22 | 510:48164 | SHORT RURAL | Planned Outage | 879911 | 169 | 449 | 75881 | 0.046256 | 0.010302
2012-09-20 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 880149 | 50 | 510 | 25500 | 0.015545 | 0.003048
2012-09-20 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 880158 | 138 | 480 | 4140 | 0.0025237 | 0.0084125
2012-09-20 | ZN3154:PA22 | URBAN | Planned Outage | 880168 | 12 | 480 | 5760 | 0.0035113 | 0.00073152
2012-09-20 | ZN14892:PA13 | URBAN | Planned Outage | 880175 | 121 | 480 | 58080 | 0.035405 | 0.0073761
2012-09-20 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 880189 | 21 | 480 | 10080 | 0.0061448 | 0.0012802
2012-09-20 | ZN12570:PA2 | SHORT RURAL | Planned Outage | 880203 | 1 | 300 | 300 | 0.00018288 | 6.096e-05
2012-09-20 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 880208 | 13 | 450 | 5850 | 0.0035662 | 0.00079248
2012-09-20 | ZN4545:PA4 | URBAN | Planned Outage | 880210 | 133 | 300 | 39900 | 0.024323 | 0.0081077
2012-09-21 | ZN12620:PA7 | URBAN | Planned Outage | 880214 | 2 | 210 | 60 | 3.6575e-05 | 0.00012192
2012-09-21 | ZN15001:PA15 | URBAN | Planned Outage | 880217 | 21 | 360 | 7560 | 0.0046085 | 0.0012801
2012-09-21 | 264:81240 | SHORT RURAL | Planned Outage | 880246 | 21 | 440 | 9240 | 0.0056326 | 0.0012801
2012-09-20 | 801:74121 | SHORT RURAL | Planned Outage | 880329 | 15 | 310 | 4650 | 0.0028346 | 0.0009144
2012-09-20 | 230:81440 | URBAN | Planned Outage | 880336 | 238 | 400 | 95200 | 0.058034 | 0.014508
2012-09-22 | 801:74121 | SHORT RURAL | Planned Outage | 880340 | 22 | 225 | 4950 | 0.0030175 | 0.0013411
2012-09-20 | 232:11454 | SHORT RURAL | Planned Outage | 880347 | 147 | 460 | 67620 | 0.041221 | 0.0089611
2012-09-20 | 227:13019 | SHORT RURAL | Planned Outage | 880353 | 12 | 230 | 2760 | 0.0016825 | 0.00073152
2012-09-21 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 880382 | 11 | 360 | 3960 | 0.002414 | 0.00067054
2012-09-22 | ZN2196:PA17 | URBAN | Planned Outage | 880384 | 2 | 660 | 1320 | 0.00080465 | 0.00012192
2012-09-22 | ZN2835:PA41 | URBAN | Planned Outage | 880387 | 23 | 270 | 6210 | 0.0037855 | 0.001402
2012-09-20 | 258:80778 | URBAN | Planned Outage | 880390 | 107 | 20 | 2140 | 0.0013045 | 0.0065227
2012-09-22 | ZN195:PA11 | URBAN | Planned Outage | 880393 | 2 | 510 | 1020 | 0.00062178 | 0.00012192
2012-09-20 | 224:80331 | URBAN | Planned Outage | 880399 | 1 | 25 | 25 | 1.524e-05 | 6.096e-05
2012-09-22 | ZN12570:PA5 | URBAN | Planned Outage | 880403 | 151 | 240 | 32400 | 0.019751 | 0.0092047
2012-09-22 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 880418 | 7 | 480 | 3360 | 0.0020482 | 0.00042671
2012-09-23 | ZN3472:PA35 | URBAN | Planned Outage | 880427 | 8 | 690 | 5520 | 0.0033649 | 0.00048767
2012-09-23 | ZN874:PA17 | URBAN | Planned Outage | 880430 | 47 | 360 | 16920 | 0.010314 | 0.0028651
2012-09-23 | ZN15001:PA3 | URBAN | Planned Outage | 880434 | 26 | 360 | 9360 | 0.0057057 | 0.0015849
2012-09-23 | ZN3472:PA34 | URBAN | Planned Outage | 880442 | 4 | 120 | 480 | 0.0002926 | 0.00024383
2012-09-23 | 227:13015 | SHORT RURAL | Planned Outage | 880444 | 93 | 515 | 47895 | 0.029196 | 0.0056691
2012-09-23 | 234:33444 | SHORT RURAL | Planned Outage | 880455 | 6 | 274 | 1644 | 0.0010022 | 0.00036575
2012-09-20 | 504:48028 | URBAN | Planned Outage | 880474 | 38 | 85 | 3230 | 0.001969 | 0.0023165
2012-09-21 | 509:48039 | LONG RURAL | Planned Outage | 880477 | 1 | 160 | 160 | 9.7534e-05 | 6.0959e-05
2012-09-21 | 509:48039 | LONG RURAL | Planned Outage | 880480 | 1 | 175 | 175 | 0.00010668 | 6.0959e-05
2012-09-21 | 511:29873 | SHORT RURAL | Planned Outage | 880481 | 3 | 155 | 465 | 0.00028346 | 0.00018288
2012-09-20 | 520:48172 | SHORT RURAL | Planned Outage | 880493 | 51 | 360 | 18360 | 0.011192 | 0.003109
2012-09-21 | 512:48049 | SHORT RURAL | Planned Outage | 880497 | 8 | 135 | 1080 | 0.00065835 | 0.00048767
2012-09-21 | 512:48049 | SHORT RURAL | Planned Outage | 880501 | 16 | 275 | 4400 | 0.0026822 | 0.00097534
2012-09-23 | 514:18137 | SHORT RURAL | Planned Outage | 880508 | 2 | 480 | 960 | 0.0005852 | 0.00012192
2012-09-24 | 232:33413 | SHORT RURAL | Planned Outage | 880669 | 23 | 404 | 9292 | 0.0056643 | 0.001402
2012-09-24 | 214:8667 | URBAN | Planned Outage | 880683 | 2 | 245 | 490 | 0.0002987 | 0.00012192
2012-09-24 | 227:13020 | SHORT RURAL | Planned Outage | 880690 | 68 | 360 | 24480 | 0.014923 | 0.0041452
2012-09-24 | ZN12590:PA1 | SHORT RURAL | Planned Outage | 880697 | 8 | 480 | 3000 | 0.0018288 | 0.00048767
2012-09-24 | ZN12610:PA10 | SHORT RURAL | Planned Outage | 880706 | 66 | 480 | 31680 | 0.019312 | 0.0040233
2012-09-24 | ZN3155:PA35 | URBAN | Planned Outage | 880710 | 1127 | 570 | 642390 | 0.39159 | 0.0687
2012-09-24 | 509:48040 | SHORT RURAL | Planned Outage | 880716 | 97 | 419 | 40643 | 0.024775 | 0.005913
2012-09-24 | 512:48049 | SHORT RURAL | Planned Outage | 880741 | 3 | 560 | 1680 | 0.0010241 | 0.00018288
2012-09-25 | 232:11457 | URBAN | Planned Outage | 880768 | 324 | 180 | 58320 | 0.035543 | 0.019746
2012-09-25 | 256:80635 | URBAN | Planned Outage | 880907 | 109 | 360 | 39240 | 0.023915 | 0.006643
2012-09-25 | 243:80081 | URBAN | Planned Outage | 881127 | 70 | 520 | 36400 | 0.022184 | 0.0042662
2012-09-25 | 227:13019 | SHORT RURAL | Planned Outage | 881130 | 12 | 430 | 5160 | 0.0031448 | 0.00073134
2012-09-25 | 512:48047 | SHORT RURAL | Planned Outage | 881138 | 101 | 446 | 45046 | 0.027453 | 0.0061555
2012-09-25 | 509:48039 | LONG RURAL | Planned Outage | 881139 | 33 | 420 | 13860 | 0.008447 | 0.0020112
2012-09-25 | 512:48049 | SHORT RURAL | Planned Outage | 881141 | 3 | 60 | 180 | 0.0001097 | 0.00018284
2012-09-25 | 810:74050 | SHORT RURAL | Planned Outage | 881143 | 1 | 130 | 130 | 7.9229e-05 | 6.0945e-05
2012-09-26 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 881144 | 32 | 480 | 15360 | 0.0093612 | 0.0019503
2012-09-25 | ZN7900:PA11 | URBAN | Planned Outage | 881192 | 2 | 540 | 1080 | 0.00065821 | 0.00012189
2012-09-25 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 881198 | 1 | 510 | 510 | 0.00031082 | 6.0945e-05
2012-09-25 | ZN12600:PA11 | URBAN | Planned Outage | 881210 | 30 | 360 | 10800 | 0.0065821 | 0.0018284
2012-09-25 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 881245 | 32 | 480 | 2760 | 0.0016821 | 0.0019502
2012-09-25 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 881245 | 7 | 480 | 3360 | 0.0020478 | 0.00042662
2012-09-25 | ZN12570:PA1 | SHORT RURAL | Planned Outage | 881257 | 52 | 480 | 24960 | 0.015212 | 0.0031691
2012-09-25 | ZN14892:PA3 | SHORT RURAL | Planned Outage | 881259 | 69 | 480 | 33120 | 0.020185 | 0.0042052
2012-09-27 | 509:48039 | LONG RURAL | Planned Outage | 881554 | 39 | 250 | 9750 | 0.0059422 | 0.0023769
2012-09-26 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 881561 | 118 | 510 | 60180 | 0.036677 | 0.0071915
2012-09-27 | 232:33413 | SHORT RURAL | Planned Outage | 881585 | 26 | 180 | 4680 | 0.0028522 | 0.0015846
2012-09-27 | 243:80075 | SHORT RURAL | Planned Outage | 881611 | 79 | 330 | 26070 | 0.015888 | 0.0048147
2012-09-26 | ZN12570:PA1 | SHORT RURAL | Planned Outage | 881625 | 216 | 480 | 103680 | 0.063188 | 0.013164
2012-09-26 | ZN14892:PA13 | URBAN | Planned Outage | 881657 | 53 | 480 | 25440 | 0.015504 | 0.0032301
2012-09-26 | 260:33350 | SHORT RURAL | Planned Outage | 881710 | 19 | 25 | 475 | 0.00028949 | 0.001158
2012-09-26 | 260:33350 | SHORT RURAL | Planned Outage | 881712 | 19 | 10 | 190 | 0.0001158 | 0.001158
2012-09-26 | 228:7490 | SHORT RURAL | Planned Outage | 881714 | 1 | 450 | 450 | 0.00027425 | 6.0945e-05
2012-09-26 | 509:48039 | LONG RURAL | Planned Outage | 881738 | 5 | 115 | 575 | 0.00035044 | 0.00030473
2012-09-26 | 813:89061 | LONG RURAL | Planned Outage | 881746 | 1 | 190 | 190 | 0.0001158 | 6.0945e-05
2012-09-26 | ZN36300:PA3 | URBAN | Planned Outage | 881749 | 216 | 420 | 90720 | 0.05529 | 0.013164
2012-09-26 | ZN15005:PA4 | URBAN | Planned Outage | 881759 | 52 | 420 | 21840 | 0.01331 | 0.0031692
2012-09-26 | 801:74121 | SHORT RURAL | Planned Outage | 881770 | 3 | 270 | 810 | 0.00049366 | 0.00018284
2012-09-26 | 513:48059 | SHORT RURAL | Planned Outage | 881772 | 13 | 340 | 4420 | 0.0026938 | 0.00079229
2012-09-26 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 881773 | 57 | 450 | 25650 | 0.015632 | 0.0034739
2012-09-26 | 812:19066 | SHORT RURAL | Planned Outage | 881783 | 41 | 305 | 12505 | 0.0076212 | 0.0024988
2012-09-27 | 524:33572 | SHORT RURAL | Planned Outage | 881826 | 354 | 390 | 138060 | 0.084141 | 0.021575
2012-09-27 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 881947 | 22 | 510 | 11220 | 0.0068381 | 0.0013408
2012-09-27 | ZN180:PA7 | URBAN | Planned Outage | 881961 | 64 | 420 | 26880 | 0.016382 | 0.0039005
2012-09-27 | ZN14891:PA14 | SHORT RURAL | Planned Outage | 881962 | 6 | 480 | 2880 | 0.0017552 | 0.00036567
2012-09-27 | ZN14892:PA8 | URBAN | Planned Outage | 881967 | 105 | 480 | 50400 | 0.030716 | 0.0063993
2012-09-28 | 504:48033 | SHORT RURAL | Planned Outage | 881970 | 411 | 480 | 197280 | 0.12023 | 0.025049
2012-09-27 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 881973 | 21 | 480 | 10080 | 0.0061433 | 0.0012799
2012-09-27 | ZN12580:PA1 | URBAN | Planned Outage | 881994 | 46 | 480 | 22080 | 0.013457 | 0.0028035
2012-09-27 | 264:81240 | SHORT RURAL | Planned Outage | 882031 | 4 | 420 | 1680 | 0.0010239 | 0.00024378
2012-09-27 | 513:48059 | SHORT RURAL | Planned Outage | 882053 | 1 | 44 | 44 | 2.6816e-05 | 6.0945e-05
2012-09-27 | 801:74123 | SHORT RURAL | Planned Outage | 882059 | 3 | 310 | 930 | 0.00056679 | 0.00018284
2012-09-27 | 810:74050 | SHORT RURAL | Planned Outage | 882075 | 1 | 285 | 285 | 0.00017369 | 6.0945e-05
2012-09-27 | 516:48067 | SHORT RURAL | Planned Outage | 882088 | 18 | 220 | 3960 | 0.0024134 | 0.001097
2012-09-27 | 513:48059 | SHORT RURAL | Planned Outage | 882132 | 1 | 60 | 60 | 3.6567e-05 | 6.0945e-05
2012-09-28 | 231:8405 | SHORT RURAL | Planned Outage | 883235 | 39 | 415 | 16185 | 0.009864 | 0.0023769
2012-09-28 | 260:33350 | SHORT RURAL | Planned Outage | 883236 | 19 | 20 | 380 | 0.00023159 | 0.001158
2012-09-28 | 260:33350 | SHORT RURAL | Planned Outage | 883237 | 19 | 10 | 190 | 0.0001158 | 0.001158
2012-09-30 | 235:2120 | SHORT RURAL | Planned Outage | 883244 | 32 | 480 | 15360 | 0.0093612 | 0.0019503
2012-09-28 | 513:48059 | SHORT RURAL | Planned Outage | 883246 | 1 | 35 | 35 | 2.1331e-05 | 6.0945e-05
2012-09-30 | 514:18137 | SHORT RURAL | Planned Outage | 883253 | 2 | 390 | 780 | 0.00047537 | 0.00012189
2012-10-02 | 264:81240 | SHORT RURAL | Planned Outage | 883400 | 4 | 290 | 1160 | 0.00070681 | 0.00024373
2012-10-02 | 225:33670 | SHORT RURAL | Planned Outage | 883403 | 3 | 23 | 69 | 4.2043e-05 | 0.00018279
2012-10-02 | 801:74121 | SHORT RURAL | Planned Outage | 883404 | 4 | 450 | 1800 | 0.0010968 | 0.00024373
2012-10-02 | 243:80083 | SHORT RURAL | Planned Outage | 883424 | 13 | 320 | 4160 | 0.0025347 | 0.00079211
2012-10-02 | 511:29878 | SHORT RURAL | Planned Outage | 883426 | 1 | 100 | 100 | 6.0931e-05 | 6.0931e-05
2012-10-02 | 502:48010 | SHORT RURAL | Planned Outage | 883441 | 83 | 345 | 28635 | 0.017448 | 0.0050573
2012-10-02 | 512:48049 | SHORT RURAL | Planned Outage | 883456 | 2 | 180 | 360 | 0.00021935 | 0.00012186
2012-10-02 | 813:89061 | LONG RURAL | Planned Outage | 883458 | 3 | 45 | 135 | 8.2257e-05 | 0.00018279
2012-10-03 | 812:19066 | SHORT RURAL | Planned Outage | 883701 | 41 | 114 | 4674 | 0.0028479 | 0.0024982
2012-10-03 | 813:89055 | SHORT RURAL | Planned Outage | 883705 | 1 | 330 | 330 | 0.00020107 | 6.0932e-05
2012-10-03 | 509:48040 | SHORT RURAL | Planned Outage | 883706 | 22 | 340 | 7480 | 0.0045577 | 0.0013405
2012-10-03 | 523:33501 | SHORT RURAL | Planned Outage | 883707 | 93 | 344 | 31992 | 0.019493 | 0.0056666
2012-10-03 | 230:81440 | URBAN | Planned Outage | 883736 | 103 | 520 | 53560 | 0.032635 | 0.0062759
2012-10-03 | 232:33413 | SHORT RURAL | Planned Outage | 883934 | 34 | 135 | 4590 | 0.0027968 | 0.0020717
2012-10-03 | 503:48011 | SHORT RURAL | Planned Outage | 883938 | 298 | 420 | 125160 | 0.076262 | 0.018158
2012-10-03 | 264:81240 | SHORT RURAL | Planned Outage | 883943 | 52 | 485 | 25220 | 0.015367 | 0.0031684
2012-10-05 | 511:29877 | SHORT RURAL | Planned Outage | 884289 | 69 | 115 | 7935 | 0.0048426 | 0.004211
2012-09-28 | ZN129:PA9 | URBAN | Planned Outage | 884926 | 3 | 480 | 1440 | 0.00087761 | 0.00018284
2012-09-28 | ZN12640:PA1 | SHORT RURAL | Planned Outage | 884932 | 1 | 300 | 300 | 0.00018284 | 6.0945e-05
2012-09-28 | ZN8700:PA63 64DEF | CBD | Planned Outage | 884935 | 39 | 329 | 12831 | 0.0078199 | 0.0023769
2012-09-29 | ZN4990:PA55 56GHJ | CBD | Planned Outage | 884945 | 92 | 240 | 22080 | 0.013457 | 0.005607
2012-09-29 | ZN8700:PA65 66GHJ | CBD | Planned Outage | 884950 | 4 | 540 | 2160 | 0.0013164 | 0.00024378
2012-09-29 | ZN8700:PA63 64ABC | CBD | Planned Outage | 884953 | 7 | 900 | 6300 | 0.0038396 | 0.00042662
2012-10-02 | ZN12610:PA17 | URBAN | Planned Outage | 884962 | 42 | 360 | 15120 | 0.0092128 | 0.0025591
2012-10-08 | ZN12660:PA10 | SHORT RURAL | Planned Outage | 884965 | 55 | 480 | 26400 | 0.016112 | 0.0033566
2012-10-02 | ZN12590:PA2 | URBAN | Planned Outage | 884970 | 89 | 480 | 42720 | 0.02603 | 0.0054229
2012-10-02 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 884971 | 2 | 480 | 960 | 0.00058494 | 0.00012186
2012-10-02 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 884994 | 21 | 480 | 10080 | 0.0061419 | 0.0012796
2012-10-02 | ZN14892:PA3 | SHORT RURAL | Planned Outage | 885011 | 75 | 480 | 36000 | 0.021935 | 0.0045699
2012-10-02 | ZN965:PA46 | URBAN | Planned Outage | 885017 | 63 | 420 | 26460 | 0.016122 | 0.0038387
2012-10-03 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 885039 | 29 | 480 | 4020 | 0.0024494 | 0.001767
2012-10-03 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 885039 | 7 | 480 | 3360 | 0.0020473 | 0.00042652
2012-10-04 | 229:34983 | SHORT RURAL | Planned Outage | 885042 | 25 | 240 | 6000 | 0.0036559 | 0.0015233
2012-10-03 | ZN384:PA3 | SHORT RURAL | Planned Outage | 885065 | 156 | 120 | 18720 | 0.011406 | 0.0095053
2012-10-03 | ZN3472:PA29 | URBAN | Planned Outage | 885084 | 2 | 420 | 840 | 0.00051182 | 0.00012186
2012-10-04 | 216:10728 | URBAN | Planned Outage | 885085 | 1 | 80 | 80 | 4.8745e-05 | 6.0932e-05
2012-10-04 | 217:33611 | URBAN | Planned Outage | 885088 | 86 | 140 | 12040 | 0.0073362 | 0.0052401
2012-10-04 | 243:80083 | SHORT RURAL | Planned Outage | 885090 | 8 | 180 | 1440 | 0.00087741 | 0.00048745
2012-10-04 | 264:81240 | SHORT RURAL | Planned Outage | 885093 | 5 | 285 | 1425 | 0.00086827 | 0.00030466
2012-10-05 | 232:11453 | SHORT RURAL | Planned Outage | 885096 | 108 | 420 | 45360 | 0.027683 | 0.0065911
2012-10-06 | 232:11454 | SHORT RURAL | Planned Outage | 885104 | 147 | 275 | 40425 | 0.024671 | 0.0089712
2012-10-03 | ZN9700:PA23 | URBAN | Planned Outage | 885114 | 47 | 420 | 19740 | 0.012028 | 0.0028638
2012-10-03 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 885124 | 10 | 480 | 4800 | 0.0029247 | 0.00060932
2012-10-03 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 885130 | 68 | 480 | 32640 | 0.019888 | 0.0041433
2012-10-03 | ZN12610:PA20 | SHORT RURAL | Planned Outage | 885132 | 21 | 480 | 10080 | 0.0061419 | 0.0012796
2012-10-03 | ZN15008:PA9 | URBAN | Planned Outage | 885134 | 61 | 330 | 20130 | 0.012266 | 0.0037168
2012-10-07 | 227:13015 | SHORT RURAL | Planned Outage | 885136 | 93 | 480 | 44640 | 0.027243 | 0.0056757
2012-10-07 | 258:80773 | URBAN | Planned Outage | 885138 | 3 | 105 | 315 | 0.00019224 | 0.00018309
2012-10-04 | 501:48115 | SHORT RURAL | Planned Outage | 885140 | 24 | 365 | 8760 | 0.0053376 | 0.0014624
2012-10-04 | 509:48039 | LONG RURAL | Planned Outage | 885142 | 1 | 215 | 215 | 0.000131 | 6.0932e-05
2012-10-05 | 509:48039 | LONG RURAL | Planned Outage | 885146 | 1 | 120 | 120 | 7.3234e-05 | 6.1029e-05
2012-10-05 | 511:29878 | SHORT RURAL | Planned Outage | 885147 | 1 | 105 | 105 | 6.408e-05 | 6.1029e-05
2012-10-06 | 501:48125 | URBAN | Planned Outage | 885179 | 74 | 135 | 9990 | 0.0060968 | 0.0045161
2012-10-04 | 513:48059 | SHORT RURAL | Planned Outage | 885194 | 8 | 270 | 2160 | 0.0013161 | 0.00048745
2012-10-04 | 813:89061 | LONG RURAL | Planned Outage | 885198 | 18 | 155 | 2790 | 0.0017 | 0.0010968
2012-10-04 | 813:89061 | LONG RURAL | Planned Outage | 885199 | 3 | 260 | 780 | 0.00047527 | 0.00018279
2012-10-06 | 810:74050 | SHORT RURAL | Planned Outage | 885200 | 1 | 140 | 140 | 8.544e-05 | 6.1029e-05
2012-10-06 | 810:74050 | SHORT RURAL | Planned Outage | 885202 | 11 | 160 | 1760 | 0.0010741 | 0.00067132
2012-10-07 | 515:35197 | LONG RURAL | Planned Outage | 885206 | 11 | 320 | 3520 | 0.0021482 | 0.00067132
2012-10-04 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 885230 | 40 | 480 | 6600 | 0.0040215 | 0.0024373
2012-10-04 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 885241 | 6 | 480 | 360 | 0.00021935 | 0.00036559
2012-10-04 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 885243 | 7 | 480 | 3360 | 0.0020473 | 0.00042652
2012-10-04 | ZN965:PA28 | SHORT RURAL | Planned Outage | 885250 | 98 | 420 | 41160 | 0.025079 | 0.0059713
2012-10-04 | ZN12640:PA1 | SHORT RURAL | Planned Outage | 885252 | 1 | 300 | 300 | 0.00018279 | 6.0932e-05
2012-10-04 | ZN4545:PA33 | SHORT RURAL | Planned Outage | 885255 | 163 | 300 | 48900 | 0.029796 | 0.0099318
2012-10-04 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 885258 | 11 | 360 | 3960 | 0.0024129 | 0.00067025
2012-10-05 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 885266 | 21 | 480 | 10080 | 0.0061517 | 0.0012816
2012-10-05 | ZN12610:PA22 | URBAN | Planned Outage | 885274 | 125 | 480 | 60000 | 0.036617 | 0.0076286
2012-10-05 | ZN12660:PA14 | SHORT RURAL | Planned Outage | 885276 | 82 | 480 | 39360 | 0.024021 | 0.0050044
2012-10-05 | ZN15009:PA1 | URBAN | Planned Outage | 885280 | 70 | 270 | 18900 | 0.011534 | 0.004272
2012-10-06 | ZN711:PA14 | URBAN | Planned Outage | 885284 | 74 | 30 | 2220 | 0.0013548 | 0.0045161
2012-10-06 | ZN188:PA22 | URBAN | Planned Outage | 885289 | 2 | 480 | 960 | 0.00058588 | 0.00012206
2012-10-06 | ZN12570:PA35 | URBAN | Planned Outage | 885290 | 95 | 480 | 45600 | 0.027829 | 0.0057977
2012-10-06 | ZN12580:PA10 | URBAN | Planned Outage | 885290 | 70 | 480 | 33600 | 0.020506 | 0.004272
2012-10-06 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 885296 | 10 | 480 | 4800 | 0.0029294 | 0.00061029
2012-10-07 | ZN3472:PA35 | URBAN | Planned Outage | 885306 | 10 | 630 | 6300 | 0.0038448 | 0.00061029
2012-10-08 | ZN690:PA35 | URBAN | Planned Outage | 885457 | 6 | 60 | 360 | 0.0002197 | 0.00036617
2012-10-08 | ZN12620:PA10 | SHORT RURAL | Planned Outage | 885458 | 116 | 540 | 3480 | 0.0021238 | 0.0070793
2012-10-08 | ZN847:PA15 | URBAN | Planned Outage | 885460 | 1 | 480 | 480 | 0.00029294 | 6.1029e-05
2012-10-08 | 260:33344 | URBAN | Planned Outage | 885478 | 110 | 30 | 3300 | 0.0020139 | 0.0067132
2012-10-08 | 229:34995 | SHORT RURAL | Planned Outage | 885480 | 4 | 240 | 960 | 0.00058588 | 0.00024411
2012-10-08 | 243:80080 | SHORT RURAL | Planned Outage | 885486 | 48 | 235 | 11280 | 0.006884 | 0.0029294
2012-10-08 | 232:33413 | SHORT RURAL | Planned Outage | 885490 | 1 | 360 | 360 | 0.0002197 | 6.1029e-05
2012-10-08 | 227:13015 | SHORT RURAL | Planned Outage | 885500 | 18 | 310 | 5580 | 0.0034054 | 0.0010985
2012-10-08 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 885503 | 25 | 510 | 12750 | 0.0077812 | 0.0015257
2012-10-08 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 885503 | 6 | 510 | 3060 | 0.0018675 | 0.00036617
2012-10-08 | 509:48039 | LONG RURAL | Planned Outage | 885513 | 2 | 190 | 380 | 0.00023191 | 0.00012206
2012-10-08 | 504:48027 | URBAN | Planned Outage | 885515 | 2 | 335 | 670 | 0.00040889 | 0.00012206
2012-10-08 | ZN2473:PA31 | URBAN | Planned Outage | 885517 | 99 | 420 | 41580 | 0.025376 | 0.0060418
2012-10-08 | 515:35197 | LONG RURAL | Planned Outage | 885518 | 39 | 380 | 14820 | 0.0090445 | 0.0023801
2012-10-08 | ZN14892:PA13 | URBAN | Planned Outage | 885527 | 124 | 480 | 59520 | 0.036324 | 0.0075676
2012-10-08 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 885532 | 2 | 390 | 780 | 0.00047602 | 0.00012206
2012-10-08 | ZN9035:PA1 | URBAN | Planned Outage | 885534 | 71 | 450 | 31950 | 0.019499 | 0.004333
2012-10-08 | ZN342:PA26 | URBAN | Planned Outage | 885536 | 130 | 420 | 54600 | 0.033322 | 0.0079337
2012-10-09 | ZN12640:PA19 | URBAN | Planned Outage | 885902 | 145 | 510 | 73950 | 0.045056 | 0.0088344
2012-10-09 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 885903 | 32 | 480 | 2760 | 0.0016816 | 0.0019497
2012-10-09 | ZN384:PA3 | SHORT RURAL | Planned Outage | 885917 | 366 | 120 | 43920 | 0.026759 | 0.022299
2012-10-09 | ZN1610:PA13 | URBAN | Planned Outage | 885923 | 73 | 420 | 30660 | 0.01868 | 0.0044477
2012-10-09 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 885924 | 11 | 480 | 5280 | 0.0032169 | 0.0006702
2012-10-09 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 885926 | 52 | 480 | 24960 | 0.015207 | 0.0031682
2012-10-09 | ZN12570:PA37 | SHORT RURAL | Planned Outage | 885934 | 38 | 480 | 18240 | 0.011113 | 0.0023152
2012-10-09 | ZN3155:PA44 | URBAN | Planned Outage | 885936 | 92 | 330 | 30360 | 0.018497 | 0.0056053
2012-10-09 | 243:80080 | SHORT RURAL | Planned Outage | 885939 | 27 | 370 | 9990 | 0.0060866 | 0.001645
2012-10-09 | 264:81240 | SHORT RURAL | Planned Outage | 885940 | 33 | 330 | 10890 | 0.006635 | 0.0020106
2012-10-09 | ZN3288:PA41 42ABC | CBD | Planned Outage | 885941 | 1 | 30 | 30 | 1.8278e-05 | 6.0927e-05
2012-10-09 | 229:34995 | SHORT RURAL | Planned Outage | 885944 | 38 | 400 | 15200 | 0.0092609 | 0.0023152
2012-10-09 | 243:80080 | SHORT RURAL | Planned Outage | 885951 | 23 | 105 | 2415 | 0.0014714 | 0.0014013
2012-10-09 | 501:48123 | SHORT RURAL | Planned Outage | 885968 | 18 | 344 | 6192 | 0.0037726 | 0.0010967
2012-10-09 | 507:80923 | SHORT RURAL | Planned Outage | 885970 | 2 | 320 | 640 | 0.00038993 | 0.00012185
2012-10-09 | 524:33572 | SHORT RURAL | Planned Outage | 885987 | 3 | 290 | 870 | 0.00053007 | 0.00018278
2012-10-09 | 509:48040 | SHORT RURAL | Planned Outage | 885988 | 97 | 510 | 49470 | 0.030141 | 0.0059099
2012-10-10 | ZN12660:PA10 | SHORT RURAL | Planned Outage | 886400 | 19 | 480 | 9120 | 0.0055566 | 0.0011576
2012-10-10 | ZN2473:PA22 | SHORT RURAL | Planned Outage | 886405 | 153 | 510 | 78030 | 0.047541 | 0.0093218
2012-10-10 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 886406 | 10 | 510 | 5100 | 0.0031073 | 0.00060927
2012-10-10 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 886428 | 23 | 1501.5667 | 15126.2667 | 0.009216 | 0.0014013
2012-10-10 | ZN965:PA28 | SHORT RURAL | Planned Outage | 886462 | 49 | 420 | 20580 | 0.012539 | 0.0029854
2012-10-10 | ZN2466:PA41 | URBAN | Planned Outage | 886467 | 27 | 538 | 14526 | 0.0088503 | 0.001645
2012-10-10 | 813:89062 | SHORT RURAL | Planned Outage | 886661 | 11 | 287 | 3157 | 0.0019235 | 0.0006702
2012-10-10 | 260:33347 | SHORT RURAL | Planned Outage | 886665 | 1 | 400 | 400 | 0.00024371 | 6.0927e-05
2012-10-10 | 243:80083 | SHORT RURAL | Planned Outage | 886668 | 3 | 365 | 1095 | 0.00066715 | 0.00018278
2012-10-10 | 225:13444 | URBAN | Planned Outage | 886669 | 266 | 135 | 35910 | 0.021879 | 0.016207
2012-10-10 | 256:80632 | URBAN | Planned Outage | 886671 | 107 | 420 | 44940 | 0.027381 | 0.0065192
2012-10-10 | 229:34983 | SHORT RURAL | Planned Outage | 886673 | 4 | 240 | 960 | 0.0005849 | 0.00024371
2012-10-10 | 202:34259 | URBAN | Planned Outage | 886676 | 4 | 40 | 160 | 9.7483e-05 | 0.00024371
2012-10-10 | 501:48115 | SHORT RURAL | Planned Outage | 886679 | 1 | 25 | 25 | 1.5232e-05 | 6.0927e-05
2012-10-10 | 507:80922 | SHORT RURAL | Planned Outage | 886683 | 35 | 135 | 4725 | 0.0028788 | 0.0021324
2012-10-10 | 813:89062 | SHORT RURAL | Planned Outage | 886697 | 1 | 442 | 442 | 0.0002693 | 6.0927e-05
2012-10-10 | 509:48040 | SHORT RURAL | Planned Outage | 886756 | 9 | 160 | 1440 | 0.00087735 | 0.00054834
2012-10-11 | ZN188:PA27 | URBAN | Planned Outage | 886914 | 42 | 15 | 630 | 0.00038384 | 0.0025589
2012-10-11 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 886915 | 114 | 540 | 61560 | 0.037507 | 0.0069457
2012-10-11 | ZN690:PA24 | SHORT RURAL | Planned Outage | 886925 | 1 | 450 | 450 | 0.00027417 | 6.0927e-05
2012-10-11 | ZN9245:PA13 | URBAN | Planned Outage | 886927 | 3 | 510 | 1530 | 0.00093219 | 0.00018278
2012-10-11 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 886945 | 66 | 480 | 18240 | 0.011113 | 0.0040212
2012-10-11 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 886960 | 15 | 480 | 7200 | 0.0043868 | 0.00091391
2012-10-11 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 886968 | 13 | 480 | 6240 | 0.0038019 | 0.00079205
2012-10-11 | ZN12640:PA1 | SHORT RURAL | Planned Outage | 886974 | 1 | 300 | 300 | 0.00018278 | 6.0927e-05
2012-10-11 | ZN129:PA28 | URBAN | Planned Outage | 886975 | 2 | 300 | 600 | 0.00036556 | 0.00012185
2012-10-11 | 509:48040 | SHORT RURAL | Planned Outage | 887877 | 9 | 250 | 2250 | 0.0013709 | 0.00054834
2012-10-11 | 509:48040 | SHORT RURAL | Planned Outage | 887881 | 22 | 15 | 330 | 0.00020106 | 0.0013404
2012-10-11 | 264:81240 | SHORT RURAL | Planned Outage | 887896 | 27 | 365 | 9855 | 0.0060044 | 0.001645
2012-10-12 | 513:48059 | SHORT RURAL | Planned Outage | 887911 | 8 | 215 | 1720 | 0.0010479 | 0.00048742
2012-10-12 | 229:34989 | SHORT RURAL | Planned Outage | 887923 | 75 | 270 | 20250 | 0.012338 | 0.0045695
2012-10-12 | 509:48040 | SHORT RURAL | Planned Outage | 887931 | 22 | 230 | 5060 | 0.0030829 | 0.0013404
2012-10-12 | 509:48040 | SHORT RURAL | Planned Outage | 887933 | 9 | 230 | 2070 | 0.0012612 | 0.00054835
2012-10-14 | 511:29872 | URBAN | Planned Outage | 887949 | 24 | 360 | 8640 | 0.0052641 | 0.0014623
2012-10-11 | 234:33444 | SHORT RURAL | Planned Outage | 887959 | 3 | 230 | 690 | 0.0004204 | 0.00018278
2012-10-11 | 227:13019 | SHORT RURAL | Planned Outage | 887961 | 12 | 330 | 3960 | 0.0024127 | 0.00073113
2012-10-11 | 217:33612 | URBAN | Planned Outage | 887967 | 4 | 250 | 1000 | 0.00060927 | 0.00024371
2012-10-12 | 214:8666 | URBAN | Planned Outage | 887970 | 1 | 590 | 590 | 0.00035947 | 6.0927e-05
2012-10-12 | 258:80778 | URBAN | Planned Outage | 887974 | 107 | 340 | 36380 | 0.022165 | 0.0065192
2012-10-12 | 232:11460 | URBAN | Planned Outage | 887976 | 135 | 65 | 8775 | 0.0053464 | 0.0082252
2012-10-12 | 227:13015 | SHORT RURAL | Planned Outage | 887978 | 18 | 205 | 3690 | 0.0022482 | 0.0010967
2012-10-12 | 235:2121 | URBAN | Planned Outage | 887979 | 1 | 215 | 215 | 0.00013099 | 6.0927e-05
2012-10-13 | 232:33413 | SHORT RURAL | Planned Outage | 887982 | 62 | 310 | 19220 | 0.01171 | 0.0037775
2012-10-11 | 264:81240 | SHORT RURAL | Planned Outage | 887988 | 222 | 429 | 95238 | 0.058026 | 0.013526
2012-10-11 | 509:48039 | LONG RURAL | Planned Outage | 887989 | 32 | 135 | 4320 | 0.0026321 | 0.0019497
2012-10-11 | 509:48039 | LONG RURAL | Planned Outage | 887991 | 1 | 115 | 115 | 7.0066e-05 | 6.0927e-05
2012-10-12 | 502:48010 | SHORT RURAL | Planned Outage | 887995 | 2 | 280 | 560 | 0.00034119 | 0.00012185
2012-10-13 | 509:48040 | SHORT RURAL | Planned Outage | 888005 | 9 | 275 | 2475 | 0.001508 | 0.00054835
2012-10-13 | 509:48040 | SHORT RURAL | Planned Outage | 888006 | 22 | 285 | 6270 | 0.0038201 | 0.0013404
2012-10-13 | 509:48040 | SHORT RURAL | Planned Outage | 888007 | 22 | 10 | 220 | 0.00013404 | 0.0013404
2012-10-14 | 504:48034 | URBAN | Planned Outage | 888008 | 89 | 405 | 36045 | 0.021961 | 0.0054225
2012-10-14 | 501:48118 | SHORT RURAL | Planned Outage | 888011 | 49 | 195 | 9555 | 0.0058216 | 0.0029854
2012-10-12 | 807:74184 | SHORT RURAL | Planned Outage | 888013 | 18 | 200 | 3600 | 0.0021934 | 0.0010967
2012-10-13 | 813:89055 | SHORT RURAL | Planned Outage | 888015 | 2 | 315 | 630 | 0.00038384 | 0.00012185
2012-10-13 | 813:89061 | LONG RURAL | Planned Outage | 888017 | 1 | 110 | 110 | 6.702e-05 | 6.0927e-05
2012-10-13 | 813:89061 | LONG RURAL | Planned Outage | 888020 | 1 | 92 | 92 | 5.6053e-05 | 6.0927e-05
2012-10-16 | 512:48047 | SHORT RURAL | Planned Outage | 888150 | 101 | 463 | 46763 | 0.028476 | 0.0061503
2012-10-12 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 888209 | 6 | 480 | 2880 | 0.0017547 | 0.00036556
2012-10-12 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 888216 | 5 | 480 | 2400 | 0.0014623 | 0.00030464
2012-10-15 | 243:80083 | SHORT RURAL | Planned Outage | 888223 | 7 | 290 | 2030 | 0.0012368 | 0.00042649
2012-10-12 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 888226 | 5 | 360 | 1200 | 0.00073113 | 0.00030464
2012-10-15 | 227:13015 | SHORT RURAL | Planned Outage | 888227 | 18 | 405 | 7290 | 0.0044416 | 0.0010967
2012-10-15 | 509:48040 | SHORT RURAL | Planned Outage | 888235 | 9 | 375 | 3375 | 0.0020563 | 0.00054835
2012-10-13 | ZN188:PA2 | URBAN | Planned Outage | 888236 | 3 | 15 | 45 | 2.7417e-05 | 0.00018278
2012-10-15 | 511:29878 | SHORT RURAL | Planned Outage | 888240 | 2 | 285 | 570 | 0.00034729 | 0.00012185
2012-10-13 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 888241 | 10 | 480 | 4800 | 0.0029245 | 0.00060927
2012-10-15 | 801:74123 | SHORT RURAL | Planned Outage | 888246 | 45 | 525 | 23625 | 0.014394 | 0.0027417
2012-10-15 | 512:48049 | SHORT RURAL | Planned Outage | 888249 | 3 | 362 | 1086 | 0.00066167 | 0.00018278
2012-10-13 | ZN3288:PA45 46GHJ | CBD | Planned Outage | 888257 | 5 | 600 | 3000 | 0.0018278 | 0.00030464
2012-10-15 | 803:74007 | SHORT RURAL | Planned Outage | 888258 | 3 | 55 | 165 | 0.00010053 | 0.00018278
2012-10-13 | ZN3288:PA45 46GHJ | CBD | Planned Outage | 888259 | 1 | 300 | 300 | 0.00018278 | 6.0927e-05
2012-10-13 | ZN1788:PA16 | URBAN | Planned Outage | 888260 | 2 | 30 | 60 | 3.6556e-05 | 0.00012185
2012-10-14 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 888295 | 4 | 420 | 360 | 0.00021934 | 0.00024371
2012-10-15 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 888323 | 1 | 510 | 510 | 0.00031073 | 6.0927e-05
2012-10-15 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 888327 | 51 | 480 | 24480 | 0.014915 | 0.0031073
2012-10-15 | ZN12570:PA6 | SHORT RURAL | Planned Outage | 888343 | 42 | 480 | 20160 | 0.012283 | 0.0025589
2012-10-15 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 888352 | 63 | 480 | 30240 | 0.018424 | 0.0038384
2012-10-15 | ZN14892:PA19 | URBAN | Planned Outage | 888355 | 93 | 480 | 44640 | 0.027198 | 0.0056662
2012-10-15 | ZN2310:PA34 | URBAN | Planned Outage | 888359 | 69 | 600 | 41400 | 0.025224 | 0.004204
2012-10-15 | ZN1068:PA26 | URBAN | Planned Outage | 888362 | 126 | 270 | 34020 | 0.020727 | 0.0076768
2012-10-16 | ZN12610:PA20 | SHORT RURAL | Planned Outage | 888678 | 200 | 420 | 84000 | 0.051151 | 0.012179
2012-10-16 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 888683 | 31 | 420 | 13020 | 0.0079284 | 0.0018877
2012-10-16 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 888687 | 11 | 480 | 5280 | 0.0032152 | 0.00066984
2012-10-16 | ZN12570:PA37 | SHORT RURAL | Planned Outage | 888692 | 97 | 480 | 46560 | 0.028352 | 0.0059068
2012-10-16 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 888814 | 57 | 480 | 27360 | 0.016661 | 0.003471
2012-10-16 | ZN72:PA23 | URBAN | Planned Outage | 888920 | 144 | 480 | 69120 | 0.04209 | 0.0087688
2012-10-16 | 227:13020 | SHORT RURAL | Planned Outage | 888975 | 157 | 315 | 49455 | 0.030115 | 0.0095604
2012-10-16 | 501:48123 | SHORT RURAL | Planned Outage | 888980 | 36 | 230 | 8280 | 0.0050421 | 0.0021922
2012-10-16 | 202:34259 | URBAN | Planned Outage | 888985 | 32 | 380 | 12160 | 0.0074048 | 0.0019486
2012-10-16 | 501:48123 | SHORT RURAL | Planned Outage | 888991 | 5 | 190 | 950 | 0.0005785 | 0.00030447
2012-10-16 | 515:35198 | SHORT RURAL | Planned Outage | 888995 | 5 | 135 | 675 | 0.00041104 | 0.00030447
2012-10-16 | 523:33511 | SHORT RURAL | Planned Outage | 888997 | 13 | 150 | 1950 | 0.0011874 | 0.00079163
2012-10-16 | 803:74010 | SHORT RURAL | Planned Outage | 889004 | 19 | 255 | 4845 | 0.0029503 | 0.001157
2012-10-16 | 515:35198 | SHORT RURAL | Planned Outage | 889005 | 2 | 115 | 230 | 0.00014006 | 0.00012179
2012-10-17 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 889161 | 31 | 420 | 13020 | 0.0079285 | 0.0018877
2012-10-17 | ZN12640:PA18 | SHORT RURAL | Planned Outage | 889163 | 107 | 480 | 51360 | 0.031275 | 0.0065157
2012-10-17 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 889181 | 421 | 480 | 202080 | 0.12306 | 0.025637
2012-10-17 | ZN35370:PA10 | SHORT RURAL | Planned Outage | 889190 | 64 | 420 | 26880 | 0.016368 | 0.0038973
2012-10-17 | 260:33344 | URBAN | Planned Outage | 889384 | 110 | 360 | 39600 | 0.024114 | 0.0066984
2012-10-17 | 264:81240 | SHORT RURAL | Planned Outage | 889389 | 41 | 380 | 15580 | 0.0094874 | 0.0024967
2012-10-17 | 243:80083 | SHORT RURAL | Planned Outage | 889393 | 15 | 450 | 6750 | 0.0041104 | 0.00091342
2012-10-17 | 507:80923 | SHORT RURAL | Planned Outage | 889396 | 15 | 247 | 3705 | 0.0022561 | 0.00091342
2012-10-17 | 514:18137 | SHORT RURAL | Planned Outage | 889409 | 36 | 400 | 14400 | 0.0087688 | 0.0021922
2012-10-17 | 514:18137 | SHORT RURAL | Planned Outage | 889411 | 33 | 275 | 9075 | 0.0055262 | 0.0020095
2012-10-18 | ZN35370:PA2 | SHORT RURAL | Planned Outage | 890301 | 15 | 480 | 7200 | 0.0043844 | 0.00091342
2012-10-18 | ZN12570:PA35 | URBAN | Planned Outage | 890308 | 3 | 480 | 1440 | 0.00087688 | 0.00018268
2012-10-18 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 890329 | 47 | 480 | 22560 | 0.013738 | 0.0028621
2012-10-19 | 238:34144 | URBAN | Planned Outage | 890337 | 757 | 570 | 11130 | 0.0067776 | 0.046097
2012-10-18 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 890389 | 18 | 480 | 8640 | 0.0052613 | 0.0010961
2012-10-18 | ZN12610:PA20 | SHORT RURAL | Planned Outage | 890523 | 21 | 480 | 10080 | 0.0061382 | 0.0012788
2012-10-18 | ZN15001:PA18 | URBAN | Planned Outage | 890524 | 110 | 390 | 3300 | 0.0020095 | 0.0066984
2012-10-18 | ZN12570:PA2 | SHORT RURAL | Planned Outage | 890528 | 2 | 330 | 660 | 0.00040191 | 0.00012179
2012-10-19 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 890532 | 6 | 60 | 360 | 0.00021922 | 0.00036537
2012-10-19 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 890538 | 1 | 510 | 510 | 0.00031056 | 6.0895e-05
2012-10-19 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 890560 | 32 | 480 | 15360 | 0.0093534 | 0.0019486
2012-10-19 | ZN12570:PA8 | SHORT RURAL | Planned Outage | 890627 | 192 | 480 | 92160 | 0.056121 | 0.011692
2012-10-19 | ZN12610:PA22 | URBAN | Planned Outage | 890641 | 33 | 480 | 15840 | 0.0096457 | 0.0020095
2012-10-19 | ZN12570:PA1 | SHORT RURAL | Planned Outage | 890673 | 494 | 480 | 237120 | 0.14439 | 0.030082
2012-10-20 | ZN80:PA24 | URBAN | Planned Outage | 891330 | 30 | 2130 | 55620 | 0.03387 | 0.0018268
2012-10-20 | ZN12570:PA34 | SHORT RURAL | Planned Outage | 891342 | 87 | 480 | 41760 | 0.02543 | 0.0052979
2012-10-20 | ZN965:PA37 | URBAN | Planned Outage | 891346 | 44 | 480 | 21120 | 0.012861 | 0.0026794
2012-10-21 | ZN263:PA35 37DEF | CBD | Planned Outage | 891356 | 14 | 600 | 8400 | 0.0051152 | 0.00085253
2012-10-22 | ZN965:PA22 | URBAN | Planned Outage | 891428 | 1 | 480 | 480 | 0.0002923 | 6.0895e-05
2012-10-22 | ZN1788:PA29 | URBAN | Planned Outage | 891431 | 23 | 480 | 11040 | 0.0067228 | 0.0014006
2012-10-22 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 891445 | 8 | 390 | 3120 | 0.0018999 | 0.00048716
2012-10-22 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 891445 | 5 | 390 | 1950 | 0.0011874 | 0.00030447
2012-10-22 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 891452 | 9 | 480 | 4320 | 0.0026307 | 0.00054805
2012-10-22 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 891454 | 11 | 480 | 5280 | 0.0032152 | 0.00066984
2012-10-18 | 509:48040 | SHORT RURAL | Planned Outage | 891461 | 9 | 345 | 3105 | 0.0018908 | 0.00054805
2012-10-18 | 813:89062 | SHORT RURAL | Planned Outage | 891464 | 11 | 285 | 3135 | 0.0019091 | 0.00066984
2012-10-18 | 243:80080 | SHORT RURAL | Planned Outage | 891471 | 59 | 255 | 15045 | 0.0091616 | 0.0035928
2012-10-22 | ZN14892:PA3 | SHORT RURAL | Planned Outage | 891476 | 142 | 480 | 68160 | 0.041506 | 0.0086471
2012-10-19 | 229:34995 | SHORT RURAL | Planned Outage | 891482 | 13 | 240 | 3120 | 0.0018999 | 0.00079163
2012-10-18 | 260:33350 | SHORT RURAL | Planned Outage | 891487 | 5 | 380 | 1900 | 0.001157 | 0.00030447
2012-10-22 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 891488 | 1 | 360 | 360 | 0.00021922 | 6.0895e-05
2012-10-19 | 258:80785 | URBAN | Planned Outage | 891490 | 1 | 370 | 370 | 0.00022531 | 6.0895e-05
2012-10-22 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 891492 | 1 | 360 | 360 | 0.00021922 | 6.0895e-05
2012-10-20 | 214:8667 | URBAN | Planned Outage | 891494 | 1 | 130 | 130 | 7.9163e-05 | 6.0895e-05
2012-10-18 | 509:48040 | SHORT RURAL | Planned Outage | 891506 | 22 | 15 | 330 | 0.00020095 | 0.0013397
2012-10-18 | 524:33576 | SHORT RURAL | Planned Outage | 891508 | 3 | 190 | 570 | 0.0003471 | 0.00018268
2012-10-18 | 509:48040 | SHORT RURAL | Planned Outage | 891509 | 24 | 220 | 5280 | 0.0032152 | 0.0014615
2012-10-18 | 501:48123 | SHORT RURAL | Planned Outage | 891511 | 18 | 450 | 8100 | 0.0049325 | 0.0010961
2012-10-18 | 501:48122 | SHORT RURAL | Planned Outage | 891516 | 35 | 351 | 12285 | 0.0074809 | 0.0021313
2012-10-19 | 510:48164 | SHORT RURAL | Planned Outage | 891521 | 16 | 320 | 5120 | 0.0031178 | 0.00097432
2012-10-19 | 509:48039 | LONG RURAL | Planned Outage | 891522 | 70 | 330 | 23100 | 0.014067 | 0.0042626
2012-10-19 | 509:48040 | SHORT RURAL | Planned Outage | 891526 | 22 | 330 | 7260 | 0.004421 | 0.0013397
2012-10-19 | 511:29878 | SHORT RURAL | Planned Outage | 891530 | 9 | 253 | 2277 | 0.0013866 | 0.00054805
2012-10-19 | 512:48047 | SHORT RURAL | Planned Outage | 891536 | 298 | 412 | 122776 | 0.074764 | 0.018147
2012-10-18 | 513:48059 | SHORT RURAL | Planned Outage | 891539 | 1 | 120 | 120 | 7.3074e-05 | 6.0895e-05
2012-10-18 | 515:35192 | SHORT RURAL | Planned Outage | 891542 | 41 | 295 | 12095 | 0.0073652 | 0.0024967
2012-10-18 | 813:89062 | SHORT RURAL | Planned Outage | 891543 | 1 | 420 | 420 | 0.00025576 | 6.0895e-05
2012-10-19 | 515:35193 | SHORT RURAL | Planned Outage | 891544 | 3 | 160 | 480 | 0.0002923 | 0.00018268
2012-10-19 | 513:48059 | SHORT RURAL | Planned Outage | 891546 | 8 | 190 | 1520 | 0.0009256 | 0.00048716
2012-10-20 | 810:74054 | LONG RURAL | Planned Outage | 891547 | 1 | 195 | 195 | 0.00011874 | 6.0895e-05
2012-10-21 | 515:35197 | LONG RURAL | Planned Outage | 891549 | 5 | 195 | 975 | 0.00059372 | 0.00030447
2012-10-23 | ZN12600:PA11 | URBAN | Planned Outage | 891811 | 19 | 120 | 2280 | 0.0013879 | 0.0011566
2012-10-23 | ZN12640:PA1 | SHORT RURAL | Planned Outage | 891813 | 130 | 480 | 62400 | 0.037984 | 0.0079134
2012-10-23 | ZN14892:PA3 | SHORT RURAL | Planned Outage | 891820 | 75 | 480 | 36000 | 0.021914 | 0.0045654
2012-10-23 | ZN12640:PA8 | SHORT RURAL | Planned Outage | 891822 | 108 | 330 | 35640 | 0.021695 | 0.0065742
2012-10-22 | 232:33413 | SHORT RURAL | Planned Outage | 891824 | 57 | 120 | 6840 | 0.0041652 | 0.003471
2012-10-22 | 231:8405 | SHORT RURAL | Planned Outage | 891826 | 1 | 275 | 275 | 0.00016746 | 6.0895e-05
2012-10-22 | 227:13015 | SHORT RURAL | Planned Outage | 891833 | 6 | 215 | 1290 | 0.00078554 | 0.00036537
2012-10-22 | 227:13020 | SHORT RURAL | Planned Outage | 891840 | 58 | 205 | 11890 | 0.0072404 | 0.0035319
2012-10-22 | 264:81240 | SHORT RURAL | Planned Outage | 891842 | 4 | 300 | 1200 | 0.00073074 | 0.00024358
2012-10-22 | 509:48039 | LONG RURAL | Planned Outage | 891843 | 3 | 10 | 30 | 1.8268e-05 | 0.00018268
2012-10-22 | 523:33501 | SHORT RURAL | Planned Outage | 891845 | 1 | 480 | 480 | 0.0002923 | 6.0895e-05
2012-10-22 | 810:74054 | LONG RURAL | Planned Outage | 891846 | 1 | 45 | 45 | 2.7403e-05 | 6.0895e-05
2012-10-22 | 810:74054 | LONG RURAL | Planned Outage | 891848 | 1 | 105 | 105 | 6.394e-05 | 6.0895e-05
2012-10-23 | 206:34440 | URBAN | Planned Outage | 891853 | 89 | 350 | 31150 | 0.018962 | 0.0054176
2012-10-23 | 213:33771 | URBAN | Planned Outage | 891856 | 211 | 250 | 52750 | 0.03211 | 0.012844
2012-10-23 | 227:13015 | SHORT RURAL | Planned Outage | 891861 | 18 | 455 | 8190 | 0.0049854 | 0.0010957
2012-10-23 | 243:80083 | SHORT RURAL | Planned Outage | 891863 | 20 | 220 | 4400 | 0.0026784 | 0.0012174
2012-10-23 | 503:48017 | URBAN | Planned Outage | 891867 | 92 | 300 | 27600 | 0.016801 | 0.0056003
2012-10-23 | 264:81240 | SHORT RURAL | Planned Outage | 891868 | 10 | 590 | 5900 | 0.0035915 | 0.00060872
2012-10-23 | 510:48164 | SHORT RURAL | Planned Outage | 891872 | 23 | 435 | 10005 | 0.0060903 | 0.0014001
2012-10-23 | 507:80923 | SHORT RURAL | Planned Outage | 891878 | 6 | 340 | 2040 | 0.0012418 | 0.00036523
2012-10-23 | 502:48010 | SHORT RURAL | Planned Outage | 891879 | 36 | 240 | 8640 | 0.0052594 | 0.0021914
2012-10-23 | 503:48017 | URBAN | Planned Outage | 891881 | 3 | 240 | 720 | 0.00043828 | 0.00018262
2012-10-23 | 238:34141 | SHORT RURAL | Planned Outage | 891888 | 9 | 425 | 3825 | 0.0023284 | 0.00054785
2012-10-23 | 264:81240 | SHORT RURAL | Planned Outage | 891892 | 1 | 40 | 40 | 2.4349e-05 | 6.0872e-05
2012-10-23 | 515:35197 | LONG RURAL | Planned Outage | 891920 | 1 | 5 | 5 | 3.0436e-06 | 6.0872e-05
2012-10-23 | 515:35192 | SHORT RURAL | Planned Outage | 891921 | 48 | 325 | 15600 | 0.0094961 | 0.0029219
2012-10-23 | 520:48172 | SHORT RURAL | Planned Outage | 891924 | 1 | 90 | 90 | 5.4785e-05 | 6.0872e-05
2012-10-23 | 810:74054 | LONG RURAL | Planned Outage | 891948 | 1 | 55 | 55 | 3.348e-05 | 6.0872e-05
2012-10-23 | 810:74054 | LONG RURAL | Planned Outage | 891951 | 1 | 35 | 35 | 2.1305e-05 | 6.0872e-05
2012-10-23 | 810:74054 | LONG RURAL | Planned Outage | 891952 | 1 | 40 | 40 | 2.4349e-05 | 6.0872e-05
2012-10-24 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 892345 | 21 | 510 | 10710 | 0.0065194 | 0.0012783
2012-10-24 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 892373 | 29 | 480 | 4260 | 0.0025932 | 0.0017653
2012-10-24 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 892410 | 419 | 480 | 201120 | 0.12243 | 0.025506
2012-10-24 | 256:80632 | URBAN | Planned Outage | 892495 | 176 | 210 | 36960 | 0.022498 | 0.010714
2012-10-24 | 217:33612 | URBAN | Planned Outage | 892496 | 94 | 95 | 8930 | 0.0054359 | 0.005722
2012-10-24 | 227:13015 | SHORT RURAL | Planned Outage | 892502 | 39 | 377 | 14703 | 0.0089501 | 0.002374
2012-10-24 | 224:80340 | SHORT RURAL | Planned Outage | 892505 | 1 | 345 | 345 | 0.00021001 | 6.0872e-05
2012-10-24 | 509:48039 | LONG RURAL | Planned Outage | 892506 | 1 | 75 | 75 | 4.5654e-05 | 6.0872e-05
2012-10-24 | 509:48039 | LONG RURAL | Planned Outage | 892507 | 1 | 15 | 15 | 9.1309e-06 | 6.0872e-05
2012-10-24 | 511:29878 | SHORT RURAL | Planned Outage | 892511 | 8 | 415 | 3320 | 0.002021 | 0.00048698
2012-10-24 | 523:33508 | SHORT RURAL | Planned Outage | 892515 | 1 | 120 | 120 | 7.3047e-05 | 6.0872e-05
2012-10-24 | 515:35197 | LONG RURAL | Planned Outage | 892517 | 2 | 160 | 320 | 0.00019479 | 0.00012174
2012-10-24 | 515:35192 | SHORT RURAL | Planned Outage | 892518 | 7 | 300 | 2100 | 0.0012783 | 0.00042611
2012-10-24 | 515:35197 | LONG RURAL | Planned Outage | 892519 | 1 | 5 | 5 | 3.0436e-06 | 6.0872e-05
2012-10-17 | 807:74184 | SHORT RURAL | Planned Outage | 892541 | 3 | 1800 | 5400 | 0.0032883 | 0.00018268
2012-10-26 | 812:19066 | SHORT RURAL | Planned Outage | 892766 | 1 | 40.0833 | 40.0833 | 2.44e-05 | 6.0873e-05
2012-10-25 | 213:33777 | SHORT RURAL | Planned Outage | 892813 | 4 | 290 | 1160 | 0.00070612 | 0.00024349
2012-10-25 | 224:80340 | SHORT RURAL | Planned Outage | 892818 | 257 | 195 | 50115 | 0.030506 | 0.015644
2012-10-25 | 232:11459 | SHORT RURAL | Planned Outage | 892823 | 150 | 285 | 42750 | 0.026023 | 0.0091309
2012-10-25 | 507:80922 | SHORT RURAL | Planned Outage | 892839 | 48 | 450 | 21600 | 0.013148 | 0.0029219
2012-10-25 | 238:34144 | URBAN | Planned Outage | 892843 | 69 | 100 | 6900 | 0.0042002 | 0.0042002
2012-10-25 | 515:35197 | LONG RURAL | Planned Outage | 892847 | 1 | 1520 | 1520 | 0.00092526 | 6.0873e-05
2012-10-25 | 813:89055 | SHORT RURAL | Planned Outage | 892850 | 2 | 103 | 206 | 0.0001254 | 0.00012175
2012-10-25 | 813:89055 | SHORT RURAL | Planned Outage | 892853 | 1 | 40 | 40 | 2.4349e-05 | 6.0873e-05
2012-10-25 | ZN12610:PA22 | URBAN | Planned Outage | 893462 | 125 | 480 | 60000 | 0.036524 | 0.0076091
2012-10-25 | ZN14144:PA2 | SHORT RURAL | Planned Outage | 893467 | 19 | 480 | 9120 | 0.0055516 | 0.0011566
2012-10-25 | ZN14892:PA19 | URBAN | Planned Outage | 893497 | 93 | 480 | 44640 | 0.027173 | 0.0056611
2012-10-25 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 893504 | 209 | 5891.35 | 700979.85 | 0.4267 | 0.012722
2012-10-26 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 893520 | 6 | 60 | 360 | 0.00021914 | 0.00036524
2012-10-27 | ZN15011:PA8 | URBAN | Planned Outage | 893522 | 1 | 600 | 600 | 0.00036524 | 6.0873e-05
2012-10-27 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 893531 | 11 | 360 | 3960 | 0.0024106 | 0.0006696
2012-10-27 | ZN187:PA20 | URBAN | Planned Outage | 893541 | 62 | 420 | 26040 | 0.015851 | 0.0037741
2012-10-27 | ZN15014:PA7 | URBAN | Planned Outage | 893552 | 137 | 360 | 49320 | 0.030022 | 0.0083395
2012-10-28 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 893558 | 63 | 510 | 32130 | 0.019558 | 0.003835
2012-10-28 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 893571 | 2 | 540 | 1080 | 0.00065742 | 0.00012175
2012-10-28 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 893571 | 17 | 540 | 9180 | 0.0055881 | 0.0010348
2012-10-30 | ZN14891:PA10 | SHORT RURAL | Planned Outage | 893965 | 23 | 450 | 10350 | 0.0062989 | 0.0013998
2012-10-29 | ZN9245:PA8 | SHORT RURAL | Planned Outage | 894060 | 7 | 480 | 3360 | 0.0020453 | 0.00042611
2012-10-29 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 894064 | 13 | 480 | 6240 | 0.0037984 | 0.00079134
2012-10-29 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 894082 | 2 | 480 | 960 | 0.00058438 | 0.00012175
2012-10-29 | ZN1285:PA24 | URBAN | Planned Outage | 894086 | 98 | 480 | 47040 | 0.028634 | 0.0059655
2012-10-29 | ZN4545:PA4 | URBAN | Planned Outage | 894092 | 1 | 60 | 60 | 3.6524e-05 | 6.0873e-05
2012-10-30 | ZN711:PA28 | URBAN | Planned Outage | 894124 | 172 | 30 | 5160 | 0.0031403 | 0.010468
2012-10-28 | 213:33775 | URBAN | Planned Outage | 894158 | 1 | 405 | 405 | 0.00024653 | 6.0873e-05
2012-10-26 | 231:8415 | SHORT RURAL | Planned Outage | 894160 | 30 | 430 | 12900 | 0.0078526 | 0.0018262
2012-10-26 | 217:33612 | URBAN | Planned Outage | 894162 | 62 | 415 | 25730 | 0.015663 | 0.0037741
2012-10-27 | 203:8083 | SHORT RURAL | Planned Outage | 894163 | 1 | 490 | 490 | 0.00029828 | 6.0873e-05
2012-10-28 | 218:7481 | URBAN | Planned Outage | 894167 | 48 | 70 | 3360 | 0.0020453 | 0.0029219
2012-10-28 | 203:8088 | URBAN | Planned Outage | 894168 | 3 | 90 | 270 | 0.00016436 | 0.00018262
2012-10-28 | 229:34995 | SHORT RURAL | Planned Outage | 894172 | 9 | 375 | 3375 | 0.0020544 | 0.00054785
2012-10-26 | 235:2120 | SHORT RURAL | Planned Outage | 894175 | 9 | 555 | 4995 | 0.0030406 | 0.00054785
2012-10-26 | 507:80922 | SHORT RURAL | Planned Outage | 894177 | 22 | 255 | 5610 | 0.003415 | 0.0013392
2012-10-26 | 504:48031 | SHORT RURAL | Planned Outage | 894191 | 6 | 270 | 1620 | 0.00098614 | 0.00036524
2012-10-26 | 504:48031 | SHORT RURAL | Planned Outage | 894197 | 31 | 255 | 7905 | 0.004812 | 0.001887
2012-10-26 | 511:29878 | SHORT RURAL | Planned Outage | 894202 | 1 | 230 | 230 | 0.00014001 | 6.0873e-05
2012-10-27 | 526:34641 | SHORT RURAL | Planned Outage | 894204 | 5 | 404 | 2020 | 0.0012296 | 0.00030436
2012-10-28 | 504:48034 | URBAN | Planned Outage | 894208 | 89 | 435 | 38715 | 0.023567 | 0.0054177
2012-10-27 | 806:74076 | SHORT RURAL | Planned Outage | 894214 | 12 | 280 | 3360 | 0.0020453 | 0.00073047
2012-10-28 | 523:33508 | SHORT RURAL | Planned Outage | 894218 | 45 | 360 | 16200 | 0.0098614 | 0.0027393
2012-10-29 | 224:80337 | URBAN | Planned Outage | 894223 | 50 | 395 | 19750 | 0.012022 | 0.0030436
2012-10-29 | 235:2123 | URBAN | Planned Outage | 894224 | 55 | 25 | 1375 | 0.000837 | 0.003348
2012-10-30 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 894421 | 8 | 510 | 4080 | 0.002483 | 0.00048687
2012-10-30 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 894440 | 1 | 510 | 510 | 0.00031038 | 6.0859e-05
2012-10-30 | 813:89062 | SHORT RURAL | Planned Outage | 894444 | 11 | 265 | 2915 | 0.001774 | 0.00066945
2012-10-30 | 206:34434 | URBAN | Planned Outage | 894447 | 334 | 355 | 118570 | 0.07216 | 0.020327
2012-10-30 | 227:13015 | SHORT RURAL | Planned Outage | 894456 | 18 | 350 | 6300 | 0.0038341 | 0.0010955
2012-10-30 | 260:33350 | SHORT RURAL | Planned Outage | 894458 | 1 | 120 | 120 | 7.3031e-05 | 6.0859e-05
2012-10-30 | 504:48031 | SHORT RURAL | Planned Outage | 894460 | 29 | 225 | 6525 | 0.003971 | 0.0017649
2012-10-30 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 894463 | 33 | 480 | 15840 | 0.00964 | 0.0020083
2012-10-30 | ZN35370:PA2 | SHORT RURAL | Planned Outage | 894472 | 15 | 420 | 6300 | 0.0038341 | 0.00091288
2012-10-30 | 524:33572 | SHORT RURAL | Planned Outage | 894473 | 363 | 345 | 125235 | 0.076217 | 0.022092
2012-10-30 | ZN12660:PA16 | URBAN | Planned Outage | 894475 | 39 | 480 | 18720 | 0.011393 | 0.0023735
2012-10-30 | 512:48049 | SHORT RURAL | Planned Outage | 894476 | 7 | 360 | 2520 | 0.0015336 | 0.00042601
2012-10-30 | ZN1290:PA17 | URBAN | Planned Outage | 894505 | 1 | 600 | 600 | 0.00036515 | 6.0859e-05
2012-10-30 | ZN630:PA26 | URBAN | Planned Outage | 894507 | 50 | 360 | 18000 | 0.010955 | 0.0030429
2012-10-30 | ZN14892:PA21 | URBAN | Planned Outage | 894508 | 61 | 360 | 21960 | 0.013365 | 0.0037124
2012-10-31 | ZN12610:PA10 | SHORT RURAL | Planned Outage | 894509 | 24 | 120 | 2880 | 0.0017527 | 0.0014606
2012-10-30 | 810:74054 | LONG RURAL | Planned Outage | 894572 | 1 | 480 | 480 | 0.00029212 | 6.0859e-05
2012-10-30 | 812:19066 | SHORT RURAL | Planned Outage | 894594 | 41 | 70 | 2870 | 0.0017466 | 0.0024952
2012-10-30 | 813:89062 | SHORT RURAL | Planned Outage | 894626 | 1 | 426 | 426 | 0.00025926 | 6.0859e-05
2012-10-31 | 225:33670 | SHORT RURAL | Planned Outage | 894824 | 3 | 205 | 615 | 0.00037428 | 0.00018258
2012-10-31 | 216:10728 | URBAN | Planned Outage | 894833 | 1 | 345 | 345 | 0.00020996 | 6.0859e-05
2012-10-31 | 511:29878 | SHORT RURAL | Planned Outage | 894837 | 5 | 480 | 2400 | 0.0014606 | 0.00030429
2012-10-31 | 510:48164 | SHORT RURAL | Planned Outage | 894843 | 8 | 280 | 2240 | 0.0013632 | 0.00048687
2012-10-31 | 235:2123 | URBAN | Planned Outage | 894844 | 81 | 190 | 15390 | 0.0093662 | 0.0049296
2012-10-31 | 807:74184 | SHORT RURAL | Planned Outage | 894845 | 16 | 245 | 3920 | 0.0023857 | 0.00097374
2012-10-31 | 513:48056 | SHORT RURAL | Planned Outage | 894848 | 5 | 170 | 850 | 0.0005173 | 0.00030429
2012-10-31 | 810:74058 | SHORT RURAL | Planned Outage | 894850 | 1 | 275 | 275 | 0.00016736 | 6.0859e-05
2012-11-01 | 232:11454 | SHORT RURAL | Planned Outage | 896383 | 5 | 270 | 1350 | 0.0008216 | 0.0003043
2012-11-01 | 264:81244 | URBAN | Planned Outage | 896386 | 51 | 335 | 17085 | 0.010398 | 0.0031038
2012-11-01 | 243:80083 | SHORT RURAL | Planned Outage | 896391 | 1 | 10 | 10 | 6.0859e-06 | 6.0859e-05
2012-10-31 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 896581 | 18 | 480 | 540 | 0.00032864 | 0.0010955
2012-10-31 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 896581 | 7 | 480 | 3360 | 0.0020449 | 0.00042601
2012-11-01 | 206:34440 | URBAN | Planned Outage | 896590 | 87 | 35 | 3045 | 0.0018532 | 0.0052948
2012-11-03 | 232:11460 | URBAN | Planned Outage | 896594 | 15 | 185 | 2775 | 0.0016888 | 0.00091289
2012-11-04 | 214:8671 | URBAN | Planned Outage | 896596 | 1 | 225 | 225 | 0.00013693 | 6.0859e-05
2012-11-01 | 501:48115 | SHORT RURAL | Planned Outage | 896598 | 23 | 400 | 9200 | 0.005599 | 0.0013998
2012-11-01 | 501:48123 | SHORT RURAL | Planned Outage | 896601 | 3 | 390 | 1170 | 0.00071205 | 0.00018258
2012-11-01 | 503:48011 | SHORT RURAL | Planned Outage | 896623 | 2 | 405 | 810 | 0.00049296 | 0.00012172
2012-11-01 | 524:33572 | SHORT RURAL | Planned Outage | 896625 | 11 | 260 | 2860 | 0.0017406 | 0.00066945
2012-11-02 | 504:48031 | SHORT RURAL | Planned Outage | 896629 | 1 | 105 | 105 | 6.3902e-05 | 6.0859e-05
2012-11-02 | 510:48164 | SHORT RURAL | Planned Outage | 896632 | 18 | 415 | 7470 | 0.0045462 | 0.0010955
2012-11-03 | 501:48118 | SHORT RURAL | Planned Outage | 896636 | 2 | 285 | 570 | 0.0003469 | 0.00012172
2012-11-01 | 810:74054 | LONG RURAL | Planned Outage | 896639 | 3 | 180 | 540 | 0.00032864 | 0.00018258
2012-10-31 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 896653 | 420 | 480 | 201600 | 0.12269 | 0.025561
2012-10-31 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 896661 | 40 | 300 | 12000 | 0.0073031 | 0.0024344
2012-10-31 | ZN711:PA23 | URBAN | Planned Outage | 896662 | 7 | 660 | 4620 | 0.0028117 | 0.00042601
2012-11-05 | 232:11459 | SHORT RURAL | Planned Outage | 896664 | 49 | 250 | 12250 | 0.0074553 | 0.0029821
2012-11-05 | 810:74062 | SHORT RURAL | Planned Outage | 896669 | 12 | 320 | 3840 | 0.002337 | 0.00073031
2012-11-01 | ZN263:PA35 37GHJ | CBD | Planned Outage | 896674 | 3 | 180 | 540 | 0.00032864 | 0.00018258
2012-11-05 | 227:13015 | SHORT RURAL | Planned Outage | 896675 | 18 | 465 | 8370 | 0.0050939 | 0.0010955
2012-11-05 | 232:11453 | SHORT RURAL | Planned Outage | 896677 | 38 | 285 | 10830 | 0.0065911 | 0.0023127
2012-11-05 | 230:81440 | URBAN | Planned Outage | 896679 | 222 | 85 | 18870 | 0.011484 | 0.013511
2012-11-01 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 896680 | 21 | 510 | 10710 | 0.006518 | 0.001278
2012-11-01 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 896687 | 5 | 570 | 2400 | 0.0014606 | 0.0003043
2012-11-01 | ZN9550:PA43 | URBAN | Planned Outage | 896687 | 162 | 570 | 92340 | 0.056197 | 0.0098592
2012-11-01 | ZN14892:PA3 | SHORT RURAL | Planned Outage | 896720 | 53 | 480 | 25440 | 0.015483 | 0.0032255
2012-11-05 | 503:48077 | URBAN | Planned Outage | 896721 | 112 | 490 | 54880 | 0.0334 | 0.0068162
2012-11-05 | 235:2120 | SHORT RURAL | Planned Outage | 896722 | 15 | 240 | 3600 | 0.0021909 | 0.00091289
2012-11-01 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 896723 | 14 | 480 | 6720 | 0.0040897 | 0.00085203
2012-11-01 | ZN2635:PA20 | URBAN | Planned Outage | 896726 | 93 | 420 | 39060 | 0.023772 | 0.0056599
2012-11-01 | ZN2635:PA18 | URBAN | Planned Outage | 896729 | 29 | 420 | 12180 | 0.0074127 | 0.0017649
2012-11-01 | ZN2635:PA20 | URBAN | Planned Outage | 896729 | 41 | 420 | 17220 | 0.01048 | 0.0024952
2012-11-01 | ZN12570:PA35 | URBAN | Planned Outage | 896737 | 31 | 360 | 11160 | 0.0067919 | 0.0018866
2012-11-01 | ZN7900:PA17 | URBAN | Planned Outage | 896741 | 127 | 15 | 1905 | 0.0011594 | 0.0077291
2012-11-01 | ZN1068:PA27 | URBAN | Planned Outage | 896762 | 63 | 360 | 22680 | 0.013803 | 0.0038341
2012-11-01 | ZN12620:PA10 | SHORT RURAL | Planned Outage | 896764 | 56 | 360 | 20160 | 0.012269 | 0.0034081
2012-11-02 | ZN12610:PA22 | URBAN | Planned Outage | 896777 | 125 | 480 | 60000 | 0.036516 | 0.0076074
2012-11-03 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 896785 | 6 | 390 | 360 | 0.00021909 | 0.00036516
2012-11-03 | ZN12570:PA11 | URBAN | Planned Outage | 896788 | 84 | 420 | 35280 | 0.021471 | 0.0051122
2012-11-03 | ZN384:PA23 | URBAN | Planned Outage | 896801 | 322 | 30 | 9660 | 0.005879 | 0.019597
2012-11-04 | ZN1285:PA27 | URBAN | Planned Outage | 896803 | 1 | 360 | 360 | 0.00021909 | 6.0859e-05
2012-11-04 | ZN15009:PA5 | URBAN | Planned Outage | 896805 | 59 | 450 | 26550 | 0.016158 | 0.0035907
2012-11-04 | ZN35800:PA6 | URBAN | Planned Outage | 896807 | 17 | 390 | 6630 | 0.004035 | 0.0010346
2012-11-05 | ZN15013:PA6 | SHORT RURAL | Planned Outage | 896813 | 1 | 540 | 540 | 0.00032864 | 6.0859e-05
2012-11-05 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 896819 | 40 | 480 | 1200 | 0.00073031 | 0.0024344
2012-11-05 | ZN2473:PA31 | URBAN | Planned Outage | 896824 | 98 | 420 | 41160 | 0.02505 | 0.0059642
2012-11-05 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 896848 | 5 | 480 | 2400 | 0.0014606 | 0.0003043
2012-11-05 | ZN14891:PA16 | SHORT RURAL | Planned Outage | 896852 | 4 | 480 | 1920 | 0.0011685 | 0.00024344
2012-11-05 | ZN12570:PA11 | URBAN | Planned Outage | 896855 | 57 | 450 | 25650 | 0.01561 | 0.003469
2012-11-05 | ZN12570:PA37 | SHORT RURAL | Planned Outage | 896856 | 7 | 360 | 2520 | 0.0015337 | 0.00042602
2012-11-06 | 526:34641 | SHORT RURAL | Planned Outage | 897094 | 6 | 423 | 2538 | 0.0015443 | 0.00036509
2012-11-06 | 501:48123 | SHORT RURAL | Planned Outage | 897097 | 28 | 180 | 5040 | 0.0030668 | 0.0017038
2012-11-06 | 232:33413 | SHORT RURAL | Planned Outage | 897102 | 19 | 73 | 1387 | 0.00084397 | 0.0011561
2012-11-06 | 503:48011 | SHORT RURAL | Planned Outage | 897107 | 15 | 405 | 6075 | 0.0036965 | 0.00091273
2012-11-06 | 523:33501 | SHORT RURAL | Planned Outage | 897116 | 4 | 70 | 280 | 0.00017038 | 0.00024339
2012-11-06 | 801:74123 | SHORT RURAL | Planned Outage | 897120 | 11 | 160 | 1760 | 0.0010709 | 0.00066933
2012-11-06 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 897228 | 1 | 660 | 660 | 0.0004016 | 6.0848e-05
2012-11-06 | ZN15013:PA6 | SHORT RURAL | Planned Outage | 897230 | 1 | 540 | 540 | 0.00032858 | 6.0848e-05
2012-11-06 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 897242 | 21 | 480 | 10080 | 0.0061335 | 0.0012778
2012-11-06 | ZN14892:PA8 | URBAN | Planned Outage | 897260 | 1 | 300 | 300 | 0.00018255 | 6.0848e-05
2012-11-07 | ZN15013:PA6 | SHORT RURAL | Planned Outage | 897659 | 1 | 540 | 540 | 0.00032858 | 6.0848e-05
2012-11-07 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 897713 | 405 | 480 | 31440 | 0.019131 | 0.024644
2012-11-07 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 897747 | 51 | 480 | 24480 | 0.014896 | 0.0031033
2012-11-07 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 897773 | 21 | 480 | 10080 | 0.0061335 | 0.0012778
2012-11-07 | ZN12600:PA11 | URBAN | Planned Outage | 897776 | 54 | 420 | 22680 | 0.0138 | 0.0032858
2012-11-07 | ZN3288:PA43 44GHJ | CBD | Planned Outage | 897779 | 18 | 300 | 5400 | 0.0032858 | 0.0010953
2012-11-07 | 806:74076 | SHORT RURAL | Planned Outage | 897873 | 12 | 315 | 3780 | 0.0023001 | 0.00073018
2012-11-07 | 229:34983 | SHORT RURAL | Planned Outage | 897877 | 1 | 235 | 235 | 0.00014299 | 6.0848e-05
2012-11-07 | 227:13015 | SHORT RURAL | Planned Outage | 897879 | 42 | 465 | 19530 | 0.011884 | 0.0025556
2012-11-07 | 509:48040 | SHORT RURAL | Planned Outage | 897887 | 9 | 330 | 2970 | 0.0018072 | 0.00054764
2012-11-07 | 235:2857 | SHORT RURAL | Planned Outage | 897888 | 1 | 140 | 140 | 8.5188e-05 | 6.0848e-05
2012-11-07 | 515:35197 | LONG RURAL | Planned Outage | 897910 | 5 | 215 | 1075 | 0.00065412 | 0.00030424
2012-11-08 | ZN15013:PA6 | SHORT RURAL | Planned Outage | 898250 | 1 | 540 | 540 | 0.00032858 | 6.0849e-05
2012-11-08 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 898253 | 11 | 510 | 5610 | 0.0034136 | 0.00066933
2012-11-08 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 898259 | 3 | 450 | 1350 | 0.00082146 | 0.00018255
2012-11-08 | ZN14144:PA4 | URBAN | Planned Outage | 898260 | 59 | 450 | 26550 | 0.016155 | 0.0035901
2012-11-08 | ZN3472:PA15 | URBAN | Planned Outage | 898264 | 45 | 120 | 5400 | 0.0032858 | 0.0027382
2012-11-08 | 264:81240 | SHORT RURAL | Planned Outage | 898533 | 13 | 105 | 1365 | 0.00083058 | 0.00079103
2012-11-08 | 243:80080 | SHORT RURAL | Planned Outage | 898540 | 32 | 345 | 11040 | 0.0067177 | 0.0019472
2012-11-08 | 232:33413 | SHORT RURAL | Planned Outage | 898555 | 30 | 295 | 8850 | 0.0053851 | 0.0018255
2012-11-08 | 509:48040 | SHORT RURAL | Planned Outage | 898562 | 51 | 282 | 14382 | 0.0087512 | 0.0031033
2012-11-08 | 526:34641 | SHORT RURAL | Planned Outage | 898565 | 4 | 320 | 1280 | 0.00077886 | 0.00024339
2012-11-08 | 504:48031 | SHORT RURAL | Planned Outage | 898569 | 2 | 50 | 100 | 6.0849e-05 | 0.0001217
2012-11-08 | 509:48039 | LONG RURAL | Planned Outage | 898572 | 1 | 40 | 40 | 2.4339e-05 | 6.0849e-05
2012-11-08 | 264:81240 | SHORT RURAL | Planned Outage | 898573 | 41 | 470 | 19270 | 0.011726 | 0.0024948
2012-11-08 | 516:48067 | SHORT RURAL | Planned Outage | 898575 | 1 | 75 | 75 | 4.5636e-05 | 6.0849e-05
2012-11-08 | 515:35192 | SHORT RURAL | Planned Outage | 898577 | 3 | 380 | 1140 | 0.00069367 | 0.00018255
2012-11-08 | 811:74234 | SHORT RURAL | Planned Outage | 898578 | 69 | 375 | 25875 | 0.015745 | 0.0041986
2012-11-09 | ZN12570:PA37 | SHORT RURAL | Planned Outage | 899128 | 38 | 480 | 18240 | 0.011099 | 0.0023122
2012-11-09 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 899134 | 5 | 480 | 2400 | 0.0014604 | 0.00030424
2012-11-09 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 899136 | 21 | 480 | 10080 | 0.0061335 | 0.0012778
2012-11-09 | ZN965:PA28 | SHORT RURAL | Planned Outage | 899138 | 22 | 180 | 3960 | 0.0024096 | 0.0013387
2012-11-09 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 899161 | 77 | 300 | 23100 | 0.014056 | 0.0046853
2012-11-09 | ZN1290:PA12 | URBAN | Planned Outage | 899166 | 5 | 240 | 1200 | 0.00073018 | 0.00030424
2012-11-10 | ZN384:PA2 | URBAN | Planned Outage | 899179 | 1 | 390 | 390 | 0.00023731 | 6.0849e-05
2012-11-10 | ZN2473:PA32 | URBAN | Planned Outage | 899186 | 60 | 450 | 27000 | 0.016429 | 0.0036509
2012-11-10 | ZN2473:PA11 | URBAN | Planned Outage | 899285 | 24 | 780 | 18720 | 0.011391 | 0.0014604
2012-11-11 | ZN1164:PA3 | URBAN | Planned Outage | 899290 | 131 | 480 | 62880 | 0.038262 | 0.0079712
2012-11-11 | ZN14144:PA5 | SHORT RURAL | Planned Outage | 899295 | 32 | 540 | 17280 | 0.010515 | 0.0019472
2012-11-09 | 511:29878 | SHORT RURAL | Planned Outage | 899764 | 36 | 375 | 13500 | 0.0082146 | 0.0021906
2012-11-09 | 501:48115 | SHORT RURAL | Planned Outage | 899768 | 102 | 150 | 15300 | 0.0093098 | 0.0062066
2012-11-11 | 227:13018 | URBAN | Planned Outage | 899846 | 99 | 660 | 65340 | 0.039759 | 0.006024
2012-11-09 | 234:33444 | SHORT RURAL | Planned Outage | 899849 | 3 | 430 | 1290 | 0.00078495 | 0.00018255
2012-11-09 | 216:10723 | URBAN | Planned Outage | 899850 | 1 | 360 | 360 | 0.00021906 | 6.0849e-05
2012-11-09 | 234:14291 | URBAN | Planned Outage | 899851 | 141 | 30 | 4230 | 0.0025739 | 0.0085797
2012-11-09 | 227:13015 | SHORT RURAL | Planned Outage | 899853 | 18 | 320 | 5760 | 0.0035049 | 0.0010953
2012-11-09 | 227:13015 | SHORT RURAL | Planned Outage | 899854 | 50 | 380 | 19000 | 0.011561 | 0.0030424
2012-11-11 | 217:33612 | URBAN | Planned Outage | 899857 | 1 | 395 | 395 | 0.00024035 | 6.0849e-05
2012-11-11 | 202:34231 37 42 | URBAN | Planned Outage | 899870 | 20 | 703 | 14060 | 0.0085553 | 0.001217
2012-11-09 | 504:48026 | SHORT RURAL | Planned Outage | 899872 | 37 | 130 | 4810 | 0.0029268 | 0.0022514
2012-11-09 | 510:48164 | SHORT RURAL | Planned Outage | 899874 | 16 | 440 | 7040 | 0.0042837 | 0.00097358
2012-11-10 | 526:34641 | SHORT RURAL | Planned Outage | 899875 | 4 | 420 | 1680 | 0.0010223 | 0.00024339
2012-11-10 | 509:48039 | LONG RURAL | Planned Outage | 899877 | 32 | 435 | 13920 | 0.0084701 | 0.0019472
2012-11-09 | 514:18137 | SHORT RURAL | Planned Outage | 899884 | 33 | 335 | 11055 | 0.0067268 | 0.002008
2012-11-09 | 520:48172 | SHORT RURAL | Planned Outage | 899885 | 1 | 110 | 110 | 6.6934e-05 | 6.0849e-05
2012-11-10 | 813:89062 | SHORT RURAL | Planned Outage | 899886 | 56 | 130 | 7280 | 0.0044298 | 0.0034075
2012-11-11 | 515:35197 | LONG RURAL | Planned Outage | 899888 | 3 | 255 | 765 | 0.00046549 | 0.00018255
2012-11-12 | 227:13015 | SHORT RURAL | Planned Outage | 899897 | 9 | 405 | 3645 | 0.0022179 | 0.00054764
2012-11-12 | 235:2121 | URBAN | Planned Outage | 899898 | 13 | 570 | 7410 | 0.0045089 | 0.00079103
2012-11-12 | 228:7490 | SHORT RURAL | Planned Outage | 899906 | 1 | 285 | 285 | 0.00017342 | 6.0849e-05
2012-11-12 | 509:48040 | SHORT RURAL | Planned Outage | 899912 | 9 | 295 | 2655 | 0.0016155 | 0.00054764
2012-11-12 | 510:48164 | SHORT RURAL | Planned Outage | 899914 | 12 | 5 | 60 | 3.6509e-05 | 0.00073018
2012-11-13 | 264:81240 | SHORT RURAL | Planned Outage | 900115 | 4 | 390 | 1560 | 0.00094912 | 0.00024336
2012-11-13 | 801:74121 | SHORT RURAL | Planned Outage | 900121 | 22 | 255 | 5610 | 0.0034132 | 0.0013385
2012-11-13 | 243:80083 | SHORT RURAL | Planned Outage | 900128 | 20 | 315 | 6300 | 0.003833 | 0.0012168
2012-11-12 | ZN116:PA48 | URBAN | Planned Outage | 900131 | 75 | 420 | 31500 | 0.019167 | 0.0045637
2012-11-12 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 900134 | 1 | 480 | 480 | 0.00029207 | 6.0849e-05
2012-11-12 | ZN3155:PA44 | URBAN | Planned Outage | 900138 | 53 | 480 | 25440 | 0.01548 | 0.003225
2012-11-13 | ZN188:PA29 | URBAN | Planned Outage | 900148 | 1 | 299 | 299 | 0.00018192 | 6.0841e-05
2012-11-13 | ZN188:PA41 | URBAN | Planned Outage | 900148 | 1 | 299 | 299 | 0.00018192 | 6.0841e-05
2012-11-13 | 232:11453 | SHORT RURAL | Planned Outage | 900154 | 1 | 200 | 200 | 0.00012168 | 6.0841e-05
2012-11-13 | 264:81240 | SHORT RURAL | Planned Outage | 900158 | 20 | 475 | 9500 | 0.0057799 | 0.0012168
2012-11-13 | 510:48164 | SHORT RURAL | Planned Outage | 900163 | 2 | 345 | 690 | 0.0004198 | 0.00012168
2012-11-13 | 510:48164 | SHORT RURAL | Planned Outage | 900164 | 16 | 20 | 320 | 0.00019469 | 0.00097346
2012-11-13 | ZN12640:PA18 | SHORT RURAL | Planned Outage | 900166 | 208 | 480 | 99840 | 0.060744 | 0.012655
2012-11-13 | ZN12570:PA41 | URBAN | Planned Outage | 900171 | 57 | 450 | 25650 | 0.015606 | 0.003468
2012-11-13 | 504:48034 | URBAN | Planned Outage | 900174 | 189 | 345 | 65205 | 0.039672 | 0.011499
2012-11-13 | ZN14892:PA1 | SHORT RURAL | Planned Outage | 900175 | 1 | 360 | 360 | 0.00021903 | 6.0841e-05
2012-11-14 | ZN188:PA29 | URBAN | Planned Outage | 900176 | 1 | 329 | 329 | 0.00020017 | 6.0841e-05
2012-11-14 | ZN188:PA41 | URBAN | Planned Outage | 900176 | 1 | 329 | 329 | 0.00020017 | 6.0841e-05
2012-11-14 | ZN195:PA3 | URBAN | Planned Outage | 900180 | 73 | 120 | 8760 | 0.0053297 | 0.0044414
2012-11-13 | 510:48164 | SHORT RURAL | Planned Outage | 900183 | 16 | 25 | 400 | 0.00024336 | 0.00097346
2012-11-13 | 812:19066 | SHORT RURAL | Planned Outage | 900186 | 17 | 315 | 5355 | 0.003258 | 0.0010343
2012-11-13 | 801:74119 | URBAN | Planned Outage | 900189 | 44 | 109 | 4796 | 0.0029179 | 0.002677
2012-11-13 | 513:48050 | SHORT RURAL | Planned Outage | 900191 | 2 | 300 | 600 | 0.00036505 | 0.00012168
2012-11-14 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 900473 | 2233 | 8 | 17864 | 0.010869 | 0.13586
2012-11-14 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 900513 | 51 | 540 | 27540 | 0.016756 | 0.0031029
2012-11-14 | 526:34636 | SHORT RURAL | Planned Outage | 900517 | 13 | 385 | 5005 | 0.0030451 | 0.00079093
2012-11-14 | 523:33508 | SHORT RURAL | Planned Outage | 900522 | 29 | 290 | 8410 | 0.0051167 | 0.0017644
2012-11-14 | 501:48122 | SHORT RURAL | Planned Outage | 900533 | 88 | 250 | 22000 | 0.013385 | 0.005354
2012-11-14 | 232:11453 | SHORT RURAL | Planned Outage | 900543 | 58 | 140 | 8120 | 0.0049403 | 0.0035288
2012-11-14 | 243:80080 | SHORT RURAL | Planned Outage | 900548 | 32 | 380 | 12160 | 0.0073983 | 0.0019469
2012-11-14 | 229:34995 | SHORT RURAL | Planned Outage | 900553 | 4 | 325 | 1300 | 0.00079093 | 0.00024336
2012-11-14 | 232:11457 | URBAN | Planned Outage | 900554 | 4 | 470 | 1880 | 0.0011438 | 0.00024336
2012-11-14 | ZN9245:PA13 | URBAN | Planned Outage | 900558 | 3 | 510 | 1530 | 0.00093087 | 0.00018252
2012-11-15 | ZN12590:PA1 | SHORT RURAL | Planned Outage | 900628 | 105 | 3 | 315 | 0.00019165 | 0.0063883
2012-11-15 | ZN12590:PA2 | URBAN | Planned Outage | 900628 | 1508 | 3 | 4524 | 0.0027524 | 0.091748
2012-11-15 | ZN12590:PA3 | SHORT RURAL | Planned Outage | 900628 | 1503 | 3 | 4509 | 0.0027433 | 0.091444
2012-11-15 | ZN12590:PA4 | URBAN | Planned Outage | 900628 | 606 | 3 | 1818 | 0.0011061 | 0.03687
2012-11-15 | ZN12590:PA6 | SHORT RURAL | Planned Outage | 900628 | 1349 | 3 | 4047 | 0.0024622 | 0.082075
2012-11-14 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 900637 | 401 | 510 | 204510 | 0.12443 | 0.024397
2012-11-14 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 900646 | 12 | 120 | 1440 | 0.00087611 | 0.00073009
2012-11-14 | 264:81240 | SHORT RURAL | Planned Outage | 900734 | 109 | 480 | 52320 | 0.031832 | 0.0066317
2012-11-14 | 504:48031 | SHORT RURAL | Planned Outage | 900742 | 15 | 335 | 5025 | 0.0030573 | 0.00091262
2012-11-14 | 510:48164 | SHORT RURAL | Planned Outage | 900745 | 16 | 15 | 240 | 0.00014602 | 0.00097346
2012-11-14 | 510:48164 | SHORT RURAL | Planned Outage | 900750 | 2 | 390 | 780 | 0.00047456 | 0.00012168
2012-11-14 | 510:48164 | SHORT RURAL | Planned Outage | 900751 | 16 | 30 | 480 | 0.00029204 | 0.00097346
2012-11-14 | 810:74054 | LONG RURAL | Planned Outage | 900754 | 1 | 50 | 50 | 3.0421e-05 | 6.0841e-05
2012-11-14 | 810:74054 | LONG RURAL | Planned Outage | 900786 | 1 | 35 | 35 | 2.1294e-05 | 6.0841e-05
2012-11-19 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 901634 | 4 | 450 | 1729.3333 | 0.0010521 | 0.00024336
2012-11-12 | 510:48164 | SHORT RURAL | Planned Outage | 901690 | 12 | 20 | 240 | 0.00014604 | 0.00073018
2012-11-12 | 510:48164 | SHORT RURAL | Planned Outage | 901691 | 6 | 560 | 3360 | 0.0020445 | 0.00036509
2012-11-15 | 509:48040 | SHORT RURAL | Planned Outage | 901697 | 31 | 260 | 8060 | 0.0049038 | 0.0018861
2012-11-15 | 515:35197 | LONG RURAL | Planned Outage | 901702 | 130 | 350 | 45500 | 0.027683 | 0.0079093
2012-11-15 | 501:48122 | SHORT RURAL | Planned Outage | 901707 | 23 | 45 | 1035 | 0.0006297 | 0.0013993
2012-11-17 | 507:80932 | SHORT RURAL | Planned Outage | 901714 | 29 | 375 | 10875 | 0.0066165 | 0.0017644
2012-11-17 | 501:48115 | SHORT RURAL | Planned Outage | 901720 | 79 | 225 | 17775 | 0.010815 | 0.0048064
2012-11-17 | 512:48046 | SHORT RURAL | Planned Outage | 901730 | 56 | 250 | 14000 | 0.0085178 | 0.0034071
2012-11-17 | 813:89062 | SHORT RURAL | Planned Outage | 901738 | 11 | 210 | 2310 | 0.0014054 | 0.00066925
2012-11-15 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 901742 | 26 | 570 | 780 | 0.00047456 | 0.0015819
2012-11-15 | ZN9245:PA8 | SHORT RURAL | Planned Outage | 901748 | 7 | 510 | 3570 | 0.002172 | 0.00042589
2012-11-18 | 515:35200 | URBAN | Planned Outage | 901749 | 14 | 345 | 4830 | 0.0029386 | 0.00085178
2012-11-15 | 222:2017 | URBAN | Planned Outage | 901795 | 25 | 435 | 10875 | 0.0066165 | 0.001521
2012-11-15 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 901797 | 11 | 480 | 5280 | 0.0032124 | 0.00066925
2012-11-15 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 901802 | 10 | 480 | 4800 | 0.0029204 | 0.00060841
2012-11-15 | 243:80075 | SHORT RURAL | Planned Outage | 901806 | 3 | 60 | 180 | 0.00010951 | 0.00018252
2012-11-15 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 901808 | 29 | 480 | 13920 | 0.0084691 | 0.0017644
2012-11-15 | 229:34983 | SHORT RURAL | Planned Outage | 901811 | 141 | 390 | 54990 | 0.033456 | 0.0085786
2012-11-15 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 901814 | 93 | 540 | 50220 | 0.030554 | 0.0056582
2012-11-15 | 229:34995 | SHORT RURAL | Planned Outage | 901815 | 198 | 570 | 112860 | 0.068665 | 0.012047
2012-11-15 | 210:8676 | URBAN | Planned Outage | 901823 | 1 | 460 | 460 | 0.00027987 | 6.0841e-05
2012-11-15 | ZN15014:PA12 | SHORT RURAL | Planned Outage | 901825 | 33 | 390 | 12870 | 0.0078302 | 0.0020078
2012-11-16 | 229:34983 | SHORT RURAL | Planned Outage | 901826 | 19 | 322 | 6118 | 0.0037223 | 0.001156
2012-11-16 | ZN14144:PA4 | URBAN | Planned Outage | 901827 | 238 | 480 | 114240 | 0.069505 | 0.01448
2012-11-16 | 232:11460 | URBAN | Planned Outage | 901831 | 235 | 380 | 89300 | 0.054331 | 0.014298
2012-11-17 | 234:33444 | SHORT RURAL | Planned Outage | 901834 | 1 | 340 | 340 | 0.00020686 | 6.0841e-05
2012-11-16 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 901835 | 11 | 480 | 5280 | 0.0032124 | 0.00066925
2012-11-18 | 224:80337 | URBAN | Planned Outage | 901839 | 63 | 485 | 30555 | 0.01859 | 0.003833
2012-11-16 | ZN1164:PA4 | URBAN | Planned Outage | 901843 | 1 | 15 | 15 | 9.1262e-06 | 6.0841e-05
2012-11-16 | ZN2635:PA9 | URBAN | Planned Outage | 901846 | 13 | 2100 | 27300 | 0.01661 | 0.00079093
2012-11-17 | ZN14144:PA5 | SHORT RURAL | Planned Outage | 901847 | 18 | 570 | 10260 | 0.0062423 | 0.0010951
2012-11-17 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 901849 | 7 | 480 | 3360 | 0.0020443 | 0.00042589
2012-11-18 | 217:33612 | URBAN | Planned Outage | 901853 | 1 | 515 | 515 | 0.00031333 | 6.0841e-05
2012-11-18 | ZN7900:PA7 | URBAN | Planned Outage | 901854 | 23 | 3 | 69 | 4.198e-05 | 0.0013993
2012-11-18 | 224:80337 | URBAN | Planned Outage | 901856 | 178 | 225 | 40050 | 0.024367 | 0.01083
2012-11-18 | ZN3472:PA39 | URBAN | Planned Outage | 901859 | 7 | 240 | 1680 | 0.0010221 | 0.00042589
2012-11-15 | 264:81240 | SHORT RURAL | Planned Outage | 901863 | 41 | 300 | 12300 | 0.0074834 | 0.0024945
2012-11-16 | 503:48011 | SHORT RURAL | Planned Outage | 901865 | 4 | 180 | 720 | 0.00043806 | 0.00024336
2012-11-16 | 510:48164 | SHORT RURAL | Planned Outage | 901867 | 13 | 310 | 4030 | 0.0024519 | 0.00079093
2012-11-16 | 511:29877 | SHORT RURAL | Planned Outage | 901890 | 15 | 40 | 600 | 0.00036505 | 0.00091262
2012-11-16 | 501:48123 | SHORT RURAL | Planned Outage | 901892 | 368 | 503 | 185104 | 0.11262 | 0.02239
2012-11-16 | 235:2120 | SHORT RURAL | Planned Outage | 901896 | 16 | 270 | 4320 | 0.0026283 | 0.00097346
2012-11-15 | 813:89062 | SHORT RURAL | Planned Outage | 901897 | 1 | 380 | 380 | 0.0002312 | 6.0841e-05
2012-11-16 | 813:89062 | SHORT RURAL | Planned Outage | 901900 | 1 | 345 | 345 | 0.0002099 | 6.0841e-05
2012-11-19 | 222:2014 | URBAN | Planned Outage | 902043 | 164 | 595 | 97580 | 0.059369 | 0.0099779
2012-11-19 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 902161 | 1 | 600 | 600 | 0.00036505 | 6.0841e-05
2012-11-19 | ZN847:PA18 | URBAN | Planned Outage | 902162 | 56 | 480 | 26880 | 0.016354 | 0.0034071
2012-11-19 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 902192 | 445 | 480 | 213600 | 0.12996 | 0.027074
2012-11-19 | ZN1285:PA24 | URBAN | Planned Outage | 902273 | 98 | 480 | 47040 | 0.02862 | 0.0059624
2012-11-20 | ZN3155:PA11 | URBAN | Planned Outage | 902277 | 136 | 420 | 57120 | 0.034749 | 0.0082735
2012-11-19 | 229:34995 | SHORT RURAL | Planned Outage | 902307 | 35 | 270 | 9450 | 0.0057495 | 0.0021294
2012-11-19 | 232:11459 | SHORT RURAL | Planned Outage | 902321 | 49 | 370 | 18130 | 0.01103 | 0.0029812
2012-11-19 | 513:48056 | SHORT RURAL | Planned Outage | 902323 | 32 | 345 | 11040 | 0.0067169 | 0.0019469
2012-11-19 | 235:8684 | SHORT RURAL | Planned Outage | 902326 | 1 | 370 | 370 | 0.00022511 | 6.0841e-05
2012-11-19 | 264:81244 | URBAN | Planned Outage | 902328 | 121 | 330 | 39930 | 0.024294 | 0.0073618
2012-11-19 | 214:8666 | URBAN | Planned Outage | 902329 | 3 | 185 | 555 | 0.00033767 | 0.00018252
2012-11-19 | 801:74121 | SHORT RURAL | Planned Outage | 902345 | 3 | 65 | 195 | 0.00011864 | 0.00018252
2012-11-19 | 513:48056 | SHORT RURAL | Planned Outage | 902349 | 8 | 110 | 880 | 0.0005354 | 0.00048673
2012-11-20 | 807:74180 | SHORT RURAL | Planned Outage | 902558 | 1 | 270 | 270 | 0.00016425 | 6.0835e-05
2012-11-20 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 902658 | 42 | 600 | 9900 | 0.0060226 | 0.002555
2012-11-20 | ZN3155:PA21 | URBAN | Planned Outage | 902667 | 10 | 300 | 3000 | 0.001825 | 0.00060835
2012-11-20 | 243:80080 | SHORT RURAL | Planned Outage | 902689 | 12 | 135 | 1620 | 0.00098552 | 0.00073001
2012-11-20 | 227:13019 | SHORT RURAL | Planned Outage | 902697 | 8 | 180 | 1440 | 0.00087602 | 0.00048668
2012-11-20 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 902734 | 29 | 420 | 12180 | 0.0074096 | 0.0017642
2012-11-20 | ZN12640:PA18 | SHORT RURAL | Planned Outage | 902736 | 107 | 480 | 51360 | 0.031245 | 0.0065093
2012-11-20 | 264:81240 | SHORT RURAL | Planned Outage | 902740 | 13 | 405 | 5265 | 0.0032029 | 0.00079085
2012-11-20 | 264:81240 | SHORT RURAL | Planned Outage | 902745 | 8 | 290 | 2320 | 0.0014114 | 0.00048668
2012-11-20 | 260:33347 | SHORT RURAL | Planned Outage | 902748 | 3 | 360 | 1080 | 0.00065701 | 0.0001825
2012-11-20 | 501:48117 | URBAN | Planned Outage | 902759 | 2 | 185 | 370 | 0.00022509 | 0.00012167
2012-11-20 | 807:74184 | SHORT RURAL | Planned Outage | 902762 | 16 | 255 | 4080 | 0.002482 | 0.00097335
2012-11-20 | 523:33501 | SHORT RURAL | Planned Outage | 902763 | 11 | 325 | 3575 | 0.0021748 | 0.00066918
2012-11-20 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 902797 | 8 | 480 | 3840 | 0.002336 | 0.00048668
2012-11-20 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 902816 | 29 | 480 | 13920 | 0.0084682 | 0.0017642
2012-11-20 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 902820 | 32 | 240 | 7680 | 0.0046721 | 0.0019467
2012-11-20 | ZN3155:PA21 | URBAN | Planned Outage | 902831 | 26 | 360 | 9360 | 0.0056941 | 0.0015817
2012-11-20 | ZN35370:PA4 | URBAN | Planned Outage | 902832 | 6 | 30 | 180 | 0.0001095 | 0.00036501
2012-11-21 | 231:8415 | SHORT RURAL | Planned Outage | 903022 | 20 | 280 | 5600 | 0.0034069 | 0.0012168
2012-11-21 | 507:80922 | SHORT RURAL | Planned Outage | 903026 | 5 | 264 | 1320 | 0.00080306 | 0.00030419
2012-11-21 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 903034 | 21 | 45 | 945 | 0.00057492 | 0.0012776
2012-11-21 | 504:48034 | URBAN | Planned Outage | 903037 | 417 | 260 | 108420 | 0.065961 | 0.025369
2012-11-21 | 504:48031 | SHORT RURAL | Planned Outage | 903038 | 15 | 370 | 5550 | 0.0033765 | 0.00091257
2012-11-21 | 801:74121 | SHORT RURAL | Planned Outage | 903041 | 1 | 225 | 225 | 0.00013689 | 6.0838e-05
2012-11-21 | 514:18137 | SHORT RURAL | Planned Outage | 903042 | 9 | 265 | 2385 | 0.001451 | 0.00054754
2012-11-21 | 515:35197 | LONG RURAL | Planned Outage | 903044 | 1 | 142 | 142 | 8.639e-05 | 6.0838e-05
2012-11-21 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 903060 | 226 | 540 | 100860 | 0.061361 | 0.013749
2012-11-21 | ZN3155:PA17 | URBAN | Planned Outage | 903104 | 21 | 300 | 6300 | 0.0038328 | 0.0012776
2012-11-21 | ZN15009:PA7 | URBAN | Planned Outage | 903105 | 53 | 495 | 26235 | 0.015961 | 0.0032244
2012-11-21 | ZN2466:PA41 | URBAN | Planned Outage | 903108 | 27 | 538 | 14526 | 0.0088373 | 0.0016426
2012-11-25 | 224:80332 | URBAN | Planned Outage | 903811 | 64 | 630 | 40320 | 0.024529 | 0.0038935
2012-11-25 | 224:80337 | URBAN | Planned Outage | 903811 | 58 | 630 | 36540 | 0.022229 | 0.0035285
2012-11-22 | ZN12590:PA1 | SHORT RURAL | Planned Outage | 904611 | 83 | 600 | 49800 | 0.030296 | 0.0050493
2012-11-22 | ZN3922:PA26 | URBAN | Planned Outage | 904617 | 812 | 420 | 341040 | 0.20747 | 0.049398
2012-11-22 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 904625 | 5 | 480 | 2400 | 0.00146 | 0.00030418
2012-11-22 | ZN116:PA45 | URBAN | Planned Outage | 904628 | 8 | 330 | 2640 | 0.001606 | 0.00048668
2012-11-22 | ZN1285:PA24 | URBAN | Planned Outage | 904634 | 98 | 480 | 47040 | 0.028617 | 0.0059619
2012-11-22 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 904635 | 5 | 360 | 1200 | 0.00073002 | 0.00030418
2012-11-24 | ZN3154:PA11 | URBAN | Planned Outage | 904653 | 162 | 600 | 97200 | 0.059132 | 0.0098553
2012-11-24 | ZN3154:PA11 | URBAN | Planned Outage | 904661 | 81 | 510 | 41310 | 0.025131 | 0.0049277
2012-11-24 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 904683 | 10 | 480 | 4800 | 0.0029201 | 0.00060835
2012-11-25 | ZN3155:PA11 | URBAN | Planned Outage | 904703 | 189 | 420 | 79380 | 0.048291 | 0.011498
2012-11-26 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 905178 | 22 | 480 | 10560 | 0.0064242 | 0.0013384
2012-11-26 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 905190 | 209 | 480 | 100320 | 0.06103 | 0.012715
2012-11-26 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 905192 | 12 | 480 | 5760 | 0.0035041 | 0.00073003
2012-11-26 | ZN12600:PA9 | SHORT RURAL | Planned Outage | 905202 | 12 | 480 | 5760 | 0.0035041 | 0.00073003
2012-11-27 | ZN2602:PA19 | URBAN | Planned Outage | 905204 | 1 | 90 | 90 | 5.4753e-05 | 6.0836e-05
2012-11-27 | ZN12600:PA9 | SHORT RURAL | Planned Outage | 905208 | 4 | 480 | 1920 | 0.0011681 | 0.00024335
2012-11-27 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 905217 | 6 | 120 | 720 | 0.00043802 | 0.00036502
2012-11-27 | ZN2635:PA16 | URBAN | Planned Outage | 905220 | 20 | 510 | 10200 | 0.0062053 | 0.0012167
2012-11-28 | ZN195:PA3 | URBAN | Planned Outage | 905223 | 73 | 120 | 8760 | 0.0053293 | 0.0044411
2012-11-28 | ZN3472:PA32 | SHORT RURAL | Planned Outage | 905769 | 3 | 210 | 630 | 0.00038327 | 0.00018251
2012-11-28 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 905771 | 11 | 450 | 4950 | 0.0030114 | 0.0006692
2012-11-28 | ZN129:PA3 | URBAN | Planned Outage | 905778 | 42 | 480 | 20160 | 0.012265 | 0.0025551
2012-11-28 | ZN12620:PA8 | SHORT RURAL | Planned Outage | 905780 | 1 | 3150 | 3150 | 0.0019163 | 6.0836e-05
2012-11-28 | ZN12640:PA1 | SHORT RURAL | Planned Outage | 905781 | 130 | 480 | 62400 | 0.037962 | 0.0079087
2012-11-28 | ZN12610:PA22 | URBAN | Planned Outage | 905783 | 70 | 480 | 33600 | 0.020441 | 0.0042585
2012-11-28 | ZN2635:PA2 | URBAN | Planned Outage | 905785 | 73 | 330 | 24090 | 0.014655 | 0.0044411
2012-11-22 | 507:80922 | SHORT RURAL | Planned Outage | 905826 | 48 | 325 | 15600 | 0.0094903 | 0.0029201
2012-11-22 | 801:74121 | SHORT RURAL | Planned Outage | 905828 | 20 | 325 | 6500 | 0.0039543 | 0.0012167
2012-11-22 | 801:74121 | SHORT RURAL | Planned Outage | 905832 | 1 | 140 | 140 | 8.5169e-05 | 6.0835e-05
2012-11-22 | 264:81240 | SHORT RURAL | Planned Outage | 905833 | 34 | 420 | 14280 | 0.0086873 | 0.0020684
2012-11-22 | 264:81240 | SHORT RURAL | Planned Outage | 905838 | 26 | 340 | 8840 | 0.0053778 | 0.0015817
2012-11-22 | 225:33670 | SHORT RURAL | Planned Outage | 905839 | 1 | 300 | 300 | 0.00018251 | 6.0835e-05
2012-11-24 | 232:33413 | SHORT RURAL | Planned Outage | 905842 | 44 | 210 | 9240 | 0.0056212 | 0.0026768
2012-11-24 | 217:33612 | URBAN | Planned Outage | 905845 | 104 | 290 | 30160 | 0.018348 | 0.0063269
2012-11-24 | 264:81240 | SHORT RURAL | Planned Outage | 905851 | 5 | 340 | 1700 | 0.0010342 | 0.00030418
2012-11-22 | 512:48048 | SHORT RURAL | Planned Outage | 905852 | 105 | 460 | 48300 | 0.029383 | 0.0063877
2012-11-22 | 264:81240 | SHORT RURAL | Planned Outage | 905853 | 4 | 190 | 760 | 0.00046235 | 0.00024334
2012-11-22 | 235:2120 | SHORT RURAL | Planned Outage | 905854 | 44 | 510 | 22440 | 0.013651 | 0.0026767
2012-11-24 | 507:80923 | SHORT RURAL | Planned Outage | 905855 | 2 | 340 | 680 | 0.00041368 | 0.00012167
2012-11-22 | 523:33501 | SHORT RURAL | Planned Outage | 905856 | 47 | 310 | 14570 | 0.0088637 | 0.0028593
2012-11-23 | 810:74050 | SHORT RURAL | Planned Outage | 905857 | 2 | 145 | 290 | 0.00017642 | 0.00012167
2012-11-23 | 810:74050 | SHORT RURAL | Planned Outage | 905861 | 1 | 155 | 155 | 9.4295e-05 | 6.0835e-05
2012-11-26 | 504:48031 | SHORT RURAL | Planned Outage | 905865 | 20 | 380 | 7600 | 0.0046235 | 0.0012167
2012-11-26 | 227:13015 | SHORT RURAL | Planned Outage | 905872 | 18 | 430 | 7740 | 0.0047087 | 0.001095
2012-11-26 | 502:48004 | URBAN | Planned Outage | 905873 | 15 | 390 | 5850 | 0.0035589 | 0.00091253
2012-11-27 | 526:34640 | SHORT RURAL | Planned Outage | 905876 | 23 | 338 | 7774 | 0.0047294 | 0.0013992
2012-11-27 | 801:74121 | SHORT RURAL | Planned Outage | 905880 | 7 | 387 | 2709 | 0.0016481 | 0.00042585
2012-11-27 | 227:13015 | SHORT RURAL | Planned Outage | 905882 | 110 | 360 | 39600 | 0.024091 | 0.006692
2012-11-27 | 229:34983 | SHORT RURAL | Planned Outage | 905886 | 9 | 150 | 1350 | 0.00082129 | 0.00054753
2012-11-27 | 264:81240 | SHORT RURAL | Planned Outage | 905888 | 71 | 450 | 31950 | 0.019437 | 0.0043194
2012-11-28 | 510:48164 | SHORT RURAL | Planned Outage | 905890 | 18 | 345 | 6210 | 0.0037779 | 0.0010951
2012-11-28 | 243:80075 | SHORT RURAL | Planned Outage | 905891 | 6 | 395 | 2370 | 0.0014418 | 0.00036502
2012-11-28 | 526:34636 | SHORT RURAL | Planned Outage | 905894 | 3 | 325 | 975 | 0.00059316 | 0.00018251
2012-11-28 | 503:48017 | URBAN | Planned Outage | 905896 | 5 | 520 | 2600 | 0.0015817 | 0.00030418
2012-11-28 | 513:48059 | SHORT RURAL | Planned Outage | 905898 | 1 | 15 | 15 | 9.1255e-06 | 6.0836e-05
2012-11-28 | 801:74119 | URBAN | Planned Outage | 905899 | 42 | 196 | 8232 | 0.0050081 | 0.0025551
2012-11-29 | 235:2120 | SHORT RURAL | Planned Outage | 907132 | 60 | 349 | 20940 | 0.012739 | 0.0036502
2012-11-29 | 217:33612 | URBAN | Planned Outage | 907146 | 61 | 390 | 23790 | 0.014473 | 0.003711
2012-11-29 | 225:13446 | URBAN | Planned Outage | 907150 | 81 | 380 | 30780 | 0.018725 | 0.0049278
2012-11-29 | 264:81240 | SHORT RURAL | Planned Outage | 907157 | 7 | 270 | 1890 | 0.0011498 | 0.00042586
2012-11-30 | 243:80083 | SHORT RURAL | Planned Outage | 907159 | 4 | 390 | 1560 | 0.00094905 | 0.00024335
2012-11-30 | 512:48048 | SHORT RURAL | Planned Outage | 907163 | 42 | 400 | 16800 | 0.010221 | 0.0025551
2012-11-30 | 504:48026 | SHORT RURAL | Planned Outage | 907190 | 1 | 180 | 180 | 0.00010951 | 6.0837e-05
2012-11-29 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 907191 | 176 | 570 | 65640 | 0.039933 | 0.010707
2012-11-29 | 807:74184 | SHORT RURAL | Planned Outage | 907217 | 24 | 325 | 7800 | 0.0047452 | 0.0014601
2012-11-29 | ZN12660:PA10 | SHORT RURAL | Planned Outage | 907218 | 20 | 480 | 9600 | 0.0058403 | 0.0012167
2012-11-29 | ZN12570:PA35 | URBAN | Planned Outage | 907220 | 67 | 480 | 32160 | 0.019565 | 0.004076
2012-11-29 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 907223 | 9 | 480 | 4320 | 0.0026281 | 0.00054753
2012-11-30 | 512:48049 | SHORT RURAL | Planned Outage | 907224 | 74 | 385 | 28490 | 0.017332 | 0.0045019
2012-11-29 | ZN2196:PA17 | URBAN | Planned Outage | 907225 | 1 | 119 | 119 | 7.2395e-05 | 6.0837e-05
2012-11-30 | 810:74058 | SHORT RURAL | Planned Outage | 907229 | 1 | 115 | 115 | 6.9962e-05 | 6.0837e-05
2012-11-30 | ZN2635:PA28 | URBAN | Planned Outage | 907231 | 3 | 60 | 180 | 0.00010951 | 0.00018251
2012-11-30 | ZN9245:PA3 | URBAN | Planned Outage | 907235 | 14 | 360 | 5040 | 0.0030662 | 0.00085171
2012-11-30 | ZN35370:PA10 | SHORT RURAL | Planned Outage | 907236 | 2 | 570 | 1140 | 0.00069354 | 0.00012167
2012-11-30 | ZN14892:PA13 | URBAN | Planned Outage | 907237 | 124 | 480 | 59520 | 0.03621 | 0.0075437
2012-11-30 | ZN12600:PA1 | SHORT RURAL | Planned Outage | 907255 | 30 | 480 | 14400 | 0.0087605 | 0.0018251
2012-11-30 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 907266 | 8 | 270 | 2160 | 0.0013141 | 0.00048669
2012-12-01 | ZN263:PA33 34GHJ | CBD | Planned Outage | 907317 | 1 | 450 | 450 | 0.00027376 | 6.0837e-05
2012-12-01 | ZN129:PA3 | URBAN | Planned Outage | 907320 | 112 | 510 | 57120 | 0.03475 | 0.0068137
2012-12-01 | ZN12570:PA35 | URBAN | Planned Outage | 907323 | 164 | 480 | 49320 | 0.030005 | 0.0099772
2012-12-02 | ZN2196:PA2 | URBAN | Planned Outage | 907374 | 2 | 300 | 600 | 0.00036502 | 0.00012167
2012-12-02 | ZN8000:PA39 | URBAN | Planned Outage | 907376 | 4 | 75 | 300 | 0.00018251 | 0.00024335
2012-12-02 | ZN8000:PA39 | URBAN | Planned Outage | 907379 | 4 | 74 | 296 | 0.00018008 | 0.00024335
2012-12-02 | ZN8000:PA39 | URBAN | Planned Outage | 907381 | 2 | 74 | 148 | 9.0038e-05 | 0.00012167
2012-12-05 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 908251 | 1 | 410.55 | 410.55 | 0.00024977 | 6.0838e-05
2012-12-05 | 801:74121 | SHORT RURAL | Planned Outage | 908293 | 130 | 345 | 44850 | 0.027286 | 0.0079089
2012-12-03 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 908383 | 1 | 60 | 60 | 3.6502e-05 | 6.0837e-05
2012-12-03 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 908384 | 1 | 60 | 60 | 3.6502e-05 | 6.0837e-05
2012-12-04 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 908385 | 1 | 60 | 60 | 3.6502e-05 | 6.0837e-05
2012-12-04 | ZN12590:PA7 | SHORT RURAL | Planned Outage | 908387 | 1 | 60 | 60 | 3.6502e-05 | 6.0837e-05
2012-12-03 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 908392 | 6 | 480 | 2880 | 0.0017521 | 0.00036502
2012-12-03 | ZN15005:PA8 | URBAN | Planned Outage | 908394 | 80 | 270 | 21600 | 0.013141 | 0.0048669
2012-12-03 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 908402 | 29 | 450 | 13050 | 0.0079392 | 0.0017643
2012-12-03 | ZN874:PA25 | URBAN | Planned Outage | 908411 | 91 | 300 | 27300 | 0.016608 | 0.0055361
2012-12-03 | ZN35800:PA7 | URBAN | Planned Outage | 908415 | 95 | 690 | 65550 | 0.039878 | 0.0057795
2012-12-04 | ZN874:PA25 | URBAN | Planned Outage | 908428 | 29 | 300 | 8700 | 0.0052928 | 0.0017643
2012-12-05 | 205:12210 | URBAN | Planned Outage | 908461 | 1 | 113 | 113 | 6.8746e-05 | 6.0838e-05
2012-12-04 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 908503 | 17 | 303 | 5151 | 0.0031337 | 0.0010342
2012-12-04 | ZN3472:PA31 | URBAN | Planned Outage | 908507 | 14 | 630 | 8820 | 0.0053658 | 0.00085172
2012-12-05 | ZN195:PA3 | URBAN | Planned Outage | 908510 | 73 | 120 | 8760 | 0.0053294 | 0.0044411
2012-12-05 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 908513 | 15 | 240 | 3600 | 0.0021902 | 0.00091256
2012-12-05 | ZN10999:PA10 | URBAN | Planned Outage | 908518 | 2 | 240 | 480 | 0.00029202 | 0.00012168
2012-12-05 | ZN12570:PA21 | SHORT RURAL | Planned Outage | 909182 | 18 | 480 | 8640 | 0.0052564 | 0.0010951
2012-12-05 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 909183 | 8 | 480 | 3840 | 0.0023362 | 0.0004867
2012-12-05 | ZN12690:PA3 | SHORT RURAL | Planned Outage | 909187 | 126 | 510 | 64260 | 0.039094 | 0.0076655
2012-12-05 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 909199 | 93 | 540 | 50220 | 0.030553 | 0.0056579
2012-12-05 | ZN847:PA7 | URBAN | Planned Outage | 909210 | 4 | 300 | 1200 | 0.00073005 | 0.00024335
2012-12-05 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 909211 | 2 | 240 | 480 | 0.00029202 | 0.00012168
2012-11-30 | 509:48039 | LONG RURAL | Planned Outage | 909458 | 1 | 250 | 250 | 0.00015209 | 6.0837e-05
2012-11-30 | 513:48059 | SHORT RURAL | Planned Outage | 909459 | 2 | 100 | 200 | 0.00012167 | 0.00012167
2012-11-30 | 810:74058 | SHORT RURAL | Planned Outage | 909462 | 1 | 120 | 120 | 7.3004e-05 | 6.0837e-05
2012-11-30 | 807:74184 | SHORT RURAL | Planned Outage | 909463 | 3 | 95 | 285 | 0.00017338 | 0.00018251
2012-11-29 | 264:81240 | SHORT RURAL | Planned Outage | 909468 | 27 | 375 | 10125 | 0.0061597 | 0.0016426
2012-11-30 | 264:81240 | SHORT RURAL | Planned Outage | 909471 | 13 | 360 | 4680 | 0.0028472 | 0.00079088
2012-12-01 | 232:33413 | SHORT RURAL | Planned Outage | 909475 | 208 | 165 | 34320 | 0.020879 | 0.012654
2012-12-03 | 208:56 | URBAN | Planned Outage | 909480 | 1 | 460 | 460 | 0.00027985 | 6.0837e-05
2012-12-03 | 232:11459 | SHORT RURAL | Planned Outage | 909484 | 243 | 287 | 69741 | 0.042428 | 0.014783
2012-12-03 | 227:13015 | SHORT RURAL | Planned Outage | 909487 | 18 | 410 | 7380 | 0.0044897 | 0.0010951
2012-12-03 | 230:81440 | URBAN | Planned Outage | 909489 | 326 | 100 | 32600 | 0.019833 | 0.019833
2012-12-04 | 227:13015 | SHORT RURAL | Planned Outage | 909490 | 42 | 345 | 14490 | 0.0088153 | 0.0025552
2012-12-04 | 243:80081 | URBAN | Planned Outage | 909491 | 1 | 125 | 125 | 7.6046e-05 | 6.0837e-05
2012-12-04 | 213:33777 | SHORT RURAL | Planned Outage | 909494 | 30 | 405 | 12150 | 0.0073917 | 0.0018251
2012-12-06 | ZN12640:PA2 | URBAN | Planned Outage | 910303 | 119 | 450 | 53550 | 0.032579 | 0.0072397
2012-12-06 | ZN12570:PA24 | SHORT RURAL | Planned Outage | 910304 | 63 | 480 | 30240 | 0.018397 | 0.0038328
2012-12-06 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 910306 | 18 | 450 | 8100 | 0.0049279 | 0.0010951
2012-12-06 | ZN2635:PA18 | URBAN | Planned Outage | 910313 | 30 | 360 | 10800 | 0.0065705 | 0.0018251
2012-12-06 | ZN2635:PA20 | URBAN | Planned Outage | 910313 | 134 | 360 | 48240 | 0.029348 | 0.0081523
2012-12-06 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 910346 | 8 | 240 | 1920 | 0.0011681 | 0.0004867
2012-12-07 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 910358 | 35 | 420 | 14700 | 0.0089432 | 0.0021293
2012-12-07 | ZN12580:PA16 | URBAN | Planned Outage | 910364 | 10 | 480 | 4800 | 0.0029202 | 0.00060838
2012-12-08 | ZN384:PA24 | SHORT RURAL | Planned Outage | 910366 | 1 | 2760 | 2760 | 0.0016791 | 6.0838e-05
2012-12-08 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 910373 | 13 | 480 | 6240 | 0.0037963 | 0.0007909
2012-12-09 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 910384 | 2 | 480 | 960 | 0.00058405 | 0.00012168
2012-12-09 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 910384 | 17 | 480 | 8160 | 0.0049644 | 0.0010342
2012-12-09 | ZN36300:PA17 | URBAN | Planned Outage | 910398 | 14 | 510 | 7140 | 0.0043438 | 0.00085173
2012-12-10 | ZN9900:PA13 | URBAN | Planned Outage | 911053 | 22 | 540 | 11880 | 0.0072276 | 0.0013384
2012-12-10 | ZN12590:PA2 | URBAN | Planned Outage | 911088 | 228 | 30 | 6840 | 0.0041613 | 0.013871
2012-12-10 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 911095 | 21 | 480 | 10080 | 0.0061325 | 0.0012776
2012-12-10 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 911103 | 22 | 480 | 10560 | 0.0064245 | 0.0013384
2012-12-10 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 911108 | 20 | 480 | 9600 | 0.0058405 | 0.0012168
2012-12-10 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 911111 | 12 | 510 | 6120 | 0.0037233 | 0.00073006
2012-12-10 | ZN269:PA16 | URBAN | Planned Outage | 911118 | 66 | 420 | 27720 | 0.016864 | 0.0040153
2012-12-10 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 911124 | 9 | 360 | 3240 | 0.0019712 | 0.00054754
2012-12-12 | 504:48031 | SHORT RURAL | Planned Outage | 911349 | 15 | 405 | 6075 | 0.0036957 | 0.00091253
2012-12-12 | 243:80075 | SHORT RURAL | Planned Outage | 911350 | 30 | 390 | 11700 | 0.0071177 | 0.0018251
2012-12-12 | 512:48048 | SHORT RURAL | Planned Outage | 911354 | 42 | 560 | 23520 | 0.014308 | 0.0025551
2012-12-12 | 810:74054 | LONG RURAL | Planned Outage | 911355 | 2 | 130 | 120 | 7.3002e-05 | 0.00012167
2012-12-10 | ZN398:PA22 | URBAN | Planned Outage | 911357 | 28 | 600 | 16800 | 0.010221 | 0.0017035
2012-12-11 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 911392 | 61 | 480 | 29280 | 0.017813 | 0.0037109
2012-12-12 | 513:48056 | SHORT RURAL | Planned Outage | 911445 | 22 | 491.6333 | 3156.5333 | 0.0019203 | 0.0013384
2012-12-03 | 502:48010 | SHORT RURAL | Planned Outage | 911604 | 2 | 450 | 900 | 0.00054753 | 0.00012167
2012-12-03 | 512:48048 | SHORT RURAL | Planned Outage | 911605 | 63 | 350 | 22050 | 0.013414 | 0.0038327
2012-12-04 | 504:48034 | URBAN | Planned Outage | 911611 | 188 | 300 | 56400 | 0.034312 | 0.011437
2012-12-04 | 504:48026 | SHORT RURAL | Planned Outage | 911612 | 37 | 385 | 14245 | 0.0086663 | 0.002251
2012-11-30 | 523:33501 | SHORT RURAL | Planned Outage | 911614 | 7 | 35 | 245 | 0.00014905 | 0.00042586
2012-12-04 | 807:74184 | SHORT RURAL | Planned Outage | 911616 | 16 | 240 | 3840 | 0.0023361 | 0.00097339
2012-12-04 | 520:48172 | SHORT RURAL | Planned Outage | 911617 | 51 | 350 | 17850 | 0.010859 | 0.0031027
2012-12-13 | 223:14394 | URBAN | Planned Outage | 911824 | 636 | 445 | 283020 | 0.17218 | 0.038692
2012-12-12 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 911832 | 50 | 210 | 10500 | 0.0063877 | 0.0030418
2012-12-12 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 911835 | 164 | 480 | 78720 | 0.047889 | 0.009977
2012-12-13 | 507:80922 | SHORT RURAL | Planned Outage | 912193 | 48 | 300 | 14400 | 0.0087603 | 0.0029201
2012-12-13 | 205:12205 | URBAN | Planned Outage | 912197 | 28 | 120 | 3360 | 0.0020441 | 0.0017034
2012-12-13 | 205:12205 | URBAN | Planned Outage | 912198 | 59 | 145 | 8555 | 0.0052045 | 0.0035893
2012-12-13 | 258:80791 | URBAN | Planned Outage | 912200 | 1 | 425 | 425 | 0.00025855 | 6.0836e-05
2012-12-13 | 511:29878 | SHORT RURAL | Planned Outage | 912201 | 41 | 450 | 18450 | 0.011224 | 0.0024943
2012-12-13 | 810:74058 | SHORT RURAL | Planned Outage | 912203 | 1 | 50 | 50 | 3.0418e-05 | 6.0836e-05
2012-12-13 | 515:35197 | LONG RURAL | Planned Outage | 912205 | 81 | 305 | 24705 | 0.015029 | 0.0049277
2012-12-13 | 810:74054 | LONG RURAL | Planned Outage | 912206 | 1 | 84 | 84 | 5.1102e-05 | 6.0836e-05
2012-12-13 | 810:74054 | LONG RURAL | Planned Outage | 912209 | 3 | 293 | 879 | 0.00053475 | 0.00018251
2012-12-13 | 513:48051 | URBAN | Planned Outage | 912210 | 31 | 540 | 16740 | 0.010184 | 0.0018859
2012-12-05 | 512:48048 | SHORT RURAL | Planned Outage | 912214 | 179 | 410 | 73390 | 0.044649 | 0.01089
2012-12-05 | 264:81240 | SHORT RURAL | Planned Outage | 912228 | 20 | 488 | 9760 | 0.0059377 | 0.0012168
2012-12-05 | 230:81432 | URBAN | Planned Outage | 912232 | 38 | 1 | 38 | 2.3118e-05 | 0.0023118
2012-12-05 | 225:33676 | SHORT RURAL | Planned Outage | 912233 | 104 | 370 | 38480 | 0.02341 | 0.0063271
2012-12-05 | 243:80083 | SHORT RURAL | Planned Outage | 912235 | 3 | 395 | 1185 | 0.00072092 | 0.00018251
2012-12-05 | 232:33413 | SHORT RURAL | Planned Outage | 912237 | 2 | 303 | 606 | 0.00036868 | 0.00012168
2012-12-05 | 514:18137 | SHORT RURAL | Planned Outage | 912238 | 9 | 210 | 1890 | 0.0011498 | 0.00054754
2012-12-05 | 810:74054 | LONG RURAL | Planned Outage | 912241 | 6 | 355 | 2130 | 0.0012958 | 0.00036503
2012-12-06 | 264:81240 | SHORT RURAL | Planned Outage | 912245 | 17 | 275 | 4675 | 0.0028442 | 0.0010342
2012-12-06 | 243:80080 | SHORT RURAL | Planned Outage | 912249 | 14 | 350 | 4900 | 0.0029811 | 0.00085173
2012-12-06 | 512:48049 | SHORT RURAL | Planned Outage | 912252 | 202 | 250 | 50500 | 0.030723 | 0.012289
2012-12-06 | 260:33353 | URBAN | Planned Outage | 912262 | 306 | 330 | 100980 | 0.061434 | 0.018616
2012-12-06 | 243:80075 | SHORT RURAL | Planned Outage | 912266 | 4 | 400 | 1600 | 0.00097341 | 0.00024335
2012-12-06 | 220:8691 | URBAN | Planned Outage | 912273 | 1 | 265 | 265 | 0.00016122 | 6.0838e-05
2012-12-06 | 217:33611 | URBAN | Planned Outage | 912276 | 141 | 315 | 44415 | 0.027021 | 0.0085781
2012-12-06 | 232:11459 | SHORT RURAL | Planned Outage | 912286 | 215 | 345 | 74175 | 0.045126 | 0.01308
2012-12-06 | 265:81651 | URBAN | Planned Outage | 912290 | 14 | 335 | 4690 | 0.0028533 | 0.00085173
2012-12-07 | 240:34852 | URBAN | Planned Outage | 912291 | 17 | 615 | 10455 | 0.0063606 | 0.0010342
2012-12-06 | 501:48115 | SHORT RURAL | Planned Outage | 912294 | 13 | 150 | 1950 | 0.0011863 | 0.00079089
2012-12-06 | 509:48039 | LONG RURAL | Planned Outage | 912297 | 54 | 310 | 16740 | 0.010184 | 0.0032852
2012-12-06 | 507:80917 | URBAN | Planned Outage | 912298 | 85 | 350 | 29750 | 0.018099 | 0.0051712
2012-12-06 | 801:74121 | SHORT RURAL | Planned Outage | 912300 | 10 | 330 | 3300 | 0.0020076 | 0.00060838
2012-12-06 | 810:74054 | LONG RURAL | Planned Outage | 912302 | 1 | 120 | 120 | 7.3005e-05 | 6.0838e-05
2012-12-06 | 802:82220 | SHORT RURAL | Planned Outage | 912303 | 42 | 275 | 11550 | 0.0070268 | 0.0025552
2012-12-06 | 810:74054 | LONG RURAL | Planned Outage | 912305 | 3 | 55 | 165 | 0.00010038 | 0.00018251
2012-12-07 | 511:29878 | SHORT RURAL | Planned Outage | 912306 | 41 | 390 | 15990 | 0.009728 | 0.0024944
2012-12-07 | 227:13019 | SHORT RURAL | Planned Outage | 912308 | 38 | 220 | 8360 | 0.0050861 | 0.0023119
2012-12-08 | 243:80083 | SHORT RURAL | Planned Outage | 912309 | 105 | 415 | 43575 | 0.02651 | 0.006388
2012-12-07 | 231:8415 | SHORT RURAL | Planned Outage | 912313 | 50 | 355 | 17750 | 0.010799 | 0.0030419
2012-12-07 | 229:34995 | SHORT RURAL | Planned Outage | 912315 | 4 | 435 | 1740 | 0.0010586 | 0.00024335
2012-12-08 | 234:33444 | SHORT RURAL | Planned Outage | 912316 | 1 | 420 | 420 | 0.00025552 | 6.0838e-05
2012-12-08 | 264:81240 | SHORT RURAL | Planned Outage | 912317 | 5 | 265 | 1325 | 0.00080611 | 0.00030419
2012-12-09 | 206:34432 | URBAN | Planned Outage | 912319 | 1 | 370 | 370 | 0.0002251 | 6.0838e-05
2012-12-07 | 511:29878 | SHORT RURAL | Planned Outage | 912320 | 1 | 95 | 95 | 5.7796e-05 | 6.0838e-05
2012-12-07 | 515:35197 | LONG RURAL | Planned Outage | 912321 | 15 | 180 | 2700 | 0.0016426 | 0.00091257
2012-12-07 | 810:74054 | LONG RURAL | Planned Outage | 912324 | 2 | 115 | 230 | 0.00013993 | 0.00012168
2012-12-09 | 812:19065 | SHORT RURAL | Planned Outage | 912338 | 7 | 912 | 6384 | 0.0038839 | 0.00042587
2012-12-09 | 523:33508 | SHORT RURAL | Planned Outage | 912345 | 29 | 320 | 9280 | 0.0056458 | 0.0017643
2012-12-10 | 520:48172 | SHORT RURAL | Planned Outage | 912347 | 3 | 140 | 420 | 0.00025552 | 0.00018251
2012-12-10 | 243:80081 | URBAN | Planned Outage | 912349 | 1 | 410 | 410 | 0.00024944 | 6.0838e-05
2012-12-11 | 515:35192 | SHORT RURAL | Planned Outage | 912352 | 2 | 305 | 610 | 0.00037109 | 0.00012167
2012-12-12 | 264:81240 | SHORT RURAL | Planned Outage | 912383 | 8 | 30 | 240 | 0.000146 | 0.00048668
2012-12-12 | 801:74121 | SHORT RURAL | Planned Outage | 912389 | 56 | 320 | 17920 | 0.010902 | 0.0034068
2012-12-12 | 264:81240 | SHORT RURAL | Planned Outage | 912390 | 2 | 170 | 340 | 0.00020684 | 0.00012167
2012-12-12 | 227:13020 | SHORT RURAL | Planned Outage | 912393 | 20 | 350 | 7000 | 0.0042585 | 0.0012167
2012-12-10 | ZN15015:PA15 | URBAN | Planned Outage | 913298 | 1 | 6180 | 6180 | 0.0037598 | 6.0838e-05
2012-12-13 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 913370 | 3 | 480 | 1440 | 0.00087603 | 0.00018251
2012-12-13 | ZN12570:PA37 | SHORT RURAL | Planned Outage | 913371 | 17 | 480 | 8160 | 0.0049642 | 0.0010342
2012-12-13 | ZN2602:PA32 | URBAN | Planned Outage | 913378 | 1 | 240 | 240 | 0.00014601 | 6.0836e-05
2012-12-13 | ZN9700:PA17 | URBAN | Planned Outage | 913379 | 32 | 390 | 12480 | 0.0075923 | 0.0019467
2012-12-14 | ZN1287:PA4 | URBAN | Planned Outage | 913380 | 146 | 540 | 78840 | 0.047963 | 0.0088821
2012-12-14 | ZN35800:PA14 | URBAN | Planned Outage | 913382 | 700 | 480 | 336000 | 0.20441 | 0.042585
2012-12-14 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 913386 | 51 | 480 | 24480 | 0.014893 | 0.0031026
2012-12-14 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 913394 | 95 | 480 | 45600 | 0.027741 | 0.0057794
2012-12-14 | ZN14891:PA14 | SHORT RURAL | Planned Outage | 913406 | 30 | 480 | 14400 | 0.0087604 | 0.0018251
2012-12-15 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 913413 | 2 | 1950 | 1020 | 0.00062053 | 0.00012167
2012-12-15 | ZN188:PA22 | URBAN | Planned Outage | 913418 | 2 | 120 | 240 | 0.00014601 | 0.00012167
2012-12-18 | 810:74058 | SHORT RURAL | Planned Outage | 913496 | 33 | 285 | 9405 | 0.0057217 | 0.0020076
2012-12-19 | 232:11457 | URBAN | Planned Outage | 913721 | 179 | 405 | 72495 | 0.044104 | 0.01089
2012-12-17 | ZN12600:PA1 | SHORT RURAL | Planned Outage | 913752 | 30 | 480 | 14400 | 0.0087604 | 0.0018251
2012-12-17 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 913755 | 11 | 480 | 5280 | 0.0032121 | 0.0006692
2012-12-17 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 913758 | 1 | 180 | 180 | 0.0001095 | 6.0836e-05
2012-12-17 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 913760 | 19 | 330 | 6270 | 0.0038144 | 0.0011559
2012-12-18 | ZN8000:PA15 | URBAN | Planned Outage | 913779 | 1 | 120 | 120 | 7.3004e-05 | 6.0837e-05
2012-12-18 | ZN15013:PA10 | SHORT RURAL | Planned Outage | 913782 | 3 | 600 | 1800 | 0.0010951 | 0.00018251
2012-12-18 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 913787 | 1 | 480 | 480 | 0.00029202 | 6.0837e-05
2012-12-18 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 913790 | 16 | 480 | 7680 | 0.0046723 | 0.00097339
2012-12-14 | 512:48049 | SHORT RURAL | Planned Outage | 913824 | 7 | 183 | 1281 | 0.00077931 | 0.00042585
2012-12-15 | 524:33572 | SHORT RURAL | Planned Outage | 913829 | 386 | 505 | 194930 | 0.11859 | 0.023483
2012-12-14 | 222:2015 | SHORT RURAL | Planned Outage | 913830 | 7 | 225 | 1575 | 0.00095817 | 0.00042585
2012-12-14 | 227:13020 | SHORT RURAL | Planned Outage | 913833 | 6 | 300 | 1800 | 0.001095 | 0.00036502
2012-12-14 | 225:33670 | SHORT RURAL | Planned Outage | 913837 | 3 | 75 | 225 | 0.00013688 | 0.00018251
2012-12-15 | 264:81240 | SHORT RURAL | Planned Outage | 913843 | 1 | 470 | 470 | 0.00028593 | 6.0836e-05
2012-12-15 | 232:33413 | SHORT RURAL | Planned Outage | 913845 | 103 | 160 | 16480 | 0.010026 | 0.0062661
2012-12-14 | 524:33576 | SHORT RURAL | Planned Outage | 913848 | 17 | 290 | 4930 | 0.0029992 | 0.0010342
2012-12-14 | 509:48039 | LONG RURAL | Planned Outage | 913850 | 23 | 75 | 1725 | 0.0010494 | 0.0013992
2012-12-14 | 504:48031 | SHORT RURAL | Planned Outage | 913852 | 3 | 52 | 156 | 9.4904e-05 | 0.00018251
2012-12-14 | 509:48039 | LONG RURAL | Planned Outage | 913856 | 12 | 105 | 1260 | 0.00076653 | 0.00073003
2012-12-14 | 507:80926 | URBAN | Planned Outage | 913861 | 22 | 155 | 3410 | 0.0020745 | 0.0013384
2012-12-15 | 509:48039 | LONG RURAL | Planned Outage | 913864 | 33 | 175 | 5775 | 0.0035133 | 0.0020076
2012-12-14 | 513:48056 | SHORT RURAL | Planned Outage | 913867 | 3 | 125 | 375 | 0.00022814 | 0.00018251
2012-12-14 | 514:18146 | SHORT RURAL | Planned Outage | 913871 | 1 | 305 | 305 | 0.00018555 | 6.0836e-05
2012-12-14 | 812:19072 | SHORT RURAL | Planned Outage | 913874 | 4 | 350 | 1400 | 0.0008517 | 0.00024334
2012-12-16 | 514:18137 | SHORT RURAL | Planned Outage | 913875 | 2 | 200 | 400 | 0.00024334 | 0.00012167
2012-12-17 | 515:35193 | SHORT RURAL | Planned Outage | 913878 | 12 | 300 | 3600 | 0.0021901 | 0.00073003
2012-12-17 | 213:33771 | URBAN | Planned Outage | 913879 | 109 | 270 | 29430 | 0.017904 | 0.0066311
2012-12-17 | 223:14395 | SHORT RURAL | Planned Outage | 913882 | 73 | 457 | 33361 | 0.020296 | 0.004441
2012-12-17 | 224:80332 | URBAN | Planned Outage | 913883 | 1 | 420 | 420 | 0.00025551 | 6.0836e-05
2012-12-17 | 232:11454 | SHORT RURAL | Planned Outage | 913887 | 2 | 280 | 560 | 0.00034068 | 0.00012167
2012-12-17 | 260:33347 | SHORT RURAL | Planned Outage | 913888 | 232 | 300 | 69600 | 0.042342 | 0.014114
2012-12-17 | 243:80080 | SHORT RURAL | Planned Outage | 913893 | 32 | 450 | 14400 | 0.0087604 | 0.0019468
2012-12-17 | 503:48077 | URBAN | Planned Outage | 913895 | 37 | 485 | 17945 | 0.010917 | 0.0022509
2012-12-17 | 523:33508 | SHORT RURAL | Planned Outage | 913897 | 2 | 130 | 260 | 0.00015817 | 0.00012167
2012-12-17 | 811:74234 | SHORT RURAL | Planned Outage | 913899 | 2 | 200 | 400 | 0.00024334 | 0.00012167
2012-12-18 | 213:33777 | SHORT RURAL | Planned Outage | 913901 | 5 | 360 | 1800 | 0.0010951 | 0.00030418
2012-12-18 | 260:33347 | SHORT RURAL | Planned Outage | 913902 | 50 | 360 | 18000 | 0.010951 | 0.0030418
2012-12-18 | 514:18146 | SHORT RURAL | Planned Outage | 913903 | 1 | 265 | 265 | 0.00016122 | 6.0837e-05
2012-12-18 | 512:48049 | SHORT RURAL | Planned Outage | 913909 | 25 | 60 | 1500 | 0.00091255 | 0.0015209
2012-12-18 | 222:2017 | URBAN | Planned Outage | 913910 | 25 | 360 | 9000 | 0.0054753 | 0.0015209
2012-12-18 | 223:14399 | SHORT RURAL | Planned Outage | 913912 | 1 | 275 | 275 | 0.0001673 | 6.0837e-05
2012-12-18 | 232:33413 | SHORT RURAL | Planned Outage | 913915 | 12 | 465 | 5580 | 0.0033947 | 0.00073004
2012-12-18 | 264:81240 | SHORT RURAL | Planned Outage | 913918 | 5 | 402 | 2010 | 0.0012228 | 0.00030418
2012-12-18 | 232:11454 | SHORT RURAL | Planned Outage | 913920 | 2 | 510 | 1020 | 0.00062053 | 0.00012167
2012-12-18 | 524:33572 | SHORT RURAL | Planned Outage | 913926 | 25 | 380 | 9500 | 0.0057795 | 0.0015209
2012-12-18 | 511:29878 | SHORT RURAL | Planned Outage | 913927 | 41 | 462 | 18942 | 0.011524 | 0.0024943
2012-12-18 | 264:81240 | SHORT RURAL | Planned Outage | 913928 | 2 | 286 | 572 | 0.00034799 | 0.00012167
2012-12-18 | 513:48059 | SHORT RURAL | Planned Outage | 913931 | 3 | 91 | 273 | 0.00016608 | 0.00018251
2012-12-18 | 515:35193 | SHORT RURAL | Planned Outage | 913933 | 11 | 180 | 1980 | 0.0012046 | 0.0006692
2012-12-18 | 807:74184 | SHORT RURAL | Planned Outage | 913940 | 22 | 220 | 4840 | 0.0029445 | 0.0013384
2012-12-18 | 526:34637 | SHORT RURAL | Planned Outage | 913943 | 2 | 175 | 350 | 0.00021293 | 0.00012167
2012-12-19 | ZN13000:PA8 | SHORT RURAL | Planned Outage | 914197 | 1 | 480 | 480 | 0.00029202 | 6.0837e-05
2012-12-19 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 914203 | 32 | 480 | 15360 | 0.0093445 | 0.0019468
2012-12-19 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 914241 | 1 | 480 | 480 | 0.00029202 | 6.0837e-05
2012-12-19 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 914245 | 93 | 540 | 50220 | 0.030552 | 0.0056578
2012-12-20 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 914543 | 21 | 480 | 10080 | 0.0061324 | 0.0012776
2012-12-20 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 914599 | 43 | 420 | 18060 | 0.010987 | 0.002616
2012-12-20 | ZN1290:PA17 | URBAN | Planned Outage | 914602 | 1 | 150 | 150 | 9.1255e-05 | 6.0837e-05
2012-12-21 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 914720 | 5 | 360 | 1200 | 0.00073004 | 0.00030418
2012-12-20 | 504:48031 | SHORT RURAL | Planned Outage | 915393 | 20 | 442 | 8840 | 0.005378 | 0.0012167
2012-12-19 | 225:33670 | SHORT RURAL | Planned Outage | 915406 | 1 | 890 | 890 | 0.00054145 | 6.0837e-05
2012-12-19 | 264:81240 | SHORT RURAL | Planned Outage | 915407 | 10 | 465 | 4650 | 0.0028289 | 0.00060837
2012-12-19 | 243:80075 | SHORT RURAL | Planned Outage | 915410 | 30 | 410 | 12300 | 0.0074829 | 0.0018251
2012-12-19 | 224:80332 | URBAN | Planned Outage | 915411 | 1 | 260 | 260 | 0.00015818 | 6.0837e-05
2012-12-20 | 243:80080 | SHORT RURAL | Planned Outage | 915414 | 2 | 540 | 1080 | 0.00065704 | 0.00012167
2012-12-20 | 225:13444 | URBAN | Planned Outage | 915416 | 267 | 25 | 6675 | 0.0040609 | 0.016243
2012-12-19 | 503:48012 | URBAN | Planned Outage | 915418 | 138 | 405 | 55890 | 0.034002 | 0.0083955
2012-12-19 | 526:34633 | SHORT RURAL | Planned Outage | 915421 | 3 | 450 | 1350 | 0.00082129 | 0.00018251
2012-12-19 | 510:48164 | SHORT RURAL | Planned Outage | 915422 | 4 | 25 | 100 | 6.0837e-05 | 0.00024335
2012-12-19 | 526:34636 | SHORT RURAL | Planned Outage | 915423 | 7 | 15 | 105 | 6.3878e-05 | 0.00042586
2012-12-20 | 511:29878 | SHORT RURAL | Planned Outage | 915426 | 1 | 40 | 40 | 2.4335e-05 | 6.0837e-05
2012-12-20 | 264:81240 | SHORT RURAL | Planned Outage | 915428 | 2 | 493 | 986 | 0.00059985 | 0.00012167
2012-12-19 | 801:74121 | SHORT RURAL | Planned Outage | 915429 | 1 | 190 | 190 | 0.00011559 | 6.0837e-05
2012-12-19 | 520:48172 | SHORT RURAL | Planned Outage | 915430 | 18 | 310 | 5580 | 0.0033947 | 0.0010951
2012-12-20 | 520:48172 | SHORT RURAL | Planned Outage | 915434 | 18 | 390 | 7020 | 0.0042708 | 0.0010951
2012-12-20 | 801:74121 | SHORT RURAL | Planned Outage | 915437 | 31 | 250 | 7750 | 0.0047149 | 0.0018859
2012-12-20 | 810:74058 | SHORT RURAL | Planned Outage | 915438 | 17 | 260 | 4420 | 0.002689 | 0.0010342
2012-12-20 | 513:48059 | SHORT RURAL | Planned Outage | 915440 | 1 | 68 | 68 | 4.1369e-05 | 6.0837e-05
2012-12-21 | 227:13020 | SHORT RURAL | Planned Outage | 918938 | 126 | 420 | 52920 | 0.032195 | 0.0076655
2012-12-21 | 801:74121 | SHORT RURAL | Planned Outage | 918940 | 19 | 195 | 3705 | 0.002254 | 0.0011559
2012-12-21 | 243:80075 | SHORT RURAL | Planned Outage | 918951 | 65 | 385 | 25025 | 0.015224 | 0.0039544
2012-12-21 | 225:33676 | SHORT RURAL | Planned Outage | 918955 | 3 | 120 | 360 | 0.00021901 | 0.00018251
2012-12-20 | 813:89061 | LONG RURAL | Planned Outage | 918960 | 14 | 390 | 5460 | 0.0033217 | 0.00085172
2012-12-23 | 515:35200 | URBAN | Planned Outage | 918971 | 7 | 285 | 1995 | 0.0012137 | 0.00042586
2012-12-24 | 507:80926 | URBAN | Planned Outage | 918973 | 1 | 435 | 435 | 0.00026464 | 6.0837e-05
2012-12-27 | 260:33347 | SHORT RURAL | Planned Outage | 918974 | 2 | 15 | 30 | 1.8238e-05 | 0.00012159
2012-12-28 | 501:48123 | SHORT RURAL | Planned Outage | 918975 | 20 | 245 | 4900 | 0.0029789 | 0.0012159
2012-12-27 | 515:35192 | SHORT RURAL | Planned Outage | 918977 | 2 | 225 | 450 | 0.00027358 | 0.00012159
2012-12-27 | 810:74054 | LONG RURAL | Planned Outage | 918979 | 2 | 85 | 170 | 0.00010335 | 0.00012159
2012-12-28 | 514:18137 | SHORT RURAL | Planned Outage | 918981 | 9 | 236 | 2124 | 0.0012912 | 0.00054714
2012-12-28 | 802:82220 | SHORT RURAL | Planned Outage | 918992 | 6 | 185 | 1110 | 0.00067481 | 0.00036476
2013-01-02 | 511:29878 | SHORT RURAL | Planned Outage | 918993 | 41 | 365 | 14965 | 0.0090945 | 0.0024916
2013-01-02 | 810:74054 | LONG RURAL | Planned Outage | 918996 | 6 | 170 | 1020 | 0.00061987 | 0.00036463
2013-01-02 | 810:74054 | LONG RURAL | Planned Outage | 919000 | 1 | 185 | 185 | 0.00011243 | 6.0772e-05
2013-01-02 | 520:48172 | SHORT RURAL | Planned Outage | 919003 | 24 | 150 | 3600 | 0.0021878 | 0.0014585
2013-01-02 | 812:19066 | SHORT RURAL | Planned Outage | 919006 | 2 | 5 | 10 | 6.0772e-06 | 0.00012154
2013-01-03 | 264:81240 | SHORT RURAL | Planned Outage | 919009 | 35 | 360 | 12600 | 0.0076572 | 0.002127
2013-01-03 | 515:35197 | LONG RURAL | Planned Outage | 919011 | 21 | 165 | 3465 | 0.0021057 | 0.0012762
2013-01-03 | 515:35197 | LONG RURAL | Planned Outage | 919013 | 1 | 90 | 90 | 5.4695e-05 | 6.0772e-05
2013-01-03 | 515:35198 | SHORT RURAL | Planned Outage | 919015 | 8 | 120 | 960 | 0.00058341 | 0.00048617
2013-01-04 | 801:74121 | SHORT RURAL | Planned Outage | 919022 | 1 | 30 | 30 | 1.8232e-05 | 6.0772e-05
2013-01-04 | 515:35197 | LONG RURAL | Planned Outage | 919025 | 1 | 305 | 305 | 0.00018535 | 6.0772e-05
2013-01-05 | 812:19072 | SHORT RURAL | Planned Outage | 919026 | 1 | 88 | 88 | 5.3479e-05 | 6.0772e-05
2012-12-20 | 223:14395 | SHORT RURAL | Planned Outage | 919037 | 130 | 60 | 7800 | 0.0047453 | 0.0079088
2012-12-21 | 243:80083 | SHORT RURAL | Planned Outage | 919049 | 2 | 150 | 300 | 0.00018251 | 0.00012167
2012-12-21 | 227:13018 | URBAN | Planned Outage | 919057 | 154 | 425 | 65450 | 0.039818 | 0.0093689
2012-12-27 | 264:81240 | SHORT RURAL | Planned Outage | 919076 | 4 | 395 | 1580 | 0.00096055 | 0.00024318
2012-12-24 | ZN7900:PA11 | URBAN | Planned Outage | 919105 | 3 | 15 | 45 | 2.7377e-05 | 0.00018251
2012-12-25 | ZN35370:PA4 | URBAN | Planned Outage | 919120 | 4 | 360 | 1440 | 0.00087544 | 0.00024318
2012-12-27 | ZN35800:PA7 | URBAN | Planned Outage | 919121 | 73 | 360 | 26280 | 0.015977 | 0.004438
2013-01-07 | 504:48031 | SHORT RURAL | Planned Outage | 919373 | 6 | 65 | 390 | 0.00023701 | 0.00036463
2013-01-04 | 811:74234 | SHORT RURAL | Planned Outage | 919377 | 12 | 190 | 2280 | 0.0013856 | 0.00072926
2013-01-02 | 235:2124 | URBAN | Planned Outage | 919385 | 2 | 75 | 150 | 9.1157e-05 | 0.00012154
2013-01-08 | 520:48172 | SHORT RURAL | Planned Outage | 920168 | 4 | 10 | 40 | 2.4309e-05 | 0.00024309
2013-01-08 | 523:33501 | SHORT RURAL | Planned Outage | 920172 | 3 | 195 | 585 | 0.00035552 | 0.00018232
2013-01-07 | 264:81240 | SHORT RURAL | Planned Outage | 920234 | 4 | 465 | 1860 | 0.0011304 | 0.00024309
2013-01-07 | 243:80080 | SHORT RURAL | Planned Outage | 920236 | 2 | 273 | 546 | 0.00033181 | 0.00012154
2013-01-07 | 203:8089 | URBAN | Planned Outage | 920238 | 2 | 235 | 470 | 0.00028563 | 0.00012154
2013-01-04 | 202:34234 | URBAN | Planned Outage | 920239 | 62 | 104 | 6448 | 0.0039186 | 0.0037678
2013-01-09 | 526:34640 | SHORT RURAL | Planned Outage | 920577 | 12 | 375 | 4500 | 0.0027348 | 0.00072927
2013-01-09 | 504:48031 | SHORT RURAL | Planned Outage | 920581 | 66 | 525 | 34650 | 0.021058 | 0.004011
2013-01-09 | 227:13015 | SHORT RURAL | Planned Outage | 920582 | 37 | 15 | 555 | 0.00033729 | 0.0022486
2013-01-09 | 515:35197 | LONG RURAL | Planned Outage | 920602 | 2 | 65 | 130 | 7.9005e-05 | 0.00012155
2013-01-09 | 810:74054 | LONG RURAL | Planned Outage | 920603 | 48 | 310 | 14880 | 0.009043 | 0.0029171
2013-01-09 | 512:48049 | SHORT RURAL | Planned Outage | 920607 | 74 | 230 | 17020 | 0.010344 | 0.0044972
2013-01-09 | 515:35192 | SHORT RURAL | Planned Outage | 920608 | 2 | 60 | 120 | 7.2927e-05 | 0.00012155
2013-01-10 | 224:80337 | URBAN | Planned Outage | 923630 | 1 | 205 | 205 | 0.00012458 | 6.0773e-05
2013-01-10 | 227:13015 | SHORT RURAL | Planned Outage | 923634 | 53 | 234 | 12402 | 0.0075371 | 0.003221
2013-01-10 | 813:89061 | LONG RURAL | Planned Outage | 923651 | 14 | 330 | 4620 | 0.0028077 | 0.00085082
2013-01-13 | 261:81867 | URBAN | Planned Outage | 923659 | 25 | 630 | 15750 | 0.0095717 | 0.0015193
2013-01-11 | 511:29878 | SHORT RURAL | Planned Outage | 923667 | 2 | 235 | 470 | 0.00028563 | 0.00012155
2013-01-13 | 224:80341 | URBAN | Planned Outage | 923670 | 1 | 630 | 630 | 0.00038287 | 6.0773e-05
2013-01-10 | 512:48049 | SHORT RURAL | Planned Outage | 923677 | 45 | 315 | 14175 | 0.0086146 | 0.0027348
2013-01-11 | 238:34147 | URBAN | Planned Outage | 923681 | 6 | 10 | 60 | 3.6464e-05 | 0.00036464
2013-01-11 | 801:74121 | SHORT RURAL | Planned Outage | 923682 | 2 | 110 | 220 | 0.0001337 | 0.00012155
2013-01-11 | 807:74181 | SHORT RURAL | Planned Outage | 923692 | 30 | 185 | 5550 | 0.0033729 | 0.0018232
2013-01-14 | 205:12210 | URBAN | Planned Outage | 923696 | 57 | 160 | 9120 | 0.0055425 | 0.0034641
2013-01-15 | 524:33576 | SHORT RURAL | Planned Outage | 923954 | 17 | 315 | 5355 | 0.0032544 | 0.0010331
2013-01-15 | 513:48050 | SHORT RURAL | Planned Outage | 923958 | 3 | 45 | 135 | 8.2043e-05 | 0.00018232
2013-01-16 | 222:2014 | URBAN | Planned Outage | 923962 | 2 | 460 | 920 | 0.00055911 | 0.00012155
2013-01-16 | 213:33777 | SHORT RURAL | Planned Outage | 923963 | 3 | 160 | 480 | 0.00029171 | 0.00018232
2013-01-10 | 264:81240 | SHORT RURAL | Planned Outage | 923975 | 4 | 410 | 1640 | 0.00099668 | 0.00024309
2013-01-16 | 810:74058 | SHORT RURAL | Planned Outage | 923977 | 14 | 349 | 4886 | 0.0029694 | 0.00085082
2013-01-16 | 512:48049 | SHORT RURAL | Planned Outage | 924001 | 1 | 77 | 77 | 4.6795e-05 | 6.0773e-05
2013-01-17 | 511:29878 | SHORT RURAL | Planned Outage | 924007 | 36 | 390 | 14040 | 0.008583 | 0.0022008
2013-01-17 | 512:48048 | SHORT RURAL | Planned Outage | 924013 | 42 | 410 | 17220 | 0.010527 | 0.0025676
2013-01-17 | 504:48031 | SHORT RURAL | Planned Outage | 924018 | 1 | 225 | 225 | 0.00013755 | 6.1132e-05
2013-01-15 | 256:80632 | URBAN | Planned Outage | 924067 | 104 | 395 | 41080 | 0.024966 | 0.0063204
2013-01-17 | 523:33501 | SHORT RURAL | Planned Outage | 924069 | 4 | 143 | 572 | 0.00034968 | 0.00024453
2013-01-17 | 810:74062 | SHORT RURAL | Planned Outage | 924092 | 132 | 290 | 38280 | 0.023401 | 0.0080695
2013-01-17 | 801:74121 | SHORT RURAL | Planned Outage | 924124 | 3 | 315 | 945 | 0.0005777 | 0.0001834
2013-01-15 | 213:33777 | SHORT RURAL | Planned Outage | 924132 | 1 | 295 | 295 | 0.00017928 | 6.0773e-05
2013-01-11 | 513:48059 | SHORT RURAL | Planned Outage | 924136 | 45 | 275 | 12375 | 0.0075206 | 0.0027348
2013-01-14 | 516:48065 | SHORT RURAL | Planned Outage | 924137 | 10 | 280 | 2800 | 0.0017016 | 0.00060773
2013-01-17 | 220:8688 | URBAN | Planned Outage | 924149 | 62 | 130 | 8060 | 0.0049273 | 0.0037902
2013-01-15 | 229:34995 | SHORT RURAL | Planned Outage | 924157 | 9 | 215 | 1935 | 0.001176 | 0.00054696
2013-01-17 | 227:13016 | SHORT RURAL | Planned Outage | 924158 | 58 | 345 | 20010 | 0.012233 | 0.0035457
2013-01-15 | 238:34141 | SHORT RURAL | Planned Outage | 924160 | 13 | 500 | 6500 | 0.0039502 | 0.00079005
2013-01-16 | 216:10729 | URBAN | Planned Outage | 924168 | 148 | 45 | 6660 | 0.0040475 | 0.0089944
2013-01-16 | 526:34640 | SHORT RURAL | Planned Outage | 924172 | 12 | 366 | 4392 | 0.0026691 | 0.00072927
2013-01-16 | 513:48059 | SHORT RURAL | Planned Outage | 924180 | 8 | 240 | 1920 | 0.0011668 | 0.00048618
2013-01-15 | 238:34141 | SHORT RURAL | Planned Outage | 924188 | 34 | 435 | 14790 | 0.0089883 | 0.0020663
2013-01-15 | 260:33350 | SHORT RURAL | Planned Outage | 924192 | 37 | 390 | 14430 | 0.0087695 | 0.0022486
2013-01-17 | 229:34995 | SHORT RURAL | Planned Outage | 924197 | 8 | 327 | 2616 | 0.0015992 | 0.00048906
2013-01-16 | 508:82578 | SHORT RURAL | Planned Outage | 924201 | 118 | 370 | 43660 | 0.026533 | 0.0071712
2013-01-16 | 813:89063 | SHORT RURAL | Planned Outage | 924207 | 128 | 230 | 29440 | 0.017892 | 0.0077789
2013-01-16 | 234:2001 | URBAN | Planned Outage | 924216 | 11 | 380 | 4180 | 0.0025403 | 0.0006685
2013-01-16 | 264:81240 | SHORT RURAL | Planned Outage | 924216 | 33 | 380 | 12540 | 0.0076209 | 0.0020055
2013-01-16 | 243:80075 | SHORT RURAL | Planned Outage | 924220 | 3 | 395 | 1185 | 0.00072016 | 0.00018232
2013-01-15 | 264:81240 | SHORT RURAL | Planned Outage | 924229 | 4 | 380 | 1520 | 0.00092375 | 0.00024309
2013-01-20 | 264:81244 | URBAN | Planned Outage | 925577 | 12 | 332 | 3984 | 0.0024355 | 0.00073359
2013-01-18 | 264:81240 | SHORT RURAL | Planned Outage | 925587 | 31 | 420 | 13020 | 0.0079595 | 0.0018951
2013-01-18 | 504:48031 | SHORT RURAL | Planned Outage | 925594 | 25 | 180 | 4500 | 0.002751 | 0.0015283
2013-01-18 | 515:35197 | LONG RURAL | Planned Outage | 925601 | 1 | 65 | 65 | 3.9736e-05 | 6.1133e-05
2013-01-18 | 814:82283 | SHORT RURAL | Planned Outage | 925613 | 5 | 45 | 225 | 0.00013755 | 0.00030566
2013-01-18 | 810:74058 | SHORT RURAL | Planned Outage | 925631 | 8 | 75 | 600 | 0.0003668 | 0.00048906
2013-01-18 | 813:89062 | SHORT RURAL | Planned Outage | 925635 | 21 | 208 | 4368 | 0.0026703 | 0.0012838
2013-01-21 | 511:29878 | SHORT RURAL | Planned Outage | 926108 | 41 | 420 | 17220 | 0.010527 | 0.0025064
2013-01-18 | 231:8405 | SHORT RURAL | Planned Outage | 926309 | 14 | 185 | 2590 | 0.0015833 | 0.00085586
2013-01-18 | 807:74179 | SHORT RURAL | Planned Outage | 926313 | 19 | 190 | 3610 | 0.0022069 | 0.0011615
2013-01-22 | 230:81434 | URBAN | Planned Outage | 926764 | 1 | 290 | 290 | 0.00017729 | 6.1133e-05
2013-01-22 | 230:81440 | URBAN | Planned Outage | 926773 | 59 | 265 | 15635 | 0.0095582 | 0.0036069
2013-01-22 | 501:48123 | SHORT RURAL | Planned Outage | 926783 | 18 | 105 | 1890 | 0.0011554 | 0.0011004
2013-01-22 | 514:18141 | SHORT RURAL | Planned Outage | 926785 | 6 | 165 | 990 | 0.00060522 | 0.0003668
2013-01-22 | 810:74054 | LONG RURAL | Planned Outage | 926789 | 54 | 212 | 11448 | 0.0069985 | 0.0033012
2013-01-22 | 807:74184 | SHORT RURAL | Planned Outage | 926801 | 4 | 45 | 180 | 0.00011004 | 0.00024453
2013-01-22 | 523:33501 | SHORT RURAL | Planned Outage | 926807 | 93 | 390 | 36270 | 0.022173 | 0.0056854
2013-01-22 | 227:13015 | SHORT RURAL | Planned Outage | 926817 | 3 | 435 | 1305 | 0.00079779 | 0.0001834
2013-01-23 | 504:48031 | SHORT RURAL | Planned Outage | 927448 | 31 | 485 | 15035 | 0.0091915 | 0.0018952
2013-01-23 | 264:81240 | SHORT RURAL | Planned Outage | 927472 | 1 | 150 | 150 | 9.1701e-05 | 6.1134e-05
2013-01-23 | 810:74054 | LONG RURAL | Planned Outage | 927477 | 2 | 85 | 170 | 0.00010393 | 0.00012227
2013-01-23 | 801:74122 | URBAN | Planned Outage | 927479 | 15 | 171 | 2565 | 0.0015681 | 0.00091701
2013-01-23 | 810:74054 | LONG RURAL | Planned Outage | 927481 | 1 | 135 | 135 | 8.2531e-05 | 6.1134e-05
2013-01-23 | 264:81240 | SHORT RURAL | Planned Outage | 927491 | 12 | 245 | 2940 | 0.0017973 | 0.00073361
2013-01-23 | 801:74122 | URBAN | Planned Outage | 927494 | 54 | 160 | 8640 | 0.005282 | 0.0033012
2013-01-24 | 813:89062 | SHORT RURAL | Planned Outage | 927675 | 7 | 245 | 1715 | 0.0010486 | 0.00042801
2013-01-24 | 524:33576 | SHORT RURAL | Planned Outage | 927681 | 6 | 375 | 2250 | 0.0013758 | 0.00036687
2013-01-24 | 813:89061 | LONG RURAL | Planned Outage | 927685 | 14 | 315 | 4410 | 0.0026965 | 0.00085603
2013-01-24 | 520:48172 | SHORT RURAL | Planned Outage | 927692 | 39 | 335 | 13065 | 0.0079886 | 0.0023847
2013-01-02 | ZN195:PA11 | URBAN | Planned Outage | 930237 | 2 | 480 | 960 | 0.00058341 | 0.00012154
2013-01-05 | ZN2466:PA15 | URBAN | Planned Outage | 930239 | 67 | 360 | 24120 | 0.014658 | 0.0040717
2013-01-05 | ZN35500:PA32 | URBAN | Planned Outage | 930240 | 21 | 14880 | 312480 | 0.1899 | 0.0012762
2013-01-07 | ZN2473:PA14 | URBAN | Planned Outage | 930489 | 2 | 480 | 960 | 0.00058341 | 0.00012154
2013-01-07 | ZN13000:PA10 | URBAN | Planned Outage | 930499 | 61 | 480 | 29280 | 0.017794 | 0.0037071
2013-01-07 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 930500 | 6 | 330 | 1980 | 0.0012033 | 0.00036463
2013-01-08 | ZN188:PA27 | URBAN | Planned Outage | 930503 | 2 | 15 | 30 | 1.8232e-05 | 0.00012155
2013-01-08 | ZN188:PA27 | URBAN | Planned Outage | 930506 | 42 | 120 | 5040 | 0.003063 | 0.0025525
2013-01-08 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 930512 | 10 | 510 | 5100 | 0.0030994 | 0.00060773
2013-01-08 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 930523 | 10 | 480 | 4800 | 0.0029171 | 0.00060773
2013-01-08 | ZN384:PA33 | URBAN | Planned Outage | 930532 | 25 | 420 | 10500 | 0.0063812 | 0.0015193
2013-01-08 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 930539 | 18 | 360 | 6480 | 0.0039381 | 0.0010939
2013-01-08 | ZN12570:PA41 | URBAN | Planned Outage | 930547 | 58 | 420 | 24360 | 0.014804 | 0.0035248
2013-01-09 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 930573 | 1 | 540 | 540 | 0.00032817 | 6.0773e-05
2013-01-09 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 930575 | 1 | 540 | 540 | 0.00032817 | 6.0773e-05
2013-01-09 | ZN13000:PA10 | URBAN | Planned Outage | 930587 | 456 | 510 | 13680 | 0.0083137 | 0.027712
2013-01-09 | ZN12640:PA2 | URBAN | Planned Outage | 930592 | 119 | 480 | 57120 | 0.034713 | 0.007232
2013-01-09 | ZN14891:PA10 | SHORT RURAL | Planned Outage | 930595 | 79 | 480 | 37920 | 0.023045 | 0.0048011
2013-01-09 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 930596 | 20 | 480 | 9600 | 0.0058342 | 0.0012155
2013-01-09 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 930600 | 24 | 480 | 11520 | 0.007001 | 0.0014585
2013-01-09 | ZN14144:PA4 | URBAN | Planned Outage | 930608 | 58 | 480 | 27840 | 0.016919 | 0.0035248
2013-01-10 | ZN12620:PA2 | SHORT RURAL | Planned Outage | 930618 | 26 | 390 | 780 | 0.00047403 | 0.0015801
2013-01-10 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 930621 | 15 | 480 | 7200 | 0.0043756 | 0.00091159
2013-01-10 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 930634 | 7 | 480 | 3360 | 0.002042 | 0.00042541
2013-01-10 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 930642 | 21 | 480 | 10080 | 0.0061259 | 0.0012762
2013-01-10 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 930663 | 55 | 480 | 26400 | 0.016044 | 0.0033425
2013-01-10 | ZN13000:PA8 | SHORT RURAL | Planned Outage | 930665 | 38 | 420 | 2280 | 0.0013856 | 0.0023094
2013-01-11 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 930673 | 10 | 480 | 4800 | 0.0029171 | 0.00060773
2013-01-11 | ZN14144:PA4 | URBAN | Planned Outage | 930680 | 58 | 450 | 26100 | 0.015862 | 0.0035248
2013-01-11 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 930699 | 13 | 420 | 5460 | 0.0033182 | 0.00079005
2013-01-24 | 223:14395 | SHORT RURAL | Planned Outage | 930700 | 2 | 250 | 500 | 0.00030572 | 0.00012229
2013-01-12 | ZN14891:PA6 | URBAN | Planned Outage | 930729 | 9 | 300 | 2700 | 0.0016409 | 0.00054696
2013-01-12 | ZN188:PA30 | URBAN | Planned Outage | 930742 | 1 | 510 | 510 | 0.00030994 | 6.0773e-05
2013-01-24 | 232:33413 | SHORT RURAL | Planned Outage | 930748 | 1 | 265 | 265 | 0.00016203 | 6.1145e-05
2013-01-13 | ZN3155:PA11 | URBAN | Planned Outage | 930749 | 2 | 385 | 770 | 0.00046795 | 0.00012155
2013-01-14 | ZN3155:PA11 | URBAN | Planned Outage | 930756 | 136 | 359 | 48824 | 0.029672 | 0.0082651
2013-01-14 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 930791 | 2 | 480 | 960 | 0.00058342 | 0.00012155
2013-01-14 | ZN690:PA3 | URBAN | Planned Outage | 930792 | 33 | 420 | 13860 | 0.0084231 | 0.0020055
2013-01-14 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 930795 | 48 | 360 | 17280 | 0.010502 | 0.0029171
2013-01-15 | ZN711:PA28 | URBAN | Planned Outage | 930805 | 172 | 30 | 5160 | 0.0031359 | 0.010453
2013-01-15 | ZN15011:PA10 | URBAN | Planned Outage | 930815 | 15 | 540 | 8100 | 0.0049226 | 0.00091159
2013-01-25 | 514:18137 | SHORT RURAL | Planned Outage | 930816 | 72 | 315 | 22680 | 0.013866 | 0.0044018
2013-01-15 | ZN12660:PA14 | SHORT RURAL | Planned Outage | 930825 | 65 | 480 | 21600 | 0.013127 | 0.0039502
2013-01-25 | 803:74016 | SHORT RURAL | Planned Outage | 930830 | 14 | 185 | 2590 | 0.0015834 | 0.0008559
2013-01-25 | 511:29878 | SHORT RURAL | Planned Outage | 930866 | 11 | 7408.1333 | 81489.4667 | 0.049819 | 0.00067249
2013-01-25 | 803:74016 | SHORT RURAL | Planned Outage | 930878 | 10 | 30 | 300 | 0.00018341 | 0.00061135
2013-01-25 | 810:74054 | LONG RURAL | Planned Outage | 930881 | 1 | 90 | 90 | 5.5022e-05 | 6.1135e-05
2013-01-25 | 810:74054 | LONG RURAL | Planned Outage | 930885 | 1 | 90 | 90 | 5.5022e-05 | 6.1135e-05
2013-01-15 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 930886 | 41 | 480 | 19680 | 0.01196 | 0.0024917
2013-01-25 | 810:74054 | LONG RURAL | Planned Outage | 930887 | 1 | 65 | 65 | 3.9738e-05 | 6.1135e-05
2013-01-15 | ZN12690:PA3 | SHORT RURAL | Planned Outage | 930893 | 182 | 510 | 92820 | 0.056409 | 0.011061
2013-01-15 | ZN12610:PA9 | SHORT RURAL | Planned Outage | 930898 | 25 | 300 | 7500 | 0.004558 | 0.0015193
2013-01-16 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 930900 | 26 | 480 | 11520 | 0.007001 | 0.0015801
2013-01-16 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 930906 | 11 | 480 | 5280 | 0.0032088 | 0.0006685
2013-01-16 | ZN847:PA23 | URBAN | Planned Outage | 930911 | 1 | 360 | 360 | 0.00021878 | 6.0773e-05
2013-01-16 | ZN965:PA43 | URBAN | Planned Outage | 930911 | 1 | 360 | 360 | 0.00021878 | 6.0773e-05
2013-01-16 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 930921 | 28 | 480 | 13440 | 0.0081679 | 0.0017016
2013-01-17 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 931149 | 28 | 510 | 14280 | 0.0087297 | 0.0017117
2013-01-17 | ZN12580:PA4 | URBAN | Planned Outage | 931153 | 52 | 480 | 24000 | 0.014672 | 0.0031789
2013-01-17 | ZN195:PA9 | URBAN | Planned Outage | 931156 | 93 | 420 | 39060 | 0.023878 | 0.0056853
2013-01-17 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 931157 | 5 | 480 | 2400 | 0.0014672 | 0.00030566
2013-01-17 | ZN3155:PA16 | URBAN | Planned Outage | 931161 | 90 | 360 | 32400 | 0.019807 | 0.0055019
2013-01-17 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 931178 | 10 | 420 | 4200 | 0.0025676 | 0.00061132
2013-01-18 | ZN2568:PA16 | URBAN | Planned Outage | 931184 | 31 | 30 | 930 | 0.00056853 | 0.0018951
2013-01-19 | ZN14891:PA6 | URBAN | Planned Outage | 931185 | 5 | 300 | 1500 | 0.00091699 | 0.00030566
2013-01-21 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 931196 | 15 | 480 | 7200 | 0.0044015 | 0.00091699
2013-01-21 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 931200 | 22 | 480 | 10260 | 0.0062722 | 0.0013449
2013-01-21 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 931209 | 9 | 360 | 3240 | 0.0019807 | 0.00055019
2013-01-21 | ZN3425:PA11 | URBAN | Planned Outage | 931239 | 69 | 420 | 28980 | 0.017716 | 0.0042181
2013-01-22 | ZN129:PA3 | URBAN | Planned Outage | 931242 | 10 | 540 | 5400 | 0.0033012 | 0.00061133
2013-01-22 | ZN12650:PA20 | URBAN | Planned Outage | 931254 | 525 | 570 | 164640 | 0.10065 | 0.032095
2013-01-22 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 931287 | 17 | 480 | 8160 | 0.0049885 | 0.0010393
2013-01-22 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 931294 | 12 | 510 | 6120 | 0.0037414 | 0.0007336
2013-01-22 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 931303 | 20 | 480 | 1200 | 0.0007336 | 0.0012227
2013-01-22 | ZN2466:PA41 | URBAN | Planned Outage | 931309 | 18 | 540 | 9720 | 0.0059422 | 0.0011004
2013-01-22 | ZN35600:PA14 | URBAN | Planned Outage | 931311 | 59 | 420 | 24780 | 0.015149 | 0.0036069
2013-01-23 | ZN1290:PA13 | URBAN | Planned Outage | 931312 | 2 | 30 | 60 | 3.6681e-05 | 0.00012227
2013-01-23 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 931316 | 75 | 600 | 13260 | 0.0081064 | 0.0045851
2013-01-23 | ZN12640:PA2 | URBAN | Planned Outage | 931326 | 119 | 480 | 57120 | 0.03492 | 0.007275
2013-01-23 | ZN12580:PA4 | URBAN | Planned Outage | 931335 | 21 | 480 | 10080 | 0.0061623 | 0.0012838
2013-01-23 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 931347 | 7 | 480 | 3360 | 0.0020541 | 0.00042794
2013-01-24 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 931362 | 8 | 480 | 3840 | 0.002348 | 0.00048916
2013-01-24 | ZN14891:PA16 | SHORT RURAL | Planned Outage | 931364 | 35 | 360 | 12600 | 0.0077043 | 0.0021401
2013-01-24 | ZN14891:PA16 | SHORT RURAL | Planned Outage | 931369 | 22 | 360 | 7920 | 0.0048427 | 0.0013452
2013-01-24 | ZN14891:PA16 | SHORT RURAL | Planned Outage | 931371 | 7 | 360 | 2520 | 0.0015409 | 0.00042801
2013-01-24 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 931373 | 9 | 360 | 3240 | 0.0019811 | 0.0005503
2013-01-25 | ZN116:PA35 | URBAN | Planned Outage | 931375 | 8 | 540 | 4320 | 0.0026411 | 0.00048908
2013-01-25 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 931376 | 3 | 480 | 1440 | 0.00088035 | 0.00018341
2013-01-25 | ZN2835:PA20 | URBAN | Planned Outage | 931380 | 139 | 125 | 17375 | 0.010622 | 0.0084978
2013-01-26 | ZN35800:PA4 | URBAN | Planned Outage | 931382 | 79 | 2280 | 180120 | 0.11012 | 0.0048297
2013-01-26 | ZN2473:PA27 | URBAN | Planned Outage | 931384 | 32 | 1560 | 49920 | 0.030519 | 0.0019563
2013-01-30 | 243:80075 | SHORT RURAL | Planned Outage | 931385 | 1 | 390 | 390 | 0.00023813 | 6.1059e-05
2013-01-30 | 801:74121 | SHORT RURAL | Planned Outage | 931394 | 3 | 125 | 375 | 0.00022897 | 0.00018318
2013-01-30 | 807:74180 | SHORT RURAL | Planned Outage | 931396 | 2 | 85 | 170 | 0.0001038 | 0.00012212
2013-01-30 | 807:74180 | SHORT RURAL | Planned Outage | 931398 | 1 | 65 | 65 | 3.9688e-05 | 6.1059e-05
2013-01-31 | 503:48077 | URBAN | Planned Outage | 931427 | 101 | 325 | 32825 | 0.020043 | 0.006167
2013-01-24 | 260:33353 | URBAN | Planned Outage | 931440 | 33 | 120 | 3960 | 0.0024213 | 0.0020178
2013-01-24 | 264:81240 | SHORT RURAL | Planned Outage | 931443 | 27 | 280 | 7560 | 0.0046226 | 0.0016509
2013-01-25 | 232:11455 | URBAN | Planned Outage | 931447 | 312 | 365 | 113880 | 0.069621 | 0.019074
2013-01-25 | 512:48048 | SHORT RURAL | Planned Outage | 931454 | 42 | 465 | 19530 | 0.01194 | 0.0025677
2013-01-26 | 801:74120 | SHORT RURAL | Planned Outage | 931458 | 13 | 270 | 3510 | 0.0021459 | 0.00079476
2013-01-31 | 213:33770 | URBAN | Planned Outage | 931777 | 80 | 195 | 15600 | 0.0095253 | 0.0048848
2013-01-31 | 265:81649 | URBAN | Planned Outage | 931785 | 1 | 400 | 400 | 0.00024424 | 6.1059e-05
2013-01-28 | ZN2835:PA20 | URBAN | Planned Outage | 931887 | 141 | 120 | 16920 | 0.010344 | 0.0086201
2013-01-29 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 931892 | 9 | 510 | 4590 | 0.0028078 | 0.00055056
2013-01-29 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 931920 | 6 | 480 | 2880 | 0.0017618 | 0.00036704
2013-01-29 | ZN2635:PA20 | URBAN | Planned Outage | 931922 | 134 | 360 | 48240 | 0.02951 | 0.0081972
2013-01-29 | ZN12580:PA16 | URBAN | Planned Outage | 931925 | 30 | 480 | 14400 | 0.0088089 | 0.0018352
2013-01-29 | ZN384:PA33 | URBAN | Planned Outage | 931926 | 25 | 420 | 10500 | 0.0064232 | 0.0015293
2013-01-30 | ZN167:PA2 | URBAN | Planned Outage | 931944 | 7 | 30 | 210 | 0.00012822 | 0.00042741
2013-01-30 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 931963 | 18 | 360 | 6480 | 0.0039566 | 0.0010991
2013-01-31 | ZN9118:PA6 | URBAN | Planned Outage | 931979 | 11 | 180 | 1980 | 0.001209 | 0.00067165
2013-01-31 | ZN690:PA3 | URBAN | Planned Outage | 931986 | 33 | 450 | 14850 | 0.0090673 | 0.002015
2013-01-28 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 931990 | 26 | 4800 | 47040 | 0.028758 | 0.0015895
2013-01-31 | ZN12610:PA18 | URBAN | Planned Outage | 931996 | 2 | 480 | 960 | 0.00058617 | 0.00012212
2013-01-31 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 932024 | 77 | 300 | 23100 | 0.014105 | 0.0047016
2013-01-31 | ZN12570:PA24 | SHORT RURAL | Planned Outage | 932028 | 72 | 360 | 25920 | 0.015827 | 0.0043963
2013-01-31 | 214:8670 | URBAN | Planned Outage | 932052 | 14 | 135 | 1890 | 0.001154 | 0.00085483
2013-01-31 | 507:80925 | SHORT RURAL | Planned Outage | 932057 | 260 | 455 | 118300 | 0.072233 | 0.015875
2013-02-01 | ZN12640:PA18 | SHORT RURAL | Planned Outage | 932981 | 107 | 480 | 51360 | 0.031361 | 0.0065334
2013-02-01 | ZN847:PA10 | URBAN | Planned Outage | 932984 | 30 | 60 | 1800 | 0.0010991 | 0.0018318
2013-02-02 | ZN9700:PA20 | URBAN | Planned Outage | 933005 | 5 | 720 | 3600 | 0.0021982 | 0.0003053
2013-02-02 | ZN5868:PA27 | URBAN | Planned Outage | 933012 | 6 | 510 | 3060 | 0.0018684 | 0.00036636
2013-02-01 | 243:80075 | SHORT RURAL | Planned Outage | 933055 | 30 | 290 | 8700 | 0.0053122 | 0.0018318
2013-02-01 | 231:8405 | SHORT RURAL | Planned Outage | 933059 | 1 | 245 | 245 | 0.0001496 | 6.106e-05
2013-02-01 | 520:48172 | SHORT RURAL | Planned Outage | 933062 | 4 | 120 | 480 | 0.00029309 | 0.00024424
2013-02-01 | 238:34141 | SHORT RURAL | Planned Outage | 933091 | 21 | 338 | 7098 | 0.0043341 | 0.0012823
2013-02-01 | 526:34640 | SHORT RURAL | Planned Outage | 933111 | 4 | 310 | 1240 | 0.00075715 | 0.00024424
2013-02-01 | 235:2120 | SHORT RURAL | Planned Outage | 933122 | 16 | 330 | 5280 | 0.003224 | 0.00097696
2013-02-03 | 228:7490 | SHORT RURAL | Planned Outage | 933138 | 11 | 315 | 3465 | 0.0021157 | 0.00067166
2013-02-04 | 227:13015 | SHORT RURAL | Planned Outage | 933463 | 1 | 206 | 206 | 0.00012578 | 6.106e-05
2013-02-04 | 222:2014 | URBAN | Planned Outage | 933469 | 1 | 510 | 510 | 0.00031141 | 6.106e-05
2013-02-04 | 256:80647 | URBAN | Planned Outage | 933471 | 139 | 5 | 695 | 0.00042437 | 0.0084874
2013-02-04 | 501:48125 | URBAN | Planned Outage | 933475 | 125 | 425 | 53125 | 0.032438 | 0.0076325
2013-02-05 | 206:34441 | URBAN | Planned Outage | 933957 | 1 | 160 | 160 | 9.7699e-05 | 6.1062e-05
2013-02-05 | 227:13019 | SHORT RURAL | Planned Outage | 933962 | 3 | 20 | 60 | 3.6637e-05 | 0.00018319
2013-02-05 | 238:34137 | URBAN | Planned Outage | 933968 | 43 | 80 | 3440 | 0.0021005 | 0.0026257
2013-02-05 | 515:35197 | LONG RURAL | Planned Outage | 933974 | 12 | 325 | 3900 | 0.0023814 | 0.00073274
2013-02-04 | 511:29878 | SHORT RURAL | Planned Outage | 934080 | 4 | 210 | 840 | 0.00051291 | 0.00024424
2013-02-06 | 508:82578 | SHORT RURAL | Planned Outage | 934326 | 34 | 370 | 12580 | 0.0076817 | 0.0020761
2013-02-06 | 238:34141 | SHORT RURAL | Planned Outage | 934364 | 15 | 235 | 3525 | 0.0021525 | 0.00091594
2013-02-06 | 512:48048 | SHORT RURAL | Planned Outage | 934370 | 43 | 265 | 11395 | 0.0069581 | 0.0026257
2013-02-06 | 264:81240 | SHORT RURAL | Planned Outage | 934375 | 213 | 270 | 57510 | 0.035117 | 0.013006
2013-02-06 | 224:80337 | URBAN | Planned Outage | 934379 | 1 | 370 | 370 | 0.00022593 | 6.1063e-05
2013-02-06 | 227:13015 | SHORT RURAL | Planned Outage | 934381 | 4 | 240 | 960 | 0.0005862 | 0.00024425
2013-02-06 | 515:35197 | LONG RURAL | Planned Outage | 934398 | 6 | 310 | 1860 | 0.0011358 | 0.00036638
2013-02-06 | 813:89062 | SHORT RURAL | Planned Outage | 934404 | 33 | 412 | 13596 | 0.0083021 | 0.0020151
2013-02-06 | 813:89062 | SHORT RURAL | Planned Outage | 934539 | 65 | 390 | 25350 | 0.015479 | 0.0039691
2013-02-07 | 508:82578 | SHORT RURAL | Planned Outage | 934718 | 7 | 350 | 2450 | 0.0014961 | 0.00042745
2013-02-07 | 806:74080 | SHORT RURAL | Planned Outage | 934723 | 6 | 1 | 6 | 3.6638e-06 | 0.00036638
2013-02-07 | 514:18137 | SHORT RURAL | Planned Outage | 934730 | 28 | 200 | 5600 | 0.0034196 | 0.0017098
2013-02-04 | ZN15009:PA1 | URBAN | Planned Outage | 935651 | 110 | 90 | 9900 | 0.006045 | 0.0067166
2013-02-04 | ZN12570:PA25 | SHORT RURAL | Planned Outage | 935702 | 524 | 480 | 251520 | 0.15358 | 0.031996
2013-02-04 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 935755 | 166 | 480 | 79680 | 0.048653 | 0.010136
2013-02-04 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935760 | 8 | 105 | 840 | 0.00051291 | 0.00048848
2013-02-04 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935761 | 2 | 45 | 90 | 5.4954e-05 | 0.00012212
2013-02-04 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935763 | 13 | 180 | 2340 | 0.0014288 | 0.00079378
2013-02-05 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935776 | 2 | 120 | 240 | 0.00014655 | 0.00012212
2013-02-05 | ZN12610:PA18 | URBAN | Planned Outage | 935779 | 90 | 480 | 43200 | 0.026379 | 0.0054956
2013-02-05 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 935781 | 1 | 480 | 480 | 0.0002931 | 6.1062e-05
2013-02-05 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935784 | 4 | 120 | 480 | 0.0002931 | 0.00024425
2013-02-05 | ZN12570:PA41 | URBAN | Planned Outage | 935785 | 58 | 360 | 20880 | 0.01275 | 0.0035416
2013-02-05 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935790 | 5 | 120 | 600 | 0.00036637 | 0.00030531
2013-02-05 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935800 | 19 | 120 | 2280 | 0.0013922 | 0.0011602
2013-02-05 | ZN195:PA3 | URBAN | Planned Outage | 935801 | 74 | 720 | 53280 | 0.032534 | 0.0045186
2013-02-06 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935805 | 2 | 120 | 240 | 0.00014655 | 0.00012213
2013-02-06 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 935808 | 4 | 480 | 1920 | 0.0011724 | 0.00024425
2013-02-06 | ZN12610:PA18 | URBAN | Planned Outage | 935810 | 2 | 480 | 960 | 0.0005862 | 0.00012213
2013-02-06 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 935812 | 3 | 480 | 1440 | 0.0008793 | 0.00018319
2013-02-06 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 935814 | 5 | 480 | 2400 | 0.0014655 | 0.00030531
2013-02-06 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935816 | 3 | 120 | 360 | 0.00021983 | 0.00018319
2013-02-06 | ZN167:PA10 | URBAN | Planned Outage | 935817 | 71 | 390 | 27690 | 0.016908 | 0.0043355
2013-02-06 | ZN167:PA10 | URBAN | Planned Outage | 935818 | 44 | 390 | 17160 | 0.010478 | 0.0026868
2013-02-06 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 935820 | 8 | 300 | 2400 | 0.0014655 | 0.0004885
2013-02-06 | ZN2473:PA20 | URBAN | Planned Outage | 935824 | 71 | 360 | 25560 | 0.015608 | 0.0043355
2013-02-06 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935826 | 1 | 120 | 120 | 7.3275e-05 | 6.1063e-05
2013-02-06 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935831 | 1 | 120 | 120 | 7.3275e-05 | 6.1063e-05
2013-02-06 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 935836 | 3 | 150 | 450 | 0.00027478 | 0.00018319
2013-02-07 | 511:29878 | SHORT RURAL | Planned Outage | 936270 | 209 | 420 | 87780 | 0.053602 | 0.012762
2013-02-07 | 235:2120 | SHORT RURAL | Planned Outage | 936271 | 16 | 305 | 4880 | 0.0029799 | 0.00097702
2013-02-07 | 806:74076 | SHORT RURAL | Planned Outage | 936288 | 7 | 495 | 3465 | 0.0021159 | 0.00042745
2013-02-07 | 508:82578 | SHORT RURAL | Planned Outage | 936292 | 5 | 410 | 2050 | 0.0012518 | 0.00030532
2013-02-07 | 261:81864 | URBAN | Planned Outage | 936304 | 310 | 310 | 96100 | 0.058682 | 0.01893
2013-02-04 | 504:48031 | SHORT RURAL | Planned Outage | 936315 | 2 | 4800 | 9600 | 0.0058618 | 0.00012212
2013-02-07 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 937000 | 14 | 510 | 5040 | 0.0030776 | 0.00085489
2013-02-07 | ZN9252:PA10 | URBAN | Planned Outage | 937076 | 139 | 480 | 66720 | 0.040742 | 0.0084879
2013-02-07 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 937078 | 7 | 480 | 3360 | 0.0020517 | 0.00042745
2013-02-07 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 937088 | 23 | 480 | 11040 | 0.0067414 | 0.0014045
2013-02-08 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 937098 | 28 | 480 | 13440 | 0.008207 | 0.0017098
2013-02-08 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 937100 | 6 | 480 | 2880 | 0.0017587 | 0.00036639
2013-02-12 | 216:10727 | URBAN | Planned Outage | 937454 | 4 | 360 | 1440 | 0.00087935 | 0.00024426
2013-02-12 | 504:48026 | SHORT RURAL | Planned Outage | 937457 | 63 | 107 | 6741 | 0.0041164 | 0.0038471
2013-02-12 | 508:82578 | SHORT RURAL | Planned Outage | 937459 | 7 | 360 | 2520 | 0.0015389 | 0.00042746
2013-02-12 | 511:29878 | SHORT RURAL | Planned Outage | 937460 | 1 | 132 | 132 | 8.0607e-05 | 6.1066e-05
2013-02-08 | 526:34640 | SHORT RURAL | Planned Outage | 937465 | 4 | 355 | 1420 | 0.00086711 | 0.00024426
2013-02-10 | 224:80329 | SHORT RURAL | Planned Outage | 937467 | 1 | 550 | 550 | 0.00033585 | 6.1064e-05
2013-02-10 | 225:33670 | SHORT RURAL | Planned Outage | 937469 | 1 | 570 | 570 | 0.00034807 | 6.1064e-05
2013-02-08 | 238:34141 | SHORT RURAL | Planned Outage | 937471 | 8 | 397 | 3176 | 0.0019394 | 0.00048851
2013-02-08 | 238:34147 | URBAN | Planned Outage | 937475 | 6 | 105 | 630 | 0.00038471 | 0.00036639
2013-02-09 | 524:33572 | SHORT RURAL | Planned Outage | 937484 | 324 | 120 | 38880 | 0.023742 | 0.019785
2013-02-10 | 501:48125 | URBAN | Planned Outage | 937485 | 2 | 390 | 780 | 0.0004763 | 0.00012213
2013-02-08 | 807:74183 | SHORT RURAL | Planned Outage | 937487 | 4 | 120 | 480 | 0.00029311 | 0.00024426
2013-02-08 | 512:48049 | SHORT RURAL | Planned Outage | 937488 | 16 | 135 | 2160 | 0.001319 | 0.00097703
2013-02-08 | 801:74119 | URBAN | Planned Outage | 937491 | 33 | 385 | 12705 | 0.0077582 | 0.0020151
2013-02-08 | 807:74184 | SHORT RURAL | Planned Outage | 937492 | 9 | 235 | 2115 | 0.0012915 | 0.00054958
2013-02-08 | 512:48049 | SHORT RURAL | Planned Outage | 937494 | 6 | 95 | 570 | 0.00034807 | 0.00036639
2013-02-08 | 806:74080 | SHORT RURAL | Planned Outage | 937496 | 17 | 415 | 7055 | 0.0043081 | 0.0010381
2013-02-11 | 243:80083 | SHORT RURAL | Planned Outage | 937508 | 7 | 300 | 2100 | 0.0012824 | 0.00042745
2013-02-11 | 243:80083 | SHORT RURAL | Planned Outage | 937511 | 1 | 60 | 60 | 3.6639e-05 | 6.1064e-05
2013-02-11 | 501:48125 | URBAN | Planned Outage | 937512 | 155 | 355 | 55025 | 0.033601 | 0.009465
2013-02-11 | 810:74058 | SHORT RURAL | Planned Outage | 937513 | 7 | 10 | 70 | 4.2745e-05 | 0.00042745
2013-02-13 | 501:48122 | SHORT RURAL | Planned Outage | 937516 | 35 | 420 | 14700 | 0.0089767 | 0.0021373
2013-02-13 | 512:48049 | SHORT RURAL | Planned Outage | 937519 | 14 | 450 | 6300 | 0.0038472 | 0.00085493
2013-02-14 | 508:82578 | SHORT RURAL | Planned Outage | 937521 | 27 | 495 | 13365 | 0.0081615 | 0.0016488
2013-02-14 | 501:48115 | SHORT RURAL | Planned Outage | 937524 | 5 | 180 | 900 | 0.0005496 | 0.00030533
2013-02-14 | 511:29878 | SHORT RURAL | Planned Outage | 937526 | 41 | 560 | 22960 | 0.014021 | 0.0025037
2013-02-14 | 223:14397 | URBAN | Planned Outage | 937528 | 226 | 280 | 63280 | 0.038643 | 0.013801
2013-02-14 | 507:80925 | SHORT RURAL | Planned Outage | 937529 | 20 | 175 | 3500 | 0.0021373 | 0.0012213
2013-02-13 | 214:8667 | URBAN | Planned Outage | 937530 | 3 | 345 | 1035 | 0.00063204 | 0.0001832
2013-02-14 | 202:34249 | URBAN | Planned Outage | 937531 | 33 | 120 | 3960 | 0.0024182 | 0.0020152
2013-02-14 | 235:2120 | SHORT RURAL | Planned Outage | 937532 | 9 | 510 | 4590 | 0.0028029 | 0.0005496
2013-02-13 | 806:74080 | SHORT RURAL | Planned Outage | 937534 | 31 | 510 | 15810 | 0.0096546 | 0.0018931
2013-02-13 | 803:74010 | SHORT RURAL | Planned Outage | 937535 | 23 | 330 | 7590 | 0.0046349 | 0.0014045
2013-02-14 | 515:35193 | SHORT RURAL | Planned Outage | 937536 | 1 | 65 | 65 | 3.9693e-05 | 6.1066e-05
2013-02-14 | 806:74080 | SHORT RURAL | Planned Outage | 937539 | 3 | 270 | 810 | 0.00049464 | 0.0001832
2013-02-08 | ZN10991:PA7 | URBAN | Planned Outage | 937956 | 10 | 2910 | 29100 | 0.01777 | 0.00061064
2013-02-09 | ZN2473:PA34 | URBAN | Planned Outage | 937957 | 124 | 480 | 59520 | 0.036345 | 0.007572
2013-02-09 | ZN14143:PA14 | URBAN | Planned Outage | 937964 | 2 | 300 | 600 | 0.00036639 | 0.00012213
2013-02-09 | ZN35500:PA32 | URBAN | Planned Outage | 937971 | 21 | 480 | 10080 | 0.0061553 | 0.0012824
2013-02-09 | ZN2473:PA14 | URBAN | Planned Outage | 937973 | 4 | 510 | 2040 | 0.0012457 | 0.00024426
2013-02-10 | ZN2835:PA9 | URBAN | Planned Outage | 937978 | 244 | 480 | 117120 | 0.071519 | 0.0149
2013-02-11 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 937984 | 1 | 480 | 480 | 0.00029311 | 6.1064e-05
2013-02-11 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 937986 | 13 | 480 | 6240 | 0.0038104 | 0.00079384
2013-02-11 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 937986 | 1 | 480 | 480 | 0.00029311 | 6.1064e-05
2013-02-11 | ZN9118:PA24 | URBAN | Planned Outage | 937990 | 44 | 300 | 13200 | 0.0080605 | 0.0026868
2013-02-12 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 938000 | 10 | 480 | 4800 | 0.0029312 | 0.00061066
2013-02-12 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 938012 | 2 | 360 | 720 | 0.00043967 | 0.00012213
2013-02-12 | ZN2400:PA21 | URBAN | Planned Outage | 938016 | 5 | 300 | 1500 | 0.00091599 | 0.00030533
2013-02-13 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 938019 | 8 | 480 | 3840 | 0.0023449 | 0.00048853
2013-02-14 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 938024 | 7 | 480 | 3360 | 0.0020518 | 0.00042746
2013-02-14 | ZN12660:PA17 | URBAN | Planned Outage | 938043 | 271 | 450 | 121950 | 0.07447 | 0.016549
2013-02-14 | ZN10999:PA17 | URBAN | Planned Outage | 938053 | 71 | 360 | 25560 | 0.015609 | 0.0043357
2013-02-15 | ZN12620:PA2 | SHORT RURAL | Planned Outage | 938062 | 1 | 300 | 300 | 0.0001832 | 6.1067e-05
2013-02-16 | ZN35500:PA14 | URBAN | Planned Outage | 938064 | 10 | 780 | 7800 | 0.0047632 | 0.00061067
2013-02-16 | ZN1850:PA15 | URBAN | Planned Outage | 938069 | 1 | 510 | 510 | 0.00031144 | 6.1067e-05
2013-02-16 | ZN630:PA33 | URBAN | Planned Outage | 938070 | 4 | 120 | 480 | 0.00029312 | 0.00024427
2013-02-15 | 508:82578 | SHORT RURAL | Planned Outage | 938220 | 13 | 313 | 4069 | 0.0024848 | 0.00079387
2013-02-15 | 807:74179 | SHORT RURAL | Planned Outage | 938230 | 56 | 385 | 21560 | 0.013166 | 0.0034197
2013-02-15 | 231:8405 | SHORT RURAL | Planned Outage | 938238 | 14 | 120 | 1680 | 0.0010259 | 0.00085493
2013-02-16 | 807:74180 | SHORT RURAL | Planned Outage | 938241 | 7 | 220 | 1540 | 0.00094043 | 0.00042747
2013-02-15 | 229:34983 | SHORT RURAL | Planned Outage | 938246 | 1 | 90 | 90 | 5.496e-05 | 6.1067e-05
2013-02-15 | 229:34983 | SHORT RURAL | Planned Outage | 938247 | 1 | 45 | 45 | 2.748e-05 | 6.1067e-05
2013-02-17 | 221:11895 | URBAN | Planned Outage | 938250 | 5 | 405 | 2025 | 0.0012366 | 0.00030533
2013-02-15 | 502:48001 | URBAN | Planned Outage | 938256 | 274 | 300 | 82200 | 0.050197 | 0.016732
2013-02-15 | 503:48011 | SHORT RURAL | Planned Outage | 938259 | 148 | 330 | 48840 | 0.029825 | 0.0090379
2013-02-15 | 511:29878 | SHORT RURAL | Planned Outage | 938262 | 41 | 8 | 328 | 0.0002003 | 0.0025037
2013-02-15 | 508:82578 | SHORT RURAL | Planned Outage | 938272 | 119 | 508 | 60452 | 0.036916 | 0.0072669
2013-02-16 | 511:29869 | SHORT RURAL | Planned Outage | 938275 | 11 | 555 | 6105 | 0.0037281 | 0.00067173
2013-02-15 | 515:35197 | LONG RURAL | Planned Outage | 938280 | 2 | 75 | 150 | 9.16e-05 | 0.00012213
2013-02-15 | 810:74054 | LONG RURAL | Planned Outage | 938282 | 1 | 330 | 330 | 0.00020152 | 6.1067e-05
2013-02-15 | 806:74080 | SHORT RURAL | Planned Outage | 938283 | 1 | 4355 | 4355 | 0.0026594 | 6.1067e-05
2013-02-15 | 806:74080 | SHORT RURAL | Planned Outage | 938285 | 1 | 34 | 34 | 2.0763e-05 | 6.1067e-05
2013-02-16 | 807:74180 | SHORT RURAL | Planned Outage | 938287 | 3 | 140 | 420 | 0.00025648 | 0.0001832
2013-02-18 | 224:80337 | URBAN | Planned Outage | 938471 | 2 | 550 | 1100 | 0.00067173 | 0.00012213
2013-02-18 | 511:29878 | SHORT RURAL | Planned Outage | 938474 | 1 | 310 | 310 | 0.00018931 | 6.1067e-05
2013-02-18 | 513:48059 | SHORT RURAL | Planned Outage | 938477 | 1 | 165 | 165 | 0.00010076 | 6.1067e-05
2013-02-18 | 811:74234 | SHORT RURAL | Planned Outage | 938481 | 1 | 190 | 190 | 0.00011603 | 6.1067e-05
2013-02-18 | 512:48049 | SHORT RURAL | Planned Outage | 938489 | 4 | 52 | 208 | 0.00012702 | 0.00024427
2013-02-19 | ZN12660:PA14 | SHORT RURAL | Planned Outage | 938494 | 243 | 480 | 116640 | 0.071223 | 0.014838
2013-02-18 | ZN12610:PA9 | SHORT RURAL | Planned Outage | 938831 | 97 | 60 | 5820 | 0.0035541 | 0.0059235
2013-02-18 | ZN2568:PA8 | URBAN | Planned Outage | 938836 | 1 | 1890 | 1890 | 0.0011542 | 6.1067e-05
2013-02-20 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 938844 | 3 | 480 | 1440 | 0.00087943 | 0.00018321
2013-02-18 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 938847 | 22 | 510 | 11220 | 0.0068517 | 0.0013435
2013-02-18 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 938852 | 3 | 480 | 1440 | 0.00087936 | 0.0001832
2013-02-18 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 938857 | 13 | 480 | 6240 | 0.0038106 | 0.00079387
2013-02-19 | 801:74121 | SHORT RURAL | Planned Outage | 938874 | 35 | 346 | 12110 | 0.0073946 | 0.0021372
2013-02-19 | 526:34639 | SHORT RURAL | Planned Outage | 938877 | 4 | 494 | 1976 | 0.0012066 | 0.00024425
2013-02-18 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 938881 | 166 | 480 | 79680 | 0.048658 | 0.010137
2013-02-19 | 526:34636 | SHORT RURAL | Planned Outage | 938883 | 9 | 525 | 4725 | 0.0028852 | 0.00054956
2013-02-19 | 508:82578 | SHORT RURAL | Planned Outage | 938885 | 41 | 420 | 17220 | 0.010515 | 0.0025035
2013-02-18 | ZN12640:PA18 | SHORT RURAL | Planned Outage | 938897 | 107 | 480 | 51360 | 0.031364 | 0.0065341
2013-02-18 | ZN10999:PA12 | URBAN | Planned Outage | 938904 | 57 | 300 | 17100 | 0.010442 | 0.0034808
2013-02-19 | 512:48048 | SHORT RURAL | Planned Outage | 938911 | 14 | 350 | 4900 | 0.002992 | 0.00085487
2013-02-19 | 515:35197 | LONG RURAL | Planned Outage | 938923 | 1 | 55 | 55 | 3.3584e-05 | 6.1062e-05
2013-02-19 | 813:89055 | SHORT RURAL | Planned Outage | 938931 | 2 | 425 | 850 | 0.00051903 | 0.00012212
2013-02-19 | 523:33501 | SHORT RURAL | Planned Outage | 938934 | 2 | 145 | 290 | 0.00017708 | 0.00012212
2013-02-19 | 810:74050 | SHORT RURAL | Planned Outage | 938938 | 2 | 160 | 320 | 0.0001954 | 0.00012212
2013-02-19 | 513:48056 | SHORT RURAL | Planned Outage | 938942 | 13 | 215 | 2795 | 0.0017067 | 0.00079381
2013-02-19 | 813:89055 | SHORT RURAL | Planned Outage | 938946 | 5 | 75 | 375 | 0.00022898 | 0.00030531
2013-02-19 | 509:48039 | LONG RURAL | Planned Outage | 938950 | 2 | 80 | 160 | 9.7699e-05 | 0.00012212
2013-02-19 | 813:89055 | SHORT RURAL | Planned Outage | 938952 | 3 | 85 | 255 | 0.00015571 | 0.00018319
2013-02-07 | 806:74080 | SHORT RURAL | Planned Outage | 938995 | 216 | 495 | 106920 | 0.065289 | 0.01319
2013-02-20 | 258:80787 | URBAN | Planned Outage | 939476 | 1 | 185 | 185 | 0.00011298 | 6.1071e-05
2013-02-20 | 224:80341 | URBAN | Planned Outage | 939477 | 28 | 15 | 420 | 0.0002565 | 0.00171
2013-02-20 | 232:11455 | URBAN | Planned Outage | 939525 | 324 | 295 | 95580 | 0.058372 | 0.019787
2013-02-20 | 232:11457 | URBAN | Planned Outage | 939527 | 62 | 345 | 21390 | 0.013063 | 0.0037864
2013-02-20 | 504:48026 | SHORT RURAL | Planned Outage | 939528 | 63 | 315 | 19845 | 0.01212 | 0.0038475
2013-02-20 | 501:48123 | SHORT RURAL | Planned Outage | 939529 | 73 | 420 | 30660 | 0.018724 | 0.0044582
2013-02-20 | 803:74007 | SHORT RURAL | Planned Outage | 939530 | 36 | 330 | 11880 | 0.0072553 | 0.0021986
2013-02-20 | 812:19072 | SHORT RURAL | Planned Outage | 939534 | 4 | 330 | 1320 | 0.00080614 | 0.00024429
2013-02-20 | 813:89061 | LONG RURAL | Planned Outage | 939536 | 9 | 330 | 2970 | 0.0018138 | 0.00054964
2013-02-20 | 810:74054 | LONG RURAL | Planned Outage | 939537 | 18 | 125 | 2250 | 0.0013741 | 0.0010993
2013-02-19 | ZN1788:PA5 | URBAN | Planned Outage | 942962 | 1 | 570 | 570 | 0.00034805 | 6.1062e-05
2013-02-19 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 942965 | 19 | 480 | 9120 | 0.0055689 | 0.0011602
2013-02-19 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 942975 | 17 | 480 | 8160 | 0.0049827 | 0.0010381
2013-02-19 | ZN12580:PA16 | URBAN | Planned Outage | 942981 | 30 | 480 | 14400 | 0.0087929 | 0.0018319
2013-02-20 | ZN2400:PA21 | URBAN | Planned Outage | 942990 | 6 | 450 | 2700 | 0.0016489 | 0.00036643
2013-02-25 | ZN15013:PA4 | URBAN | Planned Outage | 943048 | 32 | 277.3667 | 8875.7333 | 0.0054206 | 0.0019543
2013-02-20 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 943050 | 37 | 480 | 17760 | 0.010846 | 0.0022596
2013-02-20 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 943067 | 12 | 480 | 5760 | 0.0035177 | 0.00073286
2013-02-20 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 943128 | 402 | 480 | 192960 | 0.11784 | 0.024551
2013-02-20 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 943212 | 92 | 480 | 44160 | 0.026969 | 0.0056186
2013-02-20 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 943218 | 38 | 480 | 18240 | 0.011139 | 0.0023207
2013-02-20 | ZN15013:PA4 | URBAN | Planned Outage | 943251 | 1 | 240 | 240 | 0.00014657 | 6.1071e-05
2013-02-21 | ZN3288:PA41 42KLM | CBD | Planned Outage | 943258 | 7 | 360 | 2520 | 0.001539 | 0.0004275
2013-02-21 | ZN14891:PA1 | SHORT RURAL | Planned Outage | 943268 | 2 | 600 | 1200 | 0.00073286 | 0.00012214
2013-02-21 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 943288 | 4 | 480 | 1920 | 0.0011726 | 0.00024429
2013-02-21 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 943294 | 2 | 480 | 960 | 0.00058629 | 0.00012214
2013-02-21 | ZN384:PA33 | URBAN | Planned Outage | 943296 | 26 | 420 | 10920 | 0.006669 | 0.0015879
2013-02-21 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 943300 | 38 | 300 | 11400 | 0.0069622 | 0.0023207
2013-02-21 | ZN2635:PA18 | URBAN | Planned Outage | 943302 | 30 | 360 | 10800 | 0.0065957 | 0.0018322
2013-02-21 | ZN2635:PA20 | URBAN | Planned Outage | 943302 | 134 | 360 | 48240 | 0.029461 | 0.0081836
2013-02-21 | ZN35370:PA2 | SHORT RURAL | Planned Outage | 943325 | 21 | 90 | 1890 | 0.0011543 | 0.0012825
2013-02-22 | ZN12570:PA37 | SHORT RURAL | Planned Outage | 943332 | 3 | 450 | 1350 | 0.00082447 | 0.00018322
2013-02-22 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 943345 | 10 | 480 | 4800 | 0.0029315 | 0.00061072
2013-02-22 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 943353 | 128 | 480 | 61440 | 0.037523 | 0.0078172
2013-02-22 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 943368 | 30 | 480 | 14400 | 0.0087944 | 0.0018322
2013-02-23 | ZN1788:PA16 | URBAN | Planned Outage | 943380 | 2 | 735 | 1470 | 0.00089776 | 0.00012214
2013-02-23 | ZN4545:PA2 | URBAN | Planned Outage | 943382 | 10 | 329 | 3290 | 0.0020093 | 0.00061072
2013-02-24 | ZN3288:PA43 44DEF | CBD | Planned Outage | 943385 | 16 | 510 | 8160 | 0.0049835 | 0.00097716
2013-02-25 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 943887 | 40 | 360 | 3000 | 0.0018322 | 0.0024429
2013-02-25 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 943893 | 9 | 420 | 3780 | 0.0023085 | 0.00054965
2013-02-25 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 943900 | 3 | 480 | 1440 | 0.00087944 | 0.00018322
2013-02-25 | 232:11453 | SHORT RURAL | Planned Outage | 944589 | 2 | 310 | 620 | 0.00037865 | 0.00012214
2013-02-21 | 514:18137 | SHORT RURAL | Planned Outage | 944620 | 77 | 290 | 22330 | 0.013637 | 0.0047025
2013-02-22 | 508:82578 | SHORT RURAL | Planned Outage | 944629 | 110 | 390 | 42900 | 0.0262 | 0.0067179
2013-02-21 | 507:80932 | SHORT RURAL | Planned Outage | 944631 | 30 | 480 | 14400 | 0.0087943 | 0.0018322
2013-02-22 | 509:48039 | LONG RURAL | Planned Outage | 944633 | 27 | 210 | 5670 | 0.0034628 | 0.0016489
2013-02-22 | 511:29873 | SHORT RURAL | Planned Outage | 944635 | 10 | 216 | 2160 | 0.0013192 | 0.00061072
2013-02-21 | 813:89061 | LONG RURAL | Planned Outage | 944643 | 7 | 267 | 1869 | 0.0011414 | 0.0004275
2013-02-21 | 515:35192 | SHORT RURAL | Planned Outage | 944647 | 1 | 51 | 51 | 3.1147e-05 | 6.1072e-05
2013-02-21 | 807:74179 | SHORT RURAL | Planned Outage | 944650 | 25 | 98 | 2450 | 0.0014963 | 0.0015268
2013-02-21 | 810:74054 | LONG RURAL | Planned Outage | 944653 | 1 | 90 | 90 | 5.4965e-05 | 6.1072e-05
2013-02-21 | 810:74054 | LONG RURAL | Planned Outage | 944660 | 1 | 85 | 85 | 5.1911e-05 | 6.1072e-05
2013-02-22 | 806:74080 | SHORT RURAL | Planned Outage | 944664 | 5 | 230 | 1150 | 0.00070233 | 0.00030536
2013-02-22 | 806:74076 | SHORT RURAL | Planned Outage | 944666 | 3 | 50 | 150 | 9.1608e-05 | 0.00018322
2013-02-22 | 810:74058 | SHORT RURAL | Planned Outage | 944673 | 13 | 360 | 4680 | 0.0028582 | 0.00079394
2013-02-22 | 807:74180 | SHORT RURAL | Planned Outage | 944679 | 3 | 190 | 570 | 0.00034811 | 0.00018322
2013-02-25 | 224:80340 | SHORT RURAL | Planned Outage | 944680 | 1 | 185 | 185 | 0.00011298 | 6.1072e-05
2013-02-25 | 208:74 | URBAN | Planned Outage | 944688 | 3 | 455 | 1365 | 0.00083364 | 0.00018322
2013-02-25 | 202:34250 | URBAN | Planned Outage | 944690 | 56 | 110 | 6160 | 0.003762 | 0.00342
2013-02-25 | 264:81240 | SHORT RURAL | Planned Outage | 944695 | 9 | 360 | 3240 | 0.0019787 | 0.00054965
2013-02-26 | 504:48031 | SHORT RURAL | Planned Outage | 944699 | 20 | 40 | 800 | 0.00048859 | 0.0012215
2013-02-26 | 229:34995 | SHORT RURAL | Planned Outage | 944714 | 28 | 110 | 3080 | 0.0018811 | 0.0017101
2013-02-26 | 242:81538 | URBAN | Planned Outage | 944717 | 205 | 490 | 100450 | 0.061348 | 0.01252
2013-02-26 | 264:81240 | SHORT RURAL | Planned Outage | 944719 | 15 | 340 | 5100 | 0.0031147 | 0.0009161
2013-02-26 | ZN2466:PA44 | URBAN | Planned Outage | 944919 | 7 | 510 | 3570 | 0.0021803 | 0.00042751
2013-02-26 | ZN13000:PA10 | URBAN | Planned Outage | 944929 | 554 | 480 | 73560 | 0.044925 | 0.033835
2013-02-26 | ZN36300:PA11 | URBAN | Planned Outage | 944934 | 139 | 480 | 66720 | 0.040748 | 0.0084892
2013-02-28 | ZN3472:PA32 | SHORT RURAL | Planned Outage | 945094 | 23 | 450 | 10350 | 0.0063212 | 0.0014047
2013-02-27 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 945126 | 50 | 540 | 27000 | 0.01649 | 0.0030537
2013-02-27 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 945130 | 18 | 480 | 7800 | 0.0047638 | 0.0010993
2013-02-27 | ZN874:PA7 | URBAN | Planned Outage | 945146 | 3 | 210 | 630 | 0.00038477 | 0.00018322
2013-02-27 | ZN12690:PA16 | SHORT RURAL | Planned Outage | 945148 | 51 | 480 | 24480 | 0.014951 | 0.0031148
2013-02-27 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 945235 | 5 | 480 | 2400 | 0.0014658 | 0.00030537
2013-02-27 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 945248 | 10 | 480 | 4800 | 0.0029315 | 0.00061074
2013-02-27 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 945252 | 9 | 480 | 4320 | 0.0026384 | 0.00054967
2013-02-27 | ZN847:PA22 | SHORT RURAL | Planned Outage | 945256 | 1 | 330 | 330 | 0.00020154 | 6.1074e-05
2013-02-27 | 240:34852 | URBAN | Planned Outage | 945291 | 55 | 570 | 31350 | 0.019147 | 0.0033591
2013-02-27 | 260:33344 | URBAN | Planned Outage | 945295 | 2 | 300 | 600 | 0.00036644 | 0.00012215
2013-02-27 | 229:34983 | SHORT RURAL | Planned Outage | 945305 | 125 | 375 | 46875 | 0.028628 | 0.0076342
2013-02-27 | 238:34141 | SHORT RURAL | Planned Outage | 945308 | 21 | 345 | 7245 | 0.0044248 | 0.0012826
2013-02-27 | 513:48058 | URBAN | Planned Outage | 945312 | 85 | 345 | 29325 | 0.01791 | 0.0051913
2013-02-27 | 513:48059 | SHORT RURAL | Planned Outage | 945314 | 85 | 345 | 29325 | 0.01791 | 0.0051913
2013-02-27 | 813:89062 | SHORT RURAL | Planned Outage | 945319 | 14 | 360 | 5040 | 0.0030781 | 0.00085503
2013-02-27 | 813:89062 | SHORT RURAL | Planned Outage | 945320 | 33 | 360 | 11880 | 0.0072556 | 0.0020154
2013-02-28 | ZN3472:PA32 | SHORT RURAL | Planned Outage | 945718 | 38 | 450 | 17100 | 0.010444 | 0.0023208
2013-02-28 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 945769 | 14 | 480 | 6720 | 0.0041042 | 0.00085504
2013-02-28 | ZN12570:PA24 | SHORT RURAL | Planned Outage | 945782 | 12 | 480 | 5760 | 0.0035179 | 0.00073289
2013-02-28 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 945785 | 1 | 480 | 480 | 0.00029316 | 6.1074e-05
2013-02-28 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 945894 | 77 | 300 | 23100 | 0.014108 | 0.0047027
2013-02-28 | ZN15013:PA10 | SHORT RURAL | Planned Outage | 945901 | 28 | 60 | 1680 | 0.001026 | 0.0017101
2013-02-28 | ZN931:PA25 | URBAN | Planned Outage | 945907 | 23 | 120 | 2760 | 0.0016857 | 0.0014047
2013-02-28 | 232:11455 | URBAN | Planned Outage | 945932 | 236 | 360 | 84960 | 0.051889 | 0.014414
2013-02-28 | 208:72 | URBAN | Planned Outage | 945937 | 40 | 302 | 12080 | 0.0073778 | 0.002443
2013-02-28 | 238:34141 | SHORT RURAL | Planned Outage | 945938 | 7 | 420 | 2940 | 0.0017956 | 0.00042752
2013-02-28 | 520:48172 | SHORT RURAL | Planned Outage | 945941 | 15 | 250 | 3750 | 0.0022903 | 0.00091611
2013-02-28 | 813:89062 | SHORT RURAL | Planned Outage | 945944 | 54 | 300 | 16200 | 0.009894 | 0.003298
2013-03-02 | ZN1600:PA22ABC | CBD | Planned Outage | 947746 | 1 | 360 | 360 | 0.00021987 | 6.1075e-05
2013-03-02 | ZN15005:PA6 | URBAN | Planned Outage | 947748 | 1 | 600 | 600 | 0.00036645 | 6.1075e-05
2013-03-02 | ZN4545:PA19 | URBAN | Planned Outage | 947749 | 2 | 600 | 1200 | 0.0007329 | 0.00012215
2013-03-02 | ZN2196:PA17 | URBAN | Planned Outage | 947754 | 2 | 60 | 120 | 7.329e-05 | 0.00012215
2013-03-02 | ZN14891:PA6 | URBAN | Planned Outage | 947825 | 9 | 240 | 2160 | 0.0013192 | 0.00054967
2013-03-02 | ZN12650:PA14 | URBAN | Planned Outage | 947839 | 1 | 240 | 240 | 0.00014658 | 6.1075e-05
2013-03-03 | ZN188:PA2 | URBAN | Planned Outage | 947846 | 3 | 80 | 240 | 0.00014658 | 0.00018322
2013-03-03 | ZN12650:PA14 | URBAN | Planned Outage | 947848 | 1 | 240 | 240 | 0.00014658 | 6.1075e-05
2013-03-04 | 224:80337 | URBAN | Planned Outage | 947898 | 56 | 510 | 28560 | 0.017443 | 0.0034202
2013-03-04 | ZN12610:PA9 | SHORT RURAL | Planned Outage | 948141 | 97 | 60 | 5820 | 0.0035546 | 0.0059243
2013-03-04 | ZN14143:PA5 | URBAN | Planned Outage | 948150 | 1 | 480 | 480 | 0.00029316 | 6.1075e-05
2013-03-05 | 220:8688 | URBAN | Planned Outage | 948152 | 264 | 45 | 11880 | 0.0072518 | 0.016115
2013-03-04 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 948153 | 2 | 480 | 960 | 0.00058632 | 0.00012215
2013-03-05 | 220:8692 | URBAN | Planned Outage | 948158 | 198 | 20 | 3960 | 0.0024173 | 0.012086
2013-03-04 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 948168 | 18 | 480 | 8640 | 0.0052769 | 0.0010993
2013-03-05 | 261:81864 | URBAN | Planned Outage | 948171 | 92 | 375 | 34500 | 0.021059 | 0.0056159
2013-03-05 | 803:74007 | SHORT RURAL | Planned Outage | 948172 | 7 | 605 | 4235 | 0.0025851 | 0.00042729
2013-03-04 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 948174 | 19 | 480 | 9120 | 0.00557 | 0.0011604
2013-03-04 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 948179 | 16 | 480 | 7680 | 0.0046906 | 0.0009772
2013-03-04 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 948186 | 2 | 480 | 960 | 0.00058632 | 0.00012215
2013-03-04 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 948191 | 2 | 480 | 960 | 0.00058632 | 0.00012215
2013-03-04 | ZN2473:PA20 | URBAN | Planned Outage | 948197 | 71 | 360 | 25560 | 0.015611 | 0.0043363
2013-03-04 | ZN2466:PA16 | URBAN | Planned Outage | 948198 | 20 | 210 | 4200 | 0.0025651 | 0.0012215
2013-03-05 | ZN12610:PA9 | SHORT RURAL | Planned Outage | 948512 | 98 | 60 | 5880 | 0.0035893 | 0.0059821
2013-03-05 | ZN12660:PA14 | SHORT RURAL | Planned Outage | 948527 | 155 | 510 | 79050 | 0.048254 | 0.0094615
2013-03-05 | ZN12640:PA18 | SHORT RURAL | Planned Outage | 948533 | 108 | 480 | 51840 | 0.031644 | 0.0065925
2013-03-05 | ZN2466:PA41 | URBAN | Planned Outage | 948542 | 18 | 540 | 9720 | 0.0059333 | 0.0010988
2013-03-06 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 948543 | 6 | 420 | 360 | 0.00021975 | 0.00036625
2013-03-06 | ZN4545:PA2 | URBAN | Planned Outage | 948551 | 10 | 300 | 3000 | 0.0018313 | 0.00061042
2013-03-06 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 948558 | 3 | 300 | 900 | 0.00054938 | 0.00018313
2013-03-06 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 948561 | 8 | 480 | 3840 | 0.002344 | 0.00048834
2013-03-06 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 948567 | 7 | 480 | 3360 | 0.002051 | 0.0004273
2013-03-06 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 948567 | 8 | 480 | 3840 | 0.002344 | 0.00048834
2013-03-06 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 948573 | 128 | 480 | 61440 | 0.037505 | 0.0078134
2013-03-06 | ZN12650:PA13 | SHORT RURAL | Planned Outage | 948575 | 9 | 360 | 3240 | 0.0019778 | 0.00054938
2013-03-06 | ZN342:PA16 | URBAN | Planned Outage | 948577 | 187 | 20 | 3740 | 0.002283 | 0.011415
2013-03-06 | 213:33777 | SHORT RURAL | Planned Outage | 948718 | 6 | 570 | 3420 | 0.0020877 | 0.00036625
2013-03-06 | 243:80083 | SHORT RURAL | Planned Outage | 948725 | 3 | 330 | 990 | 0.00060432 | 0.00018313
2013-03-06 | 511:29878 | SHORT RURAL | Planned Outage | 948729 | 2 | 160 | 320 | 0.00019534 | 0.00012208
2013-03-06 | 813:89061 | LONG RURAL | Planned Outage | 948731 | 1 | 95 | 95 | 5.799e-05 | 6.1042e-05
2013-03-06 | 803:74010 | SHORT RURAL | Planned Outage | 948732 | 32 | 95 | 3040 | 0.0018557 | 0.0019534
2013-03-07 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 949572 | 12 | 480 | 5760 | 0.0035161 | 0.00073251
2013-03-07 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 949573 | 14 | 480 | 6720 | 0.0041021 | 0.0008546
2013-03-07 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 949578 | 11 | 480 | 5280 | 0.0032231 | 0.00067147
2013-03-07 | ZN12650:PA12 | URBAN | Planned Outage | 949587 | 96 | 330 | 31680 | 0.019338 | 0.0058601
2013-03-07 | ZN12660:PA10 | SHORT RURAL | Planned Outage | 949587 | 45 | 330 | 14850 | 0.0090648 | 0.0027469
2013-03-07 | ZN14144:PA7 | SHORT RURAL | Planned Outage | 949593 | 1 | 180 | 180 | 0.00010988 | 6.1043e-05
2013-03-09 | ZN14143:PA14 | URBAN | Planned Outage | 949614 | 2 | 570 | 1140 | 0.0006959 | 0.00012209
2013-03-09 | ZN1290:PA17 | URBAN | Planned Outage | 949619 | 4 | 570 | 2280 | 0.0013918 | 0.00024418
2013-03-09 | ZN1290:PA17 | URBAN | Planned Outage | 949622 | 6 | 120 | 720 | 0.00043952 | 0.00036626
2013-03-09 | 234:2001 | URBAN | Planned Outage | 949741 | 362 | 150 | 54300 | 0.033147 | 0.022098
2013-03-10 | 265:81651 | URBAN | Planned Outage | 949746 | 68 | 500 | 34000 | 0.020755 | 0.004151
2013-03-07 | 229:34995 | SHORT RURAL | Planned Outage | 949747 | 62 | 420 | 26040 | 0.015896 | 0.0037846
2013-03-07 | 243:80075 | SHORT RURAL | Planned Outage | 949750 | 14 | 385 | 5390 | 0.0032902 | 0.0008546
2013-03-09 | 227:13014 | SHORT RURAL | Planned Outage | 949751 | 51 | 275 | 14025 | 0.0085614 | 0.0031132
2013-03-10 | 224:80341 | URBAN | Planned Outage | 949752 | 1 | 720 | 720 | 0.00043952 | 6.1044e-05
2013-03-07 | 526:34636 | SHORT RURAL | Planned Outage | 949754 | 15 | 454 | 6810 | 0.004157 | 0.00091564
2013-03-07 | 238:34151 | URBAN | Planned Outage | 949758 | 124 | 240 | 29760 | 0.018166 | 0.0075693
2013-03-08 | 504:48026 | SHORT RURAL | Planned Outage | 949764 | 4 | 285 | 1140 | 0.0006959 | 0.00024418
2013-03-08 | 524:33570 | SHORT RURAL | Planned Outage | 949768 | 13 | 370 | 4810 | 0.0029362 | 0.00079357
2013-03-09 | 502:48010 | SHORT RURAL | Planned Outage | 949782 | 104 | 400 | 41600 | 0.025394 | 0.0063486
2013-03-07 | 801:74122 | URBAN | Planned Outage | 949786 | 49 | 175 | 8575 | 0.0052344 | 0.0029911
2013-03-09 | 810:74050 | SHORT RURAL | Planned Outage | 949787 | 1 | 142 | 142 | 8.6682e-05 | 6.1044e-05
2013-03-10 | 801:74118 | URBAN | Planned Outage | 949794 | 57 | 235 | 13395 | 0.0081768 | 0.0034795
2013-03-11 | 264:81236 | URBAN | Planned Outage | 949994 | 88 | 283 | 24904 | 0.015202 | 0.0053719
2013-03-11 | ZN180:PA7 | URBAN | Planned Outage | 950446 | 67 | 600 | 40200 | 0.02454 | 0.0040899
2013-03-11 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 950463 | 69 | 510 | 35190 | 0.021481 | 0.004212
2013-03-11 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 950465 | 16 | 480 | 7680 | 0.0046882 | 0.0009767
2013-03-11 | ZN2196:PA20 | URBAN | Planned Outage | 950472 | 2 | 60 | 120 | 7.3253e-05 | 0.00012209
2013-03-12 | 243:80080 | SHORT RURAL | Planned Outage | 950493 | 6 | 145 | 870 | 0.00053096 | 0.00036618
2013-03-12 | 511:29878 | SHORT RURAL | Planned Outage | 950495 | 49 | 368 | 18032 | 0.011005 | 0.0029905
2013-03-12 | 509:48040 | SHORT RURAL | Planned Outage | 950503 | 4 | 285 | 1140 | 0.00069574 | 0.00024412
2013-03-12 | 509:48040 | SHORT RURAL | Planned Outage | 950504 | 96 | 266 | 25536 | 0.015585 | 0.0058589
2013-03-12 | 526:34636 | SHORT RURAL | Planned Outage | 950505 | 1 | 370 | 370 | 0.00022581 | 6.103e-05
2013-03-12 | 501:48115 | SHORT RURAL | Planned Outage | 950506 | 59 | 90 | 5310 | 0.0032407 | 0.0036008
2013-03-12 | ZN12600:PA9 | SHORT RURAL | Planned Outage | 950526 | 146 | 420 | 61320 | 0.037423 | 0.0089104
2013-03-12 | 512:48049 | SHORT RURAL | Planned Outage | 950527 | 7 | 56 | 392 | 0.00023924 | 0.00042721
2013-03-12 | 512:48049 | SHORT RURAL | Planned Outage | 950534 | 9 | 95 | 855 | 0.00052181 | 0.00054927
2013-03-12 | ZN14892:PA6 | SHORT RURAL | Planned Outage | 950535 | 3 | 240 | 720 | 0.00043941 | 0.00018309
2013-03-12 | 810:74058 | SHORT RURAL | Planned Outage | 950544 | 6 | 305 | 1830 | 0.0011168 | 0.00036618
2013-03-12 | 512:48049 | SHORT RURAL | Planned Outage | 950546 | 10 | 60 | 600 | 0.00036618 | 0.0006103
2013-02-18 | 504:48031 | SHORT RURAL | Planned Outage | 950599 | 2 | 3370 | 6740 | 0.0041159 | 0.00012213
2013-03-13 | 264:81244 | URBAN | Planned Outage | 950878 | 419 | 247 | 103493 | 0.063162 | 0.025572
2013-03-13 | 504:48031 | SHORT RURAL | Planned Outage | 950884 | 139 | 491 | 68249 | 0.041653 | 0.0084833
2013-03-13 | 511:29878 | SHORT RURAL | Planned Outage | 950887 | 2 | 505 | 1010 | 0.00061641 | 0.00012206
2013-03-13 | 238:34141 | SHORT RURAL | Planned Outage | 950889 | 13 | 265 | 3445 | 0.0021025 | 0.0007934
2013-03-13 | 801:74122 | URBAN | Planned Outage | 950892 | 68 | 285 | 19380 | 0.011828 | 0.0041501
2013-03-13 | 801:74121 | SHORT RURAL | Planned Outage | 950904 | 1 | 285 | 285 | 0.00017394 | 6.1031e-05
2013-03-15 | 507:80932 | SHORT RURAL | Planned Outage | 951226 | 219 | 290 | 63510 | 0.038761 | 0.013366
2013-03-15 | 504:48031 | SHORT RURAL | Planned Outage | 951240 | 6 | 290 | 1740 | 0.001062 | 0.00036619
2013-03-13 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 951391 | 23 | 510 | 11730 | 0.0071589 | 0.0014037
2013-03-13 | ZN14143:PA10 | SHORT RURAL | Planned Outage | 951403 | 24 | 510 | 12240 | 0.0074702 | 0.0014647
2013-03-13 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 951407 | 32 | 510 | 16320 | 0.0099602 | 0.001953
2013-03-13 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 951417 | 9 | 480 | 4320 | 0.0026365 | 0.00054928
2013-03-13 | ZN13000:PA11 | URBAN | Planned Outage | 951419 | 2 | 480 | 960 | 0.00058589 | 0.00012206
2013-03-13 | ZN14892:PA6 | SHORT RURAL | Planned Outage | 951424 | 60 | 450 | 27000 | 0.016478 | 0.0036618
2013-03-13 | ZN180:PA17 | URBAN | Planned Outage | 951428 | 80 | 450 | 36000 | 0.021971 | 0.0048825
2013-03-16 | 501:48125 | URBAN | Planned Outage | 951548 | 155 | 500 | 77500 | 0.0473 | 0.0094599
2013-03-16 | 264:81241 | SHORT RURAL | Planned Outage | 951561 | 324 | 255 | 82620 | 0.050424 | 0.019774
2013-03-17 | 511:29880 | URBAN | Planned Outage | 952069 | 2 | 320 | 640 | 0.0003906 | 0.00012206
2013-03-17 | 523:33508 | SHORT RURAL | Planned Outage | 952076 | 55 | 285 | 15675 | 0.0095667 | 0.0033567
2013-03-14 | 232:11457 | URBAN | Planned Outage | 952091 | 62 | 430 | 26660 | 0.016271 | 0.0037839
2013-03-16 | 264:81236 | URBAN | Planned Outage | 952093 | 362 | 255 | 92310 | 0.056338 | 0.022093
2013-03-16 | 258:80784 | URBAN | Planned Outage | 952098 | 1 | 140 | 140 | 8.5444e-05 | 6.1032e-05
2013-03-17 | 224:80328 | URBAN | Planned Outage | 952114 | 11 | 410 | 4510 | 0.0027525 | 0.00067135
2013-03-14 | 504:48031 | SHORT RURAL | Planned Outage | 952121 | 1 | 60 | 60 | 3.6619e-05 | 6.1031e-05
2013-03-14 | 235:2120 | SHORT RURAL | Planned Outage | 952124 | 12 | 130 | 1560 | 0.00095209 | 0.00073237
2013-03-14 | 526:34639 | SHORT RURAL | Planned Outage | 952126 | 4 | 420 | 1680 | 0.0010253 | 0.00024412
2013-03-14 | 526:34636 | SHORT RURAL | Planned Outage | 952128 | 9 | 450 | 4050 | 0.0024718 | 0.00054928
2013-03-14 | 523:33501 | SHORT RURAL | Planned Outage | 952141 | 1 | 100 | 100 | 6.1031e-05 | 6.1031e-05
2013-03-14 | 512:48049 | SHORT RURAL | Planned Outage | 952145 | 14 | 295 | 4130 | 0.0025206 | 0.00085444
2013-03-15 | 810:74054 | LONG RURAL | Planned Outage | 952146 | 3 | 310 | 930 | 0.00056759 | 0.0001831
2013-03-16 | 516:48066 | SHORT RURAL | Planned Outage | 952153 | 2 | 355 | 710 | 0.00043333 | 0.00012206
2013-03-18 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 952191 | 1 | 181.3667 | 181.3667 | 0.00011069 | 6.1032e-05
2013-03-19 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 952454 | 97 | 480 | 36480 | 0.022265 | 0.0059202
2013-03-05 | ZN1788:PA11 | URBAN | Planned Outage | 952642 | 1 | 20370 | 20370 | 0.012434 | 6.1042e-05
2013-03-14 | ZN10999:PA29 | URBAN | Planned Outage | 952647 | 76 | 120 | 9120 | 0.005566 | 0.0046384
2013-03-14 | ZN195:PA25 | URBAN | Planned Outage | 952649 | 2 | 480 | 960 | 0.0005859 | 0.00012206
2013-03-14 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 952664 | 27 | 420 | 11340 | 0.0069209 | 0.0016478
2013-03-14 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 952670 | 12 | 480 | 5760 | 0.0035154 | 0.00073237
2013-03-14 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 952677 | 13 | 480 | 6240 | 0.0038083 | 0.00079341
2013-03-14 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 952683 | 128 | 480 | 61440 | 0.037498 | 0.007812
2013-03-14 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 952686 | 2 | 480 | 960 | 0.0005859 | 0.00012206
2013-03-15 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 952695 | 35 | 480 | 16800 | 0.010253 | 0.0021361
2013-03-15 | ZN2635:PA20 | URBAN | Planned Outage | 952757 | 134 | 480 | 64320 | 0.039256 | 0.0081782
2013-03-15 | ZN12650:PA13 | SHORT RURAL | Planned Outage | 952783 | 6 | 450 | 2700 | 0.0016479 | 0.00036619
2013-03-15 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 952788 | 40 | 300 | 2640 | 0.0016112 | 0.0024413
2013-03-17 | ZN2635:PA28 | URBAN | Planned Outage | 952814 | 3 | 275 | 825 | 0.00050351 | 0.0001831
2013-03-17 | ZN2835:PA9 | URBAN | Planned Outage | 952818 | 244 | 480 | 117120 | 0.07148 | 0.014892
2013-03-17 | ZN847:PA29 | URBAN | Planned Outage | 952819 | 314 | 375 | 117750 | 0.071865 | 0.019164
2013-03-19 | 264:81240 | SHORT RURAL | Planned Outage | 952851 | 15 | 1660 | 24900 | 0.015197 | 0.00091549
2013-03-18 | 260:33344 | URBAN | Planned Outage | 952855 | 1 | 75 | 75 | 4.5774e-05 | 6.1032e-05
2013-03-18 | 260:33344 | URBAN | Planned Outage | 952856 | 1 | 90 | 90 | 5.4929e-05 | 6.1032e-05
2013-03-18 | 229:34983 | SHORT RURAL | Planned Outage | 952859 | 1 | 510 | 510 | 0.00031126 | 6.1032e-05
2013-03-19 | 225:33673 | SHORT RURAL | Planned Outage | 952879 | 5 | 535 | 2675 | 0.0016326 | 0.00030516
2013-03-19 | 243:80080 | SHORT RURAL | Planned Outage | 952882 | 63 | 180 | 11340 | 0.0069211 | 0.0038451
2013-03-19 | 502:48010 | SHORT RURAL | Planned Outage | 952886 | 104 | 355 | 36920 | 0.022533 | 0.0063474
2013-03-19 | 511:29878 | SHORT RURAL | Planned Outage | 952888 | 5 | 285 | 1425 | 0.00086972 | 0.00030516
2013-03-19 | 813:89061 | LONG RURAL | Planned Outage | 952893 | 3 | 105 | 315 | 0.00019225 | 0.0001831
2013-03-18 | ZN2635:PA18 | URBAN | Planned Outage | 953095 | 11 | 3120 | 34320 | 0.020946 | 0.00067135
2013-03-18 | ZN13000:PA2 | URBAN | Planned Outage | 953145 | 54 | 480 | 25920 | 0.015819 | 0.0032957
2013-03-18 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 953149 | 9 | 420 | 3780 | 0.002307 | 0.00054929
2013-03-18 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 953155 | 13 | 480 | 6240 | 0.0038084 | 0.00079341
2013-03-18 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 953160 | 1 | 480 | 480 | 0.00029295 | 6.1032e-05
2013-03-18 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 953164 | 52 | 480 | 24960 | 0.015234 | 0.0031736
2013-03-18 | ZN14143:PA5 | URBAN | Planned Outage | 953229 | 1 | 240 | 240 | 0.00014648 | 6.1032e-05
2013-03-18 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 953238 | 1 | 240 | 240 | 0.00014648 | 6.1032e-05
2013-03-19 | ZN2400:PA11 | SHORT RURAL | Planned Outage | 953240 | 22 | 360 | 990 | 0.00060422 | 0.0013427
2013-03-19 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 953242 | 9 | 510 | 4590 | 0.0028014 | 0.00054929
2013-03-19 | ZN630:PA35 | URBAN | Planned Outage | 953246 | 2 | 15 | 30 | 1.831e-05 | 0.00012207
2013-03-19 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 953266 | 12 | 240 | 2880 | 0.0017577 | 0.00073239
2013-03-19 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 953268 | 11 | 480 | 5280 | 0.0032225 | 0.00067136
2013-03-19 | ZN12640:PA18 | SHORT RURAL | Planned Outage | 953272 | 107 | 480 | 51360 | 0.031346 | 0.0065305
2013-03-19 | ZN12610:PA20 | SHORT RURAL | Planned Outage | 953274 | 3 | 480 | 1440 | 0.00087887 | 0.0001831
2013-03-19 | ZN847:PA47 | SHORT RURAL | Planned Outage | 953275 | 11 | 300 | 3300 | 0.0020141 | 0.00067136
2013-03-19 | ZN180:PA15 | URBAN | Planned Outage | 953276 | 40 | 420 | 16800 | 0.010253 | 0.0024413
2013-03-19 | ZN180:PA15 | URBAN | Planned Outage | 953277 | 90 | 420 | 37800 | 0.02307 | 0.0054929
2013-03-19 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 953278 | 2 | 300 | 600 | 0.0003662 | 0.00012207
2013-03-19 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 953280 | 57 | 420 | 23940 | 0.014611 | 0.0034789
2013-03-20 | ZN2835:PA9 | URBAN | Planned Outage | 953283 | 87 | 510 | 44370 | 0.027081 | 0.0053099
2013-03-20 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 953295 | 335 | 480 | 26400 | 0.016113 | 0.020446
2013-03-20 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 953311 | 15 | 480 | 7200 | 0.0043944 | 0.0009155
2013-03-20 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 953312 | 2 | 480 | 960 | 0.00058592 | 0.00012207
2013-03-20 | ZN12660:PA6 | SHORT RURAL | Planned Outage | 953316 | 82 | 480 | 39360 | 0.024023 | 0.0050047
2013-03-20 | ZN80:PA30 | URBAN | Planned Outage | 953318 | 45 | 630 | 28350 | 0.017303 | 0.0027465
2013-03-21 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 954411 | 14 | 420 | 5880 | 0.0035888 | 0.00085447
2013-03-21 | ZN2568:PA32 | URBAN | Planned Outage | 954417 | 141 | 420 | 59220 | 0.036144 | 0.0086058
2013-03-21 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 954419 | 17 | 480 | 8160 | 0.0049804 | 0.0010376
2013-03-21 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 954425 | 15 | 480 | 7200 | 0.0043944 | 0.00091551
2013-03-21 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 954428 | 45 | 300 | 13500 | 0.0082396 | 0.0027465
2013-03-21 | ZN12570:PA37 | SHORT RURAL | Planned Outage | 954430 | 3 | 480 | 1440 | 0.00087889 | 0.0001831
2013-03-21 | 258:80775 | URBAN | Planned Outage | 954432 | 54 | 180 | 9720 | 0.0059325 | 0.0032958
2013-03-21 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 954432 | 3 | 180 | 540 | 0.00032958 | 0.0001831
2013-03-20 | 504:48031 | SHORT RURAL | Planned Outage | 954445 | 208 | 390 | 81120 | 0.04951 | 0.012695
2013-03-21 | 229:34995 | SHORT RURAL | Planned Outage | 954447 | 18 | 405 | 7290 | 0.0044494 | 0.0010986
2013-03-21 | 806:82656 | LONG RURAL | Planned Outage | 954449 | 12 | 350 | 4200 | 0.0025634 | 0.00073241
2013-03-24 | 512:48048 | SHORT RURAL | Planned Outage | 954453 | 4 | 330 | 1320 | 0.00080565 | 0.00024414
2013-03-22 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 954454 | 55 | 510 | 28050 | 0.01712 | 0.0033569
2013-03-22 | ZN13000:PA5 | SHORT RURAL | Planned Outage | 954464 | 3 | 240 | 720 | 0.00043945 | 0.0001831
2013-03-22 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 954465 | 12 | 480 | 5760 | 0.0035156 | 0.00073241
2013-03-22 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 954471 | 15 | 480 | 7200 | 0.0043945 | 0.00091551
2013-03-22 | ZN12580:PA16 | URBAN | Planned Outage | 954626 | 89 | 480 | 42720 | 0.026074 | 0.005432
2013-03-22 | ZN10999:PA17 | URBAN | Planned Outage | 954627 | 107 | 360 | 38520 | 0.02351 | 0.0065307
2013-03-22 | ZN14892:PA6 | SHORT RURAL | Planned Outage | 954629 | 3 | 210 | 630 | 0.00038452 | 0.0001831
2013-03-23 | ZN8100:PA23 | URBAN | Planned Outage | 954636 | 21 | 15 | 315 | 0.00019226 | 0.0012817
2013-03-23 | ZN12690:PA17 | URBAN | Planned Outage | 954637 | 1 | 360 | 360 | 0.00021972 | 6.1034e-05
2013-03-23 | ZN3288:PA45 46GHJ | CBD | Planned Outage | 954640 | 30 | 630 | 18900 | 0.011535 | 0.001831
2013-03-23 | ZN2473:PA20 | URBAN | Planned Outage | 954646 | 1 | 360 | 360 | 0.00021972 | 6.1034e-05
2013-03-24 | ZN1290:PA12 | URBAN | Planned Outage | 954649 | 22 | 450 | 4290 | 0.0026184 | 0.0013428
2013-03-24 | ZN129:PA27 | URBAN | Planned Outage | 954652 | 1 | 300 | 300 | 0.0001831 | 6.1034e-05
2013-03-24 | ZN116:PA45 | URBAN | Planned Outage | 954653 | 13 | 600 | 7800 | 0.0047607 | 0.00079344
2013-03-24 | ZN129:PA12 | URBAN | Planned Outage | 954656 | 3 | 30 | 90 | 5.4931e-05 | 0.0001831
2013-03-25 | ZN847:PA22 | SHORT RURAL | Planned Outage | 954674 | 1 | 480 | 480 | 0.00029296 | 6.1034e-05
2013-03-25 | ZN2635:PA16 | URBAN | Planned Outage | 954676 | 222 | 450 | 99900 | 0.060973 | 0.01355
2013-03-25 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 954679 | 52 | 450 | 23400 | 0.014282 | 0.0031738
2013-03-25 | ZN874:PA25 | URBAN | Planned Outage | 954687 | 6 | 390 | 2340 | 0.0014282 | 0.00036621
2013-03-25 | ZN874:PA25 | URBAN | Planned Outage | 954689 | 24 | 390 | 9360 | 0.0057128 | 0.0014648
2013-03-20 | 243:80083 | SHORT RURAL | Planned Outage | 954727 | 107 | 420 | 44940 | 0.027428 | 0.0065306
2013-03-26 | 227:13015 | SHORT RURAL | Planned Outage | 954731 | 136 | 85 | 11560 | 0.0070517 | 0.0082961
2013-03-20 | 258:80793 | SHORT RURAL | Planned Outage | 954735 | 92 | 80 | 7360 | 0.0044921 | 0.0056151
2013-03-20 | 264:81231 | URBAN | Planned Outage | 954740 | 3 | 250 | 750 | 0.00045775 | 0.0001831
2013-03-21 | 258:80775 | URBAN | Planned Outage | 954742 | 158 | 450 | 71100 | 0.043395 | 0.0096433
2013-03-21 | 231:8415 | SHORT RURAL | Planned Outage | 954748 | 20 | 330 | 6600 | 0.0040282 | 0.0012207
2013-03-20 | 510:48164 | SHORT RURAL | Planned Outage | 954751 | 1 | 370 | 370 | 0.00022582 | 6.1033e-05
2013-03-20 | 503:48011 | SHORT RURAL | Planned Outage | 954794 | 99 | 345 | 34155 | 0.020846 | 0.0060423
2013-03-20 | 524:33580 | SHORT RURAL | Planned Outage | 954796 | 25 | 175 | 4375 | 0.0026702 | 0.0015258
2013-03-21 | 524:33572 | SHORT RURAL | Planned Outage | 954823 | 15 | 485 | 7095 | 0.0043303 | 0.00091551
2013-03-21 | 504:48031 | SHORT RURAL | Planned Outage | 954836 | 1 | 508 | 508 | 0.00031005 | 6.1034e-05
2013-03-22 | 510:48164 | SHORT RURAL | Planned Outage | 954838 | 16 | 385 | 6160 | 0.0037597 | 0.00097655
2013-03-22 | 509:48039 | LONG RURAL | Planned Outage | 954901 | 44 | 280 | 12320 | 0.0075194 | 0.0026855
2013-03-22 | 511:29873 | SHORT RURAL | Planned Outage | 954904 | 10 | 395 | 3950 | 0.0024109 | 0.00061034
2013-03-20 | 523:33501 | SHORT RURAL | Planned Outage | 954905 | 2 | 45 | 90 | 5.493e-05 | 0.00012207
2013-03-20 | 512:48046 | SHORT RURAL | Planned Outage | 954906 | 8 | 355 | 2840 | 0.0017333 | 0.00048827
2013-03-27 | 802:82225 | SHORT RURAL | Planned Outage | 955119 | 28 | 245 | 6860 | 0.0041847 | 0.001708
2013-03-26 | ZN13000:PA10 | URBAN | Planned Outage | 955138 | 554 | 480 | 73560 | 0.044872 | 0.033794
2013-03-26 | ZN12640:PA2 | URBAN | Planned Outage | 955152 | 126 | 510 | 64260 | 0.039199 | 0.0076861
2013-03-26 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 955161 | 5 | 360 | 1800 | 0.001098 | 0.000305
2013-03-26 | ZN1287:PA4 | URBAN | Planned Outage | 955198 | 217 | 480 | 104160 | 0.063538 | 0.013237
2013-03-26 | ZN12640:PA10 | URBAN | Planned Outage | 955236 | 425 | 300 | 124560 | 0.075982 | 0.025925
2013-03-26 | ZN12650:PA13 | SHORT RURAL | Planned Outage | 955242 | 9 | 360 | 3240 | 0.0019764 | 0.000549
2013-03-26 | ZN3155:PA29 | URBAN | Planned Outage | 955529 | 81 | 300 | 24300 | 0.014823 | 0.004941
2013-03-27 | ZN2473:PA9 | URBAN | Planned Outage | 955548 | 101 | 420 | 42420 | 0.025877 | 0.0061611
2013-03-27 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 955550 | 3 | 480 | 1440 | 0.00087842 | 0.000183
2013-03-27 | ZN2400:PA18 | SHORT RURAL | Planned Outage | 955571 | 9 | 420 | 3780 | 0.0023058 | 0.00054901
2013-03-27 | ZN35370:PA10 | SHORT RURAL | Planned Outage | 955600 | 64 | 420 | 26880 | 0.016397 | 0.0039041
2013-03-27 | ZN13000:PA11 | URBAN | Planned Outage | 955603 | 4 | 450 | 1800 | 0.001098 | 0.000244
2013-03-27 | ZN13000:PA11 | URBAN | Planned Outage | 955604 | 4 | 450 | 1800 | 0.001098 | 0.000244
2013-03-27 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 955612 | 18 | 300 | 5400 | 0.0032941 | 0.001098
2013-03-27 | ZN12660:PA5 | SHORT RURAL | Planned Outage | 955623 | 38 | 300 | 11400 | 0.0069541 | 0.002318
2013-03-27 | ZN4990:PA55 56DEF | CBD | Planned Outage | 955626 | 1 | 360 | 360 | 0.0002196 | 6.1001e-05
2013-03-21 | 227:13015 | SHORT RURAL | Planned Outage | 955744 | 135 | 410 | 55350 | 0.033782 | 0.0082396
2013-03-20 | 813:89062 | SHORT RURAL | Planned Outage | 955747 | 5 | 250 | 1250 | 0.00076292 | 0.00030517
2013-03-20 | 520:48172 | SHORT RURAL | Planned Outage | 955749 | 2 | 385 | 770 | 0.00046996 | 0.00012207
2013-03-21 | 523:33501 | SHORT RURAL | Planned Outage | 955750 | 8 | 155 | 1240 | 0.00075682 | 0.00048827
2013-03-21 | 513:48058 | URBAN | Planned Outage | 955753 | 85 | 190 | 16150 | 0.009857 | 0.0051879
2013-03-21 | 523:33501 | SHORT RURAL | Planned Outage | 955755 | 10 | 70 | 700 | 0.00042724 | 0.00061034
2013-03-22 | 813:89062 | SHORT RURAL | Planned Outage | 955758 | 19 | 270 | 5130 | 0.0031311 | 0.0011596
2013-03-22 | 810:74054 | LONG RURAL | Planned Outage | 955760 | 21 | 360 | 7560 | 0.0046142 | 0.0012817
2013-03-22 | 803:74007 | SHORT RURAL | Planned Outage | 955762 | 36 | 170 | 6120 | 0.0037353 | 0.0021972
2013-03-24 | 813:89061 | LONG RURAL | Planned Outage | 955765 | 12 | 205 | 2460 | 0.0015014 | 0.00073241
2013-03-25 | 242:81539 | URBAN | Planned Outage | 955768 | 258 | 470 | 121260 | 0.07401 | 0.015747
2013-03-25 | 216:10724 | SHORT RURAL | Planned Outage | 955771 | 3 | 480 | 1440 | 0.00087889 | 0.0001831
2013-03-26 | 232:11454 | SHORT RURAL | Planned Outage | 955774 | 383 | 165 | 63195 | 0.038549 | 0.023363
2013-03-25 | 229:34983 | SHORT RURAL | Planned Outage | 955775 | 1 | 416 | 416 | 0.0002539 | 6.1034e-05
2013-03-26 | 213:33777 | SHORT RURAL | Planned Outage | 955782 | 1 | 522 | 522 | 0.00031842 | 6.1e-05
2013-03-26 | 243:80075 | SHORT RURAL | Planned Outage | 955783 | 2 | 340 | 680 | 0.0004148 | 0.000122
2013-03-26 | 213:33777 | SHORT RURAL | Planned Outage | 955785 | 4 | 525 | 2100 | 0.001281 | 0.000244
2013-03-26 | 229:34983 | SHORT RURAL | Planned Outage | 955787 | 140 | 30 | 4200 | 0.002562 | 0.0085401
2013-03-26 | 222:2014 | URBAN | Planned Outage | 955789 | 1 | 300 | 300 | 0.000183 | 6.1e-05
2013-03-27 | 214:8667 | URBAN | Planned Outage | 955791 | 75 | 60 | 4500 | 0.002745 | 0.0045751
2013-03-27 | 202:34234 | URBAN | Planned Outage | 955793 | 68 | 80 | 5440 | 0.0033185 | 0.0041481
2013-03-26 | 510:48164 | SHORT RURAL | Planned Outage | 955795 | 1 | 290 | 290 | 0.0001769 | 6.1e-05
2013-03-26 | 511:29878 | SHORT RURAL | Planned Outage | 955797 | 2 | 30 | 60 | 3.66e-05 | 0.000122
2013-03-27 | 509:48040 | SHORT RURAL | Planned Outage | 955799 | 24 | 350 | 8400 | 0.0051241 | 0.001464
2013-03-27 | 509:48039 | LONG RURAL | Planned Outage | 955801 | 1 | 55 | 55 | 3.3551e-05 | 6.1001e-05
2013-03-27 | 510:48164 | SHORT RURAL | Planned Outage | 955803 | 2 | 270 | 540 | 0.00032941 | 0.000122
2013-03-27 | 507:80926 | URBAN | Planned Outage | 955806 | 1 | 410 | 410 | 0.0002501 | 6.1001e-05
2013-03-25 | 515:35198 | SHORT RURAL | Planned Outage | 955808 | 8 | 250 | 2000 | 0.0012207 | 0.00048827
2013-03-26 | 514:18137 | SHORT RURAL | Planned Outage | 955812 | 28 | 330 | 9240 | 0.0056364 | 0.001708
2013-03-26 | 812:19072 | SHORT RURAL | Planned Outage | 955813 | 1 | 152 | 152 | 9.2721e-05 | 6.1e-05
2013-03-27 | 807:74179 | SHORT RURAL | Planned Outage | 955815 | 2 | 228 | 456 | 0.00027816 | 0.000122
2013-03-28 | ZN12620:PA13 | SHORT RURAL | Planned Outage | 956531 | 510 | 480 | 30600 | 0.018667 | 0.031111
2013-03-28 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 956534 | 18 | 480 | 8640 | 0.0052705 | 0.001098
2013-03-28 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 956539 | 8 | 480 | 3840 | 0.0023425 | 0.00048801
2013-03-28 | ZN12660:PA8 | URBAN | Planned Outage | 956541 | 218 | 480 | 104640 | 0.063832 | 0.013298
2013-03-28 | ZN35370:PA10 | SHORT RURAL | Planned Outage | 956562 | 1 | 180 | 180 | 0.0001098 | 6.1002e-05
2013-03-28 | ZN12650:PA12 | URBAN | Planned Outage | 956565 | 61 | 300 | 18300 | 0.011163 | 0.0037211
2013-03-28 | ZN80:PA30 | URBAN | Planned Outage | 956569 | 123 | 1080 | 132840 | 0.081035 | 0.0075032
2013-03-29 | ZN2835:PA20 | URBAN | Planned Outage | 956576 | 11 | 120 | 1320 | 0.00080523 | 0.00067102
2013-03-30 | ZN167:PA17 | URBAN | Planned Outage | 956578 | 3 | 1800 | 5400 | 0.0032941 | 0.00018301
2013-03-30 | ZN9550:PA41 | URBAN | Planned Outage | 956600 | 1 | 2070 | 2070 | 0.0012627 | 6.1002e-05
2013-03-30 | 511:29880 | URBAN | Planned Outage | 956971 | 1 | 5 | 5 | 3.0501e-06 | 6.1002e-05
2013-03-30 | 238:34147 | URBAN | Planned Outage | 956975 | 1 | 275 | 275 | 0.00016776 | 6.1002e-05
2013-03-28 | 810:74058 | SHORT RURAL | Planned Outage | 956981 | 5 | 270 | 1350 | 0.00082352 | 0.00030501
2013-04-03 | 810:74054 | LONG RURAL | Planned Outage | 956984 | 1 | 149.05 | 149.05 | 9.0937e-05 | 6.1011e-05
2013-04-02 | 526:34636 | SHORT RURAL | Planned Outage | 957018 | 20 | 430 | 8600 | 0.0052469 | 0.0012202
2013-04-02 | 512:48048 | SHORT RURAL | Planned Outage | 957022 | 181 | 360 | 65160 | 0.039755 | 0.011043
2013-04-02 | 515:35192 | SHORT RURAL | Planned Outage | 957023 | 3 | 40 | 120 | 7.3213e-05 | 0.00018303
2013-04-02 | 813:89055 | SHORT RURAL | Planned Outage | 957048 | 5 | 150 | 750 | 0.00045758 | 0.00030505
2013-04-03 | 260:33344 | URBAN | Planned Outage | 957405 | 2 | 435 | 870 | 0.0005308 | 0.00012202
2013-04-03 | 234:2001 | URBAN | Planned Outage | 957410 | 26 | 340 | 5850 | 0.0035692 | 0.0015863
2013-04-03 | 225:13446 | URBAN | Planned Outage | 957424 | 67 | 305 | 20435 | 0.012468 | 0.0040877
2013-04-03 | 504:48026 | SHORT RURAL | Planned Outage | 957429 | 84 | 10 | 840 | 0.00051249 | 0.0051249
2013-04-03 | 504:48026 | SHORT RURAL | Planned Outage | 957431 | 84 | 290 | 24360 | 0.014862 | 0.0051249
2013-04-03 | 512:48046 | SHORT RURAL | Planned Outage | 957439 | 138 | 485 | 66930 | 0.040835 | 0.0084195
2013-04-03 | 504:48031 | SHORT RURAL | Planned Outage | 957452 | 10 | 470 | 4700 | 0.0028675 | 0.00061011
2013-04-03 | 520:48172 | SHORT RURAL | Planned Outage | 957468 | 3 | 13 | 39 | 2.3794e-05 | 0.00018303
2013-04-03 | 810:74054 | LONG RURAL | Planned Outage | 957470 | 24 | 255 | 6120 | 0.0037339 | 0.0014643
2013-04-03 | 515:35197 | LONG RURAL | Planned Outage | 957472 | 6 | 295 | 1770 | 0.0010799 | 0.00036607
2013-04-01 | ZN2835:PA20 | URBAN | Planned Outage | 957674 | 11 | 120 | 1320 | 0.00080523 | 0.00067102
2013-04-03 | ZN15006:PA15 | URBAN | Planned Outage | 957677 | 42 | 540 | 22680 | 0.013837 | 0.0025625
2013-04-03 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 957702 | 18 | 480 | 8640 | 0.0052714 | 0.0010982
2013-04-03 | ZN180:PA15 | URBAN | Planned Outage | 957710 | 40 | 480 | 19200 | 0.011714 | 0.0024404
2013-04-03 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 957713 | 1 | 480 | 480 | 0.00029285 | 6.1011e-05
2013-04-03 | ZN4545:PA4 | URBAN | Planned Outage | 957714 | 65 | 360 | 23400 | 0.014277 | 0.0039657
2013-04-03 | ZN9900:PA8 | URBAN | Planned Outage | 957717 | 65 | 360 | 23400 | 0.014277 | 0.0039657
2013-04-03 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 957720 | 11 | 270 | 2970 | 0.001812 | 0.00067112
2013-04-03 | ZN35370:PA2 | SHORT RURAL | Planned Outage | 957722 | 21 | 120 | 2520 | 0.0015375 | 0.0012812
2013-04-05 | 806:82656 | LONG RURAL | Planned Outage | 957945 | 238 | 300 | 71400 | 0.043563 | 0.014521
2013-04-04 | 807:74179 | SHORT RURAL | Planned Outage | 957953 | 11 | 240 | 2640 | 0.0016107 | 0.00067114
2013-04-04 | 264:81240 | SHORT RURAL | Planned Outage | 957955 | 3 | 355 | 1065 | 0.00064978 | 0.00018304
2013-04-04 | 504:48031 | SHORT RURAL | Planned Outage | 957996 | 1 | 485 | 485 | 0.00029591 | 6.1012e-05
2013-04-04 | 508:82578 | SHORT RURAL | Planned Outage | 957997 | 10 | 10 | 100 | 6.1012e-05 | 0.00061012
2013-04-04 | 807:74180 | SHORT RURAL | Planned Outage | 958000 | 5 | 185 | 925 | 0.00056436 | 0.00030506
2013-04-04 | 803:74007 | SHORT RURAL | Planned Outage | 958004 | 65 | 200 | 13000 | 0.0079316 | 0.0039658
2013-04-04 | 523:33501 | SHORT RURAL | Planned Outage | 958006 | 3 | 60 | 180 | 0.00010982 | 0.00018304
2013-04-05 | 238:34151 | URBAN | Planned Outage | 958007 | 62 | 210 | 13020 | 0.0079439 | 0.0037828
2013-04-04 | 515:35193 | SHORT RURAL | Planned Outage | 958009 | 3 | 75 | 225 | 0.00013728 | 0.00018304
2013-04-05 | 242:81541 | URBAN | Planned Outage | 958602 | 212 | 145 | 30740 | 0.018755 | 0.012935
2013-04-05 | 264:81240 | SHORT RURAL | Planned Outage | 958605 | 7 | 265 | 1855 | 0.0011318 | 0.00042709
2013-04-06 | 265:81641 | URBAN | Planned Outage | 958608 | 2 | 122 | 244 | 0.00014887 | 0.00012203
2013-04-06 | 261:81870 | URBAN | Planned Outage | 958637 | 6 | 60 | 360 | 0.00021965 | 0.00036608
2013-04-05 | 510:48164 | SHORT RURAL | Planned Outage | 958642 | 16 | 370 | 5920 | 0.003612 | 0.00097621
2013-04-05 | 504:48031 | SHORT RURAL | Planned Outage | 958645 | 1 | 465 | 465 | 0.00028371 | 6.1013e-05
2013-04-05 | 508:82578 | SHORT RURAL | Planned Outage | 958657 | 110 | 450 | 49500 | 0.030201 | 0.0067114
2013-04-05 | 511:29878 | SHORT RURAL | Planned Outage | 958722 | 5 | 25 | 125 | 7.6266e-05 | 0.00030506
2013-04-06 | 511:29880 | URBAN | Planned Outage | 958725 | 1 | 20 | 20 | 1.2203e-05 | 6.1013e-05
2013-04-05 | 520:48172 | SHORT RURAL | Planned Outage | 958727 | 15 | 315 | 4725 | 0.0028829 | 0.00091519
2013-04-07 | 513:48058 | URBAN | Planned Outage | 958732 | 3 | 130 | 390 | 0.00023795 | 0.00018304
2013-04-04 | ZN965:PA37 | URBAN | Planned Outage | 958744 | 4 | 270 | 1080 | 0.00065893 | 0.00024405
2013-04-04 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 958746 | 31 | 480 | 14880 | 0.0090786 | 0.0018914
2013-04-04 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 958749 | 16 | 480 | 7680 | 0.0046857 | 0.0009762
2013-04-04 | ZN12570:PA22 | URBAN | Planned Outage | 958757 | 60 | 480 | 28800 | 0.017572 | 0.0036607
2013-04-04 | ZN13000:PA2 | URBAN | Planned Outage | 958758 | 83 | 480 | 39840 | 0.024307 | 0.005064
2013-04-04 | ZN188:PA2 | URBAN | Planned Outage | 958760 | 49 | 60 | 2940 | 0.0017938 | 0.0029896
2013-04-04 | ZN35370:PA2 | SHORT RURAL | Planned Outage | 958764 | 21 | 120 | 2520 | 0.0015375 | 0.0012813
2013-04-05 | ZN180:PA7 | URBAN | Planned Outage | 958768 | 64 | 480 | 30720 | 0.018743 | 0.0039048
2013-04-05 | ZN2196:PA6 | URBAN | Planned Outage | 958771 | 2 | 3090 | 6180 | 0.0037706 | 0.00012203
2013-04-06 | ZN2835:PA22 | URBAN | Planned Outage | 958773 | 21 | 300 | 6300 | 0.0038438 | 0.0012813
2013-04-06 | ZN2473:PA41 | URBAN | Planned Outage | 958775 | 32 | 720 | 23040 | 0.014057 | 0.0019524
2013-04-06 | ZN1850:PA14 | URBAN | Planned Outage | 958777 | 2 | 1620 | 3240 | 0.0019768 | 0.00012203
2013-04-06 | ZN9700:PA12 | URBAN | Planned Outage | 958779 | 55 | 90 | 4950 | 0.0030201 | 0.0033557
2013-04-06 | ZN8700:PA61 62ABC | CBD | Planned Outage | 958781 | 45 | 780 | 22050 | 0.013453 | 0.0027456
2013-04-07 | ZN35500:PA31 | URBAN | Planned Outage | 958787 | 23 | 40 | 920 | 0.00056132 | 0.0014033
2013-04-07 | ZN847:PA28 | URBAN | Planned Outage | 958788 | 2 | 405 | 810 | 0.0004942 | 0.00012203
2013-04-08 | 231:8405 | SHORT RURAL | Planned Outage | 958951 | 14 | 415 | 5810 | 0.0035448 | 0.00085418
2013-04-08 | 513:48056 | SHORT RURAL | Planned Outage | 958966 | 16 | 225 | 3600 | 0.0021965 | 0.00097621
2013-04-08 | 243:80075 | SHORT RURAL | Planned Outage | 958977 | 14 | 435 | 6090 | 0.0037157 | 0.00085418
2013-04-08 | 202:34249 | URBAN | Planned Outage | 958982 | 2 | 420 | 840 | 0.00051251 | 0.00012203
2013-04-08 | 810:74054 | LONG RURAL | Planned Outage | 958986 | 2 | 380 | 760 | 0.0004637 | 0.00012203
2013-04-09 | 504:48031 | SHORT RURAL | Planned Outage | 959383 | 1 | 400 | 400 | 0.00024394 | 6.0986e-05
2013-04-09 | 509:48039 | LONG RURAL | Planned Outage | 959386 | 31 | 340 | 10540 | 0.006428 | 0.0018906
2013-04-09 | 526:34636 | SHORT RURAL | Planned Outage | 959388 | 27 | 420 | 11340 | 0.0069158 | 0.0016466
2013-04-09 | 509:48039 | LONG RURAL | Planned Outage | 959395 | 28 | 130 | 3640 | 0.0022199 | 0.0017076
2013-04-08 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 959401 | 43 | 510 | 21930 | 0.01338 | 0.0026236
2013-04-08 | ZN2835:PA20 | URBAN | Planned Outage | 959413 | 1 | 540 | 540 | 0.00032947 | 6.1013e-05
2013-04-08 | ZN12690:PA16 | SHORT RURAL | Planned Outage | 959415 | 2 | 480 | 960 | 0.00058572 | 0.00012203
2013-04-08 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 959435 | 97 | 300 | 29100 | 0.017755 | 0.0059183
2013-04-09 | 512:48049 | SHORT RURAL | Planned Outage | 959437 | 7 | 135 | 945 | 0.00057632 | 0.0004269
2013-04-09 | 810:74058 | SHORT RURAL | Planned Outage | 959439 | 2 | 230 | 460 | 0.00028054 | 0.00012197
2013-04-08 | ZN12650:PA13 | SHORT RURAL | Planned Outage | 959442 | 48 | 420 | 20160 | 0.0123 | 0.0029286
2013-04-09 | 806:82656 | LONG RURAL | Planned Outage | 959446 | 1 | 63 | 63 | 3.8421e-05 | 6.0986e-05
2013-04-08 | ZN35370:PA2 | SHORT RURAL | Planned Outage | 959452 | 21 | 120 | 2520 | 0.0015375 | 0.0012813
2013-04-09 | ZN342:PA26 | URBAN | Planned Outage | 959455 | 230 | 960 | 220800 | 0.13466 | 0.014027
2013-04-09 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 959456 | 19 | 480 | 9120 | 0.0055619 | 0.0011587
2013-04-09 | ZN12640:PA18 | SHORT RURAL | Planned Outage | 959461 | 46 | 300 | 13800 | 0.0084161 | 0.0028054
2013-04-09 | ZN80:PA32 | URBAN | Planned Outage | 959463 | 24 | 390 | 9360 | 0.0057083 | 0.0014637
2013-04-09 | ZN35370:PA2 | SHORT RURAL | Planned Outage | 959465 | 21 | 180 | 2520 | 0.0015369 | 0.0012807
2013-04-09 | 806:82656 | LONG RURAL | Planned Outage | 959470 | 1 | 55 | 55 | 3.3542e-05 | 6.0986e-05
2013-04-09 | 807:74184 | SHORT RURAL | Planned Outage | 959473 | 2 | 270 | 540 | 0.00032933 | 0.00012197
2013-04-10 | ZN180:PA17 | URBAN | Planned Outage | 959795 | 20 | 420 | 8400 | 0.0051229 | 0.0012197
2013-04-10 | ZN180:PA34 | URBAN | Planned Outage | 959795 | 49 | 420 | 20580 | 0.012551 | 0.0029884
2013-04-10 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 959796 | 13 | 480 | 6240 | 0.0038056 | 0.00079283
2013-04-10 | ZN12580:PA12 | SHORT RURAL | Planned Outage | 959800 | 17 | 480 | 8160 | 0.0049765 | 0.0010368
2013-04-10 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 959806 | 4 | 480 | 1920 | 0.0011709 | 0.00024395
2013-04-11 | 510:48164 | SHORT RURAL | Planned Outage | 959807 | 14 | 345 | 4830 | 0.0029457 | 0.00085382
2013-04-10 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 959809 | 3 | 480 | 1440 | 0.00087821 | 0.00018296
2013-04-10 | ZN2400:PA21 | URBAN | Planned Outage | 959812 | 5 | 300 | 1500 | 0.0009148 | 0.00030493
2013-04-11 | ZN12650:PA13 | SHORT RURAL | Planned Outage | 959881 | 117 | 420 | 49140 | 0.029969 | 0.0071355
2013-04-11 | 238:34137 | URBAN | Planned Outage | 959919 | 53 | 335 | 17755 | 0.010828 | 0.0032323
2013-04-11 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 960292 | 9 | 510 | 4590 | 0.0027993 | 0.00054888
2013-04-11 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 960298 | 5 | 480 | 2400 | 0.0014637 | 0.00030493
2013-04-11 | ZN12580:PA12 | SHORT RURAL | Planned Outage | 960299 | 19 | 480 | 9120 | 0.005562 | 0.0011588
2013-04-11 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 960359 | 80 | 480 | 38400 | 0.023419 | 0.004879
2013-04-10 | 229:34995 | SHORT RURAL | Planned Outage | 960384 | 160 | 60 | 9600 | 0.0058547 | 0.0097579
2013-04-10 | 511:29873 | SHORT RURAL | Planned Outage | 960385 | 7 | 405 | 2835 | 0.001729 | 0.00042691
2013-04-10 | 242:81535 | URBAN | Planned Outage | 960387 | 232 | 225 | 52200 | 0.031835 | 0.014149
2013-04-10 | 507:80922 | SHORT RURAL | Planned Outage | 960391 | 81 | 192 | 15552 | 0.0094847 | 0.0049399
2013-04-11 | 510:48164 | SHORT RURAL | Planned Outage | 960397 | 33 | 360 | 11880 | 0.0072453 | 0.0020126
2013-04-10 | 243:80074 | URBAN | Planned Outage | 960401 | 1 | 210 | 210 | 0.00012807 | 6.0987e-05
2013-04-10 | 243:80080 | SHORT RURAL | Planned Outage | 960402 | 64 | 355 | 22720 | 0.013856 | 0.0039032
2013-04-10 | 214:8667 | URBAN | Planned Outage | 960406 | 5 | 190 | 950 | 0.00057937 | 0.00030493
2013-04-10 | 222:2017 | URBAN | Planned Outage | 960407 | 24 | 80 | 1920 | 0.0011709 | 0.0014637
2013-04-10 | 508:82578 | SHORT RURAL | Planned Outage | 960409 | 1 | 170 | 170 | 0.00010368 | 6.0987e-05
2013-04-10 | 213:33774 | URBAN | Planned Outage | 960411 | 126 | 45 | 5670 | 0.003458 | 0.0076843
2013-04-11 | 509:48039 | LONG RURAL | Planned Outage | 960413 | 2 | 73 | 146 | 8.9041e-05 | 0.00012197
2013-04-12 | ZN12620:PA13 | SHORT RURAL | Planned Outage | 960761 | 510 | 510 | 30600 | 0.018662 | 0.031103
2013-04-12 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 960768 | 8 | 480 | 3840 | 0.0023419 | 0.0004879
2013-04-13 | ZN3288:PA45 46GHJ | CBD | Planned Outage | 960772 | 5 | 600 | 3000 | 0.0018296 | 0.00030494
2013-04-13 | ZN15005:PA6 | URBAN | Planned Outage | 960774 | 113 | 600 | 67800 | 0.041349 | 0.0068916
2013-04-13 | ZN12600:PA1 | SHORT RURAL | Planned Outage | 960777 | 8 | 420 | 3360 | 0.0020492 | 0.0004879
2013-04-13 | ZN1850:PA14 | URBAN | Planned Outage | 960788 | 2 | 1590 | 3180 | 0.0019394 | 0.00012197
2013-04-14 | ZN5868:PA13 | URBAN | Planned Outage | 960791 | 15 | 570 | 8550 | 0.0052144 | 0.00091481
2013-04-14 | ZN3288:PA45 46GHJ | CBD | Planned Outage | 960793 | 3 | 540 | 1620 | 0.00098799 | 0.00018296
2013-04-11 | 261:81864 | URBAN | Planned Outage | 960816 | 99 | 45 | 4455 | 0.002717 | 0.0060377
2013-04-11 | 206:34432 | URBAN | Planned Outage | 960832 | 1 | 330 | 330 | 0.00020126 | 6.0987e-05
2013-04-11 | 260:33344 | URBAN | Planned Outage | 960835 | 2 | 400 | 800 | 0.0004879 | 0.00012197
2013-04-10 | 501:48123 | SHORT RURAL | Planned Outage | 960841 | 43 | 125 | 5375 | 0.003278 | 0.0026224
2013-04-10 | 504:48031 | SHORT RURAL | Planned Outage | 960843 | 1 | 465 | 465 | 0.00028359 | 6.0987e-05
2013-04-10 | 509:48039 | LONG RURAL | Planned Outage | 960844 | 38 | 285 | 10830 | 0.0066049 | 0.0023175
2013-04-10 | 813:89061 | LONG RURAL | Planned Outage | 960848 | 9 | 365 | 3285 | 0.0020034 | 0.00054888
2013-04-10 | 513:48056 | SHORT RURAL | Planned Outage | 960849 | 2 | 75 | 150 | 9.148e-05 | 0.00012197
2013-04-10 | 515:35197 | LONG RURAL | Planned Outage | 960852 | 10 | 98 | 980 | 0.00059767 | 0.00060987
2013-04-10 | 813:89063 | SHORT RURAL | Planned Outage | 960854 | 2 | 480 | 960 | 0.00058547 | 0.00012197
2013-04-10 | 511:29878 | SHORT RURAL | Planned Outage | 960858 | 2 | 100 | 200 | 0.00012197 | 0.00012197
2013-04-10 | 515:35197 | LONG RURAL | Planned Outage | 960860 | 24 | 200 | 4800 | 0.0029274 | 0.0014637
2013-04-10 | 513:48056 | SHORT RURAL | Planned Outage | 960862 | 1 | 10 | 10 | 6.0987e-06 | 6.0987e-05
2013-04-11 | 813:89061 | LONG RURAL | Planned Outage | 960865 | 130 | 375 | 48750 | 0.029731 | 0.0079283
2013-04-12 | 511:29878 | SHORT RURAL | Planned Outage | 960885 | 206 | 330 | 67980 | 0.041459 | 0.012563
2013-04-12 | 229:34983 | SHORT RURAL | Planned Outage | 960893 | 217 | 520 | 112840 | 0.068818 | 0.013234
2013-04-12 | 526:34640 | SHORT RURAL | Planned Outage | 960914 | 7 | 218 | 1526 | 0.00093067 | 0.00042691
2013-04-12 | 238:34141 | SHORT RURAL | Planned Outage | 960918 | 21 | 375 | 7875 | 0.0048027 | 0.0012807
2013-04-12 | 202:34254 | URBAN | Planned Outage | 960920 | 44 | 40 | 1760 | 0.0010734 | 0.0026834
2013-04-12 | 227:13015 | SHORT RURAL | Planned Outage | 960922 | 136 | 210 | 28560 | 0.017418 | 0.0082943
2013-04-12 | 216:10727 | URBAN | Planned Outage | 960923 | 57 | 125 | 7125 | 0.0043453 | 0.0034763
2013-04-12 | 202:34254 | URBAN | Planned Outage | 960926 | 44 | 15 | 660 | 0.00040252 | 0.0026834
2013-04-12 | 502:48010 | SHORT RURAL | Planned Outage | 960940 | 3 | 205 | 615 | 0.00037507 | 0.00018296
2013-04-12 | 509:48039 | LONG RURAL | Planned Outage | 960942 | 21 | 315 | 6615 | 0.0040343 | 0.0012807
2013-04-12 | 510:48164 | SHORT RURAL | Planned Outage | 960946 | 2 | 60 | 120 | 7.3185e-05 | 0.00012197
2013-04-12 | 515:35198 | SHORT RURAL | Planned Outage | 960953 | 2 | 60 | 120 | 7.3185e-05 | 0.00012197
2013-04-12 | 810:74050 | SHORT RURAL | Planned Outage | 960954 | 19 | 305 | 5795 | 0.0035342 | 0.0011588
2013-04-12 | 523:33501 | SHORT RURAL | Planned Outage | 960955 | 17 | 330 | 5610 | 0.0034214 | 0.0010368
2013-04-12 | 806:82656 | LONG RURAL | Planned Outage | 960956 | 1 | 210 | 210 | 0.00012807 | 6.0987e-05
2013-04-16 | 516:48067 | SHORT RURAL | Planned Outage | 961224 | 93 | 270 | 25110 | 0.015313 | 0.0056716
2013-04-16 | 225:13444 | URBAN | Planned Outage | 961252 | 268 | 260 | 69680 | 0.042494 | 0.016344
2013-04-15 | 214:8667 | URBAN | Planned Outage | 961321 | 6 | 335 | 2010 | 0.0012258 | 0.00036592
2013-04-15 | 225:33676 | SHORT RURAL | Planned Outage | 961323 | 59 | 240 | 14160 | 0.0086358 | 0.0035982
2013-04-15 | 261:81886 | URBAN | Planned Outage | 961330 | 30 | 135 | 4050 | 0.00247 | 0.0018296
2013-04-15 | 243:80080 | SHORT RURAL | Planned Outage | 961332 | 1 | 10 | 10 | 6.0987e-06 | 6.0987e-05
2013-04-15 | 264:81240 | SHORT RURAL | Planned Outage | 961333 | 3 | 260 | 780 | 0.0004757 | 0.00018296
2013-04-15 | 504:48031 | SHORT RURAL | Planned Outage | 961334 | 138 | 525 | 72450 | 0.044185 | 0.0084162
2013-04-15 | 515:35192 | SHORT RURAL | Planned Outage | 961336 | 11 | 144 | 1584 | 0.00096604 | 0.00067086
2013-04-08 | 510:48164 | SHORT RURAL | Planned Outage | 961339 | 2 | 60 | 120 | 7.3215e-05 | 0.00012203
2013-04-15 | ZN847:PA19 | URBAN | Planned Outage | 961513 | 321 | 3377.55 | 54893.25 | 0.033478 | 0.019577
2013-04-15 | ZN15010:PA7 | URBAN | Planned Outage | 961534 | 1 | 300 | 300 | 0.00018296 | 6.0987e-05
2013-04-17 | 523:33501 | SHORT RURAL | Planned Outage | 961540 | 93 | 370 | 34410 | 0.020985 | 0.0056716
2013-04-15 | ZN14144:PA7 | SHORT RURAL | Planned Outage | 961545 | 66 | 480 | 31680 | 0.019321 | 0.0040252
2013-04-15 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 961552 | 14 | 480 | 6720 | 0.0040983 | 0.00085382
2013-04-15 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 961566 | 1 | 480 | 480 | 0.00029274 | 6.0987e-05
2013-04-15 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 961568 | 4 | 300 | 1200 | 0.00073185 | 0.00024395
2013-04-15 | ZN874:PA7 | URBAN | Planned Outage | 961570 | 3 | 420 | 1260 | 0.00076844 | 0.00018296
2013-04-16 | ZN1285:PA27 | URBAN | Planned Outage | 961572 | 1 | 540 | 540 | 0.00032932 | 6.0985e-05
2013-04-16 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 961584 | 2 | 660 | 1320 | 0.000805 | 0.00012197
2013-04-17 | 225:33670 | SHORT RURAL | Planned Outage | 961613 | 82 | 240 | 19680 | 0.012002 | 0.0050008
2013-04-16 | ZN12650:PA20 | URBAN | Planned Outage | 961617 | 607 | 540 | 197280 | 0.12031 | 0.037018
2013-04-16 | ZN116:PA34 | URBAN | Planned Outage | 961629 | 226 | 540 | 122040 | 0.074426 | 0.013783
2013-04-16 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 961630 | 18 | 480 | 8640 | 0.0052691 | 0.0010977
2013-04-16 | ZN12570:PA24 | SHORT RURAL | Planned Outage | 961638 | 216 | 480 | 103680 | 0.063229 | 0.013173
2013-04-16 | ZN12690:PA7 | SHORT RURAL | Planned Outage | 961643 | 16 | 480 | 7680 | 0.0046836 | 0.00097576
2013-04-16 | ZN9700:PA17 | URBAN | Planned Outage | 961645 | 71 | 420 | 29820 | 0.018186 | 0.0043299
2013-04-17 | ZN690:PA35 | URBAN | Planned Outage | 962193 | 122 | 405 | 49410 | 0.030133 | 0.0074402
2013-04-17 | ZN9035:PA4 | URBAN | Planned Outage | 962196 | 1 | 420 | 420 | 0.00025614 | 6.0985e-05
2013-04-17 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 962203 | 8 | 480 | 3840 | 0.0023418 | 0.00048788
2013-04-17 | ZN14892:PA6 | SHORT RURAL | Planned Outage | 962207 | 3 | 480 | 1440 | 0.00087819 | 0.00018296
2013-04-19 | 524:33570 | SHORT RURAL | Planned Outage | 962386 | 402 | 280 | 112560 | 0.068647 | 0.024517
2013-04-19 | 214:8670 | URBAN | Planned Outage | 962513 | 98 | 101 | 9898 | 0.0060365 | 0.0059767
2013-04-16 | 526:34637 | SHORT RURAL | Planned Outage | 962562 | 8 | 215 | 1720 | 0.0010489 | 0.00048788
2013-04-17 | 512:48046 | SHORT RURAL | Planned Outage | 962570 | 138 | 330 | 45540 | 0.027773 | 0.008416
2013-04-18 | 214:8670 | URBAN | Planned Outage | 962575 | 194 | 65 | 12610 | 0.0076904 | 0.011831
2013-04-18 | 511:29878 | SHORT RURAL | Planned Outage | 962578 | 56 | 560 | 31360 | 0.019125 | 0.0034152
2013-04-18 | 264:81240 | SHORT RURAL | Planned Outage | 962585 | 46 | 215 | 9890 | 0.0060316 | 0.0028054
2013-04-16 | 205:12213 | URBAN | Planned Outage | 962587 | 73 | 430 | 31390 | 0.019143 | 0.0044519
2013-04-16 | 224:80337 | URBAN | Planned Outage | 962588 | 22 | 270 | 5940 | 0.0036225 | 0.0013417
2013-04-16 | 229:34983 | SHORT RURAL | Planned Outage | 962589 | 1 | 80 | 80 | 4.8788e-05 | 6.0985e-05
2013-04-17 | 225:13446 | URBAN | Planned Outage | 962598 | 67 | 375 | 25125 | 0.015323 | 0.004086
2013-04-17 | 229:34983 | SHORT RURAL | Planned Outage | 962599 | 1 | 570 | 570 | 0.00034762 | 6.0985e-05
2013-04-18 | 242:81539 | URBAN | Planned Outage | 962601 | 123 | 68 | 8364 | 0.0051009 | 0.0075013
2013-04-17 | 504:48031 | SHORT RURAL | Planned Outage | 962602 | 29 | 340 | 9860 | 0.0060132 | 0.0017686
2013-04-17 | 511:29878 | SHORT RURAL | Planned Outage | 962603 | 2 | 290 | 580 | 0.00035372 | 0.00012197
2013-04-17 | 504:48031 | SHORT RURAL | Planned Outage | 962606 | 1 | 495 | 495 | 0.00030188 | 6.0985e-05
2013-04-17 | 524:33572 | SHORT RURAL | Planned Outage | 962609 | 1 | 630 | 630 | 0.00038421 | 6.0985e-05
2013-04-18 | 509:48040 | SHORT RURAL | Planned Outage | 962614 | 167 | 365 | 60955 | 0.037174 | 0.010185
2013-04-18 | 238:34147 | URBAN | Planned Outage | 962617 | 106 | 260 | 27560 | 0.016808 | 0.0064646
2013-04-16 | 812:19066 | SHORT RURAL | Planned Outage | 962626 | 8 | 475 | 3800 | 0.0023174 | 0.00048788
2013-04-16 | 513:48052 | URBAN | Planned Outage | 962628 | 1 | 280 | 280 | 0.00017076 | 6.0985e-05
2013-04-17 | 523:33501 | SHORT RURAL | Planned Outage | 962629 | 3 | 45 | 135 | 8.233e-05 | 0.00018296
2013-04-18 | 802:82215 | SHORT RURAL | Planned Outage | 962630 | 1 | 210 | 210 | 0.00012807 | 6.0986e-05
2013-04-18 | 515:35193 | SHORT RURAL | Planned Outage | 962631 | 17 | 315 | 5355 | 0.0032658 | 0.0010368
2013-04-19 | 508:82578 | SHORT RURAL | Planned Outage | 963431 | 13 | 310 | 4030 | 0.0024578 | 0.00079283
2013-04-21 | 507:80923 | SHORT RURAL | Planned Outage | 963442 | 40 | 410 | 16400 | 0.010002 | 0.0024395
2013-04-19 | 214:8667 | URBAN | Planned Outage | 963443 | 54 | 170 | 9180 | 0.0055986 | 0.0032933
2013-04-19 | 504:48031 | SHORT RURAL | Planned Outage | 963451 | 2 | 360 | 720 | 0.0004391 | 0.00012197
2013-04-19 | 503:48011 | SHORT RURAL | Planned Outage | 963452 | 99 | 370 | 36630 | 0.022339 | 0.0060377
2013-04-19 | 507:80922 | SHORT RURAL | Planned Outage | 963460 | 180 | 126 | 22680 | 0.013832 | 0.010978
2013-04-19 | 238:34141 | SHORT RURAL | Planned Outage | 963462 | 13 | 440 | 5720 | 0.0034884 | 0.00079283
2013-04-19 | 813:89061 | LONG RURAL | Planned Outage | 963468 | 3 | 175 | 525 | 0.00032018 | 0.00018296
2013-04-19 | 514:18137 | SHORT RURAL | Planned Outage | 963469 | 9 | 230 | 2070 | 0.0012624 | 0.00054888
2013-04-19 | 512:48046 | SHORT RURAL | Planned Outage | 963472 | 9 | 320 | 2880 | 0.0017564 | 0.00054888
2013-04-20 | 813:89061 | LONG RURAL | Planned Outage | 963491 | 4 | 230 | 920 | 0.00056108 | 0.00024395
2013-04-21 | 514:18137 | SHORT RURAL | Planned Outage | 963493 | 4 | 323 | 1292 | 0.00078795 | 0.00024395
2013-04-22 | 231:8415 | SHORT RURAL | Planned Outage | 963720 | 193 | 320 | 61760 | 0.037665 | 0.01177
2013-04-22 | 227:13018 | URBAN | Planned Outage | 963729 | 1 | 150 | 150 | 9.148e-05 | 6.0987e-05
2013-04-22 | 216:10726 | URBAN | Planned Outage | 963731 | 63 | 65 | 4095 | 0.0024974 | 0.0038422
2013-04-22 | 503:48011 | SHORT RURAL | Planned Outage | 963734 | 98 | 40 | 3920 | 0.0023907 | 0.0059767
2013-04-22 | 509:48040 | SHORT RURAL | Planned Outage | 963736 | 99 | 300 | 29700 | 0.018113 | 0.0060377
2013-04-22 | 523:33508 | SHORT RURAL | Planned Outage | 963746 | 28 | 380 | 10640 | 0.006489 | 0.0017076
2013-04-23 | 526:34636 | SHORT RURAL | Planned Outage | 964093 | 13 | 390 | 5070 | 0.0031089 | 0.00079714
2013-04-23 | 507:80932 | SHORT RURAL | Planned Outage | 964097 | 45 | 270 | 12150 | 0.0074502 | 0.0027593
2013-04-23 | 225:33676 | SHORT RURAL | Planned Outage | 964099 | 2 | 670 | 1340 | 0.00082167 | 0.00012264
2013-04-23 | 217:33612 | URBAN | Planned Outage | 964103 | 238 | 450 | 107100 | 0.065672 | 0.014594
2013-04-23 | 213:33777 | SHORT RURAL | Planned Outage | 964120 | 121 | 100 | 12100 | 0.0074195 | 0.0074195
2013-04-23 | 217:33611 | URBAN | Planned Outage | 964121 | 86 | 480 | 41280 | 0.025312 | 0.0052734
2013-04-23 | 227:13015 | SHORT RURAL | Planned Outage | 964123 | 6 | 420 | 2520 | 0.0015452 | 0.00036791
2013-04-23 | 526:34636 | SHORT RURAL | Planned Outage | 964125 | 31 | 345 | 10695 | 0.006558 | 0.0019009
2013-04-23 | 813:89061 | LONG RURAL | Planned Outage | 964128 | 6 | 270 | 1620 | 0.00099336 | 0.00036791
2013-04-23 | 516:48067 | SHORT RURAL | Planned Outage | 964131 | 5 | 169 | 845 | 0.00051814 | 0.00030659
2013-04-23 | 520:48172 | SHORT RURAL | Planned Outage | 964137 | 1 | 125 | 125 | 7.6648e-05 | 6.1319e-05
2013-04-23 | 515:35197 | LONG RURAL | Planned Outage | 964139 | 5 | 255 | 1275 | 0.00078181 | 0.00030659
2013-04-23 | 813:89062 | SHORT RURAL | Planned Outage | 964145 | 54 | 370 | 19980 | 0.012251 | 0.0033112
2013-04-23 | 523:33501 | SHORT RURAL | Planned Outage | 964147 | 1 | 75 | 75 | 4.5989e-05 | 6.1319e-05
2013-04-26 | 229:34995 | SHORT RURAL | Planned Outage | 964526 | 123 | 165 | 20295 | 0.01237 | 0.0074971
2013-04-24 | 515:35193 | SHORT RURAL | Planned Outage | 964664 | 24 | 345 | 8280 | 0.0050468 | 0.0014628
2013-04-24 | 516:48066 | SHORT RURAL | Planned Outage | 964664 | 12 | 345 | 4140 | 0.0025234 | 0.00073142
2013-04-24 | 217:33611 | URBAN | Planned Outage | 964668 | 86 | 440 | 37840 | 0.023064 | 0.0052418
2013-04-24 | 243:80083 | SHORT RURAL | Planned Outage | 964686 | 23 | 353 | 8119 | 0.0049486 | 0.0014019
2013-04-24 | 224:80340 | SHORT RURAL | Planned Outage | 964688 | 11 | 195 | 2145 | 0.0013074 | 0.00067046
2013-04-24 | 513:48052 | URBAN | Planned Outage | 964690 | 36 | 395 | 14220 | 0.0086673 | 0.0021942
2013-04-24 | 811:74234 | SHORT RURAL | Planned Outage | 964693 | 12 | 190 | 2280 | 0.0013897 | 0.00073142
2013-04-29 | 508:82578 | SHORT RURAL | Planned Outage | 965124 | 110 | 440 | 48400 | 0.029501 | 0.0067047
2013-04-29 | 239:82129 | SHORT RURAL | Planned Outage | 965199 | 141 | 390 | 54990 | 0.033518 | 0.0085942
2013-04-26 | 511:29878 | SHORT RURAL | Planned Outage | 965251 | 56 | 480 | 26880 | 0.016384 | 0.0034133
2013-04-27 | 227:13014 | SHORT RURAL | Planned Outage | 965255 | 51 | 450 | 22950 | 0.013989 | 0.0031086
2013-04-26 | 221:11898 | URBAN | Planned Outage | 965259 | 6 | 245 | 1470 | 0.000896 | 0.00036571
2013-04-26 | 803:74007 | SHORT RURAL | Planned Outage | 965262 | 7 | 105 | 735 | 0.000448 | 0.00042666
2013-04-26 | 512:48049 | SHORT RURAL | Planned Outage | 965264 | 5 | 185 | 925 | 0.00056381 | 0.00030476
2013-04-27 | 807:74184 | SHORT RURAL | Planned Outage | 965269 | 13 | 300 | 3900 | 0.0023771 | 0.00079238
2013-04-29 | 222:2014 | URBAN | Planned Outage | 965714 | 45 | 100 | 4500 | 0.0027428 | 0.0027428
2013-04-29 | 511:29878 | SHORT RURAL | Planned Outage | 965719 | 2 | 292 | 584 | 0.00035596 | 0.0001219
2013-04-29 | 516:48067 | SHORT RURAL | Planned Outage | 965723 | 7 | 195 | 1365 | 0.000832 | 0.00042666
2013-04-29 | 520:48172 | SHORT RURAL | Planned Outage | 965724 | 5 | 75 | 375 | 0.00022857 | 0.00030476
2013-04-29 | 513:48056 | SHORT RURAL | Planned Outage | 965725 | 16 | 98 | 1568 | 0.00095573 | 0.00097523
2013-04-18 | ZN2568:PA32 | URBAN | Planned Outage | 965782 | 224 | 420 | 94080 | 0.057376 | 0.013661
2013-04-18 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 965785 | 4 | 480 | 1920 | 0.0011709 | 0.00024395
2013-04-18 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 965789 | 10 | 480 | 4800 | 0.0029273 | 0.00060986
2013-04-18 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 965790 | 11 | 360 | 3960 | 0.0024151 | 0.00067085
2013-04-18 | ZN116:PA44 | URBAN | Planned Outage | 965792 | 1 | 60 | 60 | 3.6592e-05 | 6.0986e-05
2013-04-19 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 965793 | 16 | 480 | 7680 | 0.0046838 | 0.00097579
2013-04-19 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 965797 | 6 | 480 | 2880 | 0.0017564 | 0.00036592
2013-04-19 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 965798 | 60 | 480 | 28800 | 0.017564 | 0.0036592
2013-04-19 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 965802 | 2 | 210 | 420 | 0.00025614 | 0.00012197
2013-04-19 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 965807 | 17 | 240 | 4080 | 0.0024883 | 0.0010368
2013-04-20 | ZN1290:PA16 | URBAN | Planned Outage | 965812 | 3 | 600 | 1800 | 0.0010978 | 0.00018296
2013-04-20 | ZN1610:PA14 | URBAN | Planned Outage | 965813 | 327 | 30 | 9810 | 0.0059828 | 0.019943
2013-04-21 | ZN3425:PA11 | URBAN | Planned Outage | 965818 | 43 | 600 | 25800 | 0.015735 | 0.0026224
2013-04-21 | ZN12650:PA20 | URBAN | Planned Outage | 965819 | 3 | 480 | 1440 | 0.00087821 | 0.00018296
2013-04-30 | 812:19072 | SHORT RURAL | Planned Outage | 965947 | 5 | 216 | 1080 | 0.0006581 | 0.00030468
2013-04-30 | 227:13015 | SHORT RURAL | Planned Outage | 965950 | 6 | 355 | 2130 | 0.0012979 | 0.00036561
2013-04-30 | 232:11460 | URBAN | Planned Outage | 965952 | 179 | 205 | 36695 | 0.02236 | 0.010907
2013-04-30 | 229:34983 | SHORT RURAL | Planned Outage | 965954 | 140 | 330 | 46200 | 0.028152 | 0.008531
2013-04-30 | 214:8670 | URBAN | Planned Outage | 965956 | 98 | 90 | 8820 | 0.0053745 | 0.0059717
2013-04-22 | ZN15002:PA6 | URBAN | Planned Outage | 965974 | 17 | 480 | 8160 | 0.0049765 | 0.0010368
2013-04-30 | 526:34636 | SHORT RURAL | Planned Outage | 965975 | 7 | 360 | 2520 | 0.0015356 | 0.00042655
2013-04-30 | 526:34636 | SHORT RURAL | Planned Outage | 965976 | 31 | 490 | 15190 | 0.0092561 | 0.001889
2013-04-22 | ZN847:PA45 | SHORT RURAL | Planned Outage | 965977 | 5 | 480 | 2400 | 0.0014637 | 0.00030493
2013-04-22 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 965979 | 11 | 480 | 3600 | 0.0021955 | 0.00067085
2013-04-30 | 526:34636 | SHORT RURAL | Planned Outage | 965985 | 15 | 215 | 3225 | 0.0019652 | 0.00091403
2013-04-30 | 511:29878 | SHORT RURAL | Planned Outage | 965988 | 1 | 395 | 395 | 0.0002407 | 6.0935e-05
2013-04-30 | 516:48066 | SHORT RURAL | Planned Outage | 965992 | 9 | 150 | 1350 | 0.00082263 | 0.00054842
2013-05-01 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 965996 | 640 | 300 | 38400 | 0.023399 | 0.038999
2013-04-30 | 516:48067 | SHORT RURAL | Planned Outage | 965997 | 14 | 80 | 1120 | 0.00068248 | 0.0008531
2013-04-30 | 513:48059 | SHORT RURAL | Planned Outage | 966001 | 1 | 95 | 95 | 5.7889e-05 | 6.0935e-05
2013-04-22 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 966002 | 7 | 480 | 3360 | 0.0020492 | 0.00042691
2013-04-30 | 801:74123 | SHORT RURAL | Planned Outage | 966012 | 1 | 410 | 410 | 0.00024984 | 6.0935e-05
2013-04-30 | 811:74234 | SHORT RURAL | Planned Outage | 966013 | 7 | 405 | 2835 | 0.0017275 | 0.00042655
2013-04-22 | ZN14143:PA10 | SHORT RURAL | Planned Outage | 966027 | 11 | 180 | 1980 | 0.0012075 | 0.00067085
2013-04-23 | ZN4545:PA19 | URBAN | Planned Outage | 966030 | 65 | 720 | 46800 | 0.028697 | 0.0039857
2013-04-23 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 966031 | 2 | 540 | 120 | 7.3582e-05 | 0.00012264
2013-04-23 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 966033 | 11 | 420 | 4620 | 0.0028329 | 0.0006745
2013-04-23 | ZN180:PA7 | URBAN | Planned Outage | 966034 | 163 | 540 | 88020 | 0.053973 | 0.0099949
2013-04-23 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 966036 | 9 | 480 | 4320 | 0.002649 | 0.00055187
2013-04-23 | ZN13000:PA5 | SHORT RURAL | Planned Outage | 966044 | 226 | 480 | 108480 | 0.066518 | 0.013858
2013-04-23 | ZN2835:PA21 | URBAN | Planned Outage | 966092 | 232 | 360 | 83520 | 0.051213 | 0.014226
2013-04-23 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 966105 | 40 | 300 | 2880 | 0.001766 | 0.0024527
2013-05-01 | 523:33501 | SHORT RURAL | Planned Outage | 966172 | 7 | 55 | 385 | 0.0002346 | 0.00042655
2013-04-23 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 966175 | 14 | 1800 | 13680 | 0.0083884 | 0.00085846
2013-04-23 | ZN269:PA26 | URBAN | Planned Outage | 966180 | 35 | 540 | 18900 | 0.011589 | 0.0021461
2013-04-24 | ZN847:PA45 | SHORT RURAL | Planned Outage | 966183 | 13 | 480 | 6240 | 0.0038034 | 0.00079237
2013-04-24 | ZN35370:PA4 | URBAN | Planned Outage | 966186 | 21 | 480 | 10080 | 0.0061439 | 0.00128
2013-04-24 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 966191 | 32 | 360 | 11520 | 0.0070216 | 0.0019504
2013-04-24 | ZN965:PA38 | URBAN | Planned Outage | 966196 | 53 | 390 | 20670 | 0.012599 | 0.0032304
2013-04-24 | ZN180:PA15 | URBAN | Planned Outage | 966202 | 22 | 480 | 10560 | 0.0064365 | 0.0013409
2013-04-24 | ZN269:PA9 | URBAN | Planned Outage | 966205 | 127 | 360 | 45720 | 0.027867 | 0.0077408
2013-04-24 | ZN12580:PA16 | URBAN | Planned Outage | 966218 | 30 | 480 | 14400 | 0.008777 | 0.0018285
2013-04-24 | ZN12570:PA24 | SHORT RURAL | Planned Outage | 966230 | 179 | 450 | 80550 | 0.049096 | 0.01091
2013-04-24 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 966245 | 20 | 360 | 7200 | 0.0043885 | 0.001219
2013-04-26 | ZN1610:PA4 | URBAN | Planned Outage | 966258 | 2 | 420 | 840 | 0.000512 | 0.0001219
2013-04-27 | ZN2473:PA27 | URBAN | Planned Outage | 966260 | 32 | 1500 | 48000 | 0.029257 | 0.0019505
2013-04-28 | ZN1788:PA7 | SHORT RURAL | Planned Outage | 966263 | 2 | 420 | 840 | 0.000512 | 0.0001219
2013-04-29 | ZN180:PA7 | URBAN | Planned Outage | 966269 | 42 | 420 | 17640 | 0.010752 | 0.00256
2013-04-29 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 966274 | 4 | 480 | 1920 | 0.0011703 | 0.00024381
2013-04-29 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 966277 | 5 | 480 | 2400 | 0.0014629 | 0.00030476
2013-05-01 | 239:82128 | SHORT RURAL | Planned Outage | 966517 | 49 | 120 | 5880 | 0.003583 | 0.0029859
2013-04-29 | ZN13000:PA2 | URBAN | Planned Outage | 966584 | 83 | 480 | 39840 | 0.024283 | 0.005059
2013-04-29 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 966637 | 3 | 480 | 1440 | 0.00087771 | 0.00018286
2013-04-29 | ZN12600:PA11 | URBAN | Planned Outage | 966648 | 32 | 480 | 15360 | 0.0093622 | 0.0019505
2013-04-29 | ZN14891:PA1 | SHORT RURAL | Planned Outage | 966653 | 1 | 270 | 270 | 0.00016457 | 6.0952e-05
2013-04-30 | ZN1287:PA5 | URBAN | Planned Outage | 966655 | 1 | 480 | 480 | 0.00029249 | 6.0935e-05
2013-04-30 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 966656 | 2 | 450 | 900 | 0.00054842 | 0.00012187
2013-04-30 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 966658 | 5 | 480 | 2400 | 0.0014625 | 0.00030468
2013-04-30 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 966676 | 12 | 480 | 5370 | 0.0032722 | 0.00073123
2013-05-01 | 264:81240 | SHORT RURAL | Planned Outage | 966734 | 91 | 390 | 35490 | 0.021626 | 0.0055452
2013-05-01 | 238:34151 | URBAN | Planned Outage | 966736 | 654 | 600 | 392400 | 0.23911 | 0.039852
2013-05-01 | 507:80932 | SHORT RURAL | Planned Outage | 966738 | 45 | 375 | 16875 | 0.010283 | 0.0027421
2013-05-01 | 810:74058 | SHORT RURAL | Planned Outage | 966742 | 3 | 190 | 570 | 0.00034733 | 0.00018281
2013-05-01 | 515:35193 | SHORT RURAL | Planned Outage | 966743 | 11 | 145 | 1595 | 0.00097193 | 0.00067029
2013-05-01 | 801:74123 | SHORT RURAL | Planned Outage | 966745 | 1 | 350 | 350 | 0.00021328 | 6.0936e-05
2013-05-01 | 801:74119 | URBAN | Planned Outage | 966749 | 33 | 170 | 5610 | 0.0034185 | 0.0020109
2013-04-30 | ZN12650:PA13 | SHORT RURAL | Planned Outage | 966757 | 9 | 420 | 3780 | 0.0023034 | 0.00054842
2013-04-30 | ZN9037:PA14 | URBAN | Planned Outage | 966760 | 14 | 1080 | 15120 | 0.0092134 | 0.0008531
2013-04-30 | ZN4990:PA55 56GHJ | CBD | Planned Outage | 966761 | 88 | 480 | 42240 | 0.025739 | 0.0053623
2013-05-01 | ZN847:PA22 | SHORT RURAL | Planned Outage | 966781 | 1 | 390 | 390 | 0.00023765 | 6.0936e-05
2013-05-01 | ZN14143:PA10 | SHORT RURAL | Planned Outage | 966795 | 2 | 570 | 1140 | 0.00069467 | 0.00012187
2013-05-01 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 966800 | 82 | 480 | 39360 | 0.023984 | 0.0049967
2013-05-01 | ZN188:PA2 | URBAN | Planned Outage | 966803 | 1 | 40 | 40 | 2.4374e-05 | 6.0936e-05
2013-05-01 | ZN12620:PA11 | SHORT RURAL | Planned Outage | 966825 | 3 | 330 | 990 | 0.00060327 | 0.00018281
2013-05-01 | ZN35370:PA2 | SHORT RURAL | Planned Outage | 966828 | 21 | 120 | 2520 | 0.0015356 | 0.0012797
2013-05-02 | 503:48011 | SHORT RURAL | Planned Outage | 967790 | 27 | 410 | 11070 | 0.0067457 | 0.0016453
2013-05-02 | 238:34141 | SHORT RURAL | Planned Outage | 967803 | 66 | 470 | 31020 | 0.018902 | 0.0040218
2013-05-02 | 231:8415 | SHORT RURAL | Planned Outage | 967805 | 20 | 150 | 3000 | 0.0018281 | 0.0012187
2013-05-02 | 261:81864 | URBAN | Planned Outage | 967812 | 92 | 380 | 34960 | 0.021303 | 0.0056061
2013-05-02 | 213:33773 | SHORT RURAL | Planned Outage | 967814 | 13 | 200 | 2600 | 0.0015843 | 0.00079217
2013-05-02 | 239:82128 | SHORT RURAL | Planned Outage | 967821 | 1 | 100 | 100 | 6.0936e-05 | 6.0936e-05
2013-05-03 | 231:8405 | SHORT RURAL | Planned Outage | 967824 | 2 | 405 | 810 | 0.00049359 | 0.00012187
2013-05-04 | 235:8684 | SHORT RURAL | Planned Outage | 967826 | 1 | 285 | 285 | 0.00017367 | 6.0937e-05
2013-05-05 | 240:34846 | URBAN | Planned Outage | 967836 | 37 | 300 | 11100 | 0.006764 | 0.0022547
2013-05-05 | 240:34852 | URBAN | Planned Outage | 967836 | 53 | 300 | 15900 | 0.0096889 | 0.0032296
2013-05-02 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 968056 | 16 | 480 | 7680 | 0.0046799 | 0.00097498
2013-05-02 | ZN3154:PA22 | URBAN | Planned Outage | 968062 | 85 | 420 | 35700 | 0.021754 | 0.0051796
2013-05-02 | ZN12570:PA24 | SHORT RURAL | Planned Outage | 968067 | 215 | 450 | 96750 | 0.058956 | 0.013101
2013-05-02 | ZN35370:PA2 | SHORT RURAL | Planned Outage | 968076 | 21 | 120 | 2520 | 0.0015356 | 0.0012797
2013-05-03 | ZN3472:PA12 | URBAN | Planned Outage | 968086 | 46 | 330 | 15180 | 0.0092502 | 0.0028031
2013-05-03 | ZN13000:PA4 | SHORT RURAL | Planned Outage | 968089 | 2 | 480 | 960 | 0.00058499 | 0.00012187
2013-05-03 | ZN12610:PA20 | SHORT RURAL | Planned Outage | 968091 | 22 | 480 | 10560 | 0.0064349 | 0.0013406
2013-05-03 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 968125 | 38 | 420 | 2700 | 0.0016453 | 0.0023156
2013-05-04 | ZN630:PA19 | URBAN | Planned Outage | 968135 | 11 | 120 | 1320 | 0.00080437 | 0.0006703
2013-05-07 | 813:89055 | SHORT RURAL | Planned Outage | 968168 | 41 | 245 | 10045 | 0.0061195 | 0.0024978
2013-05-04 | ZN35500:PA27 | URBAN | Planned Outage | 968255 | 1 | 310 | 310 | 0.0001889 | 6.0937e-05
2013-05-04 | ZN3472:PA34 | URBAN | Planned Outage | 968260 | 1 | 2040 | 2040 | 0.0012431 | 6.0937e-05
2013-05-04 | ZN3472:PA39 | URBAN | Planned Outage | 968270 | 2 | 405 | 810 | 0.00049359 | 0.00012187
2013-05-05 | ZN15005:PA10 | URBAN | Planned Outage | 968279 | 4 | 450 | 1800 | 0.0010969 | 0.00024375
2013-05-05 | ZN3922:PA18 | URBAN | Planned Outage | 968280 | 76 | 540 | 41040 | 0.025008 | 0.0046312
2013-05-05 | ZN12570:PA26 | URBAN | Planned Outage | 968283 | 39 | 240 | 9360 | 0.0057037 | 0.0023765
2013-05-02 | 504:48031 | SHORT RURAL | Planned Outage | 968507 | 1 | 403 | 403 | 0.00024557 | 6.0936e-05
2013-05-02 | 509:48039 | LONG RURAL | Planned Outage | 968509 | 2 | 250 | 500 | 0.00030468 | 0.00012187
2013-05-02 | 238:34144 | URBAN | Planned Outage | 968515 | 117 | 240 | 28080 | 0.017111 | 0.0071296
2013-05-03 | 502:48010 | SHORT RURAL | Planned Outage | 968522 | 18 | 270 | 4860 | 0.0029615 | 0.0010969
2013-05-03 | 526:34636 | SHORT RURAL | Planned Outage | 968528 | 1 | 330 | 330 | 0.00020109 | 6.0937e-05
2013-05-03 | 503:48078 | URBAN | Planned Outage | 968538 | 136 | 90 | 12240 | 0.0074587 | 0.0082874
2013-05-03 | 510:48164 | SHORT RURAL | Planned Outage | 968544 | 58 | 315 | 18270 | 0.011133 | 0.0035343
2013-05-03 | 238:34141 | SHORT RURAL | Planned Outage | 968553 | 21 | 515 | 10815 | 0.0065903 | 0.0012797
2013-05-05 | 501:48124 | URBAN | Planned Outage | 968556 | 90 | 170 | 15300 | 0.0093233 | 0.0054843
2013-05-05 | 501:48125 | URBAN | Planned Outage | 968560 | 52 | 110 | 5720 | 0.0034856 | 0.0031687
2013-05-05 | 501:48124 | URBAN | Planned Outage | 968562 | 75 | 100 | 7500 | 0.0045703 | 0.0045703
2013-05-03 | 512:48049 | SHORT RURAL | Planned Outage | 968567 | 46 | 185 | 8510 | 0.0051857 | 0.0028031
2013-05-03 | 813:89061 | LONG RURAL | Planned Outage | 968571 | 13 | 240 | 3120 | 0.0019012 | 0.00079218
2013-05-03 | 520:48172 | SHORT RURAL | Planned Outage | 968573 | 4 | 40 | 160 | 9.7499e-05 | 0.00024375
2013-05-06 | ZN116:PA34 | URBAN | Planned Outage | 968591 | 226 | 540 | 122040 | 0.074367 | 0.013772
2013-05-06 | ZN874:PA7 | URBAN | Planned Outage | 968597 | 2 | 300 | 600 | 0.00036562 | 0.00012187
2013-05-06 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 968601 | 31 | 480 | 14880 | 0.0090674 | 0.001889
2013-05-06 | ZN12650:PA13 | SHORT RURAL | Planned Outage | 968605 | 97 | 480 | 46560 | 0.028372 | 0.0059109
2013-05-06 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 968613 | 3 | 480 | 1440 | 0.00087749 | 0.00018281
2013-05-06 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 968626 | 16 | 480 | 7680 | 0.0046799 | 0.00097499
2013-05-06 | ZN14891:PA10 | SHORT RURAL | Planned Outage | 968628 | 7 | 480 | 3360 | 0.0020475 | 0.00042656
2013-05-06 | ZN3922:PA3 | URBAN | Planned Outage | 968633 | 19 | 360 | 6840 | 0.0041681 | 0.0011578
2013-05-07 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 968636 | 2 | 480 | 960 | 0.00058484 | 0.00012184
2013-05-07 | ZN14891:PA1 | SHORT RURAL | Planned Outage | 968640 | 7 | 480 | 3360 | 0.002047 | 0.00042645
2013-05-07 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 968643 | 4 | 420 | 1680 | 0.0010235 | 0.00024368
2013-05-07 | ZN2400:PA21 | URBAN | Planned Outage | 968644 | 5 | 300 | 1500 | 0.00091382 | 0.00030461
2013-05-06 | 243:80083 | SHORT RURAL | Planned Outage | 968710 | 7 | 55 | 385 | 0.00023461 | 0.00042656
2013-05-06 | 227:13019 | SHORT RURAL | Planned Outage | 968715 | 5 | 59 | 295 | 0.00017976 | 0.00030468
2013-05-06 | 232:11457 | URBAN | Planned Outage | 968717 | 62 | 355 | 22010 | 0.013412 | 0.0037781
2013-05-06 | 221:11893 | URBAN | Planned Outage | 968719 | 116 | 265 | 30740 | 0.018732 | 0.0070687
2013-05-07 | 227:13019 | SHORT RURAL | Planned Outage | 968736 | 120 | 520 | 62400 | 0.038015 | 0.0073105
2013-05-07 | 507:80923 | SHORT RURAL | Planned Outage | 968751 | 40 | 445 | 17800 | 0.010844 | 0.0024368
2013-05-07 | 242:81541 | URBAN | Planned Outage | 968760 | 162 | 480 | 77760 | 0.047372 | 0.0098692
2013-05-07 | 526:34636 | SHORT RURAL | Planned Outage | 968772 | 35 | 330 | 11550 | 0.0070364 | 0.0021322
2013-05-07 | 221:11895 | URBAN | Planned Outage | 968775 | 172 | 170 | 29240 | 0.017813 | 0.010478
2013-05-07 | 213:33777 | SHORT RURAL | Planned Outage | 968784 | 121 | 430 | 52030 | 0.031697 | 0.0073715
2013-05-07 | 240:34852 | URBAN | Planned Outage | 968787 | 26 | 365 | 9490 | 0.0057814 | 0.001584
2013-05-07 | 515:35197 | LONG RURAL | Planned Outage | 968792 | 140 | 375 | 52500 | 0.031984 | 0.008529
2013-05-08 | 504:48031 | SHORT RURAL | Planned Outage | 969060 | 65 | 331 | 21515 | 0.013107 | 0.00396
2013-05-08 | 810:74058 | SHORT RURAL | Planned Outage | 969065 | 130 | 375 | 48750 | 0.0297 | 0.0079199
2013-05-08 | 508:82578 | SHORT RURAL | Planned Outage | 969069 | 27 | 365 | 9855 | 0.0060039 | 0.0016449
2013-05-08 | 510:48164 | SHORT RURAL | Planned Outage | 969074 | 4 | 510 | 2040 | 0.0012428 | 0.00024369
2013-05-08 | 526:34637 | SHORT RURAL | Planned Outage | 969075 | 1 | 90 | 90 | 5.483e-05 | 6.0922e-05
2013-05-08 | 516:48065 | SHORT RURAL | Planned Outage | 969077 | 7 | 285 | 1995 | 0.0012154 | 0.00042646
2013-05-08 | 526:34637 | SHORT RURAL | Planned Outage | 969078 | 3 | 40 | 120 | 7.3107e-05 | 0.00018277
2013-05-09 | 243:80074 | URBAN | Planned Outage | 969397 | 67 | 290 | 19430 | 0.011837 | 0.0040818
2013-05-09 | 509:48039 | LONG RURAL | Planned Outage | 969405 | 6 | 355 | 2130 | 0.0012977 | 0.00036554
2013-05-09 | 508:82578 | SHORT RURAL | Planned Outage | 969406 | 2 | 370 | 740 | 0.00045083 | 0.00012185
2013-05-09 | 516:48067 | SHORT RURAL | Planned Outage | 969410 | 1 | 77 | 77 | 4.6911e-05 | 6.0923e-05
2013-05-09 | 802:82225 | SHORT RURAL | Planned Outage | 969412 | 105 | 340 | 35700 | 0.02175 | 0.0063969
2013-05-09 | 515:35198 | SHORT RURAL | Planned Outage | 969415 | 2 | 73 | 146 | 8.8948e-05 | 0.00012185
2013-05-10 | 503:48011 | SHORT RURAL | Planned Outage | 970057 | 15 | 475 | 7125 | 0.0043408 | 0.00091385
2013-05-10 | 217:33612 | URBAN | Planned Outage | 970062 | 4 | 215 | 860 | 0.00052394 | 0.00024369
2013-05-10 | 225:13446 | URBAN | Planned Outage | 970066 | 234 | 340 | 79560 | 0.048471 | 0.014256
2013-05-10 | 239:82131 | SHORT RURAL | Planned Outage | 970068 | 1 | 365 | 365 | 0.00022237 | 6.0923e-05
2013-05-10 | 265:81651 | URBAN | Planned Outage | 970073 | 16 | 200 | 3200 | 0.0019495 | 0.00097477
2013-05-12 | 265:81649 | URBAN | Planned Outage | 970083 | 22 | 180 | 3960 | 0.0024126 | 0.0013403
2013-05-12 | 224:80328 | URBAN | Planned Outage | 970089 | 17 | 330 | 5610 | 0.0034178 | 0.0010357
2013-05-10 | 501:48123 | SHORT RURAL | Planned Outage | 970115 | 41 | 505 | 20705 | 0.012614 | 0.0024979
2013-05-10 | 510:48164 | SHORT RURAL | Planned Outage | 970117 | 1 | 358 | 358 | 0.00021811 | 6.0923e-05
2013-05-10 | 507:80926 | URBAN | Planned Outage | 970121 | 1 | 635 | 635 | 0.00038686 | 6.0923e-05
2013-05-12 | 507:80923 | SHORT RURAL | Planned Outage | 970130 | 40 | 381 | 15240 | 0.0092847 | 0.0024369
2013-05-10 | 512:48049 | SHORT RURAL | Planned Outage | 970135 | 8 | 300 | 2400 | 0.0014622 | 0.00048739
2013-05-10 | 810:74054 | LONG RURAL | Planned Outage | 970139 | 2 | 215 | 430 | 0.00026197 | 0.00012185
2013-05-11 | 813:89061 | LONG RURAL | Planned Outage | 970141 | 10 | 105 | 1050 | 0.0006397 | 0.00060923
2013-05-12 | 523:33508 | SHORT RURAL | Planned Outage | 970165 | 110 | 400 | 44000 | 0.026806 | 0.0067016
2013-05-08 | ZN180:PA21 | URBAN | Planned Outage | 970185 | 38 | 420 | 15960 | 0.0097232 | 0.0023151
2013-05-08 | ZN15005:PA8 | URBAN | Planned Outage | 970231 | 56 | 510 | 28560 | 0.017399 | 0.0034117
2013-05-08 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 970232 | 22 | 450 | 1320 | 0.00080418 | 0.0013403
2013-05-08 | ZN12600:PA3 | URBAN | Planned Outage | 970235 | 81 | 480 | 38880 | 0.023687 | 0.0049347
2013-05-08 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 970237 | 2 | 480 | 960 | 0.00058486 | 0.00012184
2013-05-08 | ZN9900:PA17 | URBAN | Planned Outage | 970240 | 49 | 300 | 14700 | 0.0089556 | 0.0029852
2013-05-13 | 221:11899 | URBAN | Planned Outage | 970469 | 63 | 230 | 14490 | 0.0088278 | 0.0038382
2013-05-13 | 206:34440 | URBAN | Planned Outage | 970480 | 148 | 100 | 14800 | 0.0090167 | 0.0090167
2013-05-13 | 261:81882 | URBAN | Planned Outage | 970481 | 2 | 5 | 10 | 6.0923e-06 | 0.00012185
2013-05-13 | 261:81882 | URBAN | Planned Outage | 970482 | 2 | 5 | 10 | 6.0923e-06 | 0.00012185
2013-05-13 | 511:29878 | SHORT RURAL | Planned Outage | 970484 | 43 | 290 | 12470 | 0.0075972 | 0.0026197
2013-05-13 | 504:48031 | SHORT RURAL | Planned Outage | 970485 | 29 | 360 | 10440 | 0.0063604 | 0.0017668
2013-05-13 | 504:48031 | SHORT RURAL | Planned Outage | 970486 | 148 | 489 | 72372 | 0.044091 | 0.0090167
2013-05-13 | 807:74180 | SHORT RURAL | Planned Outage | 970510 | 21 | 285 | 5985 | 0.0036463 | 0.0012794
2013-05-09 | ZN15006:PA15 | URBAN | Planned Outage | 970587 | 42 | 540 | 22680 | 0.013817 | 0.0025588
2013-05-09 | ZN847:PA45 | SHORT RURAL | Planned Outage | 970589 | 4 | 420 | 1680 | 0.0010235 | 0.00024369
2013-05-09 | ZN12570:PA24 | SHORT RURAL | Planned Outage | 970608 | 13 | 480 | 6240 | 0.0038016 | 0.000792
2013-05-09 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 970623 | 4 | 480 | 1920 | 0.0011697 | 0.00024369
2013-05-09 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 970658 | 32 | 480 | 15360 | 0.0093578 | 0.0019495
2013-05-10 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 970665 | 7 | 480 | 3360 | 0.002047 | 0.00042646
2013-05-10 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 970670 | 12 | 480 | 5760 | 0.0035092 | 0.00073108
2013-05-10 | ZN2310:PA33 | URBAN | Planned Outage | 970713 | 7 | 240 | 1680 | 0.0010235 | 0.00042646
2013-05-10 | ZN874:PA25 | URBAN | Planned Outage | 970717 | 33 | 120 | 3960 | 0.0024126 | 0.0020105
2013-05-10 | ZN10999:PA19 | URBAN | Planned Outage | 970719 | 27 | 1320 | 35640 | 0.021713 | 0.0016449
2013-05-11 | ZN901:PA7 | URBAN | Planned Outage | 970729 | 5 | 15 | 75 | 4.5693e-05 | 0.00030462
2013-05-11 | ZN12650:PA16 | URBAN | Planned Outage | 970738 | 38 | 510 | 19380 | 0.011807 | 0.0023151
2013-05-11 | ZN340:PA24 | URBAN | Planned Outage | 970745 | 18 | 420 | 7560 | 0.0046058 | 0.0010966
2013-05-12 | ZN1068:PA11 | URBAN | Planned Outage | 970746 | 1 | 10 | 10 | 6.0923e-06 | 6.0923e-05
2013-05-12 | ZN2568:PA27 | URBAN | Planned Outage | 970748 | 85 | 360 | 30600 | 0.018643 | 0.0051785
2013-05-13 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 970751 | 10 | 360 | 3600 | 0.0021932 | 0.00060923
2013-05-13 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 970756 | 12 | 480 | 5760 | 0.0035092 | 0.00073108
2013-05-13 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 970758 | 11 | 480 | 5280 | 0.0032168 | 0.00067016
2013-05-13 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 970760 | 23 | 480 | 11040 | 0.0067259 | 0.0014012
2013-05-13 | ZN12660:PA14 | SHORT RURAL | Planned Outage | 970764 | 65 | 420 | 27300 | 0.016632 | 0.00396
2013-05-13 | ZN1610:PA23 | URBAN | Planned Outage | 970768 | 6 | 480 | 2880 | 0.0017546 | 0.00036554
2013-05-14 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 970951 | 279 | 480 | 133920 | 0.081581 | 0.016996
2013-05-14 | ZN13000:PA1 | URBAN | Planned Outage | 970971 | 521 | 480 | 31680 | 0.019299 | 0.031738
2013-05-14 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 970979 | 16 | 480 | 7680 | 0.0046785 | 0.00097469
2013-05-14 | ZN12580:PA4 | URBAN | Planned Outage | 970986 | 21 | 480 | 10080 | 0.0061405 | 0.0012793
2013-05-14 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 970988 | 6 | 240 | 1440 | 0.00087722 | 0.00036551
2013-05-14 | ZN4545:PA4 | URBAN | Planned Outage | 970990 | 65 | 390 | 25350 | 0.015443 | 0.0039597
2013-05-14 | 504:48031 | SHORT RURAL | Planned Outage | 970993 | 148 | 530 | 78440 | 0.047784 | 0.0090158
2013-05-14 | ZN1193:PA17 | URBAN | Planned Outage | 970996 | 3 | 420 | 1260 | 0.00076757 | 0.00018275
2013-05-14 | 504:48031 | SHORT RURAL | Planned Outage | 971002 | 21 | 475 | 9975 | 0.0060766 | 0.0012793
2013-05-14 | 210:8682 | URBAN | Planned Outage | 971005 | 95 | 360 | 34200 | 0.020834 | 0.0057872
2013-05-14 | 526:34636 | SHORT RURAL | Planned Outage | 971030 | 4 | 395 | 1580 | 0.0009625 | 0.00024367
2013-05-14 | 511:29873 | SHORT RURAL | Planned Outage | 971033 | 7 | 380 | 2660 | 0.0016204 | 0.00042643
2013-05-14 | 813:89061 | LONG RURAL | Planned Outage | 971037 | 9 | 310 | 2790 | 0.0016996 | 0.00054826
2013-05-14 | 523:33508 | SHORT RURAL | Planned Outage | 971040 | 18 | 275 | 4950 | 0.0030154 | 0.0010965
2013-05-15 | 504:48031 | SHORT RURAL | Planned Outage | 971350 | 148 | 540 | 79920 | 0.048687 | 0.009016
2013-05-15 | 243:80083 | SHORT RURAL | Planned Outage | 971352 | 78 | 200 | 15600 | 0.0095034 | 0.0047517
2013-05-15 | 229:34983 | SHORT RURAL | Planned Outage | 971355 | 5 | 75 | 375 | 0.00022845 | 0.0003046
2013-05-15 | 510:48164 | SHORT RURAL | Planned Outage | 971360 | 12 | 270 | 3240 | 0.0019738 | 0.00073103
2013-05-15 | 507:80932 | SHORT RURAL | Planned Outage | 971362 | 12 | 390 | 4680 | 0.002851 | 0.00073103
2013-05-15 | 509:48039 | LONG RURAL | Planned Outage | 971363 | 1 | 315 | 315 | 0.0001919 | 6.0919e-05
2013-05-15 | 515:35197 | LONG RURAL | Planned Outage | 971364 | 6 | 330 | 1980 | 0.0012062 | 0.00036552
2013-05-15 | 813:89062 | SHORT RURAL | Planned Outage | 971366 | 1 | 170 | 170 | 0.00010356 | 6.0919e-05
2013-05-15 | 813:89055 | SHORT RURAL | Planned Outage | 971368 | 2 | 260 | 520 | 0.00031678 | 0.00012184
2013-05-20 | ZN12660:PA14 | SHORT RURAL | Planned Outage | 972361 | 71 | 420 | 29820 | 0.018167 | 0.0043254
2013-05-16 | 511:29878 | SHORT RURAL | Planned Outage | 972414 | 37 | 405 | 14985 | 0.0091288 | 0.002254
2013-05-16 | 802:82215 | SHORT RURAL | Planned Outage | 972417 | 40 | 1 | 40 | 2.4368e-05 | 0.0024368
2013-05-16 | 802:82220 | SHORT RURAL | Planned Outage | 972417 | 60 | 1 | 60 | 3.6552e-05 | 0.0036552
2013-05-16 | 802:82225 | SHORT RURAL | Planned Outage | 972417 | 106 | 1 | 106 | 6.4575e-05 | 0.0064575
2013-05-16 | 802:82215 | SHORT RURAL | Planned Outage | 972418 | 40 | 2 | 80 | 4.8736e-05 | 0.0024368
2013-05-16 | 802:82220 | SHORT RURAL | Planned Outage | 972418 | 60 | 2 | 120 | 7.3104e-05 | 0.0036552
2013-05-16 | 802:82225 | SHORT RURAL | Planned Outage | 972418 | 106 | 2 | 212 | 0.00012915 | 0.0064575
2013-05-16 | 802:82215 | SHORT RURAL | Planned Outage | 972421 | 40 | 1 | 40 | 2.4368e-05 | 0.0024368
2013-05-16 | 802:82220 | SHORT RURAL | Planned Outage | 972421 | 60 | 1 | 60 | 3.6552e-05 | 0.0036552
2013-05-16 | 802:82225 | SHORT RURAL | Planned Outage | 972421 | 106 | 1 | 106 | 6.4575e-05 | 0.0064575
2013-05-20 | 515:35193 | SHORT RURAL | Planned Outage | 972451 | 1 | 133.6167 | 133.6167 | 8.1401e-05 | 6.0921e-05
2013-05-17 | 511:29878 | SHORT RURAL | Planned Outage | 972497 | 43 | 300 | 12900 | 0.0078588 | 0.0026196
2013-05-17 | 504:48031 | SHORT RURAL | Planned Outage | 972505 | 148 | 440 | 65120 | 0.039672 | 0.0090163
2013-05-19 | 203:8082 | URBAN | Planned Outage | 972515 | 5 | 290 | 1450 | 0.00088336 | 0.00030461
2013-05-17 | 265:81651 | URBAN | Planned Outage | 972520 | 9 | 370 | 3330 | 0.0020287 | 0.00054829
2013-05-18 | 265:81648 | URBAN | Planned Outage | 972523 | 12 | 270 | 3240 | 0.0019738 | 0.00073105
2013-05-18 | 265:81648 | URBAN | Planned Outage | 972524 | 1 | 205 | 205 | 0.00012489 | 6.0921e-05
2013-05-18 | 258:80787 | URBAN | Planned Outage | 972529 | 1 | 325 | 325 | 0.00019799 | 6.0921e-05
2013-05-16 | 264:81240 | SHORT RURAL | Planned Outage | 972536 | 1 | 430 | 430 | 0.00026196 | 6.092e-05
2013-05-16 | 504:48031 | SHORT RURAL | Planned Outage | 972541 | 149 | 470 | 70030 | 0.042662 | 0.0090771
2013-05-16 | 264:81240 | SHORT RURAL | Planned Outage | 972544 | 4 | 340 | 1360 | 0.00082851 | 0.00024368
2013-05-16 | 507:80922 | SHORT RURAL | Planned Outage | 972545 | 5 | 200 | 1000 | 0.0006092 | 0.0003046
2013-05-17 | 264:81240 | SHORT RURAL | Planned Outage | 972548 | 2 | 320 | 640 | 0.0003899 | 0.00012184
2013-05-17 | 524:33574 | SHORT RURAL | Planned Outage | 972552 | 4 | 160 | 640 | 0.0003899 | 0.00024368
2013-05-17 | 504:48033 | SHORT RURAL | Planned Outage | 972557 | 12 | 330 | 3960 | 0.0024125 | 0.00073105
2013-05-17 | 525:34586 | SHORT RURAL | Planned Outage | 972559 | 1 | 352 | 352 | 0.00021444 | 6.0921e-05
2013-05-18 | 504:48034 | URBAN | Planned Outage | 972563 | 75 | 350 | 26250 | 0.015992 | 0.0045691
2013-05-16 | 813:89061 | LONG RURAL | Planned Outage | 972566 | 6 | 295 | 1770 | 0.0010783 | 0.00036552
2013-05-16 | 803:74007 | SHORT RURAL | Planned Outage | 972571 | 49 | 290 | 14210 | 0.0086567 | 0.0029851
2013-05-17 | 803:74007 | SHORT RURAL | Planned Outage | 972572 | 49 | 170 | 8330 | 0.0050747 | 0.0029851
2013-05-17 | 513:48059 | SHORT RURAL | Planned Outage | 972573 | 47 | 380 | 17860 | 0.010881 | 0.0028633
2013-05-17 | 813:89062 | SHORT RURAL | Planned Outage | 972574 | 3 | 150 | 450 | 0.00027415 | 0.00018276
2013-05-17 | 801:74119 | URBAN | Planned Outage | 972575 | 52 | 370 | 19240 | 0.011721 | 0.0031679
2013-05-17 | 807:74179 | SHORT RURAL | Planned Outage | 972576 | 2 | 158 | 316 | 0.00019251 | 0.00012184
2013-05-19 | 520:48172 | SHORT RURAL | Planned Outage | 972580 | 3 | 165 | 495 | 0.00030156 | 0.00018276
2013-05-20 | 516:48066 | SHORT RURAL | Planned Outage | 972739 | 12 | 355 | 4260 | 0.0025952 | 0.00073105
2013-05-20 | 502:48010 | SHORT RURAL | Planned Outage | 972741 | 57 | 495 | 28215 | 0.017189 | 0.0034725
2013-05-20 | 264:81240 | SHORT RURAL | Planned Outage | 972746 | 29 | 330 | 9570 | 0.0058302 | 0.0017667
2013-05-20 | 509:48039 | LONG RURAL | Planned Outage | 972748 | 285 | 460 | 131100 | 0.079868 | 0.017363
2013-05-20 | 501:48124 | URBAN | Planned Outage | 972750 | 75 | 420 | 31500 | 0.01919 | 0.0045691
2013-05-15 | ZN12580:PA16 | URBAN | Planned Outage | 972892 | 18 | 390 | 7020 | 0.0042765 | 0.0010965
2013-05-15 | ZN13000:PA11 | URBAN | Planned Outage | 972897 | 65 | 510 | 33150 | 0.020195 | 0.0039597
2013-05-15 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 972939 | 11 | 180 | 1980 | 0.0012062 | 0.00067011
2013-05-15 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 972945 | 2 | 480 | 960 | 0.00058482 | 0.00012184
2013-05-15 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 972959 | 8 | 480 | 3840 | 0.0023393 | 0.00048735
2013-05-15 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 972968 | 4 | 480 | 1920 | 0.0011696 | 0.00024368
2013-05-15 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 972976 | 4 | 480 | 1920 | 0.0011696 | 0.00024368
2013-05-15 | ZN35370:PA10 | SHORT RURAL | Planned Outage | 973016 | 23 | 180 | 4140 | 0.0025221 | 0.0014011
2013-05-15 | ZN3288:PA41 42KLM | CBD | Planned Outage | 973023 | 5 | 300 | 1500 | 0.00091379 | 0.0003046
2013-05-15 | ZN12570:PA40 | SHORT RURAL | Planned Outage | 973026 | 81 | 180 | 14580 | 0.008882 | 0.0049345
2013-05-15 | ZN269:PA9 | URBAN | Planned Outage | 973030 | 127 | 510 | 64770 | 0.039457 | 0.0077367
2013-05-16 | ZN847:PA22 | SHORT RURAL | Planned Outage | 973036 | 1 | 390 | 390 | 0.00023759 | 6.092e-05
2013-05-16 | ZN269:PA19 | URBAN | Planned Outage | 973037 | 104 | 510 | 53040 | 0.032312 | 0.0063357
2013-05-16 | ZN14143:PA10 | SHORT RURAL | Planned Outage | 973039 | 1 | 540 | 540 | 0.00032897 | 6.092e-05
2013-05-16 | ZN12630:PA3 | SHORT RURAL | Planned Outage | 973045 | 19 | 480 | 9120 | 0.0055559 | 0.0011575
2013-05-16 | ZN12570:PA24 | SHORT RURAL | Planned Outage | 973050 | 5 | 480 | 2400 | 0.0014621 | 0.0003046
2013-05-21 | 512:48046 | SHORT RURAL | Planned Outage | 973211 | 138 | 360 | 49680 | 0.030266 | 0.0084073
2013-05-21 | 227:13019 | SHORT RURAL | Planned Outage | 973219 | 4 | 330 | 1320 | 0.00080418 | 0.00024369
2013-05-21 | 510:48164 | SHORT RURAL | Planned Outage | 973222 | 4 | 400 | 1600 | 0.00097476 | 0.00024369
2013-05-21 | 511:29877 | SHORT RURAL | Planned Outage | 973226 | 40 | 50 | 2000 | 0.0012184 | 0.0024369
2013-05-21 | 512:48049 | SHORT RURAL | Planned Outage | 973228 | 2 | 23 | 46 | 2.8024e-05 | 0.00012184
2013-05-21 | 813:89061 | LONG RURAL | Planned Outage | 973230 | 10 | 310 | 3100 | 0.0018886 | 0.00060922
2013-05-22 | 239:82128 | SHORT RURAL | Planned Outage | 973292 | 137 | 305 | 41785 | 0.025457 | 0.0083465
2013-05-22 | 813:89061 | LONG RURAL | Planned Outage | 973310 | 1 | 15.5833 | 15.5833 | 9.4939e-06 | 6.0923e-05
2013-05-16 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 973806 | 7 | 480 | 3360 | 0.0020469 | 0.00042644
2013-05-17 | ZN180:PA7 | URBAN | Planned Outage | 973817 | 151 | 540 | 81540 | 0.049675 | 0.0091991
2013-05-17 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 973819 | 3 | 480 | 1440 | 0.00087726 | 0.00018276
2013-05-17 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 973828 | 7 | 480 | 3360 | 0.002047 | 0.00042645
2013-05-17 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 973836 | 20 | 390 | 3720 | 0.0022663 | 0.0012184
2013-05-17 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 973847 | 5 | 420 | 2100 | 0.0012793 | 0.00030461
2013-05-18 | ZN5868:PA24 | URBAN | Planned Outage | 973890 | 9 | 250 | 2250 | 0.0013707 | 0.00054829
2013-05-19 | ZN12580:PA1 | URBAN | Planned Outage | 973893 | 3 | 540 | 1620 | 0.00098692 | 0.00018276
2013-05-19 | ZN2602:PA36 | URBAN | Planned Outage | 973895 | 5 | 420 | 2100 | 0.0012793 | 0.00030461
2013-05-22 | 265:81648 | URBAN | Planned Outage | 973907 | 2 | 315 | 630 | 0.00038382 | 0.00012185
2013-05-22 | 504:48031 | SHORT RURAL | Planned Outage | 973912 | 1 | 555 | 555 | 0.00033812 | 6.0923e-05
2013-05-22 | 507:80932 | SHORT RURAL | Planned Outage | 973913 | 1 | 290 | 290 | 0.00017668 | 6.0923e-05
2013-05-22 | 264:81240 | SHORT RURAL | Planned Outage | 973917 | 28 | 405 | 11340 | 0.0069087 | 0.0017059
2013-05-22 | 509:48039 | LONG RURAL | Planned Outage | 973921 | 4 | 390 | 1560 | 0.0009504 | 0.00024369
2013-05-22 | 812:19066 | SHORT RURAL | Planned Outage | 973923 | 45 | 188 | 8460 | 0.0051541 | 0.0027415
2013-05-22 | 813:89061 | LONG RURAL | Planned Outage | 973926 | 4 | 330 | 1320 | 0.00080419 | 0.00024369
2013-05-22 | 523:33508 | SHORT RURAL | Planned Outage | 973934 | 6 | 235 | 1410 | 0.00085902 | 0.00036554
2013-05-22 | 813:89062 | SHORT RURAL | Planned Outage | 973938 | 16 | 215 | 3440 | 0.0020958 | 0.00097477
2013-05-20 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 973942 | 1 | 480 | 480 | 0.00029242 | 6.0921e-05
2013-05-20 | ZN12650:PA17 | URBAN | Planned Outage | 974021 | 17 | 240 | 4080 | 0.0024856 | 0.0010357
2013-05-20 | ZN2473:PA15 | URBAN | Planned Outage | 974025 | 111 | 120 | 13320 | 0.0081147 | 0.0067622
2013-05-21 | ZN2473:PA26 | URBAN | Planned Outage | 974026 | 41 | 480 | 19680 | 0.01199 | 0.0024978
2013-05-21 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 974030 | 11 | 480 | 5280 | 0.0032167 | 0.00067015
2013-05-21 | ZN12650:PA13 | SHORT RURAL | Planned Outage | 974035 | 97 | 480 | 46560 | 0.028366 | 0.0059095
2013-05-23 | 235:2120 | SHORT RURAL | Planned Outage | 974367 | 76 | 350 | 26600 | 0.016206 | 0.0046302
2013-05-21 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 974472 | 16 | 480 | 7680 | 0.0046788 | 0.00097476
2013-05-21 | ZN12600:PA9 | SHORT RURAL | Planned Outage | 974478 | 34 | 480 | 16320 | 0.0099426 | 0.0020714
2013-05-21 | ZN12650:PA9 | URBAN | Planned Outage | 974478 | 66 | 480 | 31680 | 0.0193 | 0.0040209
2013-05-21 | ZN3425:PA28 | URBAN | Planned Outage | 974479 | 15 | 240 | 3600 | 0.0021932 | 0.00091384
2013-05-21 | ZN874:PA22 | URBAN | Planned Outage | 974480 | 12 | 390 | 4680 | 0.0028512 | 0.00073107
2013-05-22 | ZN180:PA21 | URBAN | Planned Outage | 974481 | 80 | 510 | 40800 | 0.024857 | 0.0048739
2013-05-22 | ZN12660:PA10 | SHORT RURAL | Planned Outage | 974487 | 32 | 180 | 5760 | 0.0035092 | 0.0019495
2013-05-22 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 974500 | 18 | 480 | 8640 | 0.0052638 | 0.0010966
2013-05-22 | ZN12570:PA35 | URBAN | Planned Outage | 974503 | 168 | 480 | 80640 | 0.049129 | 0.010235
2013-05-22 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 974994 | 2 | 480 | 960 | 0.00058486 | 0.00012185
2013-05-22 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 974996 | 32 | 420 | 13440 | 0.0081881 | 0.0019495
2013-05-22 | ZN711:PA12 | URBAN | Planned Outage | 975002 | 2 | 240 | 480 | 0.00029243 | 0.00012185
2013-05-23 | ZN180:PA7 | URBAN | Planned Outage | 975012 | 33 | 360 | 11880 | 0.0072378 | 0.0020105
2013-05-22 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 975059 | 37 | 1920 | 71040 | 0.04328 | 0.0022542
2013-05-23 | ZN10999:PA12 | URBAN | Planned Outage | 975074 | 49 | 480 | 23520 | 0.014329 | 0.0029853
2013-05-23 | ZN12570:PA41 | URBAN | Planned Outage | 975089 | 3 | 420 | 1260 | 0.00076764 | 0.00018277
2013-05-24 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 975090 | 7 | 480 | 3360 | 0.0020471 | 0.00042647
2013-05-24 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 975093 | 3 | 480 | 1440 | 0.00087731 | 0.00018277
2013-05-24 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 975097 | 2 | 480 | 960 | 0.00058487 | 0.00012185
2013-05-25 | ZN1610:PA14 | URBAN | Planned Outage | 975102 | 327 | 30 | 9810 | 0.0059767 | 0.019922
2013-05-25 | ZN12650:PA16 | URBAN | Planned Outage | 975106 | 2 | 330 | 660 | 0.0004021 | 0.00012185
2013-05-25 | ZN340:PA24 | URBAN | Planned Outage | 975111 | 18 | 420 | 7560 | 0.0046059 | 0.0010966
2013-05-25 | ZN2568:PA21 | URBAN | Planned Outage | 975115 | 1 | 540 | 540 | 0.00032899 | 6.0924e-05
2013-05-26 | ZN2473:PA34 | URBAN | Planned Outage | 975119 | 42 | 30 | 1260 | 0.00076765 | 0.0025588
2013-05-26 | ZN129:PA12 | URBAN | Planned Outage | 975126 | 3 | 35 | 105 | 6.397e-05 | 0.00018277
2013-05-25 | 265:81651 | URBAN | Planned Outage | 975290 | 60 | 490 | 29400 | 0.017912 | 0.0036555
2013-05-24 | 217:33612 | URBAN | Planned Outage | 975298 | 88 | 155 | 13640 | 0.0083101 | 0.0053613
2013-05-26 | 258:80781 | SHORT RURAL | Planned Outage | 975312 | 4 | 565 | 2260 | 0.0013769 | 0.0002437
2013-05-24 | 508:82578 | SHORT RURAL | Planned Outage | 975316 | 27 | 270 | 7290 | 0.0044414 | 0.001645
2013-05-24 | 264:81240 | SHORT RURAL | Planned Outage | 975319 | 14 | 270 | 3780 | 0.0023029 | 0.00085294
2013-05-25 | 806:82662 | SHORT RURAL | Planned Outage | 975321 | 5 | 155 | 775 | 0.00047216 | 0.00030462
2013-05-27 | 508:82578 | SHORT RURAL | Planned Outage | 975507 | 4 | 385 | 1540 | 0.00093823 | 0.0002437
2013-05-27 | 807:74179 | SHORT RURAL | Planned Outage | 975513 | 3 | 220 | 660 | 0.0004021 | 0.00018277
2013-05-27 | 513:48059 | SHORT RURAL | Planned Outage | 975514 | 7 | 135 | 945 | 0.00057573 | 0.00042647
2013-05-27 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 975662 | 13 | 615 | 3540 | 0.0021567 | 0.00079202
2013-05-27 | ZN2835:PA30 | URBAN | Planned Outage | 975675 | 93 | 360 | 33480 | 0.020397 | 0.005666
2013-05-27 | ZN2835:PA30 | URBAN | Planned Outage | 975676 | 42 | 360 | 15120 | 0.0092117 | 0.0025588
2013-05-27 | ZN12650:PA17 | URBAN | Planned Outage | 975677 | 52 | 630 | 32760 | 0.019959 | 0.0031681
2013-05-27 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 975680 | 82 | 480 | 39360 | 0.02398 | 0.0049958
2013-05-27 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 975696 | 26 | 480 | 12480 | 0.0076033 | 0.001584
2013-05-27 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 975713 | 3 | 360 | 1080 | 0.00065798 | 0.00018277
2013-05-27 | ZN1610:PA4 | URBAN | Planned Outage | 975716 | 42 | 60 | 2520 | 0.0015353 | 0.0025588
2013-05-28 | ZN2835:PA21 | URBAN | Planned Outage | 975720 | 87 | 360 | 31320 | 0.019073 | 0.005298
2013-05-28 | ZN13000:PA11 | URBAN | Planned Outage | 975906 | 4 | 510 | 2040 | 0.0012423 | 0.00024359
2013-05-28 | ZN13000:PA1 | URBAN | Planned Outage | 975909 | 521 | 480 | 31680 | 0.019292 | 0.031727
2013-05-28 | ZN12580:PA4 | URBAN | Planned Outage | 975913 | 79 | 480 | 37920 | 0.023092 | 0.0048109
2013-05-28 | ZN12580:PA4 | URBAN | Planned Outage | 975926 | 44 | 480 | 21120 | 0.012861 | 0.0026795
2013-05-28 | ZN965:PA8 | URBAN | Planned Outage | 975930 | 28 | 120 | 3360 | 0.0020461 | 0.0017051
2013-05-28 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 975934 | 7 | 450 | 3150 | 0.0019183 | 0.00042628
2013-05-28 | ZN14891:PA1 | SHORT RURAL | Planned Outage | 975937 | 13 | 330 | 4290 | 0.0026125 | 0.00079166
2013-05-28 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 975937 | 5 | 330 | 1650 | 0.0010048 | 0.00030449
2013-05-28 | ZN12650:PA20 | URBAN | Planned Outage | 975941 | 60 | 420 | 25200 | 0.015346 | 0.0036538
2013-05-29 | ZN2568:PA9 | URBAN | Planned Outage | 975943 | 109 | 75 | 8175 | 0.0049784 | 0.0066378
2013-05-29 | 813:89063 | SHORT RURAL | Planned Outage | 975951 | 33 | 245 | 8085 | 0.0049236 | 0.0020096
2013-05-29 | 807:74184 | SHORT RURAL | Planned Outage | 976025 | 73 | 285 | 20805 | 0.01267 | 0.0044455
2013-05-29 | ZN12650:PA20 | URBAN | Planned Outage | 976205 | 1 | 214.1333 | 214.1333 | 0.0001304 | 6.0898e-05
2013-05-29 | ZN12650:PA20 | URBAN | Planned Outage | 976209 | 1 | 188.5167 | 188.5167 | 0.0001148 | 6.0898e-05
2013-05-29 | ZN12650:PA20 | URBAN | Planned Outage | 976324 | 608 | 540 | 197760 | 0.12043 | 0.037026
2013-05-29 | ZN129:PA5 | URBAN | Planned Outage | 976340 | 57 | 480 | 27360 | 0.016662 | 0.0034712
2013-05-29 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 976342 | 2 | 480 | 60 | 3.6539e-05 | 0.0001218
2013-05-29 | ZN12650:PA6 | URBAN | Planned Outage | 976381 | 12 | 240 | 2880 | 0.0017539 | 0.00073077
2013-05-29 | ZN180:PA7 | URBAN | Planned Outage | 976385 | 33 | 420 | 13860 | 0.0084404 | 0.0020096
2013-05-30 | 507:80925 | SHORT RURAL | Planned Outage | 976413 | 261 | 300 | 78300 | 0.047684 | 0.015895
2013-05-29 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 976424 | 60 | 480 | 28800 | 0.017539 | 0.0036539
2013-05-30 | 813:89061 | LONG RURAL | Planned Outage | 976443 | 130 | 405 | 52650 | 0.032064 | 0.0079169
2013-05-29 | 512:48049 | SHORT RURAL | Planned Outage | 976487 | 15 | 225 | 3375 | 0.0020553 | 0.00091347
2013-05-29 | 224:80332 | URBAN | Planned Outage | 976493 | 194 | 240 | 46560 | 0.028354 | 0.011814
2013-05-29 | 512:48049 | SHORT RURAL | Planned Outage | 976507 | 26 | 55 | 1430 | 0.00087084 | 0.0015833
2013-05-30 | 220:8689 | URBAN | Planned Outage | 976510 | 43 | 120 | 5160 | 0.0031424 | 0.0026187
2013-05-28 | 216:10723 | URBAN | Planned Outage | 976513 | 1 | 195 | 195 | 0.00011875 | 6.0897e-05
2013-05-28 | 258:80787 | URBAN | Planned Outage | 976516 | 170 | 300 | 51000 | 0.031058 | 0.010353
2013-05-29 | 227:13019 | SHORT RURAL | Planned Outage | 976518 | 7 | 245 | 1715 | 0.0010444 | 0.00042628
2013-05-29 | 508:82578 | SHORT RURAL | Planned Outage | 976520 | 2 | 300 | 600 | 0.00036539 | 0.0001218
2013-05-28 | 511:29878 | SHORT RURAL | Planned Outage | 976521 | 7 | 25 | 175 | 0.00010657 | 0.00042628
2013-05-28 | 511:29878 | SHORT RURAL | Planned Outage | 976523 | 2 | 25 | 50 | 3.0449e-05 | 0.00012179
2013-05-29 | 264:81240 | SHORT RURAL | Planned Outage | 976527 | 13 | 300 | 3900 | 0.002375 | 0.00079167
2013-05-29 | 511:29878 | SHORT RURAL | Planned Outage | 976528 | 16 | 330 | 5280 | 0.0032154 | 0.00097436
2013-05-29 | ZN384:PA9 | URBAN | Planned Outage | 976762 | 54 | 300 | 16200 | 0.0098654 | 0.0032885
2013-05-29 | ZN12610:PA20 | SHORT RURAL | Planned Outage | 976763 | 26 | 450 | 11700 | 0.007125 | 0.0015833
2013-05-29 | ZN3288:PA43 44GHJ | CBD | Planned Outage | 976766 | 70 | 540 | 37800 | 0.023019 | 0.0042628
2013-05-28 | 807:74180 | SHORT RURAL | Planned Outage | 976769 | 8 | 85 | 680 | 0.0004141 | 0.00048718
2013-05-28 | 813:89055 | SHORT RURAL | Planned Outage | 976771 | 8 | 235 | 1880 | 0.0011449 | 0.00048718
2013-05-28 | 513:48056 | SHORT RURAL | Planned Outage | 976776 | 6 | 285 | 1710 | 0.0010413 | 0.00036538
2013-05-29 | 520:48172 | SHORT RURAL | Planned Outage | 976784 | 2 | 100 | 200 | 0.0001218 | 0.0001218
2013-05-29 | 806:82662 | SHORT RURAL | Planned Outage | 976792 | 1 | 295 | 295 | 0.00017965 | 6.0898e-05
2013-05-29 | 813:89063 | SHORT RURAL | Planned Outage | 976795 | 32 | 245 | 7840 | 0.0047744 | 0.0019487
2013-05-27 | 807:74180 | SHORT RURAL | Planned Outage | 976804 | 3 | 3150 | 9450 | 0.0057573 | 0.00018277
2013-06-01 | 265:81651 | URBAN | Planned Outage | 977909 | 66 | 380 | 25080 | 0.015274 | 0.0040194
2013-05-30 | ZN180:PA7 | URBAN | Planned Outage | 978113 | 33 | 480 | 15840 | 0.0096465 | 0.0020097
2013-05-30 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 978116 | 2 | 480 | 960 | 0.00058463 | 0.0001218
2013-05-30 | 523:33501 | SHORT RURAL | Planned Outage | 978118 | 6 | 165 | 990 | 0.0006029 | 0.0003654
2013-05-30 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 978120 | 4 | 390 | 1560 | 0.00095003 | 0.0002436
2013-05-30 | 227:13015 | SHORT RURAL | Planned Outage | 978124 | 6 | 305 | 1830 | 0.0011145 | 0.0003654
2013-05-30 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 978125 | 3 | 390 | 1170 | 0.00071252 | 0.0001827
2013-05-30 | ZN10999:PA36 | URBAN | Planned Outage | 978126 | 52 | 330 | 17160 | 0.01045 | 0.0031668
2013-05-31 | 225:33670 | SHORT RURAL | Planned Outage | 978128 | 11 | 325 | 3575 | 0.0021772 | 0.0006699
2013-05-31 | 213:33773 | SHORT RURAL | Planned Outage | 978135 | 84 | 330 | 27720 | 0.016881 | 0.0051156
2013-05-30 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 978136 | 43 | 420 | 18060 | 0.010998 | 0.0026187
2013-05-31 | ZN12620:PA8 | SHORT RURAL | Planned Outage | 978139 | 17 | 480 | 1440 | 0.00087696 | 0.0010353
2013-05-30 | 510:48164 | SHORT RURAL | Planned Outage | 978147 | 12 | 414 | 4968 | 0.0030255 | 0.00073079
2013-05-30 | 238:34141 | SHORT RURAL | Planned Outage | 978168 | 4 | 245 | 980 | 0.00059681 | 0.0002436
2013-05-30 | 515:35197 | LONG RURAL | Planned Outage | 978385 | 1 | 6 | 6 | 3.654e-06 | 6.0899e-05
2013-05-30 | 523:33508 | SHORT RURAL | Planned Outage | 978390 | 9 | 311 | 2799 | 0.0017046 | 0.00054809
2013-05-30 | 813:89063 | SHORT RURAL | Planned Outage | 978401 | 65 | 285 | 18525 | 0.011282 | 0.0039585
2013-05-30 | 803:74007 | SHORT RURAL | Planned Outage | 978419 | 14 | 455 | 6370 | 0.0038793 | 0.00085259
2013-05-31 | 512:48046 | SHORT RURAL | Planned Outage | 978422 | 9 | 360 | 3240 | 0.0019732 | 0.0005481
2013-05-31 | 806:82667 | SHORT RURAL | Planned Outage | 978423 | 9 | 235 | 2115 | 0.001288 | 0.0005481
2013-05-31 | 801:74121 | SHORT RURAL | Planned Outage | 978432 | 9 | 285 | 2565 | 0.0015621 | 0.0005481
2013-05-31 | 812:19071 | SHORT RURAL | Planned Outage | 978437 | 4 | 270 | 1080 | 0.00065772 | 0.0002436
2013-05-31 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 978448 | 91 | 480 | 43680 | 0.026601 | 0.0055419
2013-06-01 | 806:82662 | SHORT RURAL | Planned Outage | 978451 | 2 | 240 | 480 | 0.00029232 | 0.0001218
2013-05-31 | ZN269:PA16 | URBAN | Planned Outage | 978456 | 152 | 240 | 36480 | 0.022216 | 0.0092568
2013-05-31 | ZN180:PA7 | URBAN | Planned Outage | 978464 | 66 | 300 | 19800 | 0.012058 | 0.0040194
2013-06-01 | ZN3288:PA41 42DEF | CBD | Planned Outage | 978472 | 38 | 540 | 20520 | 0.012497 | 0.0023142
2013-06-01 | ZN9118:PA7 | URBAN | Planned Outage | 978474 | 3 | 660 | 1980 | 0.0012058 | 0.0001827
2013-06-01 | ZN8100:PA1 | URBAN | Planned Outage | 978476 | 6 | 480 | 2880 | 0.0017539 | 0.0003654
2013-06-01 | ZN12650:PA14 | URBAN | Planned Outage | 978477 | 21 | 480 | 10080 | 0.0061387 | 0.0012789
2013-06-01 | ZN4990:PA55 56KLM | CBD | Planned Outage | 978478 | 1 | 720 | 720 | 0.00043848 | 6.09e-05
2013-06-02 | ZN2196:PA2 | URBAN | Planned Outage | 978480 | 2 | 600 | 1200 | 0.0007308 | 0.0001218
2013-06-02 | 801:74122 | URBAN | Planned Outage | 978525 | 84 | 280 | 23520 | 0.014324 | 0.0051156
2013-06-03 | 265:81651 | URBAN | Planned Outage | 978531 | 9 | 360 | 3240 | 0.0019732 | 0.0005481
2013-06-04 | 261:81885 | URBAN | Planned Outage | 978532 | 17 | 90 | 1530 | 0.00093122 | 0.0010347
2013-06-03 | 240:34835 | URBAN | Planned Outage | 978534 | 12 | 550 | 6600 | 0.0040194 | 0.0007308
2013-06-03 | 812:19072 | SHORT RURAL | Planned Outage | 978537 | 1 | 130 | 130 | 7.917e-05 | 6.09e-05
2013-06-03 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 978545 | 109 | 480 | 52320 | 0.031863 | 0.0066381
2013-06-03 | ZN129:PA5 | URBAN | Planned Outage | 978617 | 65 | 510 | 33150 | 0.020188 | 0.0039585
2013-06-03 | ZN12600:PA5 | URBAN | Planned Outage | 978621 | 29 | 480 | 13920 | 0.0084772 | 0.0017661
2013-06-03 | ZN12610:PA18 | URBAN | Planned Outage | 978661 | 28 | 480 | 13440 | 0.0081849 | 0.0017052
2013-06-03 | ZN12600:PA3 | URBAN | Planned Outage | 978662 | 81 | 480 | 38880 | 0.023678 | 0.0049329
2013-06-03 | ZN3425:PA34 | URBAN | Planned Outage | 978665 | 4 | 450 | 1800 | 0.0010962 | 0.0002436
2013-06-04 | ZN3425:PA18 | SHORT RURAL | Planned Outage | 978666 | 72 | 60 | 4320 | 0.0026293 | 0.0043822
2013-06-04 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 979073 | 320 | 60 | 19200 | 0.011686 | 0.019477
2013-06-04 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 979077 | 320 | 60 | 19200 | 0.011686 | 0.019477
2013-06-04 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 979087 | 7 | 480 | 3360 | 0.002045 | 0.00042605
2013-06-05 | ZN15001:PA4 | URBAN | Planned Outage | 979092 | 322 | 59 | 18998 | 0.011563 | 0.019599
2013-06-05 | ZN15001:PA17 | URBAN | Planned Outage | 979095 | 7 | 90 | 630 | 0.00038345 | 0.00042605
2013-06-04 | 229:34983 | SHORT RURAL | Planned Outage | 979096 | 19 | 222 | 4218 | 0.0025673 | 0.0011564
2013-06-04 | 227:13015 | SHORT RURAL | Planned Outage | 979099 | 50 | 280 | 14000 | 0.008521 | 0.0030432
2013-06-04 | 509:48039 | LONG RURAL | Planned Outage | 979101 | 1 | 100 | 100 | 6.0864e-05 | 6.0864e-05
2013-06-04 | 221:11899 | URBAN | Planned Outage | 979106 | 63 | 130 | 8190 | 0.0049848 | 0.0038345
2013-06-04 | 507:80922 | SHORT RURAL | Planned Outage | 979107 | 5 | 325 | 1625 | 0.00098905 | 0.00030432
2013-06-04 | 504:48031 | SHORT RURAL | Planned Outage | 979108 | 20 | 284 | 5680 | 0.0034571 | 0.0012173
2013-06-04 | 509:48039 | LONG RURAL | Planned Outage | 979110 | 2 | 100 | 200 | 0.00012173 | 0.00012173
2013-06-04 | 514:18137 | SHORT RURAL | Planned Outage | 979111 | 9 | 360 | 3240 | 0.001972 | 0.00054778
2013-06-05 | 812:19066 | SHORT RURAL | Planned Outage | 979318 | 19 | 485 | 9215 | 0.0056087 | 0.0011564
2013-06-05 | 229:34995 | SHORT RURAL | Planned Outage | 979321 | 8 | 360 | 2880 | 0.0017529 | 0.00048692
2013-06-05 | ZN129:PA5 | URBAN | Planned Outage | 979386 | 57 | 510 | 29070 | 0.017693 | 0.0034693
2013-06-05 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 979407 | 196 | 480 | 12600 | 0.007669 | 0.01193
2013-06-05 | ZN711:PA34 | URBAN | Planned Outage | 979418 | 359 | 25 | 8975 | 0.0054626 | 0.021851
2013-06-05 | ZN3922:PA2 | SHORT RURAL | Planned Outage | 979426 | 80 | 360 | 28800 | 0.017529 | 0.0048692
2013-06-04 | ZN3155:PA21 | URBAN | Planned Outage | 979427 | 90 | 240 | 21600 | 0.013147 | 0.0054778
2013-06-06 | ZN15009:PA9 | URBAN | Planned Outage | 979442 | 136 | 120 | 16320 | 0.0099333 | 0.0082777
2013-06-07 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 979738 | 95 | 480 | 45600 | 0.027755 | 0.0057823
2013-06-06 | 205:12206 | URBAN | Planned Outage | 979804 | 3 | 490 | 1470 | 0.00089472 | 0.0001826
2013-06-06 | 264:81244 | URBAN | Planned Outage | 979836 | 78 | 315 | 24570 | 0.014955 | 0.0047475
2013-06-06 | 243:80075 | SHORT RURAL | Planned Outage | 979838 | 2 | 300 | 600 | 0.00036519 | 0.00012173
2013-06-06 | 511:29878 | SHORT RURAL | Planned Outage | 979839 | 1 | 215 | 215 | 0.00013086 | 6.0866e-05
2013-06-06 | 503:48011 | SHORT RURAL | Planned Outage | 979840 | 14 | 435 | 6090 | 0.0037067 | 0.00085212
2013-06-06 | 807:74184 | SHORT RURAL | Planned Outage | 979848 | 12 | 330 | 3960 | 0.0024103 | 0.00073039
2013-06-06 | 515:35197 | LONG RURAL | Planned Outage | 979851 | 1 | 95 | 95 | 5.7822e-05 | 6.0866e-05
2013-06-06 | 813:89061 | LONG RURAL | Planned Outage | 979854 | 10 | 335 | 3350 | 0.002039 | 0.00060866
2013-06-06 | 520:48172 | SHORT RURAL | Planned Outage | 979856 | 4 | 340 | 1360 | 0.00082777 | 0.00024346
2013-06-06 | 515:35197 | LONG RURAL | Planned Outage | 979858 | 2 | 70 | 140 | 8.5212e-05 | 0.00012173
2013-06-06 | 806:82662 | SHORT RURAL | Planned Outage | 979859 | 1 | 105 | 105 | 6.3909e-05 | 6.0866e-05
2013-06-06 | ZN874:PA8 | URBAN | Planned Outage | 981586 | 4 | 600 | 2400 | 0.0014608 | 0.00024346
2013-06-07 | 507:80922 | SHORT RURAL | Planned Outage | 981669 | 48 | 260 | 12480 | 0.0075961 | 0.0029216
2013-06-07 | 229:34995 | SHORT RURAL | Planned Outage | 981675 | 198 | 100 | 19800 | 0.012051 | 0.012051
2013-06-08 | 258:80793 | SHORT RURAL | Planned Outage | 981678 | 12 | 470 | 5640 | 0.0034328 | 0.00073039
2013-06-07 | 503:48011 | SHORT RURAL | Planned Outage | 981679 | 140 | 310 | 43400 | 0.026416 | 0.0085213
2013-06-07 | 509:48039 | LONG RURAL | Planned Outage | 981681 | 12 | 230 | 2760 | 0.0016799 | 0.00073039
2013-06-07 | 509:48039 | LONG RURAL | Planned Outage | 981683 | 1 | 180 | 180 | 0.00010956 | 6.0866e-05
2013-06-07 | 523:33508 | SHORT RURAL | Planned Outage | 981724 | 1 | 60 | 60 | 3.652e-05 | 6.0866e-05
2013-06-07 | 515:35192 | SHORT RURAL | Planned Outage | 981725 | 1 | 75 | 75 | 4.565e-05 | 6.0866e-05
2013-06-07 | 806:82662 | SHORT RURAL | Planned Outage | 981729 | 33 | 165 | 5445 | 0.0033142 | 0.0020086
2013-06-07 | 515:35193 | SHORT RURAL | Planned Outage | 981730 | 18 | 377 | 6786 | 0.0041304 | 0.0010956
2013-06-06 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 981761 | 6 | 540 | 360 | 0.00021912 | 0.00036519
2013-06-06 | ZN14143:PA12 | SHORT RURAL | Planned Outage | 981770 | 2 | 480 | 960 | 0.00058431 | 0.00012173
2013-06-06 | ZN14143:PA5 | URBAN | Planned Outage | 981770 | 3 | 480 | 600 | 0.00036519 | 0.0001826
2013-06-06 | ZN14892:PA14 | SHORT RURAL | Planned Outage | 981776 | 20 | 420 | 8400 | 0.0051127 | 0.0012173
2013-06-08 | ZN2196:PA28 | URBAN | Planned Outage | 981779 | 22 | 150 | 3300 | 0.0020086 | 0.0013391
2013-06-08 | ZN1788:PA29 | URBAN | Planned Outage | 981783 | 7 | 660 | 4620 | 0.002812 | 0.00042606
2013-06-06 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 981789 | 165 | 480 | 79200 | 0.048206 | 0.010043
2013-06-11 | 813:89061 | LONG RURAL | Planned Outage | 981960 | 1 | 60 | 60 | 3.652e-05 | 6.0866e-05
2013-06-11 | 206:34434 | URBAN | Planned Outage | 981966 | 159 | 130 | 20670 | 0.012581 | 0.0096777
2013-06-11 | 202:34249 | URBAN | Planned Outage | 981969 | 33 | 150 | 4950 | 0.0030129 | 0.0020086
2013-06-11 | 526:34636 | SHORT RURAL | Planned Outage | 982001 | 1 | 30 | 30 | 1.826e-05 | 6.0866e-05
2013-06-11 | 526:34639 | SHORT RURAL | Planned Outage | 982004 | 4 | 440 | 1760 | 0.0010712 | 0.00024346
2013-06-11 | 526:34636 | SHORT RURAL | Planned Outage | 982006 | 6 | 410 | 2460 | 0.0014973 | 0.0003652
2013-06-11 | 512:48049 | SHORT RURAL | Planned Outage | 982009 | 2 | 45 | 90 | 5.4779e-05 | 0.00012173
2013-06-11 | 806:82662 | SHORT RURAL | Planned Outage | 982014 | 3 | 65 | 195 | 0.00011869 | 0.0001826
2013-06-07 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 982082 | 116 | 480 | 7380 | 0.0044919 | 0.0070605
2013-06-07 | ZN3922:PA3 | URBAN | Planned Outage | 982219 | 18 | 360 | 6480 | 0.0039441 | 0.0010956
2013-06-08 | ZN874:PA9 | URBAN | Planned Outage | 982223 | 1 | 10 | 10 | 6.0866e-06 | 6.0866e-05
2013-06-08 | ZN5868:PA14 | URBAN | Planned Outage | 982228 | 1 | 60 | 60 | 3.652e-05 | 6.0866e-05
2013-06-08 | ZN3425:PA11 | URBAN | Planned Outage | 982231 | 9 | 480 | 4320 | 0.0026294 | 0.00054779
2013-06-08 | ZN874:PA9 | URBAN | Planned Outage | 982235 | 1 | 10 | 10 | 6.0866e-06 | 6.0866e-05
2013-06-08 | ZN12650:PA9 | URBAN | Planned Outage | 982238 | 45 | 480 | 21600 | 0.013147 | 0.002739
2013-06-08 | ZN2635:PA28 | URBAN | Planned Outage | 982243 | 7 | 480 | 3360 | 0.0020451 | 0.00042606
2013-06-08 | ZN2635:PA28 | URBAN | Planned Outage | 982246 | 9 | 89 | 801 | 0.00048754 | 0.00054779
2013-06-08 | ZN1600:PA24DEF | CBD | Planned Outage | 982249 | 25 | 1680 | 42000 | 0.025564 | 0.0015217
2013-06-08 | ZN15011:PA4 | URBAN | Planned Outage | 982251 | 20 | 35 | 700 | 0.00042606 | 0.0012173
2013-06-10 | ZN690:PA27 | URBAN | Planned Outage | 982512 | 1 | 120 | 120 | 7.3039e-05 | 6.0866e-05
2013-06-11 | ZN12570:PA26 | URBAN | Planned Outage | 982574 | 2 | 480 | 960 | 0.00058431 | 0.00012173
2013-06-11 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 982579 | 3 | 480 | 1440 | 0.00087647 | 0.0001826
2013-06-12 | ZN15009:PA3 | URBAN | Planned Outage | 982634 | 39 | 480 | 18720 | 0.011394 | 0.0023738
2013-06-12 | 511:29878 | SHORT RURAL | Planned Outage | 982645 | 17 | 195 | 3315 | 0.0020177 | 0.0010347
2013-06-12 | ZN12580:PA4 | URBAN | Planned Outage | 982646 | 79 | 510 | 40290 | 0.024523 | 0.0048084
2013-06-12 | ZN12580:PA4 | URBAN | Planned Outage | 982648 | 44 | 510 | 22440 | 0.013658 | 0.0026781
2013-06-12 | 242:81535 | URBAN | Planned Outage | 982649 | 341 | 310 | 105710 | 0.064342 | 0.020755
2013-06-12 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 982650 | 10 | 480 | 4800 | 0.0029216 | 0.00060866
2013-06-12 | 230:81438 | SHORT RURAL | Planned Outage | 982652 | 305 | 160 | 48800 | 0.029703 | 0.018564
2013-06-12 | 202:34261 | SHORT RURAL | Planned Outage | 982654 | 51 | 350 | 17850 | 0.010865 | 0.0031042
2013-06-12 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 982655 | 7 | 480 | 3360 | 0.0020451 | 0.00042606
2013-06-12 | ZN12640:PA8 | SHORT RURAL | Planned Outage | 982658 | 143 | 480 | 68640 | 0.041778 | 0.0087039
2013-06-12 | ZN12640:PA1 | SHORT RURAL | Planned Outage | 982661 | 1 | 480 | 480 | 0.00029216 | 6.0866e-05
2013-06-12 | ZN12660:PA14 | SHORT RURAL | Planned Outage | 982665 | 79 | 450 | 35550 | 0.021638 | 0.0048084
2013-06-12 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 982667 | 14 | 480 | 6720 | 0.0040902 | 0.00085213
2013-06-12 | 507:80932 | SHORT RURAL | Planned Outage | 982673 | 12 | 290 | 3480 | 0.0021181 | 0.00073039
2013-06-12 | 509:48039 | LONG RURAL | Planned Outage | 982675 | 1 | 225 | 225 | 0.00013695 | 6.0866e-05
2013-06-12 | 502:48010 | SHORT RURAL | Planned Outage | 982681 | 45 | 44 | 1980 | 0.0012051 | 0.002739
2013-06-12 | 520:48172 | SHORT RURAL | Planned Outage | 982683 | 48 | 390 | 18720 | 0.011394 | 0.0029216
2013-06-12 | 523:33501 | SHORT RURAL | Planned Outage | 982685 | 1 | 120 | 120 | 7.3039e-05 | 6.0866e-05
2013-06-15 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 983298 | 1 | 64.8833 | 64.8833 | 3.9492e-05 | 6.0866e-05
2013-06-13 | ZN2473:PA26 | URBAN | Planned Outage | 983594 | 87 | 480 | 41760 | 0.025418 | 0.0052953
2013-06-13 | 813:89062 | SHORT RURAL | Planned Outage | 983596 | 26 | 335 | 8710 | 0.0053014 | 0.0015825
2013-06-14 | 510:48164 | SHORT RURAL | Planned Outage | 983609 | 36 | 375 | 13500 | 0.0082169 | 0.0021912
2013-06-15 | 810:74058 | SHORT RURAL | Planned Outage | 983613 | 47 | 255 | 11985 | 0.0072948 | 0.0028607
2013-06-13 | 217:33611 | URBAN | Planned Outage | 983649 | 213 | 315 | 67095 | 0.040838 | 0.012964
2013-06-13 | ZN12610:PA18 | URBAN | Planned Outage | 983650 | 48 | 480 | 14640 | 0.0089108 | 0.0029216
2013-06-14 | 224:80337 | URBAN | Planned Outage | 983654 | 193 | 280 | 54040 | 0.032892 | 0.011747
2013-06-17 | ZN12630:PA4 | SHORT RURAL | Planned Outage | 983668 | 4 | 450 | 1800 | 0.0010956 | 0.00024346
2013-06-14 | 206:34438 | SHORT RURAL | Planned Outage | 983686 | 2 | 530 | 1060 | 0.00064518 | 0.00012173
2013-06-16 | 202:34249 | URBAN | Planned Outage | 983695 | 33 | 330 | 10890 | 0.0066283 | 0.0020086
2013-06-14 | 501:48115 | SHORT RURAL | Planned Outage | 983709 | 11 | 100 | 1100 | 0.00066953 | 0.00066953
2013-06-13 | 523:33501 | SHORT RURAL | Planned Outage | 983711 | 1 | 94 | 94 | 5.7214e-05 | 6.0866e-05
2013-06-13 | ZN14144:PA5 | SHORT RURAL | Planned Outage | 983712 | 11 | 480 | 5280 | 0.0032137 | 0.00066953
2013-06-13 | ZN4545:PA2 | URBAN | Planned Outage | 983716 | 56 | 480 | 26880 | 0.016361 | 0.0034085
2013-06-13 | 807:74184 | SHORT RURAL | Planned Outage | 983718 | 2 | 34 | 68 | 4.1389e-05 | 0.00012173
2013-06-14 | ZN12620:PA2 | SHORT RURAL | Planned Outage | 983719 | 9 | 450 | 930 | 0.00056605 | 0.00054779
2013-06-13 | 523:33501 | SHORT RURAL | Planned Outage | 983726 | 1 | 72 | 72 | 4.3824e-05 | 6.0866e-05
2013-06-13 | 523:33508 | SHORT RURAL | Planned Outage | 983727 | 4 | 480 | 1920 | 0.0011686 | 0.00024346
2013-06-14 | 807:74184 | SHORT RURAL | Planned Outage | 983728 | 1 | 330 | 330 | 0.00020086 | 6.0866e-05
2013-06-14 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 983739 | 3 | 360 | 1080 | 0.00065735 | 0.0001826
2013-06-14 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 983742 | 127 | 210 | 26670 | 0.016233 | 0.00773
2013-06-14 | ZN3425:PA46 | URBAN | Planned Outage | 983747 | 19 | 120 | 2280 | 0.0013877 | 0.0011565
2013-06-15 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 983759 | 83 | 540 | 44820 | 0.02728 | 0.0050519
2013-06-15 | ZN263:PA33 34DEF | CBD | Planned Outage | 983762 | 6 | 1500 | 9000 | 0.0054779 | 0.0003652
2013-06-15 | ZN2835:PA19 | URBAN | Planned Outage | 983765 | 1 | 510 | 510 | 0.00031042 | 6.0866e-05
2013-06-16 | ZN35600:PA22 | URBAN | Planned Outage | 983767 | 1 | 300 | 300 | 0.0001826 | 6.0866e-05
2013-06-17 | ZN35370:PA8 | SHORT RURAL | Planned Outage | 983920 | 11 | 480 | 5280 | 0.0032137 | 0.00066953
2013-06-17 | ZN12600:PA13 | SHORT RURAL | Planned Outage | 983926 | 9 | 480 | 4320 | 0.0026294 | 0.00054779
2013-06-17 | ZN80:PA22 | URBAN | Planned Outage | 983927 | 69 | 300 | 20700 | 0.012599 | 0.0041998
2013-06-17 | ZN10999:PA12 | URBAN | Planned Outage | 983929 | 49 | 450 | 22050 | 0.013421 | 0.0029824
2013-06-18 | ZN269:PA9 | URBAN | Planned Outage | 983935 | 1 | 360 | 360 | 0.00021912 | 6.0866e-05
2013-06-18 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 983966 | 320 | 60 | 19200 | 0.011686 | 0.019477
2013-06-18 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 984169 | 320 | 60 | 19200 | 0.011686 | 0.019477
2013-06-18 | ZN1164:PA3 | URBAN | Planned Outage | 984175 | 131 | 360 | 47160 | 0.028704 | 0.0079735
2013-06-18 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 984333 | 2 | 480 | 960 | 0.00058431 | 0.00012173
2013-06-18 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 984333 | 6 | 480 | 2880 | 0.0017529 | 0.0003652
2013-06-18 | ZN14144:PA10 | SHORT RURAL | Planned Outage | 984337 | 1 | 480 | 480 | 0.00029216 | 6.0866e-05
2013-06-19 | ZN35500:PA28 | URBAN | Planned Outage | 984345 | 37 | 24.6833 | 913.2833 | 0.00055588 | 0.002252
2013-06-18 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 984358 | 28 | 480 | 13440 | 0.0081804 | 0.0017043
2013-06-20 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 984746 | 26 | 480 | 12480 | 0.0075961 | 0.0015825
2013-06-18 | ZN2310:PA20 | URBAN | Planned Outage | 984811 | 69 | 630 | 43470 | 0.026458 | 0.0041998
2013-06-19 | ZN1290:PA13 | URBAN | Planned Outage | 984812 | 2 | 1860 | 3720 | 0.0022642 | 0.00012173
2013-06-19 | ZN35500:PA28 | URBAN | Planned Outage | 984813 | 37 | 300 | 11100 | 0.0067561 | 0.002252
2013-06-19 | ZN263:PA33 34GHJ | CBD | Planned Outage | 984815 | 9 | 480 | 4320 | 0.0026294 | 0.00054779
2013-06-19 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 984883 | 34 | 480 | 7080 | 0.0043093 | 0.0020694
2013-06-19 | ZN1193:PA26 | URBAN | Planned Outage | 984892 | 51 | 450 | 22950 | 0.013969 | 0.0031042
2013-06-19 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 984901 | 116 | 480 | 7380 | 0.0044919 | 0.0070605
2013-06-19 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 984908 | 13 | 480 | 6240 | 0.003798 | 0.00079126
2013-06-19 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 984945 | 60 | 480 | 28800 | 0.017529 | 0.003652
2013-06-19 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 984953 | 2 | 480 | 960 | 0.00058431 | 0.00012173
2013-06-19 | ZN15006:PA4 | URBAN | Planned Outage | 984957 | 38 | 330 | 12540 | 0.0076326 | 0.0023129
2013-06-17 | 264:81244 | URBAN | Planned Outage | 984959 | 12 | 360 | 4320 | 0.0026294 | 0.00073039
2013-06-17 | 216:10728 | URBAN | Planned Outage | 984966 | 263 | 240 | 63120 | 0.038419 | 0.016008
2013-06-17 | 515:35197 | LONG RURAL | Planned Outage | 984967 | 2 | 160 | 320 | 0.00019477 | 0.00012173
2013-06-17 | 513:48059 | SHORT RURAL | Planned Outage | 984969 | 3 | 110 | 330 | 0.00020086 | 0.0001826
2013-06-17 | 512:48046 | SHORT RURAL | Planned Outage | 984970 | 2 | 65 | 130 | 7.9126e-05 | 0.00012173
2013-06-20 | ZN80:PA40 | URBAN | Planned Outage | 985148 | 192 | 480 | 92160 | 0.056094 | 0.011686
2013-06-20 | 813:89063 | SHORT RURAL | Planned Outage | 985175 | 79 | 195 | 15405 | 0.0093764 | 0.0048084
2013-06-18 | 238:34141 | SHORT RURAL | Planned Outage | 985183 | 21 | 245 | 5145 | 0.0031316 | 0.0012782
2013-06-18 | 504:48034 | URBAN | Planned Outage | 985186 | 149 | 275 | 40975 | 0.02494 | 0.009069
2013-06-18 | 502:48010 | SHORT RURAL | Planned Outage | 985198 | 28 | 10 | 280 | 0.00017043 | 0.0017043
2013-06-18 | 520:48172 | SHORT RURAL | Planned Outage | 985199 | 1 | 127 | 127 | 7.73e-05 | 6.0866e-05
2013-06-18 | 516:48065 | SHORT RURAL | Planned Outage | 985203 | 7 | 345 | 2415 | 0.0014699 | 0.00042606
2013-06-18 | 526:34636 | SHORT RURAL | Planned Outage | 985207 | 33 | 79 | 2607 | 0.0015868 | 0.0020086
2013-06-18 | 810:74054 | LONG RURAL | Planned Outage | 985208 | 2 | 335 | 670 | 0.0004078 | 0.00012173
2013-06-20 | ZN12570:PA33 | SHORT RURAL | Planned Outage | 985214 | 24 | 480 | 1440 | 0.00087647 | 0.0014608
2013-06-18 | 520:48172 | SHORT RURAL | Planned Outage | 985217 | 1 | 95 | 95 | 5.7823e-05 | 6.0866e-05
2013-06-19 | 512:48049 | SHORT RURAL | Planned Outage | 985224 | 11 | 373 | 4103 | 0.0024973 | 0.00066953
2013-06-20 | ZN3155:PA21 | URBAN | Planned Outage | 985228 | 90 | 330 | 29700 | 0.018077 | 0.0054779
2013-06-20 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 985233 | 18 | 480 | 8640 | 0.0052588 | 0.0010956
2013-06-20 | ZN12640:PA13 | SHORT RURAL | Planned Outage | 985243 | 82 | 480 | 39360 | 0.023957 | 0.004991
2013-06-19 | 243:80075 | SHORT RURAL | Planned Outage | 985247 | 2 | 80 | 160 | 9.7386e-05 | 0.00012173
2013-06-20 | ZN8700:PA61 62GHJ | CBD | Planned Outage | 985264 | 2 | 480 | 960 | 0.00058431 | 0.00012173
2013-06-21 | ZN14892:PA19 | URBAN | Planned Outage | 985267 | 160 | 30 | 4800 | 0.0029216 | 0.0097386
2013-06-19 | 509:48039 | LONG RURAL | Planned Outage | 985279 | 2 | 195 | 390 | 0.00023738 | 0.00012173
2013-06-19 | 507:80925 | SHORT RURAL | Planned Outage | 985283 | 20 | 340 | 6800 | 0.0041389 | 0.0012173
2013-06-19 | 507:80925 | SHORT RURAL | Planned Outage | 985286 | 132 | 255 | 33660 | 0.020488 | 0.0080343
2013-06-19 | 810:74054 | LONG RURAL | Planned Outage | 985287 | 1 | 290 | 290 | 0.00017651 | 6.0866e-05
2013-06-20 | 229:34995 | SHORT RURAL | Planned Outage | 985290 | 1 | 255 | 255 | 0.00015521 | 6.0866e-05
2013-06-20 | 227:13015 | SHORT RURAL | Planned Outage | 985293 | 1 | 268 | 268 | 0.00016312 | 6.0866e-05
2013-06-20 | 507:80932 | SHORT RURAL | Planned Outage | 985298 | 12 | 245 | 2940 | 0.0017895 | 0.00073039
2013-06-20 | 502:48010 | SHORT RURAL | Planned Outage | 985302 | 61 | 235 | 14335 | 0.0087252 | 0.0037128
2013-06-20 | 264:81240 | SHORT RURAL | Planned Outage | 985304 | 2 | 20 | 40 | 2.4346e-05 | 0.00012173
2013-06-20 | 520:48172 | SHORT RURAL | Planned Outage | 985306 | 3 | 255 | 765 | 0.00046563 | 0.0001826
2013-06-20 | 523:33501 | SHORT RURAL | Planned Outage | 985307 | 2 | 100 | 200 | 0.00012173 | 0.00012173
2013-06-20 | 513:48056 | SHORT RURAL | Planned Outage | 985309 | 1 | 135 | 135 | 8.2169e-05 | 6.0866e-05
2013-06-20 | 810:74054 | LONG RURAL | Planned Outage | 985313 | 2 | 370 | 740 | 0.00045041 | 0.00012173
2013-06-21 | ZN129:PA5 | URBAN | Planned Outage | 985969 | 56 | 570 | 31920 | 0.019428 | 0.0034085
2013-06-21 | 515:35193 | SHORT RURAL | Planned Outage | 986192 | 53 | 353 | 18709 | 0.011387 | 0.0032259
2013-06-21 | ZN14891:PA8 | SHORT RURAL | Planned Outage | 986196 | 6 | 480 | 2880 | 0.0017529 | 0.0003652
2013-06-21 | ZN3155:PA17 | URBAN | Planned Outage | 986224 | 16 | 240 | 3840 | 0.0023373 | 0.00097386
2013-06-22 | ZN2835:PA36 | URBAN | Planned Outage | 986253 | 2 | 180 | 360 | 0.00021912 | 0.00012173
2013-06-22 | ZN2835:PA31 | URBAN | Planned Outage | 986255 | 10 | 209 | 2090 | 0.0012721 | 0.00060866
2013-06-22 | ZN167:PA1 | URBAN | Planned Outage | 986265 | 2 | 420 | 840 | 0.00051128 | 0.00012173
2013-06-23 | ZN12630:PA1 | SHORT RURAL | Planned Outage | 986268 | 11 | 540 | 1230 | 0.00074865 | 0.00066953
2013-06-23 | 240:34846 | URBAN | Planned Outage | 986496 | 37 | 90 | 3330 | 0.0020268 | 0.002252
2013-06-21 | 232:33411 | SHORT RURAL | Planned Outage | 986658 | 1 | 365 | 365 | 0.00022216 | 6.0866e-05
2013-06-21 | 512:48048 | SHORT RURAL | Planned Outage | 986660 | 40 | 500 | 20000 | 0.012173 | 0.0024346
2013-06-21 | 504:48026 | SHORT RURAL | Planned Outage | 986663 | 84 | 420 | 35280 | 0.021474 | 0.0051128
2013-06-21 | 507:80925 | SHORT RURAL | Planned Outage | 986666 | 45 | 165 | 7425 | 0.0045193 | 0.002739
2013-06-24 | ZN690:PA33 | URBAN | Planned Outage | 986699 | 123 | 300 | 36900 | 0.02246 | 0.0074865
2013-06-21 | 503:48078 | URBAN | Planned Outage | 986702 | 1 | 275 | 275 | 0.00016738 | 6.0866e-05
2013-06-21 | 501:48123 | SHORT RURAL | Planned Outage | 986704 | 354 | 365 | 129210 | 0.078645 | 0.021547
2013-06-22 | 511:29872 | URBAN | Planned Outage | 986706 | 13 | 425 | 5525 | 0.0033629 | 0.00079126
2013-06-23 | 511:29872 | URBAN | Planned Outage | 986713 | 2 | 390 | 630 | 0.00038346 | 0.00012173
2013-06-21 | 801:74121 | SHORT RURAL | Planned Outage | 986717 | 13 | 190 | 2470 | 0.0015034 | 0.00079126
2013-06-21 | 810:74054 | LONG RURAL | Planned Outage | 986718 | 2 | 320 | 640 | 0.00038954 | 0.00012173
2013-06-21 | 801:74118 | URBAN | Planned Outage | 986720 | 82 | 185 | 15170 | 0.0092334 | 0.004991
2013-06-21 | 801:74118 | URBAN | Planned Outage | 986724 | 13 | 90 | 1170 | 0.00071213 | 0.00079126
2013-06-22 | 514:18141 | SHORT RURAL | Planned Outage | 986731 | 4 | 620 | 2480 | 0.0015095 | 0.00024346
2013-06-22 | 803:74016 | SHORT RURAL | Planned Outage | 986735 | 2 | 180 | 360 | 0.00021912 | 0.00012173
2013-06-22 | 813:89055 | SHORT RURAL | Planned Outage | 986738 | 1 | 385 | 385 | 0.00023433 | 6.0866e-05
2013-06-23 | 513:48052 | URBAN | Planned Outage | 986740 | 1 | 381 | 381 | 0.0002319 | 6.0866e-05
2013-06-23 | 801:74122 | URBAN | Planned Outage | 986743 | 64 | 355 | 22720 | 0.013829 | 0.0038954
2013-06-24 | 510:48164 | SHORT RURAL | Planned Outage | 986748 | 25 | 387 | 9675 | 0.0058888 | 0.0015217
2013-06-24 | 202:34259 | URBAN | Planned Outage | 986756 | 63 | 6 | 378 | 0.00023007 | 0.0038346
2013-06-24 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 986769 | 57 | 480 | 27360 | 0.016653 | 0.0034694
2013-06-24 | ZN14891:PA20 | SHORT RURAL | Planned Outage | 986771 | 2 | 480 | 960 | 0.00058431 | 0.00012173
2013-06-24 | ZN14891:PA5 | SHORT RURAL | Planned Outage | 986771 | 6 | 480 | 2880 | 0.0017529 | 0.0003652
2013-06-24 | ZN14143:PA17 | SHORT RURAL | Planned Outage | 986779 | 21 | 480 | 10080 | 0.0061353 | 0.0012782
2013-06-24 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 986793 | 5 | 480 | 2400 | 0.0014608 | 0.00030433
2013-06-24 | ZN269:PA9 | URBAN | Planned Outage | 986796 | 5 | 300 | 1500 | 0.00091299 | 0.00030433
2013-06-25 | ZN269:PA9 | URBAN | Planned Outage | 986803 | 35 | 359 | 12565 | 0.0076478 | 0.0021303
2013-06-25 | ZN690:PA33 | URBAN | Planned Outage | 986808 | 123 | 300 | 36900 | 0.02246 | 0.0074865
2013-06-25 | ZN12620:PA11 | SHORT RURAL | Planned Outage | 987089 | 6 | 480 | 450 | 0.0002739 | 0.0003652
2013-06-25 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 987106 | 52 | 480 | 24960 | 0.015192 | 0.003165
2013-06-25 | ZN14891:PA12 | SHORT RURAL | Planned Outage | 987142 | 13 | 480 | 6240 | 0.003798 | 0.00079126
2013-06-25 | 501:48122 | SHORT RURAL | Planned Outage | 987185 | 34 | 192 | 6528 | 0.0039733 | 0.0020694
2013-06-25 | 509:48039 | LONG RURAL | Planned Outage | 987206 | 1 | 235 | 235 | 0.00014304 | 6.0866e-05
2013-06-25 | 526:34636 | SHORT RURAL | Planned Outage | 987208 | 6 | 385 | 2310 | 0.001406 | 0.0003652
2013-06-25 | 238:34141 | SHORT RURAL | Planned Outage | 987217 | 11 | 450 | 4950 | 0.0030129 | 0.00066953
2013-06-25 | 512:48046 | SHORT RURAL | Planned Outage | 987222 | 4 | 28 | 112 | 6.817e-05 | 0.00024346
2013-06-25 | 526:34637 | SHORT RURAL | Planned Outage | 987224 | 1 | 75 | 75 | 4.565e-05 | 6.0866e-05
2013-06-25 | 514:18137 | SHORT RURAL | Planned Outage | 987225 | 4 | 110 | 440 | 0.00026781 | 0.00024346
2013-06-25 | 813:89061 | LONG RURAL | Planned Outage | 987230 | 9 | 305 | 2745 | 0.0016708 | 0.00054779
2013-06-25 | ZN965:PA6 | URBAN | Planned Outage | 987245 | 24 | 390 | 9360 | 0.0056971 | 0.0014608
2013-06-26 | ZN690:PA33 | URBAN | Planned Outage | 987246 | 1 | 300 | 300 | 0.0001826 | 6.0866e-05
2013-06-26 | ZN188:PA26 | URBAN | Planned Outage | 987248 | 35 | 240 | 8400 | 0.0051128 | 0.0021303
2013-06-26 | 511:29878 | SHORT RURAL | Planned Outage | 987731 | 43 | 30 | 1290 | 0.00078517 | 0.0026172
2013-06-27 | 801:74119 | URBAN | Planned Outage | 987735 | 1 | 140.9167 | 140.9167 | 8.577e-05 | 6.0866e-05
2013-06-27 | 801:74119 | URBAN | Planned Outage | 987745 | 1 | 120.65 | 120.65 | 7.3435e-05 | 6.0866e-05
2013-06-26 | 227:13020 | SHORT RURAL | Planned Outage | 987761 | 20 | 380 | 7600 | 0.0046258 | 0.0012173
2013-06-26 | 217:33608 | URBAN | Planned Outage | 987764 | 63 | 215 | 13545 | 0.0082443 | 0.0038346
2013-06-26 | 227:13015 | SHORT RURAL | Planned Outage | 987767 | 12 | 165 | 1980 | 0.0012051 | 0.00073039
2013-06-26 | 515:35193 | SHORT RURAL | Planned Outage | 987770 | 7 | 30 | 210 | 0.00012782 | 0.00042606
2013-06-26 | 516:48067 | SHORT RURAL | Planned Outage | 987772 | 22 | 237 | 5214 | 0.0031736 | 0.0013391
2013-06-26 | 513:48056 | SHORT RURAL | Planned Outage | 987773 | 1 | 80 | 80 | 4.8693e-05 | 6.0866e-05
2013-06-26 | 810:74054 | LONG RURAL | Planned Outage | 987774 | 1 | 390 | 390 | 0.00023738 | 6.0866e-05
2013-06-28 | 504:48031 | SHORT RURAL | Planned Outage | 989201 | 94 | 217 | 20398 | 0.012415 | 0.0057214
2013-06-27 | 242:81539 | URBAN | Planned Outage | 989205 | 171 | 380 | 64980 | 0.039551 | 0.010408
2013-06-28 | 216:10724 | SHORT RURAL | Planned Outage | 989208 | 3 | 390 | 1170 | 0.00071213 | 0.0001826
2013-06-27 | 526:34636 | SHORT RURAL | Planned Outage | 989212 | 7 | 85 | 595 | 0.00036215 | 0.00042606
2013-06-28 | 524:33576 | SHORT RURAL | Planned Outage | 989214 | 3 | 220 | 660 | 0.00040172 | 0.0001826
2013-06-27 | 801:74119 | URBAN | Planned Outage | 989220 | 33 | 120 | 3960 | 0.0024103 | 0.0020086
2013-06-27 | 801:74119 | URBAN | Planned Outage | 989224 | 42 | 120 | 5040 | 0.0030677 | 0.0025564
2013-06-27 | 514:18137 | SHORT RURAL | Planned Outage | 989227 | 77 | 345 | 26565 | 0.016169 | 0.0046867
2013-06-28 | 801:74119 | URBAN | Planned Outage | 989232 | 31 | 165 | 5115 | 0.0031133 | 0.0018868
2013-06-28 | 801:74119 | URBAN | Planned Outage | 989235 | 38 | 120 | 4560 | 0.0027755 | 0.0023129
2013-06-28 | 513:48058 | URBAN | Planned Outage | 989237 | 7 | 20 | 140 | 8.5213e-05 | 0.00042606
2013-06-26 | ZN10999:PA30 | SHORT RURAL | Planned Outage | 989262 | 3 | 450 | 1350 | 0.00082169 | 0.0001826
2013-06-26 | ZN14143:PA10 | SHORT RURAL | Planned Outage | 989264 | 2 | 570 | 1140 | 0.00069387 | 0.00012173
2013-06-26 | ZN12690:PA24 | SHORT RURAL | Planned Outage | 989267 | 10 | 480 | 4800 | 0.0029216 | 0.00060866
2013-06-26 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 989270 | 2 | 480 | 960 | 0.00058431 | 0.00012173
2013-06-26 | ZN35370:PA8 | SHORT RURAL | Planned Outage | 989276 | 50 | 240 | 12000 | 0.0073039 | 0.0030433
2013-06-26 | ZN1610:PA14 | URBAN | Planned Outage | 989285 | 74 | 1440 | 106560 | 0.064859 | 0.0045041
2013-06-26 | ZN1610:PA14 | URBAN | Planned Outage | 989286 | 74 | 1440 | 106560 | 0.064859 | 0.0045041
2013-06-26 | ZN8000:PA4 | URBAN | Planned Outage | 989287 | 1 | 30 | 30 | 1.826e-05 | 6.0866e-05
2013-06-27 | ZN690:PA33 | URBAN | Planned Outage | 989454 | 1 | 300 | 300 | 0.0001826 | 6.0866e-05
2013-06-27 | ZN195:PA9 | URBAN | Planned Outage | 989471 | 24 | 510 | 12240 | 0.00745 | 0.0014608
2013-06-27 | ZN195:PA9 | URBAN | Planned Outage | 989482 | 1 | 510 | 510 | 0.00031042 | 6.0866e-05
2013-06-27 | ZN12580:PA4 | URBAN | Planned Outage | 989485 | 78 | 510 | 39780 | 0.024213 | 0.0047476
2013-06-27 | ZN15006:PA4 | URBAN | Planned Outage | 989487 | 74 | 570 | 42180 | 0.025673 | 0.0045041
2013-06-27 | ZN12650:PA1 | SHORT RURAL | Planned Outage | 989522 | 40 | 480 | 19200 | 0.011686 | 0.0024346
2013-06-27 | ZN12600:PA2 | SHORT RURAL | Planned Outage | 989538 | 9 | 480 | 4320 | 0.0026294 | 0.00054779
2013-06-27 | ZN2473:PA26 | URBAN | Planned Outage | 989541 | 87 | 480 | 41760 | 0.025418 | 0.0052953
2013-06-27 | ZN12630:PA2 | SHORT RURAL | Planned Outage | 989543 | 2 | 480 | 960 | 0.00058431 | 0.00012173
2013-06-27 | ZN12630:PA5 | SHORT RURAL | Planned Outage | 989544 | 18 | 360 | 6480 | 0.0039441 | 0.0010956
2013-06-27 | ZN1193:PA26 | URBAN | Planned Outage | 989549 | 36 | 300 | 10800 | 0.0065735 | 0.0021912
2013-06-28 | ZN12690:PA12 | SHORT RURAL | Planned Outage | 989555 | 6 | 615 | 180 | 0.00010956 | 0.0003652
2013-06-28 | ZN15014:PA19 | URBAN | Planned Outage | 989561 | 110 | 540 | 59400 | 0.036154 | 0.0066953
2013-06-28 | ZN15014:PA19 | URBAN | Planned Outage | 989562 | 97 | 540 | 52380 | 0.031882 | 0.005904
2013-06-28 | ZN180:PA21 | URBAN | Planned Outage | 989565 | 550 | 540 | 297000 | 0.18077 | 0.033476
2013-06-28 | ZN14892:PA16 | URBAN | Planned Outage | 989577 | 2 | 480 | 960 | 0.00058431 | 0.00012173
2013-06-28 | ZN14892:PA19 | URBAN | Planned Outage | 989582 | 94 | 480 | 45120 | 0.027463 | 0.0057214
2013-06-28 | ZN12640:PA8 | SHORT RURAL | Planned Outage | 989583 | 143 | 240 | 34320 | 0.020889 | 0.0087039
2013-06-29 | ZN931:PA4 | URBAN | Planned Outage | 989589 | 12 | 420 | 5040 | 0.0030677 | 0.00073039
2013-06-30 | ZN12580:PA1 | URBAN | Planned Outage | 989591 | 3 | 540 | 1620 | 0.00098603 | 0.0001826
2013-06-30 | ZN1193:PA26 | URBAN | Planned Outage | 989592 | 36 | 420 | 15120 | 0.009203 | 0.0021912
Contents

## 5b. Network data feeder
Ausgrid
Network data - Feeder Reliability
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Annual Feeder Reliability Data
Feeder ID / name | Geographical description of feeder | Feeder classification | Number of distribution customers (average) | Length of distribution lines - high voltage - overhead | Length of distribution lines - high voltage - underground | Maximum demand (MW) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Number of unplanned outages | Unplanned customer minutes off-supply (including excluded events and MEDs) | Unplanned customer minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) (including excluded events and MEDs) | Unplanned interruptions (SAIFI) (after removing excluded events and MEDs) | Number of planned outages | Planned customer minutes off-supply | Planned interruptions (SAIFI)
202:34231 37 42 | NEWCASTLE CBD 33 | URBAN | 807 | 0 | 8445.1985 | 1.4861 | 104.4525 | 103.0314 | 5 | 14253.9333 | 14253.9333 | 0.11524 | 0.11524 | 1 | 14060 | 0.024783
202:34232 | NEWCASTLE CBD 33 | URBAN | 701 | 2580.3031 | 1550.2813 | 2.8769 | 197.8386 | 531.132 | 4 | 13945.8333 | 13945.8333 | 0.18973 | 0.18973 | 1 | 37440 | 0.13695
202:34234 | NEWCASTLE CBD 33 | URBAN | 196 | 0 | 1645.6097 | 1.467 | 43.2233 | 83.9148 | 1 | 5975 | 5975 | 0.045918 | 0.045918 | 2 | 11600 | 0.64796
202:34238 43 48 | NEWCASTLE CBD 33 | URBAN | 561 | 0 | 11203.7955 | 1.7147 | 1.2166 | 0 | 0 | 143.8833 | 143.8833 | 0.0017825 | 0.0017825 | 0 | 0 | 0
202:34239 | NEWCASTLE CBD 33 | SHORT RURAL | 39 | 0 | 2488.5423 | 0.11431 | 0.11623 | 0 | 0 | 206.2 | 0 | 0.025641 | 0 | 0 | 0 | 0
202:34245 | NEWCASTLE CBD 33 | URBAN | 1190 | 4388.1029 | 3695.985 | 4.1533 | 97.0976 | 0 | 6 | 4740.9167 | 4740.9167 | 0.096639 | 0.096639 | 0 | 0 | 0
202:34249 | NEWCASTLE CBD 33 | URBAN | 727 | 926.4929 | 6473.3908 | 5.2012 | 9.6552 | 205.0552 | 0 | 376.45 | 0 | 0.0013755 | 0 | 2 | 7995 | 0.075653
202:34250 | NEWCASTLE CBD 33 | URBAN | 1181 | 2746.3214 | 1727.046 | 3.7532 | 1319.015 | 114.0083 | 8 | 71267.8833 | 71256.5 | 0.42337 | 0.42168 | 1 | 6160 | 0.047417
202:34253 | NEWCASTLE CBD 33 | URBAN | 584 | 782.066 | 2854.0793 | 2.4196 | 77.8126 | 51.9018 | 3 | 6521.6333 | 6521.6333 | 0.039384 | 0.039384 | 1 | 4350 | 0.05137
202:34254 | NEWCASTLE CBD 33 | URBAN | 2080 | 3516.2576 | 5216.1122 | 6.4396 | 4080.2913 | 101.6147 | 14 | 128494.5833 | 128494.5833 | 0.93317 | 0.93317 | 3 | 3200 | 0.043269
202:34256 | NEWCASTLE CBD 33 | URBAN | 678 | 0 | 1592.3709 | 1.7909 | 8.0315 | 329.3138 | 2 | 909.45 | 311.6 | 0.0029499 | 0.0014749 | 2 | 37290 | 0.21239
202:34259 | NEWCASTLE CBD 33 | URBAN | 997 | 0 | 6679.9722 | 5.9823 | 1704.1453 | 363.3787 | 1 | 57768 | 57768 | 0.999 | 0.999 | 3 | 12318 | 0.098295
202:34260 | NEWCASTLE CBD 33 | URBAN | 2413 | 5287.929 | 2627.9708 | 3.9628 | 10689.2584 | 0 | 17 | 547009.15 | 546910.2167 | 3.4596 | 3.4592 | 0 | 0 | 0
202:34261 | NEWCASTLE CBD 33 | SHORT RURAL | 474 | 0 | 4805.7483 | 1.1622 | 111.5159 | 102.2958 | 10 | 19458.85 | 19458.85 | 0.79958 | 0.79958 | 1 | 17850 | 0.10759
202:34262 | NEWCASTLE CBD 33 | URBAN | 790 | 0 | 5712.1197 | 4.9154 | 26.0728 | 0 | 0 | 1075.6667 | 1075.6667 | 0.0012658 | 0.0012658 | 0 | 0 | 0
203:8082 | CARRINGTON 33 | URBAN | 24 | 1572.7255 | 510.6911 | 3.3341 | 7.7533 | 46.8568 | 2 | 471.5833 | 471.5833 | 0.41667 | 0.41667 | 2 | 2850 | 0.375
203:8083 | CARRINGTON 33 | SHORT RURAL | 140 | 1058.5088 | 1886.194 | 0.85734 | 70.8647 | 2.6634 | 4 | 16762.0667 | 528.0667 | 1.0071 | 0.021429 | 2 | 630 | 0.014286
203:8084 | CARRINGTON 33 | URBAN | 1400 | 4500.6909 | 4331.519 | 4.382 | 1149.9034 | 0 | 7 | 53216.2 | 53216.2 | 0.033571 | 0.033571 | 0 | 0 | 0
203:8085 | CARRINGTON 33 | URBAN | 1548 | 4712.9056 | 4519.4588 | 4.4391 | 3086.6218 | 1331.787 | 5 | 141006.0833 | 140479.6 | 0.28941 | 0.28876 | 2 | 60840 | 0.091085
203:8086 | CARRINGTON 33 | URBAN | 2121 | 7054.61 | 1002.6025 | 3.6199 | 34.4268 | 0 | 8 | 1928.65 | 1928.65 | 0.0037718 | 0.0037718 | 0 | 0 | 0
203:8088 | CARRINGTON 33 | URBAN | 628 | 3130.9677 | 959.2108 | 2.4006 | 111.534 | 264.5682 | 4 | 9422.0833 | 9422.0833 | 0.18471 | 0.18471 | 3 | 22350 | 0.085987
203:8089 | CARRINGTON 33 | URBAN | 233 | 1549.0338 | 2012.5841 | 2.6482 | 2456.9907 | 20.3065 | 5 | 188147.7667 | 116682.7667 | 3.9914 | 3 | 2 | 1555 | 0.038627
203:8090 | CARRINGTON 33 | URBAN | 680 | 1496.6271 | 4096.2002 | 4.8964 | 7.8173 | 0 | 2 | 323.7667 | 323.7667 | 0.0058824 | 0.0058824 | 0 | 0 | 0
205:12203 | KOTARA 33 | URBAN | 678 | 3631.656 | 1848.9111 | 4.4963 | 178.4042 | 26.6062 | 7 | 8046.4333 | 7714.9833 | 0.16372 | 0.16224 | 1 | 1200 | 0.058997
205:12205 | KOTARA 33 | URBAN | 1214 | 10150.2595 | 2638.6692 | 4.0009 | 5765.778 | 269.106 | 18 | 292246.2667 | 99975.6667 | 2.4481 | 2.0807 | 4 | 13640 | 0.076606
205:12206 | KOTARA 33 | URBAN | 839 | 3325.2013 | 959.5525 | 2.4387 | 8.9146 | 25.3736 | 4 | 741.3167 | 741.3167 | 0.0059595 | 0.0059595 | 2 | 2110 | 0.0059595
205:12208 | KOTARA 33 | URBAN | 132 | 0 | 818.6235 | 2.2672 | 1.813 | 0 | 0 | 162.1667 | 162.1667 | 0.0075758 | 0.0075758 | 0 | 0 | 0
205:12210 | KOTARA 33 | URBAN | 1136 | 3858.768 | 531.1131 | 3.4103 | 334.3774 | 155.2693 | 5 | 19883.5667 | 19883.5667 | 0.31866 | 0.31866 | 2 | 9233 | 0.051056
205:12213 | KOTARA 33 | URBAN | 879 | 5378.8479 | 903.9762 | 1.8099 | 2.5518 | 280.159 | 4 | 285.9167 | 285.9167 | 0.0045506 | 0.0045506 | 1 | 31390 | 0.083049
206:34432 | CROUDACE BAY 33 11 | URBAN | 1472 | 6519.0077 | 4515.7926 | 6.7444 | 544.3502 | 181.5873 | 12 | 16367.6167 | 16367.6167 | 0.080163 | 0.080163 | 3 | 5460 | 0.012908
206:34434 | CROUDACE BAY 33 11 | URBAN | 1493 | 4818.7739 | 3774.931 | 5.7728 | 446.6295 | 3959.9584 | 10 | 15689.7167 | 8869.7167 | 0.10114 | 0.071668 | 2 | 139110 | 0.32954
206:34435 | CROUDACE BAY 33 11 | URBAN | 133 | 1024.4549 | 735.3078 | 0.72398 | 27.6071 | 0 | 2 | 7733 | 7733 | 0.26316 | 0.26316 | 0 | 0 | 0
206:34440 | CROUDACE BAY 33 11 | URBAN | 1595 | 8311.3328 | 2744.3529 | 6.23 | 57.1372 | 1491.358 | 4 | 1859.8667 | 1859.8667 | 0.021317 | 0.021317 | 3 | 48545 | 0.20188
206:34441 | CROUDACE BAY 33 11 | URBAN | 1389 | 8178.9518 | 1607.037 | 5.8299 | 1418.3508 | 4.5997 | 14 | 49336.9833 | 49336.9833 | 1.1346 | 1.1346 | 0 | 160 | 0.00071994
208:53 | BROADMEADOW 33 | URBAN | 645 | 2072.0231 | 408.5046 | 1.2574 | 11.0824 | 0 | 4 | 1787.3167 | 1787.3167 | 0.0062016 | 0.0062016 | 0 | 0 | 0
208:56 | BROADMEADOW 33 | URBAN | 345 | 2073.7061 | 1215.3204 | 2.4196 | 853.1314 | 643.8213 | 4 | 71502.7167 | 71502.7167 | 1.4232 | 1.4232 | 2 | 53960 | 0.31304
208:58 | BROADMEADOW 33 | URBAN | 1003 | 3866.7748 | 585.0451 | 2.8197 | 380.5733 | 0 | 8 | 27370.7667 | 27370.7667 | 0.079761 | 0.079761 | 0 | 0 | 0
208:59 | BROADMEADOW 33 | URBAN | 776 | 900.2965 | 4022.2299 | 3.5056 | 3.7633 | 319.5412 | 2 | 217.7 | 217.7 | 0.0025773 | 0.0025773 | 3 | 18485 | 0.072165
208:62 | BROADMEADOW 33 | URBAN | 1076 | 5341.9804 | 666.2693 | 3.7913 | 118.6488 | 0 | 6 | 6346.3 | 6013.7833 | 0.092007 | 0.091078 | 0 | 0 | 0
208:71 | BROADMEADOW 33 | URBAN | 191 | 0 | 3520.6133 | 3.296 | 117.4773 | 0 | 1 | 7228 | 7228 | 1 | 1 | 0 | 0 | 0
208:72 | BROADMEADOW 33 | URBAN | 276 | 1920.3819 | 2118.0509 | 4.039 | 57.9587 | 234.5833 | 2 | 2910 | 2910 | 0.18116 | 0.18116 | 1 | 11778 | 0.1413
208:74 | BROADMEADOW 33 | URBAN | 677 | 3899.4504 | 1711.2369 | 2.7244 | 0.96953 | 18.3383 | 0 | 72.1667 | 72.1667 | 0.0014771 | 0.0014771 | 1 | 1365 | 0.0044313
210:8675 | NEW LAMBTON 33 | URBAN | 356 | 2718.4805 | 1815.5089 | 1.6004 | 82.8941 | 0 | 1 | 10504 | 10504 | 0.14607 | 0.14607 | 0 | 0 | 0
210:8676 | NEW LAMBTON 33 | URBAN | 868 | 2827.7532 | 1190.0401 | 2.7244 | 51.4681 | 13.6361 | 5 | 3831 | 3831 | 0.14631 | 0.14631 | 2 | 1015 | 0.0023041
210:8679 | NEW LAMBTON 33 | URBAN | 1187 | 4242.8196 | 254.7926 | 2.8578 | 2.0958 | 0 | 3 | 148.7167 | 148.7167 | 0.0025274 | 0.0025274 | 0 | 0 | 0
210:8682 | NEW LAMBTON 33 | URBAN | 782 | 5603.5633 | 648.9662 | 3.8676 | 76.4187 | 624.7835 | 9 | 4006.95 | 4006.95 | 0.094629 | 0.094629 | 1 | 32760 | 0.11637
213:33770 | MARYLAND 132 | URBAN | 1148 | 123.3766 | 7518.1999 | 4.5229 | 2373.0901 | 347.9325 | 2 | 106400.55 | 106400.55 | 1.4939 | 1.4939 | 1 | 15600 | 0.069686
213:33771 | MARYLAND 132 | URBAN | 1508 | 8309.2275 | 1837.1035 | 4.8386 | 7014.5604 | 1971.5506 | 5 | 293988.4667 | 293988.4667 | 1.9894 | 1.9894 | 4 | 82630 | 0.2122
213:33773 | MARYLAND 132 | SHORT RURAL | 1270 | 5612.1722 | 13215.6791 | 5.5822 | 0 | 877.007 | 0 | 0 | 0 | 0 | 0 | 4 | 31860 | 0.080315
213:33774 | MARYLAND 132 | URBAN | 1308 | 2874.9525 | 5577.9376 | 4.6811 | 359.6649 | 130.8814 | 3 | 15581.2833 | 15581.2833 | 0.08945 | 0.08945 | 1 | 5670 | 0.09633
213:33775 | MARYLAND 132 | URBAN | 1058 | 5591.8512 | 2680.1836 | 3.2772 | 82.1521 | 227.218 | 8 | 5083.4833 | 5083.4833 | 0.05104 | 0.05104 | 2 | 14060 | 0.086957
213:33777 | MARYLAND 132 | SHORT RURAL | 567 | 15000.3614 | 17432.6864 | 1.9048 | 0 | 804.2446 | 0 | 0 | 0 | 0 | 0 | 11 | 85622 | 0.52381
214:8665 | CARDIFF 33 | URBAN | 673 | 3329.417 | 873.8188 | 2.7837 | 175.3067 | 0 | 7 | 12771.2667 | 12771.2667 | 0.2422 | 0.2422 | 0 | 0 | 0
214:8666 | CARDIFF 33 | URBAN | 1252 | 3974.0005 | 847.6566 | 4.4566 | 12.1258 | 8.1312 | 4 | 551.7667 | 551.7667 | 0.0055911 | 0.0055911 | 1 | 370 | 0.0015974
214:8667 | CARDIFF 33 | URBAN | 1118 | 4705.1213 | 4767.3967 | 4.4541 | 200.4835 | 398.977 | 5 | 9127.8 | 9127.8 | 0.065295 | 0.065295 | 6 | 18165 | 0.1297
214:8669 | CARDIFF 33 | URBAN | 1987 | 6189.2019 | 1370.5631 | 6.5426 | 14298.5293 | 0 | 11 | 443189.8833 | 12520.9833 | 0.62557 | 0.1228 | 0 | 0 | 0
214:8670 | CARDIFF 33 | URBAN | 1388 | 6756.7417 | 4853.2822 | 5.8046 | 142.5703 | 1182.6581 | 6 | 4980.9167 | 4980.9167 | 0.052594 | 0.052594 | 5 | 41318 | 0.32997
214:8671 | CARDIFF 33 | URBAN | 106 | 1908.3938 | 360.8628 | 1.7528 | 8.2506 | 1.9447 | 2 | 954.5667 | 954.5667 | 0.22642 | 0.22642 | 0 | 225 | 0.009434
216:10723 | EDGEWORTH 33 | URBAN | 704 | 2627.5737 | 326.9071 | 1.834 | 642.886 | 287.1874 | 6 | 71085.45 | 71085.45 | 2.0838 | 2.0838 | 3 | 31755 | 0.2983
216:10726 | EDGEWORTH 33 | URBAN | 761 | 3508.7098 | 677.8796 | 2.9944 | 1063.2633 | 60.4667 | 9 | 72007.5833 | 72007.5833 | 2.046 | 2.046 | 1 | 4095 | 0.082786
216:10728 | EDGEWORTH 33 | URBAN | 793 | 10334.313 | 2933.5798 | 3.9615 | 1954.1531 | 1241.3462 | 12 | 100033.8667 | 100033.8667 | 3.1362 | 3.1362 | 3 | 63545 | 0.33417
216:10729 | EDGEWORTH 33 | URBAN | 1018 | 177.2427 | 10115.3024 | 4.7159 | 2008.1876 | 1940.3028 | 3 | 86355.15 | 86355.15 | 1.9607 | 1.9607 | 3 | 83436 | 0.34774
217:33607 | MOUNT HUTTON 33 | SHORT RURAL | 44 | 511.8117 | 155.3448 | 0.09526 | 0.90895 | 0 | 1 | 1935 | 1935 | 0.97727 | 0.97727 | 0 | 0 | 0
217:33610 | MOUNT HUTTON 33 | URBAN | 1880 | 7096.1455 | 1583.3492 | 5.8013 | 754.5344 | 0 | 13 | 26375.5833 | 26375.5833 | 0.24947 | 0.24947 | 0 | 0 | 0
217:33611 | MOUNT HUTTON 33 | URBAN | 1346 | 6445.8335 | 2807.0302 | 4.9154 | 4891.5441 | 4897.1873 | 14 | 201807.1833 | 201807.1833 | 1.7459 | 1.7459 | 5 | 202040 | 0.45319
217:33612 | MOUNT HUTTON 33 | URBAN | 1842 | 10173.9564 | 2873.6666 | 5.487 | 12653.3617 | 5799.7013 | 13 | 467653.0667 | 467653.0667 | 2.0695 | 2.0695 | 11 | 214350 | 0.36048
219:1740 | DUDLEY 33 | SHORT RURAL | 135 | 480.1694 | 449.4111 | 0.5144 | 34.986 | 0 | 3 | 13792.45 | 13792.45 | 1.1259 | 1.1259 | 0 | 0 | 0
220:8687 | JEWELLS 33 | URBAN | 1500 | 7240.9596 | 407.0276 | 4.0581 | 1286.1343 | 7.0039 | 12 | 64271.3 | 64178.9333 | 1.1653 | 1.1647 | 0 | 350 | 0.00066667
220:8688 | JEWELLS 33 | URBAN | 451 | 3679.7555 | 501.9214 | 1.5432 | 32.0328 | 151.3975 | 6 | 4209.4 | 4209.4 | 1.0111 | 1.0111 | 2 | 19895 | 0.72062
220:8689 | JEWELLS 33 | URBAN | 1465 | 6158.5037 | 1362.9525 | 4.0962 | 551.0628 | 101.8025 | 15 | 27281.8 | 27281.8 | 1.0683 | 1.0683 | 1 | 5040 | 0.028669
220:8691 | JEWELLS 33 | URBAN | 1165 | 8479.1699 | 2653.7508 | 4.3439 | 202.5202 | 17.4575 | 3 | 9454.6167 | 9454.6167 | 0.99142 | 0.99142 | 2 | 815 | 0.0017167
220:8692 | JEWELLS 33 | URBAN | 899 | 2873.837 | 3082.3068 | 3.5437 | 440.6266 | 69.1987 | 3 | 25215.5333 | 25215.5333 | 1.9978 | 1.9978 | 1 | 3960 | 0.22024
221:11893 | GATESHEAD 33 | URBAN | 708 | 2329.4002 | 2291.0224 | 1.6385 | 95.8311 | 248.3659 | 7 | 11860.9167 | 11860.9167 | 1.0311 | 1.0311 | 1 | 30740 | 0.16384
221:11894 | GATESHEAD 33 | URBAN | 919 | 4472.9812 | 320.9049 | 1.8861 | 100.9377 | 0 | 7 | 10852.4667 | 10852.4667 | 1.0718 | 1.0718 | 0 | 0 | 0
221:11895 | GATESHEAD 33 | URBAN | 918 | 5321.1554 | 1711.452 | 1.6194 | 99.8126 | 248.3128 | 11 | 12499.05 | 12499.05 | 0.5817 | 0.5817 | 2 | 31095 | 0.19172
221:11897 | GATESHEAD 33 | URBAN | 837 | 5538.7979 | 869.4221 | 3.3341 | 117.9777 | 0 | 7 | 7175.8333 | 6294.8333 | 0.78973 | 0.78853 | 0 | 0 | 0
221:11898 | GATESHEAD 33 | URBAN | 259 | 6036.1652 | 3537.3882 | 2.8578 | 28.7482 | 28.7482 | 1 | 2040 | 2040 | 0.98456 | 0.98456 | 2 | 2040 | 0.034749
221:11899 | GATESHEAD 33 | URBAN | 1302 | 10780.159 | 1123.0983 | 0.9145 | 431.1885 | 104.7112 | 11 | 95617.2667 | 95617.2667 | 1.0361 | 1.0361 | 3 | 23220 | 0.097542
222:2014 | PELICAN 33 | URBAN | 1173 | 7686.0583 | 584.9851 | 3.2198 | 2422.2271 | 1648.2214 | 7 | 152559.2333 | 152559.2333 | 1.6948 | 1.6948 | 5 | 103810 | 0.18159
222:2017 | PELICAN 33 | URBAN | 1253 | 6354.9014 | 920.9733 | 4.5725 | 1036.3608 | 473.5002 | 10 | 45963.1833 | 44547.1833 | 1.3759 | 1.3567 | 3 | 21000 | 0.057462
222:2018 | PELICAN 33 | URBAN | 1043 | 4520.4834 | 522.0992 | 2.3243 | 615.8615 | 0 | 15 | 53732.0667 | 53585.4167 | 1.3816 | 1.3806 | 0 | 0 | 0
223:14393 | SWANSEA 33 | URBAN | 1047 | 3310.3437 | 1124.9518 | 2.2481 | 161.8758 | 0 | 17 | 14601.9333 | 14588.4833 | 1.2044 | 1.2034 | 0 | 0 | 0
223:14394 | SWANSEA 33 | URBAN | 1508 | 5334.0771 | 480.368 | 3.0483 | 916.8563 | 4261.8778 | 12 | 60994.6333 | 60994.6333 | 1.2069 | 1.2069 | 2 | 283525 | 0.42241
223:14395 | SWANSEA 33 | SHORT RURAL | 964 | 15900.9783 | 8846.1584 | 2.3624 | 475.3695 | 485.3343 | 4 | 40805.6167 | 40805.6167 | 1.0944 | 1.0944 | 3 | 41661 | 0.21266
223:14397 | SWANSEA 33 | URBAN | 1134 | 4337.6809 | 4116.6571 | 2.8387 | 3857.5534 | 877.9746 | 11 | 275572.6 | 275572.6 | 2.0088 | 2.0088 | 1 | 62720 | 0.19753
223:14398 | SWANSEA 33 | URBAN | 853 | 2719.4919 | 1481.4841 | 3.5627 | 1774.9427 | 0 | 5 | 101030.6333 | 101030.6333 | 2.0422 | 2.0422 | 0 | 0 | 0
223:14399 | SWANSEA 33 | SHORT RURAL | 145 | 1916.8162 | 982.1258 | 0.28578 | 15.4663 | 0.38754 | 2 | 10975 | 10975 | 1.5034 | 1.5034 | 0 | 275 | 0.0068966
224:80328 | ARGENTON 132 11 | URBAN | 60 | 1687.9238 | 3100.8864 | 3.8485 | 0 | 179.528 | 0 | 0 | 0 | 0 | 0 | 2 | 9460 | 0.43333
224:80329 | ARGENTON 132 11 | SHORT RURAL | 399 | 9769.927 | 1387.3659 | 2.2276 | 45.132 | 6.0416 | 3 | 4108.6333 | 4108.6333 | 0.13283 | 0.13283 | 0 | 550 | 0.0025063
224:80331 | ARGENTON 132 11 | URBAN | 221 | 2864.268 | 5118.9104 | 4.1012 | 11.6287 | 0.5056 | 1 | 575 | 575 | 0.10407 | 0.10407 | 0 | 25 | 0.0045249
224:80335 | ARGENTON 132 11 | SHORT RURAL | 96 | 1849.5634 | 1375.7029 | 1.105 | 0.31786 | 0 | 0 | 58.3333 | 58.3333 | 0.010417 | 0.010417 | 0 | 0 | 0
224:80337 | ARGENTON 132 11 | URBAN | 1853 | 14215.153 | 4252.0326 | 6 | 1326.4356 | 6946.5689 | 14 | 44831.8 | 4808.8 | 0.15596 | 0.011333 | 12 | 234785 | 0.40475
224:80340 | ARGENTON 132 11 | SHORT RURAL | 1072 | 25228.2886 | 1322.0064 | 4.3494 | 5100.5507 | 1132.2297 | 15 | 237812.2333 | 187664.2333 | 2.2351 | 2.1026 | 4 | 52790 | 0.25187
224:80341 | ARGENTON 132 11 | URBAN | 1366 | 6654.5719 | 1629.4392 | 3.9201 | 51.6784 | 34.2154 | 8 | 2673.3833 | 2673.3833 | 0.030015 | 0.030015 | 3 | 1770 | 0.021962
224:80346 | ARGENTON 132 11 | URBAN | 1586 | 9472.3785 | 1012.1177 | 5.7967 | 1749.8129 | 0 | 15 | 61215.9667 | 55291.05 | 1.0038 | 0.96406 | 0 | 0 | 0
225:13446 | TORONTO 33 | URBAN | 1532 | 7839.1765 | 1986.5018 | 5.3536 | 5429.4314 | 4115.6846 | 13 | 205664.05 | 205179.8 | 2.299 | 2.2963 | 4 | 155900 | 0.29308
225:33670 | TORONTO 33 | SHORT RURAL | 1101 | 6640.1527 | 407.868 | 3.7151 | 179.145 | 0 | 8 | 9778.6833 | 9778.6833 | 0.095368 | 0.095368 | 0 | 0 | 0
225:33676 | TORONTO 33 | SHORT RURAL | 1183 | 11690.8431 | 882.5595 | 3.7723 | 349.7683 | 2243.581 | 8 | 18802.9333 | 18802.9333 | 0.15469 | 0.15469 | 5 | 120611 | 0.22823
225:33679 | TORONTO 33 | URBAN | 688 | 3150.0493 | 1378.6315 | 4.2105 | 1185.8045 | 0 | 7 | 57112.5 | 57112.5 | 2.9985 | 2.9985 | 0 | 0 | 0
227:13014 | AVONDALE 33 | SHORT RURAL | 57 | 4973.0034 | 309.7332 | 0.19052 | 27.3975 | 49.431 | 4 | 29162.3167 | 28172.3167 | 2.1053 | 2 | 3 | 52615 | 2.5965
227:13015 | AVONDALE 33 | SHORT RURAL | 1522 | 54170.7877 | 2525.9791 | 4.401 | 7734.4536 | 9560.7271 | 26 | 356392.05 | 356110.7167 | 2.7924 | 2.7904 | 34 | 440544 | 0.88502
227:13016 | AVONDALE 33 | SHORT RURAL | 144 | 4586.8436 | 334.1187 | 0.4382 | 12.7272 | 42.4924 | 3 | 5889.9833 | 5670 | 1.0972 | 1.0903 | 1 | 19665 | 0.39583
227:13018 | AVONDALE 33 | URBAN | 559 | 6962.9024 | 2335.6873 | 4.5153 | 201.3365 | 4507.5967 | 6 | 9042.4167 | 9042.4167 | 1.0268 | 1.0268 | 4 | 202445 | 0.72093
227:13019 | AVONDALE 33 | SHORT RURAL | 121 | 35323.6311 | 989.7051 | 0.49535 | 210.9058 | 281.8463 | 8 | 86342.7 | 86342.7 | 3.2645 | 3.2645 | 21 | 115385 | 2.5372
227:13020 | AVONDALE 33 | SHORT RURAL | 820 | 25992.1883 | 1064.9203 | 5.4298 | 6769.9091 | 4112.286 | 19 | 252841.4833 | 244561.4833 | 3.4305 | 3.3183 | 8 | 153585 | 0.61098
228:7487 | STOCKTON 33 | URBAN | 1074 | 2941.7682 | 263.2457 | 2.0386 | 18.3644 | 0 | 8 | 1826.85 | 1565.7 | 0.0074488 | 0.0065177 | 0 | 0 | 0
228:7490 | STOCKTON 33 | SHORT RURAL | 1117 | 16203.7315 | 5383.9734 | 3.296 | 346.6891 | 272.7267 | 9 | 21330.6667 | 21223.4 | 0.077887 | 0.076992 | 6 | 16780 | 0.042972
228:7491 | STOCKTON 33 | URBAN | 764 | 2797.4639 | 181.5106 | 2.0195 | 11.1557 | 0 | 5 | 1120.2167 | 899.8833 | 0.0065445 | 0.0052356 | 0 | 0 | 0
229:34983 | WILLIAMTOWN 33 | SHORT RURAL | 1426 | 48755.0105 | 6325.0587 | 5.9823 | 9414.7594 | 9882.7921 | 25 | 319146.3833 | 318019.7833 | 2.9446 | 2.9425 | 20 | 335012 | 0.69916
229:34986 | WILLIAMTOWN 33 | SHORT RURAL | 77 | 4537.1015 | 107.3849 | 0.26673 | 1.2575 | 0 | 2 | 956.0667 | 956.0667 | 0.025974 | 0.025974 | 0 | 0 | 0
229:34989 | WILLIAMTOWN 33 | SHORT RURAL | 1220 | 12430.442 | 6821.5484 | 7.1445 | 16989.4063 | 0 | 12 | 482233.4 | 481837.45 | 3.3377 | 3.3361 | 0 | 0 | 0
229:34992 | WILLIAMTOWN 33 | URBAN | 33 | 1998.7938 | 1327.1184 | 1.6004 | 1.2504 | 0 | 0 | 158.45 | 158.45 | 0.030303 | 0.030303 | 0 | 0 | 0
229:34995 | WILLIAMTOWN 33 | SHORT RURAL | 1479 | 43902.4715 | 11900.0572 | 2.7054 | 2696.3461 | 4868.7215 | 27 | 202114.5833 | 201057.4333 | 1.1562 | 1.1535 | 25 | 364953 | 0.78431
230:81432 | TANILBA BAY 33 | URBAN | 38 | 6298.0014 | 204.424 | 0.076208 | 5.6047 | 0 | 3 | 14914.3833 | 9214.3833 | 4.0263 | 3.0263 | 0 | 0 | 0
230:81434 | TANILBA BAY 33 | URBAN | 1421 | 8685.434 | 1953.2293 | 4.1533 | 5601.0809 | 5.9394 | 16 | 273480.0833 | 61557.7 | 1.5454 | 0.55665 | 0 | 290 | 0.00070373
230:81440 | TANILBA BAY 33 | URBAN | 1585 | 9456.1826 | 1873.7415 | 3.6008 | 8723.3996 | 3828.2493 | 21 | 491285.9167 | 114987.0167 | 2.571 | 1.5394 | 5 | 215600 | 0.59748
231:8405 | SALT ASH 33 | SHORT RURAL | 94 | 16597.538 | 0 | 0.32388 | 43.5097 | 61.9205 | 4 | 27242.5167 | 13424.5167 | 2.0213 | 1.0213 | 8 | 38770 | 1.2979
231:8415 | SALT ASH 33 | SHORT RURAL | 811 | 40986.0934 | 1222.1272 | 2.4006 | 9975.3035 | 1258.8003 | 15 | 842686.2833 | 723763.2833 | 7.2182 | 6.2207 | 8 | 106340 | 0.40814
232:11453 | NELSON BAY 33 | SHORT RURAL | 1277 | 15256.3424 | 3789.3492 | 3.2198 | 309.7958 | 2482.6523 | 9 | 19511.8833 | 17841.1833 | 1.047 | 1.0462 | 11 | 156365 | 0.33986
232:11454 | NELSON BAY 33 | SHORT RURAL | 1843 | 14672.6597 | 2538.7219 | 3.8295 | 920.6388 | 3409.139 | 27 | 48753.25 | 48753.25 | 0.11394 | 0.11394 | 9 | 180534 | 0.43353
232:33413 | NELSON BAY 33 | SHORT RURAL | 1906 | 32990.3984 | 2472.4565 | 4.5725 | 6865.6153 | 8152.9748 | 28 | 304493.8833 | 67586.5333 | 1.2308 | 0.23924 | 28 | 361589 | 0.72036
235:2120 | TARRO 33 | SHORT RURAL | 787 | 61007.253 | 7550.0429 | 5.1631 | 8305.9925 | 3143.1682 | 22 | 326236.5333 | 131776.7 | 3.5286 | 1.5858 | 15 | 123455 | 0.41423
235:2121 | TARRO 33 | URBAN | 23 | 4570.1605 | 317.5361 | 1.6194 | 0.97425 | 88.9199 | 0 | 122 | 122 | 0.043478 | 0.043478 | 3 | 11135 | 1.1739
235:2123 | TARRO 33 | URBAN | 1325 | 8413.6157 | 1637.1829 | 5.7347 | 500.6678 | 474.0888 | 12 | 17704.9 | 17704.9 | 0.040755 | 0.040755 | 2 | 16765 | 0.10264
235:2124 | TARRO 33 | URBAN | 933 | 6412.5346 | 1163.4615 | 2.4006 | 2315.1468 | 1.7756 | 7 | 195577.25 | 194575.45 | 2.0064 | 2.0043 | 1 | 150 | 0.0021436
235:2857 | TARRO 33 | SHORT RURAL | 441 | 11672.7439 | 795.5838 | 1.448 | 54.1729 | 1.2138 | 7 | 7587.15 | 7587.15 | 0.17914 | 0.17914 | 2 | 170 | 0.015873
235:8684 | TARRO 33 | SHORT RURAL | 115 | 8774.9543 | 1928.7078 | 2.191 | 317.5425 | 7.0767 | 5 | 29391 | 29391 | 2.1391 | 2.1391 | 2 | 655 | 0.017391
238:34136 | THORNTON 33 | URBAN | 823 | 2349.2041 | 3176.6064 | 2.8578 | 4.1025 | 153.8876 | 2 | 291.1167 | 291.1167 | 0.0024301 | 0.0024301 | 1 | 10920 | 0.12637
238:34141 | THORNTON 33 | SHORT RURAL | 1156 | 52905.9893 | 8742.8235 | 5.2774 | 5705.7953 | 4635.5797 | 26 | 219253.6167 | 218309.6167 | 2.7984 | 2.7915 | 22 | 178129 | 0.39533
238:34143 | THORNTON 33 | URBAN | 895 | 244.521 | 7238.6423 | 2.9912 | 0 | 90.4464 | 0 | 0 | 0 | 0 | 0 | 2 | 6132 | 0.16313
238:34144 | THORNTON 33 | URBAN | 834 | 14288.5657 | 4281.8345 | 7.0111 | 8586.2494 | 2008.3474 | 19 | 248351.0667 | 246689.0667 | 7.5624 | 6.5659 | 5 | 58090 | 1.1595
238:34147 | THORNTON 33 | URBAN | 1153 | 7757.5321 | 3177.761 | 3.1817 | 2992.3661 | 435.3022 | 16 | 190725.4333 | 190725.4333 | 2.1396 | 2.1396 | 4 | 27745 | 0.10061
238:34151 | THORNTON 33 | URBAN | 1217 | 196.0068 | 8760.3862 | 5.4298 | 5.9218 | 11619.9491 | 2 | 221.1667 | 221.1667 | 0.0016434 | 0.0016434 | 3 | 433980 | 0.68858
239:82129 | RATHMINES 132 | SHORT RURAL | 1408 | 14721.6675 | 1389.2579 | 3.9819 | 912.4693 | 2851.5259 | 18 | 46471.0333 | 18342.2167 | 0.18466 | 0.14844 | 8 | 145225 | 0.30824
239:82131 | RATHMINES 132 | SHORT RURAL | 4 | 28159.4641 | 4066.831 | 1.6385 | 238.727 | 377.7117 | 3 | 29547 | 29547 | 53.75 | 53.75 | 10 | 46749 | 34.25
240:34840 | MAYFIELD WEST 132 | URBAN | 1586 | 4652.7248 | 1723.2576 | 5.2393 | 1547.7614 | 0 | 2 | 59907.5667 | 59907.5667 | 0.99369 | 0.99369 | 0 | 0 | 0
240:34843 | MAYFIELD WEST 132 | URBAN | 273 | 1347.6815 | 4501.8577 | 3.3532 | 897.0753 | 17.6924 | 7 | 54253.35 | 54253.35 | 1.8938 | 1.8938 | 2 | 1070 | 0.014652
240:34846 | MAYFIELD WEST 132 | URBAN | 865 | 2415.8718 | 6670.1356 | 4.6106 | 61.9115 | 504.3877 | 5 | 2723.1167 | 2723.1167 | 0.033526 | 0.033526 | 3 | 22185 | 0.13988
240:34852 | MAYFIELD WEST 132 | URBAN | 626 | 8641.6512 | 6571.9738 | 6.3062 | 3975.5187 | 2119.5674 | 8 | 127842.7667 | 127842.7667 | 1.631 | 1.631 | 6 | 68160 | 0.24601
242:81533 | TOMAREE 33 | URBAN | 16 | 2499.8031 | 105.5807 | 1.0098 | 10.8797 | 237.9343 | 4 | 2185 | 2185 | 0.5625 | 0.5625 | 19 | 47785 | 7
242:81535 | TOMAREE 33 | URBAN | 1705 | 3633.7105 | 2961.5806 | 4.5915 | 145.2555 | 3568.3127 | 10 | 6415.4333 | 2936.1667 | 0.0064516 | 0.0052786 | 2 | 157600 | 0.33548
242:81538 | TOMAREE 33 | URBAN | 972 | 8106.3739 | 5313.6808 | 2.6482 | 1127.6021 | 2197.3449 | 4 | 86347.8333 | 86347.8333 | 0.28292 | 0.28292 | 3 | 168265 | 0.43313
242:81539 | TOMAREE 33 | URBAN | 1979 | 1917.4042 | 1305.9618 | 4.5725 | 13927.6009 | 11601.8151 | 19 | 617696.9 | 617696.9 | 2.1213 | 2.1213 | 10 | 514547 | 0.78272
242:81541 | TOMAREE 33 | URBAN | 1530 | 4927.4657 | 3850.8884 | 3.658 | 19818.5081 | 6021.4798 | 21 | 1098702.4167 | 955902.4167 | 3.4229 | 3.3444 | 5 | 333820 | 0.56993
243:80074 | MORISSET 132 | URBAN | 1448 | 19190.5149 | 4587.999 | 2.553 | 3105.4261 | 1036.3971 | 18 | 246675.9167 | 246675.9167 | 1.3943 | 1.3943 | 12 | 82325 | 0.16989
243:80075 | MORISSET 132 | SHORT RURAL | 173 | 33143.0181 | 1416.409 | 3.4484 | 846.838 | 1717.8118 | 7 | 49800.3167 | 49800.3167 | 2.7919 | 2.7919 | 13 | 101020 | 1.6127
243:80080 | MORISSET 132 | SHORT RURAL | 1284 | 41684.3622 | 3268.1352 | 6.0395 | 5558.7281 | 3208.8548 | 19 | 186649.3667 | 186437.0167 | 2.007 | 2.0062 | 14 | 107746 | 0.28583
243:80083 | MORISSET 132 | SHORT RURAL | 343 | 41687.121 | 2222.338 | 0.70492 | 320.7163 | 889.7727 | 17 | 92263.4333 | 92263.4333 | 3.0904 | 3.0904 | 30 | 255969.2 | 1.8222
243:80084 | MORISSET 132 | SHORT RURAL | 789 | 8308.4805 | 2757.1964 | 5.1821 | 1743.6601 | 118.9538 | 10 | 68234.3833 | 68234.3833 | 1.1229 | 1.1229 | 1 | 4655 | 0.024081
256:80632 | ADAMSTOWN 132 | URBAN | 859 | 7458.9309 | 1935.2283 | 2.9721 | 0 | 1143.7511 | 0 | 0 | 0 | 0 | 0 | 2 | 78040 | 0.32596
256:80635 | ADAMSTOWN 132 | URBAN | 387 | 1569.3011 | 2080.4967 | 1.6004 | 86.8532 | 309.6691 | 6 | 11005.6833 | 11005.6833 | 0.1292 | 0.1292 | 1 | 39240 | 0.28165
256:80638 | ADAMSTOWN 132 | URBAN | 1017 | 2701.1685 | 917.0674 | 2.4006 | 0.44904 | 0 | 0 | 37.9333 | 37.9333 | 0.00098328 | 0.00098328 | 0 | 0 | 0
256:80640 | ADAMSTOWN 132 | URBAN | 1230 | 5664.4844 | 1831.2268 | 3.8295 | 448.8751 | 0 | 11 | 23770.5833 | 19432.1833 | 0.20569 | 0.17886 | 0 | 0 | 0
256:80641 | ADAMSTOWN 132 | URBAN | 1122 | 3446.9903 | 971.1967 | 1.8671 | 13.1768 | 0 | 4 | 1431.1833 | 121.4167 | 0.0035651 | 0.0017825 | 0 | 0 | 0
256:80646 | ADAMSTOWN 132 | URBAN | 1690 | 5163.8423 | 426.9432 | 4.1533 | 315.1245 | 0 | 10 | 15386.3667 | 15338.3167 | 0.063905 | 0.062722 | 0 | 0 | 0
256:80647 | ADAMSTOWN 132 | URBAN | 1788 | 3616.5199 | 3810.622 | 5.6965 | 4102.2358 | 707.7424 | 6 | 146035.95 | 146035.95 | 1.1812 | 1.1812 | 4 | 25195 | 0.12081
256:80650 | ADAMSTOWN 132 | URBAN | 1199 | 7991.1073 | 1945.7102 | 4.0771 | 390.7347 | 0 | 11 | 19434.7333 | 19434.7333 | 0.23937 | 0.23937 | 0 | 0 | 0
256:80653 | ADAMSTOWN 132 | URBAN | 576 | 316.3927 | 1262.2719 | 1.1622 | 2.1302 | 0 | 3 | 371.7 | 371.7 | 0.0069444 | 0.0069444 | 0 | 0 | 0
258:80773 | JESMOND 132 | URBAN | 389 | 1133.3027 | 1594.6941 | 3.4865 | 6.763 | 5.4157 | 2 | 393.3667 | 393.3667 | 0.010283 | 0.010283 | 1 | 315 | 0.0077121
258:80775 | JESMOND 132 | URBAN | 1953 | 7595.0773 | 1657.7645 | 4.3248 | 182.5585 | 6061.041 | 12 | 8560.25 | 8382.4333 | 0.06042 | 0.059908 | 4 | 284205 | 0.3021
258:80776 | JESMOND 132 | URBAN | 318 | 1021.0104 | 633.8319 | 1.7337 | 146.8087 | 0 | 1 | 17172 | 17172 | 1 | 1 | 0 | 0 | 0
258:80778 | JESMOND 132 | URBAN | 1174 | 4092.5244 | 1810.259 | 2.6482 | 32.8704 | 498.3252 | 3 | 2517.1 | 2517.1 | 0.03833 | 0.03833 | 2 | 38160 | 0.18058
258:80779 | JESMOND 132 | URBAN | 1196 | 5840.7215 | 2134.4337 | 4.0962 | 30.226 | 0 | 6 | 1496.4167 | 842.3 | 0.0050167 | 0.0041806 | 0 | 0 | 0
258:80784 | JESMOND 132 | URBAN | 1837 | 7627.3845 | 2345.0214 | 5.506 | 1632.5796 | 3375.2895 | 19 | 60129.4 | 21129.2167 | 0.19706 | 0.16059 | 6 | 124315 | 0.2417
258:80785 | JESMOND 132 | URBAN | 1469 | 7189.4697 | 3573.6132 | 4.02 | 2891.1786 | 27.7524 | 12 | 145848.7833 | 19540.4667 | 1.8285 | 0.82709 | 4 | 1400 | 0.0027229
258:80787 | JESMOND 132 | URBAN | 1527 | 7386.8595 | 1952.6772 | 4.0771 | 1550.0094 | 1020.5283 | 7 | 77095.8333 | 77095.8333 | 1.0203 | 1.0203 | 2 | 50760 | 0.11133
258:80790 | JESMOND 132 | URBAN | 735 | 1226.7423 | 3677.1397 | 2.6863 | 14.3177 | 0 | 2 | 1080.85 | 1080.85 | 0.014966 | 0.014966 | 0 | 0 | 0
258:80791 | JESMOND 132 | URBAN | 791 | 4711.4177 | 1163.6253 | 2.1148 | 663.9947 | 4.432 | 8 | 63672.5167 | 63414.1333 | 1.0088 | 1.0076 | 0 | 425 | 0.0012642
261:81864 | CHARLESTOWN 132 | URBAN | 1169 | 5157.494 | 2764.6968 | 4.3629 | 703.478 | 4082.9642 | 12 | 32698.3167 | 32698.3167 | 1.0684 | 1.0684 | 5 | 189780 | 0.56459
261:81865 | CHARLESTOWN 132 | URBAN | 978 | 6619.9347 | 1207.2993 | 3.6008 | 118.8586 | 1937.918 | 6 | 6693.9 | 6409.6167 | 0.10941 | 0.10838 | 3 | 109140 | 0.32822
261:81867 | CHARLESTOWN 132 | URBAN | 172 | 0 | 834.4808 | 1.7528 | 0 | 136.1313 | 0 | 0 | 0 | 0 | 0 | 1 | 15750 | 0.14535
261:81870 | CHARLESTOWN 132 | URBAN | 1592 | 8294.3824 | 2081.5922 | 5.5441 | 546.9163 | 9.842 | 14 | 20004.9833 | 20004.9833 | 0.1451 | 0.1451 | 1 | 360 | 0.0037688
261:81876 | CHARLESTOWN 132 | URBAN | 989 | 4746.9102 | 306.092 | 2.7625 | 151.6289 | 0 | 9 | 11130.75 | 10984.8167 | 0.25784 | 0.25683 | 0 | 0 | 0
261:81879 | CHARLESTOWN 132 | URBAN | 2107 | 8791.7542 | 690.9057 | 5.2584 | 6704.6526 | 0 | 14 | 258569.65 | 258569.65 | 2.8766 | 2.8766 | 0 | 0 | 0
261:81882 | CHARLESTOWN 132 | URBAN | 1417 | 8984.5649 | 2914.5316 | 5.5632 | 2449.51 | 8.6414 | 9 | 89290.8 | 89290.8 | 0.9633 | 0.9633 | 3 | 315 | 0.0035286
261:81885 | CHARLESTOWN 132 | URBAN | 1032 | 1314.6847 | 2281.6253 | 4.3248 | 172.3815 | 104.2856 | 4 | 8083.05 | 8083.05 | 0.073643 | 0.073643 | 2 | 4890 | 0.062984
261:81886 | CHARLESTOWN 132 | URBAN | 823 | 2885.3023 | 2873.0029 | 3.0102 | 39.5111 | 60.1176 | 4 | 2661.7833 | 2661.7833 | 0.019441 | 0.019441 | 1 | 4050 | 0.036452
264:81231 | RAYMOND TERRACE 33 | URBAN | 272 | 1015.8414 | 4800.09 | 0.76208 | 59.5257 | 95.8274 | 2 | 15840 | 15840 | 1.2132 | 1.2132 | 2 | 25500 | 0.61765
264:81236 | RAYMOND TERRACE 33 | URBAN | 1753 | 6655.3093 | 8399.4222 | 4.8392 | 403.0998 | 2842.7644 | 12 | 16892.3167 | 15893.1 | 0.045636 | 0.045066 | 3 | 119129 | 0.26013
264:81240 | RAYMOND TERRACE 33 | SHORT RURAL | 819 | 78844.2379 | 9005.5776 | 11.4503 | 11899.8887 | 23225.4431 | 40 | 210755.4333 | 210755.4333 | 4.6874 | 4.6874 | 51 | 411339 | 1.4078
264:81241 | RAYMOND TERRACE 33 | SHORT RURAL | 1288 | 7438.7593 | 7427.7716 | 8.7068 | 5322.3792 | 3547.2438 | 3 | 123965.25 | 123865.6833 | 1.0272 | 1.0264 | 1 | 82620 | 0.25155
264:81244 | RAYMOND TERRACE 33 | URBAN | 1241 | 31869.1345 | 7628.2377 | 4.3058 | 3198.3398 | 4100.7101 | 15 | 150635.2167 | 53544.2167 | 1.5496 | 0.55923 | 6 | 193135 | 0.55761
265:81641 | TOMAGO 33 | URBAN | 29 | 1644.6283 | 6592.0108 | 4.039 | 0 | 41.8657 | 0 | 0 | 0 | 0 | 0 | 3 | 2102 | 0.24138
265:81648 | TOMAGO 33 | URBAN | 174 | 9036.9621 | 7257.5912 | 5.8109 | 678.2382 | 120.262 | 4 | 23669.7 | 23669.7 | 1.1207 | 1.1207 | 4 | 4197 | 0.091954
265:81649 | TOMAGO 33 | URBAN | 68 | 9311.3209 | 4492.5992 | 2.6101 | 18.1352 | 80.7523 | 3 | 1409 | 1330 | 0.32353 | 0.30882 | 4 | 6274 | 0.44118
265:81651 | TOMAGO 33 | URBAN | 165 | 10586.6715 | 2016.9733 | 2.0195 | 420.4932 | 1233.6535 | 9 | 42224.4 | 41372.55 | 2.3697 | 1.8788 | 10 | 123879 | 1.7818
501:48115 | MAITLAND CENTRAL 33 | SHORT RURAL | 1169 | 15145.1594 | 5017.9711 | 4.6677 | 415.6838 | 3082.9468 | 19 | 18059.5667 | 17580.6333 | 0.061591 | 0.060736 | 15 | 133940 | 0.39778
501:48116 | MAITLAND CENTRAL 33 | URBAN | 66 | 0 | 479.034 | 1.1241 | 15.2131 | 0 | 1 | 2744.5833 | 2744.5833 | 0.5303 | 0.5303 | 0 | 0 | 0
501:48117 | MAITLAND CENTRAL 33 | URBAN | 142 | 1427.412 | 762.3016 | 1.6194 | 3.57 | 2.9547 | 0 | 447.05 | 447.05 | 0.0070423 | 0.0070423 | 1 | 370 | 0.014085
501:48118 | MAITLAND CENTRAL 33 | SHORT RURAL | 288 | 6712.1709 | 192.3398 | 1.2003 | 207.232 | 65.7988 | 5 | 35012.7833 | 35012.7833 | 1.1736 | 1.1736 | 3 | 11117 | 0.23264
501:48122 | MAITLAND CENTRAL 33 | SHORT RURAL | 949 | 16203.3536 | 3006.2761 | 3.7151 | 4920.0861 | 1020.183 | 17 | 268564.4 | 268564.4 | 1.3119 | 1.3119 | 5 | 55687 | 0.22234
501:48123 | MAITLAND CENTRAL 33 | SHORT RURAL | 1162 | 36508.9308 | 10731.545 | 4.7058 | 2597.5862 | 10660.5701 | 20 | 111939.5 | 107233.5 | 0.48021 | 0.46213 | 18 | 459403 | 0.97849
501:48124 | MAITLAND CENTRAL 33 | URBAN | 278 | 0 | 1154.0232 | 3.0293 | 3.3993 | 808.5834 | 0 | 227.5667 | 227.5667 | 0.0035971 | 0.0035971 | 3 | 54130 | 0.85971
501:48125 | MAITLAND CENTRAL 33 | URBAN | 753 | 4064.6315 | 1476.4163 | 3.7151 | 20.2765 | 4127.4845 | 3 | 1106.8 | 1106.8 | 0.025232 | 0.025232 | 7 | 225300 | 0.84462
502:48001 | TELARAH 33 | URBAN | 275 | 1959.3193 | 193.8768 | 0.78113 | 0.74258 | 316.6251 | 0 | 192.7833 | 192.7833 | 0.0036364 | 0.0036364 | 1 | 82200 | 0.99636
502:48002 | TELARAH 33 | URBAN | 350 | 2527.9176 | 464.1918 | 2.5339 | 1.7599 | 0 | 0 | 140.85 | 140.85 | 0.0028571 | 0.0028571 | 0 | 0 | 0
502:48004 | TELARAH 33 | URBAN | 1693 | 6258.2412 | 7233.0497 | 5.7347 | 141.9665 | 721.1014 | 10 | 5020.3 | 4250.4 | 0.015948 | 0.014767 | 1 | 25500 | 0.029533
502:48008 | TELARAH 33 | URBAN | 835 | 3194.8532 | 203.9044 | 2.4196 | 1124.4071 | 0 | 6 | 94238.9 | 94238.9 | 1.1257 | 1.1257 | 0 | 0 | 0
502:48010 | TELARAH 33 | SHORT RURAL | 1621 | 29032.1829 | 9538.4921 | 5.7537 | 13847.9125 | 10020.8883 | 29 | 488076.3 | 488076.3 | 2.0642 | 2.0642 | 14 | 353191 | 0.63788
503:48011 | EAST MAITLAND 33 | SHORT RURAL | 1877 | 26492.614 | 2203.4814 | 5.0869 | 1526.8437 | 9038.1268 | 34 | 60868.65 | 60868.65 | 0.18647 | 0.18647 | 14 | 360311 | 0.57059
503:48012 | EAST MAITLAND 33 | URBAN | 877 | 2744.9543 | 1525.098 | 3.1817 | 21.7724 | 1804.7508 | 6 | 1387.7167 | 1387.7167 | 0.0068415 | 0.0068415 | 4 | 115030 | 0.42645
503:48016 | EAST MAITLAND 33 | URBAN | 877 | 3958.6094 | 196.5229 | 2.191 | 654.81 | 0 | 9 | 60607.7 | 60607.7 | 1.0661 | 1.0661 | 0 | 0 | 0
503:48076 | EAST MAITLAND 33 | URBAN | 196 | 6.1606 | 2597.3043 | 5.0678 | 807.1972 | 0 | 7 | 32300.4333 | 32300.4333 | 1.449 | 1.449 | 0 | 0 | 0
503:48077 | EAST MAITLAND 33 | URBAN | 1071 | 756.3506 | 7651.13 | 5.3917 | 139.5573 | 2808.9602 | 1 | 5249 | 5249 | 0.027077 | 0.027077 | 3 | 105650 | 0.23343
503:48078 | EAST MAITLAND 33 | URBAN | 1604 | 7111.3212 | 1721.6941 | 4.7249 | 3679.6605 | 297.997 | 10 | 157930.65 | 157930.65 | 1.7556 | 1.7556 | 3 | 12790 | 0.086035
504:48026 | CESSNOCK 33 | SHORT RURAL | 1262 | 31909.727 | 900.131 | 4.4772 | 2676.3212 | 2973.0304 | 21 | 121221.8 | 120773.9833 | 1.2068 | 1.2052 | 11 | 134661 | 0.43106
504:48027 | CESSNOCK 33 | URBAN | 136 | 213.2867 | 1450.8742 | 3.7532 | 1.1845 | 12.4003 | 1 | 64 | 64 | 0.029412 | 0.029412 | 1 | 670 | 0.014706
504:48028 | CESSNOCK 33 | URBAN | 1245 | 10096.5089 | 666.5609 | 3.9057 | 967.3519 | 62.208 | 9 | 50227.4333 | 50227.4333 | 0.31647 | 0.31647 | 1 | 3230 | 0.030522
504:48029 | CESSNOCK 33 | URBAN | 368 | 2157.2551 | 409.9285 | 1.5813 | 767.0639 | 0 | 5 | 98370.25 | 98370.25 | 1.6685 | 1.6685 | 0 | 0 | 0
504:48031 | CESSNOCK 33 | SHORT RURAL | 535 | 111089.9362 | 634.0499 | 2.0386 | 2807.4493 | 8113.451 | 30 | 279279.1333 | 192183.2833 | 3.9776 | 3.6299 | 48 | 807109 | 3.5121
504:48032 | CESSNOCK 33 | URBAN | 332 | 1301.7763 | 721.1113 | 2.0767 | 870.4838 | 0 | 2 | 85005.0167 | 85005.0167 | 1.6958 | 1.6958 | 0 | 0 | 0
504:48033 | CESSNOCK 33 | SHORT RURAL | 1150 | 33944.9386 | 1119.3992 | 3.8104 | 8326.652 | 3789.7868 | 21 | 443150.0167 | 442960.2333 | 3.1496 | 3.1487 | 3 | 201695 | 0.3687
507:80917 | KURRI KURRI 132 11kV | URBAN | 1270 | 6564.652 | 1312.4863 | 3.6961 | 274.5197 | 1185.1457 | 13 | 15061.9833 | 14654.9 | 0.084252 | 0.083465 | 2 | 65025 | 0.13386
507:80920 | KURRI KURRI 132 11kV | SHORT RURAL | 83 | 1657.5855 | 130.7937 | 0.41914 | 2.3312 | 0 | 3 | 1127.8833 | 1127.8833 | 0.13253 | 0.13253 | 0 | 0 | 0
507:80922 | KURRI KURRI 132 11kV | SHORT RURAL | 1152 | 24230.9314 | 1641.4499 | 3.8295 | 676.5388 | 2689.0681 | 18 | 35826.7167 | 35826.7167 | 0.31076 | 0.31076 | 11 | 142402 | 0.51736
507:80923 | KURRI KURRI 132 11kV | SHORT RURAL | 643 | 40175.6868 | 4602.1255 | 4.2867 | 2434.2009 | 2731.0816 | 28 | 115155.3833 | 114498.55 | 1.6252 | 1.6174 | 14 | 129200 | 0.48989
507:80925 | KURRI KURRI 132 11kV | SHORT RURAL | 1522 | 27674.9866 | 789.3953 | 5.0869 | 690.2982 | 7374.6405 | 15 | 27519.2 | 27519.2 | 0.17148 | 0.17148 | 7 | 293995 | 0.55519
507:80926 | KURRI KURRI 132 11kV | URBAN | 43 | 2885.8802 | 1470.2226 | 4.0771 | 327.5783 | 244.0743 | 4 | 16293.4 | 16293.4 | 2.907 | 2.907 | 4 | 12140 | 1.0233
507:80931 | KURRI KURRI 132 11kV | URBAN | 1150 | 6536.5112 | 1402.3141 | 3.7913 | 24.7778 | 0 | 6 | 1325.3167 | 669.8 | 0.0052174 | 0.0043478 | 0 | 0 | 0
507:80932 | KURRI KURRI 132 11kV | SHORT RURAL | 1114 | 63109.3077 | 3104.6933 | 4.8392 | 2399.9758 | 3009.232 | 22 | 100573.4833 | 100573.4833 | 1.0826 | 1.0826 | 9 | 126105 | 0.35458
508:82578 | BRANDY HILL 132 | SHORT RURAL | 422 | 62039.6212 | 842.5051 | 1.5242 | 1254.2386 | 4475.945 | 25 | 166878.55 | 166878.55 | 6.173 | 6.173 | 46 | 595532 | 3.455
509:48039 | PAXTON 33 | LONG RURAL | 1161 | 277350.7225 | 2048.9439 | 2.9531 | 14179.7051 | 4745.1914 | 80 | 973746.3667 | 694388.95 | 2.7786 | 2.6288 | 66 | 325861 | 0.88803
509:48040 | PAXTON 33 | SHORT RURAL | 830 | 68761.7743 | 644.0054 | 3.2769 | 2916.6252 | 4990.0862 | 28 | 180493.9 | 180493.9 | 1.8241 | 1.8241 | 33 | 308809 | 1.1651
510:48164 | WALLALONG 33 | SHORT RURAL | 825 | 97415.9136 | 4373.3645 | 4.2486 | 13423.641 | 5803.6672 | 38 | 640731.1167 | 640731.1167 | 2.7067 | 2.7067 | 46 | 277018 | 0.96727
511:29869 | RUTHERFORD 33 | SHORT RURAL | 30 | 0 | 4376.3844 | 0.64777 | 0 | 17.7281 | 0 | 0 | 0 | 0 | 0 | 1 | 5550 | 0.33333
511:29872 | RUTHERFORD 33 | URBAN | 66 | 3208.0883 | 1022.7171 | 4.6106 | 2.9556 | 461.4402 | 2 | 130 | 130 | 0.030303 | 0.030303 | 4 | 20296 | 0.98485
511:29873 | RUTHERFORD 33 | SHORT RURAL | 1368 | 23907.1871 | 13525.1466 | 6.0776 | 747.173 | 343.4212 | 5 | 24931.0667 | 21852.0667 | 0.092836 | 0.085526 | 5 | 11459 | 0.025585
511:29877 | RUTHERFORD 33 | SHORT RURAL | 1147 | 35557.3037 | 3681.1668 | 5.6965 | 10114.3699 | 1275.4251 | 22 | 360062.5833 | 360062.5833 | 2.1831 | 2.1831 | 9 | 45404 | 0.1857
511:29878 | RUTHERFORD 33 | SHORT RURAL | 1014 | 145417.6737 | 3806.621 | 5.7918 | 8017.7636 | 20233.4083 | 49 | 280730.7667 | 280730.7667 | 1.1292 | 1.1292 | 56 | 708444.4667 | 1.6292
511:29880 | RUTHERFORD 33 | URBAN | 1435 | 5347.5501 | 5684.7734 | 6.4777 | 95.5948 | 40.4072 | 7 | 2992.7167 | 2992.7167 | 0.018118 | 0.018118 | 4 | 1265 | 0.0034843
512:48046 | BRANXTON 66 | SHORT RURAL | 1776 | 51946.276 | 897.0866 | 5.7156 | 1754.9976 | 5951.2213 | 39 | 62268.1 | 60187.1 | 1.237 | 1.2207 | 12 | 211152 | 0.34009
512:48048 | BRANXTON 66 | SHORT RURAL | 835 | 42699.3797 | 643.7632 | 1.7147 | 844.2937 | 4615.0375 | 14 | 99853.0667 | 99853.0667 | 0.9988 | 0.9988 | 18 | 545812 | 1.6192
512:48049 | BRANXTON 66 | SHORT RURAL | 908 | 177455.0367 | 321.835 | 4.0581 | 14258.9322 | 3409.7379 | 90 | 712553.95 | 712553.95 | 4.5991 | 4.5991 | 41 | 170393 | 0.78634
513:48051 | SINGLETON 66 | URBAN | 1176 | 5182.8628 | 823.2275 | 5.2012 | 1457.3533 | 415.4964 | 9 | 56821.4833 | 56821.4833 | 1.1139 | 1.1139 | 1 | 16200 | 0.02551
513:48052 | SINGLETON 66 | URBAN | 526 | 2607.3947 | 1444.4356 | 3.0293 | 1021.4834 | 222.2895 | 4 | 68382.4333 | 68382.4333 | 1.0038 | 1.0038 | 3 | 14881 | 0.072243
513:48056 | SINGLETON 66 | SHORT RURAL | 251 | 49067.9505 | 1063.0645 | 2.8769 | 2764.7414 | 367.3455 | 31 | 194889.2667 | 194889.2667 | 8.3307 | 8.3307 | 13 | 25894.5333 | 0.49402
513:48057 | SINGLETON 66 | URBAN | 349 | 2761.8908 | 243.8563 | 2.2481 | 2.5823 | 0 | 2 | 232.9333 | 232.9333 | 0.0057307 | 0.0057307 | 0 | 0 | 0
513:48058 | SINGLETON 66 | URBAN | 511 | 4997.5936 | 1848.1874 | 3.1626 | 42.2733 | 1118.6612 | 5 | 2710.6167 | 2710.6167 | 0.12329 | 0.12329 | 6 | 71730 | 0.55186
513:48059 | SINGLETON 66 | SHORT RURAL | 953 | 80322.5904 | 941.9866 | 3.9628 | 3464.4913 | 2131.5822 | 47 | 177290.9167 | 177290.9167 | 1.3473 | 1.3473 | 29 | 109081 | 0.3809
514:18137 | NEWDELL 66 | SHORT RURAL | 181 | 75649.2692 | 961.0403 | 2.2862 | 1661.3809 | 1689.6066 | 38 | 147366.35 | 147366.35 | 5.7072 | 5.7072 | 26 | 149870 | 2.7403
514:18146 | NEWDELL 66 | SHORT RURAL | 5 | 13554.4006 | 553.2759 | 2.1148 | 72.9458 | 0 | 3 | 6995 | 6995 | 1.8 | 1.8 | 0 | 0 | 0
514:18160 | NEWDELL 66 | HV CUSTOMERS | 3 | 483.6256 | 524.2751 | 6.1347 | 0 | 44.4696 | 0 | 0 | 0 | 0 | 0 | 1 | 1470 | 1
515:35192 | MT THORLEY 66 | SHORT RURAL | 335 | 87101.5492 | 708.1062 | 1.7718 | 1381.3416 | 401.0465 | 27 | 158098.7667 | 158098.7667 | 2.6269 | 2.6269 | 14 | 45901 | 0.47463
515:35193 | MT THORLEY 66 | SHORT RURAL | 149 | 44207.1933 | 443.1376 | 1.7337 | 710.9604 | 405.3964 | 17 | 83159.9833 | 83159.9833 | 3.9396 | 3.9396 | 12 | 47418.6167 | 1.0805
515:35197 | MT THORLEY 66 | LONG RURAL | 533 | 225874.7985 | 491.6984 | 1.9052 | 2036.2703 | 1597.058 | 58 | 216743.35 | 216743.35 | 2.2383 | 2.2383 | 33 | 169993 | 1.0131
515:35198 | MT THORLEY 66 | SHORT RURAL | 75 | 41929.3431 | 1981.7668 | 2.3624 | 173.7425 | 70.1423 | 7 | 14914.0167 | 14914.0167 | 2.92 | 2.92 | 7 | 6021 | 0.48
515:35200 | MT THORLEY 66 | URBAN | 73 | 7776.2712 | 1081.4672 | 3.9628 | 129.0555 | 187.5963 | 7 | 6604.25 | 6604.25 | 1.2466 | 1.2466 | 3 | 9600 | 0.38356
516:48065 | LEMINGTON 66 | SHORT RURAL | 43 | 32041.8888 | 93.8897 | 0.76208 | 21.7929 | 34.4603 | 12 | 5799.1667 | 5799.1667 | 0.53488 | 0.53488 | 4 | 9170 | 0.67442
516:48066 | LEMINGTON 66 | SHORT RURAL | 98 | 46603.2509 | 354.7051 | 0.80018 | 195.0835 | 54.196 | 11 | 49440.3667 | 49440.3667 | 3.051 | 3.051 | 5 | 13735 | 0.45918
516:48067 | LEMINGTON 66 | SHORT RURAL | 283 | 79402.6443 | 27.6255 | 2.3243 | 728.66 | 434.6969 | 18 | 63573.4 | 63573.4 | 1.2686 | 1.2686 | 9 | 37926 | 0.57597
520:48172 | MITCHELLS FLAT 66 | SHORT RURAL | 395 | 178128.076 | 0 | 1.3908 | 1271.5355 | 838.1863 | 65 | 185402.6667 | 185402.6667 | 3.2481 | 3.2481 | 26 | 122216 | 0.92911
523:33501 | SINGLETON NORTH 66 | SHORT RURAL | 778 | 169450.7893 | 965.5433 | 3.2198 | 6819.3132 | 3125.2221 | 47 | 429501.1 | 429501.1 | 3.4743 | 3.4743 | 34 | 196836 | 0.79177
523:33503 | SINGLETON NORTH 66 | URBAN | 792 | 1464.7067 | 4213.6928 | 2.6292 | 6.8053 | 0 | 4 | 524.9 | 524.9 | 0.0050505 | 0.0050505 | 0 | 0 | 0
523:33508 | SINGLETON NORTH 66 | SHORT RURAL | 479 | 32379.2852 | 2365.622 | 5.3917 | 36.4797 | 3751.8562 | 9 | 1372.0667 | 1372.0667 | 0.033403 | 0.033403 | 20 | 141114 | 0.92276
523:33509 | SINGLETON NORTH 66 | URBAN | 441 | 1787.9348 | 2985.8771 | 3.6199 | 135.005 | 0 | 3 | 7563.2167 | 7563.2167 | 0.092971 | 0.092971 | 0 | 0 | 0
523:33511 | SINGLETON NORTH 66 | SHORT RURAL | 154 | 0 | 2004.2663 | 0.20957 | 0 | 2.0152 | 0 | 0 | 0 | 0 | 0 | 1 | 1950 | 0.084416
524:33570 | NULKABA 33 | SHORT RURAL | 1257 | 17822.3525 | 859.3625 | 3.8676 | 1995.3487 | 2238.4263 | 11 | 104624.4333 | 104624.4333 | 0.78679 | 0.78679 | 2 | 117370 | 0.33015
524:33572 | NULKABA 33 | SHORT RURAL | 1740 | 29200.3889 | 9472.589 | 7.1254 | 9060.4478 | 21590.8134 | 23 | 257862.6333 | 257862.6333 | 1.2374 | 1.2374 | 16 | 614480 | 1.0678
524:33576 | NULKABA 33 | SHORT RURAL | 171 | 26292.9819 | 3371.2102 | 3.2007 | 566.6148 | 320.1651 | 10 | 35899.55 | 35899.55 | 1.4094 | 1.4094 | 7 | 20285 | 0.40351
524:33578 | NULKABA 33 | URBAN | 869 | 5574.7521 | 1816.4157 | 3.4484 | 10.158 | 0 | 5 | 597.3667 | 597.3667 | 0.0057537 | 0.0057537 | 0 | 0 | 0
524:33580 | NULKABA 33 | SHORT RURAL | 315 | 17812.9782 | 1591.5756 | 2.4196 | 471.4585 | 100.8566 | 9 | 39513.9167 | 39513.9167 | 1.3937 | 1.3937 | 5 | 8453 | 0.24444
525:34580 | TOMALPIN 33 | SHORT RURAL | 3 | 0.89952 | 2667.9889 | 0.80018 | 1.018 | 0 | 1 | 258 | 258 | 1 | 1 | 0 | 0 | 0
525:34586 | TOMALPIN 33 | SHORT RURAL | 3 | 421.5315 | 2048.3769 | 0.038104 | 0.12007 | 0.31755 | 2 | 639 | 639 | 2 | 2 | 2 | 1690 | 1.3333
526:34635 | ROTHBURY 132 11KV | SHORT RURAL | 29 | 10838.3007 | 1625.574 | 0.22862 | 0.63517 | 8.3697 | 3 | 563.4 | 563.4 | 0.10345 | 0.10345 | 1 | 7424 | 1
526:34636 | ROTHBURY 132 11KV | SHORT RURAL | 311 | 72181.7688 | 589.8809 | 3.1817 | 2255.0677 | 638.4484 | 26 | 143732 | 143732 | 2.4019 | 2.4019 | 16 | 40693 | 0.46624
526:34640 | ROTHBURY 132 11KV | SHORT RURAL | 160 | 41330.8208 | 4556.3854 | 4.3629 | 1206.6011 | 451.5184 | 24 | 56083.95 | 56083.95 | 2.475 | 2.475 | 9 | 20987 | 0.3875
526:34641 | ROTHBURY 132 11KV | SHORT RURAL | 134 | 8908.4685 | 151.0379 | 0.59061 | 63.46 | 8.6207 | 6 | 21789.5667 | 21789.5667 | 1.097 | 1.097 | 2 | 2960 | 0.059701
801:74117 | MUSWELLBROOK 33 | SHORT RURAL | 19 | 1923.3966 | 62.6792 | 0.11431 | 0.40107 | 0 | 3 | 711.5 | 711.5 | 0.15789 | 0.15789 | 0 | 0 | 0
801:74118 | MUSWELLBROOK 33 | URBAN | 794 | 3984.8432 | 2336.1212 | 4.2105 | 1215.2057 | 617.3762 | 13 | 58528.5667 | 58528.5667 | 2.1851 | 2.1851 | 3 | 29735 | 0.19144
801:74119 | MUSWELLBROOK 33 | URBAN | 617 | 0 | 7398.9356 | 2.5339 | 376.9964 | 868.657 | 3 | 30171.4333 | 30171.4333 | 0.99514 | 0.99514 | 11 | 69519.5667 | 0.56726
801:74120 | MUSWELLBROOK 33 | SHORT RURAL | 468 | 3706.3573 | 3039.4619 | 1.8861 | 2.9718 | 32.6461 | 2 | 319.5167 | 319.5167 | 0.0042735 | 0.0042735 | 1 | 3510 | 0.027778
801:74121 | MUSWELLBROOK 33 | SHORT RURAL | 476 | 190286.8696 | 1965.0562 | 2.1529 | 1377.1565 | 2449.1092 | 35 | 129722.4667 | 129722.4667 | 2.7689 | 2.7689 | 33 | 230696 | 1.5861
801:74122 | MUSWELLBROOK 33 | URBAN | 1181 | 6035.7119 | 2741.0779 | 4.7821 | 117.0552 | 2007.1021 | 12 | 4963.95 | 4817.6 | 0.069433 | 0.068586 | 6 | 85115 | 0.28196
801:74123 | MUSWELLBROOK 33 | SHORT RURAL | 271 | 75340.3662 | 158.9512 | 0.78113 | 70.2617 | 107.8913 | 22 | 18240.85 | 18240.85 | 0.5941 | 0.5941 | 6 | 28010 | 0.25092
802:82215 | BAERAMI 33 | SHORT RURAL | 40 | 26875.2886 | 0 | 0.40009 | 65.4376 | 0.57215 | 9 | 33167.9167 | 33167.9167 | 4.25 | 4.25 | 2 | 290 | 1.025
802:82220 | BAERAMI 33 | SHORT RURAL | 60 | 34729.3731 | 0 | 0.34294 | 66.6113 | 21.6119 | 5 | 39390 | 39390 | 2.5667 | 2.5667 | 3 | 12780 | 1.8
802:82225 | BAERAMI 33 | SHORT RURAL | 105 | 94616.987 | 1215.9219 | 0.49535 | 130.7588 | 144.8302 | 10 | 53531.3333 | 53531.3333 | 2.1048 | 2.1048 | 4 | 59292 | 2.8381
803:74007 | ABERDEEN 33 | SHORT RURAL | 443 | 16798.6669 | 5004.589 | 1.6575 | 194.8471 | 558.3329 | 7 | 23838.8333 | 23838.8333 | 0.89616 | 0.89616 | 9 | 68310 | 0.61851
803:74010 | ABERDEEN 33 | SHORT RURAL | 685 | 61354.5752 | 2826.546 | 3.0674 | 2509.639 | 234.0702 | 20 | 165918.85 | 165918.85 | 2.7942 | 2.7942 | 3 | 15475 | 0.10803
803:74016 | ABERDEEN 33 | SHORT RURAL | 154 | 49157.6918 | 26.4336 | 0.83829 | 56.3376 | 13.4346 | 20 | 13628.75 | 13628.75 | 1.513 | 1.513 | 3 | 3250 | 0.16883
806:82662 | MOONAN 33 | SHORT RURAL | 230 | 185393.9199 | 642.4457 | 0.26673 | 634.3062 | 339.5036 | 46 | 482260.0333 | 445162.0333 | 8.8478 | 7.8522 | 19 | 258123 | 3.3957
806:82667 | MOONAN 33 | SHORT RURAL | 40 | 37411.2239 | 0 | 0.97165 | 221.4188 | 95.2525 | 7 | 46212 | 39732 | 5.1 | 4.1 | 9 | 19880 | 1.65
807:74179 | DENMAN 66 | SHORT RURAL | 150 | 68777.6965 | 1396.6806 | 1.0098 | 141.7676 | 158.8586 | 15 | 28471.5833 | 28471.5833 | 3.16 | 3.16 | 8 | 31904 | 0.81333
807:74180 | DENMAN 66 | SHORT RURAL | 118 | 63854.2045 | 885.9582 | 0.5144 | 10.5877 | 61.9059 | 14 | 4173.9667 | 4173.9667 | 0.25424 | 0.25424 | 12 | 24405 | 0.67797
807:74181 | DENMAN 66 | SHORT RURAL | 692 | 15016.4806 | 1433.9434 | 2.2862 | 31.115 | 62.5697 | 4 | 2759.9333 | 2759.9333 | 0.037572 | 0.037572 | 1 | 5550 | 0.043353
807:74183 | DENMAN 66 | SHORT RURAL | 97 | 24076.8779 | 474.3003 | 1.0669 | 137.9546 | 14.9416 | 11 | 26221.55 | 26221.55 | 2.5258 | 2.5258 | 3 | 2840 | 0.16495
807:74184 | DENMAN 66 | SHORT RURAL | 496 | 163691.2719 | 1292.7693 | 2.7244 | 1067.1502 | 967.6963 | 50 | 79432.8 | 79432.8 | 1.0403 | 1.0403 | 21 | 72030 | 0.52419
810:74050 | MERRIWA 33 | SHORT RURAL | 98 | 102080.0236 | 0 | 0.53346 | 184.2075 | 25.9294 | 21 | 70026.0333 | 70026.0333 | 3.5612 | 3.5612 | 10 | 9857 | 0.42857
810:74054 | MERRIWA 33 | LONG RURAL | 319 | 330034.4625 | 0 | 0.80018 | 1188.6622 | 256.0612 | 49 | 301244.7667 | 301244.7667 | 3.8903 | 3.8903 | 58 | 64894.05 | 0.90909
810:74058 | MERRIWA 33 | SHORT RURAL | 200 | 124248.1351 | 0 | 0.4382 | 310.3287 | 234.6666 | 16 | 143616.55 | 143616.55 | 2.725 | 2.725 | 18 | 108601 | 1.77
810:74062 | MERRIWA 33 | SHORT RURAL | 599 | 12480.2704 | 193.5148 | 1.9814 | 2919.5534 | 411.5393 | 9 | 298808.8333 | 298808.8333 | 2.2571 | 2.2571 | 2 | 42120 | 0.2404
811:74234 | ROUCHEL 33 | SHORT RURAL | 257 | 117422.0541 | 522.3552 | 1.2193 | 799.8696 | 420.2878 | 32 | 133030 | 93664 | 5.1868 | 4.2412 | 10 | 69900 | 0.86381
812:19065 | MITCHELL LINE 66 | SHORT RURAL | 133 | 10681.9339 | 3454.7706 | 2.6101 | 81.9074 | 64.5606 | 7 | 6363.75 | 6363.75 | 0.27068 | 0.27068 | 2 | 5016 | 0.12782
812:19066 | MITCHELL LINE 66 | SHORT RURAL | 1769 | 6228.0666 | 25595.8327 | 6.7444 | 17165.1952 | 1647.226 | 18 | 516126.1167 | 516126.1167 | 3.6733 | 3.6733 | 11 | 49529.0833 | 0.12606
812:19071 | MITCHELL LINE 66 | SHORT RURAL | 831 | 13950.2432 | 3609.4685 | 3.0293 | 565.9508 | 16.1328 | 12 | 37887.15 | 37887.15 | 0.16968 | 0.16968 | 1 | 1080 | 0.0048135
812:19072 | MITCHELL LINE 66 | SHORT RURAL | 204 | 114800.9982 | 1233.3732 | 2.8197 | 684.3681 | 73.6236 | 27 | 49219.6333 | 49219.6333 | 1.0931 | 1.0931 | 7 | 5295 | 0.10294
813:89055 | SCONE 66 | SHORT RURAL | 581 | 139982.2891 | 1294.3739 | 4.763 | 1902.7244 | 370.016 | 40 | 81011.4167 | 81011.4167 | 0.79862 | 0.79862 | 12 | 15754 | 0.12565
813:89058 | SCONE 66 | SHORT RURAL | 2 | 3825.8248 | 430.0236 | 0.019052 | 0.011385 | 0 | 0 | 121.1833 | 121.1833 | 0.5 | 0.5 | 0 | 0 | 0
813:89059 | SCONE 66 | URBAN | 330 | 2120.4097 | 853.7304 | 2.5911 | 18.6082 | 0 | 3 | 1456.3833 | 1456.3833 | 0.0090909 | 0.0090909 | 0 | 0 | 0
813:89061 | SCONE 66 | LONG RURAL | 603 | 310529.4828 | 2308.151 | 2.2672 | 1993.5267 | 1913.6642 | 69 | 178314 | 177929.3333 | 1.9668 | 1.9652 | 35 | 171170.5833 | 0.85904
813:89062 | SCONE 66 | SHORT RURAL | 826 | 134713.8543 | 1931.4023 | 2.7244 | 2812.9805 | 2027.8095 | 36 | 209382.8167 | 207121.8167 | 2.793 | 2.77 | 31 | 150939 | 0.59685
813:89063 | SCONE 66 | SHORT RURAL | 1495 | 13840.8045 | 7806.3911 | 4.7249 | 2839.3944 | 1067.2206 | 11 | 121866.5167 | 121866.5167 | 1.008 | 1.008 | 3 | 45805 | 0.1398
813:89065 | SCONE 66 | URBAN | 152 | 1029.9228 | 1687.1546 | 1.1241 | 0.75079 | 0 | 0 | 135.45 | 135.45 | 0.0065789 | 0.0065789 | 0 | 0 | 0
814:82283 | ABERDEEN 66 | SHORT RURAL | 186 | 74811.1668 | 280.7799 | 0.89544 | 317.2156 | 3.0467 | 27 | 71840.1167 | 71840.1167 | 3.8871 | 3.8871 | 3 | 690 | 0.043011
ZN1068:PA11 | LIDCOMBE | URBAN | 1 | 0 | 1083.6192 | 1.2384 | 1.8622 | 0.061066 | 2 | 304.95 | 304.95 | 2 | 2 | 0 | 10 | 1
ZN1068:PA16 | LIDCOMBE | URBAN | 692 | 0.89378 | 4323.4735 | 1.5432 | 74.3489 | 0 | 1 | 9770.1167 | 9770.1167 | 0.1474 | 0.1474 | 0 | 0 | 0
ZN1068:PA17 | LIDCOMBE | URBAN | 858 | 0 | 5859.5315 | 3.2388 | 5.7552 | 0 | 0 | 360.35 | 360.35 | 0.0011655 | 0.0011655 | 0 | 0 | 0
ZN1068:PA18 | LIDCOMBE | URBAN | 548 | 0 | 2655.4104 | 3.2769 | 474.7775 | 447.9312 | 4 | 29381.3667 | 29381.3667 | 0.39234 | 0.39234 | 3 | 27720 | 0.062044
ZN1068:PA20 | LIDCOMBE | URBAN | 266 | 0 | 1010.4972 | 2.0005 | 1.6711 | 0 | 0 | 169.4 | 169.4 | 0.0037594 | 0.0037594 | 0 | 0 | 0
ZN1068:PA21 | LIDCOMBE | SHORT RURAL | 167 | 0 | 4623.0797 | 1.086 | 48.4143 | 0 | 4 | 9040.85 | 9040.85 | 0.28743 | 0.28743 | 0 | 0 | 0
ZN1068:PA26 | LIDCOMBE | URBAN | 1767 | 0 | 5090.672 | 3.8485 | 712.4516 | 645.6176 | 10 | 37541.7333 | 37541.7333 | 0.083192 | 0.083192 | 1 | 34020 | 0.071307
ZN1068:PA27 | LIDCOMBE | URBAN | 1407 | 0 | 5619.209 | 4.0771 | 25.8161 | 828.7269 | 5 | 1284.0667 | 1284.0667 | 0.0049751 | 0.0049751 | 4 | 41220 | 0.071784
ZN10990:PA1 | ARNCLIFFE | URBAN | 1466 | 2987.9832 | 1088.3767 | 2.0957 | 97.0103 | 0 | 6 | 9387.1833 | 9387.1833 | 0.040246 | 0.040246 | 0 | 0 | 0
ZN10990:PA11 | ARNCLIFFE | URBAN | 1147 | 6909.7475 | 1495.6281 | 2.2862 | 3731.075 | 0 | 9 | 330950.5333 | 330950.5333 | 2.9669 | 2.9669 | 0 | 0 | 0
ZN10990:PA12 | ARNCLIFFE | URBAN | 998 | 1876.5136 | 990.0087 | 1.3336 | 52.155 | 0 | 5 | 7930.6333 | 6162.7167 | 0.058116 | 0.048096 | 0 | 0 | 0
ZN10990:PA2 | ARNCLIFFE | URBAN | 1990 | 2766.0633 | 1849.0837 | 2.0957 | 958.738 | 0 | 11 | 92772.15 | 92772.15 | 1.0397 | 1.0397 | 0 | 0 | 0
ZN10990:PA5 | ARNCLIFFE | URBAN | 475 | 1104.3414 | 1604.9625 | 2.2862 | 800.6438 | 0 | 3 | 71018 | 10894 | 1.3579 | 0.36421 | 0 | 0 | 0
ZN10990:PA6 | ARNCLIFFE | URBAN | 992 | 1728.6952 | 662.9971 | 1.8099 | 60.6999 | 0 | 3 | 6801.0333 | 6801.0333 | 0.12399 | 0.12399 | 0 | 0 | 0
ZN10990:PA7 | ARNCLIFFE | URBAN | 1584 | 1935.3381 | 2831.274 | 2.7625 | 351.611 | 0 | 2 | 25811 | 25811 | 0.30556 | 0.30556 | 0 | 0 | 0
ZN10990:PA8 | ARNCLIFFE | URBAN | 1353 | 2157.6533 | 2380.1667 | 3.0483 | 11.7097 | 89.2886 | 3 | 779 | 525 | 0.0051737 | 0.0036955 | 1 | 5940 | 0.0081301
ZN10991:PA1 | BLAKEHURST | URBAN | 1499 | 5880.2381 | 1863.0135 | 3.9057 | 268.4977 | 0 | 4 | 13941.1 | 711.5667 | 0.02068 | 0.0020013 | 0 | 0 | 0
ZN10991:PA12 | BLAKEHURST | URBAN | 1211 | 3687.1313 | 2988.4172 | 3.0483 | 101.7364 | 0 | 8 | 6768.1 | 5548.7833 | 0.036334 | 0.033856 | 0 | 0 | 0
ZN10991:PA13 | BLAKEHURST | URBAN | 1128 | 2641.5561 | 1101.3071 | 2.3815 | 3.1342 | 0 | 0 | 266.8833 | 266.8833 | 0.00088652 | 0.00088652 | 0 | 0 | 0
ZN10991:PA5 | BLAKEHURST | URBAN | 1511 | 645.3648 | 1617.1226 | 3.0483 | 17.7054 | 0 | 3 | 1177.8667 | 1177.8667 | 0.0019854 | 0.0019854 | 0 | 0 | 0
ZN10991:PA6 | BLAKEHURST | URBAN | 1316 | 752.3943 | 2447.2168 | 2.0957 | 1100.7508 | 0 | 1 | 106514 | 106514 | 1.0008 | 1.0008 | 0 | 0 | 0
ZN10991:PA7 | BLAKEHURST | URBAN | 1571 | 1512.2301 | 1767.5854 | 3.0483 | 710.5755 | 437.424 | 4 | 47271.6333 | 29711.85 | 0.12476 | 0.091025 | 1 | 29100 | 0.0063654
ZN10991:PA8 | BLAKEHURST | URBAN | 1825 | 4710.1108 | 2168.6061 | 5.144 | 474.5182 | 0 | 3 | 18706.8 | 18706.8 | 0.041644 | 0.041644 | 0 | 0 | 0
ZN10993:PA12 | HURSTVILLE NORTH | URBAN | 1112 | 4248.3746 | 2980.0678 | 3.677 | 126.6463 | 0 | 4 | 6984.6667 | 6984.6667 | 0.061151 | 0.061151 | 0 | 0 | 0
ZN10993:PA13 | HURSTVILLE NORTH | URBAN | 732 | 1099.495 | 1318.9468 | 1.4861 | 57.1127 | 0 | 2 | 7793.7833 | 7793.7833 | 0.10929 | 0.10929 | 0 | 0 | 0
ZN10993:PA2 | HURSTVILLE NORTH | URBAN | 1022 | 2443.0252 | 958.5848 | 2.4577 | 2389.5177 | 0 | 11 | 197165.4833 | 156992.9833 | 2.271 | 2.1977 | 0 | 0 | 0
ZN10993:PA5 | HURSTVILLE NORTH | URBAN | 1588 | 4409.513 | 1522.3503 | 4.02 | 3256.4649 | 0 | 4 | 164276.0667 | 164276.0667 | 1.9484 | 1.9484 | 0 | 0 | 0
ZN10993:PA6 | HURSTVILLE NORTH | URBAN | 592 | 0 | 3337.2478 | 3.5056 | 992.6609 | 119.277 | 2 | 57424 | 57424 | 2 | 2 | 1 | 6900 | 0.077703
ZN10993:PA7 | HURSTVILLE NORTH | URBAN | 712 | 2968.971 | 1832.0587 | 3.4865 | 1237.3978 | 0 | 6 | 71972.8333 | 71972.8333 | 1.3385 | 1.3385 | 0 | 0 | 0
ZN10993:PA8 | HURSTVILLE NORTH | URBAN | 835 | 0 | 2754.2367 | 2.9531 | 89.003 | 15.2901 | 1 | 6112 | 6112 | 0.038323 | 0.038323 | 3 | 1050 | 0.0035928
ZN10994:PA1 | MORTDALE | URBAN | 1034 | 2640.8098 | 2070.9535 | 2.4387 | 6.5793 | 0 | 0 | 547.1167 | 547.1167 | 0.00096712 | 0.00096712 | 0 | 0 | 0
ZN10994:PA10 | MORTDALE | URBAN | 1095 | 4882.6286 | 3269.8656 | 2.8197 | 480.9168 | 0 | 3 | 34587.45 | 34587.45 | 0.042009 | 0.042009 | 0 | 0 | 0
ZN10994:PA11 | MORTDALE | URBAN | 731 | 4349.8497 | 1280.1936 | 2.3434 | 274.6763 | 0 | 9 | 23769.85 | 23769.85 | 0.22572 | 0.22572 | 0 | 0 | 0
ZN10994:PA12 | MORTDALE | URBAN | 2027 | 2434.8803 | 5632.4529 | 3.8104 | 133.4438 | 0 | 6 | 7101.9667 | 7101.9667 | 0.071534 | 0.071534 | 0 | 0 | 0
ZN10994:PA13 | MORTDALE | URBAN | 1059 | 1520.2289 | 3701.0877 | 2.4768 | 1798.2858 | 0 | 6 | 147239.9667 | 147007.8167 | 1.1483 | 1.1473 | 0 | 0 | 0
ZN10994:PA14 | MORTDALE | URBAN | 492 | 1233.2665 | 468.6811 | 1.5051 | 0.49727 | 0 | 0 | 67 | 67 | 0.0020325 | 0.0020325 | 0 | 0 | 0
ZN10994:PA18 | MORTDALE | SHORT RURAL | 1062 | 902.4667 | 2413.6514 | 2.191 | 5.5011 | 0 | 2 | 509.1667 | 509.1667 | 0.0018832 | 0.0018832 | 0 | 0 | 0
ZN10994:PA19 | MORTDALE | URBAN | 893 | 4828.9139 | 3226.7513 | 2.6863 | 155.0658 | 0 | 5 | 11705.9667 | 10654.5167 | 0.077268 | 0.076148 | 0 | 0 | 0
ZN10994:PA2 | MORTDALE | URBAN | 2268 | 1486.3507 | 4763.0436 | 5.5441 | 5991.2277 | 0 | 3 | 219145.8167 | 219145.8167 | 1.0009 | 1.0009 | 0 | 0 | 0
ZN10994:PA20 | MORTDALE | URBAN | 2287 | 1038.9242 | 2615.2365 | 2.8006 | 2904.5152 | 0 | 6 | 210313.2667 | 210313.2667 | 1.1207 | 1.1207 | 0 | 0 | 0
ZN10994:PA21 | MORTDALE | URBAN | 1046 | 4125.5686 | 1195.816 | 2.8006 | 3770.8161 | 0 | 11 | 273041.3167 | 120198.0667 | 2.1702 | 1.1415 | 0 | 0 | 0
ZN10994:PA3 | MORTDALE | URBAN | 1068 | 2179.7067 | 2062.9602 | 2.2862 | 2.5101 | 0 | 0 | 222.65 | 0 | 0.00093633 | 0 | 0 | 0 | 0
ZN10994:PA4 | MORTDALE | URBAN | 1682 | 4033.8275 | 2505.9097 | 3.4103 | 13869.126 | 0 | 10 | 824719.7833 | 824452.3333 | 3.7444 | 3.7438 | 0 | 0 | 0
ZN10994:PA7 | MORTDALE | URBAN | 1870 | 4545.5002 | 4660.6715 | 4.8964 | 918.4588 | 0 | 6 | 38039.6833 | 37802.3167 | 0.1369 | 0.13636 | 0 | 0 | 0
ZN10994:PA8 | MORTDALE | URBAN | 359 | 1363.3147 | 1171.9621 | 2.0195 | 84.4608 | 0 | 4 | 8481.25 | 8481.25 | 0.31198 | 0.31198 | 0 | 0 | 0
ZN10994:PA9 | MORTDALE | URBAN | 1191 | 928.4009 | 1800.8571 | 2.1529 | 68.983 | 0 | 2 | 6497.9167 | 6497.9167 | 0.058774 | 0.058774 | 0 | 0 | 0
ZN10995:PA1 | RIVERWOOD | URBAN | 2049 | 5162.3043 | 1372.6084 | 4.0009 | 3476.0187 | 0 | 6 | 176186.7167 | 81183.0833 | 1.1425 | 1.061 | 0 | 0 | 0
ZN10995:PA12 | RIVERWOOD | URBAN | 1287 | 3819.4257 | 1632.2278 | 3.0483 | 86.9599 | 0 | 6 | 5785.0833 | 5785.0833 | 0.004662 | 0.004662 | 0 | 0 | 0
ZN10995:PA13 | RIVERWOOD | URBAN | 1279 | 4387.4793 | 1388.7787 | 3.3341 | 268.8484 | 0 | 4 | 16352.3333 | 971.9333 | 0.035184 | 0.0023456 | 0 | 0 | 0
ZN10995:PA2 | RIVERWOOD | URBAN | 2324 | 4384.6168 | 3348.4335 | 4.0962 | 6991.5266 | 0 | 12 | 346133.7167 | 345220.55 | 1.102 | 1.096 | 0 | 0 | 0
ZN10995:PA5 | RIVERWOOD | URBAN | 1420 | 1543.8867 | 2015.3364 | 3.3341 | 1.6235 | 0 | 0 | 98.75 | 98.75 | 0.00070423 | 0.00070423 | 0 | 0 | 0
ZN10995:PA6 | RIVERWOOD | URBAN | 1218 | 2807.5323 | 2029.9284 | 2.7625 | 114.6345 | 0 | 7 | 8415.0667 | 8415.0667 | 0.086207 | 0.086207 | 0 | 0 | 0
ZN10995:PA7 | RIVERWOOD | URBAN | 2107 | 5551.9738 | 1428.4732 | 3.8104 | 3580.9979 | 0 | 4 | 190583.1167 | 1313.1167 | 0.99953 | 0.0014238 | 0 | 0 | 0
ZN10995:PA8 | RIVERWOOD | URBAN | 696 | 1907.1548 | 2227.2542 | 4.1914 | 2087.5809 | 0 | 4 | 101002.2333 | 100986.8167 | 1.0057 | 1.0043 | 0 | 0 | 0
ZN10996:PA10 | ROCKDALE | URBAN | 879 | 2985.824 | 2455.8496 | 2.4196 | 1072.3329 | 0 | 4 | 89874.45 | 89874.45 | 1.0046 | 1.0046 | 0 | 0 | 0
ZN10996:PA11 | ROCKDALE | URBAN | 647 | 525.4406 | 1309.9862 | 1.0098 | 51.2732 | 0 | 3 | 10297.3333 | 7070.6667 | 0.23493 | 0.14992 | 0 | 0 | 0
ZN10996:PA14 | ROCKDALE | URBAN | 491 | 118.3689 | 1057.3952 | 1.2765 | 60.2329 | 0 | 2 | 9569.0667 | 8289 | 0.11202 | 0.10998 | 0 | 0 | 0
ZN10996:PA19 | ROCKDALE | URBAN | 691 | 1638.6263 | 1152.7747 | 1.2765 | 233.9743 | 0 | 4 | 37170.95 | 37170.95 | 1.1143 | 1.1143 | 0 | 0 | 0
ZN10996:PA20 | ROCKDALE | URBAN | 279 | 1371.6677 | 654.3539 | 1.0669 | 228.3779 | 0 | 6 | 43408.6667 | 43408.6667 | 2.4767 | 2.4767 | 0 | 0 | 0
ZN10996:PA21 | ROCKDALE | URBAN | 79 | 954.7187 | 1267.3894 | 1.3908 | 1.9546 | 0 | 1 | 285 | 285 | 0.063291 | 0.063291 | 0 | 0 | 0
ZN10996:PA8 | ROCKDALE | URBAN | 1200 | 1149.1108 | 1591.8174 | 4.4772 | 14.0338 | 0 | 4 | 635.65 | 635.65 | 0.0033333 | 0.0033333 | 0 | 0 | 0
ZN10996:PA9 | ROCKDALE | URBAN | 1223 | 2464.2055 | 2421.4363 | 5.6394 | 1293.1001 | 0 | 2 | 46499.7667 | 46499.7667 | 0.07686 | 0.07686 | 0 | 0 | 0
ZN10997:PA1 | SANS SOUCI | URBAN | 1125 | 2306.0269 | 2102.4828 | 2.3053 | 2.5009 | 0 | 1 | 220 | 220 | 0.0017778 | 0.0017778 | 0 | 0 | 0
ZN10997:PA12 | SANS SOUCI | URBAN | 1387 | 2396.8437 | 2713.0712 | 3.1055 | 443.9747 | 0 | 5 | 28992.1833 | 884.5833 | 0.070656 | 0.001442 | 0 | 0 | 0
ZN10997:PA2 | SANS SOUCI | URBAN | 2311 | 834.684 | 5724.2236 | 4.0771 | 160.2078 | 0 | 3 | 7968.5667 | 1236.5667 | 0.048464 | 0.019905 | 0 | 0 | 0
ZN10997:PA5 | SANS SOUCI | URBAN | 799 | 1257.4692 | 1499.3647 | 1.8861 | 168.5115 | 0 | 2 | 18117.7667 | 186.0833 | 0.10013 | 0.0012516 | 0 | 0 | 0
ZN10997:PA7 | SANS SOUCI | URBAN | 1018 | 951.6546 | 3628.8626 | 2.3053 | 113.3948 | 0 | 1 | 9975.1167 | 9975.1167 | 0.089391 | 0.089391 | 0 | 0 | 0
ZN10997:PA8 | SANS SOUCI | URBAN | 279 | 948.843 | 505.7922 | 0.5144 | 7.3383 | 0 | 2 | 2892.95 | 2892.95 | 0.12903 | 0.12903 | 0 | 0 | 0
ZN10999:PA1 | KOGARAH | URBAN | 225 | 0 | 1500.049 | 0.53346 | 127.6033 | 0 | 4 | 48508.1 | 48508.1 | 1.0533 | 1.0533 | 0 | 0 | 0
ZN10999:PA10 | KOGARAH | URBAN | 1874 | 7763.6582 | 645.3766 | 3.7532 | 1814.2125 | 8.8838 | 12 | 98023.9667 | 98023.9667 | 0.52401 | 0.52401 | 1 | 480 | 0.0010672
ZN10999:PA11 | KOGARAH | URBAN | 2235 | 1088.2566 | 3593.9434 | 3.3913 | 334.6608 | 0 | 7 | 20012.2167 | 20012.2167 | 0.039821 | 0.039821 | 0 | 0 | 0
ZN10999:PA12 | KOGARAH | URBAN | 2635 | 3715.2172 | 2817.5037 | 4.2676 | 1662.4958 | 1312.5426 | 8 | 78999.2333 | 77793.85 | 1.0345 | 1.0342 | 3 | 62370 | 0.058444
ZN10999:PA15 | KOGARAH | URBAN | 1533 | 3653.7039 | 1464.3929 | 3.1436 | 520.1054 | 0 | 3 | 33551.95 | 7521.0167 | 0.075016 | 0.033268 | 0 | 0 | 0
ZN10999:PA16 | KOGARAH | URBAN | 1396 | 3531.4597 | 1522.0598 | 4.382 | 942.4428 | 0 | 6 | 43615.1667 | 14029.1667 | 0.17192 | 0.10458 | 0 | 0 | 0
ZN10999:PA17 | KOGARAH | URBAN | 1535 | 3762.5372 | 1549.1574 | 4.1343 | 3506.0256 | 1306.3871 | 8 | 171975.15 | 171975.15 | 1.2267 | 1.2267 | 2 | 64080 | 0.11596
ZN10999:PA19 | KOGARAH | URBAN | 1771 | 737.4017 | 3732.9813 | 4.6677 | 15.5877 | 789.9562 | 0 | 677.2167 | 677.2167 | 0.00056465 | 0.00056465 | 1 | 34320 | 0.014681
ZN10999:PA22 | KOGARAH | URBAN | 2141 | 4591.5186 | 1585.6624 | 4.2105 | 214.5719 | 0 | 4 | 10334.5333 | 10334.5333 | 0.040635 | 0.040635 | 0 | 0 | 0
ZN10999:PA24 | KOGARAH | URBAN | 2393 | 3003.186 | 2813.0613 | 3.8866 | 3577.9856 | 0 | 17 | 186689.0167 | 186689.0167 | 1.1015 | 1.1015 | 0 | 0 | 0
ZN10999:PA25 | KOGARAH | URBAN | 1038 | 355.669 | 3535.9805 | 4.2295 | 8.4212 | 0 | 2 | 403.7667 | 403.7667 | 0.0019268 | 0.0019268 | 0 | 0 | 0
ZN10999:PA28 | KOGARAH | URBAN | 468 | 0 | 1423.9406 | 3.2579 | 39.1227 | 0 | 1 | 2435.25 | 2435.25 | 0.032051 | 0.032051 | 0 | 0 | 0
ZN10999:PA29 | KOGARAH | URBAN | 2280 | 1541.2328 | 3742.7503 | 3.3913 | 3.8014 | 150.5054 | 0 | 227.3167 | 227.3167 | 0.0004386 | 0.0004386 | 1 | 9000 | 0.032895
ZN10999:PA3 | KOGARAH | URBAN | 194 | 0 | 2690.3584 | 3.7532 | 586.0528 | 0 | 2 | 31665.1 | 31665.1 | 1.8866 | 1.8866 | 0 | 0 | 0
ZN10999:PA32 | KOGARAH | URBAN | 1534 | 4084.4884 | 1637.7571 | 3.4484 | 740.9009 | 0 | 6 | 43570.4333 | 43570.4333 | 0.12907 | 0.12907 | 0 | 0 | 0
ZN10999:PA36 | KOGARAH | URBAN | 2321 | 1066.9812 | 3107.895 | 3.9628 | 98.1327 | 328.8797 | 2 | 5021.8167 | 5021.8167 | 0.024558 | 0.024558 | 1 | 16830 | 0.021973
ZN10999:PA38 | KOGARAH | URBAN | 1994 | 2899.8041 | 5638.7667 | 3.7723 | 167.1591 | 0 | 2 | 8986.1833 | 8986.1833 | 0.0667 | 0.0667 | 0 | 0 | 0
ZN10999:PA39 | KOGARAH | URBAN | 670 | 1123.7498 | 4100.8864 | 4.1914 | 1.7778 | 0 | 0 | 86.0167 | 86.0167 | 0.0014925 | 0.0014925 | 0 | 0 | 0
ZN10999:PA4 | KOGARAH | URBAN | 1673 | 4873.4868 | 2274.3625 | 4.9535 | 3314.9646 | 0 | 8 | 135711.2667 | 135711.2667 | 1.1172 | 1.1172 | 0 | 0 | 0
ZN10999:PA7 | KOGARAH | URBAN | 981 | 2811.4631 | 1348.2286 | 4.0581 | 7.0405 | 0 | 2 | 351.8333 | 122 | 0.0030581 | 0.0020387 | 0 | 0 | 0
ZN116:PA30 | LEICHHARDT | URBAN | 900 | 0 | 2477.2082 | 1.6194 | 32.3378 | 0 | 2 | 4049.5 | 4049.5 | 0.072222 | 0.072222 | 0 | 0 | 0
ZN116:PA32 | LEICHHARDT | URBAN | 1722 | 0 | 4036.7535 | 2.191 | 1057.2201 | 0 | 4 | 97853.85 | 97853.85 | 0.090012 | 0.090012 | 0 | 0 | 0
ZN116:PA33 | LEICHHARDT | URBAN | 1527 | 0 | 7827.1399 | 2.3815 | 104.042 | 0 | 4 | 8859.5 | 8859.5 | 0.045187 | 0.045187 | 0 | 0 | 0
ZN116:PA34 | LEICHHARDT | URBAN | 1369 | 1.8999 | 2312.112 | 1.8099 | 1183.6859 | 2178.4392 | 5 | 132624.3333 | 132258.95 | 1.0029 | 1.0022 | 2 | 244080 | 0.33017
ZN116:PA35 | LEICHHARDT | URBAN | 972 | 0 | 6078.7901 | 2.2862 | 147.4354 | 48.7029 | 6 | 13077.6833 | 13077.6833 | 0.21605 | 0.21605 | 1 | 4320 | 0.0082305
ZN116:PA36 | LEICHHARDT | URBAN | 1424 | 0 | 3690.5323 | 2.0957 | 185.375 | 0 | 4 | 17937.7833 | 17937.7833 | 0.066011 | 0.066011 | 0 | 0 | 0
ZN116:PA41 | LEICHHARDT | URBAN | 674 | 0 | 845.3129 | 3.3341 | 88.8643 | 248.5876 | 2 | 5405.05 | 5405.05 | 0.0727 | 0.0727 | 1 | 15120 | 0.053412
ZN116:PA42 | LEICHHARDT | URBAN | 888 | 0 | 2741.6739 | 2.4768 | 1101.5612 | 0 | 11 | 90193.5833 | 59709.1667 | 0.4786 | 0.31081 | 0 | 0 | 0
ZN116:PA44 | LEICHHARDT | URBAN | 1319 | 614.1945 | 9780.7069 | 2.8578 | 10.0753 | 0.84554 | 3 | 714.95 | 714.95 | 0.0022745 | 0.0022745 | 0 | 60 | 0.00075815
ZN116:PA45 | LEICHHARDT | URBAN | 63 | 193.559 | 9326.2317 | 2.572 | 123.964 | 132.411 | 2 | 9774 | 9774 | 1.1746 | 1.1746 | 2 | 10440 | 0.33333
ZN116:PA47 | LEICHHARDT | URBAN | 1348 | 0 | 5008.9277 | 2.2862 | 1697.0505 | 0 | 8 | 150530.2833 | 150530.2833 | 1.1269 | 1.1269 | 0 | 0 | 0
ZN116:PA48 | LEICHHARDT | URBAN | 1224 | 0 | 4845.0217 | 1.4289 | 48.1582 | 446.8658 | 3 | 6834.7 | 6834.7 | 0.044935 | 0.044935 | 4 | 63420 | 0.12337
ZN116:PA49 | LEICHHARDT | URBAN | 898 | 0 | 3941.3719 | 2.0005 | 86.0554 | 0 | 1 | 8723.6667 | 8723.6667 | 0.10802 | 0.10802 | 0 | 0 | 0
ZN116:PA50 | LEICHHARDT | URBAN | 1725 | 0 | 8437.8639 | 2.572 | 222.6861 | 0 | 11 | 17557.7833 | 17557.7833 | 1.0388 | 1.0388 | 0 | 0 | 0
ZN1164:PA10 | ROSE BAY | URBAN | 661 | 0 | 8046.5116 | 2.7625 | 567.7197 | 0 | 4 | 41675.0667 | 41675.0667 | 0.12405 | 0.12405 | 0 | 0 | 0
ZN1164:PA11 | ROSE BAY | URBAN | 131 | 0 | 4042.7381 | 5.3346 | 15.3826 | 0 | 3 | 584.7667 | 584.7667 | 0.022901 | 0.022901 | 0 | 0 | 0
ZN1164:PA12 | ROSE BAY | URBAN | 784 | 0 | 2620.1019 | 3.0483 | 1678.2997 | 0 | 6 | 111650.3 | 111650.3 | 1.9554 | 1.9554 | 0 | 0 | 0
ZN1164:PA13 | ROSE BAY | URBAN | 1010 | 0 | 3724.2101 | 2.8578 | 694.7613 | 0 | 7 | 49300.8833 | 33613.5333 | 0.36931 | 0.32079 | 0 | 0 | 0
ZN1164:PA15 | ROSE BAY | URBAN | 868 | 0 | 3337.0497 | 2.2862 | 49.2017 | 0 | 13 | 4364.25 | 4272.15 | 0.024194 | 0.023041 | 0 | 0 | 0
ZN1164:PA20 | ROSE BAY | URBAN | 2173 | 0 | 5207.1927 | 4.8583 | 3570.7447 | 0 | 8 | 149048.9667 | 149048.9667 | 0.15969 | 0.15969 | 0 | 0 | 0
ZN1164:PA21 | ROSE BAY | URBAN | 1237 | 0 | 6212.799 | 4.2867 | 1009.6247 | 326.5883 | 7 | 47762.5833 | 46956.9833 | 0.13905 | 0.13743 | 1 | 15450 | 0.083266
ZN1164:PA22 | ROSE BAY | URBAN | 799 | 0 | 1095.7147 | 2.191 | 62.9013 | 0 | 1 | 5822 | 5822 | 0.088861 | 0.088861 | 0 | 0 | 0
ZN1164:PA23 | ROSE BAY | URBAN | 473 | 0 | 6759.978 | 3.5246 | 74.5871 | 0 | 6 | 4291.4333 | 3676.3667 | 0.033827 | 0.031712 | 0 | 0 | 0
ZN1164:PA26 | ROSE BAY | URBAN | 741 | 0 | 4390.8265 | 2.2862 | 891.8649 | 0 | 9 | 79109.4167 | 79109.4167 | 0.36572 | 0.36572 | 0 | 0 | 0
ZN1164:PA27 | ROSE BAY | URBAN | 1286 | 0 | 6061.9669 | 3.9057 | 1513.2622 | 0 | 10 | 78572.5167 | 78572.5167 | 0.28694 | 0.28694 | 0 | 0 | 0
ZN1164:PA28 | ROSE BAY | URBAN | 872 | 0 | 4172.7043 | 2.572 | 14.2475 | 0 | 0 | 1123.35 | 1123.35 | 0.0011468 | 0.0011468 | 0 | 0 | 0
ZN1164:PA3 | ROSE BAY | URBAN | 785 | 0 | 2843.4966 | 1.9052 | 402.5463 | 1018.0255 | 7 | 42847.5667 | 42847.5667 | 0.48408 | 0.48408 | 2 | 108360 | 0.32866
ZN1164:PA4 | ROSE BAY | URBAN | 1217 | 0 | 9141.1701 | 3.5246 | 597.6994 | 0 | 9 | 34389.15 | 34389.15 | 0.20214 | 0.20214 | 0 | 0 | 0
ZN1164:PA8 | ROSE BAY | URBAN | 655 | 0 | 3647.7984 | 1.8099 | 58.8377 | 0 | 4 | 6592.3833 | 6592.3833 | 0.1374 | 0.1374 | 0 | 0 | 0
ZN1164:PA9 | ROSE BAY | URBAN | 897 | 0 | 6022.9375 | 3.7151 | 279.164 | 2.748 | 7 | 15238.25 | 14999.0833 | 0.10479 | 0.10368 | 0 | 150 | 0.0011148
ZN1193:PA12 | LINDFIELD | URBAN | 1348 | 7123.7635 | 2537.0811 | 5.1821 | 622.6811 | 0 | 14 | 24367.2833 | 24367.2833 | 0.09273 | 0.09273 | 0 | 0 | 0
ZN1193:PA15 | LINDFIELD | URBAN | 1038 | 333.0595 | 7419.2549 | 2.4196 | 2940.1061 | 120.2691 | 19 | 246416.4167 | 246416.4167 | 2.4884 | 2.4884 | 1 | 10080 | 0.023121
ZN1193:PA16 | LINDFIELD | URBAN | 1278 | 6887.5906 | 1746.7975 | 3.8295 | 132.2563 | 0 | 7 | 7003.75 | 2118.15 | 0.042254 | 0.0046948 | 0 | 0 | 0
ZN1193:PA17 | LINDFIELD | URBAN | 391 | 1270.7777 | 1940.3079 | 1.3717 | 85.6832 | 8.523 | 1 | 12667 | 12667 | 0.13555 | 0.13555 | 1 | 1260 | 0.0076726
ZN1193:PA21 | LINDFIELD | URBAN | 949 | 3476.9082 | 1635.6423 | 2.5339 | 1131.9235 | 0 | 10 | 90589.0667 | 85146 | 1.1064 | 1.059 | 0 | 0 | 0
ZN1193:PA25 | LINDFIELD | URBAN | 560 | 1189.7421 | 2260.5667 | 1.6956 | 239.609 | 0 | 6 | 28656.5167 | 28656.5167 | 0.26964 | 0.26964 | 0 | 0 | 0
ZN1193:PA26 | LINDFIELD | URBAN | 1293 | 598.0632 | 6462.4826 | 3.0674 | 4238.661 | 575.8355 | 10 | 280229.05 | 280229.05 | 2.5104 | 2.5104 | 2 | 38070 | 0.067285
ZN1193:PA27 | LINDFIELD | URBAN | 681 | 3563.3719 | 1470.7416 | 2.4006 | 245.09 | 0 | 5 | 20704.5333 | 16849.8667 | 0.076358 | 0.04699 | 0 | 0 | 0
ZN1193:PA28 | LINDFIELD | URBAN | 2690 | 8910.6313 | 7727.4284 | 9.0306 | 22271.03 | 0 | 22 | 500117.8 | 499967.8 | 1.477 | 1.4762 | 0 | 0 | 0
ZN12570:PA24 | AVOCA | SHORT RURAL | 1733 | 12930.1459 | 3902.8819 | 3.8104 | 5002.4597 | 13878.066 | 26 | 266234.2667 | 99075.6 | 2.4599 | 0.47028 | 12 | 738600 | 0.91229
ZN12570:PA25 | AVOCA | SHORT RURAL | 1037 | 3769.4878 | 3226.613 | 1.9052 | 553.3661 | 2358.4821 | 10 | 58901.0333 | 58901.0333 | 1.0752 | 1.0752 | 1 | 251040 | 0.50434
ZN12570:PA26 | AVOCA | URBAN | 413 | 1157.2573 | 6437.0637 | 2.553 | 4.1544 | 2581.0159 | 1 | 330 | 330 | 0.026634 | 0.026634 | 7 | 205020 | 0.58596
ZN12570:PA33 | AVOCA | SHORT RURAL | 1577 | 16198.5807 | 3382.6836 | 5.0488 | 4560.4956 | 10534.8867 | 24 | 183179.35 | 93753.95 | 1.6075 | 1.0996 | 27 | 423150 | 0.6487
ZN12570:PA35 | AVOCA | URBAN | 1019 | 4040.815 | 5571.5957 | 4.0581 | 2298.8931 | 4881.8887 | 13 | 114881.35 | 113476.7 | 1.6094 | 1.6084 | 6 | 243960 | 0.58979
ZN12570:PA39 | AVOCA | URBAN | 1673 | 4541.5639 | 6042.8441 | 4.1152 | 274.8283 | 657.4889 | 10 | 13543.1 | 13543.1 | 0.053198 | 0.053198 | 1 | 32400 | 0.090257
ZN12570:PA40 | AVOCA | SHORT RURAL | 1163 | 7539.3629 | 4940.2689 | 3.315 | 3271.1739 | 1760.5753 | 11 | 200108.1333 | 116665.1333 | 2.7446 | 2.0292 | 3 | 107700 | 0.23646
ZN12570:PA41 | AVOCA | URBAN | 775 | 3112.6786 | 3542.4224 | 2.0005 | 1081.1606 | 1312.7794 | 18 | 109600.1833 | 109493.9667 | 1.6684 | 1.6671 | 6 | 133080 | 0.40903
ZN12580:PA1 | ERINA | URBAN | 1241 | 4323.7485 | 4402.0902 | 7.3541 | 3432.8332 | 2119.2742 | 9 | 94662.0167 | 91757.5167 | 1.004 | 1.0032 | 4 | 58440 | 0.097502
ZN12580:PA10 | ERINA | URBAN | 1496 | 1789.4327 | 7371.8766 | 4.7249 | 15379.9065 | 782.8537 | 8 | 660104 | 660104 | 4.994 | 4.994 | 1 | 33600 | 0.046791
ZN12580:PA12 | ERINA | SHORT RURAL | 320 | 3889.8276 | 2181.609 | 1.2765 | 11.1621 | 108.7698 | 9 | 1773.3 | 1571.8333 | 0.028125 | 0.025 | 2 | 17280 | 0.1125
ZN12580:PA16 | ERINA | URBAN | 1247 | 8229.6421 | 5017.1709 | 5.5632 | 3916.5345 | 3813.7286 | 15 | 142767.5333 | 142531.6333 | 2.0401 | 2.0393 | 9 | 139020 | 0.23496
ZN12580:PA2 | ERINA | URBAN | 382 | 0 | 3564.8818 | 4.1914 | 5.5805 | 583.7863 | 1 | 270 | 270 | 0.0052356 | 0.0052356 | 2 | 28245 | 0.7356
ZN12580:PA4 | ERINA | URBAN | 1636 | 9432.3972 | 4692.3658 | 4.5915 | 3416.2824 | 4635.1838 | 10 | 150885.35 | 150885.35 | 1.5312 | 1.5312 | 8 | 204720 | 0.25428
ZN12580:PA7 | ERINA | URBAN | 171 | 804.5895 | 4709.618 | 5.2393 | 482.1998 | 0 | 2 | 18664 | 18664 | 1.0351 | 1.0351 | 0 | 0 | 0
ZN12580:PA8 | ERINA | URBAN | 291 | 1.3466 | 2709.9616 | 4.0581 | 1.2407 | 0 | 0 | 62 | 62 | 0.0034364 | 0.0034364 | 0 | 0 | 0
ZN12600:PA1 | LISAROW | SHORT RURAL | 617 | 5436.619 | 2606.0304 | 2.1719 | 3040.9143 | 344.4376 | 12 | 283928.95 | 283928.95 | 6.4263 | 6.4263 | 3 | 32160 | 0.11021
ZN12600:PA11 | LISAROW | URBAN | 929 | 4294.9075 | 3186.6176 | 2.553 | 451.8106 | 6390.6014 | 8 | 35889.05 | 35889.05 | 1.0657 | 1.0657 | 16 | 507630 | 1.2034
ZN12600:PA12 | LISAROW | URBAN | 312 | 845.7194 | 3298.9738 | 3.315 | 168.6033 | 0 | 5 | 10314 | 10314 | 1.1282 | 1.1282 | 0 | 0 | 0
ZN12600:PA13 | LISAROW | SHORT RURAL | 848 | 13551.3922 | 4232.5591 | 4.2295 | 5769.0868 | 3008.4805 | 19 | 276607.8167 | 276607.8167 | 4.0542 | 4.0542 | 26 | 144246.2667 | 0.70283
ZN12600:PA2 | LISAROW | SHORT RURAL | 773 | 27321.989 | 3278.6636 | 3.2579 | 2296.4145 | 2960.2496 | 19 | 142943.5333 | 127660.5167 | 2.7245 | 2.6429 | 25 | 184264.8833 | 0.39198
ZN12600:PA3 | LISAROW | URBAN | 1394 | 6520.1754 | 3323.3365 | 3.5437 | 1975.794 | 1978.9773 | 8 | 113067.8333 | 113067.8333 | 2.1076 | 2.1076 | 8 | 113250 | 0.17001
ZN12600:PA5 | LISAROW | URBAN | 75 | 1490.2321 | 1932.5782 | 2.7816 | 89.2257 | 190.9333 | 2 | 6505 | 6505 | 2 | 2 | 1 | 13920 | 0.38667
ZN12600:PA9 | LISAROW | SHORT RURAL | 1681 | 11078.4043 | 2519.3904 | 4.4582 | 8189.4605 | 1879.6268 | 10 | 372520.1667 | 372520.1667 | 2.0357 | 2.0357 | 7 | 85500 | 0.1166
ZN12610:PA10 | LONG JETTY | SHORT RURAL | 1840 | 6639.3599 | 8136.6299 | 5.487 | 10947.7476 | 2642.9429 | 19 | 404615.6167 | 404615.6167 | 4.0462 | 4.0462 | 6 | 97680 | 0.11739
ZN12610:PA11 | LONG JETTY | URBAN | 2372 | 10749.5852 | 3146.8479 | 5.2965 | 205.4325 | 1391.5495 | 13 | 7865.65 | 6505.3333 | 0.024452 | 0.023609 | 1 | 53280 | 0.046796
ZN12610:PA13 | LONG JETTY | URBAN | 1950 | 1921.4673 | 7176.1731 | 4.1343 | 5554.3895 | 0 | 16 | 272450.0833 | 272450.0833 | 2.4154 | 2.4154 | 0 | 0 | 0
ZN12610:PA16 | LONG JETTY | URBAN | 1365 | 4365.1773 | 406.8944 | 2.3053 | 797.4467 | 0 | 8 | 70149.8333 | 70149.8333 | 0.17949 | 0.17949 | 0 | 0 | 0
ZN12610:PA17 | LONG JETTY | URBAN | 1191 | 4970.2861 | 1472.9576 | 5.125 | 6452.6205 | 373.0167 | 4 | 255325.5 | 255325.5 | 2.0445 | 2.0445 | 1 | 14760 | 0.034425
ZN12610:PA18 | LONG JETTY | URBAN | 1104 | 6144.1274 | 4116.989 | 4.0771 | 8014.5429 | 2168.9241 | 18 | 398634.9167 | 398634.9167 | 2.7536 | 2.7536 | 7 | 107880 | 0.22917
ZN12610:PA2 | LONG JETTY | URBAN | 1530 | 6139.6535 | 890.9008 | 3.8866 | 2734.8636 | 0 | 18 | 142697.3333 | 142697.3333 | 1.1771 | 1.1771 | 0 | 0 | 0
ZN12610:PA20 | LONG JETTY | SHORT RURAL | 926 | 9199.3639 | 4652.3082 | 3.3722 | 287.5014 | 3818.3227 | 4 | 17289.2833 | 557.2833 | 0.24622 | 0.0064795 | 11 | 229620 | 0.54536
ZN12610:PA22 | LONG JETTY | URBAN | 2166 | 7540.9301 | 697.7488 | 4.3629 | 11778.6579 | 5431.9043 | 27 | 547483.05 | 547483.05 | 2.7207 | 2.7207 | 6 | 252480 | 0.24284
ZN12610:PA24 | LONG JETTY | SHORT RURAL | 1187 | 5923.2455 | 2783.0433 | 3.677 | 2069.4975 | 4025.3156 | 5 | 114134.7667 | 114134.7667 | 1.0042 | 1.0042 | 5 | 222000 | 0.40185
ZN12610:PA25 | LONG JETTY | SHORT RURAL | 747 | 7261.4627 | 1577.8493 | 3.6961 | 4961.1669 | 0 | 10 | 272202.7167 | 272202.7167 | 3.253 | 3.253 | 0 | 0 | 0
ZN12610:PA5 | LONG JETTY | URBAN | 256 | 2619.4109 | 1520.7656 | 3.658 | 4.6178 | 0 | 1 | 256 | 256 | 0.015625 | 0.015625 | 0 | 0 | 0
ZN12610:PA6 | LONG JETTY | URBAN | 1685 | 5003.6128 | 760.5843 | 4.9916 | 334.6735 | 212.6692 | 13 | 13596.6 | 13596.6 | 0.086053 | 0.086053 | 3 | 8640 | 0.010682
ZN12610:PA7 | LONG JETTY | URBAN | 798 | 3729.6558 | 190.9242 | 1.7147 | 55.2552 | 36.5272 | 6 | 6534.9333 | 6534.9333 | 0.057644 | 0.057644 | 3 | 4320 | 0.011278
ZN12610:PA9 | LONG JETTY | SHORT RURAL | 1159 | 1163.8779 | 7655.6577 | 4.2676 | 5613.9589 | 522.7442 | 16 | 266766.6667 | 134390.6667 | 2.2312 | 1.233 | 4 | 24840 | 0.27092
ZN12620:PA1 | NORAVILLE | SHORT RURAL | 2678 | 17034.1943 | 13302.203 | 5.7728 | 14148.9643 | 847.1595 | 14 | 497041.1833 | 380396.1833 | 2.1848 | 1.5232 | 1 | 29760 | 0.023152
ZN12620:PA10 | NORAVILLE | SHORT RURAL | 1071 | 5692.0559 | 5300.3032 | 2.8578 | 4571.2282 | 333.1412 | 8 | 324378.45 | 222146.45 | 4.1942 | 3.6097 | 2 | 23640 | 0.1606
ZN12620:PA11 | NORAVILLE | SHORT RURAL | 1631 | 16050.2973 | 3535.211 | 4.0771 | 3167.0467 | 19.9039 | 19 | 157525.5667 | 157287.0833 | 1.6199 | 1.6193 | 1 | 990 | 0.0018394
ZN12620:PA13 | NORAVILLE | SHORT RURAL | 408 | 1219.8812 | 4089.5917 | 1.3717 | 102.0337 | 474.0414 | 9 | 15084.1667 | 15084.1667 | 1.2598 | 1.2598 | 3 | 70080 | 2.8627
ZN12620:PA2 | NORAVILLE | SHORT RURAL | 505 | 5566.4754 | 416.8512 | 1.1431 | 31.859 | 11.3302 | 5 | 5651.85 | 5651.85 | 0.1604 | 0.1604 | 3 | 2010 | 0.071287
ZN12620:PA3 | NORAVILLE | URBAN | 1023 | 4587.9216 | 426.3936 | 2.7816 | 1478.1099 | 0 | 13 | 107761.65 | 107360.3333 | 1.045 | 1.043 | 0 | 0 | 0
ZN12620:PA7 | NORAVILLE | URBAN | 2123 | 6021.3775 | 3403.3121 | 5.0297 | 580.3723 | 1.4881 | 10 | 23399.85 | 23399.85 | 0.090909 | 0.090909 | 1 | 60 | 0.00094206
ZN12620:PA8 | NORAVILLE | SHORT RURAL | 1236 | 7500.8008 | 4446.5879 | 3.3532 | 4552.0514 | 23.8103 | 11 | 275299.1333 | 231399.1333 | 2.7646 | 2.0542 | 1 | 1440 | 0.013754
ZN12630:PA1 | PEATS RIDGE | SHORT RURAL | 463 | 70158.5232 | 13125.6504 | 2.2291 | 6783.7787 | 7710.262 | 41 | 617157.7167 | 203688.5333 | 8.108 | 6.6739 | 53 | 701445 | 3.1944
ZN12630:PA2 | PEATS RIDGE | SHORT RURAL | 565 | 73333.239 | 1145.5838 | 1.3336 | 2136.6727 | 4768.5418 | 21 | 324900.45 | 305432.45 | 3.731 | 3.6372 | 44 | 725100 | 7.3965
ZN12630:PA3 | PEATS RIDGE | SHORT RURAL | 419 | 56962.4037 | 462.3784 | 3.3722 | 12964.1359 | 2382.5855 | 24 | 779615.85 | 70574.6667 | 3.1527 | 1.5609 | 33 | 143280 | 0.7494
ZN12630:PA4 | PEATS RIDGE | SHORT RURAL | 272 | 28155.9727 | 19.5534 | 2.0957 | 3984.6545 | 1803.2889 | 16 | 385574.5333 | 29141.5 | 3.2757 | 1.2096 | 28 | 174495 | 1.3162
ZN12630:PA5 | PEATS RIDGE | SHORT RURAL | 287 | 33644.689 | 5883.3082 | 1.2955 | 2134.6961 | 928.9511 | 11 | 334146.95 | 72754.95 | 3.1777 | 2.2927 | 19 | 145410 | 1.1359
ZN12640:PA1 | UMINA | SHORT RURAL | 614 | 5819.6889 | 2203.8105 | 1.1812 | 0 | 734.9738 | 0 | 0 | 0 | 0 | 0 | 6 | 126180 | 0.42997
ZN12640:PA10 | UMINA | URBAN | 1636 | 6013.0277 | 1423.3159 | 4.5534 | 733.7803 | 6727.3474 | 9 | 32679.7333 | 32534.0833 | 0.239 | 0.23839 | 3 | 299610 | 0.47372
ZN12640:PA13 | UMINA | SHORT RURAL | 1988 | 18863.0233 | 909.3321 | 4.3058 | 1191.2927 | 23916.9665 | 10 | 56107.4333 | 56107.4333 | 0.067907 | 0.067907 | 13 | 1126439.85 | 0.54779
ZN12640:PA15 | UMINA | URBAN | 1022 | 2362.066 | 1099.1802 | 2.3243 | 142.7923 | 16.5049 | 6 | 12458.2 | 12458.2 | 0.058708 | 0.058708 | 1 | 1440 | 0.0029354
ZN12640:PA16 | UMINA | URBAN | 771 | 2255.0923 | 1186.4855 | 1.829 | 379.0437 | 0 | 8 | 42027 | 42027 | 0.22957 | 0.22957 | 0 | 0 | 0
ZN12640:PA18 | UMINA | SHORT RURAL | 944 | 8013.0984 | 651.7497 | 2.2672 | 282.0714 | 8362.0928 | 7 | 25230.3 | 25112.85 | 0.18114 | 0.18008 | 13 | 747960 | 1.7691
ZN12640:PA19 | UMINA | URBAN | 1859 | 4396.9258 | 3816.7771 | 3.8295 | 2751.938 | 6887.6188 | 7 | 145731.3333 | 106624.35 | 0.87843 | 0.77838 | 4 | 364740 | 0.39376
ZN12640:PA2 | UMINA | URBAN | 1909 | 5349.6889 | 1586.8435 | 2.8578 | 828.5707 | 3958.3773 | 8 | 58796.1167 | 58796.1167 | 0.19068 | 0.19068 | 6 | 280890 | 0.30644
ZN12640:PA6 | UMINA | URBAN | 1180 | 3249.0461 | 2119.4065 | 2.4387 | 314.1017 | 0 | 7 | 26119.85 | 26119.85 | 0.22966 | 0.22966 | 0 | 0 | 0
ZN12640:PA7 | UMINA | URBAN | 1620 | 3225.6465 | 2150.6109 | 2.2481 | 1549.6916 | 468.2692 | 6 | 139789.2 | 139789.2 | 1.1278 | 1.1278 | 1 | 42240 | 0.054321
ZN12640:PA8 | UMINA | SHORT RURAL | 1564 | 6786.843 | 6324.0735 | 2.8769 | 1381.7172 | 2155.1701 | 9 | 97398.5667 | 96630.15 | 0.67263 | 0.67199 | 4 | 151920 | 0.27558
ZN12650:PA1 | WEST GOSFORD | SHORT RURAL | 1695 | 52547.6402 | 2420.0156 | 4.5725 | 11879.4325 | 10155.2269 | 40 | 526859.4833 | 429613.4833 | 2.5204 | 2.4366 | 37 | 450390 | 0.62065
ZN12650:PA10 | WEST GOSFORD | URBAN | 641 | 601.0544 | 3846.2327 | 2.553 | 900.4072 | 19.639 | 2 | 71522.8 | 71522.8 | 1.5569 | 1.5569 | 4 | 1560 | 0.0062402
ZN12650:PA12 | WEST GOSFORD | URBAN | 1973 | 11489.3338 | 3416.2209 | 5.6203 | 2067.3602 | 1599.6979 | 6 | 74594.1 | 74594.1 | 0.64268 | 0.64268 | 3 | 57720 | 0.10137
ZN12650:PA13 | WEST GOSFORD | SHORT RURAL | 1734 | 11141.8352 | 5608.183 | 5.6775 | 23471.1572 | 8236.0516 | 11 | 838356.2167 | 248349.2167 | 3.342 | 2.3443 | 11 | 294180 | 0.36044
ZN12650:PA14 | WEST GOSFORD | URBAN | 465 | 1969.2109 | 4794.1053 | 5.0107 | 827.634 | 249.0611 | 3 | 33496 | 33496 | 1.9957 | 1.9957 | 1 | 10080 | 0.045161
ZN12650:PA17 | WEST GOSFORD | URBAN | 2334 | 8836.0261 | 6677.379 | 7.9447 | 14790.8001 | 244.4614 | 18 | 377542.6 | 377542.6 | 2.0608 | 2.0608 | 2 | 6240 | 0.0089974
ZN12650:PA19 | WEST GOSFORD | SHORT RURAL | 33 | 0 | 1437.903 | 0.28578 | 0.51068 | 0 | 0 | 362.3833 | 362.3833 | 0.030303 | 0.030303 | 0 | 0 | 0
ZN12650:PA20 | WEST GOSFORD | URBAN | 1942 | 4512.6043 | 4870.4545 | 4.0581 | 275.4477 | 12604.1949 | 8 | 13764.8 | 13066.2333 | 0.39444 | 0.39392 | 9 | 629862.65 | 1.1885
ZN12650:PA5 | WEST GOSFORD | URBAN | 371 | 2.0005 | 3099.223 | 5.6013 | 1572.3443 | 0 | 1 | 56926 | 56926 | 0.99191 | 0.99191 | 0 | 0 | 0
ZN12650:PA6 | WEST GOSFORD | URBAN | 1632 | 13420.7872 | 5600.8845 | 8.5353 | 5954.4638 | 3839.7711 | 10 | 141473.4667 | 115793.4667 | 1.1722 | 1.0251 | 13 | 91230 | 0.14583
ZN12650:PA8 | WEST GOSFORD | URBAN | 180 | 451.1197 | 2705.9027 | 1.1812 | 115.3311 | 0 | 2 | 19800 | 19800 | 2 | 2 | 0 | 0 | 0
ZN12650:PA9 | WEST GOSFORD | URBAN | 1192 | 4183.7064 | 5806.4057 | 5.2965 | 451.8266 | 1255.9988 | 8 | 17299.65 | 17113.3167 | 0.14262 | 0.14178 | 3 | 48090 | 0.083893
ZN12660:PA10 | WOY WOY | SHORT RURAL | 1739 | 11729.5382 | 2763.9554 | 4.7249 | 1985.8831 | 2986.7267 | 9 | 85233.9 | 59101.9 | 0.36803 | 0.34043 | 9 | 128190 | 0.18919
ZN12660:PA11 | WOY WOY | URBAN | 698 | 2955.6261 | 1370.6233 | 2.6101 | 222.9195 | 1500.1079 | 1 | 17319.6 | 17319.6 | 0.10315 | 0.10315 | 3 | 116550 | 0.31805
ZN12660:PA13 | WOY WOY | URBAN | 606 | 792.6561 | 1099.851 | 3.296 | 23.502 | 0 | 1 | 1446 | 1446 | 0.009901 | 0.009901 | 0 | 0 | 0
ZN12660:PA14 | WOY WOY | SHORT RURAL | 3684 | 14833.9258 | 5193.9242 | 3.2388 | 10289.7789 | 7142.4972 | 27 | 644269.35 | 643915.2 | 1.336 | 1.3355 | 10 | 447210 | 0.26031
ZN12660:PA17 | WOY WOY | URBAN | 1229 | 3556.0017 | 1144.1962 | 2.6863 | 9.467 | 2263.999 | 3 | 714.6667 | 714.6667 | 0.0065094 | 0.0065094 | 2 | 170910 | 0.29292
ZN12660:PA6 | WOY WOY | SHORT RURAL | 969 | 5136.0139 | 4340.5354 | 2.8578 | 165.3251 | 554.6717 | 5 | 11731.6167 | 11731.6167 | 0.044376 | 0.044376 | 1 | 39360 | 0.084623
ZN12660:PA8 | WOY WOY | URBAN | 1253 | 3596.4864 | 1331.5145 | 3.1245 | 195.3605 | 1612.2457 | 3 | 12679.5333 | 12679.5333 | 0.05826 | 0.05826 | 1 | 104640 | 0.17398
ZN12690:PA12 | BERKELEY VALE | SHORT RURAL | 1313 | 15839.1632 | 2375.9702 | 5.144 | 3055.4673 | 739.675 | 13 | 120454.8333 | 120109.3833 | 0.96725 | 0.96649 | 4 | 29160 | 0.076161
ZN12690:PA16 | BERKELEY VALE | SHORT RURAL | 368 | 13288.2149 | 5183.1988 | 3.4103 | 902.9083 | 700.2505 | 7 | 53690.9333 | 53690.9333 | 1.2826 | 1.2826 | 6 | 41640 | 0.27174
ZN12690:PA17 | BERKELEY VALE | URBAN | 166 | 2002.1663 | 4687.6327 | 3.1817 | 0 | 38.5959 | 0 | 0 | 0 | 0 | 0 | 2 | 2460 | 0.036145
ZN12690:PA22 | BERKELEY VALE | URBAN | 301 | 0 | 6645.8274 | 5.3346 | 5.4882 | 0 | 2 | 208.6333 | 208.6333 | 0.0066445 | 0.0066445 | 0 | 0 | 0
ZN12690:PA24 | BERKELEY VALE | SHORT RURAL | 891 | 30232.1725 | 3942.7595 | 4.8583 | 2142.082 | 5276.0185 | 23 | 89414.15 | 89414.15 | 1.1919 | 1.1919 | 23 | 220230 | 0.6431
ZN12690:PA26 | BERKELEY VALE | URBAN | 8 | 8424.1181 | 3334.7151 | 5.2774 | 1911.6437 | 2099.3337 | 12 | 73457.7333 | 73457.7333 | 99 | 99 | 17 | 80670 | 30.25
ZN12690:PA3 | BERKELEY VALE | SHORT RURAL | 600 | 2294.2699 | 5506.214 | 1.3527 | 98.3053 | 1047.7771 | 6 | 14737.6667 | 14737.6667 | 0.43667 | 0.43667 | 2 | 157080 | 0.51333
ZN12690:PA7 | BERKELEY VALE | SHORT RURAL | 757 | 7288.716 | 8534.1303 | 3.7913 | 474.836 | 2281.0676 | 9 | 25398.0833 | 14030.0833 | 0.24439 | 0.11493 | 14 | 122010 | 0.39234
ZN1285:PA10 | GREENACRE PARK | URBAN | 811 | 0 | 5185.7011 | 5.3727 | 167.7526 | 0 | 3 | 6331.85 | 6331.85 | 0.038224 | 0.038224 | 0 | 0 | 0
ZN1285:PA16 | GREENACRE PARK | URBAN | 73 | 0 | 2365.6011 | 2.7244 | 1.5714 | 0 | 0 | 116.9667 | 116.9667 | 0.013699 | 0.013699 | 0 | 0 | 0
ZN1285:PA17 | GREENACRE PARK | SHORT RURAL | 15 | 0 | 1598.4756 | 0.09526 | 1.4656 | 0 | 2 | 3120 | 3120 | 1.6 | 1.6 | 0 | 0 | 0
ZN1285:PA18 | GREENACRE PARK | URBAN | 64 | 374.2646 | 3758.838 | 1.848 | 37.6185 | 0 | 5 | 4128 | 4128 | 0.5625 | 0.5625 | 0 | 0 | 0
ZN1285:PA19 | GREENACRE PARK | URBAN | 1315 | 370.2627 | 5482.4215 | 2.7435 | 570.4395 | 0 | 6 | 42165.5167 | 42165.5167 | 1.1894 | 1.1894 | 0 | 0 | 0
ZN1285:PA20 | GREENACRE PARK | URBAN | 1054 | 1183.3783 | 9489.7512 | 5.5632 | 16.2174 | 2357.039 | 0 | 591.1667 | 591.1667 | 0.00094877 | 0.00094877 | 1 | 85920 | 0.16983
ZN1285:PA23 | GREENACRE PARK | URBAN | 1886 | 0 | 4409.5358 | 2.8769 | 71.9667 | 0 | 1 | 5073 | 5073 | 0.010074 | 0.010074 | 0 | 0 | 0
ZN1285:PA24 | GREENACRE PARK | URBAN | 2242 | 2970.4131 | 7820.0682 | 7.6017 | 1599.8665 | 5289.9445 | 9 | 42679.6833 | 42679.6833 | 0.052186 | 0.052186 | 3 | 141120 | 0.13113
ZN1285:PA29 | GREENACRE PARK | URBAN | 415 | 0 | 3159.4354 | 3.9247 | 35.189 | 89.4126 | 3 | 1818.2333 | 1818.2333 | 0.072289 | 0.072289 | 1 | 4620 | 0.026506
ZN1285:PA30 | GREENACRE PARK | URBAN | 2 | 0 | 3460.4519 | 2.5339 | 0.31238 | 0 | 0 | 25 | 25 | 0.5 | 0.5 | 0 | 0 | 0
ZN1285:PA31 | GREENACRE PARK | URBAN | 1874 | 1776.5552 | 9050.2762 | 8.3448 | 12355.9951 | 0 | 9 | 300271.4 | 271620.7333 | 1.4776 | 1.4354 | 0 | 0 | 0
ZN1285:PA33 | GREENACRE PARK | URBAN | 2575 | 1627.3767 | 7003.8129 | 8.6687 | 2865.7236 | 1673.5273 | 7 | 67039.8833 | 22360.2167 | 0.086602 | 0.027573 | 1 | 39150 | 0.033786
ZN1285:PA36 | GREENACRE PARK | URBAN | 1 | 0 | 0 | 3.4103 | 0.43724 | 0 | 0 | 26 | 26 | 1 | 1 | 0 | 0 | 0
ZN1285:PA8 | GREENACRE PARK | URBAN | 239 | 0 | 5302.1786 | 4.1533 | 47.925 | 0 | 2 | 2340 | 2340 | 0.075314 | 0.075314 | 0 | 0 | 0
ZN1287:PA11 | REVESBY | URBAN | 1277 | 1750.2748 | 4026.2547 | 3.8866 | 1110.5453 | 0 | 6 | 57945.0667 | 57945.0667 | 0.082224 | 0.082224 | 0 | 0 | 0
ZN1287:PA12 | REVESBY | URBAN | 883 | 54.8074 | 4660.9198 | 2.5339 | 19.0597 | 0 | 5 | 1525.3667 | 1525.3667 | 0.0056625 | 0.0056625 | 0 | 0 | 0
ZN1287:PA15 | REVESBY | URBAN | 1846 | 4115.6502 | 2440.6106 | 5.2965 | 171.9274 | 0 | 6 | 6582.8 | 6582.8 | 0.02546 | 0.02546 | 0 | 0 | 0
ZN1287:PA17 | REVESBY | URBAN | 1248 | 2728.3243 | 3278.908 | 4.9916 | 1595.2154 | 0 | 6 | 64807.9667 | 64807.9667 | 0.99279 | 0.99279 | 0 | 0 | 0
ZN1287:PA18 | REVESBY | URBAN | 248 | 278.4508 | 2609.9948 | 2.6101 | 1.8343 | 0 | 0 | 142.5167 | 142.5167 | 0.0040323 | 0.0040323 | 0 | 0 | 0
ZN1287:PA21 | REVESBY | URBAN | 1475 | 1909.0133 | 6647.6995 | 4.1152 | 203.2182 | 0 | 4 | 10014.2667 | 10014.2667 | 0.075932 | 0.075932 | 0 | 0 | 0
ZN1287:PA22 | REVESBY | URBAN | 941 | 794.3435 | 4540.6302 | 2.0386 | 325.0953 | 0 | 5 | 32339.8 | 32339.8 | 0.18491 | 0.18491 | 0 | 0 | 0
ZN1287:PA23 | REVESBY | URBAN | 884 | 41.9554 | 4132.1317 | 2.7054 | 980.7408 | 0 | 5 | 73515.05 | 73515.05 | 1.0011 | 1.0011 | 0 | 0 | 0
ZN1287:PA24 | REVESBY | URBAN | 1116 | 1082.1171 | 4691.6735 | 5.3917 | 871.8824 | 0 | 8 | 32793.05 | 32793.05 | 0.23387 | 0.23387 | 0 | 0 | 0
ZN1287:PA3 | REVESBY | URBAN | 1510 | 4099.821 | 4778.8185 | 3.9438 | 264.3372 | 0 | 6 | 13592.4667 | 5565.0833 | 0.1351 | 0.10331 | 0 | 0 | 0
ZN1287:PA4 | REVESBY | URBAN | 963 | 3415.4179 | 4160.5345 | 2.934 | 198.9679 | 2806.5147 | 7 | 13752.2167 | 13752.2167 | 0.096573 | 0.096573 | 4 | 193980 | 0.38318
ZN1287:PA5 | REVESBY | URBAN | 1111 | 1800.5523 | 7607.8912 | 3.2579 | 1215.1284 | 7.7113 | 3 | 75637.3667 | 75637.3667 | 0.14491 | 0.14491 | 0 | 480 | 0.00090009
ZN1287:PA6 | REVESBY | URBAN | 843 | 2054.6966 | 2571.6132 | 2.0386 | 533.8563 | 0 | 10 | 53106.9 | 53106.9 | 0.27402 | 0.27402 | 0 | 0 | 0
ZN129:PA11 | HUNTERS HILL | URBAN | 103 | 0 | 1849.8269 | 1.467 | 245.1396 | 0 | 2 | 33887 | 6901 | 2 | 1 | 0 | 0 | 0
ZN129:PA12 | HUNTERS HILL | URBAN | 1293 | 179.5311 | 8364.9292 | 4.1343 | 11049.8073 | 3.9754 | 9 | 542007.5333 | 205187.5333 | 3.0441 | 2.0487 | 2 | 195 | 0.0046404
ZN129:PA16 | HUNTERS HILL | URBAN | 1283 | 339.9568 | 3111.0801 | 3.0483 | 6672.0801 | 0 | 12 | 443865.7333 | 108943.7333 | 2.1832 | 1.1855 | 0 | 0 | 0
ZN129:PA18 | HUNTERS HILL | URBAN | 879 | 0 | 9714.2976 | 4.2295 | 7287.8755 | 0 | 16 | 349428.5 | 120178.5 | 2.306 | 1.3106 | 0 | 0 | 0
ZN129:PA19 | HUNTERS HILL | URBAN | 1703 | 5943.0468 | 2258.3671 | 4.8392 | 13316.1847 | 0 | 11 | 558028.5833 | 116474.5833 | 1.9918 | 1.0012 | 0 | 0 | 0
ZN129:PA2 | HUNTERS HILL | URBAN | 914 | 0 | 3860.65 | 2.3815 | 3882.8067 | 0 | 9 | 330632.9333 | 82496.1333 | 2.3381 | 1.2221 | 0 | 0 | 0
ZN129:PA21 | HUNTERS HILL | URBAN | 684 | 559.4922 | 6228.6225 | 4.382 | 5904.7742 | 10.3719 | 5 | 273266.1333 | 96940.1333 | 3.0058 | 2.0219 | 0 | 480 | 0.001462
ZN129:PA24 | HUNTERS HILL | URBAN | 1520 | 1391.4523 | 7648.8599 | 3.296 | 11241.3302 | 0 | 14 | 691642.95 | 269633.95 | 3.1013 | 2.0191 | 0 | 0 | 0
ZN129:PA25 | HUNTERS HILL | URBAN | 98 | 0 | 4011.5107 | 2.7625 | 430.2539 | 0 | 2 | 31584 | 6432 | 1.9592 | 0.97959 | 0 | 0 | 0
ZN129:PA27 | HUNTERS HILL | URBAN | 202 | 1128.2442 | 4458.4622 | 4.4201 | 1651.1156 | 6.5388 | 3 | 75753 | 23615 | 2.9307 | 1.9455 | 0 | 300 | 0.0049505
ZN129:PA28 | HUNTERS HILL | URBAN | 1003 | 0 | 6780.7217 | 4.4391 | 7522.0308 | 13.134 | 8 | 343628.7833 | 78170.3833 | 2.0389 | 1.0289 | 1 | 600 | 0.001994
ZN129:PA3 | HUNTERS HILL | URBAN | 1420 | 676.4048 | 6397.7242 | 5.125 | 21700.5583 | 2076.6113 | 14 | 858675.3167 | 491497.3167 | 4.631 | 3.6437 | 3 | 82170 | 0.11479
ZN129:PA4 | HUNTERS HILL | URBAN | 406 | 0 | 6166.0649 | 2.4577 | 1661.3606 | 0 | 4 | 137083.3 | 30973.3 | 2.0936 | 1.0961 | 0 | 0 | 0
ZN129:PA5 | HUNTERS HILL | URBAN | 903 | 182.5607 | 3408.671 | 2.553 | 4944.1869 | 1644.0097 | 19 | 392735.75 | 159031.75 | 3.1905 | 2.2027 | 6 | 130590 | 0.27575
ZN129:PA8 | HUNTERS HILL | URBAN | 1068 | 1402.1366 | 6003.9604 | 3.7913 | 8030.7233 | 0 | 8 | 429548.2333 | 149994.2333 | 3.0918 | 2.0927 | 0 | 0 | 0
ZN129:PA9 | HUNTERS HILL | URBAN | 1080 | 2391.1863 | 6943.3203 | 4.2295 | 7532.7503 | 30.0334 | 10 | 361169.4 | 78503.4 | 2.0963 | 1.0519 | 1 | 1440 | 0.0027778
ZN1290:PA1 | LEIGHTONFIELD | URBAN | 1088 | 1699.4152 | 3520.9352 | 2.5339 | 57.3238 | 0 | 3 | 4587.6833 | 4587.6833 | 0.061581 | 0.061581 | 0 | 0 | 0
ZN1290:PA10 | LEIGHTONFIELD | URBAN | 34 | 0 | 2342.2465 | 2.8387 | 74.2471 | 0 | 2 | 5304 | 5304 | 1.9412 | 1.9412 | 0 | 0 | 0
ZN1290:PA12 | LEIGHTONFIELD | URBAN | 1039 | 5851.1325 | 1886.8281 | 3.9438 | 7706.241 | 102.0985 | 10 | 396262.15 | 396262.15 | 3.3176 | 3.3176 | 2 | 5250 | 0.025024
ZN1290:PA13 | LEIGHTONFIELD | URBAN | 165 | 0 | 3663.4519 | 2.2672 | 0 | 42.2599 | 0 | 0 | 0 | 0 | 0 | 2 | 3780 | 0.024242
ZN1290:PA16 | LEIGHTONFIELD | URBAN | 27 | 292.7954 | 2468.9419 | 2.0195 | 16.4017 | 17.9254 | 1 | 1647 | 1647 | 1 | 1 | 1 | 1800 | 0.11111
ZN1290:PA17 | LEIGHTONFIELD | URBAN | 52 | 0 | 3663.508 | 2.7244 | 0 | 46.7525 | 0 | 0 | 0 | 0 | 0 | 3 | 3480 | 0.19231
ZN1290:PA2 | LEIGHTONFIELD | URBAN | 617 | 1.6503 | 5287.7683 | 2.2481 | 0 | 8.647 | 0 | 0 | 0 | 0 | 0 | 3 | 780 | 0.0097245
ZN1290:PA4 | LEIGHTONFIELD | URBAN | 1155 | 3643.0009 | 3443.7302 | 2.1529 | 350.0845 | 0 | 12 | 32976.5167 | 32976.5167 | 0.18009 | 0.18009 | 0 | 0 | 0
ZN1290:PA9 | LEIGHTONFIELD | URBAN | 73 | 52.3304 | 3108.1486 | 1.5242 | 49.4845 | 0 | 4 | 6584 | 6584 | 1 | 1 | 0 | 0 | 0
ZN13000:PA1 | LAKE MUNMORAH | URBAN | 603 | 3764.2443 | 1086.1122 | 1.1622 | 363.7499 | 373.457 | 5 | 63472.1833 | 63472.1833 | 1.1625 | 1.1625 | 3 | 65166 | 2.7264
ZN13000:PA2 | LAKE MUNMORAH | URBAN | 1354 | 9304.8713 | 1585.2697 | 3.2388 | 2312.3666 | 6584.1267 | 7 | 144783.1833 | 144783.1833 | 1.277 | 1.277 | 14 | 412249 | 1.7814
ZN13000:PA4 | LAKE MUNMORAH | SHORT RURAL | 106 | 12417.6902 | 94.7005 | 0.40009 | 19.6325 | 180.7942 | 3 | 9951 | 9951 | 2.0094 | 2.0094 | 6 | 91638 | 2.6321
ZN13000:PA5 | LAKE MUNMORAH | SHORT RURAL | 1621 | 10799.3586 | 14601.3226 | 5.0297 | 5764.923 | 4294.6335 | 8 | 232434.15 | 232434.15 | 1.6613 | 1.6613 | 5 | 173154 | 1.1715
ZN13000:PA7 | LAKE MUNMORAH | SHORT RURAL | 1354 | 14801.535 | 4603.9271 | 5.3917 | 4029.4572 | 107.5195 | 5 | 151555.0667 | 151555.0667 | 1.079 | 1.079 | 1 | 4044 | 0.99557
ZN13000:PA8 | LAKE MUNMORAH | SHORT RURAL | 131 | 2607.3841 | 7046.5162 | 0.57156 | 47.7221 | 7.7789 | 1 | 16932 | 16932 | 1 | 1 | 2 | 2760 | 0.29771
ZN14143:PA10 | SOMERSBY | SHORT RURAL | 298 | 7823.005 | 2221.3643 | 1.3527 | 470.7459 | 147.4812 | 2 | 70573 | 70573 | 1.9933 | 1.9933 | 7 | 22110 | 0.19463
ZN14143:PA12 | SOMERSBY | SHORT RURAL | 1866 | 8715.6869 | 11692.3457 | 4.7439 | 624.9258 | 4742.7304 | 16 | 26714.0333 | 22737.6 | 0.046624 | 0.045552 | 12 | 202740 | 0.21275
ZN14143:PA14 | SOMERSBY | URBAN | 62 | 0 | 3429.9785 | 2.0576 | 0 | 17.6548 | 0 | 0 | 0 | 0 | 0 | 2 | 1740 | 0.064516
ZN14143:PA17 | SOMERSBY | SHORT RURAL | 746 | 66927.7333 | 2297.5653 | 2.2672 | 19205.5152 | 13002.2963 | 24 | 1717866.2667 | 652798.2667 | 8.2306 | 7.2386 | 25 | 1163010 | 3.2614
ZN14143:PA5 | SOMERSBY | URBAN | 407 | 599.9323 | 4902.3243 | 2.3053 | 635.6647 | 6.8207 | 2 | 55918.1833 | 55918.1833 | 1.0025 | 1.0025 | 1 | 600 | 0.007371
ZN14143:PA6 | SOMERSBY | URBAN | 27 | 1359.561 | 5392.7535 | 4.2486 | 43.2893 | 0 | 2 | 2066.2667 | 2066.2667 | 1.037 | 1.037 | 0 | 0 | 0
ZN14144:PA1 | WAMBERAL | URBAN | 1179 | 5538.0851 | 924.7705 | 3.1626 | 375.3509 | 327.5043 | 6 | 24067.9833 | 24067.9833 | 0.95759 | 0.95759 | 1 | 21000 | 0.042409
ZN14144:PA10 | WAMBERAL | SHORT RURAL | 664 | 15187.0737 | 5496.8168 | 3.0293 | 2803.6081 | 1689.9138 | 32 | 187685.4167 | 187638.8333 | 3.6295 | 3.6265 | 13 | 113130 | 0.55873
ZN14144:PA4 | WAMBERAL | URBAN | 821 | 3457.783 | 1796.1396 | 1.7909 | 2145.7313 | 1653.1922 | 11 | 242972.9 | 242972.9 | 5.162 | 5.162 | 4 | 187200 | 0.48356
ZN14144:PA5 | WAMBERAL | SHORT RURAL | 272 | 4979.0756 | 732.196 | 1.2193 | 96.3942 | 234.1346 | 12 | 16031.7667 | 16031.7667 | 1.3566 | 1.3566 | 6 | 38940 | 0.27206
ZN14144:PA7 | WAMBERAL | SHORT RURAL | 1030 | 5713.0031 | 3841.5588 | 2.3815 | 2815.6407 | 379.7866 | 13 | 239760.4667 | 239760.4667 | 3.0049 | 3.0049 | 3 | 32340 | 0.066019
ZN14144:PA8 | WAMBERAL | URBAN | 486 | 1977.066 | 1042.0652 | 1.2193 | 113.7032 | 0 | 12 | 18910.5 | 18910.5 | 2.0041 | 2.0041 | 0 | 0 | 0
ZN14891:PA1 | WYONG NEW | SHORT RURAL | 1335 | 8628.9827 | 8198.2282 | 4.6677 | 2696.9949 | 673.9486 | 11 | 117172.15 | 117172.15 | 1.0712 | 1.0712 | 3 | 29280 | 0.045693
ZN14891:PA10 | WYONG NEW | SHORT RURAL | 2147 | 17040.2304 | 6492.3034 | 5.3346 | 8137.5673 | 3447.8708 | 15 | 309347.7167 | 309347.7167 | 1.1132 | 1.1132 | 6 | 131070 | 0.20494
ZN14891:PA12 | WYONG NEW | SHORT RURAL | 694 | 70113.1266 | 2940.523 | 3.5246 | 4240.4469 | 7395.4172 | 35 | 243977.7667 | 180718.7667 | 3.5692 | 3.4885 | 39 | 425501.7 | 1.2911
ZN14891:PA17 | WYONG NEW | SHORT RURAL | 689 | 5693.9234 | 5408.2788 | 1.8099 | 1935.3176 | 0 | 7 | 216839.8 | 216839.8 | 2.5501 | 2.5501 | 0 | 0 | 0
ZN14891:PA19 | WYONG NEW | URBAN | 186 | 1806.914 | 3260.9197 | 1.7147 | 364.1639 | 0 | 2 | 43069 | 43069 | 0.98925 | 0.98925 | 0 | 0 | 0
ZN14891:PA20 | WYONG NEW | SHORT RURAL | 515 | 31843.7157 | 5001.8427 | 4.0962 | 4321.7215 | 1153.1562 | 16 | 213958.0667 | 213268.1167 | 5.0777 | 5.0757 | 15 | 57090 | 0.30291
ZN14891:PA21 | WYONG NEW | SHORT RURAL | 5 | 3373.7247 | 103.721 | 0.19052 | 1.7099 | 0 | 3 | 1820 | 1820 | 3 | 3 | 0 | 0 | 0
ZN14891:PA3 | WYONG NEW | SHORT RURAL | 20 | 0 | 7541.7851 | 1.7147 | 15.3888 | 0 | 1 | 1820 | 1820 | 1 | 1 | 0 | 0 | 0
ZN14891:PA5 | WYONG NEW | SHORT RURAL | 1422 | 64034.3862 | 2689.2839 | 3.6199 | 5282.0565 | 6911.7785 | 40 | 295910.1 | 295910.1 | 1.7883 | 1.7883 | 54 | 387210 | 0.60478
ZN14891:PA6 | WYONG NEW | URBAN | 205 | 2823.1149 | 5119.2896 | 4.0962 | 708.0408 | 128.4651 | 5 | 35053.4 | 35053.4 | 2.7756 | 2.7756 | 3 | 6360 | 0.1122
ZN14891:PA8 | WYONG NEW | SHORT RURAL | 1318 | 16547.0224 | 7854.8752 | 2.9531 | 7943.9264 | 1563.0862 | 7 | 545524 | 545524 | 3.047 | 3.047 | 15 | 107340 | 0.17147
ZN14891:PA9 | WYONG NEW | URBAN | 1233 | 3225.974 | 5448.3848 | 2.6673 | 1634.8101 | 0 | 7 | 124293.85 | 124293.85 | 1.0081 | 1.0081 | 0 | 0 | 0
ZN14892:PA1 | CHARMHAVEN | SHORT RURAL | 916 | 5847.9036 | 10709.6836 | 2.8578 | 1665.8616 | 5.0732 | 3 | 118211.0333 | 118211.0333 | 1.9662 | 1.9662 | 0 | 360 | 0.0010917
ZN14892:PA12 | CHARMHAVEN | SHORT RURAL | 162 | 0 | 2363.2166 | 0.4763 | 23.0809 | 0 | 0 | 9827.05 | 9827.05 | 0.0061728 | 0.0061728 | 0 | 0 | 0
ZN14892:PA14 | CHARMHAVEN | SHORT RURAL | 715 | 2211.3956 | 8856.2554 | 2.0957 | 65.0112 | 86.8084 | 3 | 6290.8 | 6290.8 | 0.099301 | 0.099301 | 1 | 8400 | 0.027972
ZN14892:PA17 | CHARMHAVEN | URBAN | 664 | 1567.5879 | 5302.8732 | 2.3815 | 23.7007 | 0 | 3 | 2018.1833 | 2018.1833 | 0.02259 | 0.02259 | 0 | 0 | 0
ZN14892:PA19 | CHARMHAVEN | URBAN | 1713 | 7043.2822 | 1700.4337 | 3.7151 | 2649.7501 | 2726.0084 | 20 | 144637.4167 | 144637.4167 | 1.1821 | 1.1821 | 13 | 148800 | 0.26853
ZN14892:PA21 | CHARMHAVEN | URBAN | 1078 | 239.4248 | 6034.1633 | 2.572 | 2199.9746 | 278.5196 | 2 | 173457.9667 | 173457.9667 | 0.99722 | 0.99722 | 1 | 21960 | 0.056586
ZN14892:PA3 | CHARMHAVEN | SHORT RURAL | 1181 | 4979.6978 | 2966.8762 | 2.191 | 389.8063 | 2162.5431 | 9 | 36079.5667 | 36079.5667 | 1.1575 | 1.1575 | 6 | 200160 | 0.35309
ZN14892:PA5 | CHARMHAVEN | URBAN | 278 | 7160.4657 | 2762.7813 | 3.8104 | 0 | 165.1614 | 0 | 0 | 0 | 0 | 0 | 3 | 8790 | 0.10432
ZN14892:PA6 | CHARMHAVEN | SHORT RURAL | 1834 | 6597.1935 | 10476.6967 | 3.9057 | 61.8186 | 573.7385 | 10 | 3209.7833 | 3209.7833 | 0.015267 | 0.015267 | 4 | 29790 | 0.037623
ZN14892:PA8 | CHARMHAVEN | URBAN | 889 | 3705.381 | 2914.7871 | 2.3815 | 57.5877 | 561.5769 | 10 | 4903.7667 | 4903.7667 | 0.023622 | 0.023622 | 2 | 47820 | 0.11249
ZN15001:PA10 | BROOKVALE | URBAN | 358 | 0 | 2855.5995 | 4.8011 | 31.251 | 2.7937 | 1 | 1320 | 0 | 0.061453 | 0 | 1 | 118 | 0.0055866
ZN15001:PA11 | BROOKVALE | URBAN | 952 | 118.6225 | 4984.5651 | 4.8964 | 53.6074 | 0 | 2 | 2220.25 | 2220.25 | 0.028361 | 0.028361 | 0 | 0 | 0
ZN15001:PA13 | BROOKVALE | URBAN | 129 | 0 | 2307.7031 | 2.553 | 0.4658 | 0 | 0 | 37 | 37 | 0.0077519 | 0.0077519 | 0 | 0 | 0
ZN15001:PA15 | BROOKVALE | URBAN | 2801 | 0 | 5148.9136 | 6.9921 | 33.9544 | 4298.8521 | 2 | 984.7833 | 984.7833 | 0.00071403 | 0.00071403 | 5 | 124680 | 0.094609
ZN15001:PA17 | BROOKVALE | URBAN | 14 | 0 | 1627.9259 | 4.2676 | 12.6267 | 43.562 | 2 | 600 | 480 | 1 | 0.85714 | 2 | 2070 | 0.71429
ZN15001:PA18 | BROOKVALE | URBAN | 1912 | 3385.6268 | 2948.0984 | 4.5344 | 1515.2192 | 72.4455 | 10 | 67765.5333 | 67765.5333 | 0.4409 | 0.4409 | 1 | 3240 | 0.056485
ZN15001:PA2 | BROOKVALE | URBAN | 2150 | 0 | 6522.9372 | 2.8959 | 172.8397 | 23.1339 | 6 | 12103.4833 | 11473.4833 | 0.048837 | 0.040465 | 1 | 1620 | 0.012558
ZN15001:PA3 | BROOKVALE | URBAN | 474 | 852.132 | 1818.3705 | 4.5153 | 28.3918 | 208.4077 | 0 | 1275.1333 | 1275.1333 | 0.0021097 | 0.0021097 | 1 | 9360 | 0.054852
ZN15001:PA4 | BROOKVALE | URBAN | 683 | 0 | 4229.3571 | 6.2681 | 15.8744 | 583.5627 | 0 | 513.5833 | 513.5833 | 0.0014641 | 0.0014641 | 1 | 18880 | 0.46852
ZN15001:PA6 | BROOKVALE | URBAN | 1040 | 944.5965 | 4424.5467 | 3.9628 | 91.928 | 0 | 2 | 4704.3 | 4704.3 | 0.043269 | 0.043269 | 0 | 0 | 0
ZN15001:PA8 | BROOKVALE | URBAN | 683 | 2974.4032 | 1701.2234 | 2.6863 | 12.7643 | 0 | 4 | 963.5833 | 636.6333 | 0.011713 | 0.010249 | 0 | 0 | 0
ZN15002:PA2 | NARRABEEN | SHORT RURAL | 1190 | 9711.4097 | 1526.5842 | 3.0102 | 1445.0348 | 0 | 11 | 97349.0167 | 56428.0167 | 0.37647 | 0.15042 | 0 | 0 | 0
ZN15002:PA4 | NARRABEEN | URBAN | 697 | 2212.3307 | 2702.4598 | 1.3146 | 690.7844 | 0 | 5 | 106562.35 | 28157 | 1.9957 | 1.0014 | 0 | 0 | 0
ZN15002:PA6 | NARRABEEN | URBAN | 1608 | 6461.6985 | 4982.4498 | 3.8104 | 7236.7494 | 153.3239 | 23 | 385144.6667 | 384788.6667 | 2.1393 | 2.1368 | 1 | 8160 | 0.010572
ZN15002:PA8 | NARRABEEN | URBAN | 807 | 88.744 | 5211.0067 | 4.039 | 4052.7771 | 0 | 9 | 203482.5667 | 202874.5667 | 3.0942 | 3.0892 | 0 | 0 | 0
ZN15004:PA1 | NEWPORT | URBAN | 354 | 528.5111 | 583.5097 | 1.0479 | 6.7278 | 0 | 1 | 1302.0333 | 1302.0333 | 0.18927 | 0.18927 | 0 | 0 | 0
ZN15004:PA3 | NEWPORT | URBAN | 1542 | 204.761 | 7021.7582 | 3.6008 | 1555.6258 | 0 | 14 | 87610 | 28667.9333 | 0.12387 | 0.073281 | 0 | 0 | 0
ZN15004:PA5 | NEWPORT | URBAN | 1603 | 2.3017 | 12284.3793 | 4.2676 | 3543.4165 | 0 | 11 | 168377.6833 | 143561.6667 | 1.058 | 1.0193 | 0 | 0 | 0
ZN15004:PA9 | NEWPORT | URBAN | 2655 | 2028.4273 | 8162.5475 | 5.4108 | 1401.7467 | 0 | 16 | 52536.55 | 44236.9667 | 0.092279 | 0.061017 | 0 | 0 | 0
ZN15005:PA10 | BELROSE | URBAN | 769 | 6067.4489 | 7342.1753 | 5.4298 | 3739.4135 | 48.1956 | 6 | 139659.0167 | 137065.0167 | 2.1105 | 2.1053 | 1 | 1800 | 0.0052016
ZN15005:PA12 | BELROSE | URBAN | 1438 | 6164.945 | 581.3558 | 4.02 | 5636.5881 | 2027.8789 | 21 | 284344.0833 | 203815.0833 | 1.4465 | 1.267 | 1 | 102298.65 | 0.16203
ZN15005:PA2 | BELROSE | URBAN | 1891 | 7379.3254 | 5307.3471 | 5.8299 | 16616.4751 | 0 | 19 | 577999.9833 | 486233.9833 | 3.8424 | 3.2787 | 0 | 0 | 0
ZN15005:PA4 | BELROSE | URBAN | 1105 | 6154.7759 | 2399.9051 | 3.8295 | 2693.6206 | 824.8374 | 4 | 142643.0833 | 138368.0833 | 1.1575 | 1.1122 | 2 | 43680 | 0.094118
ZN15005:PA6 | BELROSE | URBAN | 1367 | 7100.2517 | 3995.011 | 3.9057 | 5867.4737 | 1317.3453 | 16 | 304654.5333 | 301252.05 | 1.7154 | 1.7081 | 2 | 68400 | 0.083394
ZN15005:PA8 | BELROSE | URBAN | 1539 | 5444.1225 | 4352.8344 | 5.6965 | 15995.9473 | 1401.4395 | 16 | 569441.5167 | 528606.3167 | 4.9708 | 4.9188 | 2 | 49890 | 0.087719
ZN15006:PA12 | DEE WHY WEST | URBAN | 3685 | 5143.4508 | 12349.2651 | 7.9066 | 1993.2114 | 105.2692 | 7 | 51122.9167 | 45960.9167 | 0.23881 | 0.23094 | 1 | 2700 | 0.0032564
ZN15006:PA13 | DEE WHY WEST | URBAN | 1323 | 1615.6975 | 6146.8313 | 3.1245 | 13797.6428 | 0 | 9 | 895511.9833 | 63708.9833 | 2.9735 | 1.034 | 0 | 0 | 0
ZN15006:PA15 | DEE WHY WEST | URBAN | 2084 | 842.0896 | 7153.5772 | 3.1436 | 427.8547 | 703.1478 | 10 | 27600.8667 | 14017.6 | 0.076296 | 0.058061 | 2 | 45360 | 0.040307
ZN15006:PA16 | DEE WHY WEST | URBAN | 2422 | 0 | 9315.8691 | 4.8202 | 28.8428 | 0 | 3 | 1213.4667 | 1213.4667 | 0.012799 | 0.012799 | 0 | 0 | 0
ZN15006:PA2 | DEE WHY WEST | URBAN | 2245 | 165.9073 | 5848.8284 | 5.3536 | 886.2194 | 0 | 7 | 33569.5333 | 8114.3667 | 0.065924 | 0.028062 | 0 | 0 | 0
ZN15006:PA6 | DEE WHY WEST | URBAN | 635 | 1682.4723 | 955.2875 | 2.4006 | 6.4905 | 0 | 2 | 548.3 | 548.3 | 0.050394 | 0.050394 | 0 | 0 | 0
ZN15006:PA8 | DEE WHY WEST | URBAN | 1772 | 5341.2733 | 2028.6582 | 3.1626 | 23.9343 | 0 | 7 | 1534.7 | 1534.7 | 0.0039503 | 0.0039503 | 0 | 0 | 0
ZN15006:PA9 | DEE WHY WEST | URBAN | 2649 | 362.0607 | 7362.2175 | 6.1157 | 3198.7399 | 0 | 8 | 106067.9667 | 106067.9667 | 0.1208 | 0.1208 | 0 | 0 | 0
ZN15008:PA1 | HARBORD | URBAN | 2311 | 2341.9272 | 4005.5668 | 3.8104 | 2000.1357 | 0 | 7 | 106448.5667 | 106448.5667 | 0.98918 | 0.98918 | 0 | 0 | 0
ZN15008:PA10 | HARBORD | URBAN | 1733 | 3871.5691 | 3521.1277 | 3.5627 | 1222.2851 | 0 | 15 | 69573.0833 | 66106.0833 | 0.1004 | 0.059435 | 0 | 0 | 0
ZN15008:PA5 | HARBORD | URBAN | 2120 | 2393.4585 | 2982.8581 | 4.8202 | 615.5931 | 0 | 13 | 25899.0333 | 25883.0333 | 0.098113 | 0.09717 | 0 | 0 | 0
ZN15008:PA7 | HARBORD | URBAN | 2707 | 5585.7029 | 2736.1689 | 5.3155 | 14656.1911 | 0 | 29 | 559148.6333 | 481040.6333 | 2.6882 | 2.5216 | 0 | 0 | 0
ZN15008:PA9 | HARBORD | URBAN | 2139 | 7681.5234 | 2186.8348 | 4.3439 | 13495.1376 | 431.1896 | 16 | 630017.8 | 630017.8 | 3.9514 | 3.9514 | 1 | 20130 | 0.028518
ZN15009:PA1 | MANLY | URBAN | 2063 | 359.3731 | 3823.2372 | 5.1059 | 5935.4049 | 718.3337 | 7 | 235736 | 219392 | 3.999 | 3.0087 | 2 | 28530 | 0.086767
ZN15009:PA11 | MANLY | URBAN | 2205 | 399.9472 | 4234.635 | 4.2295 | 2452.225 | 0 | 9 | 117575.7333 | 100015.7333 | 3.0893 | 2.0939 | 0 | 0 | 0
ZN15009:PA12 | MANLY | URBAN | 78 | 0 | 818.5678 | 0.60966 | 4.0586 | 0 | 2 | 1350 | 918 | 2.0769 | 1.3846 | 0 | 0 | 0
ZN15009:PA3 | MANLY | URBAN | 791 | 0 | 3264.935 | 1.8099 | 202.1213 | 167.0779 | 6 | 22646.3833 | 16058.3833 | 3.0493 | 2.0405 | 1 | 18720 | 0.049305
ZN15009:PA5 | MANLY | URBAN | 1805 | 474.9881 | 2641.3524 | 4.5153 | 1107.4448 | 591.1566 | 7 | 49737.5167 | 35339.5167 | 3.0039 | 2.0072 | 1 | 26550 | 0.032687
ZN15009:PA7 | MANLY | URBAN | 1566 | 2062.8535 | 1862.6408 | 2.8387 | 1877.8245 | 367.2459 | 6 | 134146.4167 | 29452.4167 | 4.039 | 2.0409 | 1 | 26235 | 0.033844
ZN15009:PA9 | MANLY | URBAN | 590 | 0 | 572.5568 | 2.3053 | 693.7071 | 185.5219 | 4 | 61024.0667 | 56296.0667 | 3.0424 | 2.0407 | 1 | 16320 | 0.23051
ZN15010:PA1 | CAREEL BAY | URBAN | 1392 | 2.2996 | 8697.8488 | 3.5437 | 1222.2906 | 0 | 14 | 69947.45 | 69947.45 | 0.13147 | 0.13147 | 0 | 0 | 0
ZN15010:PA11 | CAREEL BAY | URBAN | 476 | 0 | 3951.5015 | 1.2003 | 167.2877 | 0 | 9 | 28264.0167 | 28264.0167 | 0.46429 | 0.46429 | 0 | 0 | 0
ZN15010:PA5 | CAREEL BAY | URBAN | 894 | 0 | 4882.7867 | 1.9243 | 568.7466 | 0 | 8 | 59938.7667 | 1794.7667 | 0.096197 | 0.00783 | 0 | 0 | 0
ZN15010:PA7 | CAREEL BAY | URBAN | 1782 | 189.4107 | 7376.2593 | 4.1152 | 579.6613 | 6.0879 | 12 | 28564.7833 | 27482.5333 | 0.092593 | 0.090348 | 0 | 300 | 0.00056117
ZN15010:PA9 | CAREEL BAY | SHORT RURAL | 1130 | 841.6532 | 12623.8294 | 2.7435 | 113.0279 | 0 | 9 | 8354.75 | 8354.75 | 0.058407 | 0.058407 | 0 | 0 | 0
ZN15011:PA1 | BEACON HILL | URBAN | 95 | 0 | 1375.3196 | 3.296 | 115.1043 | 0 | 1 | 7082 | 7082 | 0.98947 | 0.98947 | 0 | 0 | 0
ZN15011:PA10 | BEACON HILL | URBAN | 1449 | 2487.2613 | 8535.4831 | 6.6301 | 216.0456 | 264.8219 | 7 | 6608.1 | 6608.1 | 0.083506 | 0.083506 | 1 | 8100 | 0.010352
ZN15011:PA2 | BEACON HILL | URBAN | 1595 | 6048.8578 | 1878.2903 | 4.02 | 2385.3631 | 0 | 14 | 120332.35 | 120332.35 | 2.5737 | 2.5737 | 0 | 0 | 0
ZN15011:PA6 | BEACON HILL | URBAN | 1220 | 4504.5787 | 4603.7243 | 4.3629 | 4179.2202 | 0 | 12 | 194254.0667 | 176774.0667 | 1.3352 | 1.3041 | 0 | 0 | 0
ZN15011:PA8 | BEACON HILL | URBAN | 250 | 0 | 4411.3799 | 5.0297 | 7.3415 | 14.8814 | 3 | 296 | 296 | 0.012 | 0.012 | 0 | 600 | 0.004
ZN15012:PA2 | KILLARNEY | URBAN | 1310 | 0 | 6867.8844 | 4.0962 | 1298.9712 | 0 | 5 | 64308.95 | 64308.95 | 1.0969 | 1.0969 | 0 | 0 | 0
ZN15012:PA4 | KILLARNEY | URBAN | 1198 | 5033.7878 | 2486.5035 | 2.8387 | 1782.6091 | 0 | 8 | 127344.5 | 127344.5 | 2.1002 | 2.1002 | 0 | 0 | 0
ZN15012:PA6 | KILLARNEY | URBAN | 1392 | 1072.0835 | 9050.9894 | 4.2295 | 1619.8085 | 35.039 | 17 | 77664.2333 | 77664.2333 | 1.1358 | 1.1358 | 1 | 1680 | 0.0028736
ZN15012:PA8 | KILLARNEY | URBAN | 1143 | 4558.4029 | 1659.5731 | 4.4391 | 6860.2226 | 0 | 19 | 313395.4167 | 313173.4167 | 5.0236 | 5.0201 | 0 | 0 | 0
ZN15013:PA1 | TERREY HILLS | URBAN | 260 | 0 | 4123.6316 | 5.506 | 978.2 | 0 | 1 | 36028 | 36028 | 1 | 1 | 0 | 0 | 0
ZN15013:PA10 | TERREY HILLS | SHORT RURAL | 624 | 25230.9203 | 767.2833 | 2.4006 | 1693.6649 | 46.8765 | 9 | 143076.1667 | 119973.1667 | 1.5337 | 1.2917 | 3 | 3960 | 0.051282
ZN15013:PA2 | TERREY HILLS | URBAN | 67 | 1965.1386 | 274.4396 | 0.66682 | 80.9784 | 0 | 4 | 24627 | 24627 | 3.2836 | 3.2836 | 0 | 0 | 0
ZN15013:PA4 | TERREY HILLS | URBAN | 810 | 9170.8401 | 2957.8179 | 3.4865 | 419.7078 | 193.8588 | 11 | 24412.1667 | 24412.1667 | 0.30864 | 0.30864 | 2 | 11275.7333 | 0.045679
ZN15013:PA6 | TERREY HILLS | SHORT RURAL | 223 | 8425.1547 | 213.0987 | 0.87639 | 305.5712 | 9.3347 | 6 | 70707.4 | 70707.4 | 3.0673 | 3.0673 | 4 | 2160 | 0.017937
ZN15013:PA8 | TERREY HILLS | URBAN | 98 | 1801.7266 | 5629.5159 | 1.7528 | 49.2666 | 0 | 1 | 5700 | 5700 | 0.15306 | 0.15306 | 0 | 0 | 0
ZN15014:PA11 | MONA VALE | URBAN | 1335 | 2132.8197 | 5078.3738 | 3.2198 | 6380.3572 | 0 | 15 | 401854.3167 | 96435.8667 | 3.0419 | 1.4974 | 0 | 0 | 0
ZN15014:PA12 | MONA VALE | SHORT RURAL | 1807 | 5242.5061 | 14849.8816 | 6.0776 | 756.7888 | 385.7082 | 14 | 25251.9167 | 25251.9167 | 0.044272 | 0.044272 | 1 | 12870 | 0.018262
ZN15014:PA14 | MONA VALE | SHORT RURAL | 844 | 7725.2923 | 5453.9849 | 4.9726 | 1711.0086 | 0 | 7 | 69778.5667 | 69778.5667 | 1.2595 | 1.2595 | 0 | 0 | 0
ZN15014:PA16 | MONA VALE | URBAN | 906 | 493.6763 | 3898.352 | 4.8964 | 32.3499 | 0 | 3 | 1339.8333 | 901.9333 | 0.0033113 | 0.0022075 | 0 | 0 | 0
ZN15014:PA18 | MONA VALE | URBAN | 530 | 557.6714 | 4108.1759 | 1.7147 | 86.6214 | 0 | 6 | 10244.55 | 10090.55 | 0.081132 | 0.079245 | 0 | 0 | 0
ZN15014:PA19 | MONA VALE | URBAN | 1891 | 4665.7923 | 6961.5382 | 4.4201 | 7130.8559 | 2436.3616 | 21 | 327162.8833 | 198734.8833 | 1.6145 | 1.4897 | 2 | 111780 | 0.10947
ZN15014:PA20 | MONA VALE | URBAN | 881 | 1799.5014 | 3810.4183 | 3.3722 | 126.4377 | 251.4286 | 6 | 7603.5 | 7373.5 | 0.057889 | 0.055619 | 1 | 15120 | 0.047673
ZN15014:PA22 | MONA VALE | URBAN | 874 | 1881.7976 | 4423.2715 | 3.658 | 883.4414 | 0 | 8 | 48976.4 | 48976.4 | 1.0698 | 1.0698 | 0 | 0 | 0
ZN15014:PA5 | MONA VALE | URBAN | 1546 | 1881.7895 | 5710.8618 | 4.2867 | 809.2387 | 0 | 4 | 38282.8667 | 38282.8667 | 0.11384 | 0.11384 | 0 | 0 | 0
ZN15014:PA7 | MONA VALE | URBAN | 1042 | 417.3628 | 5751.3821 | 4.8583 | 68.4216 | 810.7 | 5 | 2856.0333 | 2856.0333 | 0.012476 | 0.012476 | 1 | 33840 | 0.090211
ZN15015:PA15 | NORTH HEAD | URBAN | 469 | 1000.7034 | 5093.3949 | 1.6766 | 350.836 | 102.6819 | 4 | 42435.75 | 37537.75 | 2.9296 | 1.968 | 2 | 12420 | 0.029851
ZN15015:PA5 | NORTH HEAD | URBAN | 1668 | 445.1439 | 5395.2194 | 3.315 | 3275.7721 | 25.011 | 6 | 200389.4167 | 182360.4167 | 4.0743 | 3.0917 | 1 | 1530 | 0.0017986
ZN1600:PA22ABC | CITY EAST | CBD | 136 | 0 | 5250.1774 | 7.3731 | 0 | 13.0889 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0.0073529
ZN1600:PA23ABC | CITY EAST | CBD | 149 | 0 | 4503.9317 | 7.7923 | 59.1744 | 0 | 1 | 1540 | 1540 | 0.09396 | 0.09396 | 0 | 0 | 0
ZN1600:PA23DEF | CITY EAST | CBD | 224 | 0 | 3809.8016 | 6.23 | 0 | 11.0596 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0.0044643
ZN1610:PA11 | HOMEBUSH BAY | URBAN | 1222 | 0 | 10566.8708 | 4.763 | 235.7961 | 0 | 5 | 10039.3833 | 10039.3833 | 0.10475 | 0.10475 | 0 | 0 | 0
ZN1610:PA13 | HOMEBUSH BAY | URBAN | 1807 | 0 | 5910.4377 | 3.9057 | 0 | 1180.9885 | 0 | 0 | 0 | 0 | 0 | 2 | 61320 | 0.080797
ZN1610:PA17 | HOMEBUSH BAY | URBAN | 331 | 0 | 6751.5989 | 3.7151 | 11.8713 | 0 | 1 | 648 | 648 | 0.97885 | 0.97885 | 0 | 0 | 0
ZN1610:PA18 | HOMEBUSH BAY | URBAN | 196 | 0 | 2392.8555 | 3.2388 | 172.2977 | 0 | 1 | 10788 | 10788 | 0.94898 | 0.94898 | 0 | 0 | 0
ZN1610:PA20 | HOMEBUSH BAY | SHORT RURAL | 40 | 0 | 5912.6026 | 1.4289 | 16.7346 | 0 | 1 | 2375 | 2375 | 1 | 1 | 0 | 0 | 0
ZN1610:PA23 | HOMEBUSH BAY | URBAN | 132 | 0 | 5986.9844 | 3.0483 | 27.478 | 43.2914 | 1 | 1828 | 0 | 0.030303 | 0 | 1 | 2880 | 0.045455
ZN1610:PA26 | HOMEBUSH BAY | URBAN | 49 | 0 | 4438.0376 | 2.8578 | 51.3125 | 0 | 3 | 3641.1833 | 3641.1833 | 1.0816 | 1.0816 | 0 | 0 | 0
ZN1648:PA11 | ENFIELD | URBAN | 492 | 0 | 3675.8273 | 1.5242 | 44.218 | 0 | 3 | 5883.2833 | 5883.2833 | 0.10976 | 0.10976 | 0 | 0 | 0
ZN1648:PA13 | ENFIELD | URBAN | 64 | 0 | 4934.8539 | 3.9057 | 126.8619 | 0 | 2 | 6587 | 6587 | 1.0156 | 1.0156 | 0 | 0 | 0
ZN1648:PA16 | ENFIELD | URBAN | 1172 | 0 | 5199.6968 | 2.4768 | 1274.2689 | 0 | 7 | 104334.5333 | 52316.3833 | 0.40785 | 0.34727 | 0 | 0 | 0
ZN1648:PA20 | ENFIELD | URBAN | 1077 | 0 | 5256.421 | 2.4768 | 253.5693 | 0 | 6 | 20761.7333 | 20674.2333 | 0.13185 | 0.13092 | 0 | 0 | 0
ZN1648:PA21 | ENFIELD | URBAN | 339 | 0 | 2532.2596 | 0.85734 | 42.7194 | 0 | 3 | 10104.6833 | 10104.6833 | 0.10914 | 0.10914 | 0 | 0 | 0
ZN1648:PA4 | ENFIELD | URBAN | 651 | 0 | 5009.036 | 2.0005 | 489.5571 | 0 | 2 | 49627.7333 | 49627.7333 | 0.9831 | 0.9831 | 0 | 0 | 0
ZN167:PA1 | AUBURN | URBAN | 171 | 0 | 4014.5451 | 3.315 | 4.3072 | 13.7315 | 2 | 263.4833 | 263.4833 | 0.011696 | 0.011696 | 1 | 840 | 0.011696
ZN167:PA10 | AUBURN | URBAN | 1046 | 0 | 3424.112 | 1.6956 | 182.3206 | 375.0094 | 1 | 21805 | 21805 | 0.046845 | 0.046845 | 2 | 44850 | 0.10994
ZN167:PA12 | AUBURN | URBAN | 408 | 0 | 7499.6715 | 3.5437 | 18.6618 | 0 | 5 | 1067.95 | 1067.95 | 0.012255 | 0.012255 | 0 | 0 | 0
ZN167:PA17 | AUBURN | URBAN | 6 | 0 | 1502.4269 | 2.4387 | 0 | 64.9372 | 0 | 0 | 0 | 0 | 0 | 1 | 5400 | 0.5
ZN167:PA2 | AUBURN | URBAN | 118 | 0 | 4834.9213 | 4.382 | 30.7217 | 4.5377 | 2 | 1421.7667 | 1421.7667 | 0.084746 | 0.084746 | 1 | 210 | 0.059322
ZN167:PA20 | AUBURN | URBAN | 382 | 0 | 2998.9188 | 3.8485 | 43.1376 | 0 | 4 | 2273.0833 | 2273.0833 | 0.04712 | 0.04712 | 0 | 0 | 0
ZN167:PA21 | AUBURN | URBAN | 932 | 0 | 10135.1116 | 4.4772 | 76.8697 | 0 | 10 | 3481.75 | 3481.75 | 0.01073 | 0.01073 | 0 | 0 | 0
ZN1673:PA1 | TURRAMURRA | URBAN | 1432 | 3.6502 | 10967.1822 | 5.2012 | 489.6472 | 0 | 8 | 19091.1 | 19091.1 | 0.15503 | 0.15503 | 0 | 0 | 0
ZN1673:PA11 | TURRAMURRA | URBAN | 1639 | 4316.7527 | 5752.3333 | 5.4108 | 11243.1545 | 0 | 20 | 421386.0833 | 377328.8167 | 1.2739 | 1.2264 | 0 | 0 | 0
ZN1673:PA13 | TURRAMURRA | URBAN | 869 | 1106.7907 | 6376.5771 | 3.7723 | 1894.3339 | 0 | 4 | 101836.0833 | 95270.1333 | 1.0656 | 1.0345 | 0 | 0 | 0
ZN1673:PA18 | TURRAMURRA | URBAN | 1131 | 5240.183 | 4916.7207 | 4.0009 | 4586.1919 | 9.47 | 5 | 232457.35 | 174964.6 | 1.0752 | 1.0336 | 0 | 480 | 0.00088417
ZN1673:PA19 | TURRAMURRA | URBAN | 480 | 1.3312 | 5295.0667 | 2.3815 | 291.8851 | 0 | 9 | 24854.9167 | 24854.9167 | 0.36875 | 0.36875 | 0 | 0 | 0
ZN1673:PA2 | TURRAMURRA | URBAN | 796 | 1337.2689 | 6181.3023 | 2.915 | 213.5929 | 0 | 3 | 14859.55 | 14859.55 | 0.072864 | 0.072864 | 0 | 0 | 0
ZN1673:PA7 | TURRAMURRA | URBAN | 1030 | 76.4392 | 6095.8489 | 4.3439 | 2392.1844 | 0 | 23 | 111678.65 | 78188.05 | 0.93495 | 0.85146 | 0 | 0 | 0
ZN1673:PA9 | TURRAMURRA | URBAN | 486 | 296.5943 | 5332.8923 | 3.4865 | 927.7339 | 0 | 6 | 53961.3333 | 53961.3333 | 1.1276 | 1.1276 | 0 | 0 | 0
ZN1788:PA1 | MATRAVILLE | URBAN | 871 | 0 | 6917.3303 | 1.5242 | 603.5587 | 6.3133 | 8 | 80304.5 | 77404.8 | 0.55683 | 0.55568 | 1 | 840 | 0.0022962
ZN1788:PA11 | MATRAVILLE | URBAN | 576 | 0 | 6536.6007 | 2.0957 | 867.8128 | 0 | 5 | 83973.7833 | 83973.7833 | 0.86458 | 0.86458 | 0 | 0 | 0
ZN1788:PA14 | MATRAVILLE | URBAN | 1090 | 0 | 8804.5128 | 2.7625 | 609.3924 | 0 | 6 | 44734.1667 | 43916.6833 | 1.0037 | 1.0028 | 0 | 0 | 0
ZN1788:PA15 | MATRAVILLE | URBAN | 952 | 0 | 5418.8598 | 4.2867 | 30.6172 | 0 | 3 | 1448.4167 | 1448.4167 | 0.0031513 | 0.0031513 | 0 | 0 | 0
ZN1788:PA16 | MATRAVILLE | URBAN | 46 | 0 | 10942.1701 | 3.2388 | 3.9609 | 0.95827 | 1 | 248 | 248 | 0.043478 | 0.043478 | 2 | 60 | 0.043478
ZN1788:PA17 | MATRAVILLE | URBAN | 1393 | 0 | 3587.1741 | 2.7625 | 1973.0672 | 0 | 10 | 144838.5667 | 123300.5667 | 1.3238 | 1.2369 | 0 | 0 | 0
ZN1788:PA2 | MATRAVILLE | URBAN | 1118 | 0 | 4343.9489 | 3.2388 | 136.8626 | 0 | 3 | 8569.3167 | 8569.3167 | 0.085868 | 0.085868 | 0 | 0 | 0
ZN1788:PA21 | MATRAVILLE | URBAN | 36 | 0 | 4465.0582 | 3.7151 | 42.5939 | 0 | 1 | 2325 | 2325 | 0.88889 | 0.88889 | 0 | 0 | 0
ZN1788:PA29 | MATRAVILLE | URBAN | 766 | 0 | 5557.9318 | 2.0005 | 98.1671 | 154.4794 | 3 | 9951.4667 | 9951.4667 | 0.11097 | 0.11097 | 2 | 15660 | 0.039164
ZN1788:PA30 | MATRAVILLE | URBAN | 1287 | 604.8737 | 6040.8316 | 3.3341 | 2959.791 | 0 | 16 | 180025.2167 | 177379.2167 | 0.38306 | 0.38228 | 0 | 0 | 0
ZN1788:PA32 | MATRAVILLE | URBAN | 1359 | 0 | 9942.7389 | 5.8109 | 3663.6965 | 0 | 2 | 127858.6167 | 127858.6167 | 0.98087 | 0.98087 | 0 | 0 | 0
ZN1788:PA36 | MATRAVILLE | URBAN | 653 | 0 | 5540.6387 | 2.2862 | 305.365 | 0 | 3 | 27086.2167 | 27086.2167 | 0.99081 | 0.99081 | 0 | 0 | 0
ZN1788:PA37 | MATRAVILLE | SHORT RURAL | 455 | 0 | 4490.4734 | 1.1431 | 1.3988 | 0 | 2 | 248.15 | 248.15 | 0.0043956 | 0.0043956 | 0 | 0 | 0
ZN1788:PA6 | MATRAVILLE | URBAN | 1020 | 0 | 6810.5955 | 2.7625 | 77.8782 | 0 | 3 | 5716.8667 | 5716.8667 | 0.069608 | 0.069608 | 0 | 0 | 0
ZN1788:PA8 | MATRAVILLE | URBAN | 1167 | 0 | 3740.3973 | 3.5246 | 3405.963 | 0 | 14 | 195965.0167 | 192419.1333 | 1.2365 | 1.2339 | 0 | 0 | 0
ZN180:PA10 | MOSMAN | URBAN | 1325 | 0 | 5547.0118 | 3.1245 | 1680.2094 | 2022.7028 | 5 | 109051.0667 | 109051.0667 | 1.0823 | 1.0823 | 4 | 131280 | 0.23547
ZN180:PA15 | MOSMAN | URBAN | 478 | 0 | 3288.8172 | 2.7244 | 181.5001 | 1245.3901 | 3 | 13509.8667 | 13509.8667 | 0.11506 | 0.11506 | 6 | 92700 | 0.43724
ZN180:PA16 | MOSMAN | URBAN | 581 | 0 | 2962.8951 | 1.6385 | 383.4676 | 0 | 2 | 47461.4 | 47461.4 | 0.16867 | 0.16867 | 0 | 0 | 0
ZN180:PA17 | MOSMAN | URBAN | 760 | 1469.3824 | 6183.802 | 2.8387 | 345.9731 | 897.4323 | 4 | 24715.3333 | 24715.3333 | 0.10395 | 0.10395 | 2 | 64110 | 0.19342
ZN180:PA18 | MOSMAN | URBAN | 2291 | 0 | 8721.9243 | 5.0297 | 2357.2917 | 0 | 8 | 95042.9167 | 95042.9167 | 0.20471 | 0.20471 | 0 | 0 | 0
ZN180:PA19 | MOSMAN | URBAN | 1423 | 0 | 4994.5096 | 3.6961 | 514.4702 | 0 | 5 | 28227.2667 | 28227.2667 | 0.12298 | 0.12298 | 0 | 0 | 0
ZN180:PA20 | MOSMAN | URBAN | 1510 | 0 | 6560.4552 | 3.0483 | 6.7342 | 0 | 0 | 448 | 448 | 0.00066225 | 0.00066225 | 0 | 0 | 0
ZN180:PA21 | MOSMAN | URBAN | 1946 | 0 | 6008.0665 | 4.0962 | 9366.2306 | 3321.9141 | 19 | 463699.6167 | 463699.6167 | 1.222 | 1.222 | 2 | 164460 | 0.16084
ZN180:PA22 | MOSMAN | URBAN | 1408 | 0 | 4922.2603 | 3.315 | 694.8597 | 0 | 4 | 42506.7833 | 25693.25 | 0.084517 | 0.014915 | 0 | 0 | 0
ZN180:PA23 | MOSMAN | URBAN | 1267 | 0 | 6140.2769 | 4.3439 | 5618.6357 | 0 | 14 | 262304.8833 | 262304.8833 | 0.45383 | 0.45383 | 0 | 0 | 0
ZN180:PA24 | MOSMAN | URBAN | 980 | 0 | 8223.4324 | 3.5246 | 981.4647 | 0 | 5 | 56469.4167 | 56469.4167 | 0.22959 | 0.22959 | 0 | 0 | 0
ZN180:PA27 | MOSMAN | URBAN | 1222 | 0 | 2445.8388 | 2.6482 | 614.4445 | 0 | 6 | 47052.0167 | 47052.0167 | 0.21522 | 0.21522 | 0 | 0 | 0
ZN180:PA28 | MOSMAN | URBAN | 1196 | 0 | 4249.8049 | 2.4577 | 650.0628 | 0 | 6 | 53638.4167 | 53638.4167 | 0.27508 | 0.27508 | 0 | 0 | 0
ZN180:PA29 | MOSMAN | URBAN | 2055 | 0 | 4911.6783 | 4.7058 | 889.3276 | 0 | 5 | 38324.3833 | 38324.3833 | 0.086131 | 0.086131 | 0 | 0 | 0
ZN180:PA30 | MOSMAN | URBAN | 1368 | 0 | 3998.0859 | 3.6961 | 66.1923 | 0 | 2 | 3631.75 | 3631.75 | 0.057749 | 0.057749 | 0 | 0 | 0
ZN180:PA31 | MOSMAN | URBAN | 1323 | 0 | 6150.3504 | 3.0864 | 62.8709 | 0 | 3 | 4130.9 | 4130.9 | 0.015117 | 0.015117 | 0 | 0 | 0
ZN180:PA32 | MOSMAN | URBAN | 925 | 0 | 7149.3862 | 2.8387 | 12.2243 | 0 | 2 | 873.2667 | 873.2667 | 0.0021622 | 0.0021622 | 0 | 0 | 0
ZN180:PA33 | MOSMAN | URBAN | 906 | 0 | 4788.3094 | 2.4387 | 1346.2418 | 0 | 1 | 111949.8333 | 111949.8333 | 0.27594 | 0.27594 | 0 | 0 | 0
ZN180:PA34 | MOSMAN | URBAN | 1328 | 0 | 8414.3941 | 6.0966 | 759.6141 | 0 | 12 | 25266.9833 | 25266.9833 | 0.16416 | 0.16416 | 0 | 0 | 0
ZN180:PA41 | MOSMAN | URBAN | 2117 | 0 | 10618.1819 | 4.9916 | 4192.8459 | 0 | 8 | 170340.5167 | 170340.5167 | 1.0298 | 1.0298 | 0 | 0 | 0
ZN180:PA42 | MOSMAN | URBAN | 1873 | 0 | 9329.5319 | 3.8104 | 232.9443 | 0 | 3 | 12397.45 | 12397.45 | 0.047517 | 0.047517 | 0 | 0 | 0
ZN180:PA43 | MOSMAN | URBAN | 1075 | 0 | 7447.512 | 3.4484 | 33.5431 | 0 | 3 | 1972.5833 | 1972.5833 | 0.023256 | 0.023256 | 0 | 0 | 0
ZN180:PA7 | MOSMAN | URBAN | 1444 | 0 | 5288.2376 | 2.6292 | 2335.4481 | 4466.6629 | 9 | 180136.4 | 180136.4 | 0.45499 | 0.45499 | 12 | 344520 | 0.49515
ZN180:PA9 | MOSMAN | URBAN | 747 | 0 | 4439.807 | 2.3434 | 2.46 | 0 | 0 | 212.8833 | 212.8833 | 0.0013387 | 0.0013387 | 0 | 0 | 0
ZN1850:PA10 | BASS HILL | URBAN | 860 | 5.1762 | 5454.8215 | 3.7342 | 265.8141 | 0 | 8 | 14435.5167 | 14435.5167 | 0.065116 | 0.065116 | 0 | 0 | 0
ZN1850:PA11 | BASS HILL | URBAN | 274 | 1071.198 | 3904.1537 | 1.9243 | 36.8277 | 0 | 6 | 3881.1833 | 3881.1833 | 0.091241 | 0.091241 | 0 | 0 | 0
ZN1850:PA12 | BASS HILL | URBAN | 1853 | 3959.1725 | 1758.1223 | 3.8295 | 80.2873 | 0 | 6 | 4251.6833 | 4251.6833 | 0.063681 | 0.063681 | 0 | 0 | 0
ZN1850:PA13 | BASS HILL | URBAN | 1518 | 2390.6102 | 3751.2927 | 4.1914 | 1782.7061 | 0 | 9 | 86251.65 | 86251.65 | 0.8946 | 0.8946 | 0 | 0 | 0
ZN1850:PA14 | BASS HILL | URBAN | 426 | 463.2907 | 2864.0964 | 4.02 | 740.5288 | 127.2645 | 7 | 37356.8167 | 37356.8167 | 1.3146 | 1.3146 | 2 | 6420 | 0.0093897
ZN1850:PA15 | BASS HILL | URBAN | 703 | 2831.4026 | 1496.5136 | 4.9916 | 7.0377 | 12.5534 | 0 | 285.9167 | 285.9167 | 0.0014225 | 0.0014225 | 0 | 510 | 0.0014225
ZN1850:PA3 | BASS HILL | URBAN | 1007 | 6264.6982 | 3822.6755 | 3.6389 | 2477.0471 | 0 | 2 | 138042 | 138042 | 1.996 | 1.996 | 0 | 0 | 0
ZN1850:PA9 | BASS HILL | URBAN | 353 | 24.4583 | 2997.2904 | 2.8387 | 12.6363 | 0 | 2 | 902.7 | 0 | 0.0084986 | 0 | 0 | 0 | 0
ZN187:PA10 | CROWS NEST | URBAN | 689 | 0 | 3799.2075 | 3.2769 | 711.9852 | 0 | 4 | 44060.85 | 44060.85 | 1.0363 | 1.0363 | 0 | 0 | 0
ZN187:PA13 | CROWS NEST | URBAN | 851 | 0 | 2475.8488 | 1.3336 | 928.4597 | 0 | 6 | 141180.7167 | 141180.7167 | 1.2949 | 1.2949 | 0 | 0 | 0
ZN187:PA14 | CROWS NEST | URBAN | 619 | 0 | 5174.4399 | 4.0009 | 483.8778 | 0 | 3 | 24526 | 24526 | 0.30856 | 0.30856 | 0 | 0 | 0
ZN187:PA16 | CROWS NEST | URBAN | 1347 | 0 | 4749.9388 | 3.3913 | 59.7841 | 0 | 1 | 3575 | 3575 | 0.040831 | 0.040831 | 0 | 0 | 0
ZN187:PA17 | CROWS NEST | URBAN | 1478 | 0 | 8866.1234 | 3.1245 | 3425.7666 | 0 | 12 | 222343.4167 | 222343.4167 | 2.4242 | 2.4242 | 0 | 0 | 0
ZN187:PA19 | CROWS NEST | URBAN | 149 | 0 | 2094.4588 | 0.78113 | 83.9805 | 0 | 4 | 21802.4333 | 21802.4333 | 1.047 | 1.047 | 0 | 0 | 0
ZN187:PA20 | CROWS NEST | URBAN | 2216 | 0 | 9990.5583 | 5.487 | 2002.5059 | 613.6563 | 5 | 74010.2167 | 12158.2167 | 0.30686 | 0.043321 | 1 | 22680 | 0.024368
ZN187:PA21 | CROWS NEST | URBAN | 904 | 0 | 3419.6885 | 1.8861 | 40.3814 | 0 | 1 | 4341.6667 | 4341.6667 | 0.11062 | 0.11062 | 0 | 0 | 0
ZN187:PA22 | CROWS NEST | URBAN | 1140 | 0 | 3495.4143 | 2.3053 | 455.2789 | 0 | 1 | 40050 | 0 | 0.07807 | 0 | 0 | 0 | 0
ZN187:PA28 | CROWS NEST | URBAN | 713 | 0 | 3129.9409 | 2.915 | 847.6415 | 0 | 3 | 58970 | 58970 | 1.0154 | 1.0154 | 0 | 0 | 0
ZN187:PA30 | CROWS NEST | URBAN | 1878 | 0 | 7281.4651 | 4.1343 | 679.0885 | 0 | 5 | 33310.1833 | 21619.9333 | 0.17785 | 0.16028 | 0 | 0 | 0
ZN187:PA4 | CROWS NEST | URBAN | 1089 | 0 | 5829.3642 | 3.9438 | 147.8581 | 0 | 2 | 7603 | 7603 | 0.059688 | 0.059688 | 0 | 0 | 0
ZN187:PA6 | CROWS NEST | URBAN | 40 | 0 | 4673.2426 | 1.1622 | 1.3336 | 0 | 0 | 232.7 | 232.7 | 0.025 | 0.025 | 0 | 0 | 0
ZN187:PA7 | CROWS NEST | URBAN | 673 | 0 | 1149.7166 | 3.9628 | 748.473 | 0 | 2 | 38302.15 | 38302.15 | 0.92571 | 0.92571 | 0 | 0 | 0
ZN187:PA8 | CROWS NEST | URBAN | 1028 | 0 | 2197.3377 | 4.0009 | 1208.7066 | 2130.751 | 2 | 61264.9333 | 3696.9333 | 1.0661 | 0.066148 | 1 | 108000 | 0.21887
ZN188:PA1 | ZETLAND | URBAN | 1053 | 0 | 3121.4546 | 3.8104 | 1064.928 | 0 | 5 | 56676.1833 | 56676.1833 | 0.96866 | 0.96866 | 0 | 0 | 0
ZN188:PA13 | ZETLAND | URBAN | 83 | 0 | 4101.2027 | 1.5242 | 2.3591 | 0 | 0 | 313.8833 | 313.8833 | 0.012048 | 0.012048 | 0 | 0 | 0
ZN188:PA14 | ZETLAND | URBAN | 308 | 0 | 2333.9495 | 2.0957 | 277.5801 | 0 | 1 | 26860 | 26860 | 0.98052 | 0.98052 | 0 | 0 | 0
ZN188:PA15 | ZETLAND | URBAN | 201 | 0 | 2331.354 | 1.2384 | 4.7111 | 0 | 2 | 771.4667 | 771.4667 | 0.31343 | 0.31343 | 0 | 0 | 0
ZN188:PA16 | ZETLAND | URBAN | 1013 | 0 | 1749.875 | 1.5242 | 46.7638 | 0 | 1 | 6222 | 6222 | 0.10069 | 0.10069 | 0 | 0 | 0
ZN188:PA17 | ZETLAND | URBAN | 2310 | 0 | 7032.5802 | 3.9057 | 2354.6426 | 0 | 6 | 122259.1833 | 122259.1833 | 0.72771 | 0.72771 | 0 | 0 | 0
ZN188:PA18 | ZETLAND | URBAN | 96 | 0 | 1368.441 | 0.9526 | 372.7753 | 0 | 1 | 79357.4167 | 79357.4167 | 0.88542 | 0.88542 | 0 | 0 | 0
ZN188:PA2 | ZETLAND | URBAN | 968 | 0 | 7419.3226 | 3.7151 | 316.8075 | 58.7154 | 5 | 17293.0333 | 17293.0333 | 0.11364 | 0.11364 | 4 | 3205 | 0.056818
ZN188:PA20 | ZETLAND | URBAN | 1183 | 0 | 3341.7252 | 4.6677 | 65.3693 | 0 | 2 | 2840 | 2840 | 0.010989 | 0.010989 | 0 | 0 | 0
ZN188:PA21 | ZETLAND | URBAN | 2564 | 0 | 3017.9911 | 3.6199 | 29.3005 | 0 | 3 | 1641.4667 | 1641.4667 | 0.0042902 | 0.0042902 | 0 | 0 | 0
ZN188:PA22 | ZETLAND | URBAN | 71 | 0 | 5313.0274 | 3.6199 | 0 | 4.284 | 0 | 0 | 0 | 0 | 0 | 1 | 240 | 0.028169
ZN188:PA25 | ZETLAND | URBAN | 274 | 0 | 3347.7724 | 2.9531 | 176.0256 | 0 | 2 | 12088 | 12088 | 1.0036 | 1.0036 | 0 | 0 | 0
ZN188:PA26 | ZETLAND | URBAN | 841 | 0 | 4718.5778 | 3.3341 | 349.98 | 138.1042 | 2 | 21287.05 | 21287.05 | 0.080856 | 0.080856 | 1 | 8400 | 0.041617
ZN188:PA27 | ZETLAND | URBAN | 183 | 0 | 4151.1141 | 3.4294 | 0 | 96.3911 | 0 | 0 | 0 | 0 | 0 | 3 | 5700 | 0.46995
ZN188:PA3 | ZETLAND | URBAN | 711 | 0 | 3246.9146 | 1.8099 | 4.9802 | 9.1036 | 2 | 558 | 558 | 0.0098453 | 0.0098453 | 1 | 1020 | 0.0028129
ZN188:PA33 | ZETLAND | URBAN | 57 | 0 | 2872.2733 | 2.0957 | 88.4998 | 0 | 4 | 8563.6667 | 8563.6667 | 2.8421 | 2.8421 | 0 | 0 | 0
ZN188:PA34 | ZETLAND | URBAN | 104 | 0 | 870.7038 | 0.28578 | 0.72293 | 0 | 1 | 513 | 513 | 0.086538 | 0.086538 | 0 | 0 | 0
ZN188:PA38 | ZETLAND | URBAN | 920 | 0 | 4457.1042 | 2.191 | 104.5834 | 0 | 1 | 9680 | 9680 | 0.23913 | 0.23913 | 0 | 0 | 0
ZN188:PA4 | ZETLAND | URBAN | 1396 | 0 | 3229.5083 | 2.9531 | 157.7546 | 4.8055 | 2 | 10833.3 | 10833.3 | 0.089542 | 0.089542 | 0 | 330 | 0.00071633
ZN188:PA41 | ZETLAND | URBAN | 1483 | 0 | 7728.1724 | 4.9535 | 366.4136 | 0 | 3 | 15000.6 | 14513.7333 | 0.046527 | 0.045853 | 0 | 0 | 0
ZN188:PA42 | ZETLAND | URBAN | 418 | 0 | 5688.5168 | 1.9052 | 20.6395 | 0 | 1 | 2196.9 | 2196.9 | 0.021531 | 0.021531 | 0 | 0 | 0
ZN188:PA43 | ZETLAND | URBAN | 216 | 0 | 3822.7748 | 2.4768 | 0.07328 | 0 | 0 | 6 | 6 | 0.0046296 | 0.0046296 | 0 | 0 | 0
ZN188:PA44 | ZETLAND | URBAN | 1377 | 0 | 5287.3643 | 3.2388 | 725.3332 | 0 | 3 | 45414.9667 | 45414.9667 | 0.023965 | 0.023965 | 0 | 0 | 0
ZN188:PA9 | ZETLAND | URBAN | 133 | 0 | 1273.7212 | 2.9531 | 256.9656 | 2.0096 | 2 | 17646.3 | 17646.3 | 0.22556 | 0.22556 | 2 | 138 | 0.052632
ZN195:PA11 | PYMBLE | URBAN | 1258 | 1322.5795 | 8029.8662 | 4.2295 | 3859.3512 | 41.296 | 13 | 185042.5833 | 185042.5833 | 1.1828 | 1.1828 | 2 | 1980 | 0.0031797
ZN195:PA22 | PYMBLE | URBAN | 577 | 1.4 | 3441.4708 | 3.9819 | 1556.2489 | 0 | 3 | 79258 | 79258 | 1.1127 | 1.1127 | 0 | 0 | 0
ZN195:PA23 | PYMBLE | URBAN | 492 | 0 | 4002.6601 | 1.848 | 97.8736 | 0 | 2 | 10740 | 10740 | 0.23171 | 0.23171 | 0 | 0 | 0
ZN195:PA25 | PYMBLE | URBAN | 746 | 5.0864 | 5104.6988 | 3.2198 | 141.2475 | 15.2422 | 6 | 8896.2 | 7693.85 | 0.13673 | 0.13539 | 1 | 960 | 0.002681
ZN195:PA28 | PYMBLE | URBAN | 917 | 7.4042 | 8550.5914 | 3.5246 | 779.0976 | 200.223 | 10 | 44826.05 | 9184.05 | 0.28571 | 0.088332 | 1 | 11520 | 0.034896
ZN195:PA29 | PYMBLE | URBAN | 1112 | 571.8715 | 6194.658 | 3.315 | 51.4779 | 0 | 5 | 3149.0667 | 3149.0667 | 0.073741 | 0.073741 | 0 | 0 | 0
ZN195:PA3 | PYMBLE | URBAN | 293 | 439.768 | 2273.5842 | 2.4387 | 0.68545 | 943.7536 | 0 | 57 | 57 | 0.003413 | 0.003413 | 4 | 78480 | 0.98635
ZN195:PA30 | PYMBLE | URBAN | 1187 | 5602.5815 | 6757.1064 | 4.039 | 8511.4751 | 26.2905 | 12 | 427345.6833 | 418748.5833 | 1.385 | 1.3614 | 1 | 1320 | 0.018534
ZN195:PA4 | PYMBLE | URBAN | 962 | 0 | 2931.5709 | 1.829 | 11.8647 | 0 | 1 | 1315.5167 | 1315.5167 | 0.017672 | 0.017672 | 0 | 0 | 0
ZN195:PA9 | PYMBLE | URBAN | 1231 | 4925.491 | 11227.3045 | 4.8583 | 5964.9642 | 1218.9249 | 10 | 248987.7667 | 248987.7667 | 2.0544 | 2.0544 | 2 | 50880 | 0.094232
ZN2196:PA10 | MILPERRA | URBAN | 48 | 0 | 1328.0755 | 2.3624 | 14.6785 | 0 | 1 | 1260 | 1260 | 0.20833 | 0.20833 | 0 | 0 | 0
ZN2196:PA11 | MILPERRA | URBAN | 106 | 0 | 2966.9785 | 5.6584 | 163.3814 | 0 | 2 | 5855.4 | 5855.4 | 0.21698 | 0.21698 | 0 | 0 | 0
ZN2196:PA12 | MILPERRA | URBAN | 7 | 0 | 886.3883 | 2.3434 | 3.4205 | 0 | 0 | 296 | 296 | 0.14286 | 0.14286 | 0 | 0 | 0
ZN2196:PA14 | MILPERRA | URBAN | 120 | 0 | 7377.2622 | 4.4391 | 16.3737 | 0 | 2 | 748 | 748 | 0.058333 | 0.058333 | 0 | 0 | 0
ZN2196:PA17 | MILPERRA | URBAN | 87 | 0 | 3473.3226 | 4.4772 | 182.3299 | 94.0297 | 3 | 8258.4833 | 8258.4833 | 0.34483 | 0.34483 | 4 | 4259 | 0.12644
ZN2196:PA18 | MILPERRA | URBAN | 931 | 1980.8057 | 6490.5365 | 5.6203 | 4625.9179 | 209.1913 | 7 | 166911.5 | 162626.1 | 2.0483 | 2.0354 | 1 | 7548 | 0.012889
ZN2196:PA2 | MILPERRA | URBAN | 728 | 904.6645 | 7041.6215 | 4.5534 | 14.3752 | 40.4166 | 2 | 640.2167 | 640.2167 | 0.0027473 | 0.0027473 | 2 | 1800 | 0.0054945
ZN2196:PA20 | MILPERRA | URBAN | 164 | 0 | 3803.6308 | 3.1626 | 27.8737 | 1.8715 | 3 | 1787.3 | 1787.3 | 0.02439 | 0.02439 | 1 | 120 | 0.012195
ZN2196:PA21 | MILPERRA | URBAN | 635 | 3.4999 | 2821.7617 | 1.5242 | 236.1715 | 0 | 6 | 31423.0167 | 31423.0167 | 0.45354 | 0.45354 | 0 | 0 | 0
ZN2196:PA25 | MILPERRA | URBAN | 1715 | 4085.7031 | 5456.1696 | 3.7913 | 4745.5875 | 0 | 7 | 253832.5167 | 253832.5167 | 1.5714 | 1.5714 | 0 | 0 | 0
ZN2196:PA5 | MILPERRA | URBAN | 1550 | 6353.9319 | 5594.7291 | 5.0869 | 4326.8228 | 0 | 12 | 172491.7 | 158396 | 1.1677 | 1.1477 | 0 | 0 | 0
ZN2196:PA6 | MILPERRA | URBAN | 63 | 0 | 2007.2369 | 3.2007 | 62.9755 | 97.541 | 3 | 3990 | 3990 | 0.31746 | 0.31746 | 1 | 6180 | 0.031746
ZN2196:PA9 | MILPERRA | URBAN | 1392 | 1027.0417 | 5788.0593 | 4.1914 | 51.9848 | 0 | 3 | 2515.15 | 2515.15 | 0.0021552 | 0.0021552 | 0 | 0 | 0
ZN2310:PA10 | PUNCHBOWL | URBAN | 1176 | 0 | 4414.78 | 2.0195 | 46.0498 | 0 | 6 | 4624.15 | 4624.15 | 0.030612 | 0.030612 | 0 | 0 | 0
ZN2310:PA11 | PUNCHBOWL | URBAN | 608 | 0 | 3143.5427 | 3.0674 | 75.172 | 0 | 3 | 4969.8167 | 4969.8167 | 0.046053 | 0.046053 | 0 | 0 | 0
ZN2310:PA16 | PUNCHBOWL | URBAN | 979 | 0 | 5236.8107 | 1.848 | 284.4628 | 0 | 2 | 31215.05 | 31215.05 | 0.99387 | 0.99387 | 0 | 0 | 0
ZN2310:PA17 | PUNCHBOWL | URBAN | 1133 | 0 | 6375.0238 | 3.0293 | 262.0472 | 0 | 6 | 17542.55 | 9323.4167 | 0.1271 | 0.054722 | 0 | 0 | 0
ZN2310:PA20 | PUNCHBOWL | URBAN | 1734 | 0 | 7786.9483 | 3.4675 | 21.1547 | 743.277 | 4 | 1237.2167 | 1237.2167 | 0.0028835 | 0.0028835 | 1 | 43470 | 0.039792
ZN2310:PA21 | PUNCHBOWL | URBAN | 1353 | 0 | 4183.3895 | 2.7435 | 209.6253 | 0 | 3 | 15495 | 15495 | 0.18551 | 0.18551 | 0 | 0 | 0
ZN2310:PA22 | PUNCHBOWL | URBAN | 786 | 0 | 1897.1618 | 1.4861 | 102.894 | 0 | 6 | 14041.25 | 14041.25 | 0.3117 | 0.3117 | 0 | 0 | 0
ZN2310:PA23 | PUNCHBOWL | URBAN | 2 | 0 | 1263.215 | 2.6482 | 2.9382 | 7.8353 | 2 | 225 | 225 | 1.5 | 1.5 | 0 | 600 | 0.5
ZN2310:PA25 | PUNCHBOWL | URBAN | 1518 | 0 | 5906.7977 | 3.0483 | 350.0104 | 0 | 8 | 23284.7333 | 6374.45 | 0.094203 | 0.065217 | 0 | 0 | 0
ZN2310:PA26 | PUNCHBOWL | URBAN | 1192 | 0 | 7353.018 | 2.6292 | 83.3454 | 0 | 2 | 6428.55 | 6428.55 | 0.05453 | 0.05453 | 0 | 0 | 0
ZN2310:PA27 | PUNCHBOWL | URBAN | 1918 | 0 | 6386.2562 | 3.1245 | 904.6924 | 0 | 8 | 58717.4833 | 58151.5333 | 0.21898 | 0.21846 | 0 | 0 | 0
ZN2310:PA28 | PUNCHBOWL | URBAN | 2446 | 6817.6869 | 2648.3138 | 4.6677 | 3938.1948 | 0 | 9 | 171096.6333 | 171096.6333 | 1.1055 | 1.1055 | 0 | 0 | 0
ZN2310:PA3 | PUNCHBOWL | URBAN | 2445 | 0 | 7650.783 | 3.7532 | 17.894 | 0 | 4 | 966.8333 | 966.8333 | 0.001636 | 0.001636 | 0 | 0 | 0
ZN2310:PA33 | PUNCHBOWL | URBAN | 1818 | 0 | 9616.0145 | 3.9438 | 2609.6454 | 32.6715 | 7 | 134190.4167 | 134190.4167 | 1.1177 | 1.1177 | 1 | 1680 | 0.0038504
ZN2310:PA34 | PUNCHBOWL | URBAN | 2204 | 0 | 10492.3718 | 4.4201 | 6112.2589 | 876.2009 | 7 | 280429.7667 | 280429.7667 | 1.0354 | 1.0354 | 1 | 40200 | 0.030399
ZN2310:PA37 | PUNCHBOWL | URBAN | 905 | 0 | 5908.8571 | 2.8578 | 209.7874 | 0 | 5 | 14886.7 | 14886.7 | 0.25856 | 0.25856 | 0 | 0 | 0
ZN2310:PA38 | PUNCHBOWL | URBAN | 1743 | 4663.9825 | 2566.318 | 3.8295 | 1304.6669 | 0 | 12 | 69089.8 | 69089.8 | 0.21974 | 0.21974 | 0 | 0 | 0
ZN2310:PA4 | PUNCHBOWL | URBAN | 1031 | 0 | 4702.0245 | 2.7435 | 131.5609 | 0 | 6 | 9724.6667 | 9724.6667 | 0.11833 | 0.11833 | 0 | 0 | 0
ZN2310:PA40 | PUNCHBOWL | URBAN | 1589 | 0 | 7211.9369 | 3.3532 | 292.7286 | 0 | 6 | 17703.65 | 13135.4 | 0.086847 | 0.067967 | 0 | 0 | 0
ZN2400:PA11 | BEROWRA | SHORT RURAL | 688 | 21376.3582 | 1746.8787 | 1.7337 | 1228.4949 | 118.7499 | 5 | 143695.2167 | 143695.2167 | 0.21221 | 0.21221 | 2 | 13890 | 0.094477
ZN2400:PA15 | BEROWRA | URBAN | 1218 | 4069.6395 | 9139.1382 | 5.3727 | 7245.4694 | 42.9194 | 12 | 273481.3833 | 101873.3833 | 1.0985 | 0.19787 | 1 | 1620 | 0.0049261
ZN2400:PA18 | BEROWRA | SHORT RURAL | 1296 | 17023.1739 | 3811.5917 | 5.8871 | 8035.9127 | 7156.7999 | 24 | 276813.3833 | 66733.75 | 1.2917 | 0.32716 | 8 | 246530.55 | 0.40664
ZN2400:PA21 | BEROWRA | URBAN | 1450 | 10393.2901 | 3983.1325 | 4.6296 | 16504.4422 | 164.3722 | 11 | 722944.45 | 605312.45 | 0.96966 | 0.52552 | 4 | 7200 | 0.014483
ZN2400:PA23 | BEROWRA | URBAN | 311 | 1959.1089 | 3443.7966 | 2.2291 | 167.7182 | 0 | 2 | 15258.25 | 15258.25 | 0.038585 | 0.038585 | 0 | 0 | 0
ZN2400:PA26 | BEROWRA | URBAN | 963 | 5012.8834 | 2040.6166 | 2.9531 | 6069.0068 | 0 | 11 | 416769.8333 | 416143.8333 | 4.3499 | 4.3458 | 0 | 0 | 0
ZN2466:PA15 | FLEMINGTON | URBAN | 362 | 0 | 4944.0868 | 4.8773 | 9.1634 | 580.1054 | 1 | 381 | 381 | 0.0082873 | 0.0082873 | 1 | 24120 | 0.18508
ZN2466:PA16 | FLEMINGTON | URBAN | 1542 | 0 | 6850.9914 | 4.4772 | 1218.0768 | 83.4544 | 9 | 55171.8 | 54928.8 | 0.17834 | 0.17769 | 1 | 3780 | 0.011673
ZN2466:PA20 | FLEMINGTON | URBAN | 1004 | 0 | 9148.923 | 4.7439 | 3635.0531 | 0 | 7 | 155389.5333 | 155389.5333 | 1.1394 | 1.1394 | 0 | 0 | 0
ZN2466:PA27 | FLEMINGTON | URBAN | 95 | 0 | 4612.232 | 3.315 | 13.4046 | 0 | 2 | 820 | 820 | 0.042105 | 0.042105 | 0 | 0 | 0
ZN2466:PA29 | FLEMINGTON | URBAN | 13 | 0 | 885.6877 | 4.0581 | 1.5098 | 0 | 0 | 75.45 | 75.45 | 0.076923 | 0.076923 | 0 | 0 | 0
ZN2466:PA30 | FLEMINGTON | URBAN | 1778 | 0 | 6286.1089 | 2.7816 | 616.7306 | 0 | 4 | 44962.7667 | 44962.7667 | 0.12148 | 0.12148 | 0 | 0 | 0
ZN2466:PA32 | FLEMINGTON | URBAN | 22 | 0 | 1702.097 | 2.5911 | 16.9155 | 0 | 2 | 1323.9 | 1323.9 | 1 | 1 | 0 | 0 | 0
ZN2466:PA41 | FLEMINGTON | URBAN | 1118 | 0 | 8776.9157 | 3.9057 | 509.7057 | 1634.9333 | 6 | 26465.25 | 26465.25 | 0.028623 | 0.028623 | 6 | 84890 | 0.18873
ZN2466:PA44 | FLEMINGTON | URBAN | 16 | 0 | 1555.8678 | 3.2388 | 1.2915 | 57.0173 | 0 | 80.8667 | 80.8667 | 0.0625 | 0.0625 | 1 | 3570 | 0.4375
ZN2466:PA45 | FLEMINGTON | URBAN | 1374 | 0 | 8514.3112 | 3.8104 | 1391.5736 | 0 | 7 | 74060.4833 | 35648.7167 | 0.23362 | 0.15066 | 0 | 0 | 0
ZN2466:PA5 | FLEMINGTON | URBAN | 1141 | 0 | 6800.6675 | 3.4103 | 2165.071 | 0 | 10 | 128744.7333 | 128744.7333 | 0.36985 | 0.36985 | 0 | 0 | 0
ZN2466:PA6 | FLEMINGTON | URBAN | 23 | 0 | 2464.2409 | 2.4196 | 20.4328 | 0 | 2 | 1712.5167 | 1712.5167 | 1.0435 | 1.0435 | 0 | 0 | 0
ZN2473:PA1 | NORTH SYDNEY | URBAN | 347 | 0 | 1443.2033 | 2.0195 | 0 | 242.5899 | 0 | 0 | 0 | 0 | 0 | 2 | 24360 | 0.16715
ZN2473:PA11 | NORTH SYDNEY | URBAN | 523 | 0 | 5232.1989 | 4.7058 | 53.5578 | 434.4026 | 2 | 2308 | 123 | 0.011472 | 0.001912 | 1 | 18720 | 0.045889
ZN2473:PA14 | NORTH SYDNEY | URBAN | 476 | 0 | 1969.9204 | 3.6961 | 0 | 54.678 | 0 | 0 | 0 | 0 | 0 | 2 | 3000 | 0.012605
ZN2473:PA15 | NORTH SYDNEY | URBAN | 442 | 0 | 3615.4224 | 5.9442 | 992.42 | 386.9173 | 3 | 33857.2167 | 33857.2167 | 1.1719 | 1.1719 | 1 | 13200 | 0.24887
ZN2473:PA20 | NORTH SYDNEY | URBAN | 844 | 0 | 4692.8686 | 8.078 | 353.528 | 2050.6618 | 1 | 8875 | 8875 | 0.084123 | 0.084123 | 3 | 51480 | 0.16943
ZN2473:PA21 | NORTH SYDNEY | URBAN | 1892 | 0 | 4401.5138 | 4.2105 | 4962.5975 | 0 | 4 | 239016.0833 | 237664.5 | 1.0597 | 1.0592 | 0 | 0 | 0
ZN2473:PA22 | NORTH SYDNEY | SHORT RURAL | 154 | 0 | 5642.8422 | 1.4861 | 0 | 571.8022 | 0 | 0 | 0 | 0 | 0 | 1 | 78030 | 0.99351
ZN2473:PA25 | NORTH SYDNEY | URBAN | 1286 | 0 | 3446.6573 | 3.0293 | 990.2612 | 0 | 2 | 66292.2833 | 66292.2833 | 1.0109 | 1.0109 | 0 | 0 | 0
ZN2473:PA26 | NORTH SYDNEY | URBAN | 628 | 0 | 3644.7046 | 5.9633 | 1464.1235 | 4940.1856 | 4 | 49790.1833 | 49790.1833 | 0.3965 | 0.3965 | 4 | 168000 | 0.51433
ZN2473:PA27 | NORTH SYDNEY | URBAN | 221 | 0 | 648.3798 | 6.8397 | 0 | 3249.9815 | 0 | 0 | 0 | 0 | 0 | 2 | 96360 | 0.28507
ZN2473:PA3 | NORTH SYDNEY | URBAN | 112 | 0 | 479.3254 | 3.7723 | 1.8044 | 0 | 0 | 97 | 97 | 0.0089286 | 0.0089286 | 0 | 0 | 0
ZN2473:PA31 | NORTH SYDNEY | URBAN | 2188 | 0 | 7072.9664 | 4.4391 | 2894.3664 | 1811.1778 | 4 | 132223.2833 | 132223.2833 | 0.045704 | 0.045704 | 2 | 82740 | 0.090037
ZN2473:PA32 | NORTH SYDNEY | URBAN | 1897 | 0 | 5222.3057 | 3.4294 | 811.943 | 730.5432 | 9 | 48013.5 | 48013.5 | 0.19294 | 0.19294 | 3 | 43200 | 0.079072
ZN2473:PA34 | NORTH SYDNEY | URBAN | 176 | 0 | 879.8468 | 4.1152 | 0 | 1233.4004 | 0 | 0 | 0 | 0 | 0 | 2 | 60780 | 0.94318
ZN2473:PA4 | NORTH SYDNEY | URBAN | 438 | 0 | 1900.3637 | 2.7244 | 232.1761 | 0 | 3 | 17281.9167 | 17281.9167 | 0.42922 | 0.42922 | 0 | 0 | 0
ZN2473:PA41 | NORTH SYDNEY | URBAN | 836 | 0 | 3523.2205 | 5.9823 | 5.7033 | 679.6757 | 0 | 193.3333 | 193.3333 | 0.0011962 | 0.0011962 | 1 | 23040 | 0.038278
ZN2473:PA42 | NORTH SYDNEY | URBAN | 729 | 0 | 3975.9527 | 3.7151 | 393.9943 | 219.8394 | 2 | 21506.3 | 21506.3 | 0.107 | 0.107 | 1 | 12000 | 0.027435
ZN2473:PA9 | NORTH SYDNEY | URBAN | 1906 | 0 | 3434.1945 | 5.0869 | 1060.7121 | 1053.538 | 8 | 42286 | 42286 | 0.067156 | 0.067156 | 1 | 42000 | 0.052466
ZN2568:PA14 | ST PETERS | URBAN | 1373 | 0 | 7342.4689 | 6.1919 | 1121.5167 | 0 | 6 | 36731 | 36731 | 0.15732 | 0.15732 | 0 | 0 | 0
ZN2568:PA16 | ST PETERS | URBAN | 1431 | 0 | 1430.1952 | 1.5242 | 149.2605 | 6.9898 | 6 | 19859.3667 | 19859.3667 | 0.091544 | 0.091544 | 1 | 930 | 0.021663
ZN2568:PA19 | ST PETERS | URBAN | 1022 | 0 | 6506.7966 | 4.0962 | 51.0023 | 0 | 1 | 2525 | 2525 | 0.024462 | 0.024462 | 0 | 0 | 0
ZN2568:PA21 | ST PETERS | URBAN | 549 | 0 | 2504.1477 | 2.2862 | 0.5464 | 8.7936 | 0 | 48.4667 | 48.4667 | 0.0018215 | 0.0018215 | 2 | 780 | 0.003643
ZN2568:PA22 | ST PETERS | URBAN | 656 | 0 | 1581.5482 | 0.76208 | 8.3767 | 0 | 3 | 2229.0667 | 936.9333 | 0.012195 | 0.010671 | 0 | 0 | 0
ZN2568:PA25 | ST PETERS | URBAN | 288 | 0 | 3654.8163 | 2.9531 | 8.3202 | 0 | 2 | 571.3667 | 571.3667 | 0.0069444 | 0.0069444 | 0 | 0 | 0
ZN2568:PA26 | ST PETERS | URBAN | 2312 | 0 | 5588.9067 | 3.1436 | 88.4794 | 0 | 6 | 5707.8 | 5707.8 | 0.012976 | 0.012976 | 0 | 0 | 0
ZN2568:PA27 | ST PETERS | URBAN | 1953 | 0 | 6273.1812 | 3.8104 | 1353.6178 | 574.9646 | 10 | 72040.45 | 72040.45 | 0.23041 | 0.23041 | 1 | 30600 | 0.043523
ZN2568:PA28 | ST PETERS | URBAN | 251 | 0 | 3851.1836 | 4.2867 | 191.7676 | 0 | 1 | 9072 | 9072 | 1.004 | 1.004 | 0 | 0 | 0
ZN2568:PA29 | ST PETERS | URBAN | 1803 | 0 | 4795.1009 | 3.4294 | 3528.058 | 0 | 15 | 208628.4667 | 208628.4667 | 1.0715 | 1.0715 | 0 | 0 | 0
ZN2568:PA30 | ST PETERS | URBAN | 122 | 0 | 2654.6975 | 3.8104 | 42.7941 | 0 | 3 | 2277.5333 | 2277.5333 | 0.090164 | 0.090164 | 0 | 0 | 0
ZN2568:PA32 | ST PETERS | URBAN | 2318 | 0 | 3913.6625 | 3.0483 | 5524.9018 | 2304.3677 | 10 | 367548.7333 | 335652.2833 | 2.154 | 2.0785 | 2 | 153300 | 0.15746
ZN2568:PA38 | ST PETERS | URBAN | 260 | 0 | 3926.8536 | 1.8099 | 4.3169 | 0 | 0 | 483.6833 | 483.6833 | 0.0038462 | 0.0038462 | 0 | 0 | 0
ZN2568:PA39 | ST PETERS | URBAN | 1030 | 0 | 3557.9634 | 2.2862 | 19.3635 | 0 | 3 | 1717.5667 | 1717.5667 | 0.0029126 | 0.0029126 | 0 | 0 | 0
ZN2568:PA40 | ST PETERS | URBAN | 337 | 0 | 3267.879 | 2.0957 | 83.6738 | 0 | 5 | 8096.6833 | 8096.6833 | 0.15134 | 0.15134 | 0 | 0 | 0
ZN2568:PA42 | ST PETERS | URBAN | 300 | 0 | 4909.963 | 2.0005 | 205.795 | 0 | 3 | 20862 | 20862 | 0.45667 | 0.45667 | 0 | 0 | 0
ZN2568:PA8 | ST PETERS | URBAN | 3 | 0 | 4948.9213 | 2.6673 | 3.0383 | 29.9883 | 1 | 231 | 231 | 1 | 1 | 2 | 2280 | 0.66667
ZN2568:PA9 | ST PETERS | URBAN | 1236 | 0 | 4213.6622 | 3.8104 | 997.9092 | 153.6057 | 10 | 53109.4 | 53109.4 | 0.2144 | 0.2144 | 1 | 8175 | 0.088188
ZN2602:PA10 | CLOVELLY | URBAN | 723 | 0 | 3219.3285 | 1.4289 | 277.4122 | 0 | 2 | 39370.8333 | 39370.8333 | 1 | 1 | 0 | 0 | 0
ZN2602:PA15 | CLOVELLY | URBAN | 2051 | 0 | 6361.9976 | 4.382 | 442.8658 | 0 | 10 | 20495.3167 | 7664.2667 | 0.055583 | 0.027304 | 0 | 0 | 0
ZN2602:PA17 | CLOVELLY | URBAN | 1537 | 0 | 4424.6324 | 2.0957 | 110.7907 | 0 | 4 | 10720.65 | 866.3 | 0.081978 | 0.0019519 | 0 | 0 | 0
ZN2602:PA18 | CLOVELLY | URBAN | 1207 | 0 | 2593.7083 | 3.5246 | 2119.1586 | 0 | 4 | 121927.6167 | 117839.95 | 1.0762 | 1.0389 | 0 | 0 | 0
ZN2602:PA19 | CLOVELLY | URBAN | 1 | 0 | 2170.8738 | 4.0962 | 0 | 1.8179 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 1
ZN2602:PA20 | CLOVELLY | URBAN | 1475 | 0 | 5039.5335 | 3.3341 | 24.8637 | 0 | 4 | 1512.3 | 1512.3 | 0.0027119 | 0.0027119 | 0 | 0 | 0
ZN2602:PA21 | CLOVELLY | URBAN | 3198 | 0 | 7566.0184 | 3.8104 | 783.5477 | 6.7643 | 14 | 41700.9333 | 39994.9 | 0.087242 | 0.086617 | 0 | 360 | 0.0003127
ZN2602:PA22 | CLOVELLY | URBAN | 1644 | 0 | 2208.2355 | 3.8104 | 101.967 | 0 | 4 | 5426.75 | 1732.75 | 0.0054745 | 0.0018248 | 0 | 0 | 0
ZN2602:PA27 | CLOVELLY | URBAN | 1776 | 0 | 6104.1547 | 3.8104 | 867.8085 | 0 | 6 | 46185.35 | 40564.8167 | 0.11993 | 0.088401 | 0 | 0 | 0
ZN2602:PA29 | CLOVELLY | URBAN | 2203 | 0 | 6424.3728 | 4.0962 | 2223.8672 | 0 | 1 | 110098.3333 | 110098.3333 | 0.045393 | 0.045393 | 0 | 0 | 0
ZN2602:PA30 | CLOVELLY | URBAN | 1914 | 0 | 5779.7866 | 5.0488 | 9230.135 | 0 | 8 | 370742.6333 | 370742.6333 | 1.0925 | 1.0925 | 0 | 0 | 0
ZN2602:PA31 | CLOVELLY | URBAN | 1183 | 0 | 3378.0414 | 4.0962 | 964.0055 | 0 | 5 | 47725.6 | 47725.6 | 0.19189 | 0.19189 | 0 | 0 | 0
ZN2602:PA32 | CLOVELLY | URBAN | 985 | 0 | 5399.6598 | 3.9057 | 2.3882 | 0 | 0 | 124 | 124 | 0.0010152 | 0.0010152 | 0 | 0 | 0
ZN2602:PA33 | CLOVELLY | URBAN | 1519 | 0 | 3021.1743 | 2.9531 | 11.6957 | 0 | 0 | 803.1667 | 803.1667 | 0.00065833 | 0.00065833 | 0 | 0 | 0
ZN2602:PA34 | CLOVELLY | URBAN | 1245 | 0 | 3044.0542 | 3.1436 | 650.89 | 0 | 3 | 41988.85 | 41988.85 | 0.093976 | 0.093976 | 0 | 0 | 0
ZN2602:PA35 | CLOVELLY | URBAN | 1014 | 0 | 4360.1026 | 2.191 | 101.5028 | 0 | 5 | 9394.8667 | 996.8667 | 0.089744 | 0.0029586 | 0 | 0 | 0
ZN2602:PA36 | CLOVELLY | URBAN | 1227 | 0 | 6954.2593 | 4.2867 | 55.1438 | 44.3906 | 6 | 2608.7 | 2608.7 | 0.010595 | 0.010595 | 1 | 2100 | 0.004075
ZN2602:PA4 | CLOVELLY | URBAN | 1765 | 0 | 3617.3698 | 3.6199 | 1453.7913 | 0 | 7 | 81443.95 | 81443.95 | 1.0725 | 1.0725 | 0 | 0 | 0
ZN2602:PA41 | CLOVELLY | URBAN | 1440 | 0 | 3991.4048 | 3.3341 | 1191.2885 | 0 | 9 | 72458.4833 | 71818.7 | 1.134 | 1.1333 | 0 | 0 | 0
ZN2602:PA42 | CLOVELLY | URBAN | 1017 | 0 | 7893.309 | 2.4768 | 634.7984 | 0 | 5 | 51976 | 51976 | 0.40905 | 0.40905 | 0 | 0 | 0
ZN2602:PA8 | CLOVELLY | URBAN | 1353 | 0 | 6856.6917 | 4.1914 | 704.6591 | 0 | 3 | 34093.1167 | 8843.5167 | 0.12786 | 0.064302 | 0 | 0 | 0
ZN2602:PA9 | CLOVELLY | URBAN | 1041 | 0 | 3691.141 | 2.7625 | 9.2406 | 0 | 3 | 678.3333 | 558.7667 | 0.0028818 | 0.0019212 | 0 | 0 | 0
ZN262:PA13 | MARRICKVILLE | URBAN | 23 | 0 | 2805.1848 | 1.4289 | 22.0031 | 0 | 2 | 3122.7167 | 3122.7167 | 1.0435 | 1.0435 | 0 | 0 | 0
ZN262:PA14 | MARRICKVILLE | URBAN | 20 | 0 | 1487.3052 | 0.76208 | 9.5452 | 0 | 1 | 2540 | 2540 | 1 | 1 | 0 | 0 | 0
ZN262:PA15 | MARRICKVILLE | URBAN | 2407 | 0 | 8032.2928 | 4.1914 | 7539.0668 | 0 | 5 | 364758.3667 | 364758.3667 | 1.0403 | 1.0403 | 0 | 0 | 0
ZN262:PA16 | MARRICKVILLE | URBAN | 1879 | 3.3502 | 7222.4914 | 4.2867 | 5241.7299 | 8.8781 | 7 | 247971.9 | 247971.9 | 1.0346 | 1.0346 | 0 | 420 | 0.0005322
ZN262:PA17 | MARRICKVILLE | URBAN | 1599 | 0 | 4198.8949 | 2.572 | 4514.8449 | 0 | 4 | 355974.9333 | 355974.9333 | 2.0957 | 2.0957 | 0 | 0 | 0
ZN262:PA19 | MARRICKVILLE | URBAN | 2194 | 0 | 10068.1832 | 4.0009 | 6409.1 | 0 | 6 | 324853.9167 | 324853.9167 | 1.0962 | 1.0962 | 0 | 0 | 0
ZN262:PA20 | MARRICKVILLE | URBAN | 623 | 0 | 3675.5123 | 2.2862 | 969.1394 | 0 | 4 | 85963.75 | 85963.75 | 1.061 | 1.061 | 0 | 0 | 0
ZN262:PA21 | MARRICKVILLE | URBAN | 127 | 0 | 1595.3446 | 2.4768 | 193.8861 | 0 | 1 | 15875 | 15875 | 0.98425 | 0.98425 | 0 | 0 | 0
ZN262:PA25 | MARRICKVILLE | URBAN | 145 | 0 | 3596.6756 | 1.2384 | 112.0072 | 0 | 2 | 18341.8333 | 18341.8333 | 1 | 1 | 0 | 0 | 0
ZN262:PA26 | MARRICKVILLE | URBAN | 307 | 0 | 2598.0205 | 1.8099 | 406.1101 | 0 | 2 | 45502 | 45502 | 1.1173 | 1.1173 | 0 | 0 | 0
ZN262:PA27 | MARRICKVILLE | URBAN | 1064 | 0 | 3899.3976 | 3.0483 | 2030.4636 | 0 | 2 | 135078.3 | 135078.3 | 1.015 | 1.015 | 0 | 0 | 0
ZN262:PA28 | MARRICKVILLE | URBAN | 151 | 0 | 3997.2768 | 2.6673 | 246.6147 | 0 | 1 | 18750 | 18750 | 0.99338 | 0.99338 | 0 | 0 | 0
ZN262:PA29 | MARRICKVILLE | URBAN | 418 | 0 | 1853.3717 | 1.0479 | 446.0309 | 0 | 3 | 86320.2333 | 86320.2333 | 1.9617 | 1.9617 | 0 | 0 | 0
ZN262:PA30 | MARRICKVILLE | URBAN | 1952 | 0 | 8073.0801 | 4.382 | 5454.615 | 0 | 8 | 252433.2833 | 252433.2833 | 1.0394 | 1.0394 | 0 | 0 | 0
ZN262:PA31 | MARRICKVILLE | URBAN | 1353 | 0 | 4231.8665 | 2.6673 | 2262.0322 | 0 | 8 | 171981.25 | 171981.25 | 1.003 | 1.003 | 0 | 0 | 0
ZN262:PA32 | MARRICKVILLE | URBAN | 801 | 0 | 6633.8766 | 2.572 | 1486.2168 | 0 | 4 | 117181.4167 | 117181.4167 | 1.1985 | 1.1985 | 0 | 0 | 0
ZN262:PA33 | MARRICKVILLE | URBAN | 175 | 0 | 2350.1515 | 1.5242 | 165.7194 | 0 | 3 | 22049.25 | 22049.25 | 1 | 1 | 0 | 0 | 0
ZN262:PA34 | MARRICKVILLE | URBAN | 399 | 0.39743 | 4826.4767 | 2.4768 | 1112.5434 | 0 | 10 | 91092.7833 | 89936.85 | 1.5815 | 1.5714 | 0 | 0 | 0
ZN262:PA39 | MARRICKVILLE | URBAN | 736 | 0 | 1242.4117 | 2.7625 | 1253.0136 | 0 | 2 | 91981 | 91981 | 1.0014 | 1.0014 | 0 | 0 | 0
ZN262:PA40 | MARRICKVILLE | URBAN | 521 | 0 | 2673.338 | 1.7147 | 770.6847 | 0 | 5 | 91147.4667 | 91147.4667 | 2.1651 | 2.1651 | 0 | 0 | 0
ZN262:PA41 | MARRICKVILLE | URBAN | 1151 | 0 | 6488.7366 | 2.0957 | 1343.4629 | 0 | 1 | 130000 | 130000 | 0.90356 | 0.90356 | 0 | 0 | 0
ZN262:PA42 | MARRICKVILLE | URBAN | 2038 | 0 | 8103.4403 | 3.8104 | 5219.6109 | 0 | 9 | 277791.2 | 277377.7833 | 1.0564 | 1.0559 | 0 | 0 | 0
ZN262:PA5 | MARRICKVILLE | URBAN | 1474 | 0 | 6461.4424 | 3.2388 | 3693.2254 | 0 | 10 | 231242.2833 | 231242.2833 | 1.2585 | 1.2585 | 0 | 0 | 0
ZN262:PA6 | MARRICKVILLE | URBAN | 1258 | 0 | 6339.7729 | 2.8578 | 2997.721 | 0 | 7 | 212720.9667 | 202373.7667 | 1.1765 | 1.1304 | 0 | 0 | 0
ZN262:PA7 | MARRICKVILLE | URBAN | 2245 | 0 | 8529.1879 | 3.6199 | 5382.7959 | 0 | 7 | 301553.7 | 301553.7 | 1.0561 | 1.0561 | 0 | 0 | 0
ZN262:PA8 | MARRICKVILLE | URBAN | 118 | 0 | 1543.2987 | 2.3815 | 169.577 | 0 | 1 | 14440 | 14440 | 0.9661 | 0.9661 | 0 | 0 | 0
ZN263:PA31 32GHJ | DALLEY ST | CBD | 686 | 0 | 4820.8601 | 13.5841 | 4425.4475 | 165.7885 | 5 | 66066 | 66066 | 0.30612 | 0.30612 | 1 | 2475 | 0.24052
ZN263:PA33 34ABC | DALLEY ST | CBD | 261 | 0 | 4464.1207 | 11.6027 | 7.8165 | 0 | 0 | 136.6167 | 136.6167 | 0.0038314 | 0.0038314 | 0 | 0 | 0
ZN263:PA33 34DEF | DALLEY ST | CBD | 1054 | 0 | 10988.9958 | 13.0506 | 39.4215 | 579.1922 | 2 | 612.5667 | 612.5667 | 0.0018975 | 0.0018975 | 1 | 9000 | 0.0056926
ZN263:PA33 34GHJ | DALLEY ST | CBD | 555 | 0 | 3973.5722 | 12.5553 | 0 | 295.3204 | 0 | 0 | 0 | 0 | 0 | 2 | 4770 | 0.018018
ZN263:PA33 34KLM | DALLEY ST | CBD | 1010 | 0 | 7221.3176 | 15.4131 | 9765.8788 | 0 | 2 | 128491.1333 | 128491.1333 | 0.075248 | 0.075248 | 0 | 0 | 0
ZN263:PA35 37DEF | DALLEY ST | CBD | 257 | 0 | 4671.3181 | 11.3359 | 0 | 436.0148 | 0 | 0 | 0 | 0 | 0 | 1 | 7800 | 0.050584
ZN263:PA35 37GHJ | DALLEY ST | CBD | 266 | 0 | 4174.8762 | 9.6403 | 0 | 25.6705 | 0 | 0 | 0 | 0 | 0 | 1 | 540 | 0.011278
ZN263:PA35 37KLM | DALLEY ST | CBD | 299 | 0 | 2333.025 | 6.9159 | 0 | 11417.7814 | 0 | 0 | 0 | 0 | 0 | 1 | 334800 | 0.51839
ZN2635:PA1 | EPPING | URBAN | 1622 | 0 | 0 | 4.0009 | 1093.0302 | 0 | 9 | 55401.7167 | 55401.7167 | 0.14242 | 0.14242 | 0 | 0 | 0
ZN2635:PA10 | EPPING | URBAN | 2280 | 3603.2014 | 9599.6331 | 5.5822 | 8892.1262 | 0 | 4 | 323034.0833 | 323034.0833 | 2.0167 | 2.0167 | 0 | 0 | 0
ZN2635:PA11 | EPPING | SHORT RURAL | 172 | 0 | 0 | 0.4382 | 0.45809 | 0 | 1 | 212 | 212 | 0.023256 | 0.023256 | 0 | 0 | 0
ZN2635:PA12 | EPPING | SHORT RURAL | 907 | 2268.334 | 7653.8459 | 3.1817 | 1534.643 | 0 | 5 | 97814.05 | 97814.05 | 1.0518 | 1.0518 | 0 | 0 | 0
ZN2635:PA16 | EPPING | URBAN | 1234 | 1840.303 | 5418.5533 | 4.4772 | 576.231 | 2420.8403 | 11 | 26099.9167 | 26099.9167 | 0.15397 | 0.15397 | 2 | 109650 | 0.1953
ZN2635:PA17 | EPPING | URBAN | 2541 | 2803.6162 | 10105.6084 | 5.8299 | 7173.6847 | 1155.6788 | 15 | 249534.85 | 249067.5667 | 0.37938 | 0.37898 | 2 | 40200 | 0.042109
ZN2635:PA18 | EPPING | URBAN | 380 | 0 | 4003.1921 | 3.1436 | 0 | 1097.5059 | 0 | 0 | 0 | 0 | 0 | 5 | 70800 | 0.27895
ZN2635:PA19 | EPPING | URBAN | 333 | 3.0774 | 5767.2866 | 4.5915 | 1412.1477 | 29.8869 | 2 | 62369.6667 | 62369.6667 | 0.31231 | 0.31231 | 2 | 1320 | 0.012012
ZN2635:PA2 | EPPING | URBAN | 251 | 0 | 0 | 2.9912 | 0 | 346.9178 | 0 | 0 | 0 | 0 | 0 | 2 | 23520 | 0.28287
ZN2635:PA20 | EPPING | URBAN | 496 | 0 | 3691.0996 | 3.3722 | 0 | 5414.6949 | 0 | 0 | 0 | 0 | 0 | 7 | 325620 | 1.621
ZN2635:PA21 | EPPING | URBAN | 1343 | 4007.7529 | 1856.5047 | 3.5437 | 3902.9858 | 0 | 15 | 223354.3333 | 208530.7333 | 1.4118 | 1.3388 | 0 | 0 | 0
ZN2635:PA28 | EPPING | URBAN | 274 | 0 | 5128.543 | 4.1724 | 0 | 104.4578 | 0 | 0 | 0 | 0 | 0 | 4 | 5077 | 0.076642
ZN2635:PA3 | EPPING | URBAN | 530 | 2249.9264 | 2211.4754 | 2.5149 | 2.8366 | 0 | 2 | 228.7333 | 228.7333 | 0.0037736 | 0.0037736 | 0 | 0 | 0
ZN2635:PA4 | EPPING | URBAN | 538 | 2117.035 | 1680.7085 | 1.7528 | 23.6206 | 0 | 5 | 2732.8333 | 2732.8333 | 0.013011 | 0.013011 | 0 | 0 | 0
ZN2635:PA9 | EPPING | URBAN | 993 | 3.2947 | 6354.8675 | 3.6199 | 0.357 | 629.7553 | 0 | 20 | 20 | 0.001007 | 0.001007 | 2 | 35280 | 0.036254
ZN269:PA1 | WAVERLEY | URBAN | 1178 | 0 | 3638.3447 | 3.4294 | 1083.3014 | 0 | 11 | 64060.0333 | 64060.0333 | 0.19949 | 0.19949 | 0 | 0 | 0
ZN269:PA14 | WAVERLEY | URBAN | 1058 | 0 | 2384.8072 | 2.8578 | 218.4879 | 0 | 3 | 15504.1 | 13930.1667 | 0.07845 | 0.077505 | 0 | 0 | 0
ZN269:PA15 | WAVERLEY | URBAN | 243 | 0 | 1730.3276 | 4.2867 | 32.5531 | 0 | 1 | 1540 | 1540 | 0.90535 | 0.90535 | 0 | 0 | 0
ZN269:PA16 | WAVERLEY | URBAN | 1372 | 0 | 4990.3898 | 2.9531 | 792.1778 | 1847.0454 | 6 | 54400.3 | 54400.3 | 0.36589 | 0.36589 | 4 | 126840 | 0.25219
ZN269:PA18 | WAVERLEY | URBAN | 1077 | 0 | 3298.9824 | 2.3815 | 2228.2409 | 104.9874 | 8 | 189741.5667 | 188141.15 | 2.1578 | 2.1569 | 1 | 8940 | 0.13835
ZN269:PA19 | WAVERLEY | URBAN | 1338 | 0 | 4491.1487 | 2.2862 | 1624.6127 | 592.2135 | 8 | 144104.9667 | 144104.9667 | 2.216 | 2.216 | 1 | 52530 | 0.076981
ZN269:PA2 | WAVERLEY | URBAN | 1312 | 0 | 3812.6124 | 2.7625 | 1242.4044 | 0 | 6 | 91202.2 | 90478.2667 | 0.30945 | 0.30869 | 0 | 0 | 0
ZN269:PA25 | WAVERLEY | URBAN | 59 | 0 | 1310.8139 | 2.0005 | 3.5907 | 0 | 1 | 364 | 364 | 0.88136 | 0.88136 | 0 | 0 | 0
ZN269:PA26 | WAVERLEY | URBAN | 1508 | 0 | 5069.2503 | 2.9531 | 2224.4714 | 275.222 | 6 | 152758.5333 | 152758.5333 | 2.0424 | 2.0424 | 1 | 18900 | 0.02321
ZN269:PA3 | WAVERLEY | URBAN | 531 | 0 | 2565.1891 | 1.6194 | 742.6059 | 0 | 10 | 92992.9 | 92992.9 | 0.63089 | 0.63089 | 0 | 0 | 0
ZN269:PA6 | WAVERLEY | URBAN | 2050 | 0 | 3775.7249 | 3.8104 | 727.829 | 0 | 8 | 38735.55 | 38735.55 | 0.11951 | 0.11951 | 0 | 0 | 0
ZN269:PA7 | WAVERLEY | URBAN | 1244 | 0 | 3848.1861 | 2.2862 | 1251.7136 | 0 | 13 | 111028.4 | 111028.4 | 0.65916 | 0.65916 | 0 | 0 | 0
ZN269:PA9 | WAVERLEY | URBAN | 1426 | 0 | 3932.6307 | 3.3341 | 3251.0569 | 1796.2593 | 6 | 197741.0667 | 197741.0667 | 1.3282 | 1.3282 | 5 | 109255 | 0.18513
ZN2835:PA10 | BURWOOD | URBAN | 1604 | 0 | 12869.8299 | 4.5725 | 255.8791 | 0 | 3 | 11348.3833 | 1224.85 | 0.020574 | 0.0049875 | 0 | 0 | 0
ZN2835:PA15 | BURWOOD | URBAN | 1868 | 0 | 5317.1935 | 2.8578 | 1348.5103 | 0 | 7 | 95691.5 | 95575.1667 | 0.054604 | 0.054069 | 0 | 0 | 0
ZN2835:PA16 | BURWOOD | URBAN | 1456 | 0 | 5055.3268 | 5.7156 | 3135.4607 | 111.6108 | 5 | 111247.55 | 111247.55 | 1.0989 | 1.0989 | 1 | 3960 | 0.0082418
ZN2835:PA17 | BURWOOD | URBAN | 146 | 0 | 2554.5093 | 2.2862 | 6.0879 | 0 | 4 | 540 | 278 | 0.027397 | 0.020548 | 0 | 0 | 0
ZN2835:PA18 | BURWOOD | URBAN | 560 | 0 | 4374.519 | 1.8099 | 735.2234 | 0 | 2 | 82377.0167 | 430.6667 | 0.18214 | 0.0017857 | 0 | 0 | 0
ZN2835:PA19 | BURWOOD | URBAN | 788 | 0 | 5308.5427 | 1.4289 | 20.3584 | 3.5935 | 6 | 2889.3 | 2889.3 | 0.013959 | 0.013959 | 0 | 510 | 0.001269
ZN2835:PA20 | BURWOOD | URBAN | 709 | 0 | 2627.8461 | 2.3815 | 175.6609 | 427.9939 | 2 | 14958.0667 | 14958.0667 | 0.14669 | 0.14669 | 4 | 36445 | 0.42031
ZN2835:PA21 | BURWOOD | URBAN | 148 | 0 | 618.3853 | 1.8099 | 57.0493 | 465.8904 | 1 | 6392 | 6392 | 0.91892 | 0.91892 | 1 | 52200 | 0.97973
ZN2835:PA22 | BURWOOD | URBAN | 629 | 0 | 2964.2896 | 4.0009 | 139.8601 | 1360.1294 | 2 | 7089 | 4089 | 0.17806 | 0.13831 | 3 | 68940 | 0.31002
ZN2835:PA23 | BURWOOD | URBAN | 1952 | 0 | 10483.1354 | 5.8109 | 9470.118 | 0 | 8 | 330495.7667 | 319166.0333 | 1.0415 | 1.0272 | 0 | 0 | 0
ZN2835:PA27 | BURWOOD | URBAN | 931 | 0 | 4988.5014 | 2.9531 | 58.8791 | 0 | 2 | 4043.3333 | 4043.3333 | 0.052632 | 0.052632 | 0 | 0 | 0
ZN2835:PA28 | BURWOOD | URBAN | 1254 | 0 | 4106.8794 | 2.572 | 414.1089 | 0 | 6 | 32650.6 | 23639.6333 | 0.20494 | 0.13557 | 0 | 0 | 0
ZN2835:PA30 | BURWOOD | URBAN | 1822 | 0 | 6963.3755 | 5.144 | 37.582 | 1232.7916 | 4 | 1481.5833 | 1481.5833 | 0.0021954 | 0.0021954 | 2 | 48600 | 0.074094
ZN2835:PA31 | BURWOOD | URBAN | 1202 | 0 | 12536.9127 | 5.8109 | 485.839 | 59.8874 | 7 | 16955.2 | 16955.2 | 0.1015 | 0.1015 | 1 | 2090 | 0.0083195
ZN2835:PA32 | BURWOOD | SHORT RURAL | 948 | 0 | 7593.191 | 1.8099 | 431.334 | 0 | 5 | 48328.1833 | 31430.1833 | 0.18354 | 0.14768 | 0 | 0 | 0
ZN2835:PA35 | BURWOOD | URBAN | 755 | 0 | 3435.5577 | 3.7151 | 649.0569 | 0 | 6 | 35428.9667 | 33860.8667 | 0.23444 | 0.20132 | 0 | 0 | 0
ZN2835:PA36 | BURWOOD | URBAN | 770 | 0 | 6160.0567 | 3.7151 | 276.0633 | 12.6408 | 2 | 15069 | 15069 | 0.051948 | 0.051948 | 2 | 690 | 0.0038961
ZN2835:PA41 | BURWOOD | URBAN | 1188 | 0 | 4757.0403 | 3.2388 | 219.2702 | 178.239 | 2 | 13729.0667 | 118.0667 | 0.099327 | 0.00084175 | 2 | 11160 | 0.031987
ZN2835:PA9 | BURWOOD | URBAN | 1054 | 0 | 4070.7922 | 2.4768 | 1269.1082 | 3378.565 | 6 | 103911.9833 | 103911.9833 | 0.48956 | 0.48956 | 3 | 276630 | 0.54175
ZN3154:PA10 | ST IVES | URBAN | 932 | 9.1709 | 6241.3057 | 3.2198 | 2252.6785 | 0 | 7 | 141880.55 | 109306.9667 | 2.1438 | 2.0912 | 0 | 0 | 0
ZN3154:PA11 | ST IVES | URBAN | 742 | 2168.6802 | 6772.8494 | 2.8006 | 1481.8299 | 1912.8817 | 5 | 107297.9333 | 107297.9333 | 2.0593 | 2.0593 | 2 | 138510 | 0.32749
ZN3154:PA12 | ST IVES | URBAN | 719 | 3503.1085 | 4815.6141 | 3.2769 | 1239.5906 | 0 | 4 | 76711.45 | 76711.45 | 1.096 | 1.096 | 0 | 0 | 0
ZN3154:PA13 | ST IVES | URBAN | 605 | 2501.3605 | 4520.3498 | 2.0576 | 495.2489 | 0 | 7 | 48810.15 | 30557.4833 | 1.2248 | 1.0727 | 0 | 0 | 0
ZN3154:PA14 | ST IVES | URBAN | 421 | 4.6809 | 2682.0376 | 1.5432 | 345.4358 | 0 | 3 | 45393.4 | 380.25 | 0.097387 | 0.0047506 | 0 | 0 | 0
ZN3154:PA16 | ST IVES | URBAN | 1000 | 4505.1308 | 4371.3197 | 3.2579 | 1831.1886 | 0 | 6 | 113984.9 | 113984.9 | 1.089 | 1.089 | 0 | 0 | 0
ZN3154:PA17 | ST IVES | URBAN | 880 | 1319.9001 | 5780.5254 | 4.1724 | 1338.9601 | 0 | 13 | 65077.95 | 64125.5333 | 0.26705 | 0.26591 | 0 | 0 | 0
ZN3154:PA18 | ST IVES | URBAN | 1064 | 12.927 | 8457.0746 | 4.2295 | 2266.0052 | 0 | 15 | 108647.1333 | 106734.5333 | 0.3985 | 0.39756 | 0 | 0 | 0
ZN3154:PA19 | ST IVES | URBAN | 1192 | 2248.2091 | 7180.4452 | 4.4582 | 1012.378 | 0 | 13 | 46050.8 | 46050.8 | 0.1745 | 0.1745 | 0 | 0 | 0
ZN3154:PA22 | ST IVES | URBAN | 723 | 4229.1195 | 4225.2179 | 2.2672 | 2723.4128 | 464.8588 | 5 | 243599.7667 | 226489.7667 | 2.1563 | 2.0692 | 3 | 41580 | 0.1397
ZN3154:PA23 | ST IVES | URBAN | 474 | 1917.6786 | 1468.5887 | 1.5623 | 780.9284 | 0 | 7 | 101369.6 | 101369.6 | 1.7975 | 1.7975 | 0 | 0 | 0
ZN3154:PA24 | ST IVES | URBAN | 901 | 2267.8042 | 2406.8614 | 2.7054 | 224.5897 | 0 | 3 | 16834.95 | 16834.95 | 0.16981 | 0.16981 | 0 | 0 | 0
ZN3154:PA25 | ST IVES | URBAN | 421 | 2041.4617 | 1195.9547 | 1.3908 | 28.6811 | 0 | 2 | 4182 | 4182 | 0.042755 | 0.042755 | 0 | 0 | 0
ZN3154:PA3 | ST IVES | URBAN | 315 | 0 | 2461.8234 | 1.3527 | 1.091 | 0 | 0 | 163.5667 | 163.5667 | 0.0031746 | 0.0031746 | 0 | 0 | 0
ZN3154:PA4 | ST IVES | URBAN | 1270 | 3225.2938 | 5180.633 | 4.2486 | 663.2364 | 0 | 3 | 31657.3 | 30512.5 | 0.064567 | 0.06378 | 0 | 0 | 0
ZN3154:PA5 | ST IVES | URBAN | 1132 | 4893.9896 | 2850.2346 | 3.7342 | 1296.7232 | 0 | 7 | 70420.9 | 70420.9 | 1.0919 | 1.0919 | 0 | 0 | 0
ZN3154:PA6 | ST IVES | URBAN | 342 | 0 | 1771.4203 | 3.0674 | 6.7138 | 0 | 0 | 443.8667 | 0 | 0.002924 | 0 | 0 | 0 | 0
ZN3155:PA11 | DOUBLE BAY | URBAN | 985 | 0 | 3899.2513 | 1.9052 | 0 | 1814.2762 | 0 | 0 | 0 | 0 | 0 | 7 | 193114 | 0.4802
ZN3155:PA12 | DOUBLE BAY | URBAN | 1172 | 0 | 2573.4999 | 2.7625 | 56.6645 | 0 | 1 | 4159.6167 | 0 | 0.045222 | 0 | 0 | 0 | 0
ZN3155:PA15 | DOUBLE BAY | URBAN | 611 | 0 | 1800.7411 | 3.4294 | 189.7383 | 15.2196 | 4 | 11220 | 11220 | 0.29951 | 0.29951 | 1 | 900 | 0.02455
ZN3155:PA16 | DOUBLE BAY | URBAN | 719 | 0 | 2444.6371 | 3.0483 | 1012.5239 | 487.0288 | 2 | 67359 | 67359 | 0.99026 | 0.99026 | 1 | 32400 | 0.12517
ZN3155:PA17 | DOUBLE BAY | URBAN | 1185 | 0 | 7036.1658 | 3.5246 | 2901.2731 | 176.2379 | 2 | 166927.25 | 166927.25 | 0.11477 | 0.11477 | 2 | 10140 | 0.031224
ZN3155:PA18 | DOUBLE BAY | URBAN | 385 | 0 | 1054.2544 | 1.1431 | 20.2121 | 0 | 2 | 3585.6667 | 3585.6667 | 0.07013 | 0.07013 | 0 | 0 | 0
ZN3155:PA19 | DOUBLE BAY | URBAN | 913 | 0 | 4641.7242 | 3.4294 | 1933.4936 | 0 | 9 | 114335.3667 | 114335.3667 | 1.2256 | 1.2256 | 0 | 0 | 0
ZN3155:PA20 | DOUBLE BAY | URBAN | 1278 | 0 | 2323.9967 | 3.4294 | 99.8409 | 316.3985 | 1 | 5904 | 5904 | 0.037559 | 0.037559 | 1 | 18709.9333 | 0.059468
ZN3155:PA21 | DOUBLE BAY | URBAN | 486 | 0 | 3553.3316 | 2.9531 | 94.8882 | 927.0176 | 2 | 6516.15 | 6516.15 | 0.14198 | 0.14198 | 4 | 63660 | 0.44444
ZN3155:PA22 | DOUBLE BAY | URBAN | 672 | 0 | 6062.9123 | 3.3341 | 155.3451 | 0 | 4 | 9448.65 | 9448.65 | 0.10119 | 0.10119 | 0 | 0 | 0
ZN3155:PA23 | DOUBLE BAY | URBAN | 2189 | 0 | 9957.0566 | 5.4298 | 3122.7959 | 1.6065 | 10 | 116629.6833 | 115982.0833 | 0.99909 | 0.99635 | 0 | 60 | 0.00045683
ZN3155:PA24 | DOUBLE BAY | URBAN | 762 | 0 | 3013.3402 | 2.572 | 32.1217 | 71.9128 | 7 | 2532.65 | 2532.65 | 0.090551 | 0.090551 | 1 | 5670 | 0.011811
ZN3155:PA29 | DOUBLE BAY | URBAN | 2307 | 0 | 8309.0988 | 6.7635 | 1578.8701 | 810.4464 | 3 | 47340.0167 | 47340.0167 | 0.37408 | 0.37408 | 1 | 24300 | 0.035111
ZN3155:PA32 | DOUBLE BAY | URBAN | 811 | 0 | 3573.8726 | 2.4768 | 78.179 | 0 | 2 | 6401.1333 | 6401.1333 | 0.041924 | 0.041924 | 0 | 0 | 0
ZN3155:PA33 | DOUBLE BAY | URBAN | 1388 | 0 | 3328.7222 | 3.7151 | 487.8199 | 0 | 1 | 26627.8 | 26627.8 | 0.06268 | 0.06268 | 0 | 0 | 0
ZN3155:PA35 | DOUBLE BAY | URBAN | 1125 | 0 | 3772.2246 | 4.763 | 16.5353 | 15047.7243 | 0 | 704.0167 | 704.0167 | 0.00088889 | 0.00088889 | 1 | 640680 | 0.99911
ZN3155:PA36 | DOUBLE BAY | URBAN | 230 | 0 | 1812.2905 | 1.7147 | 0 | 11.6684 | 0 | 0 | 0 | 0 | 0 | 1 | 1380 | 0.3
ZN3155:PA44 | DOUBLE BAY | URBAN | 2174 | 0 | 6798.8196 | 4.0962 | 4212.3224 | 1127.0996 | 10 | 208541.9833 | 208541.9833 | 0.51334 | 0.51334 | 2 | 55800 | 0.066697
ZN3288:PA41 42ABC | CITY SOUTH | CBD | 872 | 0 | 6895.405 | 13.8127 | 0 | 4121.4953 | 0 | 0 | 0 | 0 | 0 | 2 | 60510 | 0.16628
ZN3288:PA41 42DEF | CITY SOUTH | CBD | 1074 | 0 | 7847.5725 | 14.7844 | 229.6476 | 2261.4821 | 1 | 3150 | 3150 | 0.0083799 | 0.0083799 | 2 | 31020 | 0.058659
ZN3288:PA41 42GHJ | CITY SOUTH | CBD | 498 | 0 | 4955.8134 | 8.1162 | 0 | 57.6317 | 0 | 0 | 0 | 0 | 0 | 1 | 1440 | 0.0080321
ZN3288:PA41 42KLM | CITY SOUTH | CBD | 1311 | 0 | 6429.1183 | 16.7277 | 1370.4293 | 301.9015 | 4 | 16613.9333 | 16613.9333 | 0.067887 | 0.067887 | 2 | 3660 | 0.0083905
ZN3288:PA43 44DEF | CITY SOUTH | CBD | 30 | 0 | 4249.5364 | 8.8973 | 4.87 | 201.3813 | 2 | 111 | 111 | 0.13333 | 0.13333 | 1 | 4590 | 0.3
ZN3288:PA43 44GHJ | CITY SOUTH | CBD | 589 | 0 | 4034.7314 | 14.8606 | 293.1998 | 3165.6872 | 2 | 4001.1 | 4001.1 | 0.037351 | 0.037351 | 2 | 43200 | 0.14941
ZN3288:PA43 44KLM | CITY SOUTH | CBD | 1080 | 0 | 5708.3726 | 7.8494 | 680.9733 | 919.6727 | 3 | 17593.1333 | 17593.1333 | 0.058333 | 0.058333 | 1 | 23760 | 0.0055556
ZN3288:PA45 46ABC | CITY SOUTH | CBD | 1216 | 0 | 6040.0792 | 15.6798 | 0 | 4184.5357 | 0 | 0 | 0 | 0 | 0 | 2 | 54120 | 0.10526
ZN3288:PA45 46DEF | CITY SOUTH | CBD | 561 | 0 | 4339.1238 | 12.4219 | 0 | 257.2685 | 0 | 0 | 0 | 0 | 0 | 1 | 4200 | 0.017825
ZN3288:PA45 46GHJ | CITY SOUTH | CBD | 1520 | 0 | 2401.2747 | 17.8327 | 0 | 2332.0562 | 0 | 0 | 0 | 0 | 0 | 4 | 26520 | 0.028289
ZN340:PA11 | BOTANY | URBAN | 18 | 0 | 1000.9529 | 0.85734 | 3.3518 | 0 | 0 | 792.8167 | 0 | 0.055556 | 0 | 0 | 0 | 0
ZN340:PA14 | BOTANY | SHORT RURAL | 261 | 0 | 5837.2079 | 1.1431 | 24.508 | 0 | 1 | 4347.7667 | 4347.7667 | 0.12644 | 0.12644 | 0 | 0 | 0
ZN340:PA19 | BOTANY | SHORT RURAL | 283 | 0 | 3401.7693 | 0.9526 | 8.1248 | 0 | 2 | 1729.6333 | 1481.6333 | 0.014134 | 0.0070671 | 0 | 0 | 0
ZN340:PA20 | BOTANY | URBAN | 151 | 0 | 3545.0687 | 3.0483 | 10.5072 | 0 | 1 | 699 | 0 | 0.019868 | 0 | 0 | 0 | 0
ZN340:PA27 | BOTANY | URBAN | 1595 | 0 | 8759.3044 | 3.6199 | 405.7111 | 0 | 8 | 22728.65 | 22728.65 | 0.081505 | 0.081505 | 0 | 0 | 0
ZN340:PA28 | BOTANY | SHORT RURAL | 104 | 0 | 4923.4163 | 0.57156 | 6.9147 | 0 | 2 | 2453.3667 | 2453.3667 | 0.16346 | 0.16346 | 0 | 0 | 0
ZN340:PA3 | BOTANY | URBAN | 477 | 0 | 2766.6607 | 1.2384 | 4.1584 | 0 | 2 | 680.9667 | 680.9667 | 0.010482 | 0.010482 | 0 | 0 | 0
ZN340:PA8 | BOTANY | URBAN | 529 | 119.555 | 3805.5089 | 2.4768 | 132.2733 | 0 | 4 | 10830.2667 | 10830.2667 | 0.18715 | 0.18715 | 0 | 0 | 0
ZN342:PA15 | PADDINGTON | URBAN | 121 | 0 | 3371.6981 | 1.8099 | 591.6094 | 0 | 5 | 66286 | 66286 | 2.0744 | 2.0744 | 0 | 0 | 0
ZN342:PA16 | PADDINGTON | URBAN | 1141 | 0 | 4447.4282 | 5.144 | 0 | 94.3618 | 0 | 0 | 0 | 0 | 0 | 1 | 3720 | 0.16301
ZN342:PA17 | PADDINGTON | URBAN | 1380 | 0 | 3492.2141 | 3.1436 | 1500.761 | 0.93009 | 8 | 96813.95 | 48819.7833 | 0.24348 | 0.04058 | 0 | 60 | 0.00072464
ZN342:PA18 | PADDINGTON | URBAN | 1602 | 0 | 5055.2461 | 4.0962 | 3294.6782 | 0 | 7 | 163111.6167 | 163111.6167 | 0.22347 | 0.22347 | 0 | 0 | 0
ZN342:PA22 | PADDINGTON | URBAN | 2541 | 0 | 3788.2385 | 4.1914 | 1149.0824 | 0 | 4 | 55595.4 | 55595.4 | 0.18654 | 0.18654 | 0 | 0 | 0
ZN342:PA23 | PADDINGTON | URBAN | 633 | 0 | 2269.0233 | 2.0957 | 239.6562 | 0 | 7 | 23190.3 | 23190.3 | 0.406 | 0.406 | 0 | 0 | 0
ZN342:PA24 | PADDINGTON | URBAN | 952 | 0 | 3906.138 | 2.572 | 93.737 | 0 | 10 | 7390.7333 | 7390.7333 | 0.032563 | 0.032563 | 0 | 0 | 0
ZN342:PA26 | PADDINGTON | URBAN | 2817 | 0 | 5644.806 | 3.9057 | 11493.6367 | 5269.381 | 8 | 596779.5833 | 596779.5833 | 3.9578 | 3.9578 | 2 | 273600 | 0.12673
ZN342:PA28 | PADDINGTON | URBAN | 972 | 0 | 4313.0907 | 3.1436 | 836.9534 | 530.9262 | 3 | 53991.7833 | 53991.7833 | 1.001 | 1.001 | 8 | 34250 | 0.059671
ZN342:PA35 | PADDINGTON | URBAN | 781 | 0 | 2874.5447 | 1.4289 | 770.4243 | 0 | 2 | 109340 | 109340 | 2 | 2 | 0 | 0 | 0
ZN3425:PA11 | CASTLE COVE | URBAN | 126 | 0 | 4820.0226 | 3.8485 | 0 | 891.5671 | 0 | 0 | 0 | 0 | 0 | 3 | 46980 | 0.7381
ZN3425:PA12 | CASTLE COVE | URBAN | 1196 | 4319.1154 | 4420.1595 | 4.7058 | 368.9827 | 0 | 7 | 15900.8167 | 15900.8167 | 0.11622 | 0.11622 | 0 | 0 | 0
ZN3425:PA15 | CASTLE COVE | URBAN | 1300 | 0 | 9323.8479 | 3.2769 | 171.7401 | 0 | 3 | 10628.05 | 10628.05 | 0.089231 | 0.089231 | 0 | 0 | 0
ZN3425:PA16 | CASTLE COVE | URBAN | 809 | 0 | 4556.7517 | 4.3248 | 58.4017 | 0 | 3 | 2738.4833 | 2738.4833 | 0.025958 | 0.025958 | 0 | 0 | 0
ZN3425:PA21 | CASTLE COVE | URBAN | 64 | 0 | 1388.5391 | 4.2486 | 6.8836 | 0 | 1 | 328.5667 | 328.5667 | 0.03125 | 0.03125 | 0 | 0 | 0
ZN3425:PA22 | CASTLE COVE | URBAN | 588 | 0 | 3453.4058 | 2.553 | 15.3272 | 0 | 3 | 1217.5 | 1217.5 | 0.017007 | 0.017007 | 0 | 0 | 0
ZN3425:PA24 | CASTLE COVE | URBAN | 1330 | 0 | 4619.1541 | 3.4484 | 28.9037 | 0 | 3 | 1699.75 | 1699.75 | 0.0022556 | 0.0022556 | 0 | 0 | 0
ZN3425:PA27 | CASTLE COVE | URBAN | 262 | 0 | 2671.0099 | 1.8861 | 246.459 | 0 | 3 | 26498.4167 | 26498.4167 | 1.2824 | 1.2824 | 0 | 0 | 0
ZN3425:PA28 | CASTLE COVE | URBAN | 741 | 4788.0858 | 3589.9627 | 2.915 | 4595.3582 | 51.7468 | 12 | 319696.8 | 319696.8 | 2.4926 | 2.4926 | 1 | 3600 | 0.020243
ZN3425:PA30 | CASTLE COVE | URBAN | 1434 | 4910.6034 | 3464.4539 | 3.6389 | 2747.9545 | 0 | 7 | 153139.25 | 152006.7833 | 0.95188 | 0.95119 | 0 | 0 | 0
ZN3425:PA32 | CASTLE COVE | URBAN | 168 | 0 | 1378.9381 | 2.8006 | 266.6855 | 0 | 6 | 19310.45 | 19310.45 | 2.2321 | 2.2321 | 0 | 0 | 0
ZN3425:PA33 | CASTLE COVE | URBAN | 457 | 2602.5585 | 1529.844 | 1.7337 | 158.4133 | 0 | 4 | 18529.3667 | 18529.3667 | 1.0175 | 1.0175 | 0 | 0 | 0
ZN3425:PA34 | CASTLE COVE | URBAN | 585 | 0 | 3414.3705 | 3.7913 | 374.2557 | 33.6523 | 2 | 20018.2333 | 19890 | 1.0017 | 1 | 1 | 1800 | 0.0068376
ZN3425:PA35 | CASTLE COVE | URBAN | 848 | 0 | 3411.0995 | 2.0195 | 507.8966 | 0 | 3 | 51001.1333 | 51001.1333 | 1.1002 | 1.1002 | 0 | 0 | 0
ZN3425:PA43 | CASTLE COVE | URBAN | 1292 | 0 | 6033.933 | 3.3532 | 2200.0993 | 0 | 4 | 133057.6833 | 133057.6833 | 2.0015 | 2.0015 | 0 | 0 | 0
ZN3425:PA44 | CASTLE COVE | URBAN | 921 | 296.0743 | 6408.5482 | 3.8104 | 726.09 | 0 | 2 | 38643 | 38643 | 1.0641 | 1.0641 | 0 | 0 | 0
ZN3425:PA8 | CASTLE COVE | URBAN | 266 | 0 | 3933.526 | 4.5534 | 304.1127 | 0 | 1 | 13544 | 13544 | 1 | 1 | 0 | 0 | 0
ZN3472:PA11 | SEFTON | URBAN | 427 | 1643.7651 | 2191.4454 | 2.8006 | 426.1259 | 0 | 5 | 30855.3833 | 30855.3833 | 0.15457 | 0.15457 | 0 | 0 | 0
ZN3472:PA12 | SEFTON | URBAN | 1941 | 0 | 7946.7247 | 4.8773 | 1273.9655 | 357.1545 | 7 | 52969.7667 | 52969.7667 | 0.11953 | 0.11953 | 1 | 14850 | 0.023184
ZN3472:PA15 | SEFTON | URBAN | 949 | 2146.9349 | 4643.3864 | 2.1338 | 1343.0465 | 56.82 | 4 | 127639 | 127639 | 2.0759 | 2.0759 | 1 | 5400 | 0.047418
ZN3472:PA16 | SEFTON | URBAN | 68 | 0 | 3895.1383 | 3.315 | 40.6387 | 0 | 1 | 2486 | 2486 | 0.89706 | 0.89706 | 0 | 0 | 0
ZN3472:PA17 | SEFTON | URBAN | 1486 | 0 | 7969.2536 | 3.3532 | 48.126 | 0 | 7 | 2910.5667 | 1067.55 | 0.0060565 | 0.0040377 | 0 | 0 | 0
ZN3472:PA18 | SEFTON | URBAN | 34 | 337.34 | 1509.0478 | 2.0195 | 36.2469 | 0 | 2 | 3639.7833 | 3639.7833 | 1.0294 | 1.0294 | 0 | 0 | 0
ZN3472:PA20 | SEFTON | URBAN | 1046 | 0 | 6552.6696 | 3.4103 | 25.1259 | 0 | 3 | 1494.1 | 1494.1 | 0.020076 | 0.020076 | 0 | 0 | 0
ZN3472:PA21 | SEFTON | URBAN | 1717 | 1619.4585 | 7678.7741 | 4.7058 | 596.5831 | 89.8044 | 6 | 25708.95 | 4829.6667 | 0.088526 | 0.044846 | 5 | 3870 | 0.0058241
ZN3472:PA22 | SEFTON | URBAN | 908 | 791.0096 | 4657.1756 | 3.3722 | 18.634 | 0 | 2 | 1120.5833 | 1120.5833 | 0.003304 | 0.003304 | 0 | 0 | 0
ZN3472:PA23 | SEFTON | URBAN | 1770 | 3543.6893 | 3289.0166 | 3.9247 | 481.737 | 0 | 6 | 24891.6167 | 24891.6167 | 0.10791 | 0.10791 | 0 | 0 | 0
ZN3472:PA27 | SEFTON | URBAN | 1758 | 6.6442 | 7999.307 | 4.1533 | 62.7592 | 0 | 3 | 3064.3 | 3064.3 | 0.0017065 | 0.0017065 | 0 | 0 | 0
ZN3472:PA28 | SEFTON | URBAN | 942 | 2419.9166 | 5795.8099 | 4.1724 | 48.4757 | 0 | 8 | 2356.0833 | 2145.1333 | 0.0084926 | 0.007431 | 0 | 0 | 0
ZN3472:PA30 | SEFTON | URBAN | 2444 | 3842.8624 | 7427.3644 | 5.3155 | 950.6111 | 0 | 7 | 36266.7833 | 36266.7833 | 0.65507 | 0.65507 | 0 | 0 | 0
ZN3472:PA31 | SEFTON | URBAN | 1843 | 3480.39 | 6483.5853 | 3.9628 | 4652.558 | 147.7321 | 10 | 238088.7167 | 238088.7167 | 2.0705 | 2.0705 | 1 | 7560 | 0.0065111
ZN3472:PA32 | SEFTON | SHORT RURAL | 166 | 2518.8903 | 7655.4953 | 1.1622 | 1.4327 | 194.7918 | 0 | 250 | 250 | 0.0060241 | 0.0060241 | 4 | 33990 | 0.45181
ZN3472:PA33 | SEFTON | URBAN | 1491 | 0 | 7520.4095 | 3.0102 | 2223.1391 | 0 | 8 | 149768.3 | 149768.3 | 1.0349 | 1.0349 | 0 | 0 | 0
ZN3472:PA34 | SEFTON | URBAN | 530 | 0 | 8823.2492 | 5.2584 | 1370.9966 | 322.0478 | 12 | 52873.45 | 52873.45 | 1.1094 | 1.1094 | 6 | 12420 | 0.037736
ZN3472:PA35 | SEFTON | URBAN | 383 | 0 | 4920.8814 | 4.0771 | 9.6005 | 131.4865 | 0 | 477.5167 | 477.5167 | 0.002611 | 0.002611 | 2 | 6540 | 0.02611
ZN3472:PA39 | SEFTON | URBAN | 26 | 609.923 | 8390.6676 | 3.658 | 0 | 44.9149 | 0 | 0 | 0 | 0 | 0 | 2 | 2490 | 0.34615
ZN3472:PA40 | SEFTON | URBAN | 67 | 0 | 5865.9463 | 5.2584 | 62.6878 | 0 | 5 | 2417.6 | 2417.6 | 0.74627 | 0.74627 | 0 | 0 | 0
ZN3472:PA7 | SEFTON | SHORT RURAL | 1343 | 775.4401 | 14477.2283 | 4.2676 | 109.0257 | 0 | 4 | 5180.7333 | 5180.7333 | 0.023827 | 0.023827 | 0 | 0 | 0
ZN3472:PA8 | SEFTON | URBAN | 1114 | 3.0145 | 6228.6309 | 3.5437 | 38.0587 | 11.5331 | 8 | 2177.9667 | 2177.9667 | 0.0071813 | 0.0071813 | 0 | 660 | 0.00089767
ZN35335:PA14 | ROYAL NORTH SHORE | URBAN | 203 | 0 | 7473.8926 | 3.4294 | 287.4315 | 0 | 1 | 16997 | 16997 | 1 | 1 | 0 | 0 | 0
ZN35335:PA2 | ROYAL NORTH SHORE | HV CUSTOMERS | 2 | 0 | 349.2532 | 0.4763 | 0 | 0.046974 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0.5
ZN35370:PA10 | GALSTON | SHORT RURAL | 522 | 16744.8814 | 3850.2467 | 3.658 | 3028.3427 | 1553.0807 | 12 | 167885.8667 | 167885.8667 | 4.6398 | 4.6398 | 6 | 86100 | 0.41762
ZN35370:PA2 | GALSTON | SHORT RURAL | 367 | 13144.5105 | 432.1421 | 2.6292 | 1498.2083 | 395.5587 | 18 | 115558.9167 | 72702.5833 | 2.1335 | 2.0082 | 9 | 30510 | 0.48229
ZN35370:PA8 | GALSTON | SHORT RURAL | 848 | 36666.8928 | 866.1266 | 2.9721 | 8447.3615 | 602.7996 | 25 | 576377.25 | 339558.25 | 3.8656 | 3.0106 | 17 | 41130 | 0.19222
ZN35500:PA14 | TOP RYDE | URBAN | 74 | 0 | 8800.334 | 5.5822 | 390.6617 | 214.7098 | 5 | 14192 | 14192 | 2.5946 | 2.5946 | 1 | 7800 | 0.13514
ZN35500:PA16 | TOP RYDE | URBAN | 354 | 0 | 2338.6937 | 2.21 | 263.5701 | 0 | 7 | 24185.1333 | 24185.1333 | 1.0169 | 1.0169 | 0 | 0 | 0
ZN35500:PA18 | TOP RYDE | SHORT RURAL | 597 | 636.1851 | 7235.659 | 2.7244 | 191.5104 | 0 | 4 | 14254.9833 | 14254.9833 | 0.28476 | 0.28476 | 0 | 0 | 0
ZN35500:PA19 | TOP RYDE | SHORT RURAL | 149 | 0 | 4204.7137 | 0.53346 | 9.2024 | 0 | 0 | 3498.2833 | 0 | 0.0067114 | 0 | 0 | 0 | 0
ZN35500:PA22 | TOP RYDE | URBAN | 983 | 3103.1935 | 2944.4502 | 3.1245 | 878.9764 | 0 | 9 | 57048.4333 | 13303.9333 | 0.091556 | 0.04883 | 0 | 0 | 0
ZN35500:PA23 | TOP RYDE | URBAN | 384 | 0 | 7227.5026 | 3.7151 | 348.0073 | 0 | 6 | 18996.0833 | 2553 | 0.23958 | 0.067708 | 0 | 0 | 0
ZN35500:PA24 | TOP RYDE | URBAN | 2754 | 2389.9863 | 13557.7438 | 7.2017 | 14279.9067 | 0 | 22 | 402109.1167 | 16441.1167 | 0.83588 | 0.099492 | 0 | 0 | 0
ZN35500:PA27 | TOP RYDE | URBAN | 1045 | 4465.7791 | 3303.3932 | 4.2867 | 257.2494 | 6.5529 | 11 | 12169.7667 | 11907.7667 | 0.11388 | 0.11292 | 0 | 310 | 0.00095694
ZN35500:PA28 | TOP RYDE | URBAN | 3089 | 9984.5789 | 6792.7222 | 8.3257 | 37840.5854 | 455.7158 | 20 | 921694 | 907632.1333 | 4.2269 | 4.0981 | 1 | 11100 | 0.011978
ZN35500:PA31 | TOP RYDE | URBAN | 890 | 212.7944 | 10377.3312 | 4.1914 | 507.8652 | 19.0152 | 15 | 24571.75 | 13753.65 | 0.22022 | 0.16517 | 1 | 920 | 0.025843
ZN35500:PA34 | TOP RYDE | URBAN | 938 | 2810.0909 | 6664.0254 | 3.2769 | 2712.4408 | 0 | 14 | 167858.05 | 164190.05 | 1.8731 | 1.8582 | 0 | 0 | 0
ZN35500:PA35 | TOP RYDE | URBAN | 178 | 0 | 1583.7849 | 2.2481 | 18.4015 | 0 | 1 | 1659.9 | 1659.9 | 0.050562 | 0.050562 | 0 | 0 | 0
ZN35600:PA1 | KINGSFORD | URBAN | 2780 | 0 | 14072.6195 | 6.8587 | 1818.809 | 0 | 9 | 53776.8 | 53776.8 | 0.097122 | 0.097122 | 0 | 0 | 0
ZN35600:PA10 | KINGSFORD | URBAN | 506 | 0 | 4077.2828 | 2.0195 | 3.2541 | 0 | 0 | 326.7667 | 0 | 0.0019763 | 0 | 0 | 0 | 0
ZN35600:PA12 | KINGSFORD | SHORT RURAL | 659 | 0 | 6920.986 | 1.7337 | 2.1292 | 0 | 2 | 249.05 | 249.05 | 0.0030349 | 0.0030349 | 0 | 0 | 0
ZN35600:PA14 | KINGSFORD | URBAN | 1781 | 0 | 6323.3331 | 3.4675 | 658.6998 | 416.5224 | 10 | 38523.5667 | 38523.5667 | 0.064009 | 0.064009 | 1 | 24360 | 0.032566
ZN35600:PA16 | KINGSFORD | URBAN | 1560 | 0 | 4237.7538 | 2.6482 | 23.8685 | 0 | 4 | 1827.7667 | 345.3833 | 0.0025641 | 0.00064103 | 0 | 0 | 0
ZN35600:PA19 | KINGSFORD | URBAN | 2034 | 0 | 10350.6803 | 3.2769 | 299.9687 | 0 | 7 | 18563.4167 | 18563.4167 | 0.049656 | 0.049656 | 0 | 0 | 0
ZN35600:PA2 | KINGSFORD | URBAN | 1217 | 0 | 4609.5756 | 2.2481 | 8.2522 | 0 | 0 | 744.3833 | 744.3833 | 0.00082169 | 0.00082169 | 0 | 0 | 0
ZN35600:PA20 | KINGSFORD | URBAN | 336 | 0 | 4270.956 | 2.1719 | 79.8447 | 0 | 1 | 7455.0667 | 0 | 0.13095 | 0 | 0 | 0 | 0
ZN35600:PA22 | KINGSFORD | URBAN | 1266 | 0 | 7013.3709 | 3.4865 | 155.7882 | 5.1578 | 6 | 9061.3667 | 9061.3667 | 0.10821 | 0.10821 | 0 | 300 | 0.00078989
ZN35600:PA25 | KINGSFORD | URBAN | 1097 | 0 | 4359.8315 | 2.2672 | 208.2237 | 0 | 6 | 18624.8833 | 18624.8833 | 0.044667 | 0.044667 | 0 | 0 | 0
ZN35600:PA3 | KINGSFORD | URBAN | 1148 | 0 | 3752.6251 | 2.553 | 74.9922 | 0 | 4 | 5956.9167 | 2733.1167 | 0.044425 | 0.038328 | 0 | 0 | 0
ZN35600:PA4 | KINGSFORD | URBAN | 1140 | 0 | 3153.2546 | 3.1436 | 11.9586 | 0 | 2 | 771.45 | 310 | 0.0026316 | 0.0017544 | 0 | 0 | 0
ZN35600:PA7 | KINGSFORD | URBAN | 1355 | 0 | 4595.5531 | 2.2481 | 11.1829 | 0 | 2 | 1008.75 | 1008.75 | 0.001476 | 0.001476 | 0 | 0 | 0
ZN35600:PA9 | KINGSFORD | URBAN | 2956 | 0 | 9121.5465 | 6.2872 | 579.4976 | 0 | 11 | 18691.6667 | 18691.6667 | 0.029093 | 0.029093 | 0 | 0 | 0
ZN35800:PA13 | BANKSTOWN | URBAN | 295 | 383.6871 | 2317.3098 | 3.315 | 6.7197 | 37.2712 | 1 | 411.0667 | 411.0667 | 0.0067797 | 0.0067797 | 0 | 2280 | 0.0033898
ZN35800:PA14 | BANKSTOWN | URBAN | 1943 | 3054.3806 | 3389.5664 | 3.2388 | 5939.1352 | 5358.6696 | 5 | 371864.4333 | 371864.4333 | 2.0005 | 2.0005 | 1 | 335520 | 0.35975
ZN35800:PA16 | BANKSTOWN | URBAN | 322 | 731.7831 | 4212.4531 | 3.2007 | 770.3849 | 0 | 2 | 48810 | 48810 | 1.0062 | 1.0062 | 0 | 0 | 0
ZN35800:PA18 | BANKSTOWN | URBAN | 410 | 2596.6981 | 3044.9858 | 2.5339 | 66.858 | 0 | 2 | 5350.7167 | 5350.7167 | 0.1122 | 0.1122 | 0 | 0 | 0
ZN35800:PA21 | BANKSTOWN | URBAN | 279 | 0 | 6175.2896 | 1.7528 | 52.5856 | 0 | 5 | 6084 | 6084 | 0.26882 | 0.26882 | 0 | 0 | 0
ZN35800:PA4 | BANKSTOWN | URBAN | 80 | 640.0283 | 3006.3768 | 2.553 | 2.621 | 2238.8443 | 2 | 208.2 | 208.2 | 0.025 | 0.025 | 1 | 177840 | 0.975
ZN35800:PA6 | BANKSTOWN | URBAN | 562 | 367.3228 | 3903.1188 | 2.4577 | 44.5023 | 80.3513 | 1 | 3672 | 3672 | 0.030249 | 0.030249 | 1 | 6630 | 0.030249
ZN35800:PA7 | BANKSTOWN | URBAN | 400 | 991.1449 | 2623.8846 | 2.8959 | 299.9858 | 1311.3476 | 4 | 21007.1667 | 21007.1667 | 0.53 | 0.53 | 2 | 91830 | 0.42
ZN36300:PA1 | BALGOWLAH NORTH | URBAN | 834 | 1674.0356 | 1297.4853 | 1.5242 | 7.0703 | 0 | 8 | 940.7167 | 672.7167 | 0.026379 | 0.016787 | 0 | 0 | 0
ZN36300:PA11 | BALGOWLAH NORTH | URBAN | 3572 | 1668.8564 | 16465.3678 | 8.9925 | 42963.2079 | 2937.3248 | 21 | 968868.9833 | 968868.9833 | 2.082 | 2.082 | 1 | 66240 | 0.038634
ZN36300:PA13 | BALGOWLAH NORTH | URBAN | 1409 | 2417.3764 | 2278.0411 | 2.3053 | 11.6448 | 0 | 4 | 1024.3667 | 1024.3667 | 0.0056778 | 0.0056778 | 0 | 0 | 0
ZN36300:PA17 | BALGOWLAH NORTH | URBAN | 1393 | 3518.7887 | 3888.117 | 2.8769 | 5827.64 | 331.1063 | 8 | 410795.9167 | 388895.9167 | 3.0352 | 2.9828 | 2 | 23340 | 0.031587
ZN36300:PA19 | BALGOWLAH NORTH | URBAN | 1824 | 4330.1672 | 2891.1522 | 4.2676 | 6520.6792 | 0 | 10 | 309852.6167 | 309852.6167 | 1.977 | 1.977 | 0 | 0 | 0
ZN36300:PA3 | BALGOWLAH NORTH | URBAN | 1993 | 2202.6939 | 8740.4968 | 5.7156 | 7455.8477 | 2426.6886 | 18 | 264536.8167 | 250111.3833 | 1.3322 | 1.3071 | 1 | 86100 | 0.10286
ZN36300:PA5 | BALGOWLAH NORTH | URBAN | 951 | 379.3826 | 6446.2473 | 7.0111 | 331.454 | 0 | 9 | 9587.0667 | 9587.0667 | 0.065195 | 0.065195 | 0 | 0 | 0
ZN36300:PA7 | BALGOWLAH NORTH | URBAN | 811 | 585.2861 | 1287.8072 | 2.5339 | 42.4252 | 41.9837 | 6 | 3395.3333 | 3395.3333 | 0.038224 | 0.038224 | 1 | 3360 | 0.0098644
ZN36300:PA9 | BALGOWLAH NORTH | URBAN | 1369 | 1028.1539 | 4583.8884 | 3.3532 | 279.3684 | 0 | 8 | 16895.65 | 16895.65 | 0.14828 | 0.14828 | 0 | 0 | 0
ZN3672:PA13 | MAROUBRA | URBAN | 1982 | 0 | 7926.1869 | 4.0009 | 493.1169 | 0 | 11 | 24994.3 | 18639.5833 | 0.047931 | 0.020182 | 0 | 0 | 0
ZN3672:PA26 | MAROUBRA | URBAN | 185 | 0 | 1360.1886 | 2.0957 | 8.3012 | 0 | 2 | 803.2667 | 377.3667 | 0.010811 | 0.0054054 | 0 | 0 | 0
ZN3672:PA35 | MAROUBRA | URBAN | 2388 | 0 | 10239.468 | 4.5725 | 43.27 | 0 | 3 | 1919.05 | 812.7667 | 0.0012563 | 0.00083752 | 0 | 0 | 0
ZN3672:PA37 | MAROUBRA | URBAN | 1316 | 0 | 2257.2689 | 2.6673 | 16.8036 | 0 | 2 | 1277.5667 | 318.2 | 0.0015198 | 0.00075988 | 0 | 0 | 0
ZN3672:PA42 | MAROUBRA | URBAN | 337 | 0 | 9764.9976 | 3.5246 | 79.533 | 0 | 1 | 4576 | 4576 | 0.077151 | 0.077151 | 0 | 0 | 0
ZN3672:PA44 | MAROUBRA | URBAN | 1906 | 0 | 6694.3379 | 2.6673 | 2049.5433 | 0 | 9 | 155825.8167 | 155825.8167 | 0.26495 | 0.26495 | 0 | 0 | 0
ZN3672:PA46 | MAROUBRA | URBAN | 1651 | 0 | 6268.7954 | 2.9531 | 166.4083 | 0 | 3 | 11427.5667 | 11427.5667 | 0.079346 | 0.079346 | 0 | 0 | 0
ZN3672:PA6 | MAROUBRA | URBAN | 244 | 0 | 4884.0645 | 3.2388 | 16.6899 | 0 | 1 | 1045 | 1045 | 0.045082 | 0.045082 | 0 | 0 | 0
ZN3672:PA9 | MAROUBRA | URBAN | 1285 | 0 | 6456.9399 | 2.4768 | 21.6867 | 0 | 4 | 1775.6667 | 1775.6667 | 0.012451 | 0.012451 | 0 | 0 | 0
ZN384:PA1 | CAMPERDOWN | URBAN | 415 | 0 | 2288.2589 | 6.4777 | 43.6015 | 0 | 2 | 1365 | 1365 | 1.0096 | 1.0096 | 0 | 0 | 0
ZN384:PA22 | CAMPERDOWN | URBAN | 569 | 0 | 5349.7991 | 3.5246 | 443.3409 | 18.7709 | 1 | 25508 | 25508 | 0.13533 | 0.13533 | 1 | 1080 | 0.0035149
ZN384:PA33 | CAMPERDOWN | URBAN | 867 | 0 | 3931.2009 | 5.5251 | 59.3783 | 0 | 3 | 2179.4167 | 2179.4167 | 0.041522 | 0.041522 | 0 | 0 | 0
ZN384:PA4 | CAMPERDOWN | URBAN | 87 | 0 | 1558.1597 | 3.5246 | 123.1707 | 0 | 3 | 7086.7333 | 7086.7333 | 2.0115 | 2.0115 | 0 | 0 | 0
ZN384:PA41 | CAMPERDOWN | URBAN | 492 | 0 | 1568.179 | 3.7151 | 274.7626 | 219.2898 | 2 | 14998 | 14998 | 0.97154 | 0.97154 | 1 | 11970 | 0.042683
ZN384:PA9 | CAMPERDOWN | URBAN | 827 | 0 | 3551.7287 | 4.763 | 524.8928 | 373.4451 | 10 | 22348.1167 | 22348.1167 | 1.3398 | 1.3398 | 1 | 15900 | 0.064087
ZN3922:PA1 | DRUMMOYNE | URBAN | 290 | 0 | 1117.2328 | 0.76208 | 1.1891 | 0 | 2 | 316.4167 | 316.4167 | 0.0068966 | 0.0068966 | 0 | 0 | 0
ZN3922:PA10 | DRUMMOYNE | URBAN | 1403 | 0 | 5904.3249 | 3.8104 | 55.0597 | 0 | 3 | 2930.3167 | 2930.3167 | 0.023521 | 0.023521 | 0 | 0 | 0
ZN3922:PA11 | DRUMMOYNE | URBAN | 1322 | 0 | 11866.219 | 3.7151 | 597.6679 | 0 | 7 | 32623.8833 | 31625.25 | 0.14599 | 0.14523 | 0 | 0 | 0
ZN3922:PA12 | DRUMMOYNE | URBAN | 1298 | 0 | 5724.0401 | 3.4294 | 51.7857 | 0 | 6 | 3062.3 | 3062.3 | 0.0053929 | 0.0053929 | 0 | 0 | 0
ZN3922:PA13 | DRUMMOYNE | URBAN | 2478 | 0 | 9692.6151 | 5.3346 | 1328.4044 | 0 | 4 | 50498.9833 | 50498.9833 | 0.12672 | 0.12672 | 0 | 0 | 0
ZN3922:PA14 | DRUMMOYNE | URBAN | 1817 | 0 | 6856.1613 | 3.9057 | 72.6161 | 0 | 4 | 3770.4167 | 3770.4167 | 0.028619 | 0.028619 | 0 | 0 | 0
ZN3922:PA17 | DRUMMOYNE | SHORT RURAL | 745 | 0 | 15074.5041 | 1.7147 | 71.7256 | 0 | 3 | 8482.85 | 8482.85 | 0.10738 | 0.10738 | 0 | 0 | 0
ZN3922:PA18 | DRUMMOYNE | URBAN | 992 | 0 | 6052.3991 | 4.6677 | 483.3353 | 944.6329 | 4 | 20998.7167 | 20998.7167 | 0.073589 | 0.073589 | 1 | 41040 | 0.076613
ZN3922:PA2 | DRUMMOYNE | SHORT RURAL | 1129 | 0 | 9878.098 | 2.2862 | 5155.2675 | 324.6859 | 8 | 457278 | 457278 | 2.1585 | 2.1585 | 1 | 28800 | 0.070859
ZN3922:PA21 | DRUMMOYNE | SHORT RURAL | 493 | 0 | 5512.1574 | 1.3336 | 30.5451 | 0 | 3 | 4644.6667 | 4644.6667 | 0.046653 | 0.046653 | 0 | 0 | 0
ZN3922:PA22 | DRUMMOYNE | URBAN | 903 | 0 | 6135.391 | 2.0005 | 843.3203 | 0 | 6 | 85489.6667 | 85489.6667 | 1.0044 | 1.0044 | 0 | 0 | 0
ZN3922:PA26 | DRUMMOYNE | URBAN | 1928 | 0 | 5931.1685 | 4.4772 | 35.3449 | 7510.8972 | 3 | 1600.9167 | 1600.9167 | 0.033195 | 0.033195 | 1 | 340200 | 0.42012
ZN3922:PA29 | DRUMMOYNE | URBAN | 2852 | 0 | 17328.8072 | 5.8109 | 10025.65 | 0 | 8 | 349883.1667 | 349883.1667 | 1.1083 | 1.1083 | 0 | 0 | 0
ZN3922:PA3 | DRUMMOYNE | URBAN | 749 | 0 | 3442.2885 | 1.8099 | 8.8805 | 118.8824 | 1 | 995 | 995 | 0.0066756 | 0.0066756 | 2 | 13320 | 0.049399
ZN3922:PA30 | DRUMMOYNE | URBAN | 362 | 0 | 2135.0781 | 0.66682 | 30.9906 | 0 | 1 | 9424.8 | 9424.8 | 0.24309 | 0.24309 | 0 | 0 | 0
ZN3922:PA5 | DRUMMOYNE | URBAN | 2319 | 0 | 15911.0658 | 4.9535 | 14189.2125 | 422.0916 | 9 | 580891.8667 | 580891.8667 | 2.1587 | 2.1587 | 1 | 17280 | 0.027598
ZN3922:PA7 | DRUMMOYNE | URBAN | 1899 | 0 | 6757.3632 | 4.0009 | 112.5411 | 0 | 5 | 5704.3 | 5704.3 | 0.013691 | 0.013691 | 0 | 0 | 0
ZN398:PA10 | DULWICH HILL | URBAN | 551 | 0 | 3430.2111 | 2.2862 | 290.191 | 0 | 3 | 25740.2667 | 25740.2667 | 0.08167 | 0.08167 | 0 | 0 | 0
ZN398:PA11 | DULWICH HILL | URBAN | 984 | 0 | 5516.3278 | 4.8583 | 3655.5208 | 14.3741 | 5 | 152587.6667 | 140198.6667 | 2.188 | 2.0955 | 0 | 600 | 0.0010163
ZN398:PA15 | DULWICH HILL | URBAN | 1680 | 0 | 6051.875 | 4.0009 | 2142.4951 | 0 | 9 | 108595.2667 | 108085.7833 | 1.0429 | 1.0423 | 0 | 0 | 0
ZN398:PA16 | DULWICH HILL | URBAN | 2035 | 0 | 7288.5781 | 4.5725 | 8309.6192 | 0 | 8 | 368536.2667 | 368536.2667 | 3.1027 | 3.1027 | 0 | 0 | 0
ZN398:PA19 | DULWICH HILL | URBAN | 776 | 0 | 3893.5427 | 3.0483 | 653.4889 | 0 | 2 | 43473.9 | 43473.9 | 0.99742 | 0.99742 | 0 | 0 | 0
ZN398:PA2 | DULWICH HILL | URBAN | 2423 | 0 | 12711.7386 | 4.0009 | 4097.959 | 0 | 7 | 207710.6 | 207710.6 | 1.04 | 1.04 | 0 | 0 | 0
ZN398:PA20 | DULWICH HILL | URBAN | 1649 | 0 | 7020.5833 | 3.7151 | 6108.4172 | 0 | 4 | 333429.8167 | 333429.8167 | 1.9988 | 1.9988 | 0 | 0 | 0
ZN398:PA22 | DULWICH HILL | URBAN | 89 | 0 | 2396.9465 | 0.9526 | 24.4024 | 33.8214 | 3 | 5194.85 | 5058.7167 | 1.0225 | 1.0112 | 1 | 7200 | 0.13483
ZN398:PA24 | DULWICH HILL | URBAN | 1931 | 0 | 5774.4797 | 2.9531 | 345.4514 | 0 | 6 | 23722.7833 | 23722.7833 | 1.0808 | 1.0808 | 0 | 0 | 0
ZN398:PA25 | DULWICH HILL | URBAN | 878 | 0 | 4792.4294 | 4.763 | 179.615 | 0 | 5 | 7647.3833 | 7647.3833 | 0.084282 | 0.084282 | 0 | 0 | 0
ZN398:PA26 | DULWICH HILL | URBAN | 1081 | 0 | 1966.8084 | 2.0005 | 284.2994 | 0 | 2 | 28820.2 | 28820.2 | 1.1138 | 1.1138 | 0 | 0 | 0
ZN398:PA29 | DULWICH HILL | URBAN | 769 | 0 | 3251.5426 | 2.0957 | 25.1593 | 0 | 4 | 2434.5333 | 2434.5333 | 1.0039 | 1.0039 | 0 | 0 | 0
ZN398:PA3 | DULWICH HILL | URBAN | 1791 | 3.2936 | 5005.3123 | 2.9531 | 462.4004 | 0 | 9 | 31753.8833 | 31753.8833 | 0.18146 | 0.18146 | 0 | 0 | 0
ZN398:PA30 | DULWICH HILL | URBAN | 1419 | 0 | 2523.0799 | 2.7625 | 131.5639 | 0 | 4 | 9657.8167 | 9657.8167 | 1.086 | 1.086 | 0 | 0 | 0
ZN398:PA31 | DULWICH HILL | URBAN | 651 | 0 | 3461.3184 | 4.5725 | 310.9502 | 202.9287 | 4 | 13790.8167 | 13790.8167 | 1.4578 | 1.4578 | 1 | 9000 | 0.023041
ZN398:PA4 | DULWICH HILL | URBAN | 1891 | 0 | 9303.8837 | 3.5246 | 7.066 | 0 | 0 | 406.55 | 406.55 | 0.00052882 | 0.00052882 | 0 | 0 | 0
ZN398:PA9 | DULWICH HILL | URBAN | 815 | 0 | 1663.4137 | 1.3336 | 4.7183 | 0 | 2 | 717.4667 | 717.4667 | 0.002454 | 0.002454 | 0 | 0 | 0
ZN4545:PA11 | MEADOWBANK | URBAN | 370 | 0 | 1485.6873 | 0.68587 | 0.66899 | 0 | 2 | 197.8 | 197.8 | 0.0054054 | 0.0054054 | 0 | 0 | 0
ZN4545:PA13 | MEADOWBANK | SHORT RURAL | 103 | 0 | 1454.478 | 0.28578 | 0.51155 | 0 | 1 | 363 | 363 | 0.029126 | 0.029126 | 0 | 0 | 0
ZN4545:PA17 | MEADOWBANK | URBAN | 991 | 2336.079 | 6436.949 | 3.5056 | 6072.7225 | 0 | 10 | 351298.2333 | 351298.2333 | 3.4591 | 3.4591 | 0 | 0 | 0
ZN4545:PA19 | MEADOWBANK | URBAN | 490 | 0 | 4780.4203 | 2.5339 | 856.3514 | 574.2769 | 7 | 68534.7333 | 68534.7333 | 0.50408 | 0.50408 | 2 | 45960 | 0.13061
ZN4545:PA2 | MEADOWBANK | URBAN | 886 | 0 | 3992.0443 | 2.1529 | 611.8355 | 301.2871 | 2 | 57632.3833 | 57632.3833 | 1.0011 | 1.0011 | 3 | 28380 | 0.068849
ZN4545:PA21 | MEADOWBANK | URBAN | 731 | 2017.5139 | 3039.2427 | 2.0957 | 337.1586 | 0.62006 | 11 | 32625.1 | 32625.1 | 0.49248 | 0.49248 | 0 | 60 | 0.001368
ZN4545:PA24 | MEADOWBANK | URBAN | 1656 | 2005.1765 | 4156.9291 | 4.6296 | 2088.7356 | 0 | 11 | 91492.9333 | 91313.8333 | 0.78865 | 0.78804 | 0 | 0 | 0
ZN4545:PA25 | MEADOWBANK | URBAN | 1044 | 2372.3885 | 5678.2742 | 4.6868 | 3389.9939 | 0 | 4 | 146681.1 | 107573.1 | 1.0757 | 0.98946 | 0 | 0 | 0
ZN4545:PA26 | MEADOWBANK | URBAN | 938 | 0 | 2915.4386 | 3.4675 | 816.7326 | 0 | 1 | 47766 | 47766 | 0.94883 | 0.94883 | 0 | 0 | 0
ZN4545:PA27 | MEADOWBANK | URBAN | 1053 | 1292.9537 | 3254.8012 | 2.1148 | 992.5775 | 0 | 16 | 95181.3333 | 94312.2667 | 0.52896 | 0.52707 | 0 | 0 | 0
ZN4545:PA31 | MEADOWBANK | URBAN | 2965 | 4229.8147 | 6211.6133 | 5.2584 | 5018.2916 | 0 | 13 | 193533.95 | 191136.55 | 0.52715 | 0.52681 | 0 | 0 | 0
ZN4545:PA32 | MEADOWBANK | URBAN | 778 | 0 | 5929.1324 | 3.9819 | 22.4352 | 0 | 4 | 1142.6 | 1142.6 | 0.01671 | 0.01671 | 0 | 0 | 0
ZN4545:PA33 | MEADOWBANK | SHORT RURAL | 672 | 0 | 4248.2434 | 1.105 | 0 | 529.6438 | 0 | 0 | 0 | 0 | 0 | 2 | 97200 | 0.48214
ZN4545:PA35 | MEADOWBANK | URBAN | 1344 | 0 | 4279.5651 | 3.1436 | 1359.2618 | 0 | 7 | 87685.85 | 87685.85 | 0.6183 | 0.6183 | 0 | 0 | 0
ZN4545:PA36 | MEADOWBANK | URBAN | 893 | 2350.741 | 4369.269 | 4.4772 | 1445.5522 | 0 | 10 | 65475.1167 | 22334.7167 | 0.33931 | 0.19149 | 0 | 0 | 0
ZN4545:PA4 | MEADOWBANK | URBAN | 1167 | 0 | 6811.1698 | 3.4294 | 830.9726 | 2402.1681 | 6 | 49138.8 | 49138.8 | 0.14824 | 0.14824 | 5 | 142050 | 0.31448
ZN4545:PA40 | MEADOWBANK | URBAN | 1623 | 4091.8461 | 4746.1952 | 4.1343 | 3614.3173 | 0 | 11 | 177287 | 175664.5333 | 1.0419 | 1.0413 | 0 | 0 | 0
ZN4545:PA41 | MEADOWBANK | URBAN | 2374 | 6673.9942 | 9236.4386 | 6.3824 | 12355.6651 | 0 | 18 | 392583.1667 | 377721.7667 | 1.4709 | 1.4065 | 0 | 0 | 0
ZN4545:PA42 | MEADOWBANK | URBAN | 1080 | 1598.8971 | 2864.4068 | 1.9433 | 1769.0781 | 0 | 11 | 184610.8333 | 184610.8333 | 1.3528 | 1.3528 | 0 | 0 | 0
ZN4545:PA44 | MEADOWBANK | URBAN | 1034 | 831.6059 | 9648.4303 | 4.2867 | 1147.6983 | 0 | 7 | 54294.4667 | 54294.4667 | 1.0793 | 1.0793 | 0 | 0 | 0
ZN4545:PA6 | MEADOWBANK | URBAN | 686 | 185.898 | 2340.9659 | 2.915 | 758.4676 | 0 | 4 | 52766.2167 | 52766.2167 | 1.2332 | 1.2332 | 0 | 0 | 0
ZN4545:PA9 | MEADOWBANK | URBAN | 25 | 0 | 3088.6896 | 5.7537 | 49.6518 | 0 | 1 | 1750 | 1750 | 1 | 1 | 0 | 0 | 0
ZN4990:PA51 52ABC | CITY CENTRAL | CBD | 1662 | 0 | 8052.6841 | 16.1561 | 239.6422 | 0 | 1 | 3008 | 3008 | 0.009627 | 0.009627 | 0 | 0 | 0
ZN4990:PA51 52DEF | CITY CENTRAL | CBD | 807 | 0 | 9564.5803 | 12.3266 | 0 | 18.2354 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0.0012392
ZN4990:PA51 52KLM | CITY CENTRAL | CBD | 160 | 0 | 9809.7488 | 16.4228 | 20.6508 | 0 | 1 | 255 | 255 | 0.03125 | 0.03125 | 0 | 0 | 0
ZN4990:PA55 56GHJ | CITY CENTRAL | CBD | 1377 | 0 | 8683.2342 | 10.993 | 47874.6522 | 3434.6353 | 6 | 883161.5833 | 883161.5833 | 2.0806 | 2.0806 | 2 | 63360 | 0.12781
ZN4990:PA55 56KLM | CITY CENTRAL | CBD | 968 | 0 | 7678.6243 | 14.7272 | 631.0865 | 52.288 | 1 | 8690 | 8690 | 0.056818 | 0.056818 | 0 | 720 | 0.0010331
ZN5868:PA10 | GORE HILL | URBAN | 283 | 0 | 2920.4389 | 3.3341 | 10.7031 | 0 | 1 | 651 | 651 | 0.024735 | 0.024735 | 0 | 0 | 0
ZN5868:PA13 | GORE HILL | URBAN | 666 | 0 | 3259.4633 | 3.9819 | 5.2518 | 167.8812 | 2 | 267.4667 | 267.4667 | 0.0045045 | 0.0045045 | 1 | 8550 | 0.022523
ZN5868:PA14 | GORE HILL | URBAN | 1947 | 0 | 5507.589 | 4.9535 | 1738.98 | 1.4656 | 11 | 71192.0667 | 45792.2833 | 0.10221 | 0.070365 | 0 | 60 | 0.00051361
ZN5868:PA2 | GORE HILL | URBAN | 307 | 0 | 2494.3369 | 3.677 | 63.3996 | 0 | 6 | 3496.55 | 3496.55 | 0.10423 | 0.10423 | 0 | 0 | 0
ZN5868:PA27 | GORE HILL | URBAN | 760 | 0 | 4827.9078 | 4.039 | 171.1394 | 60.9462 | 3 | 8592.6 | 8592.6 | 0.084211 | 0.084211 | 1 | 3060 | 0.0078947
ZN5868:PA28 | GORE HILL | URBAN | 46 | 0 | 1418.2541 | 4.1152 | 58.8087 | 0 | 2 | 2898 | 2898 | 1.8261 | 1.8261 | 0 | 0 | 0
ZN5868:PA30 | GORE HILL | URBAN | 1712 | 0 | 8574.8845 | 4.6677 | 4221.6484 | 0 | 7 | 183411.4 | 182242.4833 | 1.0771 | 1.0765 | 0 | 0 | 0
ZN630:PA10 | MASCOT | URBAN | 297 | 0 | 2590.0164 | 1.6194 | 0.76662 | 0 | 0 | 96 | 96 | 0.003367 | 0.003367 | 0 | 0 | 0
ZN630:PA19 | MASCOT | URBAN | 395 | 0 | 850.3739 | 1.1431 | 0 | 7.4407 | 0 | 0 | 0 | 0 | 0 | 1 | 1320 | 0.027848
ZN630:PA24 | MASCOT | URBAN | 311 | 0 | 3539.5168 | 2.0005 | 10.9497 | 0 | 1 | 1110 | 1110 | 0.032154 | 0.032154 | 0 | 0 | 0
ZN630:PA26 | MASCOT | URBAN | 293 | 0 | 1303.4944 | 1.1431 | 0 | 91.3179 | 0 | 0 | 0 | 0 | 0 | 1 | 16200 | 0.15358
ZN630:PA27 | MASCOT | URBAN | 309 | 0 | 3163.3995 | 1.5242 | 220.2678 | 0 | 2 | 29307 | 29307 | 1.2071 | 1.2071 | 0 | 0 | 0
ZN630:PA3 | MASCOT | URBAN | 1479 | 0 | 5030.8009 | 2.2862 | 19.0007 | 0 | 0 | 1685.3833 | 1685.3833 | 0.00067613 | 0.00067613 | 0 | 0 | 0
ZN630:PA31 | MASCOT | URBAN | 205 | 0 | 2389.0648 | 2.0957 | 11.9878 | 0 | 1 | 1160 | 1160 | 0.039024 | 0.039024 | 0 | 0 | 0
ZN630:PA32 | MASCOT | URBAN | 211 | 0 | 3004.5827 | 1.5242 | 118.2773 | 14.4305 | 1 | 15737 | 15737 | 1 | 1 | 2 | 1920 | 0.028436
ZN630:PA33 | MASCOT | URBAN | 123 | 0 | 2163.1037 | 3.6199 | 16.4924 | 6.4261 | 2 | 923.9333 | 923.9333 | 0.02439 | 0.02439 | 1 | 360 | 0.02439
ZN630:PA34 | MASCOT | URBAN | 81 | 0 | 2428.2398 | 1.5242 | 22.3222 | 0 | 1 | 2970 | 2970 | 0.96296 | 0.96296 | 0 | 0 | 0
ZN630:PA38 | MASCOT | URBAN | 2214 | 0 | 8003.9504 | 3.5246 | 36.4599 | 0 | 5 | 2097.75 | 2097.75 | 0.0063234 | 0.0063234 | 0 | 0 | 0
ZN630:PA41 | MASCOT | URBAN | 246 | 0 | 3269.5356 | 4.0009 | 7.6944 | 0 | 1 | 390 | 390 | 0.02439 | 0.02439 | 0 | 0 | 0
ZN630:PA8 | MASCOT | URBAN | 326 | 0 | 1430.9359 | 2.191 | 808.0042 | 0 | 3 | 74787 | 74787 | 0.56442 | 0.56442 | 0 | 0 | 0
ZN630:PA9 | MASCOT | URBAN | 78 | 0 | 2007.6216 | 1.4289 | 28.7905 | 0 | 1 | 4086 | 4086 | 1 | 1 | 0 | 0 | 0
ZN690:PA10 | CAMPSIE | URBAN | 546 | 3.3041 | 4090.4334 | 1.8099 | 90.7148 | 0 | 2 | 10164 | 10164 | 1.1374 | 1.1374 | 0 | 0 | 0
ZN690:PA11 | CAMPSIE | URBAN | 2286 | 0 | 7140.8395 | 4.763 | 716.6799 | 0 | 7 | 30513.75 | 22657.1833 | 1.0144 | 1.0048 | 0 | 0 | 0
ZN690:PA12 | CAMPSIE | URBAN | 1990 | 0 | 9339.0337 | 3.5246 | 509.9929 | 0 | 6 | 29342.8833 | 29342.8833 | 1.0492 | 1.0492 | 0 | 0 | 0
ZN690:PA14 | CAMPSIE | URBAN | 2180 | 0 | 6638.3517 | 3.7151 | 2864.2529 | 0 | 6 | 156346.1167 | 156346.1167 | 2.0729 | 2.0729 | 0 | 0 | 0
ZN690:PA15 | CAMPSIE | URBAN | 520 | 0 | 2806.0222 | 3.7151 | 136.4653 | 0 | 3 | 7449 | 7449 | 0.96923 | 0.96923 | 0 | 0 | 0
ZN690:PA17 | CAMPSIE | URBAN | 1701 | 0 | 3293.4542 | 2.3815 | 278.9322 | 0 | 6 | 23751.9333 | 23751.9333 | 0.018812 | 0.018812 | 0 | 0 | 0
ZN690:PA18 | CAMPSIE | URBAN | 1808 | 0 | 7847.8067 | 4.2867 | 776.1888 | 0 | 3 | 36719.3667 | 36719.3667 | 0.049226 | 0.049226 | 0 | 0 | 0
ZN690:PA24 | CAMPSIE | SHORT RURAL | 944 | 0 | 11949.0779 | 3.3341 | 106.7631 | 0 | 2 | 6493.7167 | 6493.7167 | 0.072034 | 0.072034 | 0 | 0 | 0
ZN690:PA25 | CAMPSIE | URBAN | 1817 | 0 | 8395.8927 | 3.7151 | 42.1823 | 0 | 5 | 2302.5333 | 2302.5333 | 0.0033021 | 0.0033021 | 0 | 0 | 0
ZN690:PA26 | CAMPSIE | URBAN | 1889 | 0 | 7311.0468 | 3.4294 | 372.0951 | 0 | 3 | 22003.5 | 22003.5 | 0.030704 | 0.030704 | 0 | 0 | 0
ZN690:PA28 | CAMPSIE | URBAN | 1273 | 3.2547 | 5367.1335 | 2.2862 | 212.8729 | 0 | 5 | 18882.0667 | 18882.0667 | 0.058916 | 0.058916 | 0 | 0 | 0
ZN690:PA3 | CAMPSIE | URBAN | 136 | 0 | 1776.6881 | 0.85734 | 188.842 | 110.3425 | 5 | 44668 | 44668 | 1.9191 | 1.9191 | 2 | 26100 | 0.44118
ZN690:PA30 | CAMPSIE | URBAN | 1138 | 0 | 7051.104 | 2.7625 | 14.5121 | 0 | 3 | 1065.3 | 1065.3 | 0.0026362 | 0.0026362 | 0 | 0 | 0
ZN690:PA33 | CAMPSIE | URBAN | 694 | 0 | 3827.5333 | 3.6199 | 69.2546 | 1359.1147 | 7 | 3879.7667 | 3879.7667 | 0.020173 | 0.020173 | 6 | 76140 | 0.36311
ZN690:PA34 | CAMPSIE | URBAN | 1978 | 0 | 7784.882 | 3.4294 | 194.6943 | 0 | 3 | 11513.0667 | 11513.0667 | 0.044489 | 0.044489 | 0 | 0 | 0
ZN690:PA35 | CAMPSIE | URBAN | 2497 | 0 | 9021.0387 | 4.382 | 1420.5792 | 1075.4374 | 8 | 65742.7667 | 42479.4167 | 0.11093 | 0.073688 | 2 | 49770 | 0.051262
ZN690:PA4 | CAMPSIE | URBAN | 1619 | 0 | 6412.4485 | 4.2867 | 395.0958 | 0 | 7 | 18690.9 | 18042.4667 | 1.0284 | 1.0278 | 0 | 0 | 0
ZN690:PA5 | CAMPSIE | URBAN | 538 | 0 | 5927.068 | 3.4294 | 1863.6349 | 0 | 6 | 110204.3333 | 110204.3333 | 2.9405 | 2.9405 | 0 | 0 | 0
ZN690:PA6 | CAMPSIE | URBAN | 904 | 0 | 7948.2682 | 4.0962 | 165.0541 | 0 | 2 | 8171.4333 | 8118 | 0.99889 | 0.99779 | 0 | 0 | 0
ZN711:PA14 | BLACKWATTLE BAY | URBAN | 640 | 0 | 2271.8026 | 7.2398 | 0 | 79.2549 | 0 | 0 | 0 | 0 | 0 | 1 | 2220 | 0.11563
ZN711:PA15 | BLACKWATTLE BAY | URBAN | 441 | 0 | 5629.1935 | 2.7625 | 282.8445 | 0 | 1 | 20763 | 20763 | 1 | 1 | 0 | 0 | 0
ZN711:PA28 | BLACKWATTLE BAY | URBAN | 521 | 0 | 635.1676 | 2.0005 | 0 | 101.2107 | 0 | 0 | 0 | 0 | 0 | 2 | 10260 | 0.65643
ZN711:PA32 | BLACKWATTLE BAY | URBAN | 500 | 0 | 1727.6531 | 3.4294 | 219.5147 | 0 | 2 | 12980.8 | 12980.8 | 0.228 | 0.228 | 0 | 0 | 0
ZN711:PA33 | BLACKWATTLE BAY | URBAN | 1069 | 0 | 3480.6459 | 2.9531 | 482.1589 | 0 | 3 | 33110.7333 | 33110.7333 | 0.11974 | 0.11974 | 0 | 0 | 0
ZN72:PA10 | FIVE DOCK | URBAN | 2343 | 0 | 5171.9702 | 3.8104 | 710.5403 | 0 | 10 | 37815.4333 | 37815.4333 | 0.10414 | 0.10414 | 0 | 0 | 0
ZN72:PA14 | FIVE DOCK | URBAN | 1879 | 1.6509 | 8426.6531 | 5.0488 | 29.3677 | 0 | 4 | 1179.6 | 1179.6 | 0.0021288 | 0.0021288 | 0 | 0 | 0
ZN72:PA15 | FIVE DOCK | URBAN | 897 | 0 | 3107.9427 | 2.4768 | 286.4019 | 0 | 1 | 23450 | 23450 | 0.074693 | 0.074693 | 0 | 0 | 0
ZN72:PA16 | FIVE DOCK | URBAN | 1350 | 0 | 5493.2835 | 2.9531 | 1317.7693 | 0 | 3 | 90493.6333 | 90493.6333 | 1.0022 | 1.0022 | 0 | 0 | 0
ZN72:PA17 | FIVE DOCK | URBAN | 687 | 0 | 4274.3886 | 1.6194 | 13.2881 | 0 | 3 | 1664 | 1167 | 0.10917 | 0.10771 | 0 | 0 | 0
ZN72:PA18 | FIVE DOCK | URBAN | 1883 | 0 | 4935.4333 | 3.3341 | 822.2633 | 0 | 3 | 50013.0333 | 50013.0333 | 0.10674 | 0.10674 | 0 | 0 | 0
ZN72:PA22 | FIVE DOCK | URBAN | 712 | 0 | 2541.9574 | 1.7147 | 315.8947 | 0 | 3 | 37360.2833 | 37360.2833 | 0.22051 | 0.22051 | 0 | 0 | 0
ZN72:PA23 | FIVE DOCK | URBAN | 1643 | 0 | 5842.9093 | 2.8578 | 106.1951 | 967.2933 | 2 | 7535.7 | 7535.7 | 0.042605 | 0.042605 | 1 | 68640 | 0.087036
ZN72:PA24 | FIVE DOCK | SHORT RURAL | 533 | 0 | 5278.3395 | 1.5242 | 3.6614 | 0 | 2 | 487.15 | 487.15 | 0.0037523 | 0.0037523 | 0 | 0 | 0
ZN72:PA25 | FIVE DOCK | URBAN | 486 | 0 | 2339.872 | 1.6194 | 97.9831 | 0 | 5 | 12269.95 | 12269.95 | 0.10494 | 0.10494 | 0 | 0 | 0
ZN72:PA26 | FIVE DOCK | URBAN | 974 | 0 | 8137.8632 | 3.0483 | 898.8592 | 0 | 4 | 59797.3667 | 59797.3667 | 1.115 | 1.115 | 0 | 0 | 0
ZN72:PA30 | FIVE DOCK | URBAN | 755 | 0 | 4805.8121 | 2.6673 | 1006.4664 | 0 | 6 | 76521.1667 | 76521.1667 | 0.26755 | 0.26755 | 0 | 0 | 0
ZN72:PA31 | FIVE DOCK | URBAN | 1218 | 0 | 6946.0485 | 3.8104 | 791.9097 | 0 | 4 | 42145.9667 | 42145.9667 | 0.30788 | 0.30788 | 0 | 0 | 0
ZN72:PA34 | FIVE DOCK | URBAN | 1082 | 0 | 4879.0174 | 2.2862 | 1405.7951 | 0 | 5 | 124695.6 | 124695.6 | 1.1488 | 1.1488 | 0 | 0 | 0
ZN7481:PA1 | DARLING HARBOUR 132 11kV | URBAN | 1927 | 0 | 8703.7979 | 4.763 | 523.1258 | 226.1809 | 5 | 22272.8833 | 22272.8833 | 0.07369 | 0.07369 | 1 | 9630 | 0.16658
ZN7481:PA12 | DARLING HARBOUR 132 11kV | URBAN | 684 | 0 | 8611.3979 | 5.4298 | 549.4294 | 0 | 1 | 20520 | 20520 | 1 | 1 | 0 | 0 | 0
ZN7481:PA13 | DARLING HARBOUR 132 11kV | URBAN | 429 | 0 | 1783.8052 | 5.4298 | 333.1116 | 0 | 1 | 12441 | 12441 | 1 | 1 | 0 | 0 | 0
ZN7481:PA14 | DARLING HARBOUR 132 11kV | URBAN | 424 | 0 | 2394.9759 | 1.4289 | 89.4154 | 0 | 1 | 12690 | 12690 | 0.99764 | 0.99764 | 0 | 0 | 0
ZN7481:PA16 | DARLING HARBOUR 132 11kV | URBAN | 98 | 0 | 1696.7677 | 4.1914 | 60.1458 | 0 | 1 | 2910 | 2910 | 0.9898 | 0.9898 | 0 | 0 | 0
ZN7481:PA17 | DARLING HARBOUR 132 11kV | URBAN | 2150 | 0 | 9032.6916 | 5.2393 | 2266.5486 | 926.9894 | 3 | 87728.9 | 87728.9 | 1.067 | 1.067 | 3 | 35880 | 0.19535
ZN7481:PA19 | DARLING HARBOUR 132 11kV | URBAN | 146 | 0 | 1518.1382 | 2.3815 | 229.5396 | 0 | 2 | 19546 | 19546 | 1.9795 | 1.9795 | 0 | 0 | 0
ZN7481:PA21 | DARLING HARBOUR 132 11kV | URBAN | 121 | 0 | 1555.4586 | 2.3815 | 41.2081 | 0 | 1 | 3509 | 3509 | 1 | 1 | 0 | 0 | 0
ZN7481:PA9 | DARLING HARBOUR 132 11kV | URBAN | 1458 | 0 | 4603.8009 | 7.4303 | 6.0541 | 0 | 0 | 165.2333 | 165.2333 | 0.00068587 | 0.00068587 | 0 | 0 | 0
ZN7900:PA11 | CAMPBELL ST | URBAN | 1217 | 0 | 3934.4955 | 3.6199 | 0.4284 | 20.0815 | 1 | 24 | 24 | 0.0032868 | 0.0032868 | 2 | 1125 | 0.0041085
ZN7900:PA12 | CAMPBELL ST | URBAN | 1107 | 0 | 2273.2985 | 3.6199 | 6291.2057 | 0 | 9 | 352444.4167 | 352444.4167 | 0.55465 | 0.55465 | 0 | 0 | 0
ZN7900:PA15 | CAMPBELL ST | URBAN | 194 | 0 | 2558.3793 | 1.8099 | 55.407 | 0 | 1 | 6208 | 6208 | 1 | 1 | 0 | 0 | 0
ZN7900:PA17 | CAMPBELL ST | URBAN | 134 | 0 | 1001.6088 | 3.2388 | 132.4654 | 30.1856 | 1 | 8294 | 8294 | 1 | 1 | 1 | 1890 | 0.9403
ZN7900:PA2 | CAMPBELL ST | URBAN | 1500 | 0 | 3295.6573 | 2.6673 | 12.1988 | 0 | 0 | 927.4667 | 927.4667 | 0.00066667 | 0.00066667 | 0 | 0 | 0
ZN7900:PA23 | CAMPBELL ST | URBAN | 293 | 0 | 2430.6886 | 3.1436 | 33.2662 | 0 | 2 | 2146 | 2146 | 0.095563 | 0.095563 | 0 | 0 | 0
ZN7900:PA6 | CAMPBELL ST | URBAN | 893 | 0 | 3237.1531 | 4.0009 | 1165.2587 | 0 | 2 | 59062.7167 | 59062.7167 | 0.11534 | 0.11534 | 0 | 0 | 0
ZN7900:PA7 | CAMPBELL ST | URBAN | 738 | 0 | 2568.6258 | 3.1436 | 17.3738 | 1.0696 | 2 | 1120.7833 | 1120.7833 | 0.00271 | 0.00271 | 1 | 69 | 0.031165
ZN80:PA21 | CHATSWOOD | URBAN | 715 | 0 | 3315.5025 | 1.848 | 45.2249 | 0 | 4 | 4962.6833 | 4962.6833 | 0.11329 | 0.11329 | 0 | 0 | 0
ZN80:PA22 | CHATSWOOD | URBAN | 1437 | 0 | 7864.0794 | 2.8197 | 273.1792 | 287.8205 | 8 | 19647 | 19497 | 0.20529 | 0.2039 | 1 | 20700 | 0.048017
ZN80:PA24 | CHATSWOOD | URBAN | 1452 | 0 | 9341.4036 | 5.9442 | 4404.4582 | 1630.3289 | 12 | 150261.6833 | 150261.6833 | 1.3244 | 1.3244 | 1 | 55620 | 0.020661
ZN80:PA25 | CHATSWOOD | URBAN | 913 | 2495.2819 | 3832.1493 | 3.0102 | 5239.9584 | 0 | 14 | 353005.2 | 289162.1333 | 3.1095 | 2.1774 | 0 | 0 | 0
ZN80:PA27 | CHATSWOOD | URBAN | 747 | 0 | 4001.9249 | 2.0576 | 314.917 | 0 | 3 | 31037.2167 | 31037.2167 | 0.96252 | 0.96252 | 0 | 0 | 0
ZN80:PA28 | CHATSWOOD | URBAN | 436 | 0 | 3047.8862 | 1.4861 | 276.9038 | 0 | 3 | 37787.2 | 37787.2 | 1.0069 | 1.0069 | 0 | 0 | 0
ZN80:PA30 | CHATSWOOD | URBAN | 1264 | 0 | 6390.5286 | 5.144 | 114.7984 | 4045.383 | 3 | 4525.6667 | 4525.6667 | 0.0023734 | 0.0023734 | 2 | 159480 | 0.13133
ZN80:PA31 | CHATSWOOD | URBAN | 784 | 2770.0996 | 2254.1335 | 2.3434 | 1104.8315 | 0 | 8 | 95609.55 | 95609.55 | 2.3189 | 2.3189 | 0 | 0 | 0
ZN80:PA32 | CHATSWOOD | URBAN | 2844 | 3156.7935 | 6976.831 | 6.8587 | 11190.078 | 316.5687 | 27 | 330857.4833 | 305774.1 | 1.3741 | 1.3045 | 1 | 9360 | 0.0084388
ZN80:PA37 | CHATSWOOD | URBAN | 1581 | 727.7501 | 7664.5311 | 7.2398 | 1158.8789 | 0 | 6 | 32461.2167 | 32461.2167 | 0.072739 | 0.072739 | 0 | 0 | 0
ZN80:PA39 | CHATSWOOD | URBAN | 589 | 0 | 4298.2729 | 3.4865 | 56.4739 | 0 | 2 | 3284.7833 | 1223.3667 | 0.010187 | 0.0016978 | 0 | 0 | 0
ZN80:PA40 | CHATSWOOD | URBAN | 2453 | 134.3105 | 11647.626 | 7.316 | 7881.4728 | 3324.7833 | 15 | 218467.3333 | 207381.8667 | 1.0249 | 1.0179 | 1 | 92160 | 0.078272
ZN8000:PA15 | MACQUARIE PARK | URBAN | 87 | 0 | 2740.2625 | 4.2486 | 0 | 2.5141 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0.011494
ZN8000:PA16 | MACQUARIE PARK | URBAN | 33 | 0 | 2347.714 | 4.2486 | 5.6559 | 0 | 0 | 269.9667 | 269.9667 | 0.030303 | 0.030303 | 0 | 0 | 0
ZN8000:PA19 | MACQUARIE PARK | URBAN | 888 | 0 | 3362.7839 | 3.8676 | 1353.0162 | 0 | 6 | 70944.2667 | 70944.2667 | 0.38626 | 0.38626 | 0 | 0 | 0
ZN8000:PA20 | MACQUARIE PARK | URBAN | 71 | 0 | 3624.7442 | 2.7625 | 202.0838 | 0 | 3 | 14834.5333 | 14834.5333 | 1.5352 | 1.5352 | 0 | 0 | 0
ZN8000:PA25 | MACQUARIE PARK | URBAN | 331 | 1.3001 | 6273.7873 | 3.9247 | 299.2817 | 0 | 4 | 15464.05 | 15464.05 | 0.15106 | 0.15106 | 0 | 0 | 0
ZN8000:PA38 | MACQUARIE PARK | URBAN | 617 | 0 | 6197.8413 | 4.401 | 1479.0845 | 0 | 1 | 68154 | 68154 | 0.98703 | 0.98703 | 0 | 0 | 0
ZN8000:PA39 | MACQUARIE PARK | URBAN | 47 | 0 | 2503.7071 | 4.4391 | 0 | 16.2862 | 0 | 0 | 0 | 0 | 0 | 3 | 744 | 0.21277
ZN8000:PA4 | MACQUARIE PARK | URBAN | 24 | 876.4612 | 2506.7407 | 4.4391 | 4.6472 | 0 | 0 | 212.3 | 212.3 | 0.041667 | 0.041667 | 0 | 0 | 0
ZN8000:PA6 | MACQUARIE PARK | URBAN | 708 | 7.9324 | 8060.0535 | 2.7054 | 916.6068 | 0 | 5 | 68707.65 | 68707.65 | 1.0056 | 1.0056 | 0 | 0 | 0
ZN8100:PA10 | GREEN SQUARE | URBAN | 255 | 0 | 3296.5488 | 2.2862 | 482.8314 | 0 | 6 | 42827.6833 | 42827.6833 | 1.8196 | 1.8196 | 0 | 0 | 0
ZN8100:PA2 | GREEN SQUARE | URBAN | 156 | 0 | 2663.3336 | 2.8578 | 2.7057 | 0 | 1 | 192 | 192 | 0.019231 | 0.019231 | 0 | 0 | 0
ZN8100:PA20 | GREEN SQUARE | URBAN | 592 | 0 | 2540.6564 | 2.9531 | 332.5102 | 0 | 4 | 22834.0833 | 22834.0833 | 0.99155 | 0.99155 | 0 | 0 | 0
ZN8100:PA23 | GREEN SQUARE | URBAN | 21 | 0 | 527.4915 | 1.7147 | 0 | 2.6634 | 0 | 0 | 0 | 0 | 0 | 1 | 315 | 1
ZN8100:PA30 | GREEN SQUARE | URBAN | 1284 | 0 | 5532.0621 | 3.6199 | 2204.054 | 0 | 5 | 123474.9833 | 123474.9833 | 1.0576 | 1.0576 | 0 | 0 | 0
ZN847:PA1 | HORNSBY | URBAN | 1208 | 3884.7986 | 7315.9371 | 3.6008 | 777.696 | 0 | 12 | 43798.4167 | 34669.15 | 0.16225 | 0.11507 | 0 | 0 | 0
ZN847:PA10 | HORNSBY | URBAN | 1441 | 853.4515 | 6784.9074 | 3.5246 | 1777.3225 | 31.2848 | 12 | 102259.7833 | 48149.7 | 0.24497 | 0.18737 | 1 | 1800 | 0.020819
ZN847:PA14 | HORNSBY | URBAN | 315 | 34.1671 | 2408.7499 | 3.1817 | 19.5709 | 0 | 2 | 1247.4 | 1247.4 | 0.0063492 | 0.0063492 | 0 | 0 | 0
ZN847:PA15 | HORNSBY | URBAN | 1277 | 822.8511 | 8509.1725 | 3.7723 | 12394.4357 | 0 | 9 | 666303.2333 | 620119.6167 | 3.9475 | 3.9217 | 0 | 0 | 0
ZN847:PA19 | HORNSBY | URBAN | 1300 | 2.6307 | 3596.0113 | 3.5056 | 258.5498 | 948.913 | 4 | 14956.7333 | 14956.7333 | 0.10154 | 0.10154 | 1 | 54893.25 | 0.24692
ZN847:PA2 | HORNSBY | URBAN | 1481 | 1312.956 | 8787.8429 | 4.1152 | 351.464 | 0 | 5 | 17319.5833 | 15403.6833 | 0.13234 | 0.10398 | 0 | 0 | 0
ZN847:PA21 | HORNSBY | URBAN | 1301 | 3835.941 | 4610.1402 | 5.1821 | 55.6233 | 12.2659 | 4 | 2176.7 | 558 | 0.0092237 | 0.0046118 | 0 | 480 | 0.00076864
ZN847:PA22 | HORNSBY | SHORT RURAL | 1553 | 2972.5062 | 6384.7033 | 5.3917 | 7882.1626 | 701.9077 | 8 | 296462.1833 | 76608.1833 | 1.0547 | 0.53187 | 1 | 26400 | 0.035415
ZN847:PA23 | HORNSBY | URBAN | 1222 | 262.7958 | 6677.0384 | 4.4391 | 383.0132 | 0 | 7 | 17497.1833 | 17497.1833 | 0.074468 | 0.074468 | 0 | 0 | 0
ZN847:PA26 | HORNSBY | URBAN | 168 | 0 | 86.4884 | 0.4382 | 1.0712 | 0 | 2 | 495.75 | 495.75 | 0.011905 | 0.011905 | 0 | 0 | 0
ZN847:PA28 | HORNSBY | URBAN | 1211 | 0 | 2460.3143 | 3.658 | 173.8693 | 7.3054 | 2 | 9639 | 9639 | 0.12139 | 0.12139 | 0 | 405 | 0.00082576
ZN847:PA29 | HORNSBY | URBAN | 572 | 0 | 1559.9263 | 3.7342 | 0 | 2161.3312 | 0 | 0 | 0 | 0 | 0 | 1 | 117375 | 0.5472
ZN847:PA36 | HORNSBY | URBAN | 1389 | 0 | 3355.9681 | 2.7816 | 5.7241 | 0 | 2 | 417.3167 | 417.3167 | 0.0014399 | 0.0014399 | 0 | 0 | 0
ZN847:PA38 | HORNSBY | URBAN | 153 | 0 | 1828.8935 | 2.8959 | 0 | 5.7835 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0.0065359
ZN847:PA39 | HORNSBY | URBAN | 1203 | 2870.7769 | 7436.8267 | 3.4675 | 893.0506 | 0 | 9 | 52229.4 | 52229.4 | 0.25353 | 0.25353 | 0 | 0 | 0
ZN847:PA44 | HORNSBY | URBAN | 1029 | 4108.7928 | 4986.404 | 2.8387 | 1063.1029 | 0 | 9 | 75945.0333 | 15375.6833 | 1.1885 | 0.14383 | 0 | 0 | 0
ZN847:PA45 | HORNSBY | SHORT RURAL | 293 | 18181.7782 | 5461.7893 | 1.2765 | 174.6422 | 85.7317 | 1 | 27745 | 27745 | 0.66553 | 0.66553 | 4 | 13620 | 0.11263
ZN847:PA46 | HORNSBY | URBAN | 866 | 4315.5244 | 1467.3569 | 3.9628 | 19.5367 | 0 | 6 | 999.7667 | 949.7667 | 0.0080831 | 0.0069284 | 0 | 0 | 0
ZN847:PA47 | HORNSBY | SHORT RURAL | 260 | 12874.1338 | 6825.1108 | 1.6385 | 2877.8238 | 0 | 12 | 356185.3833 | 24625.1167 | 4.8423 | 0.96154 | 0 | 0 | 0
ZN847:PA48 | HORNSBY | URBAN | 541 | 396.3716 | 3426.2574 | 4.5534 | 16.0637 | 0 | 3 | 715.4167 | 205.4167 | 0.0092421 | 0.0018484 | 0 | 0 | 0
ZN847:PA5 | HORNSBY | URBAN | 1007 | 422.0227 | 6250.8669 | 4.7249 | 4508.4715 | 0 | 9 | 193503.1333 | 160097.6833 | 1.6087 | 1.57 | 0 | 0 | 0
ZN847:PA7 | HORNSBY | URBAN | 1016 | 2489.037 | 2635.382 | 2.1529 | 194.881 | 9.5546 | 2 | 18356.9833 | 18356.9833 | 0.083661 | 0.083661 | 1 | 900 | 0.0029528
ZN8700:PA61 62ABC | CITY NORTH NEW 132kv 11kv | CBD | 615 | 0 | 3363.0298 | 12.0218 | 0 | 2560.9598 | 0 | 0 | 0 | 0 | 0 | 3 | 43200 | 0.15772
ZN8700:PA61 62GHJ | CITY NORTH NEW 132kv 11kv | CBD | 1824 | 0 | 11216.2357 | 12.46 | 462.981 | 58.9846 | 5 | 7535.2167 | 7535.2167 | 0.04386 | 0.04386 | 1 | 960 | 0.0010965
ZN8700:PA61 62KLM | CITY NORTH NEW 132kv 11kv | CBD | 204 | 0 | 1396.2312 | 7.9066 | 11.4438 | 0 | 0 | 293.5167 | 293.5167 | 0.004902 | 0.004902 | 0 | 0 | 0
ZN8700:PA63 64DEF | CITY NORTH NEW 132kv 11kv | CBD | 336 | 0 | 0 | 4.7439 | 0 | 1948.6975 | 0 | 0 | 0 | 0 | 0 | 2 | 83302 | 0.17262
ZN8700:PA65 66GHJ | CITY NORTH NEW 132kv 11kv | CBD | 55 | 0 | 2821.2536 | 4.6868 | 0 | 49.9205 | 0 | 0 | 0 | 0 | 0 | 1 | 2160 | 0.072727
ZN874:PA12 | CONCORD | URBAN | 109 | 0 | 3099.0507 | 2.572 | 10.8698 | 0 | 2 | 857.0333 | 857.0333 | 0.018349 | 0.018349 | 0 | 0 | 0
ZN874:PA16 | CONCORD | URBAN | 389 | 175.7883 | 3102.5671 | 2.2862 | 15.0505 | 0 | 1 | 1335 | 1335 | 0.071979 | 0.071979 | 0 | 0 | 0
ZN874:PA17 | CONCORD | URBAN | 848 | 0 | 5250.9499 | 3.1436 | 962.5266 | 262.2853 | 7 | 62092.5 | 62092.5 | 0.61439 | 0.61439 | 1 | 16920 | 0.055425
ZN874:PA18 | CONCORD | SHORT RURAL | 1835 | 0 | 13148.6394 | 4.9535 | 502.4266 | 0 | 4 | 20568.8333 | 20568.8333 | 0.042507 | 0.042507 | 0 | 0 | 0
ZN874:PA22 | CONCORD | URBAN | 1472 | 0 | 8175.5545 | 5.3346 | 2951.8675 | 123.1101 | 5 | 112214.55 | 112214.55 | 1.1168 | 1.1168 | 1 | 4680 | 0.0081522
ZN874:PA23 | CONCORD | URBAN | 18 | 0 | 2564.5638 | 2.0005 | 4.4489 | 0 | 1 | 451 | 451 | 0.61111 | 0.61111 | 0 | 0 | 0
ZN874:PA25 | CONCORD | URBAN | 1103 | 0 | 7597.4787 | 3.6199 | 387.168 | 909.825 | 9 | 21689.8333 | 21689.8333 | 0.12602 | 0.12602 | 5 | 50970 | 0.1641
ZN874:PA3 | CONCORD | URBAN | 641 | 0 | 956.8312 | 1.2384 | 146.3687 | 0 | 2 | 23968.7333 | 23968.7333 | 1.0811 | 1.0811 | 0 | 0 | 0
ZN874:PA7 | CONCORD | URBAN | 1633 | 0.74176 | 9041.2153 | 3.9057 | 10.0367 | 11.5557 | 0 | 521.1333 | 521.1333 | 0.00061237 | 0.00061237 | 1 | 600 | 0.0012247
ZN874:PA8 | CONCORD | URBAN | 1213 | 0 | 7163.7838 | 4.763 | 0 | 2030.6959 | 0 | 0 | 0 | 0 | 0 | 9 | 86460 | 0.3817
ZN901:PA10 | SURRY HILLS | URBAN | 241 | 0 | 2838.5205 | 2.7625 | 132.4654 | 0 | 1 | 9724 | 9724 | 0.21577 | 0.21577 | 0 | 0 | 0
ZN901:PA11 | SURRY HILLS | URBAN | 2413 | 0 | 2677.621 | 3.6199 | 1187.7052 | 0 | 3 | 66537.3333 | 66537.3333 | 1.0767 | 1.0767 | 0 | 0 | 0
ZN901:PA12 | SURRY HILLS | URBAN | 486 | 0 | 1980.5869 | 2.0957 | 60.2388 | 0 | 2 | 5829 | 5829 | 1.0144 | 1.0144 | 0 | 0 | 0
ZN901:PA13 | SURRY HILLS | URBAN | 1691 | 0 | 2429.215 | 2.8578 | 1171.4363 | 0 | 3 | 83126.1667 | 83126.1667 | 2.1762 | 2.1762 | 0 | 0 | 0
ZN901:PA14 | SURRY HILLS | URBAN | 951 | 0 | 4998.374 | 2.6673 | 1293.4744 | 0 | 6 | 98342.25 | 98342.25 | 2.0599 | 2.0599 | 0 | 0 | 0
ZN901:PA17 | SURRY HILLS | URBAN | 91 | 0 | 1224.3616 | 4.0009 | 13.8634 | 0 | 2 | 702.6833 | 702.6833 | 1.011 | 1.011 | 0 | 0 | 0
ZN901:PA18 | SURRY HILLS | URBAN | 1122 | 0 | 2425.466 | 3.1436 | 246.8698 | 553.4034 | 3 | 15925.55 | 15925.55 | 1.0704 | 1.0704 | 1 | 35700 | 0.075758
ZN901:PA19 | SURRY HILLS | URBAN | 746 | 0 | 3108.4619 | 2.7625 | 665.3364 | 0 | 3 | 48840.9 | 48840.9 | 1.9987 | 1.9987 | 0 | 0 | 0
ZN901:PA2 | SURRY HILLS | URBAN | 148 | 0 | 3363.7242 | 4.763 | 238.2298 | 0 | 1 | 10143 | 10143 | 0.99324 | 0.99324 | 0 | 0 | 0
ZN901:PA20 | SURRY HILLS | URBAN | 1236 | 0 | 4143.398 | 3.6199 | 197.3549 | 0 | 3 | 11056.1667 | 11056.1667 | 1.0898 | 1.0898 | 0 | 0 | 0
ZN901:PA22 | SURRY HILLS | URBAN | 723 | 0 | 1952.5799 | 4.763 | 0 | 71.8706 | 0 | 0 | 0 | 0 | 0 | 1 | 3060 | 0.0082988
ZN901:PA3 | SURRY HILLS | HV CUSTOMERS | 1 | 0 | 6053.5024 | 0.57156 | 0 | 0.042277 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1
ZN901:PA31 | SURRY HILLS | URBAN | 872 | 0 | 1244.571 | 1.7147 | 405.0541 | 0 | 1 | 47905 | 47905 | 0.99885 | 0.99885 | 0 | 0 | 0
ZN901:PA32 | SURRY HILLS | URBAN | 676 | 0 | 1957.7296 | 2.3815 | 197.1743 | 0 | 3 | 16790 | 16790 | 0.24556 | 0.24556 | 0 | 0 | 0
ZN901:PA33 | SURRY HILLS | URBAN | 56 | 0 | 4291.3314 | 2.191 | 3.5005 | 0 | 1 | 324 | 324 | 0.96429 | 0.96429 | 0 | 0 | 0
ZN901:PA8 | SURRY HILLS | URBAN | 715 | 0 | 3856.1611 | 5.144 | 6147.9324 | 0 | 2 | 242368.2167 | 242368.2167 | 0.28392 | 0.28392 | 0 | 0 | 0
ZN9035:PA1 | CARINGBAH | URBAN | 468 | 0 | 4973.8405 | 3.8866 | 930.3118 | 612.3372 | 3 | 48541 | 48541 | 1.0043 | 1.0043 | 1 | 31950 | 0.15171
ZN9035:PA11 | CARINGBAH | URBAN | 1936 | 3.2974 | 6188.9882 | 4.3629 | 973.0011 | 0 | 14 | 45226 | 23112.2333 | 0.17975 | 0.11674 | 0 | 0 | 0
ZN9035:PA2 | CARINGBAH | URBAN | 658 | 262.9944 | 4474.3817 | 2.7244 | 483.257 | 0 | 2 | 35971 | 35971 | 1.0152 | 1.0152 | 0 | 0 | 0
ZN9035:PA4 | CARINGBAH | URBAN | 1798 | 2570.7577 | 6003.1454 | 6.2872 | 3040.2943 | 13.0213 | 8 | 98064.55 | 98064.55 | 1.0189 | 1.0189 | 0 | 420 | 0.00055617
ZN9035:PA7 | CARINGBAH | URBAN | 596 | 0 | 2907.6291 | 1.4098 | 142.6025 | 0 | 4 | 20511.9 | 4941 | 0.24497 | 0.13591 | 0 | 0 | 0
ZN9037:PA10 | MIRANDA | URBAN | 1614 | 1160.3584 | 4333.0727 | 3.2388 | 2511.365 | 0 | 9 | 157242.9833 | 157242.9833 | 1.0824 | 1.0824 | 0 | 0 | 0
ZN9037:PA14 | MIRANDA | URBAN | 444 | 0 | 2365.5506 | 3.8104 | 0 | 284.1001 | 0 | 0 | 0 | 0 | 0 | 1 | 15120 | 0.031532
ZN9037:PA15 | MIRANDA | URBAN | 302 | 0 | 2310.5552 | 1.1431 | 0 | 170.4601 | 0 | 0 | 0 | 0 | 0 | 1 | 30240 | 0.18543
ZN9037:PA16 | MIRANDA | URBAN | 1238 | 1601.6885 | 2718.8164 | 2.572 | 334.1614 | 0 | 12 | 26347.1 | 25193.4167 | 0.39176 | 0.38934 | 0 | 0 | 0
ZN9037:PA2 | MIRANDA | URBAN | 1039 | 5445.313 | 604.5341 | 3.9057 | 2343.13 | 0 | 11 | 121661.4167 | 121661.4167 | 1.3455 | 1.3455 | 0 | 0 | 0
ZN9037:PA3 | MIRANDA | URBAN | 441 | 0 | 2035.5824 | 5.0488 | 6.9813 | 0 | 0 | 280.4167 | 280.4167 | 0.0022676 | 0.0022676 | 0 | 0 | 0
ZN9037:PA4 | MIRANDA | URBAN | 340 | 1167.635 | 1041.5363 | 1.6194 | 1.134 | 0 | 2 | 142 | 142 | 0.0088235 | 0.0088235 | 0 | 0 | 0
ZN9037:PA7 | MIRANDA | URBAN | 640 | 1856.3989 | 3291.0637 | 2.8578 | 2008.6131 | 0 | 3 | 142532.9833 | 142532.9833 | 2.0016 | 2.0016 | 0 | 0 | 0
ZN9037:PA8 | MIRANDA | URBAN | 1642 | 3951.7032 | 4227.202 | 5.0488 | 3619.2031 | 0 | 20 | 145370.8833 | 108410.8833 | 1.3563 | 1.3051 | 0 | 0 | 0
ZN9037:PA9 | MIRANDA | URBAN | 818 | 2968.3039 | 2057.6279 | 2.572 | 80.6565 | 0 | 9 | 6359.4 | 6045.8 | 0.06357 | 0.062347 | 0 | 0 | 0
ZN9118:PA11 | CRONULLA | URBAN | 1907 | 3823.0602 | 6360.4142 | 3.1626 | 3156.7182 | 0 | 13 | 202412.85 | 20152.85 | 0.49712 | 0.088096 | 0 | 0 | 0
ZN9118:PA12 | CRONULLA | URBAN | 1236 | 3.5085 | 3610.9406 | 4.0962 | 811.231 | 0 | 20 | 40162.1 | 39011.1 | 0.26942 | 0.26861 | 0 | 0 | 0
ZN9118:PA13 | CRONULLA | URBAN | 1170 | 0 | 4240.5404 | 2.8769 | 52.2145 | 0 | 6 | 3680.65 | 3680.65 | 0.04359 | 0.04359 | 0 | 0 | 0
ZN9118:PA15 | CRONULLA | URBAN | 1683 | 1045.518 | 6117.3569 | 2.7816 | 3.1221 | 0 | 2 | 227.6167 | 227.6167 | 0.0011884 | 0.0011884 | 0 | 0 | 0
ZN9118:PA16 | CRONULLA | URBAN | 1301 | 0 | 2390.7112 | 2.7054 | 9.9891 | 0 | 0 | 748.7667 | 748.7667 | 0.00076864 | 0.00076864 | 0 | 0 | 0
ZN9118:PA17 | CRONULLA | URBAN | 1018 | 6.5478 | 8409.3105 | 3.6961 | 278.8223 | 0 | 9 | 15298.05 | 15298.05 | 0.13458 | 0.13458 | 0 | 0 | 0
ZN9118:PA2 | CRONULLA | URBAN | 761 | 3.4747 | 3306.1021 | 2.0767 | 115.9252 | 0 | 9 | 11320.4 | 9791.0167 | 0.14455 | 0.14192 | 0 | 0 | 0
ZN9118:PA20 | CRONULLA | URBAN | 2100 | 0 | 5093.616 | 4.8964 | 730.4565 | 0 | 9 | 30253.2167 | 30253.2167 | 0.10381 | 0.10381 | 0 | 0 | 0
ZN9118:PA21 | CRONULLA | URBAN | 1318 | 3.2981 | 6050.8916 | 4.2295 | 1455.4724 | 0 | 26 | 69784.8833 | 48736.8833 | 0.26783 | 0.24962 | 0 | 0 | 0
ZN9118:PA22 | CRONULLA | URBAN | 1418 | 613.995 | 6174.1399 | 3.7342 | 215.6611 | 0 | 7 | 11711.8667 | 9871.9833 | 0.088858 | 0.087447 | 0 | 0 | 0
ZN9118:PA24 | CRONULLA | URBAN | 1338 | 0 | 3006.6206 | 3.3913 | 116.5021 | 798.6821 | 2 | 6966.65 | 6966.65 | 0.035874 | 0.035874 | 3 | 47760 | 0.095665
ZN9118:PA26 | CRONULLA | URBAN | 2099 | 6.1003 | 11378.3605 | 4.7058 | 373.7568 | 0 | 8 | 16106.55 | 16106.55 | 0.03192 | 0.03192 | 0 | 0 | 0
ZN9118:PA3 | CRONULLA | SHORT RURAL | 830 | 5044.264 | 5685.1661 | 3.9247 | 199.9024 | 0 | 9 | 10329.0667 | 8671.85 | 0.13855 | 0.13614 | 0 | 0 | 0
ZN9118:PA6 | CRONULLA | URBAN | 1728 | 0 | 4186.3033 | 4.4201 | 17.7456 | 411.9452 | 2 | 814.1667 | 814.1667 | 0.0011574 | 0.0011574 | 3 | 18900 | 0.035301
ZN9118:PA7 | CRONULLA | URBAN | 922 | 0 | 7676.4691 | 4.6677 | 2476.1283 | 45.5744 | 3 | 107576.5 | 107576.5 | 1.1421 | 1.1421 | 1 | 1980 | 0.0032538
ZN9118:PA8 | CRONULLA | URBAN | 1207 | 6.5981 | 7456.7448 | 4.7439 | 300.7878 | 0 | 10 | 12857.9333 | 12549.3 | 0.082022 | 0.081193 | 0 | 0 | 0
ZN9171:PA1 | LUCAS HEIGHTS | URBAN | 4 | 0 | 2869.5396 | 0.09526 | 0.1165 | 0 | 1 | 248 | 248 | 1 | 1 | 0 | 0 | 0
ZN9171:PA3 | LUCAS HEIGHTS | SHORT RURAL | 2 | 0 | 73.3811 | 0.5144 | 0.15727 | 0 | 0 | 62 | 62 | 0.5 | 0.5 | 0 | 0 | 0
ZN9245:PA10 | ENGADINE | URBAN | 1773 | 6554.5628 | 2981.5037 | 5.144 | 5933.3509 | 0 | 17 | 233908.8333 | 233908.8333 | 1.1077 | 1.1077 | 0 | 0 | 0
ZN9245:PA12 | ENGADINE | URBAN | 376 | 1087.694 | 980.8745 | 1.3336 | 141.2543 | 0 | 2 | 21479 | 21479 | 1.1144 | 1.1144 | 0 | 0 | 0
ZN9245:PA13 | ENGADINE | URBAN | 1238 | 1773.9477 | 3214.5859 | 3.6199 | 192.588 | 0 | 6 | 10789.1167 | 10789.1167 | 0.04685 | 0.04685 | 0 | 0 | 0
ZN9245:PA14 | ENGADINE | URBAN | 1045 | 3798.3032 | 3040.9054 | 3.0483 | 376.3868 | 0 | 10 | 25039.45 | 25039.45 | 0.18373 | 0.18373 | 0 | 0 | 0
ZN9245:PA15 | ENGADINE | URBAN | 1047 | 3632.263 | 3289.0193 | 2.8578 | 72.326 | 0 | 5 | 5132.3167 | 5132.3167 | 0.038204 | 0.038204 | 0 | 0 | 0
ZN9245:PA3 | ENGADINE | URBAN | 771 | 99.2652 | 3543.5355 | 2.9531 | 108.7139 | 73.3925 | 2 | 7465.5833 | 7465.5833 | 0.059663 | 0.059663 | 1 | 5040 | 0.018158
ZN9245:PA4 | ENGADINE | URBAN | 1626 | 4222.1394 | 11030.2103 | 5.2393 | 2216.294 | 0 | 3 | 85783.75 | 85783.75 | 1.0185 | 1.0185 | 0 | 0 | 0
ZN9245:PA8 | ENGADINE | SHORT RURAL | 1228 | 13009.2062 | 7371.045 | 3.9057 | 184.4733 | 133.4679 | 7 | 9578.3333 | 9578.3333 | 0.096906 | 0.096906 | 2 | 6930 | 0.011401
ZN9252:PA10 | JANNALI | URBAN | 1509 | 6082.6479 | 3100.5436 | 3.7151 | 1796.7299 | 2444.614 | 12 | 98075.05 | 80605 | 1.0371 | 1.006 | 2 | 133440 | 0.18423
ZN9252:PA11 | JANNALI | URBAN | 729 | 2619.4975 | 3189.3297 | 2.191 | 184.2939 | 0 | 5 | 17057.8167 | 715.1 | 0.049383 | 0.0041152 | 0 | 0 | 0
ZN9252:PA12 | JANNALI | URBAN | 1215 | 3416.1516 | 1808.7308 | 2.8578 | 3359.8749 | 0 | 15 | 238419.7333 | 238419.7333 | 1.3835 | 1.3835 | 0 | 0 | 0
ZN9252:PA16 | JANNALI | SHORT RURAL | 864 | 5170.1475 | 5746.8128 | 2.7625 | 0 | 161.8356 | 0 | 0 | 0 | 0 | 0 | 1 | 11880 | 0.025463
ZN9252:PA2 | JANNALI | URBAN | 1709 | 5259.8175 | 4014.4326 | 4.8583 | 12719.1039 | 0 | 16 | 530917.0667 | 530917.0667 | 3.7355 | 3.7355 | 0 | 0 | 0
ZN9252:PA3 | JANNALI | URBAN | 654 | 784.3451 | 3399.5874 | 1.4289 | 271.4594 | 0 | 1 | 38526 | 38526 | 1.0031 | 1.0031 | 0 | 0 | 0
ZN9252:PA4 | JANNALI | URBAN | 1281 | 2552.7688 | 3673.7062 | 3.1436 | 1588.0838 | 0 | 8 | 102447.1333 | 102447.1333 | 1.1483 | 1.1483 | 0 | 0 | 0
ZN9252:PA7 | JANNALI | URBAN | 585 | 2306.4461 | 1721.1243 | 1.6194 | 1556.7667 | 0 | 6 | 194946.2833 | 194946.2833 | 3.053 | 3.053 | 0 | 0 | 0
ZN9252:PA8 | JANNALI | URBAN | 1267 | 4131.3458 | 1320.0794 | 3.2388 | 1585.8555 | 0 | 6 | 99294.4667 | 99294.4667 | 0.26283 | 0.26283 | 0 | 0 | 0
ZN9252:PA9 | JANNALI | URBAN | 1517 | 2504.3072 | 5784.284 | 4.5725 | 1452.3901 | 0 | 9 | 64414.3167 | 14083.5833 | 0.12393 | 0.064601 | 0 | 0 | 0
ZN9301:PA13 | KURNELL | SHORT RURAL | 21 | 7678.9934 | 2557.3237 | 1.0479 | 53.2079 | 12.4012 | 8 | 10297.3167 | 10297.3167 | 2.4286 | 2.4286 | 1 | 2400 | 0.2381
ZN9301:PA15 | KURNELL | SHORT RURAL | 244 | 2610.9395 | 3058.421 | 0.66682 | 0.61571 | 0 | 0 | 187.25 | 187.25 | 0.0040984 | 0.0040984 | 0 | 0 | 0
ZN9301:PA8 | KURNELL | URBAN | 724 | 4230.0048 | 4018.309 | 4.5725 | 1855.084 | 0 | 8 | 82274.0167 | 82274.0167 | 1.0014 | 1.0014 | 0 | 0 | 0
ZN931:PA11 | DARLINGHURST | URBAN | 1613 | 0 | 1776.3165 | 2.6673 | 4.769 | 0 | 2 | 362.5833 | 362.5833 | 0.0012399 | 0.0012399 | 0 | 0 | 0
ZN931:PA12 | DARLINGHURST | URBAN | 413 | 0 | 1313.8972 | 2.0957 | 5.018 | 0 | 3 | 485.5667 | 485.5667 | 0.0072639 | 0.0072639 | 0 | 0 | 0
ZN931:PA13 | DARLINGHURST | URBAN | 497 | 0 | 2864.5089 | 4.4772 | 1006.1114 | 2.6493 | 1 | 45571 | 45571 | 0.99799 | 0.99799 | 0 | 120 | 0.0020121
ZN931:PA18 | DARLINGHURST | URBAN | 588 | 0 | 2588.9129 | 4.0962 | 996.5449 | 0 | 4 | 49336.55 | 49336.55 | 0.18878 | 0.18878 | 0 | 0 | 0
ZN931:PA2 | DARLINGHURST | URBAN | 2235 | 0 | 3774.5829 | 4.2867 | 356.8162 | 0 | 1 | 16880 | 16880 | 0.0044743 | 0.0044743 | 0 | 0 | 0
ZN931:PA25 | DARLINGHURST | URBAN | 1572 | 0 | 3067.7915 | 4.8583 | 0 | 63.2461 | 0 | 0 | 0 | 0 | 0 | 1 | 2640 | 0.013995
ZN931:PA26 | DARLINGHURST | URBAN | 214 | 0 | 2080.9624 | 1.2384 | 3.5419 | 0 | 1 | 580 | 580 | 0.093458 | 0.093458 | 0 | 0 | 0
ZN931:PA31 | DARLINGHURST | URBAN | 304 | 0 | 1485.7389 | 3.2388 | 0 | 3.8331 | 0 | 0 | 0 | 0 | 0 | 1 | 240 | 0.0065789
ZN931:PA7 | DARLINGHURST | URBAN | 486 | 0 | 978.8999 | 2.191 | 4.7779 | 0 | 2 | 442.2333 | 442.2333 | 0.0041152 | 0.0041152 | 0 | 0 | 0
ZN931:PA8 | DARLINGHURST | URBAN | 184 | 0 | 249.9321 | 0.57156 | 0 | 56.6509 | 0 | 0 | 0 | 0 | 0 | 1 | 20100 | 0.36413
ZN9550:PA1 | GWAWLEY BAY | URBAN | 825 | 1.6485 | 3985.0959 | 2.21 | 891.2209 | 0 | 5 | 81778.2333 | 81778.2333 | 0.51394 | 0.51394 | 0 | 0 | 0
ZN9550:PA11 | GWAWLEY BAY | URBAN | 451 | 0 | 5811.1202 | 2.4196 | 16.9544 | 0 | 4 | 1420.9833 | 1420.9833 | 0.044346 | 0.044346 | 0 | 0 | 0
ZN9550:PA27 | GWAWLEY BAY | URBAN | 152 | 0 | 5342.8963 | 3.4675 | 9.038 | 0 | 2 | 528.5833 | 528.5833 | 0.013158 | 0.013158 | 0 | 0 | 0
ZN9550:PA28 | GWAWLEY BAY | URBAN | 854 | 1.6498 | 4249.6484 | 1.8671 | 767.7859 | 0 | 2 | 83392 | 83392 | 0.18267 | 0.18267 | 0 | 0 | 0
ZN9550:PA29 | GWAWLEY BAY | URBAN | 443 | 580.9879 | 1437.9957 | 1.2003 | 163.3773 | 0 | 2 | 27603.3333 | 27603.3333 | 0.44695 | 0.44695 | 0 | 0 | 0
ZN9550:PA3 | GWAWLEY BAY | URBAN | 1289 | 1097.8242 | 2385.8171 | 4.1724 | 826.5551 | 0 | 2 | 40173.35 | 1300.3 | 0.065167 | 0.0007758 | 0 | 0 | 0
ZN9550:PA33 | GWAWLEY BAY | URBAN | 474 | 3.3733 | 5299.6067 | 2.7244 | 575.5214 | 0 | 3 | 42838.65 | 34057.65 | 0.32068 | 0.22574 | 0 | 0 | 0
ZN9550:PA36 | GWAWLEY BAY | URBAN | 748 | 2981.8857 | 1025.6964 | 2.6101 | 771.3457 | 0 | 7 | 59929.25 | 55407.25 | 0.35963 | 0.30882 | 0 | 0 | 0
ZN9550:PA41 | GWAWLEY BAY | URBAN | 45 | 0 | 3266.4796 | 1.8671 | 0 | 19.0584 | 0 | 0 | 0 | 0 | 0 | 0 | 2070 | 0.022222
ZN9550:PA42 | GWAWLEY BAY | URBAN | 920 | 1107.0588 | 2546.3293 | 2.572 | 295.9774 | 0 | 8 | 23336.4667 | 23336.4667 | 0.053261 | 0.053261 | 0 | 0 | 0
ZN9550:PA43 | GWAWLEY BAY | URBAN | 1051 | 2137.5998 | 2269.3269 | 2.9721 | 580.3154 | 1725.2995 | 7 | 39595.8667 | 39595.8667 | 1.0314 | 1.0314 | 2 | 117720 | 0.20171
ZN9550:PA6 | GWAWLEY BAY | URBAN | 930 | 5.125 | 3964.1451 | 2.2862 | 340.1438 | 0 | 5 | 30171.1333 | 30171.1333 | 0.083871 | 0.083871 | 0 | 0 | 0
ZN9550:PA9 | GWAWLEY BAY | URBAN | 500 | 6.6829 | 2665.4746 | 1.9814 | 429.9485 | 0 | 5 | 44004.1333 | 42912.8833 | 0.36 | 0.358 | 0 | 0 | 0
ZN965:PA11 | PENNANT HILLS | URBAN | 1144 | 3921.6378 | 5501.563 | 4.6677 | 260.1738 | 0 | 7 | 11303.3667 | 10987.9167 | 0.063811 | 0.062937 | 0 | 0 | 0
ZN965:PA15 | PENNANT HILLS | URBAN | 1205 | 4714.7792 | 5725.1842 | 4.6868 | 2576.4415 | 0 | 10 | 111479.6333 | 111479.6333 | 1.1876 | 1.1876 | 0 | 0 | 0
ZN965:PA2 | PENNANT HILLS | URBAN | 532 | 140.9604 | 6054.9825 | 1.8099 | 457.7593 | 0 | 8 | 51288.9667 | 51288.9667 | 0.20301 | 0.20301 | 0 | 0 | 0
ZN965:PA20 | PENNANT HILLS | URBAN | 963 | 0 | 8291.2247 | 3.1055 | 405.342 | 0 | 6 | 26469.4167 | 26469.4167 | 1.0478 | 1.0478 | 0 | 0 | 0
ZN965:PA21 | PENNANT HILLS | URBAN | 678 | 2.7254 | 5128.594 | 3.9057 | 1419.5788 | 0 | 12 | 73708.2333 | 49003.3 | 1.3142 | 1.2434 | 0 | 0 | 0
ZN965:PA22 | PENNANT HILLS | URBAN | 569 | 5.9334 | 4294.8568 | 3.1817 | 2083.7516 | 0 | 12 | 132812.7667 | 132812.7667 | 2.3374 | 2.3374 | 0 | 0 | 0
ZN965:PA24 | PENNANT HILLS | SHORT RURAL | 950 | 0 | 10702.7483 | 3.7532 | 452.0912 | 266.513 | 6 | 24427 | 24427 | 1.0905 | 1.0905 | 1 | 14400 | 0.050526
ZN965:PA26 | PENNANT HILLS | URBAN | 905 | 1841.0101 | 8781.0149 | 3.4484 | 2586.356 | 0 | 7 | 152096.8 | 68164.8 | 3.0939 | 2.0939 | 0 | 0 | 0
ZN965:PA28 | PENNANT HILLS | URBAN | 984 | 0 | 11297.4757 | 6.4967 | 228.4597 | 1835.6871 | 4 | 7131.25 | 7131.25 | 0.079268 | 0.079268 | 3 | 57300 | 0.15142
ZN965:PA29 | PENNANT HILLS | URBAN | 744 | 55.7436 | 6257.2448 | 2.8387 | 34.7312 | 0 | 2 | 2481.1 | 2481.1 | 0.043011 | 0.043011 | 0 | 0 | 0
ZN965:PA3 | PENNANT HILLS | URBAN | 980 | 4.2311 | 5294.8055 | 3.4294 | 254.1535 | 0 | 8 | 15029.1333 | 15029.1333 | 0.12653 | 0.12653 | 0 | 0 | 0
ZN965:PA33 | PENNANT HILLS | URBAN | 1265 | 4662.4179 | 7163.5142 | 5.4298 | 3217.3632 | 11.2456 | 18 | 120161.5667 | 119821.5667 | 1.2277 | 1.2245 | 0 | 420 | 0.00079051
ZN965:PA35 | PENNANT HILLS | URBAN | 911 | 125.4885 | 6541.3434 | 3.0864 | 2093.0456 | 0 | 7 | 137522.5833 | 123098.7333 | 1.1515 | 1.1218 | 0 | 0 | 0
ZN965:PA37 | PENNANT HILLS | URBAN | 473 | 0 | 5549.8769 | 4.763 | 220.1807 | 521.4139 | 4 | 9374.5333 | 9374.5333 | 0.1945 | 0.1945 | 2 | 22200 | 0.10148
ZN965:PA38 | PENNANT HILLS | URBAN | 971 | 0 | 11312.4131 | 4.6868 | 3562.7606 | 821.6074 | 13 | 154156.5167 | 154156.5167 | 0.46138 | 0.46138 | 2 | 35550 | 0.086509
ZN965:PA42 | PENNANT HILLS | URBAN | 1104 | 88.8318 | 7251.6282 | 3.1817 | 531.862 | 0 | 5 | 33899.4667 | 33899.4667 | 0.25362 | 0.25362 | 0 | 0 | 0
ZN965:PA43 | PENNANT HILLS | URBAN | 1021 | 2942.3419 | 7778.9946 | 4.6106 | 3866.6268 | 0 | 10 | 170069.8167 | 170069.8167 | 2.0989 | 2.0989 | 0 | 0 | 0
ZN965:PA46 | PENNANT HILLS | URBAN | 1383 | 35.4441 | 9762.3324 | 5.3536 | 1157.3126 | 920.2871 | 5 | 43838.4 | 43838.4 | 0.048445 | 0.048445 | 2 | 34860 | 0.060014
ZN965:PA47 | PENNANT HILLS | URBAN | 1085 | 36.3163 | 6556.9056 | 4.8202 | 1309.8341 | 0 | 10 | 55106.9167 | 55106.9167 | 0.26544 | 0.26544 | 0 | 0 | 0
ZN965:PA6 | PENNANT HILLS | URBAN | 1037 | 1495.6993 | 7885.3234 | 3.2769 | 382.6645 | 151.2495 | 7 | 23681 | 23596 | 0.14754 | 0.14658 | 1 | 9360 | 0.023144
ZN965:PA8 | PENNANT HILLS | URBAN | 1187 | 3.2983 | 8928.406 | 4.2867 | 1456.1393 | 71.025 | 13 | 68885.9667 | 68885.9667 | 0.21735 | 0.21735 | 1 | 3360 | 0.023589
ZN9700:PA11 | KIRRAWEE | URBAN | 1980 | 2154.391 | 5635.1149 | 3.6199 | 2748.8164 | 0 | 7 | 153993.5333 | 153993.5333 | 1.9571 | 1.9571 | 0 | 0 | 0
ZN9700:PA12 | KIRRAWEE | URBAN | 1002 | 95.2628 | 4712.6314 | 4.6677 | 1264.805 | 923.9173 | 7 | 54950.0167 | 54950.0167 | 1.1028 | 1.1028 | 2 | 40140 | 0.12375
ZN9700:PA15 | KIRRAWEE | URBAN | 1221 | 1059.6524 | 6807.4538 | 3.2388 | 297.8058 | 0 | 6 | 18646.3833 | 18646.3833 | 0.09009 | 0.09009 | 0 | 0 | 0
ZN9700:PA16 | KIRRAWEE | URBAN | 786 | 854.8647 | 2579.3118 | 1.9052 | 158.1397 | 0 | 4 | 16832.6 | 16832.6 | 1.0025 | 1.0025 | 0 | 0 | 0
ZN9700:PA17 | KIRRAWEE | URBAN | 2139 | 4601.7948 | 6400.7622 | 5.144 | 9450.5947 | 1072.9853 | 14 | 372568.15 | 171279.6333 | 2.0234 | 1.0075 | 2 | 42300 | 0.048153
ZN9700:PA18 | KIRRAWEE | URBAN | 1164 | 1475.9695 | 2584.5324 | 2.2862 | 275.5771 | 0 | 1 | 24444 | 24444 | 1 | 1 | 0 | 0 | 0
ZN9700:PA20 | KIRRAWEE | URBAN | 1789 | 7801.295 | 5865.2983 | 4.6677 | 7275.4889 | 82.8625 | 5 | 316086.8667 | 316086.8667 | 2.0179 | 2.0179 | 1 | 3600 | 0.0027949
ZN9700:PA21 | KIRRAWEE | URBAN | 483 | 570.7687 | 3597.499 | 2.0957 | 3.0734 | 0 | 0 | 297.4 | 297.4 | 0.0020704 | 0.0020704 | 0 | 0 | 0
ZN9700:PA22 | KIRRAWEE | URBAN | 224 | 256.1047 | 1178.7242 | 1.3336 | 0.63221 | 93.9109 | 0 | 96.1333 | 96.1333 | 0.0044643 | 0.0044643 | 1 | 14280 | 0.15179
ZN9700:PA23 | KIRRAWEE | URBAN | 1680 | 3477.4205 | 3249.2781 | 4.382 | 7280.2097 | 1402.1525 | 16 | 336919.7 | 317843.5167 | 3.1923 | 3.1565 | 4 | 64890 | 0.082738
ZN9700:PA24 | KIRRAWEE | URBAN | 1396 | 2968.5586 | 3542.0164 | 3.8104 | 1303.273 | 0 | 6 | 69361.0667 | 32566.5667 | 1.0423 | 1.0208 | 0 | 0 | 0
ZN9900:PA13 | MENAI | URBAN | 823 | 0 | 5372.768 | 3.0293 | 319.0396 | 0 | 5 | 21357.8667 | 21357.8667 | 0.15188 | 0.15188 | 0 | 0 | 0
ZN9900:PA17 | MENAI | URBAN | 826 | 747.1578 | 9349.3754 | 4.6296 | 0 | 335.5933 | 0 | 0 | 0 | 0 | 0 | 1 | 14700 | 0.059322
ZN9900:PA19 | MENAI | URBAN | 700 | 1756.5061 | 6549.3634 | 2.6673 | 1292.6361 | 0 | 5 | 98278.5167 | 98278.5167 | 1.0557 | 1.0557 | 0 | 0 | 0
ZN9900:PA2 | MENAI | URBAN | 659 | 0 | 5948.0648 | 2.6482 | 14.3802 | 0 | 2 | 1101.1833 | 1101.1833 | 0.0030349 | 0.0030349 | 0 | 0 | 0
ZN9900:PA21 | MENAI | URBAN | 779 | 0 | 5847.1743 | 2.4006 | 251.7287 | 0 | 3 | 21265.35 | 21265.35 | 0.094994 | 0.094994 | 0 | 0 | 0
ZN9900:PA3 | MENAI | URBAN | 921 | 0 | 5656.6568 | 3.4865 | 18.4763 | 0 | 0 | 1074.6667 | 1074.6667 | 0.0010858 | 0.0010858 | 0 | 0 | 0
ZN9900:PA5 | MENAI | URBAN | 459 | 0 | 3820.6014 | 1.7718 | 22.2621 | 226.4684 | 2 | 2547.9667 | 2547.9667 | 0.076253 | 0.076253 | 1 | 25920 | 0.15686
ZN9900:PA6 | MENAI | URBAN | 701 | 219.5566 | 6388.2421 | 2.8769 | 99.8828 | 127.676 | 2 | 7040.8333 | 7040.8333 | 0.0085592 | 0.0085592 | 3 | 9000 | 0.024251
ZN9900:PA8 | MENAI | URBAN | 1161 | 983.997 | 11295.1124 | 5.2012 | 1062.1585 | 600.1615 | 6 | 41413.0333 | 41413.0333 | 0.18088 | 0.18088 | 1 | 23400 | 0.055986
217:33608 | MOUNT HUTTON 33 | URBAN | 693 | 81.8182 | 6479.5654 | 3.1245 | 0 | 208.6952 | 0 | 0 | 0 | 0 | 0 | 1 | 13545 | 0.090909
224:80344 | ARGENTON 132 11 | URBAN | 69 | 0 | 3527.155 | 5.1631 | 3.0013 | 0 | 0 | 117.8833 | 117.8833 | 0.014493 | 0.014493 | 0 | 0 | 0
243:80078 | MORISSET 132 | URBAN | 1066 | 3710.11 | 6344.0709 | 2.0767 | 616.4775 | 0 | 5 | 60200.6333 | 60200.6333 | 0.92495 | 0.92495 | 0 | 0 | 0
243:80081 | MORISSET 132 | URBAN | 1805 | 16361.9787 | 5197.2565 | 5.8871 | 5371.5999 | 0 | 12 | 185035.7 | 184963.6 | 0.62881 | 0.62825 | 0 | 0 | 0
264:81232 | RAYMOND TERRACE 33 | URBAN | 786 | 7687.4112 | 1377.9686 | 4.6868 | 2138.6781 | 1290.5361 | 19 | 92538.1167 | 92045.8667 | 2.3295 | 2.327 | 4 | 55840 | 0.47074
264:81238 | RAYMOND TERRACE 33 | URBAN | 589 | 5627.5212 | 440.5223 | 2.1529 | 476.3938 | 44.9064 | 7 | 44874.3333 | 44874.3333 | 1.2496 | 1.2496 | 2 | 4230 | 0.23939
524:33574 | NULKABA 33 | SHORT RURAL | 55 | 1692.3058 | 517.5919 | 0.09526 | 0 | 0.30064 | 0 | 0 | 0 | 0 | 0 | 1 | 640 | 0.072727
ZN10999:PA30 | KOGARAH | SHORT RURAL | 75 | 1357.7165 | 1152.3593 | 1.9433 | 0 | 12.9367 | 0 | 0 | 0 | 0 | 0 | 1 | 1350 | 0.04
ZN12650:PA16 | WEST GOSFORD | URBAN | 143 | 0 | 974.9144 | 2.6482 | 0 | 261.6991 | 0 | 0 | 0 | 0 | 0 | 2 | 20040 | 0.27972
ZN1285:PA22 | GREENACRE PARK | URBAN | 614 | 0 | 2265.3229 | 4.3248 | 172.4231 | 0 | 1 | 8085 | 8085 | 0.089577 | 0.089577 | 0 | 0 | 0
ZN14143:PA21 | SOMERSBY | URBAN | 36 | 1968.3474 | 1526.0502 | 1.3336 | 16.316 | 0 | 1 | 2481 | 2481 | 1 | 1 | 0 | 0 | 0
ZN14892:PA9 | CHARMHAVEN | URBAN | 702 | 698.2103 | 4273.3046 | 1.5242 | 2.0337 | 0 | 2 | 270.5833 | 270.5833 | 0.002849 | 0.002849 | 0 | 0 | 0
ZN15011:PA4 | BEACON HILL | URBAN | 56 | 319.2209 | 1319.6562 | 3.6008 | 0 | 11.8079 | 0 | 0 | 0 | 0 | 0 | 1 | 665 | 0.33929
ZN1600:PA24DEF | CITY EAST | CBD | 122 | 0 | 3250.6784 | 6.6682 | 0 | 1381.0423 | 0 | 0 | 0 | 0 | 0 | 1 | 42000 | 0.20492
ZN1610:PA4 | HOMEBUSH BAY | URBAN | 44 | 0 | 2812.6234 | 3.3341 | 0 | 41.4313 | 0 | 0 | 0 | 0 | 0 | 1 | 2520 | 0.95455
ZN1648:PA10 | ENFIELD | URBAN | 471 | 0 | 4499.0561 | 2.191 | 1.3703 | 0 | 0 | 126.8333 | 126.8333 | 0.0021231 | 0.0021231 | 0 | 0 | 0
ZN180:PA35 | MOSMAN | URBAN | 1389 | 0 | 4945.1284 | 2.934 | 139.3349 | 0 | 2 | 9630.5167 | 9630.5167 | 0.071994 | 0.071994 | 0 | 0 | 0
ZN187:PA26 | CROWS NEST | URBAN | 256 | 0 | 577.102 | 1.9052 | 22.8858 | 0 | 1 | 2436 | 2436 | 0.082031 | 0.082031 | 0 | 0 | 0
ZN188:PA32 | ZETLAND | URBAN | 868 | 0 | 3899.3512 | 5.4298 | 169.0325 | 0 | 1 | 6313 | 6313 | 0.067972 | 0.067972 | 0 | 0 | 0
ZN2196:PA28 | MILPERRA | URBAN | 135 | 0 | 4276.7134 | 3.1817 | 0 | 51.775 | 0 | 0 | 0 | 0 | 0 | 1 | 3300 | 0.16296
ZN2196:PA4 | MILPERRA | URBAN | 28 | 0 | 1069.3847 | 1.829 | 21.2866 | 0 | 2 | 2360.1833 | 2360.1833 | 0.071429 | 0.071429 | 0 | 0 | 0
ZN2466:PA25 | FLEMINGTON | URBAN | 1170 | 0 | 5873.5523 | 2.0576 | 5.8372 | 0 | 0 | 575.3 | 575.3 | 0.0008547 | 0.0008547 | 0 | 0 | 0
ZN2835:PA29 | BURWOOD | URBAN | 930 | 0 | 3566.3051 | 3.2388 | 277.6948 | 0 | 4 | 17387.1833 | 17387.1833 | 0.16452 | 0.16452 | 0 | 0 | 0
ZN3155:PA30 | DOUBLE BAY | URBAN | 197 | 0 | 1960.8352 | 4.8583 | 40.4392 | 0 | 2 | 1688 | 1688 | 0.040609 | 0.040609 | 0 | 0 | 0
ZN3425:PA23 | CASTLE COVE | URBAN | 779 | 0 | 2870.1739 | 2.4006 | 1.4323 | 0 | 2 | 121 | 121 | 0.0025674 | 0.0025674 | 0 | 0 | 0
ZN3425:PA36 | CASTLE COVE | URBAN | 4 | 0 | 2024.9425 | 3.4675 | 2.3254 | 0 | 1 | 136 | 136 | 1 | 1 | 0 | 0 | 0
ZN3425:PA39 | CASTLE COVE | URBAN | 683 | 0 | 2631.3184 | 1.7147 | 202.4213 | 0 | 1 | 23940 | 23940 | 1.0015 | 1.0015 | 0 | 0 | 0
ZN3425:PA46 | CASTLE COVE | URBAN | 301 | 0 | 2545.9452 | 2.21 | 118.091 | 24.8475 | 1 | 10836 | 10836 | 1 | 1 | 1 | 2280 | 0.063123
ZN342:PA21 | PADDINGTON | URBAN | 900 | 0 | 2856.2657 | 2.4768 | 0.70837 | 0 | 0 | 58 | 58 | 0.0011111 | 0.0011111 | 0 | 0 | 0
ZN35800:PA2 | BANKSTOWN | URBAN | 73 | 0 | 1799.2535 | 1.8671 | 36.6068 | 0 | 1 | 3976 | 3976 | 0.19178 | 0.19178 | 0 | 0 | 0
ZN384:PA2 | CAMPERDOWN | URBAN | 35 | 0 | 1703.4248 | 4.0009 | 2.0124 | 0 | 1 | 102 | 102 | 0.97143 | 0.97143 | 0 | 0 | 0
ZN384:PA37 | CAMPERDOWN | URBAN | 188 | 0 | 1055.3657 | 3.7151 | 250.8734 | 0 | 1 | 13694 | 13694 | 0.8883 | 0.8883 | 0 | 0 | 0
ZN384:PA42 | CAMPERDOWN | URBAN | 2 | 0 | 930.5121 | 1.3336 | 1.3679 | 0 | 1 | 208 | 208 | 1 | 1 | 0 | 0 | 0
ZN3922:PA23 | DRUMMOYNE | URBAN | 705 | 0 | 2648.2902 | 1.4289 | 8.8922 | 0 | 1 | 1262 | 1262 | 0.0028369 | 0.0028369 | 0 | 0 | 0
ZN4545:PA29 | MEADOWBANK | URBAN | 558 | 461.656 | 3533.9896 | 4.7249 | 2465.5368 | 0 | 5 | 105820.5833 | 105820.5833 | 1.2814 | 1.2814 | 0 | 0 | 0
ZN4990:PA53 54KLM | CITY CENTRAL | CBD | 906 | 0 | 4076.1295 | 9.4307 | 1639.7017 | 0 | 1 | 35259 | 35259 | 0.023179 | 0.023179 | 0 | 0 | 0
ZN5868:PA24 | GORE HILL | URBAN | 59 | 0 | 1666.4156 | 4.2867 | 0 | 47.5614 | 0 | 0 | 0 | 0 | 0 | 1 | 2250 | 0.15254
ZN711:PA12 | BLACKWATTLE BAY | URBAN | 289 | 0 | 799.902 | 2.191 | 0 | 5.186 | 0 | 0 | 0 | 0 | 0 | 1 | 480 | 0.0069204
ZN711:PA21 | BLACKWATTLE BAY | URBAN | 1137 | 0 | 4720.3618 | 2.9531 | 511.5343 | 0 | 1 | 35128 | 35128 | 1 | 1 | 0 | 0 | 0
ZN711:PA34 | BLACKWATTLE BAY | URBAN | 415 | 0 | 2879.524 | 3.4294 | 0 | 150.9282 | 0 | 0 | 0 | 0 | 0 | 1 | 8925 | 0.86024
ZN7900:PA24 | CAMPBELL ST | URBAN | 728 | 0 | 1988.4161 | 3.9057 | 43.6419 | 0 | 1 | 2266 | 2266 | 0.01511 | 0.01511 | 0 | 0 | 0
ZN8000:PA12 | MACQUARIE PARK | URBAN | 51 | 0 | 3755.2267 | 4.2105 | 1.6818 | 0 | 0 | 81 | 81 | 0.019608 | 0.019608 | 0 | 0 | 0
ZN8100:PA1 | GREEN SQUARE | URBAN | 212 | 0 | 1468.0504 | 1.4289 | 0 | 20.2929 | 0 | 0 | 0 | 0 | 0 | 1 | 2880 | 0.028302
ZN8700:PA65 66K | CITY NORTH NEW 132kv 11kv | CBD | 288 | 0 | 4382.0111 | 6.592 | 23.7295 | 0 | 1 | 730 | 730 | 0.034722 | 0.034722 | 0 | 0 | 0
ZN874:PA9 | CONCORD | URBAN | 299 | 0 | 2982.1978 | 3.0483 | 0 | 0.30064 | 0 | 0 | 0 | 0 | 0 | 2 | 20 | 0.006689
ZN901:PA24 | SURRY HILLS | URBAN | 76 | 0 | 869.3036 | 1.9052 | 141.2797 | 0 | 1 | 15038 | 15038 | 0.96053 | 0.96053 | 0 | 0 | 0
ZN901:PA7 | SURRY HILLS | URBAN | 15 | 0 | 2024.575 | 1.7147 | 0 | 0.63415 | 0 | 0 | 0 | 0 | 0 | 1 | 75 | 0.33333
ZN9245:PA11 | ENGADINE | URBAN | 999 | 42.4516 | 5015.0689 | 2.7625 | 6.8337 | 0 | 0 | 501.65 | 501.65 | 0.001001 | 0.001001 | 0 | 0 | 0
ZN931:PA3 | DARLINGHURST | URBAN | 458 | 0 | 1601.6894 | 4.2867 | 1868.4657 | 0 | 3 | 88392 | 88392 | 0.56987 | 0.56987 | 0 | 0 | 0
ZN931:PA4 | DARLINGHURST | URBAN | 240 | 0 | 1043.6159 | 2.9531 | 0 | 73.3925 | 0 | 0 | 0 | 0 | 0 | 1 | 5040 | 0.05
ZN1610:PA16 | HOMEBUSH BAY | URBAN | 2 | 0 | 4998.1405 | 2.572 | 7.3562 | 0 | 1 | 580 | 580 | 5 | 5 | 0 | 0 | 0
Contents

## 5c. Network data outages
Ausgrid
Network data
2012-13
Causes of Outages
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Causes of unplanned sustained outages
Cause of outage | Number of outages
Weather | 0
Equipment failure | 4
Operational error | 0
Vegetation | 0
Animals | 0
Third party impacts | 0
Transmission failure | 0
Load shedding | 0
Inter-distributor connection failure | 0
Other | 6
Contents

## 5d. Outcomes planned outages
Ausgrid
Planned Outages
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Planned outages
Network categorisation
Planned outages | CBD | Urban | Rural short | Rural long | Whole network
SAIDI - after removing excluded events | 28.353 | 19.6412 | 146.3461 | 303.0339 | 35.5662
SAIFI - after removing excluded events | 4.0635 | 5.786 | 43.3443 | 99.0384 | 10.4343
Contents

## 6. Weighted av cost of debt
Ausgrid
Weighted average cost of debt
2012-13
This information will be used to compare the DBs cost against the benchmark cost of debt. There is no intention to set the regulated cost of debt for a business based on its actual cost of debt.
Note: the specific method of calculating the weighted average cost of debt for the financial year is Ausgrid's choice but must be fully described. If the description of the methodology cannot fit in this worksheet, Ausgrid can provide details as a separate attachment.
Table 1: Cost of debt
Weighted average cost of debt (%) | 2012-13 | Explanation of calculation method
| 7.592% | Total interest expense for year net of interest received over average monthly debt net of deposits held
Contents

## 7. Asset installation
Ausgrid
Asset Installation
2012-13
This information is used in the AER’s replacement capex model. The model is used by the AER to assess forecast replacement capex proposals. It may also be used to monitor the asset age profile of the business over time. This will be used as a tool to monitor any improvements/deterioration in the overall asset age where capex has been approved to address network asset age.
Table 1: Asset age profile for distribution system assets
Asset group/category | Replacement life (years) |  | Actual replacement volumes (number of assets replaced) | Replacement unit cost | Asset failures | Total quantity | Year commissioned (number of assets commissioned in each year)
| Mean | Standard deviation |  |  |  |  | 1910 | 1911 | 1912 | 1913 | 1914 | 1915 | 1916 | 1917 | 1918 | 1919 | 1920 | 1921 | 1922 | 1923 | 1924 | 1925 | 1926 | 1927 | 1928 | 1929 | 1930 | 1931 | 1932 | 1933 | 1934 | 1935 | 1936 | 1937 | 1938 | 1939 | 1940 | 1941 | 1942 | 1943 | 1944 | 1945 | 1946 | 1947 | 1948 | 1949 | 1950 | 1951 | 1952 | 1953 | 1954 | 1955 | 1956 | 1957 | 1958 | 1959 | 1960 | 1961 | 1962 | 1963 | 1964 | 1965 | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | Quantity of Unknown Age
Poles
steel towers | 47.25 | 1.6394 | 2 | 500000 | 150 | 737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 109 | 51 | 89 | 4 | 42 | 95 | 30 | 15 | 81 | 1 | 0 | 75 | 25 | 34 | 0 | 0 | 1 | 2 | 27 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Sub-Trans Poles | 35.3588 | 13.9915 | 495 | 26200 | 944 | 29042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 17 | 62 | 441 | 320 | 128 | 347 | 584 | 890 | 1137 | 875 | 897 | 716 | 1199 | 811 | 805 | 252 | 492 | 409 | 755 | 472 | 417 | 383 | 471 | 411 | 1116 | 973 | 388 | 323 | 445 | 420 | 196 | 264 | 341 | 391 | 446 | 258 | 364 | 259 | 231 | 133 | 207 | 142 | 374 | 435 | 408 | 590 | 534 | 641 | 612 | 781 | 542 | 694 | 1174 | 1015 | 642 | 279 |  | 1
HV Poles | 37.1812 | 12.3999 | 2007 | 10700 | 3687 | 131103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 12 | 0 | 0 | 1 | 27 | 0 | 1 | 2 | 17 | 39 | 26 | 122 | 118 | 259 | 730 | 1378 | 2099 | 1108 | 2035 | 2748 | 4169 | 3600 | 4385 | 3728 | 2190 | 3833 | 3154 | 3545 | 2328 | 3035 | 3371 | 1967 | 2190 | 1894 | 2236 | 2198 | 3074 | 3868 | 2665 | 1565 | 2460 | 2801 | 2664 | 1965 | 2096 | 2599 | 2609 | 1585 | 1441 | 1786 | 2017 | 1649 | 1256 | 1583 | 1492 | 2309 | 1621 | 1695 | 1581 | 2117 | 1957 | 2003 | 2174 | 2389 | 2894 | 2734 | 2838 | 2834 | 2232 |  | 3
LV Poles | 40.5784 | 12.912 | 3479 | 10700 | 6937 | 289079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 0 | 9 | 0 | 665 | 770 | 36 | 163 | 887 | 600 | 1297 | 663 | 3435 | 667 | 2463 | 4803 | 7850 | 6411 | 9757 | 7884 | 14770 | 10225 | 14449 | 11631 | 13162 | 10396 | 7198 | 5993 | 6860 | 7157 | 3662 | 4641 | 3794 | 2691 | 4039 | 3438 | 4658 | 5686 | 6093 | 6921 | 4769 | 2725 | 3491 | 3798 | 4514 | 2977 | 3331 | 4167 | 3971 | 1852 | 1862 | 2724 | 3102 | 3075 | 2065 | 1988 | 1516 | 2154 | 1551 | 1797 | 1955 | 2473 | 2271 | 2696 | 3173 | 3278 | 3140 | 3830 | 4026 | 4311 | 3361 |  | 14
Pole top structures
steel towers | NC | NC | NC | NC | NC | 0
Sub-Trans Poles | NC | NC | NC | NC | NC | 0
HV Poles | NC | NC | NC | NC | NC | 0
LV Poles | NC | NC | NC | NC | NC | 0
Conductors
132 kV O/H ccts | NC | NC | NC | NC | 253 | 1128.4904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8406 | 0 | 0 | 0 | 188.9881 | 54.7362 | 10.2861 | 62.4286 | 50.9699 | 14.6377 | 0.39252 | 8.5549 | 117.6344 | 13.0629 | 23.5078 | 19.9914 | 32.1693 | 25.9663 | 32.222 | 12.9187 | 26.6945 | 20.4072 | 28.8447 | 29.0204 | 0.69606 | 2.118 | 16.3935 | 8.7828 | 0.21074 | 50.6885 | 4.5007 | 3.9322 | 6.2282 | 0 | 0 | 0 | 0 | 0 | 0 | 35.4855 | 0 | 1.6917 | 4.6546 | 0 | 4.4363 | 3.5237 | 13.5115 | 20.5469 | 11.0098 | 2.7979 | 1.4603 | 7.5957 | 7.5308 | 3.1407 | 16.7569 | 75.9676 | 21.8399 | 15.1347 |  | 0.58074
66 kV O/H ccts | NC | NC | NC | NC | 133 | 446.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.175 | 0 | 0 | 0 | 21.0931 | 0 | 0 | 19.0042 | 22.9713 | 0.15071 | 0.37235 | 0.038097 | 20.3433 | 10.9234 | 7.6094 | 0 | 0.12416 | 0 | 3.7844 | 0 | 18.0039 | 0.03355 | 7.9439 | 0 | 57.5062 | 25.2185 | 22.7857 | 8.8891 | 1.2592 | 6.6773 | 0.16362 | 0 | 0.22057 | 6.5882 | 13.2545 | 0.55893 | 0.088235 | 0.018909 | 14.6705 | 1.8359 | 5.3047 | 1.2354 | 0.33731 | 7.6662 | 0.0015108 | 9.4452 | 0 | 0 | 2.4447 | 0 | 5.5709 | 26.5014 | 23.9332 | 1.1595 | 23.9227 | 17.9516 | 12.7278 | 10.0677 |  | 0.13454
33 kV O/H ccts | NC | NC | NC | NC | 832 | 1318.8138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7814 | 12.604 | 6.0974 | 10.8261 | 13.5184 | 2.7919 | 0 | 0 | 74.1601 | 28.4508 | 28.5376 | 67.4116 | 86.9756 | 132.1974 | 13.6441 | 52.404 | 75.2213 | 48.0335 | 15.5669 | 12.0827 | 24.6872 | 6.8809 | 17.112 | 0.0026279 | 0.66899 | 38.3567 | 1.5961 | 15.5322 | 22.1232 | 13.4431 | 3.8032 | 4.3616 | 6.9765 | 26.5748 | 0.18104 | 2.3286 | 0.27562 | 6.71e-05 | 1.5021 | 0.54448 | 20.7025 | 0.56022 | 16.3303 | 2.3599 | 1.2946 | 2.6089 | 18.0977 | 2.0702 | 15.7054 | 13.6484 | 20.8301 | 9.7995 | 12.5324 | 34.0778 | 76.3427 | 18.9579 | 37.5136 | 15.7371 | 50.2103 | 39.7832 | 4.9034 | 20.951 |  | 9.5409
11/22 kV O/H ccts | NC | NC | NC | NC | 7527 | 10117.7429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.391 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8243 | 0 | 0.0032547 | 0 | 1.0087 | 29.8175 | 12.6093 | 35.81 | 15.9681 | 139.341 | 166.5276 | 107.5594 | 217.3813 | 224.1656 | 367.6361 | 187.9895 | 517.0403 | 279.7457 | 354.406 | 273.1963 | 274.442 | 339.3358 | 402.8734 | 205.1484 | 231.4396 | 369.7519 | 277.2945 | 232.8606 | 144.4887 | 167.1494 | 181.5492 | 131.5496 | 190.7145 | 286.9998 | 110.8261 | 132.4465 | 66.6473 | 68.996 | 128.1881 | 97.5989 | 94.5071 | 69.6339 | 69.0928 | 96.5353 | 81.4972 | 61.2691 | 68.7463 | 65.4607 | 68.3991 | 61.2537 | 64.4898 | 106.5669 | 142.6857 | 180.0192 | 128.46 | 136.2035 | 130.9242 | 128.9796 | 190.6607 | 106.5795 | 140.9319 | 142.8562 | 165.3718 | 145.2976 | 169.2034 | 139.1157 | 162.5208 |  | 5.293
LV O/H ccts | NC | NC | NC | NC | 7829 | 13060.4733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63627 | 0 | 0 | 0 | 0 | 0 | 0 | 62.7613 | 75.2617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.0854 | 0 | 0 | 0 | 0 | 59.8247 | 8.1082 | 4.6724 | 18.0732 | 38.9503 | 20.1686 | 55.4362 | 37.6886 | 49.5407 | 50.0061 | 99.9909 | 384.6821 | 340.1738 | 279.8614 | 531.2308 | 607.9865 | 538.8568 | 470.7037 | 913.4068 | 547.6779 | 549.8594 | 532.3435 | 311.8682 | 444.3219 | 337.5093 | 250.979 | 205.6302 | 279.639 | 179.9566 | 272.7998 | 177.0643 | 148.5717 | 153.7013 | 135.3152 | 231.0293 | 375.2808 | 166.8872 | 178.5122 | 86.4513 | 93.5645 | 120.4824 | 103.7011 | 107.8829 | 69.3262 | 81.7589 | 110.1436 | 88.5667 | 36.1328 | 45.6653 | 64.8482 | 64.6111 | 52.1818 | 49.7908 | 49.4474 | 58.8044 | 72.3426 | 65.7377 | 69.6541 | 98.901 | 88.5843 | 104.6398 | 114.1693 | 106.6681 | 124.8645 | 137.8625 | 127.8834 | 147.0046 | 144.8825 | 102.1116 |  | 92.7547
Underground cables
132 kV U/G ccts | NC | NC | NC | NC | 33 | 586.7413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6284 | 0.047701 | 0 | 39.7957 | 0 | 0 | 16.1603 | 5.1229 | 27.0721 | 32.9145 | 13.79 | 26.9717 | 51.2048 | 88.7337 | 1.2128 | 7.3172 | 10.2502 | 18.1272 | 14.5069 | 5.7237 | 23.0057 | 19.875 | 3.8095 | 3.1128 | 0 | 0.01004 | 0.010855 | 0 | 11.3129 | 0 | 0.84789 | 0.0092633 | 0 | 0 | 0.061825 | 0.57854 | 0.013581 | 0.18597 | 9.3293 | 0.4477 | 6.4887 | 0 | 8.1079 | 16.2748 | 3.8861 | 5.4969 | 0.65551 | 0.12843 | 18.8598 | 0.25849 | 23.2619 | 22.3444 | 24.3037 | 21.8039 |  | 0.68
66 kV U/G ccts | NC | NC | NC | NC | 2 | 2.5863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.093025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0881 | 0.57057 | 0.39152 |  | 0.10373
33 kV U/G HSL ccts | NC | NC | NC | NC | 1 | 449.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.657 | 7.8517 | 18.6569 | 0 | 0 | 0 | 0 | 31.3795 | 2.7311 | 4.0973 | 5.3066 | 3.8804 | 0.13397 | 5.2674 | 1.2275 | 0.69684 | 0.63655 | 41.4582 | 14.6449 | 15.4179 | 0.94678 | 5.0141 | 13.0633 | 20.0677 | 2.6604 | 15.8547 | 50.1548 | 2.553 | 0.76971 | 6.5209 | 1.5444 | 0 | 0.11244 | 17.8157 | 30.4808 | 12.5495 | 3.0046 | 8.1817 | 29.6606 | 0.12121 | 0.78857 | 3.2869 | 7.6839 | 0.90624 | 0.06024 | 0.54041 | 3.5611 | 0.29765 | 0.38764 | 0.41961 | 0.073946 | 0.18467 | 0.034216 | 0.15437 | 0.48631 | 0.0721 | 0.002801 | 0.94144 | 0.085077 | 0.034786 | 0.07793 | 0.88325 | 0.5041 | 0.04266 | 0.26495 | 0.012125 | 0.5289 | 0 | 1.7992 | 0.44118 | 0.026241 | 0.038723 | 0.2234 | 0.39524 | 0.36455 | 0.34459 | 6.7577 | 1.6117 | 0.085378 | 5.4641 | 2.1803 | 0.25277 | 0.072577 | 0.19059 |  | 0.047275
33 kV U/G Oil ccts | NC | NC | NC | NC | 1 | 26.0736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8493 | 2.6972 | 0 | 0 | 0 | 0 | 0 | 7.8915 | 1.1508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0057401 | 0 | 7.9621 | 0 | 0.44326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0737
33 kV U/G Gas ccts | 44.3611 | 11.8721 | 10.091 | 1602046.2095 | 13 | 170.6697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5699 | 0 | 0 | 0 | 5.1391 | 0 | 4.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.465 | 10.865 | 24.1125 | 16.0764 | 12.3455 | 35.3325 | 2.7818 | 0 | 9.0183 | 5.9521 | 0.54945 | 8.6058 | 1.2236 | 0.68174 | 0.41588 | 0 | 3.518 | 0.13178 | 0.21643 | 0.0030917 | 0.044201 | 0 | 0.011833 | 0.47775 | 0 | 0.014299 | 0.10934 | 0.0156 | 0.011605 | 0.004113 | 0 | 0.15267 | 0.17731 | 0.040447 | 0.045415 | 0.010158 | 3.3523 | 0.0009125 | 0.071726 | 0 | 0 | 0.0076066 | 0.72293 | 0 | 0.024615 | 0.042704 | 0.020465 | 0.079612 | 0.051007 | 0.023854 | 0.02845 |  | 0
33 kV U/G XLPE ccts | NC | NC | NC | NC | 1 | 192.6062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13822 | 1.8195 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035469 | 2.525 | 0 | 0 | 0 | 0.26147 | 0 | 0 | 1.6982 | 0.94908 | 0 | 0.024614 | 0.5244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31008 | 0 | 0 | 0.23367 | 2.1136 | 0 | 2.6058 | 0.32992 | 0.79545 | 0.81244 | 8.2996 | 6.1811 | 5.1416 | 6.1152 | 0.55177 | 10.28 | 6.2672 | 17.0395 | 8.6313 | 19.7475 | 26.7427 | 24.9803 | 21.3999 | 15.1855 |  | 0.86622
11/22 kV U/G ccts | NC | NC | NC | 956325 | 343 | 7822.8906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00090008 | 0 | 0.0070777 | 2.3326 | 50.8591 | 63.6424 | 10.1075 | 18.5797 | 2.7475 | 1.3971 | 0.18679 | 0.33042 | 0.46281 | 1.4142 | 2.2926 | 5.2679 | 3.8718 | 28.2538 | 1.0676 | 1.2355 | 1.9857 | 0.6064 | 50.6961 | 3.994 | 1.2435 | 17.0655 | 25.5421 | 22.4904 | 27.5147 | 23.3097 | 33.8981 | 22.0585 | 214.2914 | 175.57 | 156.717 | 151.0827 | 178.9776 | 159.1072 | 188.7382 | 118.4366 | 264.2316 | 166.339 | 140.7434 | 128.4003 | 79.5679 | 147.3588 | 76.4699 | 126.4977 | 55.96 | 99.3737 | 73.2584 | 110.5207 | 88.5403 | 90.7621 | 118.5726 | 128.9586 | 157.4407 | 137.0142 | 114.9875 | 92.3257 | 79.7931 | 33.9106 | 77.6987 | 40.1624 | 46.7407 | 86.687 | 52.7123 | 60.523 | 59.4078 | 89.0844 | 71.9754 | 56.574 | 91.7297 | 60.0378 | 53.5309 | 82.4736 | 105.7894 | 124.1617 | 112.731 | 97.6398 | 116.583 | 114.1807 | 127.3942 | 132.7428 | 198.2486 | 168.2171 | 217.5191 | 222.2621 | 279.3256 | 299.3424 | 278.3007 |  | 20.705
LV U/G ccts | NC | NC | NC | 861926 | 501 | 5638.6879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005527 | 0.0022903 | 0 | 0 | 0.0092183 | 0.12126 | 13.05 | 21.0872 | 0.1698 | 0.15974 | 0.78142 | 0.14917 | 0.071385 | 0.26721 | 0.021335 | 0.12158 | 0.14686 | 0.39817 | 0.35806 | 3.8241 | 0.47529 | 0.17763 | 0.11352 | 0.033811 | 16.0222 | 2.4885 | 0.50504 | 8.0133 | 13.9527 | 11.3076 | 16.0021 | 15.5057 | 7.7803 | 12.1496 | 86.3976 | 56.8018 | 72.5332 | 67.0996 | 99.5679 | 119.1258 | 115.9703 | 72.5499 | 128.7961 | 76.8798 | 120.2146 | 97.9013 | 29.3406 | 104.4207 | 78.0966 | 70.8632 | 43.2854 | 86.0574 | 42.4199 | 92.9342 | 54.1832 | 50.0818 | 120.2058 | 112.5357 | 132.2731 | 93.7237 | 137.476 | 110.0443 | 73.2216 | 42.9288 | 53.1252 | 39.6796 | 32.965 | 75.344 | 48.387 | 31.7098 | 43.0856 | 48.0347 | 67.7973 | 54.0877 | 77.4236 | 58.8394 | 69.1845 | 62.001 | 109.1862 | 99.8984 | 97.5995 | 95.4902 | 148.9431 | 143.8432 | 154.6599 | 159.4679 | 129.5991 | 126.5173 | 148.419 | 134.3043 | 180.8536 | 221.0821 | 174.6901 |  | 19.2681
Services (incl. LV pillars and LV service pits)
Services O/H lines | NC | NC | 16602 | 477 | 19270 | 816410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4632 | 0 | 0 | 0 | 0 | 0 | 0 | 1350 | 3776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 1 | 2337 | 0 | 2 | 0 | 363 | 950 | 430 | 289 | 844 | 821 | 2175 | 1107 | 4221 | 907 | 3920 | 9152 | 16135 | 9995 | 16401 | 23238 | 32821 | 17949 | 24496 | 27406 | 17230 | 14556 | 14127 | 13112 | 14824 | 9370 | 8484 | 8156 | 5981 | 5580 | 10006 | 5930 | 4704 | 5982 | 6369 | 10126 | 17224 | 8466 | 8415 | 6414 | 7386 | 9837 | 10694 | 10476 | 8392 | 10001 | 11138 | 10817 | 4610 | 5770 | 7728 | 8190 | 7604 | 6066 | 5762 | 5526 | 6149 | 9037 | 8994 | 11553 | 13966 | 14445 | 21198 | 20154 | 24288 | 29990 | 19980 | 21706 | 25146 | 9210 |  | 49816
Services U/G cable | NC | NC | NC | 13663 | 100 | 205104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 1791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 42 | 0 | 0 | 0 | 393 | 540 | 373 | 720 | 161 | 717 | 251 | 859 | 778 | 590 | 319 | 3201 | 1898 | 1745 | 4016 | 3266 | 9734 | 2615 | 4115 | 3354 | 3395 | 3225 | 2663 | 3238 | 2676 | 1663 | 1551 | 3070 | 1807 | 534 | 4239 | 1060 | 4361 | 5258 | 5051 | 12356 | 13814 | 2382 | 4601 | 2841 | 1119 | 2269 | 1274 | 2506 | 2211 | 3083 | 1201 | 1531 | 1815 | 1932 | 2136 | 2737 | 3638 | 1779 | 2968 | 3019 | 2185 | 2229 | 2733 | 3016 | 3948 | 4076 | 3594 | 2316 | 3107 | 2579 | 3037 | 3672 | 3889 | 1921 |  | 5988
LV pillars | 32.7528 | 15.9339 | 80 | 4365 | 825 | 46484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 11372 | 31 | 0 | 0 | 0 | 6 | 52 | 44 | 81 | 144 | 150 | 220 | 296 | 369 | 536 | 442 | 346 | 412 | 953 | 1567 | 574 | 673 | 386 | 693 | 191 | 294 | 370 | 607 | 1054 | 878 | 1218 | 1156 | 1072 | 807 | 405 | 661 | 945 | 912 | 602 | 681 | 771 | 1568 | 1792 | 1393 | 1081 | 1092 | 3213 | 1025 | 896 | 1548 | 732 |  | 75
LV service pits | 40.3333 | 15.8815 | 6 | 3868 | 92 | 6078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 4 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 2218 | 33 | 40 | 353 | 76 | 74 | 60 | 39 | 53 | 77 | 160 | 72 | 55 | 130 | 85 | 39 | 45 | 134 | 95 | 111 | 47 | 108 | 45 | 29 | 44 | 47 | 41 | 57 | 58 | 55 | 61 | 59 | 39 | 41 | 41 | 22 | 26 | 16 | 12 | 21 | 13 | 26 | 26 | 12 | 48 | 113 | 60 | 787 | 116 | 24 | 0 | 5 | 10 | 2 |  | 0
Distribution transformers
11_22_33kV/433V Pole transformers | 33.7039 | 14.1476 | 52 | 12600 | 222 | 16019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 645 | 4 | 6 | 4 | 7 | 12 | 46 | 46 | 62 | 119 | 91 | 176 | 130 | 148 | 206 | 242 | 221 | 211 | 270 | 239 | 333 | 245 | 185 | 254 | 208 | 182 | 204 | 154 | 152 | 206 | 274 | 292 | 320 | 559 | 213 | 212 | 269 | 255 | 181 | 204 | 616 | 266 | 312 | 444 | 356 | 545 | 258 | 274 | 158 | 74 | 112 | 783 | 76 | 144 | 181 | 171 | 352 | 450 | 796 | 491 | 462 | 360 | 284 | 262 |  | 2
11_22_33kV/433V Ground transformers | 40.6121 | 16.8402 | 24 | 39400 | 261 | 16560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 16 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 16 | 0 | 3 | 2 | 1 | 15 | 28 | 0 | 0 | 3 | 27 | 14 | 140 | 2 | 10 | 90 | 7 | 6 | 5 | 9 | 8 | 26 | 26 | 82 | 92 | 120 | 199 | 170 | 140 | 124 | 199 | 146 | 253 | 273 | 416 | 338 | 216 | 224 | 296 | 218 | 309 | 292 | 280 | 431 | 254 | 278 | 131 | 90 | 184 | 330 | 245 | 283 | 249 | 247 | 294 | 223 | 1622 | 426 | 161 | 64 | 101 | 73 | 87 | 339 | 198 | 293 | 369 | 338 | 482 | 536 | 554 | 561 | 538 | 640 | 599 | 484 |  | 5
Distribution switchgear
11kV Circuit Breakers | 61.3979 | 19.7278 | 64 | 224000 | 126 | 1299 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 11 | 1 | 0 | 20 | 15 | 36 | 14 | 38 | 14 | 6 | 4 | 5 | 1 | 9 | 10 | 24 | 42 | 16 | 22 | 11 | 4 | 0 | 4 | 18 | 0 | 0 | 14 | 5 | 24 | 17 | 44 | 35 | 14 | 12 | 14 | 33 | 12 | 7 | 45 | 22 | 33 | 25 | 31 | 27 | 21 | 21 | 39 | 33 | 47 | 21 | 28 | 17 | 42 | 8 | 19 | 20 | 8 | 18 | 0 | 18 | 18 | 1 | 6 | 24 | 24 | 6 | 2 | 2 | 0 | 4 | 1 | 6 | 2 | 17 | 4 | 8 | 9 | 0 | 0 | 1 | 2 | 1 | 3 | 6 | 0 | 2 | 0 | 6 | 6 | 5 |  | 0
11kV RMU/RMCBs | 32.201 | 17.9305 | 280 | 30000 | 189 | 13410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 5 | 6 | 6 | 1 | 5 | 4 | 1 | 1 | 0 | 0 | 1 | 5 | 1 | 1 | 0 | 2 | 0 | 1 | 2 | 0 | 4 | 4 | 3 | 6 | 4 | 2 | 9 | 9 | 7 | 4 | 9 | 10 | 30 | 18 | 51 | 48 | 117 | 119 | 110 | 90 | 85 | 108 | 134 | 139 | 150 | 131 | 156 | 127 | 210 | 211 | 249 | 199 | 224 | 184 | 204 | 223 | 216 | 130 | 112 | 126 | 144 | 181 | 146 | 169 | 183 | 195 | 160 | 223 | 184 | 244 | 194 | 262 | 258 | 306 | 262 | 287 | 385 | 442 | 423 | 607 | 505 | 542 | 602 | 597 | 649 | 638 | 519 |  | 84
Distribution 'other assets'
DC PT Subs | 36.9853 | 12.4965 | 320 | 78000 | 1125 | 16161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 1 | 0 | 1 | 0 | 0 | 1 | 2 | 1 | 1 | 0 | 0 | 2 | 0 | 6 | 9 | 10 | 15 | 16 | 15 | 9 | 18 | 46 | 112 | 88 | 123 | 175 | 166 | 292 | 177 | 252 | 326 | 317 | 316 | 312 | 368 | 331 | 329 | 351 | 295 | 299 | 295 | 280 | 267 | 230 | 242 | 272 | 324 | 322 | 398 | 858 | 275 | 289 | 327 | 314 | 259 | 315 | 340 | 321 | 319 | 270 | 292 | 297 | 273 | 250 | 244 | 231 | 284 | 191 | 187 | 198 | 203 | 190 | 181 | 174 | 186 | 238 | 357 | 315 | 286 | 278 |  | 0
DC Kiosk and Padmount Subs | 33.6335 | 15.1496 | 58 | 185000 | 10575 | 11724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 4 | 2 | 2 | 1 | 1 | 2 | 3 | 3 | 3 | 13 | 14 | 27 | 36 | 121 | 124 | 106 | 102 | 102 | 134 | 141 | 165 | 166 | 153 | 193 | 153 | 242 | 269 | 312 | 250 | 261 | 234 | 239 | 262 | 271 | 168 | 151 | 177 | 144 | 155 | 106 | 136 | 169 | 191 | 176 | 217 | 179 | 197 | 170 | 208 | 202 | 231 | 209 | 260 | 295 | 338 | 301 | 388 | 339 | 348 | 421 | 388 | 476 | 466 | 397 |  | 0
DC Ground and Chamber Subs | 49.4955 | 16.6668 | 53 | 261000 | 1209 | 2880 | 0 | 0 | 0 | 1 | 5 | 6 | 1 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 4 | 1 | 3 | 10 | 14 | 21 | 12 | 19 | 13 | 1 | 3 | 1 | 4 | 10 | 12 | 9 | 15 | 4 | 9 | 3 | 2 | 3 | 3 | 12 | 5 | 8 | 10 | 15 | 15 | 29 | 36 | 28 | 12 | 20 | 28 | 60 | 31 | 44 | 51 | 39 | 52 | 40 | 56 | 54 | 41 | 58 | 48 | 65 | 76 | 64 | 63 | 55 | 54 | 37 | 30 | 35 | 31 | 35 | 30 | 59 | 38 | 37 | 30 | 77 | 93 | 74 | 77 | 72 | 46 | 33 | 30 | 34 | 34 | 38 | 55 | 60 | 56 | 42 | 42 | 28 | 31 | 30 | 24 | 18 | 20 | 14 | 41 | 26 | 28 | 28 |  | 0
Air Break Switches | 19.7705 | 15.7703 | 443 | 10935 | 494 | 7537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 3 | 2 | 7 | 44 | 12 | 27 | 24 | 19 | 20 | 32 | 48 | 46 | 23 | 16 | 46 | 27 | 26 | 19 | 26 | 33 | 45 | 29 | 45 | 33 | 19 | 48 | 35 | 25 | 18 | 67 | 94 | 97 | 82 | 60 | 39 | 22 | 32 | 15 | 10 | 22 | 41 | 41 | 48 | 121 | 209 | 169 | 404 | 325 | 426 | 664 | 587 | 508 | 549 | 567 |  | 1538
Zone transformers
Sub-transmission Sub Transformers | 46.7222 | 4.5069 | 0 | 3136000 | 178 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 3 | 0 | 0 | 2 | 4 | 3 | 4 | 5 | 0 | 2 | 2 | 4 | 3 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 2 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 5 | 6 | 2 | 4 | 10 | 7 | 2 | 0 | 0 |  | 0
132 / 11 kV Zone Transformers | 32.25 | 11.8401 | 3 | 1939000 | 285 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 4 | 6 | 3 | 3 | 0 | 1 | 1 | 4 | 4 | 3 | 2 | 2 | 2 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 3 | 4 | 0 | 0 | 1 | 4 | 4 | 1 | 3 | 6 | 4 | 6 | 6 | 4 | 6 | 7 | 5 | 19 | 7 | 13 | 6 |  | 0
66 / 11 kV Zone Transformers | 48 | 7.3485 | 2 | 964000 | 56 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 1 | 2 | 2 | 1 | 0 | 1 | 0 | 2 | 3 | 0 | 0 | 1 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 2 | 1 | 7 | 1 | 0 | 4 | 0 | 4 |  | 0
33 / 11 kV Zone Transformers | 46.1765 | 7.9833 | 15 | 964000 | 507 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 3 | 1 | 1 | 0 | 1 | 3 | 8 | 5 | 13 | 18 | 25 | 8 | 13 | 8 | 12 | 6 | 5 | 12 | 5 | 2 | 4 | 4 | 3 | 4 | 4 | 1 | 0 | 0 | 0 | 3 | 1 | 0 | 2 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 11 | 6 | 11 | 17 | 16 | 17 | 4 | 3 | 11 | 5 | 0 |  | 0
Zone switchgear
132kV Circuit Breakers | 33.3265 | 14.1153 | 13 | 345000 | 62 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 1 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9 | 3 | 7 | 10 | 6 | 19 | 9 | 22 | 14 | 16 | 32 | 40 | 36 | 35 | 64 | 46 | 37 | 40 |  | 1
66kV Circuit Breakers | 32 | 9.4868 | 20 | 254000 | 9 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1 | 1 | 3 | 5 | 3 | 2 | 0 | 1 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 2 | 5 | 8 | 7 | 2 | 12 | 2 | 18 | 19 | 9 | 20 |  | 1
33kV Circuit Breakers | 43.0682 | 12.0253 | 73 | 222000 | 99 | 1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 30 | 8 | 8 | 4 | 4 | 30 | 23 | 21 | 42 | 36 | 33 | 17 | 87 | 12 | 14 | 25 | 28 | 9 | 5 | 15 | 14 | 0 | 11 | 5 | 12 | 10 | 10 | 13 | 4 | 2 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 4 | 0 | 0 | 0 | 1 | 53 | 0 | 39 | 0 | 0 | 0 | 18 | 12 | 2 | 4 | 14 | 22 | 12 | 19 | 23 | 32 | 70 | 33 | 70 | 58 |  | 1
11kV Switchgear (Housings) | 56.5465 | 14.6866 | 115 | NC | 9 | 2901 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 21 | 0 | 0 | 0 | 0 | 17 | 25 | 37 | 0 | 0 | 8 | 46 | 0 | 0 | 9 | 19 | 7 | 25 | 70 | 0 | 11 | 18 | 30 | 68 | 77 | 77 | 99 | 105 | 0 | 155 | 190 | 67 | 90 | 137 | 18 | 42 | 100 | 52 | 46 | 44 | 52 | 0 | 42 | 57 | 20 | 39 | 0 | 22 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 21 | 0 | 6 | 44 | 137 | 7 | 32 | 19 | 48 | 37 | 61 | 79 | 129 | 58 | 72 | 95 |  | 2
11kV Switchgear (CB Trucks) | 43.9986 | 10.7303 | 363 | 37500 | 234 | 3883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 3 | 4 | 9 | 8 | 46 | 2 | 14 | 24 | 19 | 15 | 14 | 50 | 1 | 57 | 10 | 26 | 15 | 39 | 80 | 94 | 94 | 1 | 133 | 86 | 78 | 75 | 142 | 36 | 55 | 32 | 41 | 72 | 12 | 54 | 0 | 44 | 53 | 25 | 68 | 0 | 23 | 2 | 2 | 13 | 1 | 1 | 0 | 26 | 38 | 0 | 22 | 22 | 30 | 5 | 64 | 161 | 16 | 45 | 56 | 81 | 124 | 112 | 144 | 355 | 289 | 258 | 284 |  | 13
Zone 'other assets'
Sub-transmission Sub Buildings | 44 | 0 | 0 | NC | 161 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 1 | 2 | 2 | 3 | 1 | 1 | 1 | 5 | 2 | 0 | 4 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 4 | 1 | 0 | 0 | 1 |  | 1
Zone Sub Buildings | 43 | 16.5288 | 5 | NC | 1256 | 191 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 1 | 0 | 2 | 0 | 3 | 3 | 1 | 1 | 3 | 5 | 1 | 3 | 4 | 2 | 5 | 7 | 3 | 7 | 6 | 1 | 8 | 4 | 6 | 6 | 6 | 3 | 4 | 4 | 5 | 4 | 2 | 2 | 0 | 4 | 1 | 1 | 2 | 3 | 3 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | 0 | 2 | 3 | 4 | 3 | 2 | 1 | 8 | 6 | 4 | 7 |  | 0
SCADA and protection
Fibre Cable | NC | NC | NC | NC | 7 | 1619.4474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049315 | 0 | 0 | 0.042159 | 0 | 20.4241 | 74.8361 | 42.4735 | 61.0782 | 28.009 | 72.5341 | 159.28 | 120.2197 | 105.3928 |  | 935.1085
Copper Comms/Pilot Cable | NC | NC | NC | NC | 6 | 5258.7488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2476 | 0 | 0 | 0 | 0 | 0.00060937 | 0 | 0 | 0 | 0 | 1.0809 | 0.015614 | 0 | 0 | 0.023001 | 0 | 0 | 0.058448 | 0.1152 | 0.052341 | 0.0045878 | 0 | 0.015478 | 0 | 0.01083 | 0.0026415 | 0.049337 | 0 | 0.05038 | 0.00534 | 0 | 0 | 0.016246 | 0 | 0.11817 | 0.12834 | 0.17118 | 2.1915 | 0.5393 | 2.9447 | 10.6568 | 17.2198 | 7.2564 | 18.3607 | 12.4244 | 20.9228 | 14.1566 | 9.9719 | 68.054 | 39.3908 | 23.9216 | 17.3744 |  | 4990.1314
Relays - Zone and ST Substations | 46.714 | 12.8743 | 1052 | 20000 | 144 | 35222 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 74 | 0 | 122 | 0 | 0 | 0 | 142 | 220 | 0 | 110 | 0 | 423 | 602 | 205 | 404 | 198 | 177 | 606 | 1280 | 674 | 1091 | 796 | 291 | 1030 | 1559 | 469 | 1271 | 1413 | 271 | 1175 | 1603 | 737 | 721 | 1066 | 308 | 774 | 1312 | 816 | 981 | 661 | 413 | 0 | 604 | 846 | 93 | 373 | 69 | 254 | 15 | 19 | 45 | 0 | 5 | 0 | 14 | 73 | 70 | 0 | 163 | 247 | 2 | 425 | 532 | 6 | 252 | 300 | 531 | 418 | 398 | 107 | 2265 | 978 | 464 | 814 |  | 13
Relays - DC Substations | 47.7434 | 17.3678 | 115 | 8000 | 12 | 14054 | 0 | 0 | 0 | 0 | 7 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 3 | 17 | 0 | 12 | 37 | 29 | 65 | 27 | 52 | 14 | 6 | 10 | 7 | 19 | 86 | 81 | 48 | 65 | 17 | 26 | 18 | 7 | 30 | 6 | 18 | 21 | 51 | 39 | 88 | 126 | 105 | 122 | 83 | 18 | 39 | 60 | 78 | 48 | 88 | 258 | 202 | 301 | 122 | 270 | 216 | 140 | 143 | 160 | 245 | 288 | 242 | 277 | 219 | 196 | 150 | 214 | 131 | 69 | 134 | 58 | 135 | 61 | 132 | 103 | 372 | 466 | 368 | 484 | 454 | 415 | 295 | 164 | 223 | 196 | 281 | 498 | 474 | 480 | 253 | 371 | 172 | 221 | 294 | 215 | 161 | 142 | 95 | 300 | 210 | 100 | 157 |  | 3
Other
1-3 Three Phase Meters | 38.84 | 24.13 | 6415 | 230 | 6415 | 209171 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 3 | 0 | 6 | 47 | 33 | 49 | 39 | 138 | 338 | 1888 | 794 | 9 | 3144 | 596 | 270 | 661 | 31 | 63 | 133 | 231 | 347 | 822 | 2257 | 1256 | 1311 | 9598 | 2496 | 2038 | 1561 | 2769 | 2365 | 2511 | 2209 | 1434 | 1423 | 818 | 630 | 533 | 514 | 510 | 979 | 450 | 348 | 559 | 400 | 534 | 343 | 574 | 559 | 306 | 5885 | 13703 | 17113 | 16111 | 14478 | 16749 | 29890 | 35472 | 8812
4-6) Single Phase Meters | 59.74 | 41.91 | 38403 | 230 | 38403 | 2213676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 9 | 7 | 62 | 12 | 22 | 15 | 13 | 16 | 0 | 1 | 9 | 24 | 26 | 35 | 0 | 27 | 69 | 2 | 56 | 49 | 95 | 16744 | 30 | 19158 | 9905 | 10949 | 21820 | 1515 | 15613 | 17176 | 16405 | 16480 | 17002 | 18563 | 18790 | 20273 | 34691 | 3953 | 11561 | 21269 | 15285 | 14223 | 13302 | 12977 | 15910 | 110516 | 27348 | 23712 | 31340 | 33320 | 37534 | 39750 | 35753 | 38740 | 41266 | 43178 | 43378 | 41285 | 42653 | 45543 | 46307 | 39708 | 37004 | 38980 | 47844 | 50493 | 47839 | 33419 | 37296 | 17628 | 42959 | 46653 | 77322 | 55071 | 56142 | 83881 | 85637 | 109102 | 32659 |  | 228271
Control Load Device (Freq Inject Relays & Time Switches) | NC | NC | NC | NC | NC | 325891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 4 | 24 | 2 | 6 | 1 | 4 | 3 | 0 | 0 | 1 | 8 | 4 | 6 | 0 | 9 | 12 | 0 | 15 | 16 | 22 | 2213 | 4 | 2023 | 669 | 409 | 574 | 32 | 285 | 141 | 243 | 332 | 253 | 320 | 524 | 624 | 636 | 1188 | 2394 | 3792 | 2682 | 2892 | 2402 | 2142 | 2778 | 13984 | 2897 | 3324 | 5943 | 6830 | 8562 | 9260 | 8613 | 9072 | 9382 | 9440 | 9680 | 9574 | 8477 | 9534 | 8374 | 6732 | 5657 | 5949 | 6542 | 6929 | 6093 | 4246 | 3863 | 8638 | 9133 | 6292 | 7234 | 6889 | 7679 | 7112 | 9186 | 12948 | 4689 |  | 37440
NC - Not Captured at present
Contents