## Inputs
CitiPower - Victoria Market Transformer Replacement Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | Victoria Market Transformer Replacement Risk Monetisation Model
|  | Model start & timeline |  | 2019 | FY19/20
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 50
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex regulator, real $2019 |  | 3748000 |  |  |  |  | 0 | 0 | 0 | 50000 | 750000 | 2948000 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 3883856.708 |  |  |  |  | 0 | 0 | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 12300 | 2400
|  |  | Opex ($2021) | 12745.8478 | 2486.9947
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 9.357% | 10.08% | 10.86% | 11.71% | 12.63% | 13.63% | 14.72% | 15.9% | 17.18% | 18.57% | 20.08% | 21.72%
|  |  | Major | 2 |  |  |  |  | 0.05031% | 0.05419% | 0.0584% | 0.06297% | 0.06792% | 0.0733% | 0.07914% | 0.08548% | 0.09236% | 0.09984% | 0.108% | 0.1168%
|  |  | Catastrophic | 3 |  |  |  |  | 0.05031% | 0.05419% | 0.0584% | 0.06297% | 0.06792% | 0.0733% | 0.07914% | 0.08548% | 0.09236% | 0.09984% | 0.108% | 0.1168%
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 6536 | 26450 | 20% | 209.6855
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 162268 | 47770 | 40% | 18803.9359
|  |  | Industrial | 5615 | 47070 | 80% | 1282.2851
|  |  | Total | 174419 | 46948.5412 | 40.87% | 20295.9065
Asset information
|  | Assets at risk |  | 3
|  | N-rating, MVA |  | 62.8
|  |  | N-1 Rating before transfers, MVA | 62.8
|  |  | N-2 Rating before transfers, MVA | 35.4
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major | Catastrophic
|  |  | Average Consequence Loss Oil | 500 | 4050 | 12150
|  |  | Average Consequences Loss SF6 kgs | 0 | 0 | 0
|  |  | Average Consequence Fire | 0.05 | 2.5 | 5
|  |  | Average Consequence Waste | 10 | 405 | 1215
|  |  | Average Consequence Disturbance | 2 | 3 | 5
|  |  | Average Cost of Fault (Air Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (SF6 Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (Oil Insulated) | 63521.9894 | 866510.4 | 2571967.0088
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Switching time only (hours required) | 0 | 0 | 0 | 0
|  |  | Number of weeks generation required | 1.1905 | 6 | 6 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 0 | 15.8631 | 51.2631
|  |  | Number of generators | 0 | 0 | 16 | 52
|  |  | Generator sites | 0 | 0 | 4 | 13
|  |  | Number of days to connect all generators | 0 | 0 | 2 | 5
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Generator hire | 0 | 0 | 735045.0973 | 4683494.5841
|  |  | Fuel cost | 0 | 0 | 2742573.2342 | 17725792.5593
|  |  | Fitter cost | 0 | 0 | 676462.5558 | 4235351.9575
|  |  | Traffic management cost | 0 | 0 | 1740896.2832 | 11315825.8407
|  |  | Transformer hire | 0 | 0 | 183761.2743 | 1170873.646
|  |  | Earthing and bunding | 0 | 0 | 8289.9823 | 26942.4425
|  |  | Temporary fencing | 0 | 0 | 74609.8407 | 484963.9646
|  |  | Miscellaneous materials | 0 | 0 | 8289.9823 | 26942.4425
|  |  | Installation & removal of step-down transformers | 0 | 0 | 10362.4779 | 33678.0531
|  |  | Council permits | 0 | 0 | 16579.9646 | 53884.885
|  |  | Crane hire | 0 | 0 | 10362.4779 | 33678.0531
|  |  | Cable hire | 0 | 0 | 12434.9735 | 40413.6637
|  |  | Total | 0 | 0 | 6219668.1439 | 39831842.092
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major | Catastrophic
|  |  | Minor | 1.172% | 4.103% | 4.103%
|  |  | Serious | 0.2345% | 0.8206% | 0.8206%
|  |  | Fataility | 0.02345% | 0.08206% | 0.08206%
|  |  | Value of event | 8261.6388 | 28915.7357 | 28915.7357
|  |  | Weighted likelyhood of consequence | 0.05217% | 0.1826% | 0.1826%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 44.276 | 45.568 | 50.336 | 52.09 | 52.704 | 53.43 | 58.786 | 58.786 | 58.786 | 58.786 | 58.786 | 58.786
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 40.454 | 43.122 | 47.029 | 47.835 | 48.425 | 49.197 | 53.947 | 53.947 | 53.947 | 53.947 | 53.947 | 53.947
|  |  | Weighting to 50% PoE | 70% |  |  |  |  | 41.6006 | 43.8558 | 48.0211 | 49.1115 | 49.7087 | 50.4669 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 6.2006 | 8.4558 | 12.6211 | 13.7115 | 14.3087 | 15.0669 | 19.9987 | 19.9987 | 19.9987 | 19.9987 | 19.9987 | 19.9987
|  |  | N-3 | [5 empty] | 41.6006 | 43.8558 | 48.0211 | 49.1115 | 49.7087 | 50.4669 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987
|  |  | N-4 | [5 empty] | 41.6006 | 43.8558 | 48.0211 | 49.1115 | 49.7087 | 50.4669 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987
End

## Base Case
CitiPower - Victoria Market Transformer Replacement Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 70923038.5919 | 0 | 0 | 0 | 0 | 20% | 14184607.7184 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 39831842.092 | 0 | 0 | 20% | 7966368.4184 | 7966368.4184
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 11651570.1239 | 0 | 20% | 2330314.0248 | 2330314.0248
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2571967.0088 | 20% | 514393.4018 | 514393.4018
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 20% | 10362.4779 | 10362.4779
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3883856.708 | 0 | 80% | 3107085.3664 | 3107085.3664
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 866510.4 | 80% | 693208.32 | 693208.32
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 80% | 41449.9115 | 41449.9115
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 6040646.2969 | 0 | 6219668.1439 | 0 | 0 | 4% | 490412.5776 | 248786.7258
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 12745.8478 | 0 | 100% | 12745.8478 | 12745.8478
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 63521.9894 | 100% | 63521.9894 | 63521.9894
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 6040646.2969 | 0 | 1234061.1397 | 0 | 0 | 4% | 290988.2975 | 49362.4456
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 6040646.2969 | 8261.6388 | 1285873.5291 | 12745.8478 | 63521.9894 | 5.766% | 427330.1628 | 185704.3109
[5 empty] | 2 | Major |  | 6040646.2969 | 28915.7357 | 6271480.5333 | 3883856.708 | 866510.4 | 25.48% | 4355288.764 | 4113662.9122
[5 empty] | 3 | Catastrophic |  | 70923038.5919 | 28915.7357 | 39883654.4814 | 11651570.1239 | 2571967.0088 | 20% | 25011829.1883 | 10827221.47
[5 empty] | Subtotal |  |  | 2025: 29794448.1151; 2026: 15126588.693
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 62.8
|  |  | N-1 Rating before transfers, MVA |  |  | 62.8
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 44.276 | 45.568 | 50.336 | 52.09 | 52.704 | 53.43 | 58.786 | 58.786 | 58.786 | 58.786 | 58.786 | 58.786
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 40.454 | 43.122 | 47.029 | 47.835 | 48.425 | 49.197 | 53.947 | 53.947 | 53.947 | 53.947 | 53.947 | 53.947
|  |  | Weighting to 50% PoE |  |  | 70% |  | 41.6006 | 43.8558 | 48.0211 | 49.1115 | 49.7087 | 50.4669 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 6.2006 | 8.4558 | 12.6211 | 13.7115 | 14.3087 | 15.0669 | 19.9987 | 19.9987 | 19.9987 | 19.9987 | 19.9987 | 19.9987
|  |  | N-3 |  |  |  |  | 41.6006 | 43.8558 | 48.0211 | 49.1115 | 49.7087 | 50.4669 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987
|  |  | N-4 |  |  |  |  | 41.6006 | 43.8558 | 48.0211 | 49.1115 | 49.7087 | 50.4669 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987 | 55.3987
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 6040646.2969 | 8237670.0573 | 15369399.9326 | 16697239.3196 | 17424482.2413 | 18347783.6199 | 24353504.7209 | 24353504.7209 | 24353504.7209 | 24353504.7209 | 24353504.7209 | 24353504.7209
|  |  | N-3 |  |  | Catastrophic |  | 70923038.5919 | 74767830.1726 | 93564648.5463 | 95689191.5654 | 96852780.2402 | 98330062.4459 | 107939216.2075 | 107939216.2075 | 107939216.2075 | 107939216.2075 | 107939216.2075 | 107939216.2075
|  |  | N-4 |  |  | Catastrophic |  | 70923038.5919 | 74767830.1726 | 93564648.5463 | 95689191.5654 | 96852780.2402 | 98330062.4459 | 107939216.2075 | 107939216.2075 | 107939216.2075 | 107939216.2075 | 107939216.2075 | 107939216.2075
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 9.357% | 10.08% | 10.86% | 11.71% | 12.63% | 13.63% | 14.72% | 15.9% | 17.18% | 18.57% | 20.08% | 21.72%
|  |  | Major |  |  |  |  | 0.05031% | 0.05419% | 0.0584% | 0.06297% | 0.06792% | 0.0733% | 0.07914% | 0.08548% | 0.09236% | 0.09984% | 0.108% | 0.1168%
|  |  | Catastrophic |  |  |  |  | 0.05031% | 0.05419% | 0.0584% | 0.06297% | 0.06792% | 0.0733% | 0.07914% | 0.08548% | 0.09236% | 0.09984% | 0.108% | 0.1168%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 7136.1494 | 8103.5883 | 10928.7428 | 12050.9502 | 13157.3701 | 14415.6766 | 17084.7033 | 18453.1019 | 19939.2407 | 21553.6132 | 23307.668 | 25204.4696
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 22610.124 | 33213.1392 | 66781.8224 | 78225.0803 | 88056.1757 | 100063.4023 | 143394.5322 | 154879.7109 | 167353.1018 | 180902.7771 | 195624.8279 | 211544.9741
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 121.5598 | 178.5653 | 359.0421 | 420.5649 | 473.4203 | 537.9753 | 770.9383 | 832.6866 | 899.7479 | 972.5956 | 1051.7464 | 1137.3386
|  |  | Other significant risks |  |  | Significant |  | 17377.2693 | 18718.3484 | 20172.6684 | 21750.2043 | 23461.8326 | 25319.414 | 27335.8836 | 29525.35 | 31903.2033 | 34486.233 | 37292.7575 | 40327.6798
|  |  | Other major risks |  |  | Major |  | 2069.547 | 2229.2629 | 2402.4653 | 2590.342 | 2794.1885 | 3015.4173 | 3255.5689 | 3516.3235 | 3799.5141 | 4107.1402 | 4441.3834 | 4802.8277
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 5447.0784 | 5867.453 | 6323.3241 | 6817.8184 | 7354.3454 | 7936.6228 | 8568.7053 | 9255.0154 | 10000.3772 | 10810.0536 | 11689.7867 | 12641.1134
|  |  | Annual opex, pre-replacement |  |  |  |  | 12745.8478 | 12745.8478 | 12745.8478 | 12745.8478 | 12745.8478 | 12745.8478 | 12745.8478 | 12745.8478 | 12745.8478 | 12745.8478 | 12745.8478 | 12745.8478
|  |  | Subtotal |  |  |  |  | 67507.5757 | 81056.2049 | 119713.9127 | 134600.808 | 148043.1804 | 164034.3561 | 213156.1794 | 229208.0361 | 246641.0327 | 265578.2606 | 286154.0179 | 308404.251
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 144760.291
|  |  | Post-replacement opex |  |  | 2486.9947
|  |  | Total annuity |  |  | 147247.2857
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 67507.5757 | 81056.2049 | 119713.9127 | 134600.808 | 148043.1804 | 164034.3561 | 213156.1794 | 229208.0361 | 246641.0327 | 265578.2606 | 286154.0179 | 308404.251
|  |  | Annualised cost |  |  |  |  | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - Victoria Market Transformer Replacement Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 60639197.9961 | 0 | 0 | 0 | 0 | 20% | 12127839.5992 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 43815026.3012 | 0 | 0 | 20% | 8763005.2602 | 8763005.2602
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 3612846.3891 | 0 | 6841634.9583 | 0 | 0 | 4% | 418179.2539 | 273665.3983
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 14020.4326 | 0 | 100% | 14020.4326 | 14020.4326
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 3612846.3891 | 0 | 1357467.2536 | 0 | 0 | 4% | 198812.5457 | 54298.6901
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 3612846.3891 | 8261.6388 | 1414460.882 | 14020.4326 | 57169.7904 | 6.565% | 335258.0358 | 190744.1802
[5 empty] | 2 | Major |  | 3612846.3891 | 28915.7357 | 6898628.5867 | 4272242.3788 | 779859.36 | 29.04% | 4528588.1361 | 4384074.2805
[5 empty] | 3 | Catastrophic |  | 60639197.9961 | 28915.7357 | 43872019.9295 | 12816727.1363 | 2314770.308 | 20% | 23934326.2211 | 11806486.6219
[5 empty] | Subtotal |  |  | 2025: 28798172.393; 2026: 16381305.0826
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 62.8
|  |  | N-1 Rating before transfers, MVA |  |  | 62.8
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 42.0622 | 43.2896 | 47.8192 | 49.4855 | 50.0688 | 50.7585 | 55.8467 | 55.8467 | 55.8467 | 55.8467 | 55.8467 | 55.8467
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 38.4313 | 40.9659 | 44.6776 | 45.4432 | 46.0037 | 46.7371 | 51.2497 | 51.2497 | 51.2497 | 51.2497 | 51.2497 | 51.2497
|  |  | Weighting to 50% PoE |  |  | 70% |  | 39.5206 | 41.663 | 45.62 | 46.6559 | 47.2233 | 47.9436 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 4.1206 | 6.263 | 10.22 | 11.2559 | 11.8233 | 12.5436 | 17.2288 | 17.2288 | 17.2288 | 17.2288 | 17.2288 | 17.2288
|  |  | N-3 |  |  |  |  | 39.5206 | 41.663 | 45.62 | 46.6559 | 47.2233 | 47.9436 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288
|  |  | N-4 |  |  |  |  | 39.5206 | 41.663 | 45.62 | 46.6559 | 47.2233 | 47.9436 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 3612846.3891 | 5491301.7043 | 8960763.3592 | 9869005.4999 | 10366439.6583 | 13747472.2516 | 18882363.793 | 18882363.793 | 18882363.793 | 18882363.793 | 18882363.793 | 18882363.793
|  |  | N-3 |  |  | Catastrophic |  | 60639197.9961 | 63926494.7976 | 69998052.6937 | 71587476.4399 | 72457986.2172 | 73563177.9673 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574
|  |  | N-4 |  |  | Catastrophic |  | 60639197.9961 | 63926494.7976 | 69998052.6937 | 71587476.4399 | 72457986.2172 | 73563177.9673 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 8.422% | 9.072% | 9.777% | 10.54% | 11.37% | 12.27% | 13.25% | 14.31% | 15.46% | 16.71% | 18.07% | 19.54%
|  |  | Major |  |  |  |  | 0.04528% | 0.04877% | 0.05256% | 0.05667% | 0.06113% | 0.06597% | 0.07123% | 0.07693% | 0.08313% | 0.08986% | 0.09717% | 0.1051%
|  |  | Catastrophic |  |  |  |  | 0.04528% | 0.04877% | 0.05256% | 0.05667% | 0.06113% | 0.06597% | 0.07123% | 0.07693% | 0.08313% | 0.08986% | 0.09717% | 0.1051%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 5491.2669 | 6235.7112 | 7358.4591 | 8114.0554 | 8859.0217 | 9706.2553 | 13146.6792 | 14199.6619 | 15343.2457 | 16585.5054 | 17935.2505 | 19394.8394
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 12170.5875 | 19926.1478 | 35041.9989 | 41611.8713 | 47148.955 | 67477.1944 | 100062.1873 | 108076.6638 | 116780.7249 | 126235.8284 | 136509.0277 | 147618.2704
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 65.4333 | 107.1298 | 188.3978 | 223.7197 | 253.489 | 362.7806 | 537.9687 | 581.0573 | 627.8534 | 678.6872 | 733.9195 | 793.6466
|  |  | Other significant risks |  |  | Significant |  | 16063.9873 | 17303.7147 | 18648.1249 | 20106.439 | 21688.7115 | 23405.9067 | 25269.9822 | 27293.9803 | 29492.128 | 31879.9461 | 34474.3684 | 37279.9273
|  |  | Other major risks |  |  | Major |  | 1985.0297 | 2138.2231 | 2304.3521 | 2484.5562 | 2680.0779 | 2892.272 | 3122.6161 | 3372.7219 | 3644.3474 | 3939.4105 | 4260.0037 | 4606.6872
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 5345.7641 | 5758.3199 | 6205.7119 | 6691.0088 | 7217.5565 | 7789.0037 | 8409.3296 | 9082.8745 | 9814.3728 | 10608.9895 | 11472.3597 | 12405.992
|  |  | Annual opex, pre-replacement |  |  |  |  | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326
|  |  | Subtotal |  |  |  |  | 55142.5014 | 65489.679 | 83767.4773 | 93252.0829 | 101868.2442 | 125653.8452 | 164569.1958 | 176627.3924 | 189723.1048 | 203948.7997 | 219405.3622 | 236119.7953
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 2735.6942
|  |  | Total annuity |  |  | 161972.0143
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 55142.5014 | 65489.679 | 83767.4773 | 93252.0829 | 101868.2442 | 125653.8452 | 164569.1958 | 176627.3924 | 189723.1048 | 203948.7997 | 219405.3622 | 236119.7953
|  |  | Annualised cost |  |  |  |  | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
CitiPower - Victoria Market Transformer Replacement Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 60639197.9961 | 0 | 0 | 0 | 0 | 20% | 12127839.5992 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 35848657.8828 | 0 | 0 | 20% | 7169731.5766 | 7169731.5766
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 3612846.3891 | 0 | 5597701.3296 | 0 | 0 | 4% | 368421.9087 | 223908.0532
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 11471.263 | 0 | 100% | 11471.263 | 11471.263
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 3612846.3891 | 0 | 1110655.0257 | 0 | 0 | 4% | 188940.0566 | 44426.201
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 3612846.3891 | 8261.6388 | 1157286.1761 | 11471.263 | 57169.7904 | 6.447% | 312473.8992 | 167960.0437
[5 empty] | 2 | Major |  | 3612846.3891 | 28915.7357 | 5644332.48 | 3495471.0372 | 779859.36 | 28.38% | 3849123.7354 | 3704609.8798
[5 empty] | 3 | Catastrophic |  | 60639197.9961 | 28915.7357 | 35895289.0333 | 10486413.1115 | 2314770.308 | 20% | 21872917.2369 | 9745077.6377
[5 empty] | Subtotal |  |  | 2025: 26034514.8715; 2026: 13617647.5612
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 62.8
|  |  | N-1 Rating before transfers, MVA |  |  | 62.8
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 42.0622 | 43.2896 | 47.8192 | 49.4855 | 50.0688 | 50.7585 | 55.8467 | 55.8467 | 55.8467 | 55.8467 | 55.8467 | 55.8467
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 38.4313 | 40.9659 | 44.6776 | 45.4432 | 46.0037 | 46.7371 | 51.2497 | 51.2497 | 51.2497 | 51.2497 | 51.2497 | 51.2497
|  |  | Weighting to 50% PoE |  |  | 70% |  | 39.5206 | 41.663 | 45.62 | 46.6559 | 47.2233 | 47.9436 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 4.1206 | 6.263 | 10.22 | 11.2559 | 11.8233 | 12.5436 | 17.2288 | 17.2288 | 17.2288 | 17.2288 | 17.2288 | 17.2288
|  |  | N-3 |  |  |  |  | 39.5206 | 41.663 | 45.62 | 46.6559 | 47.2233 | 47.9436 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288
|  |  | N-4 |  |  |  |  | 39.5206 | 41.663 | 45.62 | 46.6559 | 47.2233 | 47.9436 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288 | 52.6288
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 3612846.3891 | 5491301.7043 | 8960763.3592 | 9869005.4999 | 10366439.6583 | 13747472.2516 | 18882363.793 | 18882363.793 | 18882363.793 | 18882363.793 | 18882363.793 | 18882363.793
|  |  | N-3 |  |  | Catastrophic |  | 60639197.9961 | 63926494.7976 | 69998052.6937 | 71587476.4399 | 72457986.2172 | 73563177.9673 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574
|  |  | N-4 |  |  | Catastrophic |  | 60639197.9961 | 63926494.7976 | 69998052.6937 | 71587476.4399 | 72457986.2172 | 73563177.9673 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574 | 92288029.8574
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 8.422% | 9.072% | 9.777% | 10.54% | 11.37% | 12.27% | 13.25% | 14.31% | 15.46% | 16.71% | 18.07% | 19.54%
|  |  | Major |  |  |  |  | 0.04528% | 0.04877% | 0.05256% | 0.05667% | 0.06113% | 0.06597% | 0.07123% | 0.07693% | 0.08313% | 0.08986% | 0.09717% | 0.1051%
|  |  | Catastrophic |  |  |  |  | 0.04528% | 0.04877% | 0.05256% | 0.05667% | 0.06113% | 0.06597% | 0.07123% | 0.07693% | 0.08313% | 0.08986% | 0.09717% | 0.1051%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 5491.2669 | 6235.7112 | 7358.4591 | 8114.0554 | 8859.0217 | 9706.2553 | 13146.6792 | 14199.6619 | 15343.2457 | 16585.5054 | 17935.2505 | 19394.8394
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 12170.5875 | 19926.1478 | 35041.9989 | 41611.8713 | 47148.955 | 67477.1944 | 100062.1873 | 108076.6638 | 116780.7249 | 126235.8284 | 136509.0277 | 147618.2704
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 65.4333 | 107.1298 | 188.3978 | 223.7197 | 253.489 | 362.7806 | 537.9687 | 581.0573 | 627.8534 | 678.6872 | 733.9195 | 793.6466
|  |  | Other significant risks |  |  | Significant |  | 14145.1655 | 15236.8092 | 16420.6314 | 17704.7518 | 19098.024 | 20610.1026 | 22251.5167 | 24033.751 | 25969.3329 | 28071.9293 | 30356.4513 | 32826.89
|  |  | Other major risks |  |  | Major |  | 1677.3805 | 1806.8312 | 1947.2128 | 2099.488 | 2264.7068 | 2444.0141 | 2638.6584 | 2850.0017 | 3079.5294 | 3328.8622 | 3599.7684 | 3892.7212
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 4412.3953 | 4752.919 | 5122.1965 | 5522.7607 | 5957.3733 | 6429.046 | 6941.0632 | 7497.0074 | 8100.7863 | 8756.6631 | 9469.2892 | 10239.9095
|  |  | Annual opex, pre-replacement |  |  |  |  | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263
|  |  | Subtotal |  |  |  |  | 49433.4921 | 59536.8112 | 77550.1595 | 86747.9099 | 95052.8329 | 118500.6559 | 157049.3366 | 168709.406 | 181372.7355 | 195128.7387 | 210074.9697 | 226237.54
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 2238.2952
|  |  | Total annuity |  |  | 132522.5571
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 49433.4921 | 59536.8112 | 77550.1595 | 86747.9099 | 95052.8329 | 118500.6559 | 157049.3366 | 168709.406 | 181372.7355 | 195128.7387 | 210074.9697 | 226237.54
|  |  | Annualised cost |  |  |  |  | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - Victoria Market Transformer Replacement Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 81916109.5736 | 0 | 0 | 0 | 0 | 20% | 16383221.9147 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 43815026.3012 | 0 | 0 | 20% | 8763005.2602 | 8763005.2602
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 8873720.7109 | 0 | 6841634.9583 | 0 | 0 | 4% | 628614.2268 | 273665.3983
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 14020.4326 | 0 | 100% | 14020.4326 | 14020.4326
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 8873720.7109 | 0 | 1357467.2536 | 0 | 0 | 4% | 409247.5186 | 54298.6901
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 8873720.7109 | 8261.6388 | 1414460.882 | 14020.4326 | 69874.1883 | 5.379% | 558397.4065 | 203448.5781
[5 empty] | 2 | Major |  | 8873720.7109 | 28915.7357 | 6898628.5867 | 4272242.3788 | 953161.44 | 23.2% | 4877664.773 | 4522715.9445
[5 empty] | 3 | Catastrophic |  | 81916109.5736 | 28915.7357 | 43872019.9295 | 12816727.1363 | 2829163.7097 | 20% | 28292587.217 | 11909365.3022
[5 empty] | Subtotal |  |  | 2025: 33728649.3965; 2026: 16635529.8249
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 62.8
|  |  | N-1 Rating before transfers, MVA |  |  | 62.8
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 46.4898 | 47.8464 | 52.8528 | 54.6945 | 55.3392 | 56.1015 | 61.7253 | 61.7253 | 61.7253 | 61.7253 | 61.7253 | 61.7253
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 42.4767 | 45.2781 | 49.3805 | 50.2268 | 50.8462 | 51.6569 | 56.6444 | 56.6444 | 56.6444 | 56.6444 | 56.6444 | 56.6444
|  |  | Weighting to 50% PoE |  |  | 70% |  | 43.6806 | 46.0486 | 50.4222 | 51.5671 | 52.1941 | 52.9902 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 8.2806 | 10.6486 | 15.0222 | 16.1671 | 16.7941 | 17.5902 | 22.7686 | 22.7686 | 22.7686 | 22.7686 | 22.7686 | 22.7686
|  |  | N-3 |  |  |  |  | 43.6806 | 46.0486 | 50.4222 | 51.5671 | 52.1941 | 52.9902 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686
|  |  | N-4 |  |  |  |  | 43.6806 | 46.0486 | 50.4222 | 51.5671 | 52.1941 | 52.9902 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 8873720.7109 | 11411283.1542 | 20122624.7197 | 21656279.2116 | 22496244.7862 | 23562657.8784 | 30499265.7501 | 30499265.7501 | 30499265.7501 | 30499265.7501 | 30499265.7501 | 30499265.7501
|  |  | N-3 |  |  | Catastrophic |  | 81916109.5736 | 86356843.8494 | 108067169.071 | 110521016.258 | 111864961.1774 | 113571222.125 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196
|  |  | N-4 |  |  | Catastrophic |  | 81916109.5736 | 86356843.8494 | 108067169.071 | 110521016.258 | 111864961.1774 | 113571222.125 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 10.29% | 11.09% | 11.95% | 12.88% | 13.9% | 15% | 16.19% | 17.49% | 18.9% | 20.43% | 22.09% | 23.89%
|  |  | Major |  |  |  |  | 0.05534% | 0.05961% | 0.06424% | 0.06927% | 0.07472% | 0.08063% | 0.08705% | 0.09403% | 0.1016% | 0.1098% | 0.1188% | 0.1284%
|  |  | Catastrophic |  |  |  |  | 0.05534% | 0.05961% | 0.06424% | 0.06927% | 0.07472% | 0.08063% | 0.08705% | 0.09403% | 0.1016% | 0.1098% | 0.1188% | 0.1284%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 9066.4778 | 10295.609 | 13884.9677 | 15310.7322 | 16716.4387 | 18315.1171 | 21706.1156 | 23444.666 | 25332.8054 | 27383.8656 | 29612.3922 | 32022.2786
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 36535.7459 | 50609.576 | 96178.6479 | 111603.515 | 125055.4583 | 141354.1679 | 197539.1548 | 213361.0447 | 230544.2876 | 249210.2115 | 269491.1903 | 291422.6558
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 196.4287 | 272.0945 | 517.0895 | 600.0189 | 672.3412 | 759.9686 | 1062.0385 | 1147.1024 | 1239.4854 | 1339.8398 | 1448.8774 | 1566.7885
|  |  | Other significant risks |  |  | Significant |  | 20941.4568 | 22557.5997 | 24310.2098 | 26211.3083 | 28274.0024 | 30512.5854 | 32942.6456 | 35581.1854 | 38446.7514 | 41559.5769 | 44941.7372 | 48599.1412
|  |  | Other major risks |  |  | Major |  | 2502.8718 | 2696.0292 | 2905.4969 | 3132.7115 | 3379.2397 | 3646.7897 | 3937.2245 | 4252.5764 | 4595.0618 | 4967.0991 | 5371.3267 | 5808.4507
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 6590.6448 | 7099.2734 | 7650.8506 | 8249.1597 | 8898.3258 | 9602.8473 | 10367.63 | 11198.0248 | 12099.8688 | 13079.5298 | 14143.9551 | 15295.0045
|  |  | Annual opex, pre-replacement |  |  |  |  | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326 | 14020.4326
|  |  | Subtotal |  |  |  |  | 89854.0584 | 107550.6143 | 159467.695 | 179127.8783 | 197016.2387 | 218211.9087 | 281575.2416 | 303005.0323 | 326278.693 | 351560.5552 | 379029.9115 | 408734.7518
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 2735.6942
|  |  | Total annuity |  |  | 161972.0143
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 89854.0584 | 107550.6143 | 159467.695 | 179127.8783 | 197016.2387 | 218211.9087 | 281575.2416 | 303005.0323 | 326278.693 | 351560.5552 | 379029.9115 | 408734.7518
|  |  | Annualised cost |  |  |  |  | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - Victoria Market Transformer Replacement Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 81916109.5736 | 0 | 0 | 0 | 0 | 20% | 16383221.9147 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 35848657.8828 | 0 | 0 | 20% | 7169731.5766 | 7169731.5766
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 8873720.7109 | 0 | 5597701.3296 | 0 | 0 | 4% | 578856.8816 | 223908.0532
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 11471.263 | 0 | 100% | 11471.263 | 11471.263
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 8873720.7109 | 0 | 1110655.0257 | 0 | 0 | 4% | 399375.0295 | 44426.201
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 8873720.7109 | 8261.6388 | 1157286.1761 | 11471.263 | 69874.1883 | 5.292% | 535613.27 | 180664.4416
[5 empty] | 2 | Major |  | 8873720.7109 | 28915.7357 | 5644332.48 | 3495471.0372 | 953161.44 | 22.1% | 4198200.3722 | 3843251.5438
[5 empty] | 3 | Catastrophic |  | 81916109.5736 | 28915.7357 | 35895289.0333 | 10486413.1115 | 2829163.7097 | 20% | 26231178.2328 | 9847956.318
[5 empty] | Subtotal |  |  | 2025: 30964991.875; 2026: 13871872.3034
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 62.8
|  |  | N-1 Rating before transfers, MVA |  |  | 62.8
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 46.4898 | 47.8464 | 52.8528 | 54.6945 | 55.3392 | 56.1015 | 61.7253 | 61.7253 | 61.7253 | 61.7253 | 61.7253 | 61.7253
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 42.4767 | 45.2781 | 49.3805 | 50.2268 | 50.8462 | 51.6569 | 56.6444 | 56.6444 | 56.6444 | 56.6444 | 56.6444 | 56.6444
|  |  | Weighting to 50% PoE |  |  | 70% |  | 43.6806 | 46.0486 | 50.4222 | 51.5671 | 52.1941 | 52.9902 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 8.2806 | 10.6486 | 15.0222 | 16.1671 | 16.7941 | 17.5902 | 22.7686 | 22.7686 | 22.7686 | 22.7686 | 22.7686 | 22.7686
|  |  | N-3 |  |  |  |  | 43.6806 | 46.0486 | 50.4222 | 51.5671 | 52.1941 | 52.9902 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686
|  |  | N-4 |  |  |  |  | 43.6806 | 46.0486 | 50.4222 | 51.5671 | 52.1941 | 52.9902 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686 | 58.1686
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 8873720.7109 | 11411283.1542 | 20122624.7197 | 21656279.2116 | 22496244.7862 | 23562657.8784 | 30499265.7501 | 30499265.7501 | 30499265.7501 | 30499265.7501 | 30499265.7501 | 30499265.7501
|  |  | N-3 |  |  | Catastrophic |  | 81916109.5736 | 86356843.8494 | 108067169.071 | 110521016.258 | 111864961.1774 | 113571222.125 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196
|  |  | N-4 |  |  | Catastrophic |  | 81916109.5736 | 86356843.8494 | 108067169.071 | 110521016.258 | 111864961.1774 | 113571222.125 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196 | 124669794.7196
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 10.29% | 11.09% | 11.95% | 12.88% | 13.9% | 15% | 16.19% | 17.49% | 18.9% | 20.43% | 22.09% | 23.89%
|  |  | Major |  |  |  |  | 0.05534% | 0.05961% | 0.06424% | 0.06927% | 0.07472% | 0.08063% | 0.08705% | 0.09403% | 0.1016% | 0.1098% | 0.1188% | 0.1284%
|  |  | Catastrophic |  |  |  |  | 0.05534% | 0.05961% | 0.06424% | 0.06927% | 0.07472% | 0.08063% | 0.08705% | 0.09403% | 0.1016% | 0.1098% | 0.1188% | 0.1284%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 9066.4778 | 10295.609 | 13884.9677 | 15310.7322 | 16716.4387 | 18315.1171 | 21706.1156 | 23444.666 | 25332.8054 | 27383.8656 | 29612.3922 | 32022.2786
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 36535.7459 | 50609.576 | 96178.6479 | 111603.515 | 125055.4583 | 141354.1679 | 197539.1548 | 213361.0447 | 230544.2876 | 249210.2115 | 269491.1903 | 291422.6558
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 196.4287 | 272.0945 | 517.0895 | 600.0189 | 672.3412 | 759.9686 | 1062.0385 | 1147.1024 | 1239.4854 | 1339.8398 | 1448.8774 | 1566.7885
|  |  | Other significant risks |  |  | Significant |  | 18596.2302 | 20031.3818 | 21587.7178 | 23275.9129 | 25107.6066 | 27095.4915 | 29253.41 | 31596.4606 | 34141.1129 | 36905.3341 | 39908.7275 | 43156.5401
|  |  | Other major risks |  |  | Major |  | 2126.8561 | 2290.9947 | 2468.9933 | 2662.0727 | 2871.564 | 3098.9189 | 3345.7207 | 3613.696 | 3904.7286 | 4220.8734 | 4564.3723 | 4935.8256
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 5449.8607 | 5870.45 | 6326.554 | 6821.3009 | 7358.102 | 7940.6768 | 8573.0821 | 9259.7428 | 10005.4853 | 10815.5754 | 11695.7578 | 12647.5704
|  |  | Annual opex, pre-replacement |  |  |  |  | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263 | 11471.263
|  |  | Subtotal |  |  |  |  | 83442.8624 | 100841.3691 | 152435.2332 | 171744.8156 | 189252.7737 | 210035.6039 | 272950.7847 | 293893.9756 | 316639.1683 | 341346.9628 | 368192.5806 | 397222.9219
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 2238.2952
|  |  | Total annuity |  |  | 132522.5571
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 83442.8624 | 100841.3691 | 152435.2332 | 171744.8156 | 189252.7737 | 210035.6039 | 272950.7847 | 293893.9756 | 316639.1683 | 341346.9628 | 368192.5806 | 397222.9219
|  |  | Annualised cost |  |  |  |  | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - Victoria Market Transformer Replacement Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 67507.5757 | 81056.2049 | 119713.9127 | 134600.808 | 148043.1804 | 164034.3561 | 213156.1794 | 229208.0361 | 246641.0327 | 265578.2606 | 286154.0179 | 308404.251
|  |  | Annualised cost | Scenario Base case | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857 | 147247.2857
|  |  | Risk cost | Scenario A | 55142.5014 | 65489.679 | 83767.4773 | 93252.0829 | 101868.2442 | 125653.8452 | 164569.1958 | 176627.3924 | 189723.1048 | 203948.7997 | 219405.3622 | 236119.7953
|  |  | Annualised cost | Scenario A | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143
|  |  | Risk cost | Scenario B | 49433.4921 | 59536.8112 | 77550.1595 | 86747.9099 | 95052.8329 | 118500.6559 | 157049.3366 | 168709.406 | 181372.7355 | 195128.7387 | 210074.9697 | 226237.54
|  |  | Annualised cost | Scenario B | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571
|  |  | Risk cost | Scenario C | 89854.0584 | 107550.6143 | 159467.695 | 179127.8783 | 197016.2387 | 218211.9087 | 281575.2416 | 303005.0323 | 326278.693 | 351560.5552 | 379029.9115 | 408734.7518
|  |  | Annualised cost | Scenario C | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143 | 161972.0143
|  |  | Risk cost | Scenario D | 83442.8624 | 100841.3691 | 152435.2332 | 171744.8156 | 189252.7737 | 210035.6039 | 272950.7847 | 293893.9756 | 316639.1683 | 341346.9628 | 368192.5806 | 397222.9219
|  |  | Annualised cost | Scenario D | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571 | 132522.5571
Charts
End