## Inputs
CitiPower - J18 FR Circuit Breaker Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | J18 FR Circuit Breaker Risk Monetisation Model
|  | Model start & timeline |  | 2019
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 25
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex, real $2019 |  | 1800000 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1800000 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 1865246.0177 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1865246.0177 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 5507 | 4612
|  |  | Opex ($2021) | 5706.6166 | 4779.1748
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 18.28% | 18.31% | 18.72% | 20.6% | 22.69% | 25.03% | 27.64% | 30.55% | 33.81% | 37.45% | 41.52% | 46.08%
|  |  | Major | 2 |  |  |  |  | 0.2285% | 0.2288% | 0.234% | 0.2575% | 0.2837% | 0.3129% | 0.3455% | 0.3819% | 0.4226% | 0.4681% | 0.519% | 0.576%
|  |  | Catastrophic | 3 | bar: 2010 to 2021
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 8570 | 26450 | 20% | 365.5472
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 120153 | 47770 | 40% | 18512.1474
|  |  | Industrial | 2463 | 47070 | 80% | 747.8346
|  |  | Total | 131186 | 46364.084 | 40.02% | 19625.5292
Asset information
|  | Assets at risk |  | 1 |  |  | Sections lost
|  | N-rating, MVA |  | 90 |  | Total Sections | 3
|  |  | N-1 Rating before transfers, MVA | 61.3 |  | Significant | 1
|  |  | N-2 Rating before transfers, MVA | 0 |  | Major | 3
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major
|  |  | Average Consequence Loss Oil | 20 | 100
|  |  | Average Consequences Loss SF6 kgs | 0 | 0
|  |  | Average Consequence Fire | 0.005 | 0.05
|  |  | Average Consequence Waste | 1 | 1
|  |  | Average Consequence Disturbance | 2 | 5
|  |  | Average Cost of Fault (Air Insulated) | 1917.0584 | 3626.8673
|  |  | Average Cost of Fault (SF6 Insulated) | 1917.0584 | 3626.8673
|  |  | Average Cost of Fault (Oil Insulated) | 3989.554 | 13989.3451
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major
|  |  | Switching time only (hours required) | 2 | 2
|  |  | Number of weeks generation required | 2 | 12
|  |  | Max demand load net of transfers, MVA | 1.4271 | 60.0956
|  |  | Number of generators | 2 | 61
|  |  | Generator sites | 1 | 16
|  |  | Number of days to connect all generators | 1 | 6
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major
|  |  | Generator hire | 36268.6726 | 5530972.5664
|  |  | Fuel cost | 80529.9773 | 20346840.2782
|  |  | Fitter cost | 64661.8619 | 5212740.8708
|  |  | Traffic management cost | 145074.6903 | 13927170.2655
|  |  | Transformer hire | 18134.3363 | 1450746.9027
|  |  | Earthing and bunding | 2072.4956 | 33159.9292
|  |  | Temporary fencing | 6217.4867 | 596878.7257
|  |  | Miscellaneous materials | 2072.4956 | 33159.9292
|  |  | Installation & removal of step-down transformers | 2590.6195 | 41449.9115
|  |  | Council permits | 4144.9912 | 66319.8584
|  |  | Crane hire | 2590.6195 | 41449.9115
|  |  | Cable hire | 3108.7434 | 49739.8938
|  |  | Total | 0 | 0
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major
|  |  | Minor | 0.4284% | 1.5%
|  |  | Serious | 0.08569% | 0.2999%
|  |  | Fataility | 0.01714% | 0.05998%
|  |  | Value of event | 4243.0068 | 14850.5238
|  |  | Weighted likelyhood of consequence | 0.02679% | 0.09377%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 56.564 | 55.151 | 58.241 | 60.448 | 60.736 | 61.081 | 67.139 | 67.139 | 67.139 | 67.139 | 67.139 | 67.139
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 52.817 | 51.352 | 54.781 | 56.273 | 56.488 | 57.654 | 62.875 | 62.875 | 62.875 | 62.875 | 62.875 | 62.875
|  |  | Selected | 70% |  |  |  |  | 53.9411 | 52.4917 | 55.819 | 57.5255 | 57.7624 | 58.6821 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.8542 | 2.8542 | 2.8542 | 2.8542 | 2.8542 | 2.8542
|  |  | N-2 | [5 empty] | 53.9411 | 52.4917 | 55.819 | 57.5255 | 57.7624 | 58.6821 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542
|  |  | N-3 | [5 empty] | 53.9411 | 52.4917 | 55.819 | 57.5255 | 57.7624 | 58.6821 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542
|  |  | N-4 | [5 empty] | 53.9411 | 52.4917 | 55.819 | 57.5255 | 57.7624 | 58.6821 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542
End

## Base Case
CitiPower - J18 FR Circuit Breaker Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 2117245.2656 | 0 | 0 | 0 | 0 | 100% | 2117245.2656 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 186524.6018 | 0 | 100% | 186524.6018 | 186524.6018
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 13989.3451 | 100% | 13989.3451 | 13989.3451
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 705748.4219 | 0 | 0 | 0 | 0 | 100% | 705748.4219 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 62174.8673 | 0 | 100% | 62174.8673 | 62174.8673
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3989.554 | 100% | 3989.554 | 3989.554
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 705748.4219 | 4243.0068 | 51812.3894 | 62174.8673 | 3989.554 | 100% | 827968.2393 | 122219.8174
[5 empty] | 2 | Major |  | 2117245.2656 | 14850.5238 | 51812.3894 | 186524.6018 | 13989.3451 | 100% | 2384422.1256 | 267176.8601
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 3212390.3649; 2026: 389396.6775
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 90
|  |  | N-1 Rating before transfers, MVA |  |  | 61.3
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 56.564 | 55.151 | 58.241 | 60.448 | 60.736 | 61.081 | 67.139 | 67.139 | 67.139 | 67.139 | 67.139 | 67.139
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 52.817 | 51.352 | 54.781 | 56.273 | 56.488 | 57.654 | 62.875 | 62.875 | 62.875 | 62.875 | 62.875 | 62.875
|  |  | Selected |  |  | 70% |  | 53.9411 | 52.4917 | 55.819 | 57.5255 | 57.7624 | 58.6821 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.8542 | 2.8542 | 2.8542 | 2.8542 | 2.8542 | 2.8542
|  |  | N-2 |  |  |  |  | 53.9411 | 52.4917 | 55.819 | 57.5255 | 57.7624 | 58.6821 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542
|  |  | N-3 |  |  |  |  | 53.9411 | 52.4917 | 55.819 | 57.5255 | 57.7624 | 58.6821 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542
|  |  | N-4 |  |  |  |  | 53.9411 | 52.4917 | 55.819 | 57.5255 | 57.7624 | 58.6821 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542 | 64.1542
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Adjustment |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Adjustment |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Adjustment |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 705748.4219 | 686784.9272 | 730318.276 | 752645.5864 | 755745.1117 | 767778.1778 | 839373.4167 | 839373.4167 | 839373.4167 | 839373.4167 | 839373.4167 | 839373.4167
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 2117245.2656 | 2060354.7815 | 2190954.8281 | 2257936.7592 | 2267235.335 | 2303334.5334 | 2518120.25 | 2518120.25 | 2518120.25 | 2518120.25 | 2518120.25 | 2518120.25
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 18.28% | 18.31% | 18.72% | 20.6% | 22.69% | 25.03% | 27.64% | 30.55% | 33.81% | 37.45% | 41.52% | 46.08%
|  |  | Major |  |  |  |  | 0.2285% | 0.2288% | 0.234% | 0.2575% | 0.2837% | 0.3129% | 0.3455% | 0.3819% | 0.4226% | 0.4681% | 0.519% | 0.576%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 129005.1328 | 125724.7376 | 136713.925 | 155035.3833 | 171504.5601 | 192176.2788 | 231990.4099 | 256443.3929 | 283770.6007 | 314326.9561 | 348512.5218 | 386778.3483
|  |  | Network Performance |  |  | Major |  | 4837.6925 | 4714.6777 | 5126.7722 | 5813.8269 | 6431.421 | 7206.6105 | 8699.6404 | 9616.6272 | 10641.3975 | 11787.2609 | 13069.2196 | 14504.1881
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 22340.7992 | 22373.8959 | 22879.2726 | 25175.7223 | 27735.8804 | 30591.8433 | 33779.7516 | 37340.3113 | 41319.3822 | 45768.6441 | 50746.3495 | 56318.1752
|  |  | Other major risks |  |  | Major |  | 610.4723 | 611.3766 | 625.1863 | 687.9378 | 757.8952 | 835.9357 | 923.0467 | 1020.3406 | 1129.0705 | 1250.6485 | 1386.6665 | 1538.9191
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166
|  |  | Subtotal |  |  |  |  | 162500.7133 | 159131.3043 | 171051.7727 | 192419.4867 | 212136.3733 | 236517.2848 | 281099.4652 | 310127.2886 | 342567.0674 | 378840.1261 | 419421.374 | 464846.2473
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1865246.0177 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 104155.2882
|  |  | Post-replacement opex |  |  | 4779.1748
|  |  | Total annuity |  |  | 108934.463
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 162500.7133 | 159131.3043 | 171051.7727 | 192419.4867 | 212136.3733 | 236517.2848 | 281099.4652 | 310127.2886 | 342567.0674 | 378840.1261 | 419421.374 | 464846.2473
|  |  | Annualised cost |  |  |  |  | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - J18 FR Circuit Breaker Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1810244.7021 | 0 | 0 | 0 | 0 | 100% | 1810244.7021 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 205177.0619 | 0 | 100% | 205177.0619 | 205177.0619
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 12590.4106 | 100% | 12590.4106 | 12590.4106
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 603414.9007 | 0 | 0 | 0 | 0 | 100% | 603414.9007 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 68392.354 | 0 | 100% | 68392.354 | 68392.354
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3590.5986 | 100% | 3590.5986 | 3590.5986
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 603414.9007 | 4243.0068 | 56993.6283 | 68392.354 | 3590.5986 | 100% | 736634.4884 | 133219.5877
[5 empty] | 2 | Major |  | 1810244.7021 | 14850.5238 | 56993.6283 | 205177.0619 | 12590.4106 | 100% | 2099856.3267 | 289611.6247
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2836490.8151; 2026: 422831.2124
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 90
|  |  | N-1 Rating before transfers, MVA |  |  | 61.3
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 53.7358 | 52.3935 | 55.3289 | 57.4256 | 57.6992 | 58.0269 | 63.782 | 63.782 | 63.782 | 63.782 | 63.782 | 63.782
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 50.1761 | 48.7844 | 52.0419 | 53.4594 | 53.6636 | 54.7713 | 59.7312 | 59.7312 | 59.7312 | 59.7312 | 59.7312 | 59.7312
|  |  | Selected |  |  | 70% |  | 51.244 | 49.8671 | 53.0281 | 54.6492 | 54.8743 | 55.748 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 51.244 | 49.8671 | 53.0281 | 54.6492 | 54.8743 | 55.748 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465
|  |  | N-3 |  |  |  |  | 51.244 | 49.8671 | 53.0281 | 54.6492 | 54.8743 | 55.748 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465
|  |  | N-4 |  |  |  |  | 51.244 | 49.8671 | 53.0281 | 54.6492 | 54.8743 | 55.748 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 603414.9007 | 587201.1127 | 624422.126 | 643511.9764 | 646162.0705 | 656450.342 | 717664.2712 | 717664.2712 | 717664.2712 | 717664.2712 | 717664.2712 | 717664.2712
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1810244.7021 | 1761603.3382 | 1873266.378 | 1930535.9292 | 1938486.2114 | 1969351.026 | 2152992.8137 | 2152992.8137 | 2152992.8137 | 2152992.8137 | 2152992.8137 | 2152992.8137
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 16.45% | 16.48% | 16.85% | 18.54% | 20.42% | 22.53% | 24.87% | 27.5% | 30.43% | 33.7% | 37.37% | 41.47%
|  |  | Major |  |  |  |  | 0.2056% | 0.2059% | 0.2106% | 0.2317% | 0.2553% | 0.2816% | 0.3109% | 0.3437% | 0.3803% | 0.4213% | 0.4671% | 0.5184%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 99269.4497 | 96745.1856 | 105201.3653 | 119299.7274 | 131972.759 | 147879.6465 | 178516.6204 | 197333.1909 | 218361.4772 | 241874.5927 | 268180.3855 | 297625.939
|  |  | Network Performance |  |  | Major |  | 3722.6044 | 3627.9445 | 3945.0512 | 4473.7398 | 4948.9785 | 5545.4867 | 6694.3733 | 7399.9947 | 8188.5554 | 9070.2972 | 10056.7645 | 11160.9727
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 21916.3218 | 21948.7897 | 22444.5642 | 24697.3811 | 27208.8959 | 30010.5953 | 33137.933 | 36630.8417 | 40534.3099 | 44899.0354 | 49782.1639 | 55248.1243
|  |  | Other major risks |  |  | Major |  | 595.5601 | 596.4424 | 609.9147 | 671.1334 | 739.3819 | 815.5161 | 900.4992 | 995.4165 | 1101.4904 | 1220.0986 | 1352.7941 | 1501.3276
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782
|  |  | Subtotal |  |  |  |  | 131781.2142 | 129195.6403 | 138478.1737 | 155419.2598 | 171147.2936 | 190528.5228 | 225526.7042 | 248636.7219 | 274463.1111 | 303341.3021 | 335649.3862 | 371813.6419
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 2051770.6195 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 114570.817
|  |  | Post-replacement opex |  |  | 5257.0923
|  |  | Total annuity |  |  | 119827.9093
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 131781.2142 | 129195.6403 | 138478.1737 | 155419.2598 | 171147.2936 | 190528.5228 | 225526.7042 | 248636.7219 | 274463.1111 | 303341.3021 | 335649.3862 | 371813.6419
|  |  | Annualised cost |  |  |  |  | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
CitiPower - J18 FR Circuit Breaker Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1810244.7021 | 0 | 0 | 0 | 0 | 100% | 1810244.7021 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 167872.1416 | 0 | 100% | 167872.1416 | 167872.1416
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 12590.4106 | 100% | 12590.4106 | 12590.4106
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 603414.9007 | 0 | 0 | 0 | 0 | 100% | 603414.9007 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 55957.3805 | 0 | 100% | 55957.3805 | 55957.3805
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3590.5986 | 100% | 3590.5986 | 3590.5986
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 603414.9007 | 4243.0068 | 46631.1504 | 55957.3805 | 3590.5986 | 100% | 713837.037 | 110422.1364
[5 empty] | 2 | Major |  | 1810244.7021 | 14850.5238 | 46631.1504 | 167872.1416 | 12590.4106 | 100% | 2052188.9285 | 241944.2264
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2766025.9655; 2026: 352366.3628
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 90
|  |  | N-1 Rating before transfers, MVA |  |  | 61.3
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 53.7358 | 52.3935 | 55.3289 | 57.4256 | 57.6992 | 58.0269 | 63.782 | 63.782 | 63.782 | 63.782 | 63.782 | 63.782
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 50.1761 | 48.7844 | 52.0419 | 53.4594 | 53.6636 | 54.7713 | 59.7312 | 59.7312 | 59.7312 | 59.7312 | 59.7312 | 59.7312
|  |  | Selected |  |  | 70% |  | 51.244 | 49.8671 | 53.0281 | 54.6492 | 54.8743 | 55.748 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 51.244 | 49.8671 | 53.0281 | 54.6492 | 54.8743 | 55.748 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465
|  |  | N-3 |  |  |  |  | 51.244 | 49.8671 | 53.0281 | 54.6492 | 54.8743 | 55.748 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465
|  |  | N-4 |  |  |  |  | 51.244 | 49.8671 | 53.0281 | 54.6492 | 54.8743 | 55.748 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465 | 60.9465
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 603414.9007 | 587201.1127 | 624422.126 | 643511.9764 | 646162.0705 | 656450.342 | 717664.2712 | 717664.2712 | 717664.2712 | 717664.2712 | 717664.2712 | 717664.2712
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1810244.7021 | 1761603.3382 | 1873266.378 | 1930535.9292 | 1938486.2114 | 1969351.026 | 2152992.8137 | 2152992.8137 | 2152992.8137 | 2152992.8137 | 2152992.8137 | 2152992.8137
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 16.45% | 16.48% | 16.85% | 18.54% | 20.42% | 22.53% | 24.87% | 27.5% | 30.43% | 33.7% | 37.37% | 41.47%
|  |  | Major |  |  |  |  | 0.2056% | 0.2059% | 0.2106% | 0.2317% | 0.2553% | 0.2816% | 0.3109% | 0.3437% | 0.3803% | 0.4213% | 0.4671% | 0.5184%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 99269.4497 | 96745.1856 | 105201.3653 | 119299.7274 | 131972.759 | 147879.6465 | 178516.6204 | 197333.1909 | 218361.4772 | 241874.5927 | 268180.3855 | 297625.939
|  |  | Network Performance |  |  | Major |  | 3722.6044 | 3627.9445 | 3945.0512 | 4473.7398 | 4948.9785 | 5545.4867 | 6694.3733 | 7399.9947 | 8188.5554 | 9070.2972 | 10056.7645 | 11160.9727
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 18165.8502 | 18192.762 | 18603.6962 | 20470.9955 | 22552.7227 | 24874.976 | 27467.1422 | 30362.3204 | 33597.8002 | 37215.6039 | 41263.0979 | 45793.6856
|  |  | Other major risks |  |  | Major |  | 497.5364 | 498.2735 | 509.5284 | 560.671 | 617.6865 | 681.2897 | 752.2854 | 831.5801 | 920.1952 | 1019.2816 | 1130.1367 | 1254.2229
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549
|  |  | Subtotal |  |  |  |  | 126791.3956 | 124200.1204 | 133395.5959 | 149941.0886 | 165228.1016 | 184117.3538 | 218566.3762 | 241063.0409 | 266203.983 | 294315.7304 | 325766.3395 | 360970.7752
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1678721.4159 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 93739.7594
|  |  | Post-replacement opex |  |  | 4301.2573
|  |  | Total annuity |  |  | 98041.0167
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 126791.3956 | 124200.1204 | 133395.5959 | 149941.0886 | 165228.1016 | 184117.3538 | 218566.3762 | 241063.0409 | 266203.983 | 294315.7304 | 325766.3395 | 360970.7752
|  |  | Annualised cost |  |  |  |  | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - J18 FR Circuit Breaker Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 2445418.2817 | 0 | 0 | 0 | 0 | 100% | 2445418.2817 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 205177.0619 | 0 | 100% | 205177.0619 | 205177.0619
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 15388.2796 | 100% | 15388.2796 | 15388.2796
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 815139.4272 | 0 | 0 | 0 | 0 | 100% | 815139.4272 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 68392.354 | 0 | 100% | 68392.354 | 68392.354
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 4388.5094 | 100% | 4388.5094 | 4388.5094
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 815139.4272 | 4243.0068 | 56993.6283 | 68392.354 | 4388.5094 | 100% | 949156.9257 | 134017.4985
[5 empty] | 2 | Major |  | 2445418.2817 | 14850.5238 | 56993.6283 | 205177.0619 | 15388.2796 | 100% | 2737827.7754 | 292409.4937
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 3686984.7011; 2026: 426426.9922
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 90
|  |  | N-1 Rating before transfers, MVA |  |  | 61.3
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 59.3922 | 57.9086 | 61.1531 | 63.4704 | 63.7728 | 64.1351 | 70.4959 | 70.4959 | 70.4959 | 70.4959 | 70.4959 | 70.4959
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 55.4579 | 53.9196 | 57.52 | 59.0867 | 59.3124 | 60.5367 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187
|  |  | Selected |  |  | 70% |  | 56.6382 | 55.1163 | 58.61 | 60.4018 | 60.6505 | 61.6162 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0.31621 | 6.0619 | 6.0619 | 6.0619 | 6.0619 | 6.0619 | 6.0619
|  |  | N-2 |  |  |  |  | 56.6382 | 55.1163 | 58.61 | 60.4018 | 60.6505 | 61.6162 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619
|  |  | N-3 |  |  |  |  | 56.6382 | 55.1163 | 58.61 | 60.4018 | 60.6505 | 61.6162 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619
|  |  | N-4 |  |  |  |  | 56.6382 | 55.1163 | 58.61 | 60.4018 | 60.6505 | 61.6162 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 815139.4272 | 793236.5909 | 843517.6088 | 869305.6523 | 872885.604 | 886783.7953 | 969476.2962 | 969476.2962 | 969476.2962 | 969476.2962 | 969476.2962 | 969476.2962
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 2445418.2817 | 2379709.7727 | 2530552.8265 | 2607916.9569 | 2618656.8119 | 2660351.386 | 2908428.8887 | 2908428.8887 | 2908428.8887 | 2908428.8887 | 2908428.8887 | 2908428.8887
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 20.11% | 20.14% | 20.59% | 22.66% | 24.96% | 27.53% | 30.4% | 33.61% | 37.19% | 41.19% | 45.67% | 50.69%
|  |  | Major |  |  |  |  | 0.2513% | 0.2517% | 0.2574% | 0.2832% | 0.312% | 0.3442% | 0.38% | 0.4201% | 0.4649% | 0.5149% | 0.5709% | 0.6336%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 163901.0212 | 159733.2791 | 173695.0418 | 196972.4544 | 217896.5436 | 244159.9622 | 294743.8158 | 325811.3307 | 360530.5482 | 399352.3977 | 442785.1589 | 491401.8916
|  |  | Network Performance |  |  | Major |  | 6146.2883 | 5989.998 | 6513.5641 | 7386.467 | 8171.1204 | 9155.9986 | 11052.8931 | 12217.9249 | 13519.8956 | 14975.7149 | 16604.4435 | 18427.5709
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 26947.0524 | 26986.973 | 27596.549 | 30366.4833 | 33454.498 | 36899.3068 | 40744.502 | 45039.1822 | 49838.6628 | 55205.2789 | 61209.2937 | 67929.9252
|  |  | Other major risks |  |  | Major |  | 734.9389 | 736.0277 | 752.6529 | 828.1986 | 912.4194 | 1006.3712 | 1111.2429 | 1228.3736 | 1359.272 | 1505.6381 | 1669.3882 | 1852.683
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782
|  |  | Subtotal |  |  |  |  | 204006.5791 | 199723.556 | 214835.0859 | 241830.8816 | 266711.8596 | 297498.9169 | 353929.732 | 390574.0896 | 431525.6567 | 477316.3078 | 528545.5625 | 585889.3489
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 2051770.6195 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 114570.817
|  |  | Post-replacement opex |  |  | 5257.0923
|  |  | Total annuity |  |  | 119827.9093
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 204006.5791 | 199723.556 | 214835.0859 | 241830.8816 | 266711.8596 | 297498.9169 | 353929.732 | 390574.0896 | 431525.6567 | 477316.3078 | 528545.5625 | 585889.3489
|  |  | Annualised cost |  |  |  |  | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - J18 FR Circuit Breaker Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 2445418.2817 | 0 | 0 | 0 | 0 | 100% | 2445418.2817 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 167872.1416 | 0 | 100% | 167872.1416 | 167872.1416
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 15388.2796 | 100% | 15388.2796 | 15388.2796
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 815139.4272 | 0 | 0 | 0 | 0 | 100% | 815139.4272 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 55957.3805 | 0 | 100% | 55957.3805 | 55957.3805
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 4388.5094 | 100% | 4388.5094 | 4388.5094
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 815139.4272 | 4243.0068 | 46631.1504 | 55957.3805 | 4388.5094 | 100% | 926359.4744 | 111220.0472
[5 empty] | 2 | Major |  | 2445418.2817 | 14850.5238 | 46631.1504 | 167872.1416 | 15388.2796 | 100% | 2690160.3772 | 244742.0955
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 3616519.8516; 2026: 355962.1426
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 90
|  |  | N-1 Rating before transfers, MVA |  |  | 61.3
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 59.3922 | 57.9086 | 61.1531 | 63.4704 | 63.7728 | 64.1351 | 70.4959 | 70.4959 | 70.4959 | 70.4959 | 70.4959 | 70.4959
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 55.4579 | 53.9196 | 57.52 | 59.0867 | 59.3124 | 60.5367 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187
|  |  | Selected |  |  | 70% |  | 56.6382 | 55.1163 | 58.61 | 60.4018 | 60.6505 | 61.6162 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0.31621 | 6.0619 | 6.0619 | 6.0619 | 6.0619 | 6.0619 | 6.0619
|  |  | N-2 |  |  |  |  | 56.6382 | 55.1163 | 58.61 | 60.4018 | 60.6505 | 61.6162 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619
|  |  | N-3 |  |  |  |  | 56.6382 | 55.1163 | 58.61 | 60.4018 | 60.6505 | 61.6162 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619
|  |  | N-4 |  |  |  |  | 56.6382 | 55.1163 | 58.61 | 60.4018 | 60.6505 | 61.6162 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619 | 67.3619
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 815139.4272 | 793236.5909 | 843517.6088 | 869305.6523 | 872885.604 | 886783.7953 | 969476.2962 | 969476.2962 | 969476.2962 | 969476.2962 | 969476.2962 | 969476.2962
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 2445418.2817 | 2379709.7727 | 2530552.8265 | 2607916.9569 | 2618656.8119 | 2660351.386 | 2908428.8887 | 2908428.8887 | 2908428.8887 | 2908428.8887 | 2908428.8887 | 2908428.8887
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 20.11% | 20.14% | 20.59% | 22.66% | 24.96% | 27.53% | 30.4% | 33.61% | 37.19% | 41.19% | 45.67% | 50.69%
|  |  | Major |  |  |  |  | 0.2513% | 0.2517% | 0.2574% | 0.2832% | 0.312% | 0.3442% | 0.38% | 0.4201% | 0.4649% | 0.5149% | 0.5709% | 0.6336%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 163901.0212 | 159733.2791 | 173695.0418 | 196972.4544 | 217896.5436 | 244159.9622 | 294743.8158 | 325811.3307 | 360530.5482 | 399352.3977 | 442785.1589 | 491401.8916
|  |  | Network Performance |  |  | Major |  | 6146.2883 | 5989.998 | 6513.5641 | 7386.467 | 8171.1204 | 9155.9986 | 11052.8931 | 12217.9249 | 13519.8956 | 14975.7149 | 16604.4435 | 18427.5709
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 22363.1427 | 22396.2725 | 22902.1547 | 25200.901 | 27763.6196 | 30622.4388 | 33813.5354 | 37377.6561 | 41360.7065 | 45814.4182 | 50797.1019 | 56374.5001
|  |  | Other major risks |  |  | Major |  | 615.1322 | 616.0435 | 629.9585 | 693.189 | 763.6805 | 842.3167 | 930.0926 | 1028.1292 | 1137.689 | 1260.1951 | 1397.2514 | 1550.6662
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549
|  |  | Subtotal |  |  |  |  | 198161.5393 | 193871.5479 | 208876.6739 | 235388.9664 | 259730.919 | 289916.6711 | 345676.2918 | 381570.9958 | 421684.7942 | 466538.6809 | 516719.9106 | 572890.5837
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1678721.4159 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 93739.7594
|  |  | Post-replacement opex |  |  | 4301.2573
|  |  | Total annuity |  |  | 98041.0167
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 198161.5393 | 193871.5479 | 208876.6739 | 235388.9664 | 259730.919 | 289916.6711 | 345676.2918 | 381570.9958 | 421684.7942 | 466538.6809 | 516719.9106 | 572890.5837
|  |  | Annualised cost |  |  |  |  | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - J18 FR Circuit Breaker Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 162500.7133 | 159131.3043 | 171051.7727 | 192419.4867 | 212136.3733 | 236517.2848 | 281099.4652 | 310127.2886 | 342567.0674 | 378840.1261 | 419421.374 | 464846.2473
|  |  | Annualised cost | Scenario Base case | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463 | 108934.463
|  |  | Risk cost | Scenario A | 131781.2142 | 129195.6403 | 138478.1737 | 155419.2598 | 171147.2936 | 190528.5228 | 225526.7042 | 248636.7219 | 274463.1111 | 303341.3021 | 335649.3862 | 371813.6419
|  |  | Annualised cost | Scenario A | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093
|  |  | Risk cost | Scenario B | 126791.3956 | 124200.1204 | 133395.5959 | 149941.0886 | 165228.1016 | 184117.3538 | 218566.3762 | 241063.0409 | 266203.983 | 294315.7304 | 325766.3395 | 360970.7752
|  |  | Annualised cost | Scenario B | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167
|  |  | Risk cost | Scenario C | 204006.5791 | 199723.556 | 214835.0859 | 241830.8816 | 266711.8596 | 297498.9169 | 353929.732 | 390574.0896 | 431525.6567 | 477316.3078 | 528545.5625 | 585889.3489
|  |  | Annualised cost | Scenario C | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093 | 119827.9093
|  |  | Risk cost | Scenario D | 198161.5393 | 193871.5479 | 208876.6739 | 235388.9664 | 259730.919 | 289916.6711 | 345676.2918 | 381570.9958 | 421684.7942 | 466538.6809 | 516719.9106 | 572890.5837
|  |  | Annualised cost | Scenario D | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167 | 98041.0167
Charts
End