## Inputs
CitiPower - J18 TK Circuit Breaker Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | J18 TK Circuit Breaker Risk Monetisation Model
|  | Model start & timeline |  | 2019
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 25
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex, real $2019 |  | 1125000 |  |  |  |  | 0 | 0 | 0 | 0 | 1125000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 1165778.7611 |  |  |  |  | 0 | 0 | 0 | 0 | 1165778.7611 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 5507 | 4612
|  |  | Opex ($2021) | 5706.6166 | 4779.1748
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 10.96% | 11.8% | 12.7% | 13.68% | 14.75% | 15.91% | 17.17% | 18.54% | 20.04% | 21.66% | 23.44% | 25.37%
|  |  | Major | 2 |  |  |  |  | 0.137% | 0.1474% | 0.1587% | 0.171% | 0.1844% | 0.1989% | 0.2146% | 0.2318% | 0.2505% | 0.2708% | 0.293% | 0.3171%
|  |  | Catastrophic | 3 | bar: 2010 to 2021
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 66398 | 26450 | 20% | 1902.424
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 125231 | 47770 | 40% | 12960.5587
|  |  | Industrial | 3669 | 47070 | 80% | 748.3048
|  |  | Total | 195298 | 40508.4118 | 36.43% | 15611.2875
Asset information
|  | Assets at risk |  | 1 |  |  | Sections lost
|  | N-rating, MVA |  | 87 |  | Total Sections | 2
|  |  | N-1 Rating before transfers, MVA | 52.9 |  | Significant | 1
|  |  | N-2 Rating before transfers, MVA | 0 |  | Major | 2
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major
|  |  | Average Consequence Loss Oil | 20 | 100
|  |  | Average Consequences Loss SF6 kgs | 0 | 0
|  |  | Average Consequence Fire | 0.005 | 0.05
|  |  | Average Consequence Waste | 1 | 1
|  |  | Average Consequence Disturbance | 2 | 5
|  |  | Average Cost of Fault (Air Insulated) | 1917.0584 | 3626.8673
|  |  | Average Cost of Fault (SF6 Insulated) | 1917.0584 | 3626.8673
|  |  | Average Cost of Fault (Oil Insulated) | 3989.554 | 13989.3451
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major
|  |  | Switching time only (hours required) | 2 | 2
|  |  | Number of weeks generation required | 2 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 49.4243
|  |  | Number of generators | 0 | 50
|  |  | Generator sites | 0 | 13
|  |  | Number of days to connect all generators | 0 | 5
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major
|  |  | Generator hire | 0 | 4503360.177
|  |  | Fuel cost | 0 | 15235205.7232
|  |  | Fitter cost | 0 | 4235351.9575
|  |  | Traffic management cost | 0 | 11315825.8407
|  |  | Transformer hire | 0 | 1170873.646
|  |  | Earthing and bunding | 0 | 26942.4425
|  |  | Temporary fencing | 0 | 484963.9646
|  |  | Miscellaneous materials | 0 | 26942.4425
|  |  | Installation & removal of step-down transformers | 0 | 33678.0531
|  |  | Council permits | 0 | 53884.885
|  |  | Crane hire | 0 | 33678.0531
|  |  | Cable hire | 0 | 40413.6637
|  |  | Total | 0 | 0
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major
|  |  | Minor | 0.4284% | 1.5%
|  |  | Serious | 0.08569% | 0.2999%
|  |  | Fataility | 0.01714% | 0.05998%
|  |  | Value of event | 4243.0068 | 14850.5238
|  |  | Weighted likelyhood of consequence | 0.02679% | 0.09377%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 49.596 | 48.719 | 49.887 | 52.18 | 52.287 | 53.261 | 55.216 | 55.216 | 55.216 | 55.216 | 55.216 | 55.216
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 45.076 | 44.983 | 45.595 | 47.041 | 47.727 | 48.38 | 49.229 | 49.229 | 49.229 | 49.229 | 49.229 | 49.229
|  |  | Selected | 70% |  |  |  |  | 46.432 | 46.1038 | 46.8826 | 48.5827 | 49.095 | 49.8443 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 46.432 | 46.1038 | 46.8826 | 48.5827 | 49.095 | 49.8443 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251
|  |  | N-3 | [5 empty] | 46.432 | 46.1038 | 46.8826 | 48.5827 | 49.095 | 49.8443 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251
|  |  | N-4 | [5 empty] | 46.432 | 46.1038 | 46.8826 | 48.5827 | 49.095 | 49.8443 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251
End

## Base Case
CitiPower - J18 TK Circuit Breaker Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1449726.6052 | 0 | 0 | 0 | 0 | 100% | 1449726.6052 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 233155.7522 | 0 | 100% | 233155.7522 | 233155.7522
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 13989.3451 | 100% | 13989.3451 | 13989.3451
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 724863.3026 | 0 | 0 | 0 | 0 | 100% | 724863.3026 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 77718.5841 | 0 | 100% | 77718.5841 | 77718.5841
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3989.554 | 100% | 3989.554 | 3989.554
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 724863.3026 | 4243.0068 | 51812.3894 | 77718.5841 | 3989.554 | 100% | 862626.8368 | 137763.5342
[5 empty] | 2 | Major |  | 1449726.6052 | 14850.5238 | 51812.3894 | 233155.7522 | 13989.3451 | 100% | 1763534.6157 | 313808.0105
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2626161.4525; 2026: 451571.5447
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 87
|  |  | N-1 Rating before transfers, MVA |  |  | 52.9
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 49.596 | 48.719 | 49.887 | 52.18 | 52.287 | 53.261 | 55.216 | 55.216 | 55.216 | 55.216 | 55.216 | 55.216
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 45.076 | 44.983 | 45.595 | 47.041 | 47.727 | 48.38 | 49.229 | 49.229 | 49.229 | 49.229 | 49.229 | 49.229
|  |  | Selected |  |  | 70% |  | 46.432 | 46.1038 | 46.8826 | 48.5827 | 49.095 | 49.8443 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 46.432 | 46.1038 | 46.8826 | 48.5827 | 49.095 | 49.8443 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251
|  |  | N-3 |  |  |  |  | 46.432 | 46.1038 | 46.8826 | 48.5827 | 49.095 | 49.8443 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251
|  |  | N-4 |  |  |  |  | 46.432 | 46.1038 | 46.8826 | 48.5827 | 49.095 | 49.8443 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251 | 51.0251
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 724863.3026 | 719739.678 | 731897.7488 | 758438.4987 | 766436.1613 | 778133.699 | 796567.5074 | 796567.5074 | 796567.5074 | 796567.5074 | 796567.5074 | 796567.5074
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1449726.6052 | 1439479.3561 | 1463795.4975 | 1516876.9974 | 1532872.3226 | 1556267.3981 | 1593135.0147 | 1593135.0147 | 1593135.0147 | 1593135.0147 | 1593135.0147 | 1593135.0147
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 10.96% | 11.8% | 12.7% | 13.68% | 14.75% | 15.91% | 17.17% | 18.54% | 20.04% | 21.66% | 23.44% | 25.37%
|  |  | Major |  |  |  |  | 0.137% | 0.1474% | 0.1587% | 0.171% | 0.1844% | 0.1989% | 0.2146% | 0.2318% | 0.2505% | 0.2708% | 0.293% | 0.3171%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 79472.411 | 84899.4896 | 92948.0418 | 103765.7561 | 113039.4453 | 123793.5391 | 136778.6729 | 147715.3928 | 159617.8767 | 172575.397 | 186685.7082 | 202055.8669
|  |  | Network Performance |  |  | Major |  | 1986.8103 | 2122.4872 | 2323.701 | 2594.1439 | 2825.9861 | 3094.8385 | 3419.4668 | 3692.8848 | 3990.4469 | 4314.3849 | 4667.1427 | 5051.3967
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 15104.0895 | 16250.3946 | 17495.4094 | 18848.1166 | 20318.3439 | 21916.8447 | 23655.3879 | 25546.855 | 27605.3475 | 29846.3048 | 32286.6332 | 34944.8478
|  |  | Other major risks |  |  | Major |  | 430.0652 | 462.7044 | 498.1543 | 536.6705 | 578.5329 | 624.0477 | 673.55 | 727.4065 | 786.0189 | 849.8266 | 919.3111 | 994.9996
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166 | 5706.6166
|  |  | Subtotal |  |  |  |  | 102699.9925 | 109441.6924 | 118971.9231 | 131451.3037 | 142468.9248 | 155135.8866 | 170233.6942 | 183389.1557 | 197706.3066 | 213292.53 | 230265.4119 | 248753.7276
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 1165778.7611 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 65097.0551
|  |  | Post-replacement opex |  |  | 4779.1748
|  |  | Total annuity |  |  | 69876.2299
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 102699.9925 | 109441.6924 | 118971.9231 | 131451.3037 | 142468.9248 | 155135.8866 | 170233.6942 | 183389.1557 | 197706.3066 | 213292.53 | 230265.4119 | 248753.7276
|  |  | Annualised cost |  |  |  |  | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - J18 TK Circuit Breaker Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1239516.2474 | 0 | 0 | 0 | 0 | 100% | 1239516.2474 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 256471.3274 | 0 | 100% | 256471.3274 | 256471.3274
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 12590.4106 | 100% | 12590.4106 | 12590.4106
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 619758.1237 | 0 | 0 | 0 | 0 | 100% | 619758.1237 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 85490.4425 | 0 | 100% | 85490.4425 | 85490.4425
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3590.5986 | 100% | 3590.5986 | 3590.5986
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 619758.1237 | 4243.0068 | 56993.6283 | 85490.4425 | 3590.5986 | 100% | 770075.7999 | 150317.6762
[5 empty] | 2 | Major |  | 1239516.2474 | 14850.5238 | 56993.6283 | 256471.3274 | 12590.4106 | 100% | 1580422.1376 | 340905.8902
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2350497.9375; 2026: 491223.5663
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 87
|  |  | N-1 Rating before transfers, MVA |  |  | 52.9
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 47.1162 | 46.283 | 47.3926 | 49.571 | 49.6726 | 50.5979 | 52.4552 | 52.4552 | 52.4552 | 52.4552 | 52.4552 | 52.4552
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 42.8222 | 42.7338 | 43.3152 | 44.6889 | 45.3406 | 45.961 | 46.7675 | 46.7675 | 46.7675 | 46.7675 | 46.7675 | 46.7675
|  |  | Selected |  |  | 70% |  | 44.1104 | 43.7986 | 44.5385 | 46.1536 | 46.6402 | 47.3521 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 44.1104 | 43.7986 | 44.5385 | 46.1536 | 46.6402 | 47.3521 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738
|  |  | N-3 |  |  |  |  | 44.1104 | 43.7986 | 44.5385 | 46.1536 | 46.6402 | 47.3521 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738
|  |  | N-4 |  |  |  |  | 44.1104 | 43.7986 | 44.5385 | 46.1536 | 46.6402 | 47.3521 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 619758.1237 | 615377.4247 | 625772.5752 | 648464.9164 | 655302.9179 | 665304.3127 | 681065.2188 | 681065.2188 | 681065.2188 | 681065.2188 | 681065.2188 | 681065.2188
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1239516.2474 | 1230754.8494 | 1251545.1504 | 1296929.8328 | 1310605.8358 | 1330608.6254 | 1362130.4376 | 1362130.4376 | 1362130.4376 | 1362130.4376 | 1362130.4376 | 1362130.4376
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 9.867% | 10.62% | 11.43% | 12.31% | 13.27% | 14.32% | 15.45% | 16.69% | 18.03% | 19.5% | 21.09% | 22.83%
|  |  | Major |  |  |  |  | 0.1233% | 0.1327% | 0.1429% | 0.1539% | 0.1659% | 0.179% | 0.1932% | 0.2086% | 0.2254% | 0.2437% | 0.2637% | 0.2854%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 61154.0202 | 65330.1573 | 71523.5182 | 79847.7493 | 86983.8531 | 95259.1283 | 105251.1888 | 113666.9948 | 122825.9562 | 132796.768 | 143654.6525 | 155481.9896
|  |  | Network Performance |  |  | Major |  | 1528.8505 | 1633.2539 | 1788.088 | 1996.1937 | 2174.5963 | 2381.4782 | 2631.2797 | 2841.6749 | 3070.6489 | 3319.9192 | 3591.3663 | 3887.0497
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 14832.4481 | 15958.1373 | 17180.761 | 18509.1403 | 19952.9261 | 21522.6785 | 23229.9546 | 25087.4043 | 27108.8756 | 29309.5302 | 31705.9702 | 34316.3778
|  |  | Other major risks |  |  | Major |  | 420.4819 | 452.3938 | 487.0537 | 524.7117 | 565.6412 | 610.1418 | 658.541 | 711.1975 | 768.5037 | 830.8896 | 898.8258 | 972.8276
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782
|  |  | Subtotal |  |  |  |  | 84213.079 | 89651.2205 | 97256.6991 | 107155.0732 | 115954.295 | 126050.705 | 138048.2423 | 148584.5496 | 160051.2626 | 172534.3852 | 186128.093 | 200935.523
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 1282356.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 71606.7606
|  |  | Post-replacement opex |  |  | 5257.0923
|  |  | Total annuity |  |  | 76863.8529
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 84213.079 | 89651.2205 | 97256.6991 | 107155.0732 | 115954.295 | 126050.705 | 138048.2423 | 148584.5496 | 160051.2626 | 172534.3852 | 186128.093 | 200935.523
|  |  | Annualised cost |  |  |  |  | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
CitiPower - J18 TK Circuit Breaker Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1239516.2474 | 0 | 0 | 0 | 0 | 100% | 1239516.2474 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 209840.177 | 0 | 100% | 209840.177 | 209840.177
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 12590.4106 | 100% | 12590.4106 | 12590.4106
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 619758.1237 | 0 | 0 | 0 | 0 | 100% | 619758.1237 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 69946.7257 | 0 | 100% | 69946.7257 | 69946.7257
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3590.5986 | 100% | 3590.5986 | 3590.5986
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 619758.1237 | 4243.0068 | 46631.1504 | 69946.7257 | 3590.5986 | 100% | 744169.6052 | 124411.4815
[5 empty] | 2 | Major |  | 1239516.2474 | 14850.5238 | 46631.1504 | 209840.177 | 12590.4106 | 100% | 1523428.5093 | 283912.2618
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2267598.1145; 2026: 408323.7433
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 87
|  |  | N-1 Rating before transfers, MVA |  |  | 52.9
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 47.1162 | 46.283 | 47.3926 | 49.571 | 49.6726 | 50.5979 | 52.4552 | 52.4552 | 52.4552 | 52.4552 | 52.4552 | 52.4552
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 42.8222 | 42.7338 | 43.3152 | 44.6889 | 45.3406 | 45.961 | 46.7675 | 46.7675 | 46.7675 | 46.7675 | 46.7675 | 46.7675
|  |  | Selected |  |  | 70% |  | 44.1104 | 43.7986 | 44.5385 | 46.1536 | 46.6402 | 47.3521 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 44.1104 | 43.7986 | 44.5385 | 46.1536 | 46.6402 | 47.3521 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738
|  |  | N-3 |  |  |  |  | 44.1104 | 43.7986 | 44.5385 | 46.1536 | 46.6402 | 47.3521 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738
|  |  | N-4 |  |  |  |  | 44.1104 | 43.7986 | 44.5385 | 46.1536 | 46.6402 | 47.3521 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738 | 48.4738
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 619758.1237 | 615377.4247 | 625772.5752 | 648464.9164 | 655302.9179 | 665304.3127 | 681065.2188 | 681065.2188 | 681065.2188 | 681065.2188 | 681065.2188 | 681065.2188
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1239516.2474 | 1230754.8494 | 1251545.1504 | 1296929.8328 | 1310605.8358 | 1330608.6254 | 1362130.4376 | 1362130.4376 | 1362130.4376 | 1362130.4376 | 1362130.4376 | 1362130.4376
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 9.867% | 10.62% | 11.43% | 12.31% | 13.27% | 14.32% | 15.45% | 16.69% | 18.03% | 19.5% | 21.09% | 22.83%
|  |  | Major |  |  |  |  | 0.1233% | 0.1327% | 0.1429% | 0.1539% | 0.1659% | 0.179% | 0.1932% | 0.2086% | 0.2254% | 0.2437% | 0.2637% | 0.2854%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 61154.0202 | 65330.1573 | 71523.5182 | 79847.7493 | 86983.8531 | 95259.1283 | 105251.1888 | 113666.9948 | 122825.9562 | 132796.768 | 143654.6525 | 155481.9896
|  |  | Network Performance |  |  | Major |  | 1528.8505 | 1633.2539 | 1788.088 | 1996.1937 | 2174.5963 | 2381.4782 | 2631.2797 | 2841.6749 | 3070.6489 | 3319.9192 | 3591.3663 | 3887.0497
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 12276.18 | 13207.8645 | 14219.7776 | 15319.2201 | 16514.1795 | 17813.3961 | 19226.4352 | 20763.7666 | 22436.8515 | 24258.2387 | 26241.6691 | 28402.1914
|  |  | Other major risks |  |  | Major |  | 350.1845 | 376.7613 | 405.6267 | 436.9889 | 471.0757 | 508.1365 | 548.4442 | 592.2974 | 640.023 | 691.9791 | 748.5575 | 810.1875
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549
|  |  | Subtotal |  |  |  |  | 80445.1901 | 85683.9919 | 93072.9654 | 102736.1069 | 111279.6596 | 121098.0941 | 132793.3029 | 143000.6885 | 154109.4345 | 166202.8599 | 179372.2003 | 193717.3731
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 1049200.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 58587.3496
|  |  | Post-replacement opex |  |  | 4301.2573
|  |  | Total annuity |  |  | 62888.6069
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 80445.1901 | 85683.9919 | 93072.9654 | 102736.1069 | 111279.6596 | 121098.0941 | 132793.3029 | 143000.6885 | 154109.4345 | 166202.8599 | 179372.2003 | 193717.3731
|  |  | Annualised cost |  |  |  |  | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - J18 TK Circuit Breaker Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1674434.229 | 0 | 0 | 0 | 0 | 100% | 1674434.229 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 256471.3274 | 0 | 100% | 256471.3274 | 256471.3274
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 15388.2796 | 100% | 15388.2796 | 15388.2796
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 837217.1145 | 0 | 0 | 0 | 0 | 100% | 837217.1145 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 85490.4425 | 0 | 100% | 85490.4425 | 85490.4425
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 4388.5094 | 100% | 4388.5094 | 4388.5094
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 837217.1145 | 4243.0068 | 56993.6283 | 85490.4425 | 4388.5094 | 100% | 988332.7015 | 151115.587
[5 empty] | 2 | Major |  | 1674434.229 | 14850.5238 | 56993.6283 | 256471.3274 | 15388.2796 | 100% | 2018137.9882 | 343703.7592
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 3006470.6897; 2026: 494819.3462
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 87
|  |  | N-1 Rating before transfers, MVA |  |  | 52.9
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 52.0758 | 51.155 | 52.3814 | 54.789 | 54.9014 | 55.9241 | 57.9768 | 57.9768 | 57.9768 | 57.9768 | 57.9768 | 57.9768
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 47.3298 | 47.2321 | 47.8747 | 49.393 | 50.1133 | 50.799 | 51.6904 | 51.6904 | 51.6904 | 51.6904 | 51.6904 | 51.6904
|  |  | Selected |  |  | 70% |  | 48.7536 | 48.409 | 49.2267 | 51.0118 | 51.5498 | 52.3365 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.67636 | 0.67636 | 0.67636 | 0.67636 | 0.67636 | 0.67636
|  |  | N-2 |  |  |  |  | 48.7536 | 48.409 | 49.2267 | 51.0118 | 51.5498 | 52.3365 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764
|  |  | N-3 |  |  |  |  | 48.7536 | 48.409 | 49.2267 | 51.0118 | 51.5498 | 52.3365 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764
|  |  | N-4 |  |  |  |  | 48.7536 | 48.409 | 49.2267 | 51.0118 | 51.5498 | 52.3365 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 837217.1145 | 831299.3281 | 845341.8998 | 875996.466 | 885233.7663 | 898744.4224 | 920035.471 | 920035.471 | 920035.471 | 920035.471 | 920035.471 | 920035.471
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1674434.229 | 1662598.6563 | 1690683.7996 | 1751992.932 | 1770467.5326 | 1797488.8448 | 1840070.942 | 1840070.942 | 1840070.942 | 1840070.942 | 1840070.942 | 1840070.942
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 12.06% | 12.98% | 13.97% | 15.05% | 16.22% | 17.5% | 18.89% | 20.4% | 22.04% | 23.83% | 25.78% | 27.9%
|  |  | Major |  |  |  |  | 0.1508% | 0.1622% | 0.1746% | 0.1881% | 0.2028% | 0.2187% | 0.2361% | 0.255% | 0.2755% | 0.2979% | 0.3222% | 0.3488%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 100969.6981 | 107864.8016 | 118090.4872 | 131834.3931 | 143616.6152 | 157279.6914 | 173777.3039 | 187672.4066 | 202794.5124 | 219257.0419 | 237184.1923 | 256711.9789
|  |  | Network Performance |  |  | Major |  | 2524.2425 | 2696.62 | 2952.2622 | 3295.8598 | 3590.4154 | 3931.9923 | 4344.4326 | 4691.8102 | 5069.8628 | 5481.426 | 5929.6048 | 6417.7995
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 18224.777 | 19607.9225 | 21110.1724 | 22742.3654 | 24516.3593 | 26445.1298 | 28542.877 | 30825.144 | 33308.946 | 36012.9121 | 38957.4419 | 42164.8758
|  |  | Other major risks |  |  | Major |  | 518.1402 | 557.4637 | 600.1735 | 646.5776 | 697.0132 | 751.8492 | 811.4893 | 876.3753 | 946.9912 | 1023.8664 | 1107.5809 | 1198.77
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782 | 6277.2782
|  |  | Subtotal |  |  |  |  | 128514.1359 | 137004.0861 | 149030.3735 | 164796.4741 | 178697.6814 | 194685.9409 | 213753.381 | 230343.0143 | 248397.5905 | 268052.5247 | 289456.0982 | 312770.7024
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 1282356.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 71606.7606
|  |  | Post-replacement opex |  |  | 5257.0923
|  |  | Total annuity |  |  | 76863.8529
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 128514.1359 | 137004.0861 | 149030.3735 | 164796.4741 | 178697.6814 | 194685.9409 | 213753.381 | 230343.0143 | 248397.5905 | 268052.5247 | 289456.0982 | 312770.7024
|  |  | Annualised cost |  |  |  |  | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - J18 TK Circuit Breaker Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1674434.229 | 0 | 0 | 0 | 0 | 100% | 1674434.229 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 209840.177 | 0 | 100% | 209840.177 | 209840.177
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 15388.2796 | 100% | 15388.2796 | 15388.2796
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 837217.1145 | 0 | 0 | 0 | 0 | 100% | 837217.1145 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 69946.7257 | 0 | 100% | 69946.7257 | 69946.7257
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 4388.5094 | 100% | 4388.5094 | 4388.5094
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 837217.1145 | 4243.0068 | 46631.1504 | 69946.7257 | 4388.5094 | 100% | 962426.5068 | 125209.3923
[5 empty] | 2 | Major |  | 1674434.229 | 14850.5238 | 46631.1504 | 209840.177 | 15388.2796 | 100% | 1961144.3599 | 286710.1309
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2923570.8667; 2026: 411919.5231
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 87
|  |  | N-1 Rating before transfers, MVA |  |  | 52.9
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 52.0758 | 51.155 | 52.3814 | 54.789 | 54.9014 | 55.9241 | 57.9768 | 57.9768 | 57.9768 | 57.9768 | 57.9768 | 57.9768
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 47.3298 | 47.2321 | 47.8747 | 49.393 | 50.1133 | 50.799 | 51.6904 | 51.6904 | 51.6904 | 51.6904 | 51.6904 | 51.6904
|  |  | Selected |  |  | 70% |  | 48.7536 | 48.409 | 49.2267 | 51.0118 | 51.5498 | 52.3365 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.67636 | 0.67636 | 0.67636 | 0.67636 | 0.67636 | 0.67636
|  |  | N-2 |  |  |  |  | 48.7536 | 48.409 | 49.2267 | 51.0118 | 51.5498 | 52.3365 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764
|  |  | N-3 |  |  |  |  | 48.7536 | 48.409 | 49.2267 | 51.0118 | 51.5498 | 52.3365 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764
|  |  | N-4 |  |  |  |  | 48.7536 | 48.409 | 49.2267 | 51.0118 | 51.5498 | 52.3365 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764 | 53.5764
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 837217.1145 | 831299.3281 | 845341.8998 | 875996.466 | 885233.7663 | 898744.4224 | 920035.471 | 920035.471 | 920035.471 | 920035.471 | 920035.471 | 920035.471
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1674434.229 | 1662598.6563 | 1690683.7996 | 1751992.932 | 1770467.5326 | 1797488.8448 | 1840070.942 | 1840070.942 | 1840070.942 | 1840070.942 | 1840070.942 | 1840070.942
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 12.06% | 12.98% | 13.97% | 15.05% | 16.22% | 17.5% | 18.89% | 20.4% | 22.04% | 23.83% | 25.78% | 27.9%
|  |  | Major |  |  |  |  | 0.1508% | 0.1622% | 0.1746% | 0.1881% | 0.2028% | 0.2187% | 0.2361% | 0.255% | 0.2755% | 0.2979% | 0.3222% | 0.3488%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 100969.6981 | 107864.8016 | 118090.4872 | 131834.3931 | 143616.6152 | 157279.6914 | 173777.3039 | 187672.4066 | 202794.5124 | 219257.0419 | 237184.1923 | 256711.9789
|  |  | Network Performance |  |  | Major |  | 2524.2425 | 2696.62 | 2952.2622 | 3295.8598 | 3590.4154 | 3931.9923 | 4344.4326 | 4691.8102 | 5069.8628 | 5481.426 | 5929.6048 | 6417.7995
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 15100.4492 | 16246.478 | 17491.1928 | 18843.574 | 20313.4469 | 21911.5625 | 23649.6867 | 25540.6978 | 27598.6942 | 29839.1115 | 32278.8518 | 34936.4257
|  |  | Other major risks |  |  | Major |  | 432.2211 | 465.024 | 500.6516 | 539.3609 | 581.4331 | 627.1761 | 676.9265 | 731.0531 | 789.9592 | 854.0868 | 923.9197 | 999.9876
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549 | 5135.9549
|  |  | Subtotal |  |  |  |  | 124162.5659 | 132408.8785 | 144170.5486 | 159649.1427 | 173237.8656 | 188886.3772 | 207584.3046 | 223771.9226 | 241388.9836 | 260567.6212 | 281452.5235 | 304202.1466
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 1049200.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 58587.3496
|  |  | Post-replacement opex |  |  | 4301.2573
|  |  | Total annuity |  |  | 62888.6069
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 124162.5659 | 132408.8785 | 144170.5486 | 159649.1427 | 173237.8656 | 188886.3772 | 207584.3046 | 223771.9226 | 241388.9836 | 260567.6212 | 281452.5235 | 304202.1466
|  |  | Annualised cost |  |  |  |  | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - J18 TK Circuit Breaker Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 102699.9925 | 109441.6924 | 118971.9231 | 131451.3037 | 142468.9248 | 155135.8866 | 170233.6942 | 183389.1557 | 197706.3066 | 213292.53 | 230265.4119 | 248753.7276
|  |  | Annualised cost | Scenario Base case | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299 | 69876.2299
|  |  | Risk cost | Scenario A | 84213.079 | 89651.2205 | 97256.6991 | 107155.0732 | 115954.295 | 126050.705 | 138048.2423 | 148584.5496 | 160051.2626 | 172534.3852 | 186128.093 | 200935.523
|  |  | Annualised cost | Scenario A | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529
|  |  | Risk cost | Scenario B | 80445.1901 | 85683.9919 | 93072.9654 | 102736.1069 | 111279.6596 | 121098.0941 | 132793.3029 | 143000.6885 | 154109.4345 | 166202.8599 | 179372.2003 | 193717.3731
|  |  | Annualised cost | Scenario B | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069
|  |  | Risk cost | Scenario C | 128514.1359 | 137004.0861 | 149030.3735 | 164796.4741 | 178697.6814 | 194685.9409 | 213753.381 | 230343.0143 | 248397.5905 | 268052.5247 | 289456.0982 | 312770.7024
|  |  | Annualised cost | Scenario C | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529 | 76863.8529
|  |  | Risk cost | Scenario D | 124162.5659 | 132408.8785 | 144170.5486 | 159649.1427 | 173237.8656 | 188886.3772 | 207584.3046 | 223771.9226 | 241388.9836 | 260567.6212 | 281452.5235 | 304202.1466
|  |  | Annualised cost | Scenario D | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069 | 62888.6069
Charts
End