## Inputs
CitiPower - North Richmond Transformer No.1 Replacement Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | North Richmond Transformer No.1 Replacement Risk Monetisation Model
|  | Model start & timeline |  | 2019 | FY19/20
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 50
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex regulator, real $2019 |  | 3748000 |  |  |  |  | 0 | 0 | 0 | 50000 | 750000 | 2948000 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 3883856.708 |  |  |  |  | 0 | 0 | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 11500 | 4900
|  |  | Opex ($2021) | 11916.8496 | 5077.6142
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 11.85% | 12.69% | 13.6% | 14.57% | 15.62% | 16.75% | 17.97% | 19.29% | 20.7% | 22.23% | 23.87% | 25.64%
|  |  | Major | 2 |  |  |  |  | 0.06373% | 0.06825% | 0.07312% | 0.07835% | 0.084% | 0.09008% | 0.09663% | 0.1037% | 0.1113% | 0.1195% | 0.1283% | 0.1379%
|  |  | Catastrophic | 3 |  |  |  |  | 0.06373% | 0.06825% | 0.07312% | 0.07835% | 0.084% | 0.09008% | 0.09663% | 0.1037% | 0.1113% | 0.1195% | 0.1283% | 0.1379%
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 44487 | 26450 | 20% | 1927.4604
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 74037 | 47770 | 40% | 11586.7253
|  |  | Industrial | 10627 | 47070 | 80% | 3277.4912
|  |  | Total | 129151 | 40368.5727 | 39.32% | 16791.6769
Asset information
|  | Assets at risk |  | 3
|  | N-rating, MVA |  | 97.1
|  |  | N-1 Rating before transfers, MVA | 65.2
|  |  | N-2 Rating before transfers, MVA | 32.2
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major | Catastrophic
|  |  | Average Consequence Loss Oil | 500 | 4050 | 12150
|  |  | Average Consequences Loss SF6 kgs | 0 | 0 | 0
|  |  | Average Consequence Fire | 0.05 | 2.5 | 5
|  |  | Average Consequence Waste | 10 | 405 | 1215
|  |  | Average Consequence Disturbance | 2 | 3 | 5
|  |  | Average Cost of Fault (Air Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (SF6 Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (Oil Insulated) | 63521.9894 | 866510.4 | 2571967.0088
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Switching time only (hours required) | 0 | 0 | 0 | 0
|  |  | Number of weeks generation required | 1.1905 | 6 | 6 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 0 | 18.5617 | 50.7617
|  |  | Number of generators | 0 | 0 | 19 | 51
|  |  | Generator sites | 0 | 0 | 5 | 13
|  |  | Number of days to connect all generators | 0 | 0 | 2 | 5
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Generator hire | 0 | 0 | 872866.0531 | 4593427.3805
|  |  | Fuel cost | 0 | 0 | 3087832.5478 | 16888915.9427
|  |  | Fitter cost | 0 | 0 | 845578.1947 | 4235351.9575
|  |  | Traffic management cost | 0 | 0 | 2176120.354 | 11315825.8407
|  |  | Transformer hire | 0 | 0 | 229701.5929 | 1170873.646
|  |  | Earthing and bunding | 0 | 0 | 10362.4779 | 26942.4425
|  |  | Temporary fencing | 0 | 0 | 93262.3009 | 484963.9646
|  |  | Miscellaneous materials | 0 | 0 | 10362.4779 | 26942.4425
|  |  | Installation & removal of step-down transformers | 0 | 0 | 12953.0973 | 33678.0531
|  |  | Council permits | 0 | 0 | 20724.9558 | 53884.885
|  |  | Crane hire | 0 | 0 | 12953.0973 | 33678.0531
|  |  | Cable hire | 0 | 0 | 15543.7168 | 40413.6637
|  |  | Total | 0 | 0 | 7388260.8664 | 38904898.2719
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major | Catastrophic
|  |  | Minor | 1.172% | 4.103% | 4.103%
|  |  | Serious | 0.2345% | 0.8206% | 0.8206%
|  |  | Fataility | 0.02345% | 0.08206% | 0.08206%
|  |  | Value of event | 8261.6388 | 28915.7357 | 28915.7357
|  |  | Weighted likelyhood of consequence | 0.05217% | 0.1826% | 0.1826%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 50.599 | 52.313 | 52.234 | 52.236 | 52.915 | 53.263 | 55.456 | 55.456 | 55.456 | 55.456 | 55.456 | 55.456
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 46.625 | 48.399 | 48.405 | 48.499 | 48.771 | 49.47 | 50.508 | 50.508 | 50.508 | 50.508 | 50.508 | 50.508
|  |  | Weighting to 50% PoE | 70% |  |  |  |  | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 15.6172 | 17.3732 | 17.3537 | 17.4201 | 17.8142 | 18.4079 | 19.7924 | 19.7924 | 19.7924 | 19.7924 | 19.7924 | 19.7924
|  |  | N-3 | [5 empty] | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
|  |  | N-4 | [5 empty] | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
End

## Base Case
CitiPower - North Richmond Transformer No.1 Replacement Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 67446201.5376 | 0 | 0 | 0 | 0 | 20% | 13489240.3075 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 38904898.2719 | 0 | 0 | 20% | 7780979.6544 | 7780979.6544
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 11651570.1239 | 0 | 20% | 2330314.0248 | 2330314.0248
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2571967.0088 | 20% | 514393.4018 | 514393.4018
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 20% | 10362.4779 | 10362.4779
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3883856.708 | 0 | 80% | 3107085.3664 | 3107085.3664
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 866510.4 | 80% | 693208.32 | 693208.32
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 80% | 41449.9115 | 41449.9115
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 15734338.5502 | 0 | 7388260.8664 | 0 | 0 | 4% | 924903.9767 | 295530.4347
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 11916.8496 | 0 | 100% | 11916.8496 | 11916.8496
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 63521.9894 | 100% | 63521.9894 | 63521.9894
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 15734338.5502 | 0 | 1465924.7751 | 0 | 0 | 4% | 688010.533 | 58636.991
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 15734338.5502 | 8261.6388 | 1517737.1645 | 11916.8496 | 63521.9894 | 4.75% | 823523.4001 | 194149.8581
[5 empty] | 2 | Major |  | 15734338.5502 | 28915.7357 | 7440073.2558 | 3883856.708 | 866510.4 | 17.13% | 4789780.1631 | 4160406.6211
[5 empty] | 3 | Catastrophic |  | 67446201.5376 | 28915.7357 | 38956710.6612 | 11651570.1239 | 2571967.0088 | 20% | 24131073.0135 | 10641832.7059
[5 empty] | Subtotal |  |  | 2025: 29744376.5766; 2026: 14996389.1851
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 97.1
|  |  | N-1 Rating before transfers, MVA |  |  | 65.2
|  |  | N-2 Rating before transfers, MVA |  |  | 32.2
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 50.599 | 52.313 | 52.234 | 52.236 | 52.915 | 53.263 | 55.456 | 55.456 | 55.456 | 55.456 | 55.456 | 55.456
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 46.625 | 48.399 | 48.405 | 48.499 | 48.771 | 49.47 | 50.508 | 50.508 | 50.508 | 50.508 | 50.508 | 50.508
|  |  | Weighting to 50% PoE |  |  | 70% |  | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 15.6172 | 17.3732 | 17.3537 | 17.4201 | 17.8142 | 18.4079 | 19.7924 | 19.7924 | 19.7924 | 19.7924 | 19.7924 | 19.7924
|  |  | N-3 |  |  |  |  | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
|  |  | N-4 |  |  |  |  | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 15734338.5502 | 17503509.6241 | 17483863.3621 | 17550761.4027 | 17947817.3937 | 18545970.5068 | 19940855.1034 | 19940855.1034 | 19940855.1034 | 19940855.1034 | 19940855.1034 | 19940855.1034
|  |  | N-3 |  |  | Catastrophic |  | 67446201.5376 | 79912046.904 | 79880612.8849 | 79987649.7499 | 80622939.3355 | 81579984.3164 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671
|  |  | N-4 |  |  | Catastrophic |  | 67446201.5376 | 79912046.904 | 79880612.8849 | 79987649.7499 | 80622939.3355 | 81579984.3164 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 11.85% | 12.69% | 13.6% | 14.57% | 15.62% | 16.75% | 17.97% | 19.29% | 20.7% | 22.23% | 23.87% | 25.64%
|  |  | Major |  |  |  |  | 0.06373% | 0.06825% | 0.07312% | 0.07835% | 0.084% | 0.09008% | 0.09663% | 0.1037% | 0.1113% | 0.1195% | 0.1283% | 0.1379%
|  |  | Catastrophic |  |  |  |  | 0.06373% | 0.06825% | 0.07312% | 0.07835% | 0.084% | 0.09008% | 0.09663% | 0.1037% | 0.1113% | 0.1195% | 0.1283% | 0.1379%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 8597.3355 | 10908.3372 | 11681.1321 | 12534.791 | 13544.1849 | 14696.8274 | 16196.9319 | 17380.3519 | 18656.0184 | 20031.3583 | 21514.4085 | 23107.2584
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 74610.1323 | 88882.1141 | 95109.4983 | 102313.529 | 112162.7968 | 124288.939 | 143355.4824 | 153829.6733 | 165120.3167 | 177293.1475 | 190419.2988 | 204517.2633
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 401.1297 | 477.8608 | 511.3414 | 550.0727 | 603.0258 | 668.2201 | 770.7284 | 827.0413 | 887.7436 | 953.189 | 1023.7597 | 1099.5552
|  |  | Other significant risks |  |  | Significant |  | 23015.8175 | 24647.1282 | 26403.626 | 28295.2925 | 30332.9238 | 32528.1978 | 34893.7476 | 37443.2404 | 40191.4636 | 43154.4175 | 46349.4164 | 49780.9616
|  |  | Other major risks |  |  | Major |  | 2651.6254 | 2839.5667 | 3041.9308 | 3259.8675 | 3494.6206 | 3747.5355 | 4020.0677 | 4313.7918 | 4630.4114 | 4971.7698 | 5339.8619 | 5735.2062
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 6782.547 | 7263.2791 | 7780.9026 | 8338.3591 | 8938.83 | 9585.7568 | 10282.8623 | 11034.1741 | 11844.0499 | 12717.2048 | 13658.7412 | 14669.9856
|  |  | Annual opex, pre-replacement |  |  |  |  | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496
|  |  | Subtotal |  |  |  |  | 127975.437 | 146935.1357 | 156445.2808 | 167208.7614 | 180993.2315 | 197432.3262 | 221436.6698 | 236745.1223 | 253246.8531 | 271037.9364 | 290222.3359 | 310827.0799
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 144760.291
|  |  | Post-replacement opex |  |  | 5077.6142
|  |  | Total annuity |  |  | 149837.9052
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 127975.437 | 146935.1357 | 156445.2808 | 167208.7614 | 180993.2315 | 197432.3262 | 221436.6698 | 236745.1223 | 253246.8531 | 271037.9364 | 290222.3359 | 310827.0799
|  |  | Annualised cost |  |  |  |  | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - North Richmond Transformer No.1 Replacement Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 57666502.3147 | 0 | 0 | 0 | 0 | 20% | 11533300.4629 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 42795388.0991 | 0 | 0 | 20% | 8559077.6198 | 8559077.6198
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 11992991.0744 | 0 | 8127086.953 | 0 | 0 | 4% | 804803.1211 | 325083.4781
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 13108.5345 | 0 | 100% | 13108.5345 | 13108.5345
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 11992991.0744 | 0 | 1612517.2526 | 0 | 0 | 4% | 544220.3331 | 64500.6901
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 11992991.0744 | 8261.6388 | 1669510.8809 | 13108.5345 | 57169.7904 | 4.947% | 679753.9251 | 200034.2821
[5 empty] | 2 | Major |  | 11992991.0744 | 28915.7357 | 8184080.5814 | 4272242.3788 | 779859.36 | 19.46% | 4915212.0033 | 4435492.3603
[5 empty] | 3 | Catastrophic |  | 57666502.3147 | 28915.7357 | 42852381.7274 | 12816727.1363 | 2314770.308 | 20% | 23135859.4444 | 11602558.9815
[5 empty] | Subtotal |  |  | 2025: 28730825.3728; 2026: 16238085.6239
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 97.1
|  |  | N-1 Rating before transfers, MVA |  |  | 65.2
|  |  | N-2 Rating before transfers, MVA |  |  | 32.2
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 48.069 | 49.6974 | 49.6223 | 49.6242 | 50.2692 | 50.5998 | 52.6832 | 52.6832 | 52.6832 | 52.6832 | 52.6832 | 52.6832
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 44.2937 | 45.9791 | 45.9847 | 46.074 | 46.3325 | 46.9965 | 47.9826 | 47.9826 | 47.9826 | 47.9826 | 47.9826 | 47.9826
|  |  | Weighting to 50% PoE |  |  | 70% |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 13.2263 | 14.8945 | 14.876 | 14.9391 | 15.3135 | 15.8775 | 17.1928 | 17.1928 | 17.1928 | 17.1928 | 17.1928 | 17.1928
|  |  | N-3 |  |  |  |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
|  |  | N-4 |  |  |  |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 11992991.0744 | 13505632.3425 | 13488834.7885 | 13546032.6132 | 13885515.4856 | 14396936.3972 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274
|  |  | N-3 |  |  | Catastrophic |  | 57666502.3147 | 59784200.09 | 59760683.5145 | 59840760.4691 | 60316036.4904 | 69750886.5905 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187
|  |  | N-4 |  |  | Catastrophic |  | 57666502.3147 | 59784200.09 | 59760683.5145 | 59840760.4691 | 60316036.4904 | 69750886.5905 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 10.67% | 11.43% | 12.24% | 13.12% | 14.06% | 15.08% | 16.18% | 17.36% | 18.63% | 20% | 21.49% | 23.08%
|  |  | Major |  |  |  |  | 0.05736% | 0.06143% | 0.0658% | 0.07052% | 0.0756% | 0.08107% | 0.08696% | 0.09332% | 0.1002% | 0.1076% | 0.1155% | 0.1241%
|  |  | Catastrophic |  |  |  |  | 0.05736% | 0.06143% | 0.0658% | 0.07052% | 0.0756% | 0.08107% | 0.08696% | 0.09332% | 0.1002% | 0.1076% | 0.1155% | 0.1241%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 6615.6497 | 7344.7198 | 7865.0523 | 8439.8315 | 9119.469 | 11309.2087 | 12463.5391 | 13374.1808 | 14355.8062 | 15414.1302 | 16555.3373 | 17781.0354
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 51182.246 | 61722.9495 | 66039.4476 | 71070.8859 | 78098.3223 | 86835.1405 | 100866.5048 | 108236.2615 | 116180.4832 | 124745.4218 | 133981.1271 | 143900.6111
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 275.1734 | 331.8438 | 355.0508 | 382.1015 | 419.8835 | 466.8556 | 542.293 | 581.9154 | 624.6263 | 670.6743 | 720.3286 | 773.6592
|  |  | Other significant risks |  |  | Significant |  | 21342.0567 | 22854.7349 | 24483.4964 | 26237.5967 | 28127.0469 | 30162.6758 | 32356.1976 | 34720.2857 | 37268.652 | 40016.1334 | 42978.785 | 46160.7807
|  |  | Other major risks |  |  | Major |  | 2544.2555 | 2724.5868 | 2918.7567 | 3127.8687 | 3353.1161 | 3595.79 | 3857.2869 | 4139.1174 | 4442.9164 | 4770.4526 | 5123.6398 | 5502.9758
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 6655.3773 | 7127.0958 | 7635.0141 | 8182.0186 | 8771.231 | 9406.0282 | 10090.0632 | 10827.2882 | 11621.9792 | 12478.7628 | 13402.6459 | 14394.9299
|  |  | Annual opex, pre-replacement |  |  |  |  | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345
|  |  | Subtotal |  |  |  |  | 101723.2931 | 115214.4651 | 122405.3524 | 130548.8374 | 140997.6033 | 154884.2333 | 173284.4191 | 184987.5835 | 197602.9978 | 211204.1096 | 225870.3983 | 241622.5265
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 5585.3756
|  |  | Total annuity |  |  | 164821.6957
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 101723.2931 | 115214.4651 | 122405.3524 | 130548.8374 | 140997.6033 | 154884.2333 | 173284.4191 | 184987.5835 | 197602.9978 | 211204.1096 | 225870.3983 | 241622.5265
|  |  | Annualised cost |  |  |  |  | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
CitiPower - North Richmond Transformer No.1 Replacement Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 57666502.3147 | 0 | 0 | 0 | 0 | 20% | 11533300.4629 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 35014408.4447 | 0 | 0 | 20% | 7002881.6889 | 7002881.6889
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 11992991.0744 | 0 | 6649434.7798 | 0 | 0 | 4% | 745697.0342 | 265977.3912
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 10725.1646 | 0 | 100% | 10725.1646 | 10725.1646
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 11992991.0744 | 0 | 1319332.2976 | 0 | 0 | 4% | 532492.9349 | 52773.2919
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 11992991.0744 | 8261.6388 | 1365963.448 | 10725.1646 | 57169.7904 | 4.877% | 655280.6791 | 175561.0361
[5 empty] | 2 | Major |  | 11992991.0744 | 28915.7357 | 6696065.9302 | 3495471.0372 | 779859.36 | 18.38% | 4226398.8608 | 3746679.2178
[5 empty] | 3 | Catastrophic |  | 57666502.3147 | 28915.7357 | 35061039.5951 | 10486413.1115 | 2314770.308 | 20% | 21111528.213 | 9578227.7501
[5 empty] | Subtotal |  |  | 2025: 25993207.7529; 2026: 13500468.004
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 97.1
|  |  | N-1 Rating before transfers, MVA |  |  | 65.2
|  |  | N-2 Rating before transfers, MVA |  |  | 32.2
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 48.069 | 49.6974 | 49.6223 | 49.6242 | 50.2692 | 50.5998 | 52.6832 | 52.6832 | 52.6832 | 52.6832 | 52.6832 | 52.6832
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 44.2937 | 45.9791 | 45.9847 | 46.074 | 46.3325 | 46.9965 | 47.9826 | 47.9826 | 47.9826 | 47.9826 | 47.9826 | 47.9826
|  |  | Weighting to 50% PoE |  |  | 70% |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 13.2263 | 14.8945 | 14.876 | 14.9391 | 15.3135 | 15.8775 | 17.1928 | 17.1928 | 17.1928 | 17.1928 | 17.1928 | 17.1928
|  |  | N-3 |  |  |  |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
|  |  | N-4 |  |  |  |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 11992991.0744 | 13505632.3425 | 13488834.7885 | 13546032.6132 | 13885515.4856 | 14396936.3972 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274
|  |  | N-3 |  |  | Catastrophic |  | 57666502.3147 | 59784200.09 | 59760683.5145 | 59840760.4691 | 60316036.4904 | 69750886.5905 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187
|  |  | N-4 |  |  | Catastrophic |  | 57666502.3147 | 59784200.09 | 59760683.5145 | 59840760.4691 | 60316036.4904 | 69750886.5905 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 10.67% | 11.43% | 12.24% | 13.12% | 14.06% | 15.08% | 16.18% | 17.36% | 18.63% | 20% | 21.49% | 23.08%
|  |  | Major |  |  |  |  | 0.05736% | 0.06143% | 0.0658% | 0.07052% | 0.0756% | 0.08107% | 0.08696% | 0.09332% | 0.1002% | 0.1076% | 0.1155% | 0.1241%
|  |  | Catastrophic |  |  |  |  | 0.05736% | 0.06143% | 0.0658% | 0.07052% | 0.0756% | 0.08107% | 0.08696% | 0.09332% | 0.1002% | 0.1076% | 0.1155% | 0.1241%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 6615.6497 | 7344.7198 | 7865.0523 | 8439.8315 | 9119.469 | 11309.2087 | 12463.5391 | 13374.1808 | 14355.8062 | 15414.1302 | 16555.3373 | 17781.0354
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 51182.246 | 61722.9495 | 66039.4476 | 71070.8859 | 78098.3223 | 86835.1405 | 100866.5048 | 108236.2615 | 116180.4832 | 124745.4218 | 133981.1271 | 143900.6111
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 275.1734 | 331.8438 | 355.0508 | 382.1015 | 419.8835 | 466.8556 | 542.293 | 581.9154 | 624.6263 | 670.6743 | 720.3286 | 773.6592
|  |  | Other significant risks |  |  | Significant |  | 18730.9573 | 20058.5665 | 21488.0567 | 23027.5512 | 24685.8361 | 26472.4154 | 28397.5702 | 30472.4234 | 32709.0092 | 35120.3492 | 37720.5344 | 40513.228
|  |  | Other major risks |  |  | Major |  | 2149.1435 | 2301.47 | 2465.4862 | 2642.1239 | 2832.3914 | 3037.3791 | 3258.2666 | 3496.3301 | 3752.9504 | 4029.6215 | 4327.9603 | 4648.387
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 5494.1948 | 5883.6113 | 6302.9117 | 6754.4787 | 7240.8895 | 7764.9319 | 8329.6214 | 8938.2207 | 9594.2597 | 10301.5579 | 11064.2484 | 11883.4058
|  |  | Annual opex, pre-replacement |  |  |  |  | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646
|  |  | Subtotal |  |  |  |  | 95172.5292 | 108368.3254 | 115241.1698 | 123042.1373 | 133121.9564 | 146611.0958 | 164582.9597 | 175824.4964 | 187942.2994 | 201006.9195 | 215094.7008 | 230225.4911
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 4569.8527
|  |  | Total annuity |  |  | 134854.1147
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 95172.5292 | 108368.3254 | 115241.1698 | 123042.1373 | 133121.9564 | 146611.0958 | 164582.9597 | 175824.4964 | 187942.2994 | 201006.9195 | 215094.7008 | 230225.4911
|  |  | Annualised cost |  |  |  |  | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - North Richmond Transformer No.1 Replacement Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 89028986.0297 | 0 | 0 | 0 | 0 | 20% | 17805797.2059 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 42795388.0991 | 0 | 0 | 20% | 8559077.6198 | 8559077.6198
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 19957444.6085 | 0 | 8127086.953 | 0 | 0 | 4% | 1123381.2625 | 325083.4781
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 13108.5345 | 0 | 100% | 13108.5345 | 13108.5345
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 19957444.6085 | 0 | 1612517.2526 | 0 | 0 | 4% | 862798.4744 | 64500.6901
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 19957444.6085 | 8261.6388 | 1669510.8809 | 13108.5345 | 69874.1883 | 4.655% | 1011036.4644 | 212738.68
[5 empty] | 2 | Major |  | 19957444.6085 | 28915.7357 | 8184080.5814 | 4272242.3788 | 953161.44 | 16.09% | 5372431.8087 | 4574134.0243
[5 empty] | 3 | Catastrophic |  | 89028986.0297 | 28915.7357 | 42852381.7274 | 12816727.1363 | 2829163.7097 | 20% | 29511234.8677 | 11705437.6618
[5 empty] | Subtotal |  |  | 2025: 35894703.1408; 2026: 16492310.3661
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 97.1
|  |  | N-1 Rating before transfers, MVA |  |  | 65.2
|  |  | N-2 Rating before transfers, MVA |  |  | 32.2
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 53.1289 | 54.9287 | 54.8457 | 54.8478 | 55.5607 | 55.9261 | 58.2288 | 58.2288 | 58.2288 | 58.2288 | 58.2288 | 58.2288
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 48.9563 | 50.819 | 50.8253 | 50.924 | 51.2096 | 51.9435 | 53.0334 | 53.0334 | 53.0334 | 53.0334 | 53.0334 | 53.0334
|  |  | Weighting to 50% PoE |  |  | 70% |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 18.0081 | 19.8519 | 19.8314 | 19.9011 | 20.3149 | 20.9383 | 22.392 | 22.392 | 22.392 | 22.392 | 22.392 | 22.392
|  |  | N-3 |  |  |  |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
|  |  | N-4 |  |  |  |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 19957444.6085 | 22000837.1988 | 21978145.7663 | 22055413.0032 | 22514012.6728 | 23204879.5184 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275
|  |  | N-3 |  |  | Catastrophic |  | 89028986.0297 | 92298414.1741 | 92262107.8821 | 92385735.4611 | 93119494.9325 | 94224881.8854 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62
|  |  | N-4 |  |  | Catastrophic |  | 89028986.0297 | 92298414.1741 | 92262107.8821 | 92385735.4611 | 93119494.9325 | 94224881.8854 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 13.04% | 13.96% | 14.96% | 16.03% | 17.19% | 18.43% | 19.77% | 21.21% | 22.77% | 24.45% | 26.26% | 28.2%
|  |  | Major |  |  |  |  | 0.07011% | 0.07508% | 0.08043% | 0.08619% | 0.0924% | 0.09908% | 0.1063% | 0.1141% | 0.1224% | 0.1315% | 0.1412% | 0.1516%
|  |  | Catastrophic |  |  |  |  | 0.07011% | 0.07508% | 0.08043% | 0.08619% | 0.0924% | 0.09908% | 0.1063% | 0.1141% | 0.1224% | 0.1315% | 0.1412% | 0.1516%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 12483.3312 | 13859.0424 | 14840.8783 | 15925.452 | 17207.887 | 18672.3192 | 20578.2019 | 22081.7371 | 23702.4714 | 25449.8407 | 27334.056 | 29357.7718
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 104099.0911 | 122891.2979 | 131513.4654 | 141431.1205 | 154768.5733 | 171062.541 | 196243.143 | 210581.5422 | 226037.605 | 242701.3179 | 260670.0563 | 279969.136
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 559.6725 | 660.7059 | 707.0616 | 760.3824 | 832.0891 | 919.6911 | 1055.0707 | 1132.1588 | 1215.2559 | 1304.8458 | 1401.4519 | 1505.2104
|  |  | Other significant risks |  |  | Significant |  | 27741.4064 | 29707.6564 | 31824.7969 | 34104.8589 | 36560.8549 | 39206.8607 | 42058.1032 | 45131.0558 | 48443.542 | 52014.8471 | 55865.8406 | 60001.9478
|  |  | Other major risks |  |  | Major |  | 3206.8449 | 3434.139 | 3678.8758 | 3942.4459 | 4226.3535 | 4532.2259 | 4861.8232 | 5217.0497 | 5599.9657 | 6012.8007 | 6457.967 | 6936.0918
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 8206.4764 | 8788.1335 | 9414.427 | 10088.9161 | 10815.45 | 11598.1927 | 12441.6487 | 13350.691 | 14330.5923 | 15387.0576 | 16526.2603 | 17749.8056
|  |  | Annual opex, pre-replacement |  |  |  |  | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345
|  |  | Subtotal |  |  |  |  | 169405.357 | 192449.5096 | 205088.0396 | 219361.7102 | 237519.7423 | 259100.3652 | 290346.5252 | 310602.7693 | 332437.9669 | 355979.2443 | 381364.1666 | 408628.498
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 5585.3756
|  |  | Total annuity |  |  | 164821.6957
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 169405.357 | 192449.5096 | 205088.0396 | 219361.7102 | 237519.7423 | 259100.3652 | 290346.5252 | 310602.7693 | 332437.9669 | 355979.2443 | 381364.1666 | 408628.498
|  |  | Annualised cost |  |  |  |  | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - North Richmond Transformer No.1 Replacement Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 89028986.0297 | 0 | 0 | 0 | 0 | 20% | 17805797.2059 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 35014408.4447 | 0 | 0 | 20% | 7002881.6889 | 7002881.6889
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 19957444.6085 | 0 | 6649434.7798 | 0 | 0 | 4% | 1064275.1755 | 265977.3912
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 10725.1646 | 0 | 100% | 10725.1646 | 10725.1646
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 19957444.6085 | 0 | 1319332.2976 | 0 | 0 | 4% | 851071.0762 | 52773.2919
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 19957444.6085 | 8261.6388 | 1365963.448 | 10725.1646 | 69874.1883 | 4.607% | 986563.2184 | 188265.434
[5 empty] | 2 | Major |  | 19957444.6085 | 28915.7357 | 6696065.9302 | 3495471.0372 | 953161.44 | 15.04% | 4683618.6661 | 3885320.8818
[5 empty] | 3 | Catastrophic |  | 89028986.0297 | 28915.7357 | 35061039.5951 | 10486413.1115 | 2829163.7097 | 20% | 27486903.6363 | 9681106.4304
[5 empty] | Subtotal |  |  | 2025: 33157085.5209; 2026: 13754692.7462
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 97.1
|  |  | N-1 Rating before transfers, MVA |  |  | 65.2
|  |  | N-2 Rating before transfers, MVA |  |  | 32.2
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 53.1289 | 54.9287 | 54.8457 | 54.8478 | 55.5607 | 55.9261 | 58.2288 | 58.2288 | 58.2288 | 58.2288 | 58.2288 | 58.2288
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 48.9563 | 50.819 | 50.8253 | 50.924 | 51.2096 | 51.9435 | 53.0334 | 53.0334 | 53.0334 | 53.0334 | 53.0334 | 53.0334
|  |  | Weighting to 50% PoE |  |  | 70% |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 18.0081 | 19.8519 | 19.8314 | 19.9011 | 20.3149 | 20.9383 | 22.392 | 22.392 | 22.392 | 22.392 | 22.392 | 22.392
|  |  | N-3 |  |  |  |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
|  |  | N-4 |  |  |  |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 19957444.6085 | 22000837.1988 | 21978145.7663 | 22055413.0032 | 22514012.6728 | 23204879.5184 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275
|  |  | N-3 |  |  | Catastrophic |  | 89028986.0297 | 92298414.1741 | 92262107.8821 | 92385735.4611 | 93119494.9325 | 94224881.8854 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62
|  |  | N-4 |  |  | Catastrophic |  | 89028986.0297 | 92298414.1741 | 92262107.8821 | 92385735.4611 | 93119494.9325 | 94224881.8854 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 13.04% | 13.96% | 14.96% | 16.03% | 17.19% | 18.43% | 19.77% | 21.21% | 22.77% | 24.45% | 26.26% | 28.2%
|  |  | Major |  |  |  |  | 0.07011% | 0.07508% | 0.08043% | 0.08619% | 0.0924% | 0.09908% | 0.1063% | 0.1141% | 0.1224% | 0.1315% | 0.1412% | 0.1516%
|  |  | Catastrophic |  |  |  |  | 0.07011% | 0.07508% | 0.08043% | 0.08619% | 0.0924% | 0.09908% | 0.1063% | 0.1141% | 0.1224% | 0.1315% | 0.1412% | 0.1516%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 12483.3312 | 13859.0424 | 14840.8783 | 15925.452 | 17207.887 | 18672.3192 | 20578.2019 | 22081.7371 | 23702.4714 | 25449.8407 | 27334.056 | 29357.7718
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 104099.0911 | 122891.2979 | 131513.4654 | 141431.1205 | 154768.5733 | 171062.541 | 196243.143 | 210581.5422 | 226037.605 | 242701.3179 | 260670.0563 | 279969.136
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 559.6725 | 660.7059 | 707.0616 | 760.3824 | 832.0891 | 919.6911 | 1055.0707 | 1132.1588 | 1215.2559 | 1304.8458 | 1401.4519 | 1505.2104
|  |  | Other significant risks |  |  | Significant |  | 24550.0626 | 26290.1172 | 28163.704 | 30181.4698 | 32354.9305 | 34696.5425 | 37219.7809 | 39939.2241 | 42870.6451 | 46031.1109 | 49439.0899 | 53099.3835
|  |  | Other major risks |  |  | Major |  | 2723.9301 | 2916.9963 | 3124.8784 | 3348.7578 | 3589.9122 | 3849.7237 | 4129.6873 | 4431.4207 | 4756.6739 | 5107.3405 | 5485.4698 | 5891.5943
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 6787.2534 | 7268.319 | 7786.3018 | 8344.1451 | 8945.0327 | 9592.4084 | 10289.9976 | 11041.8307 | 11852.2684 | 12726.0292 | 13668.219 | 14680.1651
|  |  | Annual opex, pre-replacement |  |  |  |  | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646
|  |  | Subtotal |  |  |  |  | 161928.5055 | 184611.6433 | 196861.4542 | 210716.4923 | 228423.5894 | 249518.3904 | 280241.046 | 299933.0783 | 321160.0844 | 344045.6496 | 368723.5075 | 395228.4258
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 4569.8527
|  |  | Total annuity |  |  | 134854.1147
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 161928.5055 | 184611.6433 | 196861.4542 | 210716.4923 | 228423.5894 | 249518.3904 | 280241.046 | 299933.0783 | 321160.0844 | 344045.6496 | 368723.5075 | 395228.4258
|  |  | Annualised cost |  |  |  |  | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - North Richmond Transformer No.1 Replacement Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 127975.437 | 146935.1357 | 156445.2808 | 167208.7614 | 180993.2315 | 197432.3262 | 221436.6698 | 236745.1223 | 253246.8531 | 271037.9364 | 290222.3359 | 310827.0799
|  |  | Annualised cost | Scenario Base case | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052
|  |  | Risk cost | Scenario A | 101723.2931 | 115214.4651 | 122405.3524 | 130548.8374 | 140997.6033 | 154884.2333 | 173284.4191 | 184987.5835 | 197602.9978 | 211204.1096 | 225870.3983 | 241622.5265
|  |  | Annualised cost | Scenario A | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957
|  |  | Risk cost | Scenario B | 95172.5292 | 108368.3254 | 115241.1698 | 123042.1373 | 133121.9564 | 146611.0958 | 164582.9597 | 175824.4964 | 187942.2994 | 201006.9195 | 215094.7008 | 230225.4911
|  |  | Annualised cost | Scenario B | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147
|  |  | Risk cost | Scenario C | 169405.357 | 192449.5096 | 205088.0396 | 219361.7102 | 237519.7423 | 259100.3652 | 290346.5252 | 310602.7693 | 332437.9669 | 355979.2443 | 381364.1666 | 408628.498
|  |  | Annualised cost | Scenario C | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957
|  |  | Risk cost | Scenario D | 161928.5055 | 184611.6433 | 196861.4542 | 210716.4923 | 228423.5894 | 249518.3904 | 280241.046 | 299933.0783 | 321160.0844 | 344045.6496 | 368723.5075 | 395228.4258
|  |  | Annualised cost | Scenario D | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147
Charts
End