## Inputs
CitiPower - North Richmond Transformer No.2 Replacement Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | North Richmond Transformer No.2 Replacement Risk Monetisation Model
|  | Model start & timeline |  | 2019 | FY19/20
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 50
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex regulator, real $2019 |  | 3748000 |  |  |  |  | 0 | 0 | 0 | 0 | 50000 | 750000 | 2948000 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 3883856.708 |  |  |  |  | 0 | 0 | 0 | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 11500 | 4900
|  |  | Opex ($2021) | 11916.8496 | 5077.6142
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 16.28% | 17.53% | 18.87% | 20.33% | 21.9% | 23.61% | 25.45% | 27.45% | 29.62% | 31.96% | 34.5% | 37.24%
|  |  | Major | 2 |  |  |  |  | 0.08755% | 0.09424% | 0.1015% | 0.1093% | 0.1178% | 0.1269% | 0.1369% | 0.1476% | 0.1592% | 0.1718% | 0.1855% | 0.2002%
|  |  | Catastrophic | 3 |  |  |  |  | 0.08755% | 0.09424% | 0.1015% | 0.1093% | 0.1178% | 0.1269% | 0.1369% | 0.1476% | 0.1592% | 0.1718% | 0.1855% | 0.2002%
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 44487 | 26450 | 20% | 1927.4604
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 74037 | 47770 | 40% | 11586.7253
|  |  | Industrial | 10627 | 47070 | 80% | 3277.4912
|  |  | Total | 129151 | 40368.5727 | 39.32% | 16791.6769
Asset information
|  | Assets at risk |  | 3
|  | N-rating, MVA |  | 97.1
|  |  | N-1 Rating before transfers, MVA | 65.2
|  |  | N-2 Rating before transfers, MVA | 32.2
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major | Catastrophic
|  |  | Average Consequence Loss Oil | 500 | 4050 | 12150
|  |  | Average Consequences Loss SF6 kgs | 0 | 0 | 0
|  |  | Average Consequence Fire | 0.05 | 2.5 | 5
|  |  | Average Consequence Waste | 10 | 405 | 1215
|  |  | Average Consequence Disturbance | 2 | 3 | 5
|  |  | Average Cost of Fault (Air Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (SF6 Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (Oil Insulated) | 63521.9894 | 866510.4 | 2571967.0088
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Switching time only (hours required) | 0 | 0 | 0 | 0
|  |  | Number of weeks generation required | 1.1905 | 6 | 6 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 0 | 18.5617 | 50.7617
|  |  | Number of generators | 0 | 0 | 19 | 51
|  |  | Generator sites | 0 | 0 | 5 | 13
|  |  | Number of days to connect all generators | 0 | 0 | 2 | 5
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Generator hire | 0 | 0 | 872866.0531 | 4593427.3805
|  |  | Fuel cost | 0 | 0 | 3087832.5478 | 16888915.9427
|  |  | Fitter cost | 0 | 0 | 845578.1947 | 4235351.9575
|  |  | Traffic management cost | 0 | 0 | 2176120.354 | 11315825.8407
|  |  | Transformer hire | 0 | 0 | 229701.5929 | 1170873.646
|  |  | Earthing and bunding | 0 | 0 | 10362.4779 | 26942.4425
|  |  | Temporary fencing | 0 | 0 | 93262.3009 | 484963.9646
|  |  | Miscellaneous materials | 0 | 0 | 10362.4779 | 26942.4425
|  |  | Installation & removal of step-down transformers | 0 | 0 | 12953.0973 | 33678.0531
|  |  | Council permits | 0 | 0 | 20724.9558 | 53884.885
|  |  | Crane hire | 0 | 0 | 12953.0973 | 33678.0531
|  |  | Cable hire | 0 | 0 | 15543.7168 | 40413.6637
|  |  | Total | 0 | 0 | 7388260.8664 | 38904898.2719
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major | Catastrophic
|  |  | Minor | 1.172% | 4.103% | 4.103%
|  |  | Serious | 0.2345% | 0.8206% | 0.8206%
|  |  | Fataility | 0.02345% | 0.08206% | 0.08206%
|  |  | Value of event | 8261.6388 | 28915.7357 | 28915.7357
|  |  | Weighted likelyhood of consequence | 0.05217% | 0.1826% | 0.1826%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 50.599 | 52.313 | 52.234 | 52.236 | 52.915 | 53.263 | 55.456 | 55.456 | 55.456 | 55.456 | 55.456 | 55.456
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 46.625 | 48.399 | 48.405 | 48.499 | 48.771 | 49.47 | 50.508 | 50.508 | 50.508 | 50.508 | 50.508 | 50.508
|  |  | Weighting to 50% PoE | 70% |  |  |  |  | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 15.6172 | 17.3732 | 17.3537 | 17.4201 | 17.8142 | 18.4079 | 19.7924 | 19.7924 | 19.7924 | 19.7924 | 19.7924 | 19.7924
|  |  | N-3 | [5 empty] | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
|  |  | N-4 | [5 empty] | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
End

## Base Case
CitiPower - North Richmond Transformer No.2 Replacement Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 67446201.5376 | 0 | 0 | 0 | 0 | 20% | 13489240.3075 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 38904898.2719 | 0 | 0 | 20% | 7780979.6544 | 7780979.6544
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 11651570.1239 | 0 | 20% | 2330314.0248 | 2330314.0248
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2571967.0088 | 20% | 514393.4018 | 514393.4018
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 20% | 10362.4779 | 10362.4779
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3883856.708 | 0 | 80% | 3107085.3664 | 3107085.3664
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 866510.4 | 80% | 693208.32 | 693208.32
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 80% | 41449.9115 | 41449.9115
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 15734338.5502 | 0 | 7388260.8664 | 0 | 0 | 4% | 924903.9767 | 295530.4347
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 11916.8496 | 0 | 100% | 11916.8496 | 11916.8496
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 63521.9894 | 100% | 63521.9894 | 63521.9894
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 15734338.5502 | 0 | 1465924.7751 | 0 | 0 | 4% | 688010.533 | 58636.991
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 15734338.5502 | 8261.6388 | 1517737.1645 | 11916.8496 | 63521.9894 | 4.75% | 823523.4001 | 194149.8581
[5 empty] | 2 | Major |  | 15734338.5502 | 28915.7357 | 7440073.2558 | 3883856.708 | 866510.4 | 17.13% | 4789780.1631 | 4160406.6211
[5 empty] | 3 | Catastrophic |  | 67446201.5376 | 28915.7357 | 38956710.6612 | 11651570.1239 | 2571967.0088 | 20% | 24131073.0135 | 10641832.7059
[5 empty] | Subtotal |  |  | 2025: 29744376.5766; 2026: 14996389.1851
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 97.1
|  |  | N-1 Rating before transfers, MVA |  |  | 65.2
|  |  | N-2 Rating before transfers, MVA |  |  | 32.2
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 50.599 | 52.313 | 52.234 | 52.236 | 52.915 | 53.263 | 55.456 | 55.456 | 55.456 | 55.456 | 55.456 | 55.456
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 46.625 | 48.399 | 48.405 | 48.499 | 48.771 | 49.47 | 50.508 | 50.508 | 50.508 | 50.508 | 50.508 | 50.508
|  |  | Weighting to 50% PoE |  |  | 70% |  | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 15.6172 | 17.3732 | 17.3537 | 17.4201 | 17.8142 | 18.4079 | 19.7924 | 19.7924 | 19.7924 | 19.7924 | 19.7924 | 19.7924
|  |  | N-3 |  |  |  |  | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
|  |  | N-4 |  |  |  |  | 47.8172 | 49.5732 | 49.5537 | 49.6201 | 50.0142 | 50.6079 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924 | 51.9924
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 15734338.5502 | 17503509.6241 | 17483863.3621 | 17550761.4027 | 17947817.3937 | 18545970.5068 | 19940855.1034 | 19940855.1034 | 19940855.1034 | 19940855.1034 | 19940855.1034 | 19940855.1034
|  |  | N-3 |  |  | Catastrophic |  | 67446201.5376 | 79912046.904 | 79880612.8849 | 79987649.7499 | 80622939.3355 | 81579984.3164 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671
|  |  | N-4 |  |  | Catastrophic |  | 67446201.5376 | 79912046.904 | 79880612.8849 | 79987649.7499 | 80622939.3355 | 81579984.3164 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671 | 83811799.671
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 16.28% | 17.53% | 18.87% | 20.33% | 21.9% | 23.61% | 25.45% | 27.45% | 29.62% | 31.96% | 34.5% | 37.24%
|  |  | Major |  |  |  |  | 0.08755% | 0.09424% | 0.1015% | 0.1093% | 0.1178% | 0.1269% | 0.1369% | 0.1476% | 0.1592% | 0.1718% | 0.1855% | 0.2002%
|  |  | Catastrophic |  |  |  |  | 0.08755% | 0.09424% | 0.1015% | 0.1093% | 0.1178% | 0.1269% | 0.1369% | 0.1476% | 0.1592% | 0.1718% | 0.1855% | 0.2002%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 11809.8192 | 15061.2062 | 16210.8019 | 17484.4231 | 18988.8114 | 20709.7587 | 22939.6291 | 24740.58 | 26690.9033 | 28803.3431 | 31091.7497 | 33561.9688
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 102488.9826 | 122720.0653 | 131990.7374 | 142714.2283 | 157251.1158 | 175139.4276 | 203033.6135 | 218973.4336 | 236235.3161 | 254932.0562 | 275186.2402 | 297049.6059
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 551.016 | 659.7853 | 709.6276 | 767.2808 | 845.4361 | 941.6098 | 1091.5786 | 1177.2765 | 1270.0823 | 1370.6025 | 1479.4959 | 1597.0409
|  |  | Other significant risks |  |  | Significant |  | 31615.9166 | 34030.437 | 36642.3347 | 39468.2979 | 42526.4548 | 45836.4999 | 49419.8306 | 53299.6966 | 57501.362 | 62052.282 | 66982.2949 | 72303.9941
|  |  | Other major risks |  |  | Major |  | 3642.4327 | 3920.6068 | 4221.5204 | 4547.0963 | 4899.423 | 5280.7694 | 5693.6007 | 6140.5956 | 6624.6645 | 7148.9707 | 7716.9517 | 8330.0584
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 9316.9161 | 10028.4527 | 10798.1547 | 11630.9397 | 12532.15 | 13507.5895 | 14563.5636 | 15706.924 | 16945.1156 | 18286.2294 | 19739.0583 | 21307.3134
|  |  | Annual opex, pre-replacement |  |  |  |  | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496 | 11916.8496
|  |  | Subtotal |  |  |  |  | 171341.9327 | 198337.4029 | 212490.0264 | 228529.1157 | 248960.2408 | 273332.5044 | 308658.6657 | 331955.3558 | 357184.2934 | 384510.3333 | 414112.6403 | 446066.8311
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 144760.291
|  |  | Post-replacement opex |  |  | 5077.6142
|  |  | Total annuity |  |  | 149837.9052
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 171341.9327 | 198337.4029 | 212490.0264 | 228529.1157 | 248960.2408 | 273332.5044 | 308658.6657 | 331955.3558 | 357184.2934 | 384510.3333 | 414112.6403 | 446066.8311
|  |  | Annualised cost |  |  |  |  | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - North Richmond Transformer No.2 Replacement Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 57666502.3147 | 0 | 0 | 0 | 0 | 20% | 11533300.4629 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 42795388.0991 | 0 | 0 | 20% | 8559077.6198 | 8559077.6198
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 11992991.0744 | 0 | 8127086.953 | 0 | 0 | 4% | 804803.1211 | 325083.4781
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 13108.5345 | 0 | 100% | 13108.5345 | 13108.5345
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 11992991.0744 | 0 | 1612517.2526 | 0 | 0 | 4% | 544220.3331 | 64500.6901
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 11992991.0744 | 8261.6388 | 1669510.8809 | 13108.5345 | 57169.7904 | 4.947% | 679753.9251 | 200034.2821
[5 empty] | 2 | Major |  | 11992991.0744 | 28915.7357 | 8184080.5814 | 4272242.3788 | 779859.36 | 19.46% | 4915212.0033 | 4435492.3603
[5 empty] | 3 | Catastrophic |  | 57666502.3147 | 28915.7357 | 42852381.7274 | 12816727.1363 | 2314770.308 | 20% | 23135859.4444 | 11602558.9815
[5 empty] | Subtotal |  |  | 2025: 28730825.3728; 2026: 16238085.6239
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 97.1
|  |  | N-1 Rating before transfers, MVA |  |  | 65.2
|  |  | N-2 Rating before transfers, MVA |  |  | 32.2
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 48.069 | 49.6974 | 49.6223 | 49.6242 | 50.2692 | 50.5998 | 52.6832 | 52.6832 | 52.6832 | 52.6832 | 52.6832 | 52.6832
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 44.2937 | 45.9791 | 45.9847 | 46.074 | 46.3325 | 46.9965 | 47.9826 | 47.9826 | 47.9826 | 47.9826 | 47.9826 | 47.9826
|  |  | Weighting to 50% PoE |  |  | 70% |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 13.2263 | 14.8945 | 14.876 | 14.9391 | 15.3135 | 15.8775 | 17.1928 | 17.1928 | 17.1928 | 17.1928 | 17.1928 | 17.1928
|  |  | N-3 |  |  |  |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
|  |  | N-4 |  |  |  |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 11992991.0744 | 13505632.3425 | 13488834.7885 | 13546032.6132 | 13885515.4856 | 14396936.3972 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274
|  |  | N-3 |  |  | Catastrophic |  | 57666502.3147 | 59784200.09 | 59760683.5145 | 59840760.4691 | 60316036.4904 | 69750886.5905 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187
|  |  | N-4 |  |  | Catastrophic |  | 57666502.3147 | 59784200.09 | 59760683.5145 | 59840760.4691 | 60316036.4904 | 69750886.5905 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 14.66% | 15.78% | 16.99% | 18.3% | 19.71% | 21.25% | 22.91% | 24.71% | 26.66% | 28.76% | 31.05% | 33.52%
|  |  | Major |  |  |  |  | 0.07879% | 0.08481% | 0.09132% | 0.09837% | 0.106% | 0.1142% | 0.1232% | 0.1328% | 0.1433% | 0.1547% | 0.1669% | 0.1802%
|  |  | Catastrophic |  |  |  |  | 0.07879% | 0.08481% | 0.09132% | 0.09837% | 0.106% | 0.1142% | 0.1232% | 0.1328% | 0.1433% | 0.1547% | 0.1669% | 0.1802%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 9087.6558 | 10140.8984 | 10914.9356 | 11772.4806 | 12785.4041 | 15936.1593 | 17652.0446 | 19037.8763 | 20538.6501 | 22164.1725 | 23925.1014 | 25825.935
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 70307.0234 | 85221.2446 | 91648.0009 | 99134.755 | 109493.0643 | 122362.1098 | 142856.6986 | 154072.1326 | 166217.7842 | 179373.0176 | 193624.0858 | 209007.3919
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 377.9947 | 458.1787 | 492.7312 | 532.9826 | 588.6724 | 657.8608 | 768.0468 | 828.3448 | 893.644 | 964.3711 | 1040.9897 | 1123.6957
|  |  | Other significant risks |  |  | Significant |  | 29316.7377 | 31555.6689 | 33977.6236 | 36598.0766 | 39433.8376 | 42503.1689 | 45825.912 | 49423.6256 | 53319.7366 | 57539.7037 | 62111.1953 | 67045.8889
|  |  | Other major risks |  |  | Major |  | 3494.943 | 3761.8532 | 4050.5823 | 4362.975 | 4701.0352 | 5066.9401 | 5463.055 | 5891.9501 | 6356.4181 | 6859.494 | 7404.4763 | 7992.757
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 9142.228 | 9840.4237 | 10595.6941 | 11412.8647 | 12297.1778 | 13254.3282 | 14290.5033 | 15412.4262 | 16627.4023 | 17943.3707 | 19368.9597 | 20907.8108
|  |  | Annual opex, pre-replacement |  |  |  |  | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345
|  |  | Subtotal |  |  |  |  | 134835.1172 | 154086.8021 | 164788.1022 | 176922.669 | 192407.7259 | 212889.1017 | 239964.7948 | 257774.89 | 277062.1698 | 297952.6641 | 320583.3427 | 345012.0138
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 5585.3756
|  |  | Total annuity |  |  | 164821.6957
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 134835.1172 | 154086.8021 | 164788.1022 | 176922.669 | 192407.7259 | 212889.1017 | 239964.7948 | 257774.89 | 277062.1698 | 297952.6641 | 320583.3427 | 345012.0138
|  |  | Annualised cost |  |  |  |  | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
CitiPower - North Richmond Transformer No.2 Replacement Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 57666502.3147 | 0 | 0 | 0 | 0 | 20% | 11533300.4629 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 35014408.4447 | 0 | 0 | 20% | 7002881.6889 | 7002881.6889
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 11992991.0744 | 0 | 6649434.7798 | 0 | 0 | 4% | 745697.0342 | 265977.3912
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 10725.1646 | 0 | 100% | 10725.1646 | 10725.1646
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 11992991.0744 | 0 | 1319332.2976 | 0 | 0 | 4% | 532492.9349 | 52773.2919
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 11992991.0744 | 8261.6388 | 1365963.448 | 10725.1646 | 57169.7904 | 4.877% | 655280.6791 | 175561.0361
[5 empty] | 2 | Major |  | 11992991.0744 | 28915.7357 | 6696065.9302 | 3495471.0372 | 779859.36 | 18.38% | 4226398.8608 | 3746679.2178
[5 empty] | 3 | Catastrophic |  | 57666502.3147 | 28915.7357 | 35061039.5951 | 10486413.1115 | 2314770.308 | 20% | 21111528.213 | 9578227.7501
[5 empty] | Subtotal |  |  | 2025: 25993207.7529; 2026: 13500468.004
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 97.1
|  |  | N-1 Rating before transfers, MVA |  |  | 65.2
|  |  | N-2 Rating before transfers, MVA |  |  | 32.2
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 48.069 | 49.6974 | 49.6223 | 49.6242 | 50.2692 | 50.5998 | 52.6832 | 52.6832 | 52.6832 | 52.6832 | 52.6832 | 52.6832
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 44.2937 | 45.9791 | 45.9847 | 46.074 | 46.3325 | 46.9965 | 47.9826 | 47.9826 | 47.9826 | 47.9826 | 47.9826 | 47.9826
|  |  | Weighting to 50% PoE |  |  | 70% |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 13.2263 | 14.8945 | 14.876 | 14.9391 | 15.3135 | 15.8775 | 17.1928 | 17.1928 | 17.1928 | 17.1928 | 17.1928 | 17.1928
|  |  | N-3 |  |  |  |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
|  |  | N-4 |  |  |  |  | 45.4263 | 47.0945 | 47.076 | 47.1391 | 47.5135 | 48.0775 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928 | 49.3928
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 11992991.0744 | 13505632.3425 | 13488834.7885 | 13546032.6132 | 13885515.4856 | 14396936.3972 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274 | 15589562.7274
|  |  | N-3 |  |  | Catastrophic |  | 57666502.3147 | 59784200.09 | 59760683.5145 | 59840760.4691 | 60316036.4904 | 69750886.5905 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187
|  |  | N-4 |  |  | Catastrophic |  | 57666502.3147 | 59784200.09 | 59760683.5145 | 59840760.4691 | 60316036.4904 | 69750886.5905 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187 | 71659088.7187
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 14.66% | 15.78% | 16.99% | 18.3% | 19.71% | 21.25% | 22.91% | 24.71% | 26.66% | 28.76% | 31.05% | 33.52%
|  |  | Major |  |  |  |  | 0.07879% | 0.08481% | 0.09132% | 0.09837% | 0.106% | 0.1142% | 0.1232% | 0.1328% | 0.1433% | 0.1547% | 0.1669% | 0.1802%
|  |  | Catastrophic |  |  |  |  | 0.07879% | 0.08481% | 0.09132% | 0.09837% | 0.106% | 0.1142% | 0.1232% | 0.1328% | 0.1433% | 0.1547% | 0.1669% | 0.1802%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 9087.6558 | 10140.8984 | 10914.9356 | 11772.4806 | 12785.4041 | 15936.1593 | 17652.0446 | 19037.8763 | 20538.6501 | 22164.1725 | 23925.1014 | 25825.935
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 70307.0234 | 85221.2446 | 91648.0009 | 99134.755 | 109493.0643 | 122362.1098 | 142856.6986 | 154072.1326 | 166217.7842 | 179373.0176 | 193624.0858 | 209007.3919
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 377.9947 | 458.1787 | 492.7312 | 532.9826 | 588.6724 | 657.8608 | 768.0468 | 828.3448 | 893.644 | 964.3711 | 1040.9897 | 1123.6957
|  |  | Other significant risks |  |  | Significant |  | 25729.9738 | 27694.9824 | 29820.6225 | 32120.4754 | 34609.2946 | 37303.1077 | 40219.3289 | 43376.8793 | 46796.3197 | 50499.9938 | 54512.185 | 58843.1422
|  |  | Other major risks |  |  | Major |  | 2952.1932 | 3177.6534 | 3421.5441 | 3685.4235 | 3970.9844 | 4280.0658 | 4614.6658 | 4976.9552 | 5369.2933 | 5794.2437 | 6254.5925 | 6751.5158
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 7547.1577 | 8123.5372 | 8747.0334 | 9421.63 | 10151.6545 | 10941.8081 | 11797.1988 | 12723.3767 | 13726.3724 | 14812.7402 | 15989.6026 | 17259.966
|  |  | Annual opex, pre-replacement |  |  |  |  | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646
|  |  | Subtotal |  |  |  |  | 126727.1633 | 145541.6593 | 155770.0323 | 167392.9117 | 182324.2387 | 202206.2762 | 228633.1481 | 245740.7295 | 264267.2283 | 284333.7034 | 306071.7217 | 329536.8112
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 4569.8527
|  |  | Total annuity |  |  | 134854.1147
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 126727.1633 | 145541.6593 | 155770.0323 | 167392.9117 | 182324.2387 | 202206.2762 | 228633.1481 | 245740.7295 | 264267.2283 | 284333.7034 | 306071.7217 | 329536.8112
|  |  | Annualised cost |  |  |  |  | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147
|  |  | Feasible ? |  |  |  |  | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - North Richmond Transformer No.2 Replacement Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 89028986.0297 | 0 | 0 | 0 | 0 | 20% | 17805797.2059 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 42795388.0991 | 0 | 0 | 20% | 8559077.6198 | 8559077.6198
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 19957444.6085 | 0 | 8127086.953 | 0 | 0 | 4% | 1123381.2625 | 325083.4781
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 13108.5345 | 0 | 100% | 13108.5345 | 13108.5345
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 19957444.6085 | 0 | 1612517.2526 | 0 | 0 | 4% | 862798.4744 | 64500.6901
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 19957444.6085 | 8261.6388 | 1669510.8809 | 13108.5345 | 69874.1883 | 4.655% | 1011036.4644 | 212738.68
[5 empty] | 2 | Major |  | 19957444.6085 | 28915.7357 | 8184080.5814 | 4272242.3788 | 953161.44 | 16.09% | 5372431.8087 | 4574134.0243
[5 empty] | 3 | Catastrophic |  | 89028986.0297 | 28915.7357 | 42852381.7274 | 12816727.1363 | 2829163.7097 | 20% | 29511234.8677 | 11705437.6618
[5 empty] | Subtotal |  |  | 2025: 35894703.1408; 2026: 16492310.3661
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 97.1
|  |  | N-1 Rating before transfers, MVA |  |  | 65.2
|  |  | N-2 Rating before transfers, MVA |  |  | 32.2
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 53.1289 | 54.9287 | 54.8457 | 54.8478 | 55.5607 | 55.9261 | 58.2288 | 58.2288 | 58.2288 | 58.2288 | 58.2288 | 58.2288
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 48.9563 | 50.819 | 50.8253 | 50.924 | 51.2096 | 51.9435 | 53.0334 | 53.0334 | 53.0334 | 53.0334 | 53.0334 | 53.0334
|  |  | Weighting to 50% PoE |  |  | 70% |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 18.0081 | 19.8519 | 19.8314 | 19.9011 | 20.3149 | 20.9383 | 22.392 | 22.392 | 22.392 | 22.392 | 22.392 | 22.392
|  |  | N-3 |  |  |  |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
|  |  | N-4 |  |  |  |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 19957444.6085 | 22000837.1988 | 21978145.7663 | 22055413.0032 | 22514012.6728 | 23204879.5184 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275
|  |  | N-3 |  |  | Catastrophic |  | 89028986.0297 | 92298414.1741 | 92262107.8821 | 92385735.4611 | 93119494.9325 | 94224881.8854 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62
|  |  | N-4 |  |  | Catastrophic |  | 89028986.0297 | 92298414.1741 | 92262107.8821 | 92385735.4611 | 93119494.9325 | 94224881.8854 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 17.91% | 19.28% | 20.76% | 22.36% | 24.09% | 25.97% | 28% | 30.2% | 32.58% | 35.16% | 37.95% | 40.97%
|  |  | Major |  |  |  |  | 0.0963% | 0.1037% | 0.1116% | 0.1202% | 0.1295% | 0.1396% | 0.1505% | 0.1624% | 0.1752% | 0.189% | 0.204% | 0.2202%
|  |  | Catastrophic |  |  |  |  | 0.0963% | 0.1037% | 0.1116% | 0.1202% | 0.1295% | 0.1396% | 0.1505% | 0.1624% | 0.1752% | 0.189% | 0.204% | 0.2202%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 17147.8574 | 19135.2625 | 20595.8239 | 22213.9596 | 24125.2849 | 26311.7484 | 29144.7988 | 31432.9069 | 33910.7926 | 36594.6474 | 39502.068 | 42640.4813
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 142996.7968 | 169676.7482 | 182511.3116 | 197278.2429 | 216983.987 | 241049.5717 | 277938.1281 | 299758.573 | 323388.8243 | 348983.2905 | 376709.7832 | 406639.1274
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 768.8 | 912.2406 | 981.2436 | 1060.6357 | 1166.5806 | 1295.9654 | 1494.291 | 1611.6052 | 1738.6496 | 1876.2542 | 2025.3214 | 2186.2319
|  |  | Other significant risks |  |  | Significant |  | 38107.2707 | 41017.5385 | 44165.7089 | 47571.8965 | 51257.9517 | 55247.6125 | 59566.6698 | 64243.1466 | 69307.4945 | 74792.8057 | 80735.0449 | 87149.391
|  |  | Other major risks |  |  | Major |  | 4405.1158 | 4741.5362 | 5105.4578 | 5499.2055 | 5925.3053 | 6386.5012 | 6885.7746 | 7426.3649 | 8011.7923 | 8645.882 | 9332.7917 | 10074.2758
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 11272.9115 | 12133.8283 | 13065.1216 | 14072.7417 | 15163.1524 | 16343.3758 | 17621.0414 | 19004.4391 | 20502.577 | 22125.2444 | 23883.0805 | 25780.5756
|  |  | Annual opex, pre-replacement |  |  |  |  | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345 | 13108.5345
|  |  | Subtotal |  |  |  |  | 227807.2867 | 260725.6889 | 279533.2019 | 300805.2164 | 327730.7964 | 359743.3096 | 405759.2383 | 436585.5703 | 469968.6649 | 506126.6588 | 545296.6242 | 587578.6176
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 5585.3756
|  |  | Total annuity |  |  | 164821.6957
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 227807.2867 | 260725.6889 | 279533.2019 | 300805.2164 | 327730.7964 | 359743.3096 | 405759.2383 | 436585.5703 | 469968.6649 | 506126.6588 | 545296.6242 | 587578.6176
|  |  | Annualised cost |  |  |  |  | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - North Richmond Transformer No.2 Replacement Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 89028986.0297 | 0 | 0 | 0 | 0 | 20% | 17805797.2059 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 35014408.4447 | 0 | 0 | 20% | 7002881.6889 | 7002881.6889
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 19957444.6085 | 0 | 6649434.7798 | 0 | 0 | 4% | 1064275.1755 | 265977.3912
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 10725.1646 | 0 | 100% | 10725.1646 | 10725.1646
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 19957444.6085 | 0 | 1319332.2976 | 0 | 0 | 4% | 851071.0762 | 52773.2919
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 19957444.6085 | 8261.6388 | 1365963.448 | 10725.1646 | 69874.1883 | 4.607% | 986563.2184 | 188265.434
[5 empty] | 2 | Major |  | 19957444.6085 | 28915.7357 | 6696065.9302 | 3495471.0372 | 953161.44 | 15.04% | 4683618.6661 | 3885320.8818
[5 empty] | 3 | Catastrophic |  | 89028986.0297 | 28915.7357 | 35061039.5951 | 10486413.1115 | 2829163.7097 | 20% | 27486903.6363 | 9681106.4304
[5 empty] | Subtotal |  |  | 2025: 33157085.5209; 2026: 13754692.7462
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 97.1
|  |  | N-1 Rating before transfers, MVA |  |  | 65.2
|  |  | N-2 Rating before transfers, MVA |  |  | 32.2
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 53.1289 | 54.9287 | 54.8457 | 54.8478 | 55.5607 | 55.9261 | 58.2288 | 58.2288 | 58.2288 | 58.2288 | 58.2288 | 58.2288
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 48.9563 | 50.819 | 50.8253 | 50.924 | 51.2096 | 51.9435 | 53.0334 | 53.0334 | 53.0334 | 53.0334 | 53.0334 | 53.0334
|  |  | Weighting to 50% PoE |  |  | 70% |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 18.0081 | 19.8519 | 19.8314 | 19.9011 | 20.3149 | 20.9383 | 22.392 | 22.392 | 22.392 | 22.392 | 22.392 | 22.392
|  |  | N-3 |  |  |  |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
|  |  | N-4 |  |  |  |  | 50.2081 | 52.0519 | 52.0314 | 52.1011 | 52.5149 | 53.1383 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592 | 54.592
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 19957444.6085 | 22000837.1988 | 21978145.7663 | 22055413.0032 | 22514012.6728 | 23204879.5184 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275 | 24815971.2275
|  |  | N-3 |  |  | Catastrophic |  | 89028986.0297 | 92298414.1741 | 92262107.8821 | 92385735.4611 | 93119494.9325 | 94224881.8854 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62
|  |  | N-4 |  |  | Catastrophic |  | 89028986.0297 | 92298414.1741 | 92262107.8821 | 92385735.4611 | 93119494.9325 | 94224881.8854 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62 | 96802628.62
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 17.91% | 19.28% | 20.76% | 22.36% | 24.09% | 25.97% | 28% | 30.2% | 32.58% | 35.16% | 37.95% | 40.97%
|  |  | Major |  |  |  |  | 0.0963% | 0.1037% | 0.1116% | 0.1202% | 0.1295% | 0.1396% | 0.1505% | 0.1624% | 0.1752% | 0.189% | 0.204% | 0.2202%
|  |  | Catastrophic |  |  |  |  | 0.0963% | 0.1037% | 0.1116% | 0.1202% | 0.1295% | 0.1396% | 0.1505% | 0.1624% | 0.1752% | 0.189% | 0.204% | 0.2202%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 17147.8574 | 19135.2625 | 20595.8239 | 22213.9596 | 24125.2849 | 26311.7484 | 29144.7988 | 31432.9069 | 33910.7926 | 36594.6474 | 39502.068 | 42640.4813
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 142996.7968 | 169676.7482 | 182511.3116 | 197278.2429 | 216983.987 | 241049.5717 | 277938.1281 | 299758.573 | 323388.8243 | 348983.2905 | 376709.7832 | 406639.1274
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 768.8 | 912.2406 | 981.2436 | 1060.6357 | 1166.5806 | 1295.9654 | 1494.291 | 1611.6052 | 1738.6496 | 1876.2542 | 2025.3214 | 2186.2319
|  |  | Other significant risks |  |  | Significant |  | 33723.4482 | 36298.9217 | 39084.9297 | 42099.2729 | 45361.288 | 48891.9822 | 52714.1794 | 56852.679 | 61334.4294 | 66188.7158 | 71447.3657 | 77123.8118
|  |  | Other major risks |  |  | Major |  | 3741.7549 | 4027.5142 | 4336.6332 | 4671.087 | 5033.0209 | 5424.7659 | 5848.8544 | 6308.0379 | 6805.3065 | 7343.9094 | 7927.3782 | 8557.2032
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 9323.3811 | 10035.4115 | 10805.6475 | 11639.0104 | 12540.8461 | 13516.9624 | 14573.6693 | 15717.823 | 16956.8739 | 18298.9182 | 19752.7552 | 21322.0986
|  |  | Annual opex, pre-replacement |  |  |  |  | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646 | 10725.1646
|  |  | Subtotal |  |  |  |  | 218427.203 | 250811.2633 | 269040.7541 | 289687.373 | 315936.1721 | 347216.1607 | 392439.0856 | 422406.7897 | 454860.0408 | 490010.9001 | 528089.8363 | 569194.1189
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 4569.8527
|  |  | Total annuity |  |  | 134854.1147
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 218427.203 | 250811.2633 | 269040.7541 | 289687.373 | 315936.1721 | 347216.1607 | 392439.0856 | 422406.7897 | 454860.0408 | 490010.9001 | 528089.8363 | 569194.1189
|  |  | Annualised cost |  |  |  |  | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - North Richmond Transformer No.2 Replacement Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 171341.9327 | 198337.4029 | 212490.0264 | 228529.1157 | 248960.2408 | 273332.5044 | 308658.6657 | 331955.3558 | 357184.2934 | 384510.3333 | 414112.6403 | 446066.8311
|  |  | Annualised cost | Scenario Base case | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052 | 149837.9052
|  |  | Risk cost | Scenario A | 134835.1172 | 154086.8021 | 164788.1022 | 176922.669 | 192407.7259 | 212889.1017 | 239964.7948 | 257774.89 | 277062.1698 | 297952.6641 | 320583.3427 | 345012.0138
|  |  | Annualised cost | Scenario A | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957
|  |  | Risk cost | Scenario B | 126727.1633 | 145541.6593 | 155770.0323 | 167392.9117 | 182324.2387 | 202206.2762 | 228633.1481 | 245740.7295 | 264267.2283 | 284333.7034 | 306071.7217 | 329536.8112
|  |  | Annualised cost | Scenario B | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147
|  |  | Risk cost | Scenario C | 227807.2867 | 260725.6889 | 279533.2019 | 300805.2164 | 327730.7964 | 359743.3096 | 405759.2383 | 436585.5703 | 469968.6649 | 506126.6588 | 545296.6242 | 587578.6176
|  |  | Annualised cost | Scenario C | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957 | 164821.6957
|  |  | Risk cost | Scenario D | 218427.203 | 250811.2633 | 269040.7541 | 289687.373 | 315936.1721 | 347216.1607 | 392439.0856 | 422406.7897 | 454860.0408 | 490010.9001 | 528089.8363 | 569194.1189
|  |  | Annualised cost | Scenario D | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147 | 134854.1147
Charts
End