## Inputs
CitiPower - Celestial Avenue Transformer No. 1 Replacement Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | Celestial Avenue Transformer No. 1 Replacement Risk Monetisation Model
|  | Model start & timeline |  | 2019 | FY19/20
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 50
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex regulator, real $2019 |  | 3748000 |  |  |  |  | 0 | 50000 | 750000 | 2948000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 3883856.708 |  |  |  |  | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 10300 | 3400
|  |  | Opex ($2021) | 10673.3522 | 3523.2425
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 10.56% | 11.35% | 12.21% | 13.14% | 14.14% | 15.23% | 16.41% | 17.69% | 19.07% | 20.57% | 22.2% | 23.95%
|  |  | Major | 2 |  |  |  |  | 0.05675% | 0.06102% | 0.06564% | 0.07064% | 0.07605% | 0.0819% | 0.08824% | 0.09511% | 0.1026% | 0.1106% | 0.1194% | 0.1288%
|  |  | Catastrophic | 3 |  |  |  |  | 0.05675% | 0.06102% | 0.06564% | 0.07064% | 0.07605% | 0.0819% | 0.08824% | 0.09511% | 0.1026% | 0.1106% | 0.1194% | 0.1288%
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 13791 | 26450 | 20% | 497.5245
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 139552 | 47770 | 40% | 18185.0433
|  |  | Industrial | 1764 | 47070 | 80% | 452.9975
|  |  | Total | 155107 | 45866.4178 | 39.44% | 19135.5653
Asset information
|  | Assets at risk |  | 3
|  | N-rating, MVA |  | 67.1
|  |  | N-1 Rating before transfers, MVA | 67.1
|  |  | N-2 Rating before transfers, MVA | 35.4
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major | Catastrophic
|  |  | Average Consequence Loss Oil | 500 | 4050 | 12150
|  |  | Average Consequences Loss SF6 kgs | 0 | 0 | 0
|  |  | Average Consequence Fire | 0.05 | 2.5 | 5
|  |  | Average Consequence Waste | 10 | 405 | 1215
|  |  | Average Consequence Disturbance | 2 | 3 | 5
|  |  | Average Cost of Fault (Air Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (SF6 Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (Oil Insulated) | 63521.9894 | 866510.4 | 2571967.0088
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Switching time only (hours required) | 0 | 0 | 0 | 0
|  |  | Number of weeks generation required | 1.1905 | 6 | 6 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 0 | 14.9466 | 50.3466
|  |  | Number of generators | 0 | 0 | 15 | 51
|  |  | Generator sites | 0 | 0 | 4 | 13
|  |  | Number of days to connect all generators | 0 | 0 | 2 | 5
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Generator hire | 0 | 0 | 689104.7788 | 4593427.3805
|  |  | Fuel cost | 0 | 0 | 2493873.745 | 16800863.3419
|  |  | Fitter cost | 0 | 0 | 676462.5558 | 4235351.9575
|  |  | Traffic management cost | 0 | 0 | 1740896.2832 | 11315825.8407
|  |  | Transformer hire | 0 | 0 | 183761.2743 | 1170873.646
|  |  | Earthing and bunding | 0 | 0 | 8289.9823 | 26942.4425
|  |  | Temporary fencing | 0 | 0 | 74609.8407 | 484963.9646
|  |  | Miscellaneous materials | 0 | 0 | 8289.9823 | 26942.4425
|  |  | Installation & removal of step-down transformers | 0 | 0 | 10362.4779 | 33678.0531
|  |  | Council permits | 0 | 0 | 16579.9646 | 53884.885
|  |  | Crane hire | 0 | 0 | 10362.4779 | 33678.0531
|  |  | Cable hire | 0 | 0 | 12434.9735 | 40413.6637
|  |  | Total | 0 | 0 | 5925028.3362 | 38816845.6711
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major | Catastrophic
|  |  | Minor | 1.172% | 4.103% | 4.103%
|  |  | Serious | 0.2345% | 0.8206% | 0.8206%
|  |  | Fataility | 0.02345% | 0.08206% | 0.08206%
|  |  | Value of event | 8261.6388 | 28915.7357 | 28915.7357
|  |  | Weighted likelyhood of consequence | 0.05217% | 0.1826% | 0.1826%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 58.829 | 58.016 | 47.6505 | 48.8986 | 48.3559 | 48.8852 | 54.1573 | 54.1573 | 54.1573 | 54.1573 | 54.1573 | 54.1573
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 54.281 | 53.331 | 44.8325 | 45.875 | 45.4209 | 45.3691 | 50.2641 | 50.2641 | 50.2641 | 50.2641 | 50.2641 | 50.2641
|  |  | Weighting to 50% PoE | 70% |  |  |  |  | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 20.2454 | 19.3365 | 10.2779 | 11.3821 | 10.9014 | 11.0239 | 16.032 | 16.032 | 16.032 | 16.032 | 16.032 | 16.032
|  |  | N-3 | [5 empty] | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
|  |  | N-4 | [5 empty] | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
End

## Base Case
CitiPower - Celestial Avenue Transformer No. 1 Replacement Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 102221393.5861 | 0 | 0 | 0 | 0 | 20% | 20444278.7172 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 38816845.6711 | 0 | 0 | 20% | 7763369.1342 | 7763369.1342
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 11651570.1239 | 0 | 20% | 2330314.0248 | 2330314.0248
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2571967.0088 | 20% | 514393.4018 | 514393.4018
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 20% | 10362.4779 | 10362.4779
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3883856.708 | 0 | 80% | 3107085.3664 | 3107085.3664
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 866510.4 | 80% | 693208.32 | 693208.32
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 80% | 41449.9115 | 41449.9115
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 23244430.3764 | 0 | 5925028.3362 | 0 | 0 | 4% | 1166778.3485 | 237001.1334
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 10673.3522 | 0 | 100% | 10673.3522 | 10673.3522
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 63521.9894 | 100% | 63521.9894 | 63521.9894
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 23244430.3764 | 0 | 1175600.8604 | 0 | 0 | 4% | 976801.2495 | 47024.0344
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 23244430.3764 | 8261.6388 | 1227413.2497 | 10673.3522 | 63521.9894 | 4.525% | 1111070.6192 | 181293.4041
[5 empty] | 2 | Major |  | 23244430.3764 | 28915.7357 | 5976840.7256 | 3883856.708 | 866510.4 | 14.8% | 5031654.5349 | 4101877.3199
[5 empty] | 3 | Catastrophic |  | 102221393.5861 | 28915.7357 | 38868658.0605 | 11651570.1239 | 2571967.0088 | 20% | 31068500.903 | 10624222.1858
[5 empty] | Subtotal |  |  | 2025: 37211226.0571; 2026: 14907392.9098
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 67.1
|  |  | N-1 Rating before transfers, MVA |  |  | 67.1
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 58.829 | 58.016 | 47.6505 | 48.8986 | 48.3559 | 48.8852 | 54.1573 | 54.1573 | 54.1573 | 54.1573 | 54.1573 | 54.1573
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 54.281 | 53.331 | 44.8325 | 45.875 | 45.4209 | 45.3691 | 50.2641 | 50.2641 | 50.2641 | 50.2641 | 50.2641 | 50.2641
|  |  | Weighting to 50% PoE |  |  | 70% |  | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 20.2454 | 19.3365 | 10.2779 | 11.3821 | 10.9014 | 11.0239 | 16.032 | 16.032 | 16.032 | 16.032 | 16.032 | 16.032
|  |  | N-3 |  |  |  |  | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
|  |  | N-4 |  |  |  |  | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 23244430.3764 | 22200891.4605 | 9440313.7176 | 10454555.3234 | 10013028.6933 | 10125560.326 | 18406939.5197 | 18406939.5197 | 18406939.5197 | 18406939.5197 | 18406939.5197 | 18406939.5197
|  |  | N-3 |  |  | Catastrophic |  | 102221393.5861 | 100551731.3206 | 73422065.8667 | 75196988.6769 | 74424317.0742 | 74621247.4314 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153
|  |  | N-4 |  |  | Catastrophic |  | 102221393.5861 | 100551731.3206 | 73422065.8667 | 75196988.6769 | 74424317.0742 | 74621247.4314 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 10.56% | 11.35% | 12.21% | 13.14% | 14.14% | 15.23% | 16.41% | 17.69% | 19.07% | 20.57% | 22.2% | 23.95%
|  |  | Major |  |  |  |  | 0.05675% | 0.06102% | 0.06564% | 0.07064% | 0.07605% | 0.0819% | 0.08824% | 0.09511% | 0.1026% | 0.1106% | 0.1194% | 0.1288%
|  |  | Catastrophic |  |  |  |  | 0.05675% | 0.06102% | 0.06564% | 0.07064% | 0.07605% | 0.0819% | 0.08824% | 0.09511% | 0.1026% | 0.1106% | 0.1194% | 0.1288%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 11602.4354 | 12271.4734 | 9638.7544 | 10623.419 | 11319.4616 | 12223.4325 | 16674.9596 | 17972.8079 | 19378.7576 | 20902.1208 | 22553.0281 | 24334.3288
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 98145.2328 | 100790.7119 | 46102.4156 | 54942.9996 | 56652.5305 | 61701.0676 | 120848.9716 | 130254.9092 | 140444.2937 | 151484.6124 | 163449.2866 | 176358.9638
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 527.6625 | 541.8855 | 247.8624 | 295.3925 | 304.5835 | 331.7262 | 649.7257 | 700.2952 | 755.0768 | 814.4334 | 878.7596 | 948.1665
|  |  | Other significant risks |  |  | Significant |  | 19136.932 | 20576.5288 | 22133.9675 | 23819.2901 | 25643.4153 | 27618.2162 | 29756.6054 | 32072.6266 | 34581.5556 | 37300.0099 | 40246.068 | 43424.8139
|  |  | Other major risks |  |  | Major |  | 2327.877 | 2502.9941 | 2692.4459 | 2897.4539 | 3119.3462 | 3359.5673 | 3619.6877 | 3901.4159 | 4206.6099 | 4537.2913 | 4895.6592 | 5282.3319
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 6029.4057 | 6482.9744 | 6973.6711 | 7504.6598 | 8079.3805 | 8701.5741 | 9375.3088 | 10105.0095 | 10895.4889 | 11751.9827 | 12680.1868 | 13681.7031
|  |  | Annual opex, pre-replacement |  |  |  |  | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522
|  |  | Subtotal |  |  |  |  | 148442.8977 | 153839.9204 | 98462.4692 | 110756.567 | 115792.0698 | 124608.9361 | 191598.611 | 205680.4165 | 220935.1348 | 237463.8028 | 255376.3406 | 274703.6602
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 144760.291
|  |  | Post-replacement opex |  |  | 3523.2425
|  |  | Total annuity |  |  | 148283.5335
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 148442.8977 | 153839.9204 | 98462.4692 | 110756.567 | 115792.0698 | 124608.9361 | 191598.611 | 205680.4165 | 220935.1348 | 237463.8028 | 255376.3406 | 274703.6602
|  |  | Annualised cost |  |  |  |  | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - Celestial Avenue Transformer No. 1 Replacement Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 87399291.5161 | 0 | 0 | 0 | 0 | 20% | 17479858.3032 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 42698530.2382 | 0 | 0 | 20% | 8539706.0476 | 8539706.0476
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 18045010.6442 | 0 | 6517531.1698 | 0 | 0 | 4% | 982501.6726 | 260701.2468
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 11740.6874 | 0 | 100% | 11740.6874 | 11740.6874
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 18045010.6442 | 0 | 1293160.9464 | 0 | 0 | 4% | 773526.8636 | 51726.4379
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 18045010.6442 | 8261.6388 | 1350154.5747 | 11740.6874 | 57169.7904 | 4.661% | 907692.6086 | 185892.1828
[5 empty] | 2 | Major |  | 18045010.6442 | 28915.7357 | 6574524.7981 | 4272242.3788 | 779859.36 | 17.15% | 5092910.5548 | 4371110.129
[5 empty] | 3 | Catastrophic |  | 87399291.5161 | 28915.7357 | 42755523.8665 | 12816727.1363 | 2314770.308 | 20% | 29063045.7125 | 11583187.4093
[5 empty] | Subtotal |  |  | 2025: 35063648.8758; 2026: 16140189.7211
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 67.1
|  |  | N-1 Rating before transfers, MVA |  |  | 67.1
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 55.8875 | 55.1152 | 45.268 | 46.4537 | 45.9381 | 46.4409 | 51.4494 | 51.4494 | 51.4494 | 51.4494 | 51.4494 | 51.4494
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 51.5669 | 50.6645 | 42.5909 | 43.5813 | 43.1499 | 43.1007 | 47.7509 | 47.7509 | 47.7509 | 47.7509 | 47.7509 | 47.7509
|  |  | Weighting to 50% PoE |  |  | 70% |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 17.4631 | 16.5997 | 7.994 | 9.043 | 8.5863 | 8.7027 | 13.4604 | 13.4604 | 13.4604 | 13.4604 | 13.4604 | 13.4604
|  |  | N-3 |  |  |  |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
|  |  | N-4 |  |  |  |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 18045010.6442 | 17152784.871 | 6608286.3664 | 7475462.9394 | 7097957.6707 | 7194172.2166 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617
|  |  | N-3 |  |  | Catastrophic |  | 87399291.5161 | 85971730.2791 | 62775866.3161 | 64293425.3188 | 63632791.0985 | 63801166.5538 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241
|  |  | N-4 |  |  | Catastrophic |  | 87399291.5161 | 85971730.2791 | 62775866.3161 | 64293425.3188 | 63632791.0985 | 63801166.5538 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 9.5% | 10.21% | 10.99% | 11.82% | 12.73% | 13.71% | 14.77% | 15.92% | 17.17% | 18.52% | 19.98% | 21.56%
|  |  | Major |  |  |  |  | 0.05108% | 0.05492% | 0.05908% | 0.06357% | 0.06844% | 0.07371% | 0.07942% | 0.0856% | 0.0923% | 0.09955% | 0.1074% | 0.1159%
|  |  | Catastrophic |  |  |  |  | 0.05108% | 0.05492% | 0.05908% | 0.06357% | 0.06844% | 0.07371% | 0.07942% | 0.0856% | 0.0923% | 0.09955% | 0.1074% | 0.1159%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 8928.074 | 9442.8988 | 7417.0215 | 8174.7209 | 8710.3257 | 9405.9313 | 12831.3814 | 13830.0757 | 14911.954 | 16084.1819 | 17354.5552 | 18725.266
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 68572.4953 | 70085.3505 | 29044.8153 | 35357.9765 | 36143.4635 | 39454.5371 | 82186.1081 | 88582.8312 | 95512.3552 | 103020.5766 | 111157.427 | 119936.9484
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 368.6693 | 376.803 | 156.1549 | 190.0966 | 194.3197 | 212.1212 | 441.8608 | 476.2518 | 513.5073 | 553.8741 | 597.6206 | 644.8223
|  |  | Other significant risks |  |  | Significant |  | 17660.1321 | 18988.6349 | 20425.8858 | 21981.1518 | 23664.509 | 25486.9143 | 27460.2836 | 29597.5771 | 31912.8917 | 34421.5625 | 37140.2728 | 40073.7144
|  |  | Other major risks |  |  | Major |  | 2232.6036 | 2400.5537 | 2582.2517 | 2778.8693 | 2991.6803 | 3222.0697 | 3471.5442 | 3741.742 | 4034.4453 | 4351.5929 | 4695.2937 | 5066.141
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 5916.2696 | 6361.3275 | 6842.8168 | 7363.8419 | 7927.7785 | 8538.2973 | 9199.39 | 9915.3985 | 10691.0453 | 11531.4678 | 12442.2551 | 13424.9788
|  |  | Annual opex, pre-replacement |  |  |  |  | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874
|  |  | Subtotal |  |  |  |  | 115418.9314 | 119396.2558 | 78209.6335 | 87587.3445 | 91372.7641 | 98060.5583 | 147331.2556 | 157884.5637 | 169316.8862 | 181703.9432 | 195128.1118 | 209612.5584
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 3875.5667
|  |  | Total annuity |  |  | 163111.8869
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 115418.9314 | 119396.2558 | 78209.6335 | 87587.3445 | 91372.7641 | 98060.5583 | 147331.2556 | 157884.5637 | 169316.8862 | 181703.9432 | 195128.1118 | 209612.5584
|  |  | Annualised cost |  |  |  |  | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
CitiPower - Celestial Avenue Transformer No. 1 Replacement Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 87399291.5161 | 0 | 0 | 0 | 0 | 20% | 17479858.3032 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 34935161.104 | 0 | 0 | 20% | 6987032.2208 | 6987032.2208
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 18045010.6442 | 0 | 5332525.5026 | 0 | 0 | 4% | 935101.4459 | 213301.0201
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 9606.017 | 0 | 100% | 9606.017 | 9606.017
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 18045010.6442 | 0 | 1058040.7743 | 0 | 0 | 4% | 764122.0567 | 42321.631
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 18045010.6442 | 8261.6388 | 1104671.9248 | 9606.017 | 57169.7904 | 4.608% | 885790.6534 | 163990.2276
[5 empty] | 2 | Major |  | 18045010.6442 | 28915.7357 | 5379156.653 | 3495471.0372 | 779859.36 | 15.93% | 4415803.2725 | 3694002.8467
[5 empty] | 3 | Catastrophic |  | 87399291.5161 | 28915.7357 | 34981792.2544 | 10486413.1115 | 2314770.308 | 20% | 27042236.5851 | 9562378.2819
[5 empty] | Subtotal |  |  | 2025: 32343830.511; 2026: 13420371.3562
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 67.1
|  |  | N-1 Rating before transfers, MVA |  |  | 67.1
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 55.8875 | 55.1152 | 45.268 | 46.4537 | 45.9381 | 46.4409 | 51.4494 | 51.4494 | 51.4494 | 51.4494 | 51.4494 | 51.4494
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 51.5669 | 50.6645 | 42.5909 | 43.5813 | 43.1499 | 43.1007 | 47.7509 | 47.7509 | 47.7509 | 47.7509 | 47.7509 | 47.7509
|  |  | Weighting to 50% PoE |  |  | 70% |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 17.4631 | 16.5997 | 7.994 | 9.043 | 8.5863 | 8.7027 | 13.4604 | 13.4604 | 13.4604 | 13.4604 | 13.4604 | 13.4604
|  |  | N-3 |  |  |  |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
|  |  | N-4 |  |  |  |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 18045010.6442 | 17152784.871 | 6608286.3664 | 7475462.9394 | 7097957.6707 | 7194172.2166 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617
|  |  | N-3 |  |  | Catastrophic |  | 87399291.5161 | 85971730.2791 | 62775866.3161 | 64293425.3188 | 63632791.0985 | 63801166.5538 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241
|  |  | N-4 |  |  | Catastrophic |  | 87399291.5161 | 85971730.2791 | 62775866.3161 | 64293425.3188 | 63632791.0985 | 63801166.5538 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 9.5% | 10.21% | 10.99% | 11.82% | 12.73% | 13.71% | 14.77% | 15.92% | 17.17% | 18.52% | 19.98% | 21.56%
|  |  | Major |  |  |  |  | 0.05108% | 0.05492% | 0.05908% | 0.06357% | 0.06844% | 0.07371% | 0.07942% | 0.0856% | 0.0923% | 0.09955% | 0.1074% | 0.1159%
|  |  | Catastrophic |  |  |  |  | 0.05108% | 0.05492% | 0.05908% | 0.06357% | 0.06844% | 0.07371% | 0.07942% | 0.0856% | 0.0923% | 0.09955% | 0.1074% | 0.1159%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 8928.074 | 9442.8988 | 7417.0215 | 8174.7209 | 8710.3257 | 9405.9313 | 12831.3814 | 13830.0757 | 14911.954 | 16084.1819 | 17354.5552 | 18725.266
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 68572.4953 | 70085.3505 | 29044.8153 | 35357.9765 | 36143.4635 | 39454.5371 | 82186.1081 | 88582.8312 | 95512.3552 | 103020.5766 | 111157.427 | 119936.9484
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 368.6693 | 376.803 | 156.1549 | 190.0966 | 194.3197 | 212.1212 | 441.8608 | 476.2518 | 513.5073 | 553.8741 | 597.6206 | 644.8223
|  |  | Other significant risks |  |  | Significant |  | 15579.4022 | 16751.3798 | 18019.2928 | 19391.3162 | 20876.3389 | 22484.0271 | 24224.8926 | 26110.3686 | 28152.8911 | 30365.9884 | 32764.3782 | 35352.1996
|  |  | Other major risks |  |  | Major |  | 1886.7619 | 2028.6957 | 2182.2477 | 2348.4083 | 2528.2537 | 2722.9547 | 2933.7843 | 3162.127 | 3409.4891 | 3677.5089 | 3967.9688 | 4281.3699
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 4884.114 | 5251.5269 | 5649.0153 | 6079.1421 | 6544.694 | 7048.7013 | 7594.4594 | 8185.5527 | 8825.8798 | 9519.6817 | 10271.5726 | 11082.8498
|  |  | Annual opex, pre-replacement |  |  |  |  | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017
|  |  | Subtotal |  |  |  |  | 109825.5338 | 113542.6716 | 72074.5645 | 81147.6775 | 84603.4126 | 90934.2897 | 139818.5036 | 149953.224 | 160932.0935 | 172827.8286 | 185719.5393 | 199629.4729
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 3170.9182
|  |  | Total annuity |  |  | 133455.1802
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 109825.5338 | 113542.6716 | 72074.5645 | 81147.6775 | 84603.4126 | 90934.2897 | 139818.5036 | 149953.224 | 160932.0935 | 172827.8286 | 185719.5393 | 199629.4729
|  |  | Annualised cost |  |  |  |  | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - Celestial Avenue Transformer No. 1 Replacement Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 118065709.592 | 0 | 0 | 0 | 0 | 20% | 23613141.9184 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 42698530.2382 | 0 | 0 | 20% | 8539706.0476 | 8539706.0476
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 29082733.8186 | 0 | 6517531.1698 | 0 | 0 | 4% | 1424010.5995 | 260701.2468
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 11740.6874 | 0 | 100% | 11740.6874 | 11740.6874
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 29082733.8186 | 0 | 1293160.9464 | 0 | 0 | 4% | 1215035.7906 | 51726.4379
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 29082733.8186 | 8261.6388 | 1350154.5747 | 11740.6874 | 69874.1883 | 4.462% | 1361905.9334 | 198596.5807
[5 empty] | 2 | Major |  | 29082733.8186 | 28915.7357 | 6574524.7981 | 4272242.3788 | 953161.44 | 13.87% | 5673061.1457 | 4509751.793
[5 empty] | 3 | Catastrophic |  | 118065709.592 | 28915.7357 | 42755523.8665 | 12816727.1363 | 2829163.7097 | 20% | 35299208.008 | 11686066.0896
[5 empty] | Subtotal |  |  | 2025: 42334175.0872; 2026: 16394414.4633
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 67.1
|  |  | N-1 Rating before transfers, MVA |  |  | 67.1
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 61.7705 | 60.9168 | 50.033 | 51.3436 | 50.7737 | 51.3294 | 56.8651 | 56.8651 | 56.8651 | 56.8651 | 56.8651 | 56.8651
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 56.995 | 55.9976 | 47.0741 | 48.1688 | 47.692 | 47.6376 | 52.7773 | 52.7773 | 52.7773 | 52.7773 | 52.7773 | 52.7773
|  |  | Weighting to 50% PoE |  |  | 70% |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 23.0277 | 22.0733 | 12.5618 | 13.7212 | 13.2165 | 13.3451 | 18.6037 | 18.6037 | 18.6037 | 18.6037 | 18.6037 | 18.6037
|  |  | N-3 |  |  |  |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
|  |  | N-4 |  |  |  |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 29082733.8186 | 27877446.3706 | 15864869.6637 | 17329180.982 | 16691726.9098 | 16854194.4545 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791
|  |  | N-3 |  |  | Catastrophic |  | 118065709.592 | 116137249.6753 | 84802486.0761 | 99260025.0535 | 98240098.538 | 98500046.6094 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887
|  |  | N-4 |  |  | Catastrophic |  | 118065709.592 | 116137249.6753 | 84802486.0761 | 99260025.0535 | 98240098.538 | 98500046.6094 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 11.61% | 12.48% | 13.43% | 14.45% | 15.56% | 16.76% | 18.05% | 19.46% | 20.98% | 22.63% | 24.42% | 26.35%
|  |  | Major |  |  |  |  | 0.06243% | 0.06712% | 0.0722% | 0.0777% | 0.08365% | 0.09009% | 0.09707% | 0.1046% | 0.1128% | 0.1217% | 0.1313% | 0.1417%
|  |  | Catastrophic |  |  |  |  | 0.06243% | 0.06712% | 0.0722% | 0.0777% | 0.08365% | 0.09009% | 0.09707% | 0.1046% | 0.1128% | 0.1217% | 0.1313% | 0.1417%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 14740.8942 | 15590.907 | 12246.0375 | 15425.2044 | 16435.8583 | 17748.424 | 21185.5362 | 22834.4525 | 24620.7115 | 26556.1444 | 28653.6223 | 30916.7647
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 135076.0074 | 139218.1227 | 85224.8898 | 100179.1917 | 103883.7955 | 112972.9056 | 169682.6707 | 182889.4411 | 197196.2403 | 212697.8267 | 229497.29 | 247623.6214
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 726.2151 | 748.4845 | 458.1983 | 538.5978 | 558.515 | 607.3812 | 912.2724 | 983.2766 | 1060.1948 | 1143.5367 | 1233.8564 | 1331.3098
|  |  | Other significant risks |  |  | Significant |  | 23059.7589 | 24794.4546 | 26671.1484 | 28701.9406 | 30899.9882 | 33279.5982 | 35856.3298 | 38647.1058 | 41670.3332 | 44946.036 | 48495.9984 | 52326.3466
|  |  | Other major risks |  |  | Major |  | 2815.2871 | 3027.0702 | 3256.1893 | 3504.1218 | 3772.4739 | 4062.9923 | 4377.5767 | 4718.293 | 5087.3885 | 5487.3078 | 5920.7106 | 6388.3447
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 7295.2199 | 7844.0109 | 8437.7245 | 9080.189 | 9775.5666 | 10528.3836 | 11343.5623 | 12226.4564 | 13182.8892 | 14219.1954 | 15342.2668 | 16554.0416
|  |  | Annual opex, pre-replacement |  |  |  |  | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874
|  |  | Subtotal |  |  |  |  | 195454.07 | 202963.7374 | 148034.8752 | 169169.9326 | 177066.8849 | 190940.3723 | 255098.6356 | 274039.7127 | 294558.445 | 316790.7345 | 340884.4319 | 366881.1163
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 3875.5667
|  |  | Total annuity |  |  | 163111.8869
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 195454.07 | 202963.7374 | 148034.8752 | 169169.9326 | 177066.8849 | 190940.3723 | 255098.6356 | 274039.7127 | 294558.445 | 316790.7345 | 340884.4319 | 366881.1163
|  |  | Annualised cost |  |  |  |  | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - Celestial Avenue Transformer No. 1 Replacement Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 118065709.592 | 0 | 0 | 0 | 0 | 20% | 23613141.9184 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 34935161.104 | 0 | 0 | 20% | 6987032.2208 | 6987032.2208
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 29082733.8186 | 0 | 5332525.5026 | 0 | 0 | 4% | 1376610.3728 | 213301.0201
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 9606.017 | 0 | 100% | 9606.017 | 9606.017
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 29082733.8186 | 0 | 1058040.7743 | 0 | 0 | 4% | 1205630.9837 | 42321.631
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 29082733.8186 | 8261.6388 | 1104671.9248 | 9606.017 | 69874.1883 | 4.426% | 1340003.9782 | 176694.6255
[5 empty] | 2 | Major |  | 29082733.8186 | 28915.7357 | 5379156.653 | 3495471.0372 | 953161.44 | 12.83% | 4995953.8635 | 3832644.5107
[5 empty] | 3 | Catastrophic |  | 118065709.592 | 28915.7357 | 34981792.2544 | 10486413.1115 | 2829163.7097 | 20% | 33278398.8807 | 9665256.9623
[5 empty] | Subtotal |  |  | 2025: 39614356.7223; 2026: 13674596.0985
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 67.1
|  |  | N-1 Rating before transfers, MVA |  |  | 67.1
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 61.7705 | 60.9168 | 50.033 | 51.3436 | 50.7737 | 51.3294 | 56.8651 | 56.8651 | 56.8651 | 56.8651 | 56.8651 | 56.8651
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 56.995 | 55.9976 | 47.0741 | 48.1688 | 47.692 | 47.6376 | 52.7773 | 52.7773 | 52.7773 | 52.7773 | 52.7773 | 52.7773
|  |  | Weighting to 50% PoE |  |  | 70% |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 23.0277 | 22.0733 | 12.5618 | 13.7212 | 13.2165 | 13.3451 | 18.6037 | 18.6037 | 18.6037 | 18.6037 | 18.6037 | 18.6037
|  |  | N-3 |  |  |  |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
|  |  | N-4 |  |  |  |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 29082733.8186 | 27877446.3706 | 15864869.6637 | 17329180.982 | 16691726.9098 | 16854194.4545 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791
|  |  | N-3 |  |  | Catastrophic |  | 118065709.592 | 116137249.6753 | 84802486.0761 | 99260025.0535 | 98240098.538 | 98500046.6094 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887
|  |  | N-4 |  |  | Catastrophic |  | 118065709.592 | 116137249.6753 | 84802486.0761 | 99260025.0535 | 98240098.538 | 98500046.6094 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 11.61% | 12.48% | 13.43% | 14.45% | 15.56% | 16.76% | 18.05% | 19.46% | 20.98% | 22.63% | 24.42% | 26.35%
|  |  | Major |  |  |  |  | 0.06243% | 0.06712% | 0.0722% | 0.0777% | 0.08365% | 0.09009% | 0.09707% | 0.1046% | 0.1128% | 0.1217% | 0.1313% | 0.1417%
|  |  | Catastrophic |  |  |  |  | 0.06243% | 0.06712% | 0.0722% | 0.0777% | 0.08365% | 0.09009% | 0.09707% | 0.1046% | 0.1128% | 0.1217% | 0.1313% | 0.1417%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 14740.8942 | 15590.907 | 12246.0375 | 15425.2044 | 16435.8583 | 17748.424 | 21185.5362 | 22834.4525 | 24620.7115 | 26556.1444 | 28653.6223 | 30916.7647
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 135076.0074 | 139218.1227 | 85224.8898 | 100179.1917 | 103883.7955 | 112972.9056 | 169682.6707 | 182889.4411 | 197196.2403 | 212697.8267 | 229497.29 | 247623.6214
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 726.2151 | 748.4845 | 458.1983 | 538.5978 | 558.515 | 607.3812 | 912.2724 | 983.2766 | 1060.1948 | 1143.5367 | 1233.8564 | 1331.3098
|  |  | Other significant risks |  |  | Significant |  | 20516.6446 | 22060.0317 | 23729.7569 | 25536.5859 | 27492.2248 | 29609.4027 | 31901.963 | 34384.962 | 37074.7769 | 39989.2232 | 43147.6828 | 46555.6063
|  |  | Other major risks |  |  | Major |  | 2392.5917 | 2572.577 | 2767.2955 | 2978.0027 | 3206.0637 | 3452.9628 | 3720.3146 | 4009.8747 | 4323.5531 | 4663.4274 | 5031.7578 | 5429.18
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 6033.6964 | 6487.5879 | 6978.6338 | 7510.0003 | 8085.13 | 8707.7664 | 9381.9805 | 10112.2004 | 10903.2424 | 11760.3457 | 12689.2104 | 13691.4394
|  |  | Annual opex, pre-replacement |  |  |  |  | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017
|  |  | Subtotal |  |  |  |  | 189092.0663 | 196283.7279 | 141010.8288 | 161773.5997 | 169267.6042 | 182704.8597 | 246390.7544 | 264820.2243 | 284784.7361 | 306416.5212 | 329859.4367 | 355153.9386
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 3170.9182
|  |  | Total annuity |  |  | 133455.1802
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 189092.0663 | 196283.7279 | 141010.8288 | 161773.5997 | 169267.6042 | 182704.8597 | 246390.7544 | 264820.2243 | 284784.7361 | 306416.5212 | 329859.4367 | 355153.9386
|  |  | Annualised cost |  |  |  |  | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - Celestial Avenue Transformer No. 1 Replacement Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 148442.8977 | 153839.9204 | 98462.4692 | 110756.567 | 115792.0698 | 124608.9361 | 191598.611 | 205680.4165 | 220935.1348 | 237463.8028 | 255376.3406 | 274703.6602
|  |  | Annualised cost | Scenario Base case | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335
|  |  | Risk cost | Scenario A | 115418.9314 | 119396.2558 | 78209.6335 | 87587.3445 | 91372.7641 | 98060.5583 | 147331.2556 | 157884.5637 | 169316.8862 | 181703.9432 | 195128.1118 | 209612.5584
|  |  | Annualised cost | Scenario A | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869
|  |  | Risk cost | Scenario B | 109825.5338 | 113542.6716 | 72074.5645 | 81147.6775 | 84603.4126 | 90934.2897 | 139818.5036 | 149953.224 | 160932.0935 | 172827.8286 | 185719.5393 | 199629.4729
|  |  | Annualised cost | Scenario B | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802
|  |  | Risk cost | Scenario C | 195454.07 | 202963.7374 | 148034.8752 | 169169.9326 | 177066.8849 | 190940.3723 | 255098.6356 | 274039.7127 | 294558.445 | 316790.7345 | 340884.4319 | 366881.1163
|  |  | Annualised cost | Scenario C | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869
|  |  | Risk cost | Scenario D | 189092.0663 | 196283.7279 | 141010.8288 | 161773.5997 | 169267.6042 | 182704.8597 | 246390.7544 | 264820.2243 | 284784.7361 | 306416.5212 | 329859.4367 | 355153.9386
|  |  | Annualised cost | Scenario D | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802
Charts
End