## Inputs
CitiPower - B Switchboard Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | B Switchboard Risk Monetisation Model
|  | Model start & timeline |  | 2019
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 50
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex regulator, real $2019 |  | 8144815.1422 |  |  |  |  | 0 | 0 | 75000 | 2199100 | 5870715.1422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 8440046.6716 |  |  |  |  | 0 | 0 | 77718.5841 | 2278812.5097 | 6083515.5778 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 45400 | 20100
|  |  | Opex ($2021) | 47045.6496 | 20828.5805
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 4.969% | 5.33% | 5.721% | 6.144% | 6.601% | 7.097% | 7.634% | 8.215% | 8.845% | 9.528% | 10.27% | 11.07%
|  |  | Major | 2 |  |  |  |  | 0.5521% | 0.5922% | 0.6357% | 0.6826% | 0.7335% | 0.7885% | 0.8482% | 0.9128% | 0.9828% | 1.059% | 1.141% | 1.23%
|  |  | Catastrophic | 3 | bar: 2010 to 2021
Value of customer reliability (VCR)
|  | Sector |  | MWh | Weighted VCR $/MWh ($2018) | Load Duration | Load Duration Adjusted VCR $/MWh ($2021)
|  |  | Residential | 15960 | 26450 | 20% | 609.4591
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 89537 | 47770 | 40% | 12350.1947
|  |  | Industrial | 41037 | 47070 | 80% | 11154.9037
|  |  | Total | 146534 | 45251.8602 | 50.38% | 24114.5575
Asset information
|  | Assets at risk |  | 1 |  |  | Sections lost
|  | N-rating, MVA |  | 58 |  | Total Sections | 4
|  |  | N-1 Rating before transfers, MVA | 29 |  | Significant | 1
|  |  | N-2 Rating before transfers, MVA | 0 |  | Major | 4
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 16.51
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major
|  |  | Average Consequence Loss Oil | 0 | 0
|  |  | Average Consequences Loss SF6 kgs | 0 | 0
|  |  | Average Consequence Fire | 0.05 | 5
|  |  | Average Consequence Waste | 10 | 40
|  |  | Average Consequence Disturbance | 3 | 5
|  |  | Average Cost of Fault (Air Insulated) | 12124.0991 | 95334.7965
|  |  | Average Cost of Fault (SF6 Insulated) | 12124.0991 | 95334.7965
|  |  | Average Cost of Fault (Oil Insulated) | 12124.0991 | 95334.7965
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major
|  |  | Switching time only (hours required) | 2 | 0
|  |  | Number of weeks generation required | 2 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 16.3777
|  |  | Number of generators | 0 | 17
|  |  | Generator sites | 0 | 5
|  |  | Number of days to connect all generators | 0 | 2
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major
|  |  | Generator hire | 0 | 1500314.0885
|  |  | Fuel cost | 0 | 6980895.935
|  |  | Fitter cost | 0 | 1628981.5221
|  |  | Traffic management cost | 0 | 4352240.708
|  |  | Transformer hire | 0 | 441268.8496
|  |  | Earthing and bunding | 0 | 10362.4779
|  |  | Temporary fencing | 0 | 186524.6018
|  |  | Miscellaneous materials | 0 | 10362.4779
|  |  | Installation & removal of step-down transformers | 0 | 12953.0973
|  |  | Council permits | 0 | 20724.9558
|  |  | Crane hire | 0 | 12953.0973
|  |  | Cable hire | 0 | 15543.7168
|  |  | Total | 0 | 15173125.5279
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major
|  |  | Minor | 0.7692% | 3.846%
|  |  | Serious | 0.1923% | 0.9615%
|  |  | Fataility | 0.01923% | 0.09615%
|  |  | Value of event | 6517.2332 | 32586.1661
|  |  | Weighted likelyhood of consequence | 0.04115% | 0.2058%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 32.974 | 33.311 | 32.837 | 33.248 | 33.672 | 34.452 | 35.855 | 35.855 | 35.855 | 35.855 | 35.855 | 35.855
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 30.814 | 30.805 | 30.827 | 31.247 | 31.366 | 32.366 | 33.04 | 33.04 | 33.04 | 33.04 | 33.04 | 33.04
|  |  | Selected | 70% |  |  |  |  | 31.462 | 31.5568 | 31.43 | 31.8473 | 32.0578 | 32.9918 | 33.8845 | 33.8845 | 33.8845 | 33.8845 | 33.8845 | 33.8845
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 14.952 | 15.0468 | 14.92 | 15.3373 | 15.5478 | 16.4818 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745
|  |  | N-3 | [5 empty] | 14.952 | 15.0468 | 14.92 | 15.3373 | 15.5478 | 16.4818 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745
|  |  | N-4 | [5 empty] | 14.952 | 15.0468 | 14.92 | 15.3373 | 15.5478 | 16.4818 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745
End

## Base Case
CitiPower - B Switchboard Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 21633651.8523 | 0 | 0 | 0 | 0 | 100% | 21633651.8523 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 32586.1661 | 0 | 0 | 0 | 100% | 32586.1661 | 32586.1661
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 15173125.5279 | 0 | 0 | 100% | 15173125.5279 | 15173125.5279
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 8440046.6716 | 0 | 100% | 8440046.6716 | 8440046.6716
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 95334.7965 | 100% | 95334.7965 | 95334.7965
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 379346.1045 | 0 | 0 | 0 | 0 | 100% | 379346.1045 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 6517.2332 | 0 | 0 | 0 | 100% | 6517.2332 | 6517.2332
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 47045.6496 | 0 | 100% | 47045.6496 | 47045.6496
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 12124.0991 | 100% | 12124.0991 | 12124.0991
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 379346.1045 | 6517.2332 | 51812.3894 | 47045.6496 | 12124.0991 | 100% | 496845.4758 | 117499.3713
[5 empty] | 2 | Major |  | 21633651.8523 | 32586.1661 | 15224937.9173 | 8440046.6716 | 95334.7965 | 100% | 45426557.4038 | 23792905.5515
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 45923402.8796; 2026: 23910404.9228
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 58
|  |  | N-1 Rating before transfers, MVA |  |  | 29
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 16.51
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 32.974 | 33.311 | 32.837 | 33.248 | 33.672 | 34.452 | 35.855 | 35.855 | 35.855 | 35.855 | 35.855 | 35.855
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 30.814 | 30.805 | 30.827 | 31.247 | 31.366 | 32.366 | 33.04 | 33.04 | 33.04 | 33.04 | 33.04 | 33.04
|  |  | Selected |  |  | 70% |  | 31.462 | 31.5568 | 31.43 | 31.8473 | 32.0578 | 32.9918 | 33.8845 | 33.8845 | 33.8845 | 33.8845 | 33.8845 | 33.8845
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 14.952 | 15.0468 | 14.92 | 15.3373 | 15.5478 | 16.4818 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745
|  |  | N-3 |  |  |  |  | 14.952 | 15.0468 | 14.92 | 15.3373 | 15.5478 | 16.4818 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745
|  |  | N-4 |  |  |  |  | 14.952 | 15.0468 | 14.92 | 15.3373 | 15.5478 | 16.4818 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745 | 17.3745
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 379346.1045 | 380489.1345 | 378960.2716 | 383991.774 | 386529.8312 | 397791.3296 | 408554.8623 | 408554.8623 | 408554.8623 | 408554.8623 | 408554.8623 | 408554.8623
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 21633651.8523 | 21770815.4555 | 21587351.9018 | 22191132.1933 | 22495699.0549 | 23847078.859 | 25138702.7894 | 25138702.7894 | 25138702.7894 | 25138702.7894 | 25138702.7894 | 25138702.7894
|  |  | N-3 |  |  | Catastrophic |  | 21633651.8523 | 21770815.4555 | 21587351.9018 | 22191132.1933 | 22495699.0549 | 23847078.859 | 25138702.7894 | 25138702.7894 | 25138702.7894 | 25138702.7894 | 25138702.7894 | 25138702.7894
|  |  | N-4 |  |  | Catastrophic |  | 21633651.8523 | 21770815.4555 | 21587351.9018 | 22191132.1933 | 22495699.0549 | 23847078.859 | 25138702.7894 | 25138702.7894 | 25138702.7894 | 25138702.7894 | 25138702.7894 | 25138702.7894
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 4.969% | 5.33% | 5.721% | 6.144% | 6.601% | 7.097% | 7.634% | 8.215% | 8.845% | 9.528% | 10.27% | 11.07%
|  |  | Major |  |  |  |  | 0.5521% | 0.5922% | 0.6357% | 0.6826% | 0.7335% | 0.7885% | 0.8482% | 0.9128% | 0.9828% | 1.059% | 1.141% | 1.23%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 18849.6147 | 20280.8172 | 21680.093 | 23591.5004 | 25516.3646 | 28230.806 | 31187.0803 | 33562.1278 | 36135.7386 | 38925.2513 | 41949.5588 | 45208.8408
|  |  | Network Performance |  |  | Major |  | 121535.6063 | 131189.7762 | 139631.0808 | 154106.6134 | 167838.5033 | 191181.2594 | 216683.6353 | 233185.1457 | 251066.2469 | 270447.4058 | 291459.8876 | 314104.9396
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 5838.5149 | 6262.947 | 6722.0695 | 7218.8694 | 7756.5987 | 8338.799 | 8969.3274 | 9652.3852 | 10392.5493 | 11194.8063 | 12064.5897 | 13001.9512
|  |  | Other major risks |  |  | Major |  | 131362.6253 | 140912.0597 | 151242.006 | 162419.6661 | 174518.2113 | 187617.3232 | 201803.7842 | 217172.1217 | 233825.3123 | 251875.5504 | 271445.0871 | 292535.0839
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 47045.6496 | 47045.6496 | 47045.6496 | 47045.6496 | 47045.6496 | 47045.6496 | 47045.6496 | 47045.6496 | 47045.6496 | 47045.6496 | 47045.6496 | 47045.6496
|  |  | Subtotal |  |  |  |  | 324632.0106 | 345691.2496 | 366320.8989 | 394382.2989 | 422675.3275 | 462413.8372 | 505689.4767 | 540617.4299 | 578465.4967 | 619488.6634 | 663964.7728 | 711896.465
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 77718.5841 | 2278812.5097 | 6083515.5778 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 315108.8547
|  |  | Post-replacement opex |  |  | 20828.5805
|  |  | Total annuity |  |  | 335937.4352
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 324632.0106 | 345691.2496 | 366320.8989 | 394382.2989 | 422675.3275 | 462413.8372 | 505689.4767 | 540617.4299 | 578465.4967 | 619488.6634 | 663964.7728 | 711896.465
|  |  | Annualised cost |  |  |  |  | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352
|  |  | Feasible ? |  |  |  |  | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - B Switchboard Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 17421817.7027 | 0 | 0 | 0 | 0 | 100% | 17421817.7027 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 32586.1661 | 0 | 0 | 0 | 100% | 32586.1661 | 32586.1661
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 16690438.0807 | 0 | 0 | 100% | 16690438.0807 | 16690438.0807
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 9284051.3388 | 0 | 100% | 9284051.3388 | 9284051.3388
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 85801.3168 | 100% | 85801.3168 | 85801.3168
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 324340.9194 | 0 | 0 | 0 | 0 | 100% | 324340.9194 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 6517.2332 | 0 | 0 | 0 | 100% | 6517.2332 | 6517.2332
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 51750.2145 | 0 | 100% | 51750.2145 | 51750.2145
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 10911.6892 | 100% | 10911.6892 | 10911.6892
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 324340.9194 | 6517.2332 | 56993.6283 | 51750.2145 | 10911.6892 | 100% | 450513.6846 | 126172.7653
[5 empty] | 2 | Major |  | 17421817.7027 | 32586.1661 | 16747431.709 | 9284051.3388 | 85801.3168 | 100% | 43571688.2334 | 26149870.5307
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 44022201.918; 2026: 26276043.296
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 58
|  |  | N-1 Rating before transfers, MVA |  |  | 29
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 16.51
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 31.3253 | 31.6454 | 31.1952 | 31.5856 | 31.9884 | 32.7294 | 34.0622 | 34.0622 | 34.0622 | 34.0622 | 34.0622 | 34.0622
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 29.2733 | 29.2647 | 29.2857 | 29.6846 | 29.7977 | 30.7477 | 31.388 | 31.388 | 31.388 | 31.388 | 31.388 | 31.388
|  |  | Selected |  |  | 70% |  | 29.8889 | 29.979 | 29.8585 | 30.2549 | 30.4549 | 31.3422 | 32.1903 | 32.1903 | 32.1903 | 32.1903 | 32.1903 | 32.1903
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 13.3789 | 13.469 | 13.3485 | 13.7449 | 13.9449 | 14.8322 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803
|  |  | N-3 |  |  |  |  | 13.3789 | 13.469 | 13.3485 | 13.7449 | 13.9449 | 14.8322 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803
|  |  | N-4 |  |  |  |  | 13.3789 | 13.469 | 13.3485 | 13.7449 | 13.9449 | 14.8322 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 324340.9194 | 325318.21 | 324011.0322 | 328312.9668 | 330483.0057 | 340111.5868 | 349314.4073 | 349314.4073 | 349314.4073 | 349314.4073 | 349314.4073 | 349314.4073
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 17421817.7027 | 17539092.5834 | 17382231.245 | 17898463.3942 | 18158868.0609 | 19314297.7934 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539
|  |  | N-3 |  |  | Catastrophic |  | 17421817.7027 | 17539092.5834 | 17382231.245 | 17898463.3942 | 18158868.0609 | 19314297.7934 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539
|  |  | N-4 |  |  | Catastrophic |  | 17421817.7027 | 17539092.5834 | 17382231.245 | 17898463.3942 | 18158868.0609 | 19314297.7934 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 4.472% | 4.797% | 5.149% | 5.529% | 5.941% | 6.387% | 6.87% | 7.393% | 7.96% | 8.575% | 9.241% | 9.959%
|  |  | Major |  |  |  |  | 0.4969% | 0.533% | 0.5721% | 0.6144% | 0.6601% | 0.7097% | 0.7634% | 0.8215% | 0.8845% | 0.9528% | 1.027% | 1.107%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 14504.7785 | 15606.0889 | 16682.8316 | 18153.6596 | 19634.8426 | 21723.6052 | 23998.4583 | 25826.0573 | 27806.4508 | 29952.9809 | 32280.1855 | 34788.203
|  |  | Network Performance |  |  | Major |  | 88180.2259 | 95220.8137 | 101296.3648 | 111980.7849 | 122055.5271 | 139485.1462 | 158532.3794 | 170605.3894 | 183687.7503 | 197867.5994 | 213240.9742 | 229808.7873
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 5642.5443 | 6052.7303 | 6496.4423 | 6976.5671 | 7496.2474 | 8058.9061 | 8668.2707 | 9328.4016 | 10043.722 | 10819.0511 | 11659.6401 | 12565.5389
|  |  | Other major risks |  |  | Major |  | 129938.0638 | 139383.9394 | 149601.8626 | 160658.3067 | 172625.6492 | 185582.7079 | 199615.3238 | 214816.9994 | 231289.5946 | 249144.087 | 268501.4018 | 289362.6883
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145
|  |  | Subtotal |  |  |  |  | 290015.827 | 308013.7868 | 325827.7159 | 349519.5327 | 373562.4809 | 406600.5799 | 442564.6467 | 472327.0622 | 504577.7323 | 539533.9329 | 577432.4161 | 618275.432
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 85490.4425 | 2506693.7607 | 6691867.1356 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 346619.7402
|  |  | Post-replacement opex |  |  | 22911.4386
|  |  | Total annuity |  |  | 369531.1787
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 290015.827 | 308013.7868 | 325827.7159 | 349519.5327 | 373562.4809 | 406600.5799 | 442564.6467 | 472327.0622 | 504577.7323 | 539533.9329 | 577432.4161 | 618275.432
|  |  | Annualised cost |  |  |  |  | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
CitiPower - B Switchboard Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 17421817.7027 | 0 | 0 | 0 | 0 | 100% | 17421817.7027 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 32586.1661 | 0 | 0 | 0 | 100% | 32586.1661 | 32586.1661
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 13655812.9751 | 0 | 0 | 100% | 13655812.9751 | 13655812.9751
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 7596042.0044 | 0 | 100% | 7596042.0044 | 7596042.0044
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 85801.3168 | 100% | 85801.3168 | 85801.3168
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 324340.9194 | 0 | 0 | 0 | 0 | 100% | 324340.9194 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 6517.2332 | 0 | 0 | 0 | 100% | 6517.2332 | 6517.2332
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 42341.0846 | 0 | 100% | 42341.0846 | 42341.0846
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 10911.6892 | 100% | 10911.6892 | 10911.6892
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 324340.9194 | 6517.2332 | 46631.1504 | 42341.0846 | 10911.6892 | 100% | 430742.0768 | 106401.1575
[5 empty] | 2 | Major |  | 17421817.7027 | 32586.1661 | 13702444.1256 | 7596042.0044 | 85801.3168 | 100% | 38838691.3156 | 21416873.6129
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 39269433.3924; 2026: 21523274.7704
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 58
|  |  | N-1 Rating before transfers, MVA |  |  | 29
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 16.51
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 31.3253 | 31.6454 | 31.1952 | 31.5856 | 31.9884 | 32.7294 | 34.0622 | 34.0622 | 34.0622 | 34.0622 | 34.0622 | 34.0622
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 29.2733 | 29.2647 | 29.2857 | 29.6846 | 29.7977 | 30.7477 | 31.388 | 31.388 | 31.388 | 31.388 | 31.388 | 31.388
|  |  | Selected |  |  | 70% |  | 29.8889 | 29.979 | 29.8585 | 30.2549 | 30.4549 | 31.3422 | 32.1903 | 32.1903 | 32.1903 | 32.1903 | 32.1903 | 32.1903
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 13.3789 | 13.469 | 13.3485 | 13.7449 | 13.9449 | 14.8322 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803
|  |  | N-3 |  |  |  |  | 13.3789 | 13.469 | 13.3485 | 13.7449 | 13.9449 | 14.8322 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803
|  |  | N-4 |  |  |  |  | 13.3789 | 13.469 | 13.3485 | 13.7449 | 13.9449 | 14.8322 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803 | 15.6803
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 324340.9194 | 325318.21 | 324011.0322 | 328312.9668 | 330483.0057 | 340111.5868 | 349314.4073 | 349314.4073 | 349314.4073 | 349314.4073 | 349314.4073 | 349314.4073
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 17421817.7027 | 17539092.5834 | 17382231.245 | 17898463.3942 | 18158868.0609 | 19314297.7934 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539
|  |  | N-3 |  |  | Catastrophic |  | 17421817.7027 | 17539092.5834 | 17382231.245 | 17898463.3942 | 18158868.0609 | 19314297.7934 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539
|  |  | N-4 |  |  | Catastrophic |  | 17421817.7027 | 17539092.5834 | 17382231.245 | 17898463.3942 | 18158868.0609 | 19314297.7934 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539 | 20418636.2539
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 4.472% | 4.797% | 5.149% | 5.529% | 5.941% | 6.387% | 6.87% | 7.393% | 7.96% | 8.575% | 9.241% | 9.959%
|  |  | Major |  |  |  |  | 0.4969% | 0.533% | 0.5721% | 0.6144% | 0.6601% | 0.7097% | 0.7634% | 0.8215% | 0.8845% | 0.9528% | 1.027% | 1.107%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 14504.7785 | 15606.0889 | 16682.8316 | 18153.6596 | 19634.8426 | 21723.6052 | 23998.4583 | 25826.0573 | 27806.4508 | 29952.9809 | 32280.1855 | 34788.203
|  |  | Network Performance |  |  | Major |  | 88180.2259 | 95220.8137 | 101296.3648 | 111980.7849 | 122055.5271 | 139485.1462 | 158532.3794 | 170605.3894 | 183687.7503 | 197867.5994 | 213240.9742 | 229808.7873
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 4758.3426 | 5104.2514 | 5478.4326 | 5883.3205 | 6321.5655 | 6796.0541 | 7309.9296 | 7866.6162 | 8469.844 | 9123.677 | 9832.5435 | 10596.4855
|  |  | Other major risks |  |  | Major |  | 106419.9184 | 114156.1374 | 122524.6672 | 131579.9497 | 141381.2626 | 151993.1579 | 163485.9399 | 175936.1876 | 189427.3247 | 204050.2425 | 219903.9793 | 236989.4764
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846
|  |  | Subtotal |  |  |  |  | 256204.3501 | 272428.3759 | 288323.3808 | 309938.7992 | 331734.2824 | 362339.048 | 395667.7918 | 422575.3352 | 451732.4545 | 483335.5844 | 517598.7671 | 554524.0368
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 69946.7257 | 2050931.2588 | 5475164.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 283597.9692
|  |  | Post-replacement opex |  |  | 18745.7225
|  |  | Total annuity |  |  | 302343.6917
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 256204.3501 | 272428.3759 | 288323.3808 | 309938.7992 | 331734.2824 | 362339.048 | 395667.7918 | 422575.3352 | 451732.4545 | 483335.5844 | 517598.7671 | 554524.0368
|  |  | Annualised cost |  |  |  |  | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - B Switchboard Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 26300701.3274 | 0 | 0 | 0 | 0 | 100% | 26300701.3274 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 32586.1661 | 0 | 0 | 0 | 100% | 32586.1661 | 32586.1661
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 16690438.0807 | 0 | 0 | 100% | 16690438.0807 | 16690438.0807
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 9284051.3388 | 0 | 100% | 9284051.3388 | 9284051.3388
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 104868.2761 | 100% | 104868.2761 | 104868.2761
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 438144.7507 | 0 | 0 | 0 | 0 | 100% | 438144.7507 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 6517.2332 | 0 | 0 | 0 | 100% | 6517.2332 | 6517.2332
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 51750.2145 | 0 | 100% | 51750.2145 | 51750.2145
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 13336.509 | 100% | 13336.509 | 13336.509
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 438144.7507 | 6517.2332 | 56993.6283 | 51750.2145 | 13336.509 | 100% | 566742.3358 | 128597.5851
[5 empty] | 2 | Major |  | 26300701.3274 | 32586.1661 | 16747431.709 | 9284051.3388 | 104868.2761 | 100% | 52469638.8174 | 26168937.49
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 53036381.1532; 2026: 26297535.0751
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 58
|  |  | N-1 Rating before transfers, MVA |  |  | 29
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 16.51
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 34.6227 | 34.9766 | 34.4789 | 34.9104 | 35.3556 | 36.1746 | 37.6477 | 37.6477 | 37.6477 | 37.6477 | 37.6477 | 37.6477
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 32.3547 | 32.3453 | 32.3684 | 32.8094 | 32.9343 | 33.9843 | 34.692 | 34.692 | 34.692 | 34.692 | 34.692 | 34.692
|  |  | Selected |  |  | 70% |  | 33.0351 | 33.1346 | 33.0015 | 33.4397 | 33.6607 | 34.6414 | 35.5787 | 35.5787 | 35.5787 | 35.5787 | 35.5787 | 35.5787
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 16.5251 | 16.6246 | 16.4915 | 16.9297 | 17.1507 | 18.1314 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687
|  |  | N-3 |  |  |  |  | 16.5251 | 16.6246 | 16.4915 | 16.9297 | 17.1507 | 18.1314 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687
|  |  | N-4 |  |  |  |  | 16.5251 | 16.6246 | 16.4915 | 16.9297 | 17.1507 | 18.1314 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 438144.7507 | 439464.9504 | 437699.1137 | 443510.499 | 446441.955 | 459448.9857 | 471880.866 | 471880.866 | 471880.866 | 471880.866 | 471880.866 | 471880.866
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 26300701.3274 | 26459125.2891 | 26247224.8846 | 26944591.1212 | 27296365.8464 | 28857209.5201 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598
|  |  | N-3 |  |  | Catastrophic |  | 26300701.3274 | 26459125.2891 | 26247224.8846 | 26944591.1212 | 27296365.8464 | 28857209.5201 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598
|  |  | N-4 |  |  | Catastrophic |  | 26300701.3274 | 26459125.2891 | 26247224.8846 | 26944591.1212 | 27296365.8464 | 28857209.5201 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 5.466% | 5.863% | 6.293% | 6.758% | 7.262% | 7.807% | 8.397% | 9.036% | 9.729% | 10.48% | 11.29% | 12.17%
|  |  | Major |  |  |  |  | 0.6073% | 0.6515% | 0.6992% | 0.7509% | 0.8068% | 0.8674% | 0.933% | 1.004% | 1.081% | 1.164% | 1.255% | 1.352%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 23948.4354 | 25766.7783 | 27544.5582 | 29973.0013 | 32418.5412 | 35867.239 | 39623.1855 | 42640.6833 | 45910.4558 | 49454.5318 | 53296.9145 | 57437.8322
|  |  | Network Performance |  |  | Major |  | 162390.1507 | 175235.8206 | 186587.9545 | 205658.0665 | 223839.3164 | 254291.9477 | 287554.4233 | 309453.0881 | 333182.567 | 358902.7279 | 386787.769 | 416839.3457
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 7028.9806 | 7539.9539 | 8092.691 | 8690.7877 | 9338.1593 | 10039.0695 | 10798.1619 | 11620.4943 | 12511.5769 | 13477.4131 | 14524.5442 | 15653.0325
|  |  | Other major risks |  |  | Major |  | 158928.9864 | 170482.3633 | 182980.0422 | 196503.3269 | 211140.744 | 226988.696 | 244152.1765 | 262745.5495 | 282893.4014 | 304731.4702 | 328407.6613 | 353923.3802
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145 | 51750.2145
|  |  | Subtotal |  |  |  |  | 404046.7677 | 430775.1306 | 456955.4603 | 492575.397 | 528486.9754 | 578937.1667 | 633878.1616 | 678210.0298 | 726248.2156 | 778316.3574 | 834767.1035 | 895603.8051
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 85490.4425 | 2506693.7607 | 6691867.1356 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 346619.7402
|  |  | Post-replacement opex |  |  | 22911.4386
|  |  | Total annuity |  |  | 369531.1787
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 404046.7677 | 430775.1306 | 456955.4603 | 492575.397 | 528486.9754 | 578937.1667 | 633878.1616 | 678210.0298 | 726248.2156 | 778316.3574 | 834767.1035 | 895603.8051
|  |  | Annualised cost |  |  |  |  | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - B Switchboard Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 26300701.3274 | 0 | 0 | 0 | 0 | 100% | 26300701.3274 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 32586.1661 | 0 | 0 | 0 | 100% | 32586.1661 | 32586.1661
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 13655812.9751 | 0 | 0 | 100% | 13655812.9751 | 13655812.9751
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 7596042.0044 | 0 | 100% | 7596042.0044 | 7596042.0044
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 104868.2761 | 100% | 104868.2761 | 104868.2761
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 438144.7507 | 0 | 0 | 0 | 0 | 100% | 438144.7507 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 6517.2332 | 0 | 0 | 0 | 100% | 6517.2332 | 6517.2332
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 42341.0846 | 0 | 100% | 42341.0846 | 42341.0846
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 13336.509 | 100% | 13336.509 | 13336.509
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 438144.7507 | 6517.2332 | 46631.1504 | 42341.0846 | 13336.509 | 100% | 546970.728 | 108825.9773
[5 empty] | 2 | Major |  | 26300701.3274 | 32586.1661 | 13702444.1256 | 7596042.0044 | 104868.2761 | 100% | 47736641.8996 | 21435940.5722
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 48283612.6276; 2026: 21544766.5495
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 58
|  |  | N-1 Rating before transfers, MVA |  |  | 29
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 16.51
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 34.6227 | 34.9766 | 34.4789 | 34.9104 | 35.3556 | 36.1746 | 37.6477 | 37.6477 | 37.6477 | 37.6477 | 37.6477 | 37.6477
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 32.3547 | 32.3453 | 32.3684 | 32.8094 | 32.9343 | 33.9843 | 34.692 | 34.692 | 34.692 | 34.692 | 34.692 | 34.692
|  |  | Selected |  |  | 70% |  | 33.0351 | 33.1346 | 33.0015 | 33.4397 | 33.6607 | 34.6414 | 35.5787 | 35.5787 | 35.5787 | 35.5787 | 35.5787 | 35.5787
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 16.5251 | 16.6246 | 16.4915 | 16.9297 | 17.1507 | 18.1314 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687
|  |  | N-3 |  |  |  |  | 16.5251 | 16.6246 | 16.4915 | 16.9297 | 17.1507 | 18.1314 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687
|  |  | N-4 |  |  |  |  | 16.5251 | 16.6246 | 16.4915 | 16.9297 | 17.1507 | 18.1314 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687 | 19.0687
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 438144.7507 | 439464.9504 | 437699.1137 | 443510.499 | 446441.955 | 459448.9857 | 471880.866 | 471880.866 | 471880.866 | 471880.866 | 471880.866 | 471880.866
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 26300701.3274 | 26459125.2891 | 26247224.8846 | 26944591.1212 | 27296365.8464 | 28857209.5201 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598
|  |  | N-3 |  |  | Catastrophic |  | 26300701.3274 | 26459125.2891 | 26247224.8846 | 26944591.1212 | 27296365.8464 | 28857209.5201 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598
|  |  | N-4 |  |  | Catastrophic |  | 26300701.3274 | 26459125.2891 | 26247224.8846 | 26944591.1212 | 27296365.8464 | 28857209.5201 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598 | 30349035.1598
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 5.466% | 5.863% | 6.293% | 6.758% | 7.262% | 7.807% | 8.397% | 9.036% | 9.729% | 10.48% | 11.29% | 12.17%
|  |  | Major |  |  |  |  | 0.6073% | 0.6515% | 0.6992% | 0.7509% | 0.8068% | 0.8674% | 0.933% | 1.004% | 1.081% | 1.164% | 1.255% | 1.352%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 23948.4354 | 25766.7783 | 27544.5582 | 29973.0013 | 32418.5412 | 35867.239 | 39623.1855 | 42640.6833 | 45910.4558 | 49454.5318 | 53296.9145 | 57437.8322
|  |  | Network Performance |  |  | Major |  | 162390.1507 | 175235.8206 | 186587.9545 | 205658.0665 | 223839.3164 | 254291.9477 | 287554.4233 | 309453.0881 | 333182.567 | 358902.7279 | 386787.769 | 416839.3457
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 5948.2897 | 6380.7019 | 6848.4568 | 7354.5974 | 7902.437 | 8495.5837 | 9137.9672 | 9833.8678 | 10587.9483 | 11405.2892 | 12291.4261 | 13246.4117
|  |  | Other major risks |  |  | Major |  | 130184.5865 | 139648.3831 | 149885.6922 | 160963.1129 | 172953.1603 | 185934.8015 | 199994.0405 | 215224.5573 | 231728.4048 | 249616.7713 | 269010.8115 | 289911.6767
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846 | 42341.0846
|  |  | Subtotal |  |  |  |  | 364812.547 | 389372.7685 | 413207.7463 | 446289.8627 | 479454.5395 | 526930.6565 | 578650.7011 | 619493.2811 | 663750.4606 | 711720.4048 | 763728.0058 | 819776.3509
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 69946.7257 | 2050931.2588 | 5475164.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 283597.9692
|  |  | Post-replacement opex |  |  | 18745.7225
|  |  | Total annuity |  |  | 302343.6917
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 364812.547 | 389372.7685 | 413207.7463 | 446289.8627 | 479454.5395 | 526930.6565 | 578650.7011 | 619493.2811 | 663750.4606 | 711720.4048 | 763728.0058 | 819776.3509
|  |  | Annualised cost |  |  |  |  | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - B Switchboard Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 324632.0106 | 345691.2496 | 366320.8989 | 394382.2989 | 422675.3275 | 462413.8372 | 505689.4767 | 540617.4299 | 578465.4967 | 619488.6634 | 663964.7728 | 711896.465
|  |  | Annualised cost | Scenario Base case | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352 | 335937.4352
|  |  | Risk cost | Scenario A | 290015.827 | 308013.7868 | 325827.7159 | 349519.5327 | 373562.4809 | 406600.5799 | 442564.6467 | 472327.0622 | 504577.7323 | 539533.9329 | 577432.4161 | 618275.432
|  |  | Annualised cost | Scenario A | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787
|  |  | Risk cost | Scenario B | 256204.3501 | 272428.3759 | 288323.3808 | 309938.7992 | 331734.2824 | 362339.048 | 395667.7918 | 422575.3352 | 451732.4545 | 483335.5844 | 517598.7671 | 554524.0368
|  |  | Annualised cost | Scenario B | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917
|  |  | Risk cost | Scenario C | 404046.7677 | 430775.1306 | 456955.4603 | 492575.397 | 528486.9754 | 578937.1667 | 633878.1616 | 678210.0298 | 726248.2156 | 778316.3574 | 834767.1035 | 895603.8051
|  |  | Annualised cost | Scenario C | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787 | 369531.1787
|  |  | Risk cost | Scenario D | 364812.547 | 389372.7685 | 413207.7463 | 446289.8627 | 479454.5395 | 526930.6565 | 578650.7011 | 619493.2811 | 663750.4606 | 711720.4048 | 763728.0058 | 819776.3509
|  |  | Annualised cost | Scenario D | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917 | 302343.6917
Charts
End