## Inputs
CitiPower - Celestial Avenue Transformer No. 2 Replacement Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | Celestial Avenue Transformer No. 2 Replacement Risk Monetisation Model
|  | Model start & timeline |  | 2019 | FY19/20
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 50
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex regulator, real $2019 |  | 3748000 |  |  |  |  | 0 | 0 | 50000 | 750000 | 2948000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 3883856.708 |  |  |  |  | 0 | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 10300 | 3400
|  |  | Opex ($2021) | 10673.3522 | 3523.2425
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 9.357% | 10.04% | 10.78% | 11.57% | 12.43% | 13.36% | 14.36% | 15.45% | 16.62% | 17.89% | 19.26% | 20.73%
|  |  | Major | 2 |  |  |  |  | 0.05031% | 0.05398% | 0.05793% | 0.06221% | 0.06683% | 0.07182% | 0.07721% | 0.08304% | 0.08934% | 0.09616% | 0.1035% | 0.1115%
|  |  | Catastrophic | 3 |  |  |  |  | 0.05031% | 0.05398% | 0.05793% | 0.06221% | 0.06683% | 0.07182% | 0.07721% | 0.08304% | 0.08934% | 0.09616% | 0.1035% | 0.1115%
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 13791 | 26450 | 20% | 497.5245
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 139552 | 47770 | 40% | 18185.0433
|  |  | Industrial | 1764 | 47070 | 80% | 452.9975
|  |  | Total | 155107 | 45866.4178 | 39.44% | 19135.5653
Asset information
|  | Assets at risk |  | 3
|  | N-rating, MVA |  | 67.1
|  |  | N-1 Rating before transfers, MVA | 67.1
|  |  | N-2 Rating before transfers, MVA | 35.4
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major | Catastrophic
|  |  | Average Consequence Loss Oil | 500 | 4050 | 12150
|  |  | Average Consequences Loss SF6 kgs | 0 | 0 | 0
|  |  | Average Consequence Fire | 0.05 | 2.5 | 5
|  |  | Average Consequence Waste | 10 | 405 | 1215
|  |  | Average Consequence Disturbance | 2 | 3 | 5
|  |  | Average Cost of Fault (Air Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (SF6 Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (Oil Insulated) | 63521.9894 | 866510.4 | 2571967.0088
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Switching time only (hours required) | 0 | 0 | 0 | 0
|  |  | Number of weeks generation required | 1.1905 | 6 | 6 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 0 | 14.9466 | 50.3466
|  |  | Number of generators | 0 | 0 | 15 | 51
|  |  | Generator sites | 0 | 0 | 4 | 13
|  |  | Number of days to connect all generators | 0 | 0 | 2 | 5
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Generator hire | 0 | 0 | 689104.7788 | 4593427.3805
|  |  | Fuel cost | 0 | 0 | 2493873.745 | 16800863.3419
|  |  | Fitter cost | 0 | 0 | 676462.5558 | 4235351.9575
|  |  | Traffic management cost | 0 | 0 | 1740896.2832 | 11315825.8407
|  |  | Transformer hire | 0 | 0 | 183761.2743 | 1170873.646
|  |  | Earthing and bunding | 0 | 0 | 8289.9823 | 26942.4425
|  |  | Temporary fencing | 0 | 0 | 74609.8407 | 484963.9646
|  |  | Miscellaneous materials | 0 | 0 | 8289.9823 | 26942.4425
|  |  | Installation & removal of step-down transformers | 0 | 0 | 10362.4779 | 33678.0531
|  |  | Council permits | 0 | 0 | 16579.9646 | 53884.885
|  |  | Crane hire | 0 | 0 | 10362.4779 | 33678.0531
|  |  | Cable hire | 0 | 0 | 12434.9735 | 40413.6637
|  |  | Total | 0 | 0 | 5925028.3362 | 38816845.6711
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major | Catastrophic
|  |  | Minor | 1.172% | 4.103% | 4.103%
|  |  | Serious | 0.2345% | 0.8206% | 0.8206%
|  |  | Fataility | 0.02345% | 0.08206% | 0.08206%
|  |  | Value of event | 8261.6388 | 28915.7357 | 28915.7357
|  |  | Weighted likelyhood of consequence | 0.05217% | 0.1826% | 0.1826%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 58.829 | 58.016 | 47.6505 | 48.8986 | 48.3559 | 48.8852 | 54.1573 | 54.1573 | 54.1573 | 54.1573 | 54.1573 | 54.1573
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 54.281 | 53.331 | 44.8325 | 45.875 | 45.4209 | 45.3691 | 50.2641 | 50.2641 | 50.2641 | 50.2641 | 50.2641 | 50.2641
|  |  | Weighting to 50% PoE | 70% |  |  |  |  | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 20.2454 | 19.3365 | 10.2779 | 11.3821 | 10.9014 | 11.0239 | 16.032 | 16.032 | 16.032 | 16.032 | 16.032 | 16.032
|  |  | N-3 | [5 empty] | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
|  |  | N-4 | [5 empty] | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
End

## Base Case
CitiPower - Celestial Avenue Transformer No. 2 Replacement Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 102221393.5861 | 0 | 0 | 0 | 0 | 20% | 20444278.7172 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 38816845.6711 | 0 | 0 | 20% | 7763369.1342 | 7763369.1342
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 11651570.1239 | 0 | 20% | 2330314.0248 | 2330314.0248
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2571967.0088 | 20% | 514393.4018 | 514393.4018
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 20% | 10362.4779 | 10362.4779
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3883856.708 | 0 | 80% | 3107085.3664 | 3107085.3664
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 866510.4 | 80% | 693208.32 | 693208.32
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 80% | 41449.9115 | 41449.9115
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 23244430.3764 | 0 | 5925028.3362 | 0 | 0 | 4% | 1166778.3485 | 237001.1334
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 10673.3522 | 0 | 100% | 10673.3522 | 10673.3522
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 63521.9894 | 100% | 63521.9894 | 63521.9894
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 23244430.3764 | 0 | 1175600.8604 | 0 | 0 | 4% | 976801.2495 | 47024.0344
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 23244430.3764 | 8261.6388 | 1227413.2497 | 10673.3522 | 63521.9894 | 4.525% | 1111070.6192 | 181293.4041
[5 empty] | 2 | Major |  | 23244430.3764 | 28915.7357 | 5976840.7256 | 3883856.708 | 866510.4 | 14.8% | 5031654.5349 | 4101877.3199
[5 empty] | 3 | Catastrophic |  | 102221393.5861 | 28915.7357 | 38868658.0605 | 11651570.1239 | 2571967.0088 | 20% | 31068500.903 | 10624222.1858
[5 empty] | Subtotal |  |  | 2025: 37211226.0571; 2026: 14907392.9098
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 67.1
|  |  | N-1 Rating before transfers, MVA |  |  | 67.1
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 58.829 | 58.016 | 47.6505 | 48.8986 | 48.3559 | 48.8852 | 54.1573 | 54.1573 | 54.1573 | 54.1573 | 54.1573 | 54.1573
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 54.281 | 53.331 | 44.8325 | 45.875 | 45.4209 | 45.3691 | 50.2641 | 50.2641 | 50.2641 | 50.2641 | 50.2641 | 50.2641
|  |  | Weighting to 50% PoE |  |  | 70% |  | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 20.2454 | 19.3365 | 10.2779 | 11.3821 | 10.9014 | 11.0239 | 16.032 | 16.032 | 16.032 | 16.032 | 16.032 | 16.032
|  |  | N-3 |  |  |  |  | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
|  |  | N-4 |  |  |  |  | 55.6454 | 54.7365 | 45.6779 | 46.7821 | 46.3014 | 46.4239 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432 | 51.432
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Adjustment |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 23244430.3764 | 22200891.4605 | 9440313.7176 | 10454555.3234 | 10013028.6933 | 10125560.326 | 18406939.5197 | 18406939.5197 | 18406939.5197 | 18406939.5197 | 18406939.5197 | 18406939.5197
|  |  | N-3 |  |  | Catastrophic |  | 102221393.5861 | 100551731.3206 | 73422065.8667 | 75196988.6769 | 74424317.0742 | 74621247.4314 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153
|  |  | N-4 |  |  | Catastrophic |  | 102221393.5861 | 100551731.3206 | 73422065.8667 | 75196988.6769 | 74424317.0742 | 74621247.4314 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153 | 94481408.2153
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 9.357% | 10.04% | 10.78% | 11.57% | 12.43% | 13.36% | 14.36% | 15.45% | 16.62% | 17.89% | 19.26% | 20.73%
|  |  | Major |  |  |  |  | 0.05031% | 0.05398% | 0.05793% | 0.06221% | 0.06683% | 0.07182% | 0.07721% | 0.08304% | 0.08934% | 0.09616% | 0.1035% | 0.1115%
|  |  | Catastrophic |  |  |  |  | 0.05031% | 0.05398% | 0.05793% | 0.06221% | 0.06683% | 0.07182% | 0.07721% | 0.08304% | 0.08934% | 0.09616% | 0.1035% | 0.1115%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 10285.3339 | 10854.6836 | 8507.3334 | 9355.9946 | 9947.3114 | 10718.3698 | 14590.0714 | 15691.5989 | 16882.5295 | 18170.3812 | 19563.3183 | 21063.0375
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 87003.8449 | 89154.0279 | 40690.7993 | 48388.0384 | 49785.0855 | 54103.8584 | 105739.094 | 113722.2296 | 122353.299 | 131686.7885 | 141781.866 | 152650.8296
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 467.7626 | 479.3227 | 218.7677 | 260.1507 | 267.6617 | 290.881 | 568.4898 | 611.4098 | 657.8134 | 707.9935 | 762.2681 | 820.7034
|  |  | Other significant risks |  |  | Significant |  | 16964.519 | 18200.8876 | 19535.8273 | 20977.5355 | 22534.909 | 24217.6046 | 26036.1049 | 28001.7899 | 30127.0155 | 32425.1978 | 34910.9056 | 37587.1672
|  |  | Other major risks |  |  | Major |  | 2063.6178 | 2214.0136 | 2376.3999 | 2551.7739 | 2741.2177 | 2945.9061 | 3167.1143 | 3406.2264 | 3664.7456 | 3944.3038 | 4246.6731 | 4572.2221
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 5344.9512 | 5734.4895 | 6155.0843 | 6609.3182 | 7099.9944 | 7630.1554 | 8203.1038 | 8822.4253 | 9492.0126 | 10216.0928 | 10999.256 | 11842.4564
|  |  | Annual opex, pre-replacement |  |  |  |  | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522 | 10673.3522
|  |  | Subtotal |  |  |  |  | 132803.3817 | 137310.7772 | 88157.5641 | 98816.1635 | 103049.532 | 110580.1275 | 168977.3303 | 180929.0322 | 193850.7678 | 207824.1098 | 222937.6393 | 239209.7684
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 144760.291
|  |  | Post-replacement opex |  |  | 3523.2425
|  |  | Total annuity |  |  | 148283.5335
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 132803.3817 | 137310.7772 | 88157.5641 | 98816.1635 | 103049.532 | 110580.1275 | 168977.3303 | 180929.0322 | 193850.7678 | 207824.1098 | 222937.6393 | 239209.7684
|  |  | Annualised cost |  |  |  |  | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - Celestial Avenue Transformer No. 2 Replacement Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 87399291.5161 | 0 | 0 | 0 | 0 | 20% | 17479858.3032 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 42698530.2382 | 0 | 0 | 20% | 8539706.0476 | 8539706.0476
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 18045010.6442 | 0 | 6517531.1698 | 0 | 0 | 4% | 982501.6726 | 260701.2468
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 11740.6874 | 0 | 100% | 11740.6874 | 11740.6874
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 18045010.6442 | 0 | 1293160.9464 | 0 | 0 | 4% | 773526.8636 | 51726.4379
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 18045010.6442 | 8261.6388 | 1350154.5747 | 11740.6874 | 57169.7904 | 4.661% | 907692.6086 | 185892.1828
[5 empty] | 2 | Major |  | 18045010.6442 | 28915.7357 | 6574524.7981 | 4272242.3788 | 779859.36 | 17.15% | 5092910.5548 | 4371110.129
[5 empty] | 3 | Catastrophic |  | 87399291.5161 | 28915.7357 | 42755523.8665 | 12816727.1363 | 2314770.308 | 20% | 29063045.7125 | 11583187.4093
[5 empty] | Subtotal |  |  | 2025: 35063648.8758; 2026: 16140189.7211
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 67.1
|  |  | N-1 Rating before transfers, MVA |  |  | 67.1
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 55.8875 | 55.1152 | 45.268 | 46.4537 | 45.9381 | 46.4409 | 51.4494 | 51.4494 | 51.4494 | 51.4494 | 51.4494 | 51.4494
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 51.5669 | 50.6645 | 42.5909 | 43.5813 | 43.1499 | 43.1007 | 47.7509 | 47.7509 | 47.7509 | 47.7509 | 47.7509 | 47.7509
|  |  | Weighting to 50% PoE |  |  | 70% |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 17.4631 | 16.5997 | 7.994 | 9.043 | 8.5863 | 8.7027 | 13.4604 | 13.4604 | 13.4604 | 13.4604 | 13.4604 | 13.4604
|  |  | N-3 |  |  |  |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
|  |  | N-4 |  |  |  |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 18045010.6442 | 17152784.871 | 6608286.3664 | 7475462.9394 | 7097957.6707 | 7194172.2166 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617
|  |  | N-3 |  |  | Catastrophic |  | 87399291.5161 | 85971730.2791 | 62775866.3161 | 64293425.3188 | 63632791.0985 | 63801166.5538 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241
|  |  | N-4 |  |  | Catastrophic |  | 87399291.5161 | 85971730.2791 | 62775866.3161 | 64293425.3188 | 63632791.0985 | 63801166.5538 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 8.422% | 9.036% | 9.698% | 10.41% | 11.19% | 12.02% | 12.93% | 13.9% | 14.96% | 16.1% | 17.33% | 18.66%
|  |  | Major |  |  |  |  | 0.04528% | 0.04858% | 0.05214% | 0.05599% | 0.06015% | 0.06464% | 0.06949% | 0.07474% | 0.08041% | 0.08654% | 0.09318% | 0.1003%
|  |  | Catastrophic |  |  |  |  | 0.04528% | 0.04858% | 0.05214% | 0.05599% | 0.06015% | 0.06464% | 0.06949% | 0.07474% | 0.08041% | 0.08654% | 0.09318% | 0.1003%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 7914.5644 | 8352.679 | 6546.3931 | 7199.4378 | 7654.4561 | 8247.7856 | 11227.0599 | 12074.6853 | 12991.1064 | 13982.1083 | 15053.9734 | 16208.0074
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 60788.1868 | 61993.7212 | 25635.4626 | 31139.6018 | 31762.1367 | 34596.5276 | 71910.2902 | 77339.4042 | 83209.1604 | 89556.6135 | 96422.0019 | 103813.6893
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 326.8182 | 333.2996 | 137.8251 | 167.4172 | 170.7642 | 186.0028 | 386.6145 | 415.8032 | 447.3611 | 481.4872 | 518.3979 | 558.1381
|  |  | Other significant risks |  |  | Significant |  | 15655.3645 | 16796.3223 | 18028.2445 | 19358.6959 | 20795.8867 | 22348.7284 | 24026.8947 | 25840.8875 | 27802.1091 | 29922.9403 | 32216.8257 | 34686.5598
|  |  | Other major risks |  |  | Major |  | 1979.1598 | 2123.4003 | 2279.1406 | 2447.337 | 2629.0274 | 2825.3385 | 3037.4933 | 3266.8192 | 3514.7579 | 3782.8746 | 4072.8688 | 4385.094
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 5244.6583 | 5626.8872 | 6039.5899 | 6485.3006 | 6966.7697 | 7486.9827 | 8049.1803 | 8656.8808 | 9313.904 | 10024.3975 | 10792.8654 | 11620.2438
|  |  | Annual opex, pre-replacement |  |  |  |  | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874
|  |  | Subtotal |  |  |  |  | 103649.4394 | 106966.9971 | 70407.3432 | 78538.4776 | 81719.7283 | 87432.0531 | 130378.2203 | 139335.1677 | 149019.0863 | 159491.1088 | 170817.6205 | 183012.4198
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 3875.5667
|  |  | Total annuity |  |  | 163111.8869
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 103649.4394 | 106966.9971 | 70407.3432 | 78538.4776 | 81719.7283 | 87432.0531 | 130378.2203 | 139335.1677 | 149019.0863 | 159491.1088 | 170817.6205 | 183012.4198
|  |  | Annualised cost |  |  |  |  | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
End

## Scenario B
CitiPower - Celestial Avenue Transformer No. 2 Replacement Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 87399291.5161 | 0 | 0 | 0 | 0 | 20% | 17479858.3032 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 34935161.104 | 0 | 0 | 20% | 6987032.2208 | 6987032.2208
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 18045010.6442 | 0 | 5332525.5026 | 0 | 0 | 4% | 935101.4459 | 213301.0201
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 9606.017 | 0 | 100% | 9606.017 | 9606.017
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 18045010.6442 | 0 | 1058040.7743 | 0 | 0 | 4% | 764122.0567 | 42321.631
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 18045010.6442 | 8261.6388 | 1104671.9248 | 9606.017 | 57169.7904 | 4.608% | 885790.6534 | 163990.2276
[5 empty] | 2 | Major |  | 18045010.6442 | 28915.7357 | 5379156.653 | 3495471.0372 | 779859.36 | 15.93% | 4415803.2725 | 3694002.8467
[5 empty] | 3 | Catastrophic |  | 87399291.5161 | 28915.7357 | 34981792.2544 | 10486413.1115 | 2314770.308 | 20% | 27042236.5851 | 9562378.2819
[5 empty] | Subtotal |  |  | 2025: 32343830.511; 2026: 13420371.3562
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 67.1
|  |  | N-1 Rating before transfers, MVA |  |  | 67.1
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 55.8875 | 55.1152 | 45.268 | 46.4537 | 45.9381 | 46.4409 | 51.4494 | 51.4494 | 51.4494 | 51.4494 | 51.4494 | 51.4494
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 51.5669 | 50.6645 | 42.5909 | 43.5813 | 43.1499 | 43.1007 | 47.7509 | 47.7509 | 47.7509 | 47.7509 | 47.7509 | 47.7509
|  |  | Weighting to 50% PoE |  |  | 70% |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 17.4631 | 16.5997 | 7.994 | 9.043 | 8.5863 | 8.7027 | 13.4604 | 13.4604 | 13.4604 | 13.4604 | 13.4604 | 13.4604
|  |  | N-3 |  |  |  |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
|  |  | N-4 |  |  |  |  | 52.8631 | 51.9997 | 43.394 | 44.443 | 43.9863 | 44.1027 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604 | 48.8604
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 18045010.6442 | 17152784.871 | 6608286.3664 | 7475462.9394 | 7097957.6707 | 7194172.2166 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617 | 13908955.9617
|  |  | N-3 |  |  | Catastrophic |  | 87399291.5161 | 85971730.2791 | 62775866.3161 | 64293425.3188 | 63632791.0985 | 63801166.5538 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241
|  |  | N-4 |  |  | Catastrophic |  | 87399291.5161 | 85971730.2791 | 62775866.3161 | 64293425.3188 | 63632791.0985 | 63801166.5538 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241 | 80781604.0241
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 8.422% | 9.036% | 9.698% | 10.41% | 11.19% | 12.02% | 12.93% | 13.9% | 14.96% | 16.1% | 17.33% | 18.66%
|  |  | Major |  |  |  |  | 0.04528% | 0.04858% | 0.05214% | 0.05599% | 0.06015% | 0.06464% | 0.06949% | 0.07474% | 0.08041% | 0.08654% | 0.09318% | 0.1003%
|  |  | Catastrophic |  |  |  |  | 0.04528% | 0.04858% | 0.05214% | 0.05599% | 0.06015% | 0.06464% | 0.06949% | 0.07474% | 0.08041% | 0.08654% | 0.09318% | 0.1003%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 7914.5644 | 8352.679 | 6546.3931 | 7199.4378 | 7654.4561 | 8247.7856 | 11227.0599 | 12074.6853 | 12991.1064 | 13982.1083 | 15053.9734 | 16208.0074
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 60788.1868 | 61993.7212 | 25635.4626 | 31139.6018 | 31762.1367 | 34596.5276 | 71910.2902 | 77339.4042 | 83209.1604 | 89556.6135 | 96422.0019 | 103813.6893
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 326.8182 | 333.2996 | 137.8251 | 167.4172 | 170.7642 | 186.0028 | 386.6145 | 415.8032 | 447.3611 | 481.4872 | 518.3979 | 558.1381
|  |  | Other significant risks |  |  | Significant |  | 13810.8378 | 14817.3671 | 15904.1433 | 17077.8399 | 18345.6998 | 19715.5846 | 21196.0281 | 22796.2949 | 24526.4439 | 26397.3972 | 28421.0153 | 30599.7635
|  |  | Other major risks |  |  | Major |  | 1672.5778 | 1794.4748 | 1926.0901 | 2068.232 | 2221.7777 | 2387.6792 | 2566.97 | 2760.7722 | 2970.304 | 3196.888 | 3441.9607 | 3705.8205
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 4329.6723 | 4645.2175 | 4985.9198 | 5353.8715 | 5751.3433 | 6180.7996 | 6644.916 | 7146.5967 | 7688.9952 | 8275.5357 | 8909.9362 | 9592.9698
|  |  | Annual opex, pre-replacement |  |  |  |  | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017
|  |  | Subtotal |  |  |  |  | 98448.6744 | 101542.7761 | 64741.8509 | 72612.4172 | 75512.1948 | 80920.3964 | 123537.8957 | 132139.5736 | 141439.388 | 151496.0469 | 162373.3024 | 174084.4057
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 3170.9182
|  |  | Total annuity |  |  | 133455.1802
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 98448.6744 | 101542.7761 | 64741.8509 | 72612.4172 | 75512.1948 | 80920.3964 | 123537.8957 | 132139.5736 | 141439.388 | 151496.0469 | 162373.3024 | 174084.4057
|  |  | Annualised cost |  |  |  |  | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - Celestial Avenue Transformer No. 2 Replacement Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 118065709.592 | 0 | 0 | 0 | 0 | 20% | 23613141.9184 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 42698530.2382 | 0 | 0 | 20% | 8539706.0476 | 8539706.0476
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 29082733.8186 | 0 | 6517531.1698 | 0 | 0 | 4% | 1424010.5995 | 260701.2468
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 11740.6874 | 0 | 100% | 11740.6874 | 11740.6874
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 29082733.8186 | 0 | 1293160.9464 | 0 | 0 | 4% | 1215035.7906 | 51726.4379
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 29082733.8186 | 8261.6388 | 1350154.5747 | 11740.6874 | 69874.1883 | 4.462% | 1361905.9334 | 198596.5807
[5 empty] | 2 | Major |  | 29082733.8186 | 28915.7357 | 6574524.7981 | 4272242.3788 | 953161.44 | 13.87% | 5673061.1457 | 4509751.793
[5 empty] | 3 | Catastrophic |  | 118065709.592 | 28915.7357 | 42755523.8665 | 12816727.1363 | 2829163.7097 | 20% | 35299208.008 | 11686066.0896
[5 empty] | Subtotal |  |  | 2025: 42334175.0872; 2026: 16394414.4633
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 67.1
|  |  | N-1 Rating before transfers, MVA |  |  | 67.1
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 61.7705 | 60.9168 | 50.033 | 51.3436 | 50.7737 | 51.3294 | 56.8651 | 56.8651 | 56.8651 | 56.8651 | 56.8651 | 56.8651
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 56.995 | 55.9976 | 47.0741 | 48.1688 | 47.692 | 47.6376 | 52.7773 | 52.7773 | 52.7773 | 52.7773 | 52.7773 | 52.7773
|  |  | Weighting to 50% PoE |  |  | 70% |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 23.0277 | 22.0733 | 12.5618 | 13.7212 | 13.2165 | 13.3451 | 18.6037 | 18.6037 | 18.6037 | 18.6037 | 18.6037 | 18.6037
|  |  | N-3 |  |  |  |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
|  |  | N-4 |  |  |  |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 29082733.8186 | 27877446.3706 | 15864869.6637 | 17329180.982 | 16691726.9098 | 16854194.4545 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791
|  |  | N-3 |  |  | Catastrophic |  | 118065709.592 | 116137249.6753 | 84802486.0761 | 99260025.0535 | 98240098.538 | 98500046.6094 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887
|  |  | N-4 |  |  | Catastrophic |  | 118065709.592 | 116137249.6753 | 84802486.0761 | 99260025.0535 | 98240098.538 | 98500046.6094 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 10.29% | 11.04% | 11.85% | 12.73% | 13.67% | 14.69% | 15.8% | 16.99% | 18.28% | 19.67% | 21.18% | 22.81%
|  |  | Major |  |  |  |  | 0.05534% | 0.05937% | 0.06373% | 0.06843% | 0.07351% | 0.079% | 0.08493% | 0.09134% | 0.09828% | 0.1058% | 0.1139% | 0.1226%
|  |  | Catastrophic |  |  |  |  | 0.05534% | 0.05937% | 0.06373% | 0.06843% | 0.07351% | 0.079% | 0.08493% | 0.09134% | 0.09828% | 0.1058% | 0.1139% | 0.1226%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 13067.5167 | 13790.8755 | 10808.5671 | 13584.9041 | 14443.4962 | 15563.073 | 18536.6857 | 19936.1764 | 21449.2537 | 23085.4693 | 24855.1958 | 26760.5892
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 119742.2601 | 123144.843 | 75220.9801 | 88227.3377 | 91290.9555 | 99062.6308 | 148467.0629 | 159676.0931 | 171794.8798 | 184899.9266 | 199074.3104 | 214335.299
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 643.7756 | 662.069 | 404.4139 | 474.3405 | 490.8116 | 532.5948 | 798.21 | 858.4736 | 923.6284 | 994.0856 | 1070.292 | 1152.3403
|  |  | Other significant risks |  |  | Significant |  | 20442.0289 | 21931.8373 | 23540.4226 | 25277.6626 | 27154.2778 | 29181.9046 | 31373.1742 | 33741.7995 | 36302.6693 | 39071.9496 | 42067.1958 | 45292.0569
|  |  | Other major risks |  |  | Major |  | 2495.6974 | 2677.583 | 2873.9697 | 3086.0634 | 3315.1729 | 3562.7189 | 3830.2435 | 4119.4209 | 4432.0687 | 4770.1607 | 5135.8401 | 5529.5523
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 6467.0709 | 6938.389 | 7447.2834 | 7996.8793 | 8590.5681 | 9232.0311 | 9925.2645 | 10674.6063 | 11484.7669 | 12360.8606 | 13308.4412 | 14328.6631
|  |  | Annual opex, pre-replacement |  |  |  |  | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874 | 11740.6874
|  |  | Subtotal |  |  |  |  | 174599.0371 | 180886.2843 | 132036.3243 | 150387.875 | 157025.9695 | 168875.6406 | 224671.3283 | 240747.2574 | 258127.9542 | 276923.1398 | 297251.9627 | 319139.1883
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 3875.5667
|  |  | Total annuity |  |  | 163111.8869
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 174599.0371 | 180886.2843 | 132036.3243 | 150387.875 | 157025.9695 | 168875.6406 | 224671.3283 | 240747.2574 | 258127.9542 | 276923.1398 | 297251.9627 | 319139.1883
|  |  | Annualised cost |  |  |  |  | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - Celestial Avenue Transformer No. 2 Replacement Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 118065709.592 | 0 | 0 | 0 | 0 | 20% | 23613141.9184 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 34935161.104 | 0 | 0 | 20% | 6987032.2208 | 6987032.2208
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 29082733.8186 | 0 | 5332525.5026 | 0 | 0 | 4% | 1376610.3728 | 213301.0201
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 9606.017 | 0 | 100% | 9606.017 | 9606.017
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 29082733.8186 | 0 | 1058040.7743 | 0 | 0 | 4% | 1205630.9837 | 42321.631
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 29082733.8186 | 8261.6388 | 1104671.9248 | 9606.017 | 69874.1883 | 4.426% | 1340003.9782 | 176694.6255
[5 empty] | 2 | Major |  | 29082733.8186 | 28915.7357 | 5379156.653 | 3495471.0372 | 953161.44 | 12.83% | 4995953.8635 | 3832644.5107
[5 empty] | 3 | Catastrophic |  | 118065709.592 | 28915.7357 | 34981792.2544 | 10486413.1115 | 2829163.7097 | 20% | 33278398.8807 | 9665256.9623
[5 empty] | Subtotal |  |  | 2025: 39614356.7223; 2026: 13674596.0985
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 67.1
|  |  | N-1 Rating before transfers, MVA |  |  | 67.1
|  |  | N-2 Rating before transfers, MVA |  |  | 35.4
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 61.7705 | 60.9168 | 50.033 | 51.3436 | 50.7737 | 51.3294 | 56.8651 | 56.8651 | 56.8651 | 56.8651 | 56.8651 | 56.8651
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 56.995 | 55.9976 | 47.0741 | 48.1688 | 47.692 | 47.6376 | 52.7773 | 52.7773 | 52.7773 | 52.7773 | 52.7773 | 52.7773
|  |  | Weighting to 50% PoE |  |  | 70% |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 23.0277 | 22.0733 | 12.5618 | 13.7212 | 13.2165 | 13.3451 | 18.6037 | 18.6037 | 18.6037 | 18.6037 | 18.6037 | 18.6037
|  |  | N-3 |  |  |  |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
|  |  | N-4 |  |  |  |  | 58.4277 | 57.4733 | 47.9618 | 49.1212 | 48.6165 | 48.7451 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037 | 54.0037
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 29082733.8186 | 27877446.3706 | 15864869.6637 | 17329180.982 | 16691726.9098 | 16854194.4545 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791 | 23495431.8791
|  |  | N-3 |  |  | Catastrophic |  | 118065709.592 | 116137249.6753 | 84802486.0761 | 99260025.0535 | 98240098.538 | 98500046.6094 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887
|  |  | N-4 |  |  | Catastrophic |  | 118065709.592 | 116137249.6753 | 84802486.0761 | 99260025.0535 | 98240098.538 | 98500046.6094 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887 | 109126026.4887
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 10.29% | 11.04% | 11.85% | 12.73% | 13.67% | 14.69% | 15.8% | 16.99% | 18.28% | 19.67% | 21.18% | 22.81%
|  |  | Major |  |  |  |  | 0.05534% | 0.05937% | 0.06373% | 0.06843% | 0.07351% | 0.079% | 0.08493% | 0.09134% | 0.09828% | 0.1058% | 0.1139% | 0.1226%
|  |  | Catastrophic |  |  |  |  | 0.05534% | 0.05937% | 0.06373% | 0.06843% | 0.07351% | 0.079% | 0.08493% | 0.09134% | 0.09828% | 0.1058% | 0.1139% | 0.1226%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 13067.5167 | 13790.8755 | 10808.5671 | 13584.9041 | 14443.4962 | 15563.073 | 18536.6857 | 19936.1764 | 21449.2537 | 23085.4693 | 24855.1958 | 26760.5892
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 119742.2601 | 123144.843 | 75220.9801 | 88227.3377 | 91290.9555 | 99062.6308 | 148467.0629 | 159676.0931 | 171794.8798 | 184899.9266 | 199074.3104 | 214335.299
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 643.7756 | 662.069 | 404.4139 | 474.3405 | 490.8116 | 532.5948 | 798.21 | 858.4736 | 923.6284 | 994.0856 | 1070.292 | 1152.3403
|  |  | Other significant risks |  |  | Significant |  | 18187.6074 | 19513.1143 | 20944.2989 | 22489.9498 | 24159.605 | 25963.6177 | 27913.2261 | 30020.6308 | 32299.0785 | 34762.9525 | 37427.872 | 40297.0837
|  |  | Other major risks |  |  | Major |  | 2120.9861 | 2275.5629 | 2442.4635 | 2622.7128 | 2817.4232 | 3027.8019 | 3255.1596 | 3500.9191 | 3766.625 | 4053.9549 | 4364.7301 | 4699.3292
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 5348.7548 | 5738.5703 | 6159.4644 | 6614.0216 | 7105.0469 | 7635.5852 | 8208.9414 | 8828.7036 | 9498.7674 | 10223.3629 | 11007.0834 | 11850.8838
|  |  | Annual opex, pre-replacement |  |  |  |  | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017 | 9606.017
|  |  | Subtotal |  |  |  |  | 168716.9178 | 174731.0521 | 125586.2049 | 143619.2835 | 149913.3554 | 161391.3204 | 216785.3027 | 232427.0136 | 249338.2497 | 267625.7687 | 287405.5007 | 308701.5422
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 3170.9182
|  |  | Total annuity |  |  | 133455.1802
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 168716.9178 | 174731.0521 | 125586.2049 | 143619.2835 | 149913.3554 | 161391.3204 | 216785.3027 | 232427.0136 | 249338.2497 | 267625.7687 | 287405.5007 | 308701.5422
|  |  | Annualised cost |  |  |  |  | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - Celestial Avenue Transformer No. 2 Replacement Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 132803.3817 | 137310.7772 | 88157.5641 | 98816.1635 | 103049.532 | 110580.1275 | 168977.3303 | 180929.0322 | 193850.7678 | 207824.1098 | 222937.6393 | 239209.7684
|  |  | Annualised cost | Scenario Base case | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335 | 148283.5335
|  |  | Risk cost | Scenario A | 103649.4394 | 106966.9971 | 70407.3432 | 78538.4776 | 81719.7283 | 87432.0531 | 130378.2203 | 139335.1677 | 149019.0863 | 159491.1088 | 170817.6205 | 183012.4198
|  |  | Annualised cost | Scenario A | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869
|  |  | Risk cost | Scenario B | 98448.6744 | 101542.7761 | 64741.8509 | 72612.4172 | 75512.1948 | 80920.3964 | 123537.8957 | 132139.5736 | 141439.388 | 151496.0469 | 162373.3024 | 174084.4057
|  |  | Annualised cost | Scenario B | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802
|  |  | Risk cost | Scenario C | 174599.0371 | 180886.2843 | 132036.3243 | 150387.875 | 157025.9695 | 168875.6406 | 224671.3283 | 240747.2574 | 258127.9542 | 276923.1398 | 297251.9627 | 319139.1883
|  |  | Annualised cost | Scenario C | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869 | 163111.8869
|  |  | Risk cost | Scenario D | 168716.9178 | 174731.0521 | 125586.2049 | 143619.2835 | 149913.3554 | 161391.3204 | 216785.3027 | 232427.0136 | 249338.2497 | 267625.7687 | 287405.5007 | 308701.5422
|  |  | Annualised cost | Scenario D | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802 | 133455.1802
Charts
End