## Inputs
CitiPower - J18 AR Circuit Breaker Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | J18 AR Circuit Breaker Risk Monetisation Model
|  | Model start & timeline |  | 2019
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 25
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex, real $2019 |  | 1275000 |  |  |  |  | 0 | 0 | 1275000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 1321215.9292 |  |  |  |  | 0 | 0 | 1321215.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 4221 | 3999
|  |  | Opex ($2021) | 4374.0019 | 4143.9549
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 14.96% | 16.02% | 17.17% | 18.41% | 19.74% | 21.18% | 22.74% | 24.42% | 26.24% | 28.21% | 30.33% | 32.63%
|  |  | Major | 2 |  |  |  |  | 0.187% | 0.2003% | 0.2146% | 0.2301% | 0.2468% | 0.2648% | 0.2842% | 0.3053% | 0.328% | 0.3526% | 0.3791% | 0.4079%
|  |  | Catastrophic | 3 | bar: 2010 to 2021
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 48218 | 26450 | 20% | 3038.4782
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 39459 | 47770 | 40% | 8981.5763
|  |  | Industrial | 1121 | 47070 | 80% | 502.8414
|  |  | Total | 88798 | 36184.2384 | 32.72% | 12522.8959
Asset information
|  | Assets at risk |  | 1 |  |  | Sections lost
|  | N-rating, MVA |  | 60 |  | Total Sections | 2
|  |  | N-1 Rating before transfers, MVA | 32.9 |  | Significant | 1
|  |  | N-2 Rating before transfers, MVA | 0 |  | Major | 2
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major
|  |  | Average Consequence Loss Oil | 20 | 100
|  |  | Average Consequences Loss SF6 kgs | 0 | 0
|  |  | Average Consequence Fire | 0.005 | 0.05
|  |  | Average Consequence Waste | 1 | 1
|  |  | Average Consequence Disturbance | 2 | 5
|  |  | Average Cost of Fault (Air Insulated) | 1917.0584 | 3626.8673
|  |  | Average Cost of Fault (SF6 Insulated) | 1917.0584 | 3626.8673
|  |  | Average Cost of Fault (Oil Insulated) | 3989.554 | 13989.3451
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major
|  |  | Switching time only (hours required) | 2 | 2
|  |  | Number of weeks generation required | 2 | 12
|  |  | Max demand load net of transfers, MVA | 1.1104 | 33.8304
|  |  | Number of generators | 2 | 34
|  |  | Generator sites | 1 | 9
|  |  | Number of days to connect all generators | 1 | 3
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major
|  |  | Generator hire | 36268.6726 | 3021180.4248
|  |  | Fuel cost | 51231.6145 | 9364989.6398
|  |  | Fitter cost | 64661.8619 | 2932166.7398
|  |  | Traffic management cost | 145074.6903 | 7834033.2743
|  |  | Transformer hire | 18134.3363 | 799724.2301
|  |  | Earthing and bunding | 2072.4956 | 18652.4602
|  |  | Temporary fencing | 6217.4867 | 335744.2832
|  |  | Miscellaneous materials | 2072.4956 | 18652.4602
|  |  | Installation & removal of step-down transformers | 2590.6195 | 23315.5752
|  |  | Council permits | 4144.9912 | 37304.9204
|  |  | Crane hire | 2590.6195 | 23315.5752
|  |  | Cable hire | 3108.7434 | 27978.6903
|  |  | Total | 0 | 0
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major
|  |  | Minor | 0.4284% | 1.5%
|  |  | Serious | 0.08569% | 0.2999%
|  |  | Fataility | 0.01714% | 0.05998%
|  |  | Value of event | 4243.0068 | 14850.5238
|  |  | Weighted likelyhood of consequence | 0.02679% | 0.09377%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 35.437 | 35.13 | 36.846 | 35.554 | 36.66 | 37.007 | 37.929 | 37.929 | 37.929 | 37.929 | 37.929 | 37.929
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 30.433 | 30.238 | 31.823 | 32.009 | 32.429 | 32.225 | 33.403 | 33.403 | 33.403 | 33.403 | 33.403 | 33.403
|  |  | Selected | 70% |  |  |  |  | 31.9342 | 31.7056 | 33.3299 | 33.0725 | 33.6983 | 33.6596 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0.4299 | 0.1725 | 0.7983 | 0.7596 | 1.8608 | 1.8608 | 1.8608 | 1.8608 | 1.8608 | 1.8608
|  |  | N-2 | [5 empty] | 31.9342 | 31.7056 | 33.3299 | 33.0725 | 33.6983 | 33.6596 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608
|  |  | N-3 | [5 empty] | 31.9342 | 31.7056 | 33.3299 | 33.0725 | 33.6983 | 33.6596 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608
|  |  | N-4 | [5 empty] | 31.9342 | 31.7056 | 33.3299 | 33.0725 | 33.6983 | 33.6596 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608
End

## Base Case
CitiPower - J18 AR Circuit Breaker Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 799817.322 | 0 | 0 | 0 | 0 | 100% | 799817.322 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 233155.7522 | 0 | 100% | 233155.7522 | 233155.7522
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 13989.3451 | 100% | 13989.3451 | 13989.3451
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 399908.661 | 0 | 0 | 0 | 0 | 100% | 399908.661 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 77718.5841 | 0 | 100% | 77718.5841 | 77718.5841
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3989.554 | 100% | 3989.554 | 3989.554
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 399908.661 | 4243.0068 | 51812.3894 | 77718.5841 | 3989.554 | 100% | 537672.1952 | 137763.5342
[5 empty] | 2 | Major |  | 799817.322 | 14850.5238 | 51812.3894 | 233155.7522 | 13989.3451 | 100% | 1113625.3325 | 313808.0105
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 1651297.5277; 2026: 451571.5447
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 60
|  |  | N-1 Rating before transfers, MVA |  |  | 32.9
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 35.437 | 35.13 | 36.846 | 35.554 | 36.66 | 37.007 | 37.929 | 37.929 | 37.929 | 37.929 | 37.929 | 37.929
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 30.433 | 30.238 | 31.823 | 32.009 | 32.429 | 32.225 | 33.403 | 33.403 | 33.403 | 33.403 | 33.403 | 33.403
|  |  | Selected |  |  | 70% |  | 31.9342 | 31.7056 | 33.3299 | 33.0725 | 33.6983 | 33.6596 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0.4299 | 0.1725 | 0.7983 | 0.7596 | 1.8608 | 1.8608 | 1.8608 | 1.8608 | 1.8608 | 1.8608
|  |  | N-2 |  |  |  |  | 31.9342 | 31.7056 | 33.3299 | 33.0725 | 33.6983 | 33.6596 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608
|  |  | N-3 |  |  |  |  | 31.9342 | 31.7056 | 33.3299 | 33.0725 | 33.6983 | 33.6596 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608
|  |  | N-4 |  |  |  |  | 31.9342 | 31.7056 | 33.3299 | 33.0725 | 33.6983 | 33.6596 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608 | 34.7608
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Adjustment | bar: 2019 to 2030
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Adjustment | bar: 2019 to 2030
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Adjustment | bar: 2019 to 2030
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 399908.661 | 397045.927 | 417386.8667 | 414163.4733 | 422000.3016 | 421515.6655 | 435305.8784 | 435305.8784 | 435305.8784 | 435305.8784 | 435305.8784 | 435305.8784
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 799817.322 | 794091.854 | 834773.7335 | 828326.9467 | 844000.6031 | 843031.331 | 870611.7568 | 870611.7568 | 870611.7568 | 870611.7568 | 870611.7568 | 870611.7568
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 14.96% | 16.02% | 17.17% | 18.41% | 19.74% | 21.18% | 22.74% | 24.42% | 26.24% | 28.21% | 30.33% | 32.63%
|  |  | Major |  |  |  |  | 0.187% | 0.2003% | 0.2146% | 0.2301% | 0.2468% | 0.2648% | 0.2842% | 0.3053% | 0.328% | 0.3526% | 0.3791% | 0.4079%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 59840.3725 | 63624.8336 | 71663.5402 | 76229.0783 | 83303.1853 | 89282.8236 | 98981.5649 | 106305.3357 | 114221.0011 | 122778.4309 | 132031.8029 | 142039.9821
|  |  | Network Performance |  |  | Major |  | 1496.0093 | 1590.6208 | 1791.5885 | 1905.727 | 2082.5796 | 2232.0706 | 2474.5391 | 2657.6334 | 2855.525 | 3069.4608 | 3300.7951 | 3550.9996
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 20614.2602 | 22075.9901 | 23653.4097 | 25356.1405 | 27194.628 | 29180.214 | 31325.2149 | 33643.0071 | 36148.1192 | 38856.3339 | 41784.7971 | 44952.138
|  |  | Other major risks |  |  | Major |  | 586.9587 | 628.5791 | 673.4937 | 721.9763 | 774.3243 | 830.8607 | 891.9363 | 957.9318 | 1029.2609 | 1106.373 | 1189.7564 | 1279.9415
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 4374.0019 | 4374.0019 | 4374.0019 | 4374.0019 | 4374.0019 | 4374.0019 | 4374.0019 | 4374.0019 | 4374.0019 | 4374.0019 | 4374.0019 | 4374.0019
|  |  | Subtotal |  |  |  |  | 86911.6026 | 92294.0255 | 102156.0341 | 108586.9239 | 117728.7192 | 125899.9709 | 138047.2572 | 147937.9098 | 158627.9082 | 170184.6005 | 182681.1534 | 196197.063
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 1321215.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 73776.6625
|  |  | Post-replacement opex |  |  | 4143.9549
|  |  | Total annuity |  |  | 77920.6174
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 86911.6026 | 92294.0255 | 102156.0341 | 108586.9239 | 117728.7192 | 125899.9709 | 138047.2572 | 147937.9098 | 158627.9082 | 170184.6005 | 182681.1534 | 196197.063
|  |  | Annualised cost |  |  |  |  | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - J18 AR Circuit Breaker Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 683843.8103 | 0 | 0 | 0 | 0 | 100% | 683843.8103 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 256471.3274 | 0 | 100% | 256471.3274 | 256471.3274
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 12590.4106 | 100% | 12590.4106 | 12590.4106
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 341921.9051 | 0 | 0 | 0 | 0 | 100% | 341921.9051 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 85490.4425 | 0 | 100% | 85490.4425 | 85490.4425
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3590.5986 | 100% | 3590.5986 | 3590.5986
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 341921.9051 | 4243.0068 | 56993.6283 | 85490.4425 | 3590.5986 | 100% | 492239.5813 | 150317.6762
[5 empty] | 2 | Major |  | 683843.8103 | 14850.5238 | 56993.6283 | 256471.3274 | 12590.4106 | 100% | 1024749.7004 | 340905.8902
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 1516989.2817; 2026: 491223.5663
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 60
|  |  | N-1 Rating before transfers, MVA |  |  | 32.9
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 33.6651 | 33.3735 | 35.0037 | 33.7763 | 34.827 | 35.1566 | 36.0326 | 36.0326 | 36.0326 | 36.0326 | 36.0326 | 36.0326
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 28.9113 | 28.7261 | 30.2318 | 30.4085 | 30.8075 | 30.6137 | 31.7328 | 31.7328 | 31.7328 | 31.7328 | 31.7328 | 31.7328
|  |  | Selected |  |  | 70% |  | 30.3375 | 30.1203 | 31.6634 | 31.4189 | 32.0134 | 31.9766 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.12276 | 0.12276 | 0.12276 | 0.12276 | 0.12276 | 0.12276
|  |  | N-2 |  |  |  |  | 30.3375 | 30.1203 | 31.6634 | 31.4189 | 32.0134 | 31.9766 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228
|  |  | N-3 |  |  |  |  | 30.3375 | 30.1203 | 31.6634 | 31.4189 | 32.0134 | 31.9766 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228
|  |  | N-4 |  |  |  |  | 30.3375 | 30.1203 | 31.6634 | 31.4189 | 32.0134 | 31.9766 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Unserved energy day 2 | bar: 2019 to 2030
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Unserved energy day 2 | bar: 2019 to 2030
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Unserved energy day 2 | bar: 2019 to 2030
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 341921.9051 | 339474.2676 | 356865.7711 | 354109.7697 | 360810.2578 | 360395.894 | 372186.526 | 372186.526 | 372186.526 | 372186.526 | 372186.526 | 372186.526
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 683843.8103 | 678948.5351 | 713731.5421 | 708219.5394 | 721620.5157 | 720791.788 | 744373.0521 | 744373.0521 | 744373.0521 | 744373.0521 | 744373.0521 | 744373.0521
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 13.47% | 14.42% | 15.45% | 16.56% | 17.77% | 19.06% | 20.46% | 21.98% | 23.62% | 25.38% | 27.3% | 29.37%
|  |  | Major |  |  |  |  | 0.1683% | 0.1803% | 0.1932% | 0.2071% | 0.2221% | 0.2383% | 0.2558% | 0.2747% | 0.2952% | 0.3173% | 0.3412% | 0.3671%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 46047.1666 | 48959.3094 | 55145.0942 | 58658.2757 | 64101.8011 | 68703.1328 | 76166.3142 | 81801.9558 | 87893.0604 | 94478.0026 | 101598.4723 | 109299.7662
|  |  | Network Performance |  |  | Major |  | 1151.1792 | 1223.9827 | 1378.6274 | 1466.4569 | 1602.545 | 1717.5783 | 1904.1579 | 2045.0489 | 2197.3265 | 2361.9501 | 2539.9618 | 2732.4942
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 20243.5205 | 21678.9616 | 23228.012 | 24900.1198 | 26705.5428 | 28655.4188 | 30761.8427 | 33037.9502 | 35498.0088 | 38157.5173 | 41033.3131 | 44143.6906
|  |  | Other major risks |  |  | Major |  | 573.8792 | 614.5722 | 658.4859 | 705.8882 | 757.0697 | 812.3463 | 872.0609 | 936.5858 | 1006.3255 | 1081.7193 | 1163.2446 | 1251.42
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021
|  |  | Subtotal |  |  |  |  | 72827.1476 | 77288.2281 | 85221.6216 | 90542.1427 | 97978.3607 | 104699.8783 | 114515.7777 | 122632.9427 | 131406.1233 | 140890.5913 | 151146.394 | 162238.7731
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 1453337.5221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 81154.3287
|  |  | Post-replacement opex |  |  | 4558.3504
|  |  | Total annuity |  |  | 85712.6791
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 72827.1476 | 77288.2281 | 85221.6216 | 90542.1427 | 97978.3607 | 104699.8783 | 114515.7777 | 122632.9427 | 131406.1233 | 140890.5913 | 151146.394 | 162238.7731
|  |  | Annualised cost |  |  |  |  | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
CitiPower - J18 AR Circuit Breaker Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 683843.8103 | 0 | 0 | 0 | 0 | 100% | 683843.8103 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 209840.177 | 0 | 100% | 209840.177 | 209840.177
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 12590.4106 | 100% | 12590.4106 | 12590.4106
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 341921.9051 | 0 | 0 | 0 | 0 | 100% | 341921.9051 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 69946.7257 | 0 | 100% | 69946.7257 | 69946.7257
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3590.5986 | 100% | 3590.5986 | 3590.5986
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 341921.9051 | 4243.0068 | 46631.1504 | 69946.7257 | 3590.5986 | 100% | 466333.3866 | 124411.4815
[5 empty] | 2 | Major |  | 683843.8103 | 14850.5238 | 46631.1504 | 209840.177 | 12590.4106 | 100% | 967756.0721 | 283912.2618
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 1434089.4587; 2026: 408323.7433
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 60
|  |  | N-1 Rating before transfers, MVA |  |  | 32.9
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 33.6651 | 33.3735 | 35.0037 | 33.7763 | 34.827 | 35.1566 | 36.0326 | 36.0326 | 36.0326 | 36.0326 | 36.0326 | 36.0326
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 28.9113 | 28.7261 | 30.2318 | 30.4085 | 30.8075 | 30.6137 | 31.7328 | 31.7328 | 31.7328 | 31.7328 | 31.7328 | 31.7328
|  |  | Selected |  |  | 70% |  | 30.3375 | 30.1203 | 31.6634 | 31.4189 | 32.0134 | 31.9766 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.12276 | 0.12276 | 0.12276 | 0.12276 | 0.12276 | 0.12276
|  |  | N-2 |  |  |  |  | 30.3375 | 30.1203 | 31.6634 | 31.4189 | 32.0134 | 31.9766 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228
|  |  | N-3 |  |  |  |  | 30.3375 | 30.1203 | 31.6634 | 31.4189 | 32.0134 | 31.9766 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228
|  |  | N-4 |  |  |  |  | 30.3375 | 30.1203 | 31.6634 | 31.4189 | 32.0134 | 31.9766 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228 | 33.0228
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Unserved energy day 2 | bar: 2019 to 2030
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Unserved energy day 2 | bar: 2019 to 2030
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Unserved energy day 2 | bar: 2019 to 2030
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 341921.9051 | 339474.2676 | 356865.7711 | 354109.7697 | 360810.2578 | 360395.894 | 372186.526 | 372186.526 | 372186.526 | 372186.526 | 372186.526 | 372186.526
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 683843.8103 | 678948.5351 | 713731.5421 | 708219.5394 | 721620.5157 | 720791.788 | 744373.0521 | 744373.0521 | 744373.0521 | 744373.0521 | 744373.0521 | 744373.0521
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 13.47% | 14.42% | 15.45% | 16.56% | 17.77% | 19.06% | 20.46% | 21.98% | 23.62% | 25.38% | 27.3% | 29.37%
|  |  | Major |  |  |  |  | 0.1683% | 0.1803% | 0.1932% | 0.2071% | 0.2221% | 0.2383% | 0.2558% | 0.2747% | 0.2952% | 0.3173% | 0.3412% | 0.3671%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 46047.1666 | 48959.3094 | 55145.0942 | 58658.2757 | 64101.8011 | 68703.1328 | 76166.3142 | 81801.9558 | 87893.0604 | 94478.0026 | 101598.4723 | 109299.7662
|  |  | Network Performance |  |  | Major |  | 1151.1792 | 1223.9827 | 1378.6274 | 1466.4569 | 1602.545 | 1717.5783 | 1904.1579 | 2045.0489 | 2197.3265 | 2361.9501 | 2539.9618 | 2732.4942
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 16754.692 | 17942.745 | 19224.8274 | 20608.7592 | 22103.0302 | 23716.8588 | 25460.2554 | 27344.0917 | 29380.1766 | 31581.3374 | 33961.5101 | 36535.8359
|  |  | Other major risks |  |  | Major |  | 477.9364 | 511.8263 | 548.3984 | 587.8758 | 630.5006 | 676.5359 | 726.2672 | 780.0047 | 838.0851 | 900.8743 | 968.77 | 1042.204
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017
|  |  | Subtotal |  |  |  |  | 68367.576 | 72574.4652 | 80233.5491 | 85257.9693 | 92374.4787 | 98750.7075 | 108193.5964 | 115907.7028 | 124245.2502 | 133258.7661 | 143005.316 | 153546.902
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 1189094.3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 66398.9962
|  |  | Post-replacement opex |  |  | 3729.5594
|  |  | Total annuity |  |  | 70128.5556
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 68367.576 | 72574.4652 | 80233.5491 | 85257.9693 | 92374.4787 | 98750.7075 | 108193.5964 | 115907.7028 | 124245.2502 | 133258.7661 | 143005.316 | 153546.902
|  |  | Annualised cost |  |  |  |  | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556
|  |  | Feasible ? |  |  |  |  | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - J18 AR Circuit Breaker Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 923789.0069 | 0 | 0 | 0 | 0 | 100% | 923789.0069 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 256471.3274 | 0 | 100% | 256471.3274 | 256471.3274
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 15388.2796 | 100% | 15388.2796 | 15388.2796
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 461894.5034 | 0 | 0 | 0 | 0 | 100% | 461894.5034 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 85490.4425 | 0 | 100% | 85490.4425 | 85490.4425
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 4388.5094 | 100% | 4388.5094 | 4388.5094
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 461894.5034 | 4243.0068 | 56993.6283 | 85490.4425 | 4388.5094 | 100% | 613010.0904 | 151115.587
[5 empty] | 2 | Major |  | 923789.0069 | 14850.5238 | 56993.6283 | 256471.3274 | 15388.2796 | 100% | 1267492.766 | 343703.7592
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 1880502.8565; 2026: 494819.3462
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 60
|  |  | N-1 Rating before transfers, MVA |  |  | 32.9
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 37.2088 | 36.8865 | 38.6883 | 37.3317 | 38.493 | 38.8573 | 39.8255 | 39.8255 | 39.8255 | 39.8255 | 39.8255 | 39.8255
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 31.9547 | 31.7499 | 33.4141 | 33.6095 | 34.0505 | 33.8362 | 35.0731 | 35.0731 | 35.0731 | 35.0731 | 35.0731 | 35.0731
|  |  | Selected |  |  | 70% |  | 33.5309 | 33.2909 | 34.9964 | 34.7261 | 35.3832 | 35.3426 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0.63091 | 0.39088 | 2.0964 | 1.8261 | 2.4832 | 2.4426 | 3.5988 | 3.5988 | 3.5988 | 3.5988 | 3.5988 | 3.5988
|  |  | N-2 |  |  |  |  | 33.5309 | 33.2909 | 34.9964 | 34.7261 | 35.3832 | 35.3426 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988
|  |  | N-3 |  |  |  |  | 33.5309 | 33.2909 | 34.9964 | 34.7261 | 35.3832 | 35.3426 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988
|  |  | N-4 |  |  |  |  | 33.5309 | 33.2909 | 34.9964 | 34.7261 | 35.3832 | 35.3426 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 461894.5034 | 458588.0457 | 482081.8311 | 478358.8117 | 487410.3483 | 486850.5936 | 502778.2896 | 502778.2896 | 502778.2896 | 502778.2896 | 502778.2896 | 502778.2896
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 923789.0069 | 917176.0913 | 964163.6621 | 956717.6234 | 974820.6966 | 973701.1873 | 1005556.5791 | 1005556.5791 | 1005556.5791 | 1005556.5791 | 1005556.5791 | 1005556.5791
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 16.46% | 17.63% | 18.89% | 20.25% | 21.71% | 23.3% | 25.01% | 26.86% | 28.86% | 31.03% | 33.36% | 35.89%
|  |  | Major |  |  |  |  | 0.2057% | 0.2203% | 0.2361% | 0.2531% | 0.2714% | 0.2912% | 0.3127% | 0.3358% | 0.3608% | 0.3878% | 0.417% | 0.4487%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 76027.1932 | 80835.351 | 91048.5279 | 96849.0439 | 105836.6969 | 113433.8274 | 125756.0783 | 135060.929 | 145117.7819 | 155989.9964 | 167746.4056 | 180461.7972
|  |  | Network Performance |  |  | Major |  | 1900.6798 | 2020.8838 | 2276.2132 | 2421.2261 | 2645.9174 | 2835.8457 | 3143.902 | 3376.5232 | 3627.9445 | 3899.7499 | 4193.6601 | 4511.5449
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 24873.4156 | 26637.1565 | 28540.4901 | 30595.0257 | 32813.3669 | 35209.1989 | 37797.383 | 40594.059 | 43616.7576 | 46884.5222 | 50418.0413 | 54239.7931
|  |  | Other major risks |  |  | Major |  | 707.1645 | 757.3086 | 811.4214 | 869.8329 | 932.9016 | 1001.0164 | 1074.5998 | 1154.1108 | 1240.0478 | 1332.9521 | 1433.4119 | 1542.0663
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021 | 4811.4021
|  |  | Subtotal |  |  |  |  | 108319.8553 | 115062.102 | 127488.0547 | 135546.5308 | 147040.2849 | 157291.2905 | 172583.3651 | 184997.0241 | 198413.934 | 212918.6227 | 228602.921 | 245566.6037
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 1453337.5221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 81154.3287
|  |  | Post-replacement opex |  |  | 4558.3504
|  |  | Total annuity |  |  | 85712.6791
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 108319.8553 | 115062.102 | 127488.0547 | 135546.5308 | 147040.2849 | 157291.2905 | 172583.3651 | 184997.0241 | 198413.934 | 212918.6227 | 228602.921 | 245566.6037
|  |  | Annualised cost |  |  |  |  | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - J18 AR Circuit Breaker Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 923789.0069 | 0 | 0 | 0 | 0 | 100% | 923789.0069 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 209840.177 | 0 | 100% | 209840.177 | 209840.177
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 15388.2796 | 100% | 15388.2796 | 15388.2796
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 461894.5034 | 0 | 0 | 0 | 0 | 100% | 461894.5034 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 69946.7257 | 0 | 100% | 69946.7257 | 69946.7257
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 4388.5094 | 100% | 4388.5094 | 4388.5094
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 461894.5034 | 4243.0068 | 46631.1504 | 69946.7257 | 4388.5094 | 100% | 587103.8957 | 125209.3923
[5 empty] | 2 | Major |  | 923789.0069 | 14850.5238 | 46631.1504 | 209840.177 | 15388.2796 | 100% | 1210499.1377 | 286710.1309
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 1797603.0334; 2026: 411919.5231
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 60
|  |  | N-1 Rating before transfers, MVA |  |  | 32.9
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 37.2088 | 36.8865 | 38.6883 | 37.3317 | 38.493 | 38.8573 | 39.8255 | 39.8255 | 39.8255 | 39.8255 | 39.8255 | 39.8255
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 31.9547 | 31.7499 | 33.4141 | 33.6095 | 34.0505 | 33.8362 | 35.0731 | 35.0731 | 35.0731 | 35.0731 | 35.0731 | 35.0731
|  |  | Selected |  |  | 70% |  | 33.5309 | 33.2909 | 34.9964 | 34.7261 | 35.3832 | 35.3426 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0.63091 | 0.39088 | 2.0964 | 1.8261 | 2.4832 | 2.4426 | 3.5988 | 3.5988 | 3.5988 | 3.5988 | 3.5988 | 3.5988
|  |  | N-2 |  |  |  |  | 33.5309 | 33.2909 | 34.9964 | 34.7261 | 35.3832 | 35.3426 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988
|  |  | N-3 |  |  |  |  | 33.5309 | 33.2909 | 34.9964 | 34.7261 | 35.3832 | 35.3426 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988
|  |  | N-4 |  |  |  |  | 33.5309 | 33.2909 | 34.9964 | 34.7261 | 35.3832 | 35.3426 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988 | 36.4988
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 461894.5034 | 458588.0457 | 482081.8311 | 478358.8117 | 487410.3483 | 486850.5936 | 502778.2896 | 502778.2896 | 502778.2896 | 502778.2896 | 502778.2896 | 502778.2896
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 923789.0069 | 917176.0913 | 964163.6621 | 956717.6234 | 974820.6966 | 973701.1873 | 1005556.5791 | 1005556.5791 | 1005556.5791 | 1005556.5791 | 1005556.5791 | 1005556.5791
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 16.46% | 17.63% | 18.89% | 20.25% | 21.71% | 23.3% | 25.01% | 26.86% | 28.86% | 31.03% | 33.36% | 35.89%
|  |  | Major |  |  |  |  | 0.2057% | 0.2203% | 0.2361% | 0.2531% | 0.2714% | 0.2912% | 0.3127% | 0.3358% | 0.3608% | 0.3878% | 0.417% | 0.4487%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 76027.1932 | 80835.351 | 91048.5279 | 96849.0439 | 105836.6969 | 113433.8274 | 125756.0783 | 135060.929 | 145117.7819 | 155989.9964 | 167746.4056 | 180461.7972
|  |  | Network Performance |  |  | Major |  | 1900.6798 | 2020.8838 | 2276.2132 | 2421.2261 | 2645.9174 | 2835.8457 | 3143.902 | 3376.5232 | 3627.9445 | 3899.7499 | 4193.6601 | 4511.5449
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 20609.2919 | 22070.6695 | 23647.709 | 25350.0294 | 27188.0738 | 29173.1812 | 31317.6652 | 33634.8987 | 36139.4071 | 38846.9691 | 41774.7264 | 44941.304
|  |  | Other major risks |  |  | Major |  | 589.9011 | 631.7302 | 676.8699 | 725.5956 | 778.206 | 835.0259 | 896.4076 | 962.7339 | 1034.4206 | 1111.9193 | 1195.7207 | 1286.3579
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017 | 3936.6017
|  |  | Subtotal |  |  |  |  | 103063.6678 | 109495.2362 | 121585.9217 | 129282.4967 | 140385.4959 | 150214.4819 | 165050.6547 | 176971.6865 | 189856.1559 | 203785.2364 | 218847.1146 | 235137.6057
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 1189094.3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 66398.9962
|  |  | Post-replacement opex |  |  | 3729.5594
|  |  | Total annuity |  |  | 70128.5556
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 103063.6678 | 109495.2362 | 121585.9217 | 129282.4967 | 140385.4959 | 150214.4819 | 165050.6547 | 176971.6865 | 189856.1559 | 203785.2364 | 218847.1146 | 235137.6057
|  |  | Annualised cost |  |  |  |  | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - J18 AR Circuit Breaker Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 86911.6026 | 92294.0255 | 102156.0341 | 108586.9239 | 117728.7192 | 125899.9709 | 138047.2572 | 147937.9098 | 158627.9082 | 170184.6005 | 182681.1534 | 196197.063
|  |  | Annualised cost | Scenario Base case | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174 | 77920.6174
|  |  | Risk cost | Scenario A | 72827.1476 | 77288.2281 | 85221.6216 | 90542.1427 | 97978.3607 | 104699.8783 | 114515.7777 | 122632.9427 | 131406.1233 | 140890.5913 | 151146.394 | 162238.7731
|  |  | Annualised cost | Scenario A | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791
|  |  | Risk cost | Scenario B | 68367.576 | 72574.4652 | 80233.5491 | 85257.9693 | 92374.4787 | 98750.7075 | 108193.5964 | 115907.7028 | 124245.2502 | 133258.7661 | 143005.316 | 153546.902
|  |  | Annualised cost | Scenario B | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556
|  |  | Risk cost | Scenario C | 108319.8553 | 115062.102 | 127488.0547 | 135546.5308 | 147040.2849 | 157291.2905 | 172583.3651 | 184997.0241 | 198413.934 | 212918.6227 | 228602.921 | 245566.6037
|  |  | Annualised cost | Scenario C | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791 | 85712.6791
|  |  | Risk cost | Scenario D | 103063.6678 | 109495.2362 | 121585.9217 | 129282.4967 | 140385.4959 | 150214.4819 | 165050.6547 | 176971.6865 | 189856.1559 | 203785.2364 | 218847.1146 | 235137.6057
|  |  | Annualised cost | Scenario D | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556 | 70128.5556
Charts
End