## Inputs
CitiPower - J18 AP Circuit Breaker Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | J18 AP Circuit Breaker Risk Monetisation Model
|  | Model start & timeline |  | 2019
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 25
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex, real $2019 |  | 1575000 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1575000 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 1632090.2655 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1632090.2655 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 10948 | 9782
|  |  | Opex ($2021) | 11344.8408 | 10136.5759
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 24.11% | 25.86% | 27.74% | 29.78% | 31.98% | 34.35% | 36.92% | 39.7% | 42.7% | 45.94% | 49.45% | 53.25%
|  |  | Major | 2 |  |  |  |  | 0.3014% | 0.3232% | 0.3468% | 0.3722% | 0.3997% | 0.4294% | 0.4615% | 0.4962% | 0.5337% | 0.5743% | 0.6182% | 0.6656%
|  |  | Catastrophic | 3 | bar: 2010 to 2021
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 66398 | 26450 | 20% | 1902.424
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 125231 | 47770 | 40% | 12960.5587
|  |  | Industrial | 3669 | 47070 | 80% | 748.3048
|  |  | Total | 195298 | 40508.4118 | 36.43% | 15611.2875
Asset information
|  | Assets at risk |  | 1 |  |  | Sections lost
|  | N-rating, MVA |  | 87 |  | Total Sections | 3
|  |  | N-1 Rating before transfers, MVA | 70 |  | Significant | 1
|  |  | N-2 Rating before transfers, MVA | 0 |  | Major | 3
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major
|  |  | Average Consequence Loss Oil | 20 | 100
|  |  | Average Consequences Loss SF6 kgs | 0 | 0
|  |  | Average Consequence Fire | 0.005 | 0.05
|  |  | Average Consequence Waste | 1 | 1
|  |  | Average Consequence Disturbance | 2 | 5
|  |  | Average Cost of Fault (Air Insulated) | 1917.0584 | 3626.8673
|  |  | Average Cost of Fault (SF6 Insulated) | 1917.0584 | 3626.8673
|  |  | Average Cost of Fault (Oil Insulated) | 3989.554 | 13989.3451
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major
|  |  | Switching time only (hours required) | 2 | 2
|  |  | Number of weeks generation required | 2 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 57.6427
|  |  | Number of generators | 0 | 58
|  |  | Generator sites | 0 | 15
|  |  | Number of days to connect all generators | 0 | 5
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major
|  |  | Generator hire | 0 | 5223897.8053
|  |  | Fuel cost | 0 | 17768583.2518
|  |  | Fitter cost | 0 | 4886944.5664
|  |  | Traffic management cost | 0 | 13056722.1239
|  |  | Transformer hire | 0 | 1351008.0531
|  |  | Earthing and bunding | 0 | 31087.4336
|  |  | Temporary fencing | 0 | 559573.8053
|  |  | Miscellaneous materials | 0 | 31087.4336
|  |  | Installation & removal of step-down transformers | 0 | 38859.292
|  |  | Council permits | 0 | 62174.8673
|  |  | Crane hire | 0 | 38859.292
|  |  | Cable hire | 0 | 46631.1504
|  |  | Total | 0 | 0
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major
|  |  | Minor | 0.4284% | 1.5%
|  |  | Serious | 0.08569% | 0.2999%
|  |  | Fataility | 0.01714% | 0.05998%
|  |  | Value of event | 4243.0068 | 14850.5238
|  |  | Weighted likelyhood of consequence | 0.02679% | 0.09377%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 57.517 | 57.959 | 60.644 | 63.062 | 65.878 | 67.934 | 72.836 | 72.836 | 72.836 | 72.836 | 72.836 | 72.836
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 49.68 | 49.22 | 49.958 | 51.467 | 52.884 | 53.311 | 55.749 | 55.749 | 55.749 | 55.749 | 55.749 | 55.749
|  |  | Selected | 70% |  |  |  |  | 52.0311 | 51.8417 | 53.1638 | 54.9455 | 56.7822 | 57.6979 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 52.0311 | 51.8417 | 53.1638 | 54.9455 | 56.7822 | 57.6979 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751
|  |  | N-3 | [5 empty] | 52.0311 | 51.8417 | 53.1638 | 54.9455 | 56.7822 | 57.6979 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751
|  |  | N-4 | [5 empty] | 52.0311 | 51.8417 | 53.1638 | 54.9455 | 56.7822 | 57.6979 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751
End

## Base Case
CitiPower - J18 AP Circuit Breaker Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1624544.9252 | 0 | 0 | 0 | 0 | 100% | 1624544.9252 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 233155.7522 | 0 | 100% | 233155.7522 | 233155.7522
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 13989.3451 | 100% | 13989.3451 | 13989.3451
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 541514.9751 | 0 | 0 | 0 | 0 | 100% | 541514.9751 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 77718.5841 | 0 | 100% | 77718.5841 | 77718.5841
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3989.554 | 100% | 3989.554 | 3989.554
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 541514.9751 | 4243.0068 | 51812.3894 | 77718.5841 | 3989.554 | 100% | 679278.5093 | 137763.5342
[5 empty] | 2 | Major |  | 1624544.9252 | 14850.5238 | 51812.3894 | 233155.7522 | 13989.3451 | 100% | 1938352.9357 | 313808.0105
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2617631.445; 2026: 451571.5447
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 87
|  |  | N-1 Rating before transfers, MVA |  |  | 70
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 57.517 | 57.959 | 60.644 | 63.062 | 65.878 | 67.934 | 72.836 | 72.836 | 72.836 | 72.836 | 72.836 | 72.836
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 49.68 | 49.22 | 49.958 | 51.467 | 52.884 | 53.311 | 55.749 | 55.749 | 55.749 | 55.749 | 55.749 | 55.749
|  |  | Selected |  |  | 70% |  | 52.0311 | 51.8417 | 53.1638 | 54.9455 | 56.7822 | 57.6979 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 52.0311 | 51.8417 | 53.1638 | 54.9455 | 56.7822 | 57.6979 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751
|  |  | N-3 |  |  |  |  | 52.0311 | 51.8417 | 53.1638 | 54.9455 | 56.7822 | 57.6979 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751
|  |  | N-4 |  |  |  |  | 52.0311 | 51.8417 | 53.1638 | 54.9455 | 56.7822 | 57.6979 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751 | 60.8751
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Adjustment |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Adjustment |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Adjustment |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 541514.9751 | 539543.7898 | 553303.5787 | 571846.666 | 590962.1672 | 600492.3379 | 633559.1264 | 633559.1264 | 633559.1264 | 633559.1264 | 633559.1264 | 633559.1264
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1624544.9252 | 1618631.3695 | 1659910.736 | 1715539.998 | 1772886.5016 | 1801477.0136 | 1900677.3791 | 1900677.3791 | 1900677.3791 | 1900677.3791 | 1900677.3791 | 1900677.3791
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 24.11% | 25.86% | 27.74% | 29.78% | 31.98% | 34.35% | 36.92% | 39.7% | 42.7% | 45.94% | 49.45% | 53.25%
|  |  | Major |  |  |  |  | 0.3014% | 0.3232% | 0.3468% | 0.3722% | 0.3997% | 0.4294% | 0.4615% | 0.4962% | 0.5337% | 0.5743% | 0.6182% | 0.6656%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 130571.647 | 139516.8044 | 153505.1819 | 170291.2131 | 188979.1262 | 206294.0588 | 233921.5868 | 251505.9779 | 270517.7818 | 291077.2644 | 313315.0555 | 337373.0546
|  |  | Network Performance |  |  | Major |  | 4896.4368 | 5231.8802 | 5756.4443 | 6385.9205 | 7086.7172 | 7736.0272 | 8772.0595 | 9431.4742 | 10144.4168 | 10915.3974 | 11749.3146 | 12651.4895
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 33217.9393 | 35623.2959 | 38220.2776 | 41024.8424 | 44054.3131 | 47327.4959 | 50864.8099 | 54688.4276 | 58822.4274 | 63292.9604 | 68128.4312 | 73359.6951
|  |  | Other major risks |  |  | Major |  | 945.8286 | 1014.3174 | 1088.2623 | 1168.1179 | 1254.3773 | 1347.5761 | 1448.2955 | 1557.167 | 1674.8762 | 1802.1676 | 1939.85 | 2088.802
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 11344.8408 | 11344.8408 | 11344.8408 | 11344.8408 | 11344.8408 | 11344.8408 | 11344.8408 | 11344.8408 | 11344.8408 | 11344.8408 | 11344.8408 | 11344.8408
|  |  | Subtotal |  |  |  |  | 180976.6925 | 192731.1385 | 209915.0069 | 230214.9347 | 252719.3746 | 274049.9988 | 306351.5925 | 328527.8874 | 352504.3429 | 378432.6305 | 406477.492 | 436817.8821
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1632090.2655 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 91135.8772
|  |  | Post-replacement opex |  |  | 10136.5759
|  |  | Total annuity |  |  | 101272.453
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 180976.6925 | 192731.1385 | 209915.0069 | 230214.9347 | 252719.3746 | 274049.9988 | 306351.5925 | 328527.8874 | 352504.3429 | 378432.6305 | 406477.492 | 436817.8821
|  |  | Annualised cost |  |  |  |  | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - J18 AP Circuit Breaker Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1388985.9111 | 0 | 0 | 0 | 0 | 100% | 1388985.9111 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 256471.3274 | 0 | 100% | 256471.3274 | 256471.3274
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 12590.4106 | 100% | 12590.4106 | 12590.4106
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 462995.3037 | 0 | 0 | 0 | 0 | 100% | 462995.3037 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 85490.4425 | 0 | 100% | 85490.4425 | 85490.4425
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3590.5986 | 100% | 3590.5986 | 3590.5986
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 462995.3037 | 4243.0068 | 56993.6283 | 85490.4425 | 3590.5986 | 100% | 613312.9799 | 150317.6762
[5 empty] | 2 | Major |  | 1388985.9111 | 14850.5238 | 56993.6283 | 256471.3274 | 12590.4106 | 100% | 1729891.8012 | 340905.8902
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2343204.7811; 2026: 491223.5663
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 87
|  |  | N-1 Rating before transfers, MVA |  |  | 70
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 54.6412 | 55.0611 | 57.6118 | 59.9089 | 62.5841 | 64.5373 | 69.1942 | 69.1942 | 69.1942 | 69.1942 | 69.1942 | 69.1942
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 47.196 | 46.759 | 47.4601 | 48.8936 | 50.2398 | 50.6454 | 52.9616 | 52.9616 | 52.9616 | 52.9616 | 52.9616 | 52.9616
|  |  | Selected |  |  | 70% |  | 49.4295 | 49.2496 | 50.5056 | 52.1982 | 53.9431 | 54.813 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 49.4295 | 49.2496 | 50.5056 | 52.1982 | 53.9431 | 54.813 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313
|  |  | N-3 |  |  |  |  | 49.4295 | 49.2496 | 50.5056 | 52.1982 | 53.9431 | 54.813 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313
|  |  | N-4 |  |  |  |  | 49.4295 | 49.2496 | 50.5056 | 52.1982 | 53.9431 | 54.813 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 462995.3037 | 461309.9403 | 473074.5598 | 488928.8994 | 505272.653 | 513420.9489 | 541693.053 | 541693.053 | 541693.053 | 541693.053 | 541693.053 | 541693.053
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1388985.9111 | 1383929.8209 | 1419223.6793 | 1466786.6983 | 1515817.9589 | 1540262.8466 | 1625079.1591 | 1625079.1591 | 1625079.1591 | 1625079.1591 | 1625079.1591 | 1625079.1591
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 21.7% | 23.27% | 24.97% | 26.8% | 28.78% | 30.92% | 33.23% | 35.73% | 38.43% | 41.35% | 44.51% | 47.93%
|  |  | Major |  |  |  |  | 0.2713% | 0.2909% | 0.3121% | 0.335% | 0.3598% | 0.3865% | 0.4154% | 0.4466% | 0.4804% | 0.5169% | 0.5563% | 0.5991%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 100474.8824 | 107358.181 | 118122.2375 | 131039.0885 | 145419.4376 | 158743.2783 | 180002.661 | 193533.85 | 208163.4331 | 223983.9549 | 241095.9352 | 259608.5655
|  |  | Network Performance |  |  | Major |  | 3767.8081 | 4025.9318 | 4429.5839 | 4913.9658 | 5453.2289 | 5952.8729 | 6750.0998 | 7257.5194 | 7806.1287 | 8399.3983 | 9041.0976 | 9735.3212
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 32620.5271 | 34982.6242 | 37532.9002 | 40287.026 | 43262.0127 | 46476.3285 | 49950.0253 | 53704.8766 | 57764.528 | 62154.6601 | 66903.1669 | 72040.3484
|  |  | Other major risks |  |  | Major |  | 924.7523 | 991.7149 | 1064.0122 | 1142.0883 | 1226.4255 | 1317.5475 | 1416.0226 | 1522.4681 | 1637.5542 | 1762.0092 | 1896.6236 | 2042.2564
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249
|  |  | Subtotal |  |  |  |  | 150267.2947 | 159837.7767 | 173628.0586 | 189861.4934 | 207840.4296 | 224969.3521 | 250598.1336 | 268498.0389 | 287850.9689 | 308779.3474 | 331416.148 | 355905.8164
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1795299.292 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 100249.4649
|  |  | Post-replacement opex |  |  | 11150.2334
|  |  | Total annuity |  |  | 111399.6983
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 150267.2947 | 159837.7767 | 173628.0586 | 189861.4934 | 207840.4296 | 224969.3521 | 250598.1336 | 268498.0389 | 287850.9689 | 308779.3474 | 331416.148 | 355905.8164
|  |  | Annualised cost |  |  |  |  | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
CitiPower - J18 AP Circuit Breaker Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1388985.9111 | 0 | 0 | 0 | 0 | 100% | 1388985.9111 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 209840.177 | 0 | 100% | 209840.177 | 209840.177
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 12590.4106 | 100% | 12590.4106 | 12590.4106
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 462995.3037 | 0 | 0 | 0 | 0 | 100% | 462995.3037 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 69946.7257 | 0 | 100% | 69946.7257 | 69946.7257
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3590.5986 | 100% | 3590.5986 | 3590.5986
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 462995.3037 | 4243.0068 | 46631.1504 | 69946.7257 | 3590.5986 | 100% | 587406.7852 | 124411.4815
[5 empty] | 2 | Major |  | 1388985.9111 | 14850.5238 | 46631.1504 | 209840.177 | 12590.4106 | 100% | 1672898.1729 | 283912.2618
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2260304.9581; 2026: 408323.7433
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 87
|  |  | N-1 Rating before transfers, MVA |  |  | 70
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 54.6412 | 55.0611 | 57.6118 | 59.9089 | 62.5841 | 64.5373 | 69.1942 | 69.1942 | 69.1942 | 69.1942 | 69.1942 | 69.1942
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 47.196 | 46.759 | 47.4601 | 48.8936 | 50.2398 | 50.6454 | 52.9616 | 52.9616 | 52.9616 | 52.9616 | 52.9616 | 52.9616
|  |  | Selected |  |  | 70% |  | 49.4295 | 49.2496 | 50.5056 | 52.1982 | 53.9431 | 54.813 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 49.4295 | 49.2496 | 50.5056 | 52.1982 | 53.9431 | 54.813 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313
|  |  | N-3 |  |  |  |  | 49.4295 | 49.2496 | 50.5056 | 52.1982 | 53.9431 | 54.813 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313
|  |  | N-4 |  |  |  |  | 49.4295 | 49.2496 | 50.5056 | 52.1982 | 53.9431 | 54.813 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313 | 57.8313
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 462995.3037 | 461309.9403 | 473074.5598 | 488928.8994 | 505272.653 | 513420.9489 | 541693.053 | 541693.053 | 541693.053 | 541693.053 | 541693.053 | 541693.053
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1388985.9111 | 1383929.8209 | 1419223.6793 | 1466786.6983 | 1515817.9589 | 1540262.8466 | 1625079.1591 | 1625079.1591 | 1625079.1591 | 1625079.1591 | 1625079.1591 | 1625079.1591
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 21.7% | 23.27% | 24.97% | 26.8% | 28.78% | 30.92% | 33.23% | 35.73% | 38.43% | 41.35% | 44.51% | 47.93%
|  |  | Major |  |  |  |  | 0.2713% | 0.2909% | 0.3121% | 0.335% | 0.3598% | 0.3865% | 0.4154% | 0.4466% | 0.4804% | 0.5169% | 0.5563% | 0.5991%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 100474.8824 | 107358.181 | 118122.2375 | 131039.0885 | 145419.4376 | 158743.2783 | 180002.661 | 193533.85 | 208163.4331 | 223983.9549 | 241095.9352 | 259608.5655
|  |  | Network Performance |  |  | Major |  | 3767.8081 | 4025.9318 | 4429.5839 | 4913.9658 | 5453.2289 | 5952.8729 | 6750.0998 | 7257.5194 | 7806.1287 | 8399.3983 | 9041.0976 | 9735.3212
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 26998.6086 | 28953.6149 | 31064.3687 | 33343.8403 | 35806.109 | 38466.4601 | 41341.4896 | 44449.2187 | 47809.2177 | 51442.7414 | 55372.8764 | 59624.7009
|  |  | Other major risks |  |  | Major |  | 770.1496 | 825.9172 | 886.1275 | 951.1507 | 1021.3882 | 1097.2761 | 1179.2878 | 1267.9375 | 1363.7832 | 1467.4314 | 1579.5406 | 1700.8261
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567
|  |  | Subtotal |  |  |  |  | 142221.8053 | 151374.0015 | 164712.6743 | 180458.402 | 197910.5204 | 214470.2441 | 239483.895 | 256718.8822 | 275352.9194 | 295503.8828 | 317299.8064 | 340879.7704
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1468881.2389 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 82022.2895
|  |  | Post-replacement opex |  |  | 9122.9183
|  |  | Total annuity |  |  | 91145.2077
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 142221.8053 | 151374.0015 | 164712.6743 | 180458.402 | 197910.5204 | 214470.2441 | 239483.895 | 256718.8822 | 275352.9194 | 295503.8828 | 317299.8064 | 340879.7704
|  |  | Annualised cost |  |  |  |  | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - J18 AP Circuit Breaker Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1876349.3886 | 0 | 0 | 0 | 0 | 100% | 1876349.3886 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 256471.3274 | 0 | 100% | 256471.3274 | 256471.3274
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 15388.2796 | 100% | 15388.2796 | 15388.2796
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 625449.7962 | 0 | 0 | 0 | 0 | 100% | 625449.7962 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 85490.4425 | 0 | 100% | 85490.4425 | 85490.4425
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 4388.5094 | 100% | 4388.5094 | 4388.5094
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 625449.7962 | 4243.0068 | 56993.6283 | 85490.4425 | 4388.5094 | 100% | 776565.3832 | 151115.587
[5 empty] | 2 | Major |  | 1876349.3886 | 14850.5238 | 56993.6283 | 256471.3274 | 15388.2796 | 100% | 2220053.1478 | 343703.7592
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2996618.531; 2026: 494819.3462
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 87
|  |  | N-1 Rating before transfers, MVA |  |  | 70
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 60.3929 | 60.857 | 63.6762 | 66.2151 | 69.1719 | 71.3307 | 76.4778 | 76.4778 | 76.4778 | 76.4778 | 76.4778 | 76.4778
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 52.164 | 51.681 | 52.4559 | 54.0404 | 55.5282 | 55.9766 | 58.5365 | 58.5365 | 58.5365 | 58.5365 | 58.5365 | 58.5365
|  |  | Selected |  |  | 70% |  | 54.6327 | 54.4338 | 55.822 | 57.6928 | 59.6213 | 60.5828 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 54.6327 | 54.4338 | 55.822 | 57.6928 | 59.6213 | 60.5828 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189
|  |  | N-3 |  |  |  |  | 54.6327 | 54.4338 | 55.822 | 57.6928 | 59.6213 | 60.5828 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189
|  |  | N-4 |  |  |  |  | 54.6327 | 54.4338 | 55.822 | 57.6928 | 59.6213 | 60.5828 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 625449.7962 | 623173.0773 | 639065.6334 | 660482.8992 | 682561.3031 | 693568.6502 | 731760.7909 | 731760.7909 | 731760.7909 | 731760.7909 | 731760.7909 | 731760.7909
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1876349.3886 | 1869519.2318 | 1917196.9001 | 1981448.6977 | 2047683.9093 | 2080705.9507 | 2195282.3728 | 2195282.3728 | 2195282.3728 | 2195282.3728 | 2195282.3728 | 2195282.3728
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 26.52% | 28.44% | 30.52% | 32.76% | 35.18% | 37.79% | 40.61% | 43.67% | 46.97% | 50.54% | 54.4% | 58.58%
|  |  | Major |  |  |  |  | 0.3315% | 0.3556% | 0.3815% | 0.4095% | 0.4397% | 0.4724% | 0.5077% | 0.5458% | 0.5871% | 0.6317% | 0.68% | 0.7322%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 165891.2776 | 177256.0999 | 195028.3336 | 216354.9862 | 240097.9799 | 262096.6018 | 297197.376 | 319538.3449 | 343692.8417 | 369813.6644 | 398066.778 | 428632.4659
|  |  | Network Performance |  |  | Major |  | 6220.9229 | 6647.1037 | 7313.5625 | 8113.312 | 9003.6742 | 9828.6226 | 11144.9016 | 11982.6879 | 12888.4816 | 13868.0124 | 14927.5042 | 16073.7175
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 40081.1671 | 42983.4994 | 46117.049 | 49501.0708 | 53156.4667 | 57105.9286 | 61374.0945 | 65987.7178 | 70975.8519 | 76370.0511 | 82204.5886 | 88516.6949
|  |  | Other major risks |  |  | Major |  | 1139.529 | 1222.0439 | 1311.1324 | 1407.3419 | 1511.2668 | 1623.5521 | 1744.8983 | 1876.0661 | 2017.8814 | 2171.2414 | 2337.1204 | 2516.577
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249 | 12479.3249
|  |  | Subtotal |  |  |  |  | 225812.2214 | 240588.0718 | 262249.4023 | 287856.0358 | 316248.7124 | 343134.0299 | 383940.5953 | 411864.1415 | 442054.3815 | 474702.2941 | 510015.3161 | 548218.7801
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1795299.292 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 100249.4649
|  |  | Post-replacement opex |  |  | 11150.2334
|  |  | Total annuity |  |  | 111399.6983
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 225812.2214 | 240588.0718 | 262249.4023 | 287856.0358 | 316248.7124 | 343134.0299 | 383940.5953 | 411864.1415 | 442054.3815 | 474702.2941 | 510015.3161 | 548218.7801
|  |  | Annualised cost |  |  |  |  | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - J18 AP Circuit Breaker Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1876349.3886 | 0 | 0 | 0 | 0 | 100% | 1876349.3886 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 209840.177 | 0 | 100% | 209840.177 | 209840.177
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 15388.2796 | 100% | 15388.2796 | 15388.2796
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 625449.7962 | 0 | 0 | 0 | 0 | 100% | 625449.7962 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 69946.7257 | 0 | 100% | 69946.7257 | 69946.7257
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 4388.5094 | 100% | 4388.5094 | 4388.5094
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 625449.7962 | 4243.0068 | 46631.1504 | 69946.7257 | 4388.5094 | 100% | 750659.1885 | 125209.3923
[5 empty] | 2 | Major |  | 1876349.3886 | 14850.5238 | 46631.1504 | 209840.177 | 15388.2796 | 100% | 2163059.5195 | 286710.1309
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2913718.708; 2026: 411919.5231
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 87
|  |  | N-1 Rating before transfers, MVA |  |  | 70
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 60.3929 | 60.857 | 63.6762 | 66.2151 | 69.1719 | 71.3307 | 76.4778 | 76.4778 | 76.4778 | 76.4778 | 76.4778 | 76.4778
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 52.164 | 51.681 | 52.4559 | 54.0404 | 55.5282 | 55.9766 | 58.5365 | 58.5365 | 58.5365 | 58.5365 | 58.5365 | 58.5365
|  |  | Selected |  |  | 70% |  | 54.6327 | 54.4338 | 55.822 | 57.6928 | 59.6213 | 60.5828 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 54.6327 | 54.4338 | 55.822 | 57.6928 | 59.6213 | 60.5828 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189
|  |  | N-3 |  |  |  |  | 54.6327 | 54.4338 | 55.822 | 57.6928 | 59.6213 | 60.5828 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189
|  |  | N-4 |  |  |  |  | 54.6327 | 54.4338 | 55.822 | 57.6928 | 59.6213 | 60.5828 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189 | 63.9189
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Unserved energy day 1 |  |  |  | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  |  |  | Unserved energy day 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 625449.7962 | 623173.0773 | 639065.6334 | 660482.8992 | 682561.3031 | 693568.6502 | 731760.7909 | 731760.7909 | 731760.7909 | 731760.7909 | 731760.7909 | 731760.7909
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1876349.3886 | 1869519.2318 | 1917196.9001 | 1981448.6977 | 2047683.9093 | 2080705.9507 | 2195282.3728 | 2195282.3728 | 2195282.3728 | 2195282.3728 | 2195282.3728 | 2195282.3728
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 26.52% | 28.44% | 30.52% | 32.76% | 35.18% | 37.79% | 40.61% | 43.67% | 46.97% | 50.54% | 54.4% | 58.58%
|  |  | Major |  |  |  |  | 0.3315% | 0.3556% | 0.3815% | 0.4095% | 0.4397% | 0.4724% | 0.5077% | 0.5458% | 0.5871% | 0.6317% | 0.68% | 0.7322%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 165891.2776 | 177256.0999 | 195028.3336 | 216354.9862 | 240097.9799 | 262096.6018 | 297197.376 | 319538.3449 | 343692.8417 | 369813.6644 | 398066.778 | 428632.4659
|  |  | Network Performance |  |  | Major |  | 6220.9229 | 6647.1037 | 7313.5625 | 8113.312 | 9003.6742 | 9828.6226 | 11144.9016 | 11982.6879 | 12888.4816 | 13868.0124 | 14927.5042 | 16073.7175
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 33209.9334 | 35614.7102 | 38211.066 | 41014.9549 | 44043.6954 | 47316.0894 | 50852.5509 | 54675.247 | 58808.2504 | 63277.706 | 68112.0114 | 73342.0145
|  |  | Other major risks |  |  | Major |  | 950.5701 | 1019.4022 | 1093.7178 | 1173.9737 | 1260.6656 | 1354.3315 | 1455.5559 | 1564.9732 | 1683.2724 | 1811.2019 | 1949.5746 | 2099.2733
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567 | 10210.3567
|  |  | Subtotal |  |  |  |  | 216483.0606 | 230747.6728 | 251857.0367 | 276867.5836 | 304616.3718 | 330806.0019 | 370860.7411 | 397971.6097 | 427283.2028 | 458980.9414 | 493266.2248 | 530357.8279
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1468881.2389 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 82022.2895
|  |  | Post-replacement opex |  |  | 9122.9183
|  |  | Total annuity |  |  | 91145.2077
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 216483.0606 | 230747.6728 | 251857.0367 | 276867.5836 | 304616.3718 | 330806.0019 | 370860.7411 | 397971.6097 | 427283.2028 | 458980.9414 | 493266.2248 | 530357.8279
|  |  | Annualised cost |  |  |  |  | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - J18 AP Circuit Breaker Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 180976.6925 | 192731.1385 | 209915.0069 | 230214.9347 | 252719.3746 | 274049.9988 | 306351.5925 | 328527.8874 | 352504.3429 | 378432.6305 | 406477.492 | 436817.8821
|  |  | Annualised cost | Scenario Base case | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453 | 101272.453
|  |  | Risk cost | Scenario A | 150267.2947 | 159837.7767 | 173628.0586 | 189861.4934 | 207840.4296 | 224969.3521 | 250598.1336 | 268498.0389 | 287850.9689 | 308779.3474 | 331416.148 | 355905.8164
|  |  | Annualised cost | Scenario A | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983
|  |  | Risk cost | Scenario B | 142221.8053 | 151374.0015 | 164712.6743 | 180458.402 | 197910.5204 | 214470.2441 | 239483.895 | 256718.8822 | 275352.9194 | 295503.8828 | 317299.8064 | 340879.7704
|  |  | Annualised cost | Scenario B | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077
|  |  | Risk cost | Scenario C | 225812.2214 | 240588.0718 | 262249.4023 | 287856.0358 | 316248.7124 | 343134.0299 | 383940.5953 | 411864.1415 | 442054.3815 | 474702.2941 | 510015.3161 | 548218.7801
|  |  | Annualised cost | Scenario C | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983 | 111399.6983
|  |  | Risk cost | Scenario D | 216483.0606 | 230747.6728 | 251857.0367 | 276867.5836 | 304616.3718 | 330806.0019 | 370860.7411 | 397971.6097 | 427283.2028 | 458980.9414 | 493266.2248 | 530357.8279
|  |  | Annualised cost | Scenario D | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077 | 91145.2077
Charts
End