## Inputs
CitiPower - J18 FB Circuit Breaker Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | J18 FB Circuit Breaker Risk Monetisation Model
|  | Model start & timeline |  | 2019
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 25
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex, real $2019 |  | 1650000 |  |  |  |  | 0 | 0 | 0 | 0 | 1650000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 1709808.8496 |  |  |  |  | 0 | 0 | 0 | 0 | 1709808.8496 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 10739 | 9350
|  |  | Opex ($2021) | 11128.265 | 9688.9168
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 18.17% | 20.15% | 22.37% | 24.87% | 27.68% | 30.84% | 34.39% | 38.4% | 42.91% | 47.99% | 53.73% | 60.2%
|  |  | Major | 2 |  |  |  |  | 0.2271% | 0.2518% | 0.2796% | 0.3109% | 0.346% | 0.3855% | 0.4299% | 0.4799% | 0.5363% | 0.5999% | 0.6716% | 0.7525%
|  |  | Catastrophic | 3 | bar: 2010 to 2021
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 58.106 | 26450 | 20% | 2.8367
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 104032.081 | 47770 | 40% | 18344.7704
|  |  | Industrial | 10530.941 | 47070 | 80% | 3659.579
|  |  | Total | 114621.128 | 47694.8788 | 43.62% | 22007.186
Asset information
|  | Assets at risk |  | 1 |  |  | Sections lost
|  | N-rating, MVA |  | 90 |  | Total Sections | 3
|  |  | N-1 Rating before transfers, MVA | 64 |  | Significant | 1
|  |  | N-2 Rating before transfers, MVA | 0 |  | Major | 3
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major
|  |  | Average Consequence Loss Oil | 20 | 100
|  |  | Average Consequences Loss SF6 kgs | 0 | 0
|  |  | Average Consequence Fire | 0.005 | 0.05
|  |  | Average Consequence Waste | 1 | 1
|  |  | Average Consequence Disturbance | 2 | 5
|  |  | Average Cost of Fault (Air Insulated) | 1917.0584 | 3626.8673
|  |  | Average Cost of Fault (SF6 Insulated) | 1917.0584 | 3626.8673
|  |  | Average Cost of Fault (Oil Insulated) | 3989.554 | 13989.3451
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major
|  |  | Switching time only (hours required) | 2 | 2
|  |  | Number of weeks generation required | 2 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 37.4104
|  |  | Number of generators | 0 | 38
|  |  | Generator sites | 0 | 10
|  |  | Number of days to connect all generators | 0 | 4
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major
|  |  | Generator hire | 0 | 3399583.5752
|  |  | Fuel cost | 0 | 13807001.1522
|  |  | Fitter cost | 0 | 3257963.0442
|  |  | Traffic management cost | 0 | 8704481.4159
|  |  | Transformer hire | 0 | 894627.2566
|  |  | Earthing and bunding | 0 | 20724.9558
|  |  | Temporary fencing | 0 | 373049.2035
|  |  | Miscellaneous materials | 0 | 20724.9558
|  |  | Installation & removal of step-down transformers | 0 | 25906.1947
|  |  | Council permits | 0 | 41449.9115
|  |  | Crane hire | 0 | 25906.1947
|  |  | Cable hire | 0 | 31087.4336
|  |  | Total | 0 | 0
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major
|  |  | Minor | 0.4284% | 1.5%
|  |  | Serious | 0.08569% | 0.2999%
|  |  | Fataility | 0.01714% | 0.05998%
|  |  | Value of event | 4243.0068 | 14850.5238
|  |  | Weighted likelyhood of consequence | 0.02679% | 0.09377%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 34.753 | 38.834 | 39.972 | 42.061 | 43.94 | 45.378 | 48.209 | 48.209 | 48.209 | 48.209 | 48.209 | 48.209
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 28.901 | 31.806 | 31.869 | 33.234 | 34.048 | 34.771 | 36.292 | 36.292 | 36.292 | 36.292 | 36.292 | 36.292
|  |  | Selected | 70% |  |  |  |  | 30.6566 | 33.9144 | 34.2999 | 35.8821 | 37.0156 | 37.9531 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 30.6566 | 33.9144 | 34.2999 | 35.8821 | 37.0156 | 37.9531 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671
|  |  | N-3 | [5 empty] | 30.6566 | 33.9144 | 34.2999 | 35.8821 | 37.0156 | 37.9531 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671
|  |  | N-4 | [5 empty] | 30.6566 | 33.9144 | 34.2999 | 35.8821 | 37.0156 | 37.9531 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671
End

## Base Case
CitiPower - J18 FB Circuit Breaker Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1349330.9965 | 0 | 0 | 0 | 0 | 100% | 1349330.9965 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 233155.7522 | 0 | 100% | 233155.7522 | 233155.7522
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 13989.3451 | 100% | 13989.3451 | 13989.3451
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 449776.9988 | 0 | 0 | 0 | 0 | 100% | 449776.9988 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 77718.5841 | 0 | 100% | 77718.5841 | 77718.5841
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3989.554 | 100% | 3989.554 | 3989.554
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 449776.9988 | 4243.0068 | 51812.3894 | 77718.5841 | 3989.554 | 100% | 587540.5331 | 137763.5342
[5 empty] | 2 | Major |  | 1349330.9965 | 14850.5238 | 51812.3894 | 233155.7522 | 13989.3451 | 100% | 1663139.007 | 313808.0105
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2250679.5401; 2026: 451571.5447
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 90
|  |  | N-1 Rating before transfers, MVA |  |  | 64
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 34.753 | 38.834 | 39.972 | 42.061 | 43.94 | 45.378 | 48.209 | 48.209 | 48.209 | 48.209 | 48.209 | 48.209
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 28.901 | 31.806 | 31.869 | 33.234 | 34.048 | 34.771 | 36.292 | 36.292 | 36.292 | 36.292 | 36.292 | 36.292
|  |  | Selected |  |  | 70% |  | 30.6566 | 33.9144 | 34.2999 | 35.8821 | 37.0156 | 37.9531 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 30.6566 | 33.9144 | 34.2999 | 35.8821 | 37.0156 | 37.9531 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671
|  |  | N-3 |  |  |  |  | 30.6566 | 33.9144 | 34.2999 | 35.8821 | 37.0156 | 37.9531 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671
|  |  | N-4 |  |  |  |  | 30.6566 | 33.9144 | 34.2999 | 35.8821 | 37.0156 | 37.9531 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671 | 39.8671
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Adjustment |  |  |  | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Adjustment |  |  |  | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Adjustment |  |  |  | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 449776.9988 | 497573.6725 | 503229.5193 | 526442.6991 | 543072.796 | 556827.2873 | 584908.4566 | 584908.4566 | 584908.4566 | 584908.4566 | 584908.4566 | 584908.4566
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1349330.9965 | 1492721.0176 | 1509688.558 | 1579328.0974 | 1629218.388 | 1670481.8618 | 1754725.3698 | 1754725.3698 | 1754725.3698 | 1754725.3698 | 1754725.3698 | 1754725.3698
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 18.17% | 20.15% | 22.37% | 24.87% | 27.68% | 30.84% | 34.39% | 38.4% | 42.91% | 47.99% | 53.73% | 60.2%
|  |  | Major |  |  |  |  | 0.2271% | 0.2518% | 0.2796% | 0.3109% | 0.346% | 0.3855% | 0.4299% | 0.4799% | 0.5363% | 0.5999% | 0.6716% | 0.7525%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 81712.8337 | 100250.429 | 112579.3767 | 130923.2712 | 150309.7721 | 171705.8534 | 201160.0903 | 224578.0703 | 250964.189 | 280710.1887 | 314260.787 | 352120.9512
|  |  | Network Performance |  |  | Major |  | 3064.2313 | 3759.3911 | 4221.7266 | 4909.6227 | 5636.6165 | 6438.9695 | 7543.5034 | 8421.6776 | 9411.1571 | 10526.6321 | 11784.7795 | 13204.5357
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 25028.0668 | 27756.399 | 30819.6006 | 34260.9986 | 38129.7049 | 42481.4045 | 47379.2517 | 52894.8903 | 59109.6149 | 66115.6926 | 74017.8676 | 82935.075
|  |  | Other major risks |  |  | Major |  | 712.6349 | 790.3198 | 877.5397 | 975.5281 | 1085.6834 | 1209.5912 | 1349.0497 | 1506.0989 | 1683.0534 | 1882.5404 | 2107.5425 | 2361.4459
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 11128.265 | 11128.265 | 11128.265 | 11128.265 | 11128.265 | 11128.265 | 11128.265 | 11128.265 | 11128.265 | 11128.265 | 11128.265 | 11128.265
|  |  | Subtotal |  |  |  |  | 121646.0317 | 143684.8039 | 159626.5086 | 182197.6856 | 206290.0418 | 232964.0836 | 268560.1601 | 298529.0021 | 332296.2794 | 370363.3188 | 413299.2415 | 461750.2728
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 1709808.8496 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 95475.6808
|  |  | Post-replacement opex |  |  | 9688.9168
|  |  | Total annuity |  |  | 105164.5977
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 121646.0317 | 143684.8039 | 159626.5086 | 182197.6856 | 206290.0418 | 232964.0836 | 268560.1601 | 298529.0021 | 332296.2794 | 370363.3188 | 413299.2415 | 461750.2728
|  |  | Annualised cost |  |  |  |  | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - J18 FB Circuit Breaker Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1153678.002 | 0 | 0 | 0 | 0 | 100% | 1153678.002 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 256471.3274 | 0 | 100% | 256471.3274 | 256471.3274
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 12590.4106 | 100% | 12590.4106 | 12590.4106
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 384559.334 | 0 | 0 | 0 | 0 | 100% | 384559.334 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 85490.4425 | 0 | 100% | 85490.4425 | 85490.4425
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3590.5986 | 100% | 3590.5986 | 3590.5986
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 384559.334 | 4243.0068 | 56993.6283 | 85490.4425 | 3590.5986 | 100% | 534877.0102 | 150317.6762
[5 empty] | 2 | Major |  | 1153678.002 | 14850.5238 | 56993.6283 | 256471.3274 | 12590.4106 | 100% | 1494583.8922 | 340905.8902
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2029460.9024; 2026: 491223.5663
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 90
|  |  | N-1 Rating before transfers, MVA |  |  | 64
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 33.0153 | 36.8923 | 37.9734 | 39.9579 | 41.743 | 43.1091 | 45.7985 | 45.7985 | 45.7985 | 45.7985 | 45.7985 | 45.7985
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 27.4559 | 30.2157 | 30.2755 | 31.5723 | 32.3456 | 33.0324 | 34.4774 | 34.4774 | 34.4774 | 34.4774 | 34.4774 | 34.4774
|  |  | Selected |  |  | 70% |  | 29.1238 | 32.2187 | 32.5849 | 34.088 | 35.1648 | 36.0554 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 29.1238 | 32.2187 | 32.5849 | 34.088 | 35.1648 | 36.0554 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737
|  |  | N-3 |  |  |  |  | 29.1238 | 32.2187 | 32.5849 | 34.088 | 35.1648 | 36.0554 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737
|  |  | N-4 |  |  |  |  | 29.1238 | 32.2187 | 32.5849 | 34.088 | 35.1648 | 36.0554 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 384559.334 | 425425.49 | 430261.239 | 450108.5078 | 464327.2406 | 476087.3306 | 500096.7304 | 500096.7304 | 500096.7304 | 500096.7304 | 500096.7304 | 500096.7304
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1153678.002 | 1276276.47 | 1290783.7171 | 1350325.5233 | 1392981.7218 | 1428261.9918 | 1500290.1912 | 1500290.1912 | 1500290.1912 | 1500290.1912 | 1500290.1912 | 1500290.1912
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 16.35% | 18.13% | 20.13% | 22.38% | 24.91% | 27.75% | 30.95% | 34.56% | 38.62% | 43.19% | 48.36% | 54.18%
|  |  | Major |  |  |  |  | 0.2044% | 0.2267% | 0.2517% | 0.2798% | 0.3114% | 0.3469% | 0.3869% | 0.4319% | 0.4827% | 0.5399% | 0.6044% | 0.6773%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 62878.0256 | 77142.7051 | 86629.8304 | 100745.4572 | 115663.3696 | 132127.6542 | 154792.6895 | 172812.8251 | 193116.9435 | 216006.4902 | 241823.6756 | 270957.0719
|  |  | Network Performance |  |  | Major |  | 2357.926 | 2892.8514 | 3248.6186 | 3777.9546 | 4337.3764 | 4954.787 | 5804.7259 | 6480.4809 | 7241.8854 | 8100.2434 | 9068.3878 | 10160.8902
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 24577.9464 | 27257.2106 | 30265.3216 | 33644.8273 | 37443.9564 | 41717.3923 | 46527.1536 | 51943.5955 | 58046.5506 | 64926.6265 | 72686.6839 | 81443.5187
|  |  | Other major risks |  |  | Major |  | 696.7549 | 772.7088 | 857.9851 | 953.79 | 1061.4907 | 1182.6374 | 1318.9883 | 1472.5379 | 1645.5492 | 1840.591 | 2060.5792 | 2308.8249
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915
|  |  | Subtotal |  |  |  |  | 102751.7443 | 120306.5674 | 133242.8473 | 151363.1207 | 170747.2845 | 192223.5625 | 220684.6487 | 244950.5309 | 272292.0202 | 303115.0427 | 337880.418 | 377111.3972
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 1880789.7345 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 105023.2489
|  |  | Post-replacement opex |  |  | 10657.8085
|  |  | Total annuity |  |  | 115681.0574
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 102751.7443 | 120306.5674 | 133242.8473 | 151363.1207 | 170747.2845 | 192223.5625 | 220684.6487 | 244950.5309 | 272292.0202 | 303115.0427 | 337880.418 | 377111.3972
|  |  | Annualised cost |  |  |  |  | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574
|  |  | Feasible ? |  |  |  |  | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
CitiPower - J18 FB Circuit Breaker Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1153678.002 | 0 | 0 | 0 | 0 | 100% | 1153678.002 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 209840.177 | 0 | 100% | 209840.177 | 209840.177
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 12590.4106 | 100% | 12590.4106 | 12590.4106
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 384559.334 | 0 | 0 | 0 | 0 | 100% | 384559.334 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 69946.7257 | 0 | 100% | 69946.7257 | 69946.7257
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 3590.5986 | 100% | 3590.5986 | 3590.5986
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 384559.334 | 4243.0068 | 46631.1504 | 69946.7257 | 3590.5986 | 100% | 508970.8155 | 124411.4815
[5 empty] | 2 | Major |  | 1153678.002 | 14850.5238 | 46631.1504 | 209840.177 | 12590.4106 | 100% | 1437590.2639 | 283912.2618
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 1946561.0794; 2026: 408323.7433
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 90
|  |  | N-1 Rating before transfers, MVA |  |  | 64
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 33.0153 | 36.8923 | 37.9734 | 39.9579 | 41.743 | 43.1091 | 45.7985 | 45.7985 | 45.7985 | 45.7985 | 45.7985 | 45.7985
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 27.4559 | 30.2157 | 30.2755 | 31.5723 | 32.3456 | 33.0324 | 34.4774 | 34.4774 | 34.4774 | 34.4774 | 34.4774 | 34.4774
|  |  | Selected |  |  | 70% |  | 29.1238 | 32.2187 | 32.5849 | 34.088 | 35.1648 | 36.0554 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 29.1238 | 32.2187 | 32.5849 | 34.088 | 35.1648 | 36.0554 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737
|  |  | N-3 |  |  |  |  | 29.1238 | 32.2187 | 32.5849 | 34.088 | 35.1648 | 36.0554 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737
|  |  | N-4 |  |  |  |  | 29.1238 | 32.2187 | 32.5849 | 34.088 | 35.1648 | 36.0554 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737 | 37.8737
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 384559.334 | 425425.49 | 430261.239 | 450108.5078 | 464327.2406 | 476087.3306 | 500096.7304 | 500096.7304 | 500096.7304 | 500096.7304 | 500096.7304 | 500096.7304
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1153678.002 | 1276276.47 | 1290783.7171 | 1350325.5233 | 1392981.7218 | 1428261.9918 | 1500290.1912 | 1500290.1912 | 1500290.1912 | 1500290.1912 | 1500290.1912 | 1500290.1912
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 16.35% | 18.13% | 20.13% | 22.38% | 24.91% | 27.75% | 30.95% | 34.56% | 38.62% | 43.19% | 48.36% | 54.18%
|  |  | Major |  |  |  |  | 0.2044% | 0.2267% | 0.2517% | 0.2798% | 0.3114% | 0.3469% | 0.3869% | 0.4319% | 0.4827% | 0.5399% | 0.6044% | 0.6773%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 62878.0256 | 77142.7051 | 86629.8304 | 100745.4572 | 115663.3696 | 132127.6542 | 154792.6895 | 172812.8251 | 193116.9435 | 216006.4902 | 241823.6756 | 270957.0719
|  |  | Network Performance |  |  | Major |  | 2357.926 | 2892.8514 | 3248.6186 | 3777.9546 | 4337.3764 | 4954.787 | 5804.7259 | 6480.4809 | 7241.8854 | 8100.2434 | 9068.3878 | 10160.8902
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 20342.1101 | 22559.622 | 25049.3062 | 27846.3779 | 30990.7537 | 34527.693 | 38508.5258 | 42991.482 | 48042.6357 | 53736.9789 | 60159.6449 | 67407.3008
|  |  | Other major risks |  |  | Major |  | 580.2694 | 643.5251 | 714.5447 | 794.3326 | 884.0276 | 984.9207 | 1098.4761 | 1226.3547 | 1370.4416 | 1532.8757 | 1716.0857 | 1922.8289
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385
|  |  | Subtotal |  |  |  |  | 96173.7696 | 113254.1421 | 125657.7384 | 143179.5609 | 161890.9658 | 182610.4935 | 210219.8557 | 233526.5813 | 259787.3446 | 289392.0267 | 322783.2325 | 360463.5303
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 1538827.9646 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 85928.1128
|  |  | Post-replacement opex |  |  | 8720.0251
|  |  | Total annuity |  |  | 94648.1379
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 96173.7696 | 113254.1421 | 125657.7384 | 143179.5609 | 161890.9658 | 182610.4935 | 210219.8557 | 233526.5813 | 259787.3446 | 289392.0267 | 322783.2325 | 360463.5303
|  |  | Annualised cost |  |  |  |  | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - J18 FB Circuit Breaker Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1558477.301 | 0 | 0 | 0 | 0 | 100% | 1558477.301 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 256471.3274 | 0 | 100% | 256471.3274 | 256471.3274
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 15388.2796 | 100% | 15388.2796 | 15388.2796
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 519492.4337 | 0 | 0 | 0 | 0 | 100% | 519492.4337 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 85490.4425 | 0 | 100% | 85490.4425 | 85490.4425
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 4388.5094 | 100% | 4388.5094 | 4388.5094
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 519492.4337 | 4243.0068 | 56993.6283 | 85490.4425 | 4388.5094 | 100% | 670608.0206 | 151115.587
[5 empty] | 2 | Major |  | 1558477.301 | 14850.5238 | 56993.6283 | 256471.3274 | 15388.2796 | 100% | 1902181.0602 | 343703.7592
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2572789.0808; 2026: 494819.3462
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 90
|  |  | N-1 Rating before transfers, MVA |  |  | 64
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 36.4907 | 40.7757 | 41.9706 | 44.1641 | 46.137 | 47.6469 | 50.6195 | 50.6195 | 50.6195 | 50.6195 | 50.6195 | 50.6195
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 30.3461 | 33.3963 | 33.4625 | 34.8957 | 35.7504 | 36.5096 | 38.1066 | 38.1066 | 38.1066 | 38.1066 | 38.1066 | 38.1066
|  |  | Selected |  |  | 70% |  | 32.1894 | 35.6101 | 36.0149 | 37.6762 | 38.8664 | 39.8508 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 32.1894 | 35.6101 | 36.0149 | 37.6762 | 38.8664 | 39.8508 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605
|  |  | N-3 |  |  |  |  | 32.1894 | 35.6101 | 36.0149 | 37.6762 | 38.8664 | 39.8508 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605
|  |  | N-4 |  |  |  |  | 32.1894 | 35.6101 | 36.0149 | 37.6762 | 38.8664 | 39.8508 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 519492.4337 | 574697.5918 | 581230.0948 | 608041.3175 | 627249.0794 | 643135.5168 | 675569.2674 | 675569.2674 | 675569.2674 | 675569.2674 | 675569.2674 | 675569.2674
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1558477.301 | 1724092.7753 | 1743690.2845 | 1824123.9525 | 1881747.2382 | 1929406.5504 | 2026707.8021 | 2026707.8021 | 2026707.8021 | 2026707.8021 | 2026707.8021 | 2026707.8021
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 19.98% | 22.16% | 24.61% | 27.36% | 30.45% | 33.92% | 37.83% | 42.23% | 47.2% | 52.79% | 59.1% | 66.22%
|  |  | Major |  |  |  |  | 0.2498% | 0.277% | 0.3076% | 0.342% | 0.3806% | 0.424% | 0.4729% | 0.5279% | 0.59% | 0.6599% | 0.7388% | 0.8278%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 103816.1553 | 127368.17 | 143032.0981 | 166338.0161 | 190968.5654 | 218152.2868 | 255573.8947 | 285326.4383 | 318850.0022 | 356642.2948 | 399268.3299 | 447369.6685
|  |  | Network Performance |  |  | Major |  | 3893.1058 | 4776.3064 | 5363.7037 | 6237.6756 | 7161.3212 | 8180.7108 | 9584.0211 | 10699.7414 | 11956.8751 | 13374.0861 | 14972.5624 | 16776.3626
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 30199.1679 | 33491.2066 | 37187.3027 | 41339.735 | 46007.7628 | 51258.5762 | 57168.3778 | 63823.6141 | 71322.3759 | 79775.9938 | 89310.8537 | 100070.464
|  |  | Other major risks |  |  | Major |  | 858.5785 | 952.1729 | 1057.2549 | 1175.3108 | 1308.0253 | 1457.3087 | 1625.3276 | 1814.5395 | 2027.7333 | 2268.0742 | 2539.1554 | 2845.0568
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915 | 12241.0915
|  |  | Subtotal |  |  |  |  | 151008.099 | 178828.9474 | 198881.4509 | 227331.829 | 257686.7662 | 291289.9739 | 336192.7127 | 373905.4248 | 416398.0779 | 464301.5403 | 518331.9928 | 579302.6434
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 1880789.7345 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 105023.2489
|  |  | Post-replacement opex |  |  | 10657.8085
|  |  | Total annuity |  |  | 115681.0574
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 151008.099 | 178828.9474 | 198881.4509 | 227331.829 | 257686.7662 | 291289.9739 | 336192.7127 | 373905.4248 | 416398.0779 | 464301.5403 | 518331.9928 | 579302.6434
|  |  | Annualised cost |  |  |  |  | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - J18 FB Circuit Breaker Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1558477.301 | 0 | 0 | 0 | 0 | 100% | 1558477.301 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 14850.5238 | 0 | 0 | 0 | 100% | 14850.5238 | 14850.5238
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 209840.177 | 0 | 100% | 209840.177 | 209840.177
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 15388.2796 | 100% | 15388.2796 | 15388.2796
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 519492.4337 | 0 | 0 | 0 | 0 | 100% | 519492.4337 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 4243.0068 | 0 | 0 | 0 | 100% | 4243.0068 | 4243.0068
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 69946.7257 | 0 | 100% | 69946.7257 | 69946.7257
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 4388.5094 | 100% | 4388.5094 | 4388.5094
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 519492.4337 | 4243.0068 | 46631.1504 | 69946.7257 | 4388.5094 | 100% | 644701.8259 | 125209.3923
[5 empty] | 2 | Major |  | 1558477.301 | 14850.5238 | 46631.1504 | 209840.177 | 15388.2796 | 100% | 1845187.4318 | 286710.1309
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 2489889.2578; 2026: 411919.5231
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 90
|  |  | N-1 Rating before transfers, MVA |  |  | 64
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 36.4907 | 40.7757 | 41.9706 | 44.1641 | 46.137 | 47.6469 | 50.6195 | 50.6195 | 50.6195 | 50.6195 | 50.6195 | 50.6195
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 30.3461 | 33.3963 | 33.4625 | 34.8957 | 35.7504 | 36.5096 | 38.1066 | 38.1066 | 38.1066 | 38.1066 | 38.1066 | 38.1066
|  |  | Selected |  |  | 70% |  | 32.1894 | 35.6101 | 36.0149 | 37.6762 | 38.8664 | 39.8508 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 32.1894 | 35.6101 | 36.0149 | 37.6762 | 38.8664 | 39.8508 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605
|  |  | N-3 |  |  |  |  | 32.1894 | 35.6101 | 36.0149 | 37.6762 | 38.8664 | 39.8508 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605
|  |  | N-4 |  |  |  |  | 32.1894 | 35.6101 | 36.0149 | 37.6762 | 38.8664 | 39.8508 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605 | 41.8605
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 519492.4337 | 574697.5918 | 581230.0948 | 608041.3175 | 627249.0794 | 643135.5168 | 675569.2674 | 675569.2674 | 675569.2674 | 675569.2674 | 675569.2674 | 675569.2674
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 1558477.301 | 1724092.7753 | 1743690.2845 | 1824123.9525 | 1881747.2382 | 1929406.5504 | 2026707.8021 | 2026707.8021 | 2026707.8021 | 2026707.8021 | 2026707.8021 | 2026707.8021
|  |  | N-3 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-4 |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 19.98% | 22.16% | 24.61% | 27.36% | 30.45% | 33.92% | 37.83% | 42.23% | 47.2% | 52.79% | 59.1% | 66.22%
|  |  | Major |  |  |  |  | 0.2498% | 0.277% | 0.3076% | 0.342% | 0.3806% | 0.424% | 0.4729% | 0.5279% | 0.59% | 0.6599% | 0.7388% | 0.8278%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 103816.1553 | 127368.17 | 143032.0981 | 166338.0161 | 190968.5654 | 218152.2868 | 255573.8947 | 285326.4383 | 318850.0022 | 356642.2948 | 399268.3299 | 447369.6685
|  |  | Network Performance |  |  | Major |  | 3893.1058 | 4776.3064 | 5363.7037 | 6237.6756 | 7161.3212 | 8180.7108 | 9584.0211 | 10699.7414 | 11956.8751 | 13374.0861 | 14972.5624 | 16776.3626
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 25022.0347 | 27749.7094 | 30812.1727 | 34252.7412 | 38120.5151 | 42471.1659 | 47367.8327 | 52882.142 | 59095.3688 | 66099.7579 | 74000.0284 | 82915.0866
|  |  | Other major risks |  |  | Major |  | 716.2073 | 794.2817 | 881.9388 | 980.4185 | 1091.126 | 1215.655 | 1355.8126 | 1513.649 | 1691.4906 | 1891.9777 | 2118.1077 | 2373.284
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385 | 10015.4385
|  |  | Subtotal |  |  |  |  | 143462.9416 | 170703.906 | 190105.3518 | 217824.2899 | 247356.9663 | 280035.2569 | 323896.9996 | 360437.4092 | 401609.1751 | 448023.5549 | 500374.4667 | 559449.8401
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 1538827.9646 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 85928.1128
|  |  | Post-replacement opex |  |  | 8720.0251
|  |  | Total annuity |  |  | 94648.1379
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 143462.9416 | 170703.906 | 190105.3518 | 217824.2899 | 247356.9663 | 280035.2569 | 323896.9996 | 360437.4092 | 401609.1751 | 448023.5549 | 500374.4667 | 559449.8401
|  |  | Annualised cost |  |  |  |  | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - J18 FB Circuit Breaker Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 121646.0317 | 143684.8039 | 159626.5086 | 182197.6856 | 206290.0418 | 232964.0836 | 268560.1601 | 298529.0021 | 332296.2794 | 370363.3188 | 413299.2415 | 461750.2728
|  |  | Annualised cost | Scenario Base case | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977 | 105164.5977
|  |  | Risk cost | Scenario A | 102751.7443 | 120306.5674 | 133242.8473 | 151363.1207 | 170747.2845 | 192223.5625 | 220684.6487 | 244950.5309 | 272292.0202 | 303115.0427 | 337880.418 | 377111.3972
|  |  | Annualised cost | Scenario A | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574
|  |  | Risk cost | Scenario B | 96173.7696 | 113254.1421 | 125657.7384 | 143179.5609 | 161890.9658 | 182610.4935 | 210219.8557 | 233526.5813 | 259787.3446 | 289392.0267 | 322783.2325 | 360463.5303
|  |  | Annualised cost | Scenario B | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379
|  |  | Risk cost | Scenario C | 151008.099 | 178828.9474 | 198881.4509 | 227331.829 | 257686.7662 | 291289.9739 | 336192.7127 | 373905.4248 | 416398.0779 | 464301.5403 | 518331.9928 | 579302.6434
|  |  | Annualised cost | Scenario C | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574 | 115681.0574
|  |  | Risk cost | Scenario D | 143462.9416 | 170703.906 | 190105.3518 | 217824.2899 | 247356.9663 | 280035.2569 | 323896.9996 | 360437.4092 | 401609.1751 | 448023.5549 | 500374.4667 | 559449.8401
|  |  | Annualised cost | Scenario D | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379 | 94648.1379
Charts
End