## Inputs
CitiPower - LQ Switchboard Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | CitiPower
|  | Title |  | LQ Switchboard Risk Monetisation Model
|  | Model start & timeline |  | 2019
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 50
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex regulator, real $2019 |  | 18244386.1898 |  |  |  |  | 0 | 0 | 0 | 0 | 75000 | 4925984.2712 | 6621700.9593 | 6621700.9593 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 18905704.8255 |  |  |  |  | 0 | 0 | 0 | 0 | 77718.5841 | 5104540.3029 | 6861722.9693 | 6861722.9693 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 57400 | 49800
|  |  | Opex ($2021) | 59480.623 | 51605.1398
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 10.15% | 10.86% | 11.7% | 12.62% | 13.68% | 14.87% | 16.17% | 17.59% | 19.15% | 20.86% | 22.73% | 24.77%
|  |  | Major | 2 |  |  |  |  | 1.128% | 1.206% | 1.3% | 1.403% | 1.52% | 1.652% | 1.797% | 1.955% | 2.128% | 2.318% | 2.525% | 2.752%
|  |  | Catastrophic | 3 | bar: 2010 to 2021
Value of customer reliability (VCR)
|  | Sector |  | MWh | Weighted VCR $/MWh ($2018) | Load Duration | Load Duration Adjusted VCR $/MWh ($2021)
|  |  | Residential | 4598 | 26450 | 20% | 109.5107
|  |  | Agricultural | 0 | 50930 | 15% | 0
|  |  | Commercial | 228272 | 47770 | 40% | 19638.1153
|  |  | Industrial | 2073 | 47070 | 80% | 351.4515
|  |  | Total | 234943 | 47346.5762 | 40.13% | 20099.0775
Asset information
|  | Assets at risk |  | 1 |  |  | Sections lost
|  | N-rating, MVA |  | 199.5 |  | Total Sections | 4
|  |  | N-1 Rating before transfers, MVA | 131 |  | Significant | 1
|  |  | N-2 Rating before transfers, MVA | 65.5 |  | Major | 4
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 11.1
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major
|  |  | Average Consequence Loss Oil | 0 | 0
|  |  | Average Consequences Loss SF6 kgs | 0 | 0
|  |  | Average Consequence Fire | 0.05 | 5
|  |  | Average Consequence Waste | 10 | 40
|  |  | Average Consequence Disturbance | 3 | 5
|  |  | Average Cost of Fault (Air Insulated) | 12124.0991 | 95334.7965
|  |  | Average Cost of Fault (SF6 Insulated) | 12124.0991 | 95334.7965
|  |  | Average Cost of Fault (Oil Insulated) | 12124.0991 | 95334.7965
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major
|  |  | Switching time only (hours required) | 2 | 0
|  |  | Number of weeks generation required | 2 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 19.6625
|  |  | Number of generators | 0 | 20
|  |  | Generator sites | 0 | 5
|  |  | Number of days to connect all generators | 0 | 2
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major
|  |  | Generator hire | 0 | 1765075.3982
|  |  | Fuel cost | 0 | 6676373.7657
|  |  | Fitter cost | 0 | 1628981.5221
|  |  | Traffic management cost | 0 | 4352240.708
|  |  | Transformer hire | 0 | 441268.8496
|  |  | Earthing and bunding | 0 | 10362.4779
|  |  | Temporary fencing | 0 | 186524.6018
|  |  | Miscellaneous materials | 0 | 10362.4779
|  |  | Installation & removal of step-down transformers | 0 | 12953.0973
|  |  | Council permits | 0 | 20724.9558
|  |  | Crane hire | 0 | 12953.0973
|  |  | Cable hire | 0 | 15543.7168
|  |  | Total | 0 | 15133364.6683
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major
|  |  | Minor | 0.7692% | 3.846%
|  |  | Serious | 0.1923% | 0.9615%
|  |  | Fataility | 0.01923% | 0.09615%
|  |  | Value of event | 6517.2332 | 32586.1661
|  |  | Weighted likelyhood of consequence | 0.04115% | 0.2058%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 91.72 | 89.144 | 93.226 | 96.936 | 96.785 | 97.952 | 106.052 | 106.052 | 106.052 | 106.052 | 106.052 | 106.052
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 86.109 | 83.646 | 88.987 | 91.969 | 91.484 | 91.998 | 100.141 | 100.141 | 100.141 | 100.141 | 100.141 | 100.141
|  |  | Selected | 70% |  |  |  |  | 87.7923 | 85.2954 | 90.2587 | 93.4591 | 93.0743 | 93.7842 | 101.9143 | 101.9143 | 101.9143 | 101.9143 | 101.9143 | 101.9143
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 11.1923 | 8.6954 | 13.6587 | 16.8591 | 16.4743 | 17.1842 | 25.3143 | 25.3143 | 25.3143 | 25.3143 | 25.3143 | 25.3143
|  |  | N-3 | [5 empty] | 76.6923 | 74.1954 | 79.1587 | 82.3591 | 81.9743 | 82.6842 | 90.8143 | 90.8143 | 90.8143 | 90.8143 | 90.8143 | 90.8143
|  |  | N-4 | [5 empty] | 76.6923 | 74.1954 | 79.1587 | 82.3591 | 81.9743 | 82.6842 | 90.8143 | 90.8143 | 90.8143 | 90.8143 | 90.8143 | 90.8143
End

## Base Case
CitiPower - LQ Switchboard Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 10797835.4515 | 0 | 0 | 0 | 0 | 100% | 10797835.4515 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 32586.1661 | 0 | 0 | 0 | 100% | 32586.1661 | 32586.1661
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 15133364.6683 | 0 | 0 | 100% | 15133364.6683 | 15133364.6683
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 18905704.8255 | 0 | 100% | 18905704.8255 | 18905704.8255
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 95334.7965 | 100% | 95334.7965 | 95334.7965
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 882272.1213 | 0 | 0 | 0 | 0 | 100% | 882272.1213 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 6517.2332 | 0 | 0 | 0 | 100% | 6517.2332 | 6517.2332
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 6301901.6085 | 0 | 100% | 6301901.6085 | 6301901.6085
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 12124.0991 | 100% | 12124.0991 | 12124.0991
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 882272.1213 | 6517.2332 | 51812.3894 | 6301901.6085 | 12124.0991 | 100% | 7254627.4515 | 6372355.3302
[5 empty] | 2 | Major |  | 10797835.4515 | 32586.1661 | 15185177.0577 | 18905704.8255 | 95334.7965 | 100% | 45016638.2973 | 34218802.8457
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 52271265.7488; 2026: 40591158.176
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 199.5
|  |  | N-1 Rating before transfers, MVA |  |  | 131
|  |  | N-2 Rating before transfers, MVA |  |  | 65.5
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 11.1
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 91.72 | 89.144 | 93.226 | 96.936 | 96.785 | 97.952 | 106.052 | 106.052 | 106.052 | 106.052 | 106.052 | 106.052
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 86.109 | 83.646 | 88.987 | 91.969 | 91.484 | 91.998 | 100.141 | 100.141 | 100.141 | 100.141 | 100.141 | 100.141
|  |  | Selected |  |  | 70% |  | 87.7923 | 85.2954 | 90.2587 | 93.4591 | 93.0743 | 93.7842 | 101.9143 | 101.9143 | 101.9143 | 101.9143 | 101.9143 | 101.9143
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 11.1923 | 8.6954 | 13.6587 | 16.8591 | 16.4743 | 17.1842 | 25.3143 | 25.3143 | 25.3143 | 25.3143 | 25.3143 | 25.3143
|  |  | N-3 |  |  |  |  | 76.6923 | 74.1954 | 79.1587 | 82.3591 | 81.9743 | 82.6842 | 90.8143 | 90.8143 | 90.8143 | 90.8143 | 90.8143 | 90.8143
|  |  | N-4 |  |  |  |  | 76.6923 | 74.1954 | 79.1587 | 82.3591 | 81.9743 | 82.6842 | 90.8143 | 90.8143 | 90.8143 | 90.8143 | 90.8143 | 90.8143
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 2 | 2 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | Adjustment |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | Adjustment |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 882272.1213 | 857179.428 | 907058.3037 | 939220.8476 | 935353.785 | 942487.9526 | 1024191.7077 | 1024191.7077 | 1024191.7077 | 1024191.7077 | 1024191.7077 | 1024191.7077
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 10797835.4515 | 8388936.8928 | 16471636.201 | 20331141.4612 | 19867093.9596 | 20723194.0672 | 36633173.6066 | 36633173.6066 | 36633173.6066 | 36633173.6066 | 36633173.6066 | 36633173.6066
|  |  | N-3 |  |  | Catastrophic |  | 184973337.8753 | 178951091.4784 | 190922021.6484 | 198641032.1689 | 197712937.1657 | 199425137.3808 | 240937442.4497 | 240937442.4497 | 240937442.4497 | 240937442.4497 | 240937442.4497 | 240937442.4497
|  |  | N-4 |  |  | Catastrophic |  | 184973337.8753 | 178951091.4784 | 190922021.6484 | 198641032.1689 | 197712937.1657 | 199425137.3808 | 240937442.4497 | 240937442.4497 | 240937442.4497 | 240937442.4497 | 240937442.4497 | 240937442.4497
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 10.15% | 10.86% | 11.7% | 12.62% | 13.68% | 14.87% | 16.17% | 17.59% | 19.15% | 20.86% | 22.73% | 24.77%
|  |  | Major |  |  |  |  | 1.128% | 1.206% | 1.3% | 1.403% | 1.52% | 1.652% | 1.797% | 1.955% | 2.128% | 2.318% | 2.525% | 2.752%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 89592.2456 | 93072.2952 | 106118.5561 | 118567.3288 | 127964.7627 | 140135.5411 | 165598.1677 | 180174.6016 | 196137.4391 | 213623.5383 | 232783.5734 | 253662.0846
|  |  | Network Performance |  |  | Major |  | 131786.8868 | 111548.9605 | 225907.5617 | 298352.5061 | 316217.8766 | 357933.4965 | 676521.6415 | 736071.0504 | 801284.3626 | 872720.6876 | 950995.5779 | 1036290.9943
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 647094.7113 | 691908.5047 | 745514.5315 | 804446.7411 | 871795.1976 | 947485.281 | 1030325.0445 | 1121017.2613 | 1220335.4571 | 1329131.141 | 1448341.7839 | 1578244.5074
|  |  | Other major risks |  |  | Major |  | 386091.4354 | 412829.7498 | 444813.9825 | 479976.1017 | 520159.8056 | 565320.5718 | 614747.2208 | 668859.065 | 728117.6312 | 793030.9755 | 864158.4432 | 941665.3802
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 59480.623 | 59480.623 | 59480.623 | 59480.623 | 59480.623 | 59480.623 | 59480.623 | 59480.623 | 59480.623 | 59480.623 | 59480.623 | 59480.623
|  |  | Subtotal |  |  |  |  | 1314045.9021 | 1368840.1333 | 1581835.2548 | 1760823.3007 | 1895618.2655 | 2070355.5133 | 2546672.6975 | 2765602.6014 | 3005355.513 | 3267986.9654 | 3555760.0014 | 3869343.5896
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 77718.5841 | 5104540.3029 | 6861722.9693 | 6861722.9693 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 108.5% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 718060.5215
|  |  | Post-replacement opex |  |  | 51605.1398
|  |  | Total annuity |  |  | 769665.6614
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 1314045.9021 | 1368840.1333 | 1581835.2548 | 1760823.3007 | 1895618.2655 | 2070355.5133 | 2546672.6975 | 2765602.6014 | 3005355.513 | 3267986.9654 | 3555760.0014 | 3869343.5896
|  |  | Annualised cost |  |  |  |  | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
CitiPower - LQ Switchboard Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 5906636.3422 | 0 | 0 | 0 | 0 | 100% | 5906636.3422 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 32586.1661 | 0 | 0 | 0 | 100% | 32586.1661 | 32586.1661
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 16646701.1351 | 0 | 0 | 100% | 16646701.1351 | 16646701.1351
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 20796275.308 | 0 | 100% | 20796275.308 | 20796275.308
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 85801.3168 | 100% | 85801.3168 | 85801.3168
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 754342.6637 | 0 | 0 | 0 | 0 | 100% | 754342.6637 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 6517.2332 | 0 | 0 | 0 | 100% | 6517.2332 | 6517.2332
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 6932091.7693 | 0 | 100% | 6932091.7693 | 6932091.7693
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 10911.6892 | 100% | 10911.6892 | 10911.6892
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 754342.6637 | 6517.2332 | 56993.6283 | 6932091.7693 | 10911.6892 | 100% | 7760856.9838 | 7006514.3201
[5 empty] | 2 | Major |  | 5906636.3422 | 32586.1661 | 16703694.7635 | 20796275.308 | 85801.3168 | 100% | 43524993.8966 | 37618357.5544
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 51285850.8804; 2026: 44624871.8745
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 199.5
|  |  | N-1 Rating before transfers, MVA |  |  | 131
|  |  | N-2 Rating before transfers, MVA |  |  | 65.5
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 11.1
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 87.134 | 84.6868 | 88.5647 | 92.0892 | 91.9457 | 93.0544 | 100.7494 | 100.7494 | 100.7494 | 100.7494 | 100.7494 | 100.7494
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 81.8035 | 79.4637 | 84.5376 | 87.3705 | 86.9098 | 87.3981 | 95.1339 | 95.1339 | 95.1339 | 95.1339 | 95.1339 | 95.1339
|  |  | Selected |  |  | 70% |  | 83.4027 | 81.0306 | 85.7458 | 88.7861 | 88.4206 | 89.095 | 96.8186 | 96.8186 | 96.8186 | 96.8186 | 96.8186 | 96.8186
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 6.8027 | 4.4306 | 9.1458 | 12.1861 | 11.8206 | 12.495 | 20.2186 | 20.2186 | 20.2186 | 20.2186 | 20.2186 | 20.2186
|  |  | N-3 |  |  |  |  | 72.3027 | 69.9306 | 74.6458 | 77.6861 | 77.3206 | 77.995 | 85.7186 | 85.7186 | 85.7186 | 85.7186 | 85.7186 | 85.7186
|  |  | N-4 |  |  |  |  | 72.3027 | 69.9306 | 74.6458 | 77.6861 | 77.3206 | 77.995 | 85.7186 | 85.7186 | 85.7186 | 85.7186 | 85.7186 | 85.7186
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2.5 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 8 | 7 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | Unserved energy day 2 |  |  |  | 3 | 2.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 5 | 4.5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  |  |  | Unserved energy day 1 |  |  |  | 8 | 7 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | Unserved energy day 2 |  |  |  | 3 | 2.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 5 | 4.5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 754342.6637 | 732888.411 | 775534.8497 | 803033.8247 | 799727.4862 | 805827.1995 | 875683.91 | 875683.91 | 875683.91 | 875683.91 | 875683.91 | 875683.91
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 5906636.3422 | 3847028.0745 | 7941086.1926 | 13226234.7383 | 10263579.2995 | 13561439.7163 | 21944244.9836 | 21944244.9836 | 21944244.9836 | 21944244.9836 | 21944244.9836 | 21944244.9836
|  |  | N-3 |  |  | Catastrophic |  | 156947465.1773 | 136618600.0572 | 162033589.8033 | 168633343.7983 | 167839822.5705 | 169303753.7545 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178
|  |  | N-4 |  |  | Catastrophic |  | 156947465.1773 | 136618600.0572 | 162033589.8033 | 168633343.7983 | 167839822.5705 | 169303753.7545 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 9.139% | 9.772% | 10.53% | 11.36% | 12.31% | 13.38% | 14.55% | 15.83% | 17.24% | 18.77% | 20.46% | 22.29%
|  |  | Major |  |  |  |  | 1.015% | 1.086% | 1.17% | 1.262% | 1.368% | 1.487% | 1.617% | 1.759% | 1.915% | 2.086% | 2.273% | 2.477%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 68941.233 | 71619.1311 | 81658.2289 | 91237.5595 | 98468.8849 | 107834.2989 | 127427.7901 | 138644.356 | 150927.7594 | 164383.3127 | 179126.9598 | 195192.9741
|  |  | Network Performance |  |  | Major |  | 67640.3631 | 49728.6012 | 101977.4842 | 177105.6194 | 151355.9308 | 213622.33 | 368967.8782 | 401445.5075 | 437012.1708 | 475972.8006 | 518663.1129 | 565182.3473
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 640342.5913 | 684688.7745 | 737735.4484 | 796052.7289 | 862698.4369 | 937598.7309 | 1019574.1015 | 1109319.989 | 1207601.8475 | 1315262.3012 | 1433229.0387 | 1561776.2903
|  |  | Other major risks |  |  | Major |  | 382003.8111 | 408459.0419 | 440104.6513 | 474894.5024 | 514652.7737 | 559335.4141 | 608238.7738 | 661777.7254 | 720408.9098 | 784635.004 | 855009.4316 | 931695.7877
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853
|  |  | Subtotal |  |  |  |  | 1224356.6838 | 1279924.234 | 1426904.4982 | 1604719.0955 | 1692604.7116 | 1883819.4592 | 2189637.2289 | 2376616.2632 | 2581379.3728 | 2805682.1038 | 3051457.2283 | 3319276.0848
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 85490.4425 | 5614994.3332 | 7547895.2662 | 7547895.2662 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 108.5% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 789866.5737
|  |  | Post-replacement opex |  |  | 56765.6538
|  |  | Total annuity |  |  | 846632.2275
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 1224356.6838 | 1279924.234 | 1426904.4982 | 1604719.0955 | 1692604.7116 | 1883819.4592 | 2189637.2289 | 2376616.2632 | 2581379.3728 | 2805682.1038 | 3051457.2283 | 3319276.0848
|  |  | Annualised cost |  |  |  |  | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
CitiPower - LQ Switchboard Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 5906636.3422 | 0 | 0 | 0 | 0 | 100% | 5906636.3422 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 32586.1661 | 0 | 0 | 0 | 100% | 32586.1661 | 32586.1661
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 13620028.2015 | 0 | 0 | 100% | 13620028.2015 | 13620028.2015
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 17015134.3429 | 0 | 100% | 17015134.3429 | 17015134.3429
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 85801.3168 | 100% | 85801.3168 | 85801.3168
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 754342.6637 | 0 | 0 | 0 | 0 | 100% | 754342.6637 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 6517.2332 | 0 | 0 | 0 | 100% | 6517.2332 | 6517.2332
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 5671711.4476 | 0 | 100% | 5671711.4476 | 5671711.4476
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 10911.6892 | 100% | 10911.6892 | 10911.6892
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 754342.6637 | 6517.2332 | 46631.1504 | 5671711.4476 | 10911.6892 | 100% | 6490114.1843 | 5735771.5205
[5 empty] | 2 | Major |  | 5906636.3422 | 32586.1661 | 13666659.3519 | 17015134.3429 | 85801.3168 | 100% | 36706817.52 | 30800181.1778
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 43196931.7042; 2026: 36535952.6983
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 199.5
|  |  | N-1 Rating before transfers, MVA |  |  | 131
|  |  | N-2 Rating before transfers, MVA |  |  | 65.5
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 11.1
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 87.134 | 84.6868 | 88.5647 | 92.0892 | 91.9457 | 93.0544 | 100.7494 | 100.7494 | 100.7494 | 100.7494 | 100.7494 | 100.7494
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 81.8035 | 79.4637 | 84.5376 | 87.3705 | 86.9098 | 87.3981 | 95.1339 | 95.1339 | 95.1339 | 95.1339 | 95.1339 | 95.1339
|  |  | Selected |  |  | 70% |  | 83.4027 | 81.0306 | 85.7458 | 88.7861 | 88.4206 | 89.095 | 96.8186 | 96.8186 | 96.8186 | 96.8186 | 96.8186 | 96.8186
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 6.8027 | 4.4306 | 9.1458 | 12.1861 | 11.8206 | 12.495 | 20.2186 | 20.2186 | 20.2186 | 20.2186 | 20.2186 | 20.2186
|  |  | N-3 |  |  |  |  | 72.3027 | 69.9306 | 74.6458 | 77.6861 | 77.3206 | 77.995 | 85.7186 | 85.7186 | 85.7186 | 85.7186 | 85.7186 | 85.7186
|  |  | N-4 |  |  |  |  | 72.3027 | 69.9306 | 74.6458 | 77.6861 | 77.3206 | 77.995 | 85.7186 | 85.7186 | 85.7186 | 85.7186 | 85.7186 | 85.7186
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2.5 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 8 | 7 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | Unserved energy day 2 |  |  |  | 3 | 2.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 5 | 4.5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  |  |  | Unserved energy day 1 |  |  |  | 8 | 7 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | Unserved energy day 2 |  |  |  | 3 | 2.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 5 | 4.5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 754342.6637 | 732888.411 | 775534.8497 | 803033.8247 | 799727.4862 | 805827.1995 | 875683.91 | 875683.91 | 875683.91 | 875683.91 | 875683.91 | 875683.91
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 5906636.3422 | 3847028.0745 | 7941086.1926 | 13226234.7383 | 10263579.2995 | 13561439.7163 | 21944244.9836 | 21944244.9836 | 21944244.9836 | 21944244.9836 | 21944244.9836 | 21944244.9836
|  |  | N-3 |  |  | Catastrophic |  | 156947465.1773 | 136618600.0572 | 162033589.8033 | 168633343.7983 | 167839822.5705 | 169303753.7545 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178
|  |  | N-4 |  |  | Catastrophic |  | 156947465.1773 | 136618600.0572 | 162033589.8033 | 168633343.7983 | 167839822.5705 | 169303753.7545 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178 | 204676300.7178
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 9.139% | 9.772% | 10.53% | 11.36% | 12.31% | 13.38% | 14.55% | 15.83% | 17.24% | 18.77% | 20.46% | 22.29%
|  |  | Major |  |  |  |  | 1.015% | 1.086% | 1.17% | 1.262% | 1.368% | 1.487% | 1.617% | 1.759% | 1.915% | 2.086% | 2.273% | 2.477%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 68941.233 | 71619.1311 | 81658.2289 | 91237.5595 | 98468.8849 | 107834.2989 | 127427.7901 | 138644.356 | 150927.7594 | 164383.3127 | 179126.9598 | 195192.9741
|  |  | Network Performance |  |  | Major |  | 67640.3631 | 49728.6012 | 101977.4842 | 177105.6194 | 151355.9308 | 213622.33 | 368967.8782 | 401445.5075 | 437012.1708 | 475972.8006 | 518663.1129 | 565182.3473
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 524206.2787 | 560509.5764 | 603935.3923 | 651675.9065 | 706234.3555 | 767550.29 | 834658.1235 | 908127.167 | 988584.0475 | 1076718.5657 | 1173290.1593 | 1278523.3224
|  |  | Other major risks |  |  | Major |  | 312767.153 | 334427.4793 | 360337.449 | 388821.7792 | 421374.0233 | 457958.1145 | 497997.9364 | 541833.1678 | 589837.6853 | 642423.0576 | 700042.4025 | 762829.6643
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607
|  |  | Subtotal |  |  |  |  | 1027087.5885 | 1069817.3487 | 1201441.1152 | 1362373.4254 | 1430965.7552 | 1600497.594 | 1882584.2888 | 2043582.759 | 2219894.2236 | 2413030.2973 | 2624655.1952 | 2855260.8689
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 69946.7257 | 4594086.2726 | 6175550.6723 | 6175550.6723 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 108.5% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 646254.4694
|  |  | Post-replacement opex |  |  | 46444.6258
|  |  | Total annuity |  |  | 692699.0952
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 1027087.5885 | 1069817.3487 | 1201441.1152 | 1362373.4254 | 1430965.7552 | 1600497.594 | 1882584.2888 | 2043582.759 | 2219894.2236 | 2413030.2973 | 2624655.1952 | 2855260.8689
|  |  | Annualised cost |  |  |  |  | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
CitiPower - LQ Switchboard Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 20670019.7467 | 0 | 0 | 0 | 0 | 100% | 20670019.7467 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 32586.1661 | 0 | 0 | 0 | 100% | 32586.1661 | 32586.1661
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 16646701.1351 | 0 | 0 | 100% | 16646701.1351 | 16646701.1351
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 20796275.308 | 0 | 100% | 20796275.308 | 20796275.308
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 104868.2761 | 100% | 104868.2761 | 104868.2761
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 1019024.3001 | 0 | 0 | 0 | 0 | 100% | 1019024.3001 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 6517.2332 | 0 | 0 | 0 | 100% | 6517.2332 | 6517.2332
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 6932091.7693 | 0 | 100% | 6932091.7693 | 6932091.7693
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 13336.509 | 100% | 13336.509 | 13336.509
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 1019024.3001 | 6517.2332 | 56993.6283 | 6932091.7693 | 13336.509 | 100% | 8027963.4401 | 7008939.1399
[5 empty] | 2 | Major |  | 20670019.7467 | 32586.1661 | 16703694.7635 | 20796275.308 | 104868.2761 | 100% | 58307444.2604 | 37637424.5137
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 66335407.7005; 2026: 44646363.6536
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 199.5
|  |  | N-1 Rating before transfers, MVA |  |  | 131
|  |  | N-2 Rating before transfers, MVA |  |  | 65.5
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 11.1
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 96.306 | 93.6012 | 97.8873 | 101.7828 | 101.6243 | 102.8496 | 111.3546 | 111.3546 | 111.3546 | 111.3546 | 111.3546 | 111.3546
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 90.4145 | 87.8283 | 93.4364 | 96.5674 | 96.0582 | 96.5979 | 105.1481 | 105.1481 | 105.1481 | 105.1481 | 105.1481 | 105.1481
|  |  | Selected |  |  | 70% |  | 92.1819 | 89.5602 | 94.7716 | 98.1321 | 97.728 | 98.4734 | 107.01 | 107.01 | 107.01 | 107.01 | 107.01 | 107.01
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 15.5819 | 12.9602 | 18.1716 | 21.5321 | 21.128 | 21.8734 | 30.41 | 30.41 | 30.41 | 30.41 | 30.41 | 30.41
|  |  | N-3 |  |  |  |  | 81.0819 | 78.4602 | 83.6716 | 87.0321 | 86.628 | 87.3734 | 95.91 | 95.91 | 95.91 | 95.91 | 95.91 | 95.91
|  |  | N-4 |  |  |  |  | 81.0819 | 78.4602 | 83.6716 | 87.0321 | 86.628 | 87.3734 | 95.91 | 95.91 | 95.91 | 95.91 | 95.91 | 95.91
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 1 |  |  |  | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | Unserved energy day 2 |  |  |  | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  |  |  | Unserved energy day 1 |  |  |  | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | Unserved energy day 2 |  |  |  | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 1019024.3001 | 990042.2394 | 1047652.3408 | 1084800.0789 | 1080333.6217 | 1088573.5853 | 1182941.4223 | 1182941.4223 | 1182941.4223 | 1182941.4223 | 1182941.4223 | 1182941.4223
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 20670019.7467 | 17192172.4525 | 24105384.6257 | 28563113.2013 | 28027138.3369 | 29015933.9611 | 48408089.2918 | 48408089.2918 | 48408089.2918 | 48408089.2918 | 48408089.2918 | 48408089.2918
|  |  | N-3 |  |  | Catastrophic |  | 215116663.6645 | 208160969.0761 | 221987393.4225 | 253993135.6309 | 252813990.9294 | 254989341.3027 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898
|  |  | N-4 |  |  | Catastrophic |  | 215116663.6645 | 208160969.0761 | 221987393.4225 | 253993135.6309 | 252813990.9294 | 254989341.3027 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 11.17% | 11.94% | 12.87% | 13.89% | 15.05% | 16.36% | 17.79% | 19.35% | 21.07% | 22.94% | 25% | 27.24%
|  |  | Major |  |  |  |  | 1.241% | 1.327% | 1.43% | 1.543% | 1.672% | 1.817% | 1.976% | 2.15% | 2.341% | 2.549% | 2.778% | 3.027%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 113826.948 | 118248.351 | 134823.6255 | 150639.7913 | 162579.231 | 178042.205 | 210392.4721 | 228911.8314 | 249192.6164 | 271408.7054 | 295751.53 | 322277.6785
|  |  | Network Performance |  |  | Major |  | 269189.7085 | 241293.5103 | 359663.804 | 457447.8802 | 486708.7468 | 547084.2228 | 980003.4002 | 1066266.1591 | 1160733.5993 | 1264215.642 | 1377603.9712 | 1501162.174
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 782911.8019 | 837131.4504 | 901988.7121 | 973290.0557 | 1054774.1113 | 1146350.597 | 1246577.3913 | 1356304.7708 | 1476468.6143 | 1608099.1522 | 1752330.6188 | 1909498.3001
|  |  | Other major risks |  |  | Major |  | 467130.1931 | 499480.7527 | 538178.3238 | 580720.8048 | 629338.8771 | 683978.6735 | 743779.7414 | 809249.4045 | 880946.0621 | 959484.4089 | 1045541.1942 | 1139316.469
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853 | 65428.6853
|  |  | Subtotal |  |  |  |  | 1698487.3368 | 1761582.7497 | 2000083.1507 | 2227527.2173 | 2398829.6517 | 2620884.3837 | 3246181.6903 | 3526160.8511 | 3832769.5775 | 4168636.5939 | 4536655.9996 | 4937683.3069
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 85490.4425 | 5614994.3332 | 7547895.2662 | 7547895.2662 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 108.5% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 789866.5737
|  |  | Post-replacement opex |  |  | 56765.6538
|  |  | Total annuity |  |  | 846632.2275
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 1698487.3368 | 1761582.7497 | 2000083.1507 | 2227527.2173 | 2398829.6517 | 2620884.3837 | 3246181.6903 | 3526160.8511 | 3832769.5775 | 4168636.5939 | 4536655.9996 | 4937683.3069
|  |  | Annualised cost |  |  |  |  | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
CitiPower - LQ Switchboard Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 20670019.7467 | 0 | 0 | 0 | 0 | 100% | 20670019.7467 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 32586.1661 | 0 | 0 | 0 | 100% | 32586.1661 | 32586.1661
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 13620028.2015 | 0 | 0 | 100% | 13620028.2015 | 13620028.2015
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 17015134.3429 | 0 | 100% | 17015134.3429 | 17015134.3429
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 104868.2761 | 100% | 104868.2761 | 104868.2761
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 1019024.3001 | 0 | 0 | 0 | 0 | 100% | 1019024.3001 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 6517.2332 | 0 | 0 | 0 | 100% | 6517.2332 | 6517.2332
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 5671711.4476 | 0 | 100% | 5671711.4476 | 5671711.4476
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 13336.509 | 100% | 13336.509 | 13336.509
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 1019024.3001 | 6517.2332 | 46631.1504 | 5671711.4476 | 13336.509 | 100% | 6757220.6405 | 5738196.3403
[5 empty] | 2 | Major |  | 20670019.7467 | 32586.1661 | 13666659.3519 | 17015134.3429 | 104868.2761 | 100% | 51489267.8838 | 30819248.1371
[5 empty] | 3 | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 58246488.5243; 2026: 36557444.4774
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 199.5
|  |  | N-1 Rating before transfers, MVA |  |  | 131
|  |  | N-2 Rating before transfers, MVA |  |  | 65.5
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 11.1
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 96.306 | 93.6012 | 97.8873 | 101.7828 | 101.6243 | 102.8496 | 111.3546 | 111.3546 | 111.3546 | 111.3546 | 111.3546 | 111.3546
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 90.4145 | 87.8283 | 93.4364 | 96.5674 | 96.0582 | 96.5979 | 105.1481 | 105.1481 | 105.1481 | 105.1481 | 105.1481 | 105.1481
|  |  | Selected |  |  | 70% |  | 92.1819 | 89.5602 | 94.7716 | 98.1321 | 97.728 | 98.4734 | 107.01 | 107.01 | 107.01 | 107.01 | 107.01 | 107.01
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 15.5819 | 12.9602 | 18.1716 | 21.5321 | 21.128 | 21.8734 | 30.41 | 30.41 | 30.41 | 30.41 | 30.41 | 30.41
|  |  | N-3 |  |  |  |  | 81.0819 | 78.4602 | 83.6716 | 87.0321 | 86.628 | 87.3734 | 95.91 | 95.91 | 95.91 | 95.91 | 95.91 | 95.91
|  |  | N-4 |  |  |  |  | 81.0819 | 78.4602 | 83.6716 | 87.0321 | 86.628 | 87.3734 | 95.91 | 95.91 | 95.91 | 95.91 | 95.91 | 95.91
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 1 |  |  |  | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | Unserved energy day 2 |  |  |  | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  |  |  | Unserved energy day 1 |  |  |  | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  |  | Unserved energy day 2 |  |  |  | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 1019024.3001 | 990042.2394 | 1047652.3408 | 1084800.0789 | 1080333.6217 | 1088573.5853 | 1182941.4223 | 1182941.4223 | 1182941.4223 | 1182941.4223 | 1182941.4223 | 1182941.4223
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 20670019.7467 | 17192172.4525 | 24105384.6257 | 28563113.2013 | 28027138.3369 | 29015933.9611 | 48408089.2918 | 48408089.2918 | 48408089.2918 | 48408089.2918 | 48408089.2918 | 48408089.2918
|  |  | N-3 |  |  | Catastrophic |  | 215116663.6645 | 208160969.0761 | 221987393.4225 | 253993135.6309 | 252813990.9294 | 254989341.3027 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898
|  |  | N-4 |  |  | Catastrophic |  | 215116663.6645 | 208160969.0761 | 221987393.4225 | 253993135.6309 | 252813990.9294 | 254989341.3027 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898 | 279902450.2898
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 11.17% | 11.94% | 12.87% | 13.89% | 15.05% | 16.36% | 17.79% | 19.35% | 21.07% | 22.94% | 25% | 27.24%
|  |  | Major |  |  |  |  | 1.241% | 1.327% | 1.43% | 1.543% | 1.672% | 1.817% | 1.976% | 2.15% | 2.341% | 2.549% | 2.778% | 3.027%
Catastrophic | bar: 2019 to 2030
Risk costs
|  |  | Network Performance |  |  | Significant |  | 113826.948 | 118248.351 | 134823.6255 | 150639.7913 | 162579.231 | 178042.205 | 210392.4721 | 228911.8314 | 249192.6164 | 271408.7054 | 295751.53 | 322277.6785
|  |  | Network Performance |  |  | Major |  | 269189.7085 | 241293.5103 | 359663.804 | 457447.8802 | 486708.7468 | 547084.2228 | 980003.4002 | 1066266.1591 | 1160733.5993 | 1264215.642 | 1377603.9712 | 1501162.174
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other significant risks |  |  | Significant |  | 640967.4198 | 685356.8749 | 738455.3102 | 796829.4951 | 863540.2341 | 938513.6137 | 1020568.9737 | 1110402.4328 | 1208780.192 | 1316545.6977 | 1434627.5439 | 1563300.2283
|  |  | Other major risks |  |  | Major |  | 382507.611 | 408997.7318 | 440685.0766 | 475520.8097 | 515331.5156 | 560073.085 | 609040.9401 | 662650.5008 | 721359.01 | 785669.8078 | 856137.0476 | 932924.5403
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607 | 53532.5607
|  |  | Subtotal |  |  |  |  | 1460024.248 | 1507429.0287 | 1727160.377 | 1933970.537 | 2081692.2883 | 2277245.6873 | 2873538.3468 | 3121763.4847 | 3393597.9784 | 3691372.4136 | 4017652.6535 | 4373197.1818
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 69946.7257 | 4594086.2726 | 6175550.6723 | 6175550.6723 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 108.5% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 646254.4694
|  |  | Post-replacement opex |  |  | 46444.6258
|  |  | Total annuity |  |  | 692699.0952
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 1460024.248 | 1507429.0287 | 1727160.377 | 1933970.537 | 2081692.2883 | 2277245.6873 | 2873538.3468 | 3121763.4847 | 3393597.9784 | 3691372.4136 | 4017652.6535 | 4373197.1818
|  |  | Annualised cost |  |  |  |  | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
CitiPower - LQ Switchboard Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 1314045.9021 | 1368840.1333 | 1581835.2548 | 1760823.3007 | 1895618.2655 | 2070355.5133 | 2546672.6975 | 2765602.6014 | 3005355.513 | 3267986.9654 | 3555760.0014 | 3869343.5896
|  |  | Annualised cost | Scenario Base case | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614 | 769665.6614
|  |  | Risk cost | Scenario A | 1224356.6838 | 1279924.234 | 1426904.4982 | 1604719.0955 | 1692604.7116 | 1883819.4592 | 2189637.2289 | 2376616.2632 | 2581379.3728 | 2805682.1038 | 3051457.2283 | 3319276.0848
|  |  | Annualised cost | Scenario A | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275
|  |  | Risk cost | Scenario B | 1027087.5885 | 1069817.3487 | 1201441.1152 | 1362373.4254 | 1430965.7552 | 1600497.594 | 1882584.2888 | 2043582.759 | 2219894.2236 | 2413030.2973 | 2624655.1952 | 2855260.8689
|  |  | Annualised cost | Scenario B | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952
|  |  | Risk cost | Scenario C | 1698487.3368 | 1761582.7497 | 2000083.1507 | 2227527.2173 | 2398829.6517 | 2620884.3837 | 3246181.6903 | 3526160.8511 | 3832769.5775 | 4168636.5939 | 4536655.9996 | 4937683.3069
|  |  | Annualised cost | Scenario C | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275 | 846632.2275
|  |  | Risk cost | Scenario D | 1460024.248 | 1507429.0287 | 1727160.377 | 1933970.537 | 2081692.2883 | 2277245.6873 | 2873538.3468 | 3121763.4847 | 3393597.9784 | 3691372.4136 | 4017652.6535 | 4373197.1818
|  |  | Annualised cost | Scenario D | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952 | 692699.0952
Charts
End