12 March, 2010

Mr Chris Pattas

General Manager

Network Regulation South

Australian Energy Regulator

GPO Box 520

Melbourne 3001

Dear Mr Pattas,

#### Proposed 2010-11 Distribution Loss Factors

CitiPower has completed a review of its proposed Distribution Loss Factors (DLF’s) for 2010-11 taking into account clause 3.6.3 of the National Electricity Rules including:-

- Site specific DLF’s for end users with load of more than 40 GWh or a demand of more than 10MW;

- Site specific DLF’s for generators over 10MW;

The 2010-11 loss factors are based on forecast sales and demand data with estimated losses derived from an average top down loss of 4.07% (average of last 5 years) of sales.

The proposed DLF’s set out in the attached submission have been calculated in accordance with the Essential Services Commission’s guidance paper – Calculation Methodology for Distribution Loss Factors (DLF’s) for the Victorian Jurisdiction, 14 February 2007.

The actual top down loss for 2008-09 has been calculated to be 4.11%. See attached reconciliation for 2008-09.

CitiPower has identified four end use customers that qualify for site specific loss factors as set out in the attached submission. The site specific loss factors for these connection points have been calculated taking into account the characteristics of their specific supply arrangements and their electricity consumption characteristics.

Consistent with the requirements set out in your letter of 19 October 2009, please find attached:

- Citipower’s 2010-11 DLF Review;

- a copy of the published methodology used to calculate the DLF’s; and

- a letter and report from independent consultants, Parsons Brinckerhoff Australia Ltd, to certify that the DLF’s calculated by CitiPower are consistent with the published methodology and are consistent with the requirements of clause 3.6.3 of the National Electricity Rules.

Please give me a call on telephone 9683 4282 if you require further information or wish to discuss any aspect of this matter.

Yours Sincerely

Rolf Herrmann

Manager Regulation

2010-11 DLF Proposal

| Company Name | CITIPOWER PTY |
| --- | --- |

Forecast Sales (MWh) – 2010/11 (Including loads for site specific DLF’s)

|  | DLF A | DLF B | DLF C | DLF D | DLF E | Total |
| --- | --- | --- | --- | --- | --- | --- |
| Short Subtrans. | 114,358 | 7,536 | 433,143 | 1,693,148 | 3,764,928 | 6,013,112 |
| Long Subtrans. | - | - | - | - | - | - |

Forecast Losses (MWh) – 2010/11 (Including loads for site specific DLF’s)

|  | DLF A | DLF B | DLF C | DLF D | DLF E | Total |
| --- | --- | --- | --- | --- | --- | --- |
| Short Subtransmission | 20,071 | 47,104 | 31,777 | 126,144 | 19,876 | 244,971 |
| Long Subtransmission | - | - | - | - | - | - |

Proposed Network Average DLFs for General Customers

| DLF TYPE | DLF A | DLF B | DLF C | DLF D | DLF E |
| --- | --- | --- | --- | --- | --- |
| 2009/10 DLFs |  |  |  |  |  |
| Short Subtransmission | 1.0034 | 1.0118 | 1.0174 | 1.0409 | 1.0460 |
| DLF CODE | ESTA | EZSB | EHVC | EDSD | ELVE |
| Long Subtransmission | --- | --- | --- | --- | --- |
| Proposed 2010/11 DLFs |  |  |  |  |  |
| Short Subtransmission | 1.0033 | 1.0113 | 1.0166 | 1.0399 | 1.0451 |
| DLF CODE | ESTA | EZSB | EHVC | EDSD | ELVE |
| Long Subtransmission | --- | --- | --- | --- | --- |
| % Difference |  |  |  |  |  |
| Short Subtransmission | -0.007% | -0.046% | -0.080% | -0.100% | -0.089% |
| Long Subtransmission | --- | --- | --- | --- | --- |

2010-11 DLF Proposal  cont.

Site-Specific Distribution Loss Factors (DLF) for Large Customers

(Customers with demand > 10 MW or annual energy consumption > 40 GWh)

| No | NMI Number | DLF CODE | DLF 2009/10 | Proposed DLF 2010/11 | % Difference |
| --- | --- | --- | --- | --- | --- |
| 1 | VAAA000673 | ESS4 | 1.0181 | 1.0181 | 0.001% |
| 2 | VAAA000577 | ESS3 | 1.0152 | 1.0140 | -0.115% |
| 3 | VAAA000574 | ESS2 | 1.0146 | 1.0132 | -0.134% |
| 4 | VAAA000431 | ESS1 | 1.0166 | 1.0158 | -0.077% |

Energy Procured (MWh) - 2008-09

| Energy obtained from transmission connections | 6,234,689 |
| --- | --- |
| Energy obtained from embedded generation | 117,329 |
| Inter DB supply from other Distributors | 17,137 |
| Total Energy Procured (pa) | 6,369,065 |

Energy Supplied (MWh) – 2008-09

| Total annual energy supplied to CitiPower customers | 6,098,571 |
| --- | --- |
| Inter DB supply to other distributors | 19,190 |
| Net Energy Supplied (pa) | 6,117,761 |

RECONCILIATION -2008/09 - CITIPOWER

|  | MWh |  |
| --- | --- | --- |
| MEi x DLFi for 2008/09 | 6,390,246 | A |
| Actual Consumption or Sales for 2008/09 | 6,117,761 | B |
| Losses recovered through application of DLFs to customers' actual consumption for 2008/09 | 272,485 | C =A-B |
| Actual Measured Losses 2008/09 | 251,304 | D |
| Actual Measured Losses 2008/09 as %age of Sales | 4.11% | D/B |
| Difference or error in overall losses | 21,181 | E = C - D |
| Difference or error in overall losses as % of total energy sales (Over-recovered) | 0.35% | F = E/B |

Definitions:	DLF A	is the distribution loss factor to be applied to a second tier customer or pool customer connected to either a 66kV or a 22kV subtransmission line.

DLF B	is the distribution loss factor to be applied to a second tier customer or pool customer connected to the lower voltage side of a zone substation

DLF C	is the distribution loss factor to be applied to a second tier customer or pool customer connected to a distribution line at voltages of 22kV, 11kV or 6.6kV.

DLF D	is the distribution loss factor to be applied to a second tier customer or pool customer connected to the lower voltage terminals of a distribution transformer.

DLF E	is the distribution loss factor to be applied to a second tier customer or pool customer connected to low voltage lines of 240/415 V