## INDEX
Operation and Maintenance Model (O&M Model)
Prepared for the Directlink Joint Venture
Presents a bottom up cost study of the Directlink HVDC link
Period July 2015 to June 2020
INDEX
Costed Worksheets | Cost (2014$) | Hyperlink to worksheet
ELECTRICITY COSTS | 3816967.4208 | …
CABLE REPAIRS | 2030266.9309 | …
CONTROL ROOM OPERATIONS | 1111355.8247 | …
OPERATIONS MANAGER | 811137.6542 | …
SENIOR RELIABILITY ENGINEER | 729617.2352 | …
RELIABILITY ENGINEER | 698889.0289 | …
PHASE REACTOR MAINTENANCE | 570175.6292 | …
WORKS PLANNER | 565289.0291 | …
WORK PRACTICES SPECIALIST | 565289.0291 | …
VEGETATION MANAGEMENT | 502097.7 | …
POWER TRANSFORMER MAINTENANCE | 460285.1846 | …
CIRCUIT BREAKER MAINTENANCE | 398815.3484 | …
TRAVEL | 394698.4809 | …
SITE SECURITY | 316025.5666 | …
REMOTE COMMUNICATIONS | 287807.9393 | …
CONTROL SYSTEM REPAIRS | 218096.8106 | …
REACTOR MAINTENANCE | 212865.682 | …
OTHER COSTS | 201368.8843 | …
INCIDENTAL INVESTIGATIONS | 179573.2652 | …
ENERGISED MAINTENANCE INSPECTION | 178692.8228 | …
AIR BLAST COOLER MAINTENANCE | 172301.2813 | …
DIAL BEFORE YOU DIG | 168226.219 | …
FIRE SPRINKER SYSTEM | 150271.7525 | …
YARD MAINTENANCE | 140777.7998 | …
CABLE MARKER SIGN MAINTENANCE | 140064.6824 | …
BUILDING AIR-CONDITIONERS | 137349.2043 | …
VALVE COOLING SYSTEM MAINTENANCE | 116498.894 | …
TRAINING COURSES FOR CONTRACTORS | 106947.4361 | …
IGBT VALVE REPAIRS | 93724.6565 | …
NITROGEN BOTTLE REPLACEMENT | 87120.759 | …
FIRE DETECTION & ALARM SYSTEM | 70272.6921 | …
OIL FILLED CAPACITOR MAINTENANCE | 69234.7253 | …
IGBT VALVE MAINTENANCE | 67609.441 | …
PRESTART INSPECTIONS | 41032.6967 | …
ONSITE TEST EQUIPMENT MAINTENANCE | 39514.5577 | …
VALVE COOLING MCC THERMOGRAPHIC IMAGING | 38363.6232 | …
CONVERTER STATION THERMOGRAPHIC INSPECTION | 38363.6232 | …
ZINC OXIDE SURGE ARRESTOR MAINTENANCE | 36385.6684 | …
VALVE DEHUMIDIFIER MAINTENANCE | 35496.6918 | …
UNINTERRUPTIBLE POWER SUPPLY | 34083.1784 | …
OUTDOOR POST TYPE CURRENT TRANSFORMER | 31086.5688 | …
AC FILTER RESISTOR MAINTENANCE | 31051.809 | …
VALVE COOLING SYSTEM PUMP MAINTENANCE | 28384.8793 | …
PHASE REACTOR FAN MAINTENANCE | 26914.4278 | …
PORTABLE FIRE EXTINGUISHER INSPECTION | 26271.9361 | …
EMERGENCY LIGHTING MAINTENANCE | 25807.1581 | …
NITROGEN DISCHARGE UNIT MAINTENANCE | 19124.5643 | …
ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | 19050.6254 | …
DIRECT VOLTAGE DIVIDER MAINTENANCE | 17147.8619 | …
INSPECT SPILL KITS | 16469.4879 | …
CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE | 15494.7192 | …
HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | 13716.7661 | …
CABLE SCREEN CURRENT TRANSFORMER | 12383.3012 | …
DC ZERO SEQUENCE SMOOTHING REACTOR MAINTENANCE | 8382.9067 | …
AIR GAP SURGE LIMITER MAINTENANCE | 8382.9067 | …
FUNCTIONAL TEST OF HIGH VOLTAGE TEST EQUIPMENT | 4474.8413 | …
CHECK EYE WASH STATION | 3880.7027 | …
DISCONNECTOR & EARTH SWITCH MAINTENANCE | 3629.8044 | …
MOTORISED OPERATING MECHANISM MAINTENANCE | 3629.8044 | …
INSULATING WALL BUSHING MAINTENANCE | 3008.2117 | …
PLC FILTER TUNING UNIT MAINTENANCE | 2413.6742 | …
FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | 970.1757 | …
VALVE HUMIDITY CONTROL SYSTEM | 0 | …
MANUAL OPERATING MECHANISM MAINTENANCE | 0 | …
Summary Worksheets
Read Me |  | …
Asset Mgt Team |  | …
Summary of PMs |  | …
Modelling Assumptions |  | …
Supporting Worksheets
Blank |  | …
DL OPEX Budget |  | …
Schematics |  | …
Components in Schematic |  | …
Grouped Components |  | …
ABB Maintenance |  | …
Byron Bay Trees |  | …
Electricity Invoices |  | …
Maintenance Documents |  | …
Chart Summary
DL PMs |  | …
OnSite Contractors |  | …

## Read Me
READ ME
Return to Index
MOMCSA
Directlink is operated in accordance with the Management Operations, Maintenance and Commercial Services Agreement (the MOMCSA)
The MOMCSA requires a margin to be applied to all costs incurred in the operation and maintenance of Directlink
Costs shown on individual worksheets describing maintenance tasks are the actual incurred costs and do not include the margin
Costs shown on the Summary Sheets have been adjusted and include the margin
The applicable margin percentage is included in the Modelling Assumptions worksheet
KEY for information shown in the worksheets
Information shown in Red have been estimated by Phacelift
Information shown in Blue have been discussed with APA staff
Important notes are highlighted
Disclaimer
This O&M Model its findings and its outcomes have been prepared for distribution to the Directlink Joint Venture (“the company”) and the Australian Energy Regulator (AER) in accordance with the agreed scope of work and associated terms and conditions. Phacelift Consulting Services Pty Ltd and its staff (“Phacelift”) disclaim any assumption of responsibility for any reliance on this model to any person other than the company or AER or for any purpose other than that for which it was prepared. Whilst Phacelift has prepared this model with due care and skill, it is a condition on the use of this model by the company that: (a) any compensation for liability made by the company on Phacelift in relation to the advice or content provided in the model be limited to a payment which is equal to the fees paid for that advice; and (b) the company indemnify Phacelift for any other loss suffered by the company following any negligence claim made against Phacelift.

## Summary
SUMMARY
Return to Index
With Escalation (2014$) |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 |  | Total in AER Period
APA Staff Costs |  | 1147888.7577 | 1066650.8105 | 1100631.3048 | 1126427.0271 | 1151751.7477 |  | 5593349.6478
APA Material Costs |  | 1198063.3466 | 1150031.0398 | 1194458.7541 | 1227273.1076 | 1281016.4351 |  | 6050842.6832
Contractor Labour |  | 1227375.4179 | 808596.1049 | 891801.0324 | 859825.2209 | 898305.2121 |  | 4685902.9881
Contractor Materials |  | 5007.86 | 4667.96 | 4807.9988 | 4952.2388 | 5100.8059 |  | 24536.8635
|  | 3578335.3822 | 3029945.9151 | 3191699.09 | 3218477.5944 | 3336174.2008 |  | 16354632.1826
[7 empty] | Average per year | 3270926.4365
Without Escalation |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  | 1119891.4709 | 1015253.5972 | 1022045.5813 | 1020487.2916 | 1017980.7205 |  | 5195658.6613
APA Material Costs |  | 1163168.2977 | 1084014.5535 | 1093098.9663 | 1090416.2604 | 1105016.0298 |  | 5535714.1076
Contractor Labour |  | 1197439.4321 | 769633.4133 | 828125.9133 | 778959.2133 | 793970.9133 |  | 4368128.8853
Contractor Materials |  | 4862 | 4400 | 4400 | 4400 | 4400 |  | 22462
|  | 3485361.2007 | 2873301.5639 | 2947670.4608 | 2894262.7652 | 2921367.6636 |  | 15121963.6542
As shown in the Report |  | Budget | No escalation from 2014$ | Adjusted to 2014$
|  | 2015/16 | 3485361.2007 | 3578335.3822
|  | 2016/17 | 2873301.5639 | 3029945.9151
|  | 2017/18 | 2947670.4608 | 3191699.09
|  | 2018/19 | 2894262.7652 | 3218477.5944
|  | 2019/20 | 2921367.6636 | 3336174.2008
|  | Total | 15121963.6542 | 16354632.1826
[5 empty] | Cumulative | Rank
Electricity Costs | … | ELECTRICITY COSTS | 3816967.4208 |  | 23.34% | 1
Cable Repairs | … | CABLE REPAIRS | 2030266.9309 |  | 12.41% | 2
Control Room Costs | … | CONTROL ROOM OPERATIONS | 1111355.8247 |  | 6.795% | 3
Operations Manager | … | OPERATIONS MANAGER | 811137.6542 |  | 4.96% | 4
Senior Reliability Engineer | … | SENIOR RELIABILITY ENGINEER | 729617.2352 |  | 4.461% | 5
Reliability Engineer | … | RELIABILITY ENGINEER | 698889.0289 |  | 4.273% | 6
0104 (2) | … | PHASE REACTOR MAINTENANCE | 570175.6292 |  | 3.486% | 7
Works Planner | … | WORKS PLANNER | 565289.0291 |  | 3.456% | 8
Work Practices Specialist | … | WORK PRACTICES SPECIALIST | 565289.0291 |  | 3.456% | 9
0017 | … | VEGETATION MANAGEMENT | 502097.7 |  | 3.07% | 10
0028 | … | POWER TRANSFORMER MAINTENANCE | 460285.1846 |  | 2.814% | 11
0140 | … | CIRCUIT BREAKER MAINTENANCE | 398815.3484 |  | 2.439% | 12
Travel | … | TRAVEL | 394698.4809 |  | 2.413% | 13
Site Security | … | SITE SECURITY | 316025.5666 |  | 1.932% | 14
Remote Comms | … | REMOTE COMMUNICATIONS | 287807.9393 |  | 1.76% | 15
Control System Repairs | … | CONTROL SYSTEM REPAIRS | 218096.8106 |  | 1.334% | 16
0104 (1) | … | REACTOR MAINTENANCE | 212865.682 |  | 1.302% | 17
Other Items | … | OTHER COSTS | 201368.8843 |  | 1.231% | 18
Incidental Investigations | … | INCIDENTAL INVESTIGATIONS | 179573.2652 |  | 1.098% | 19
0005 | … | ENERGISED MAINTENANCE INSPECTION | 178692.8228 |  | 1.093% | 20
0056 | … | AIR BLAST COOLER MAINTENANCE | 172301.2813 |  | 1.054% | 21
DBYD | … | DIAL BEFORE YOU DIG | 168226.219 |  | 1.029% | 22
0000 (2) | … | FIRE SPRINKER SYSTEM | 150271.7525 |  | 0.9188% | 23
0010 (1) | … | YARD MAINTENANCE | 140777.7998 |  | 0.8608% | 24
0019 | … | CABLE MARKER SIGN MAINTENANCE | 140064.6824 |  | 0.8564% | 25
Building ac | … | BUILDING AIR-CONDITIONERS | 137349.2043 |  | 0.8398% | 26
0050 (1) | … | VALVE COOLING SYSTEM MAINTENANCE | 116498.894 |  | 0.7123% | 27
Training Courses | … | TRAINING COURSES FOR CONTRACTORS | 106947.4361 |  | 0.6539% | 28
IGBT Repairs | … | IGBT VALVE REPAIRS | 93724.6565 |  | 0.5731% | 29
0050 (2) | … | NITROGEN BOTTLE REPLACEMENT | 87120.759 |  | 0.5327% | 30
0000 (1) | … | FIRE DETECTION & ALARM SYSTEM | 70272.6921 |  | 0.4297% | 31
0010 (2) | … | OIL FILLED CAPACITOR MAINTENANCE | 69234.7253 |  | 0.4233% | 32
0110 | … | IGBT VALVE MAINTENANCE | 67609.441 |  | 0.4134% | 33
Prestart Inspection | … | PRESTART INSPECTIONS | 41032.6967 |  | 0.2509% | 34
Onsite Test Equipment | … | ONSITE TEST EQUIPMENT MAINTENANCE | 39514.5577 |  | 0.2416% | 35
0054 | … | VALVE COOLING MCC THERMOGRAPHIC IMAGING | 38363.6232 |  | 0.2346% | 36
0126 | … | CONVERTER STATION THERMOGRAPHIC INSPECTION | 38363.6232 |  | 0.2346% | 37
0038 (1) | … | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | 36385.6684 |  | 0.2225% | 38
0060 | … | VALVE DEHUMIDIFIER MAINTENANCE | 35496.6918 |  | 0.217% | 39
0006 | … | UNINTERRUPTIBLE POWER SUPPLY | 34083.1784 |  | 0.2084% | 40
0022 | … | OUTDOOR POST TYPE CURRENT TRANSFORMER | 31086.5688 |  | 0.1901% | 41
0042 | … | AC FILTER RESISTOR MAINTENANCE | 31051.809 |  | 0.1899% | 42
0052 | … | VALVE COOLING SYSTEM PUMP MAINTENANCE | 28384.8793 |  | 0.1736% | 43
0104 (3) | … | PHASE REACTOR FAN MAINTENANCE | 26914.4278 |  | 0.1646% | 44
0003 | … | PORTABLE FIRE EXTINGUISHER INSPECTION | 26271.9361 |  | 0.1606% | 45
0004 | … | EMERGENCY LIGHTING MAINTENANCE | 25807.1581 |  | 0.1578% | 46
0124 | … | NITROGEN DISCHARGE UNIT MAINTENANCE | 19124.5643 |  | 0.1169% | 47
0016 | … | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | 19050.6254 |  | 0.1165% | 48
0120 | … | DIRECT VOLTAGE DIVIDER MAINTENANCE | 17147.8619 |  | 0.1049% | 49
0011 | … | INSPECT SPILL KITS | 16469.4879 |  | 0.1007% | 50
0026 | … | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE | 15494.7192 |  | 0.09474% | 51
0014 | … | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | 13716.7661 |  | 0.08387% | 52
0024 | … | CABLE SCREEN CURRENT TRANSFORMER | 12383.3012 |  | 0.07572% | 53
0104 (4) | … | DC ZERO SEQUENCE SMOOTHING REACTOR MAINTENANCE | 8382.9067 |  | 0.05126% | 54
0038 (2) | … | AIR GAP SURGE LIMITER MAINTENANCE | 8382.9067 |  | 0.05126% | 55
0013 | … | FUNCTIONAL TEST OF HIGH VOLTAGE TEST EQUIPMENT | 4474.8413 |  | 0.02736% | 56
0001 | … | CHECK EYE WASH STATION | 3880.7027 |  | 0.02373% | 57
0160 (1) | … | DISCONNECTOR & EARTH SWITCH MAINTENANCE | 3629.8044 |  | 0.02219% | 58
0160 (2) | … | MOTORISED OPERATING MECHANISM MAINTENANCE | 3629.8044 |  | 0.02219% | 59
0142 | … | INSULATING WALL BUSHING MAINTENANCE | 3008.2117 |  | 0.01839% | 60
0150 | … | PLC FILTER TUNING UNIT MAINTENANCE | 2413.6742 |  | 0.01476% | 61
0128 | … | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | 970.1757 |  | 0.005932% | 62
0062 | … | VALVE HUMIDITY CONTROL SYSTEM | 0 |  | 0% | 63
0180 | … | MANUAL OPERATING MECHANISM MAINTENANCE | 0 |  | 0% | 64
WARNING: This list must be MANUALLY sorted !

## Asset Mgt Team
ASSET MGT TEAM
Return to Index
The following tables are only valid if the Working section is manually updated
| 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | Total
Operations Manager | 151910.6322 | 140995.7934 | 144520.6883 | 148133.7055 | 151837.0481 | 737397.8675
Senior Reliability Engineer | 126188.5351 | 129343.2485 | 132576.8297 | 135891.2505 | 139288.5317 | 663288.3957
Reliability Engineer | 113683.365 | 116525.4491 | 119438.5854 | 122424.55 | 125485.1637 | 597557.1132
Work Practices Specialist | 97767.6939 | 100211.8862 | 102717.1834 | 105285.113 | 107917.2408 | 513899.1174
O&M Supervisor | 117442.2435 | 110161.2131 | 119516.9356 | 121028.2471 | 121342.7654 | 589491.4047
Works Planner | 97767.6939 | 100211.8862 | 102717.1834 | 105285.113 | 107917.2408 | 513899.1174
Technicians | 384396.8021 | 310472.5075 | 318946.852 | 326677.0749 | 334719.2345 | 1675212.471
Total | 1089156.9657 | 1007921.9841 | 1040434.2578 | 1064725.0539 | 1088507.2252 | 5290745.4867
Converting to hours | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Operations Manager | 965.2 | 874 | 874 | 874 | 874
Senior Reliability Engineer | 874 | 874 | 874 | 874 | 874
Reliability Engineer | 874 | 874 | 874 | 874 | 874
Work Practices Specialist | 874 | 874 | 874 | 874 | 874
O&M Supervisor | 902.8983 | 826.265 | 874.5733 | 864.0317 | 845.1483
Works Planner | 874 | 874 | 874 | 874 | 874
Technicians | 3740.8232 | 2947.7232 | 2954.3232 | 2952.1232 | 2951.0232
Working
APA Staff Cost from Summary tab | 1147888.7577 | 1066650.8105 | 1100631.3048 | 1126427.0271 | 1151751.7477 | Live APA Staff Values
Setting O&M Supervisor cost to $0 | 1030446.5142 | 956489.5974 | 981114.3692 | 1005398.78 | 1030408.9822 | Pasted Values
Setting Technician cost to $0 | 763491.9556 | 756178.303 | 781684.4528 | 799749.9522 | 817032.5132 | Pasted Values

## Summary of PMs
SUMMARY OF PMS
Return to Index
Sheet Name | Link |  | Total | APA Staff Costs | APA Material Costs | Contractor Labour | Contractor Materials | Maintenance Connect Reference |  | Photographic evidence
0000 (1) | … | FIRE DETECTION & ALARM SYSTEM | 63884.2655 | 24489.1346 |  | 39395.131 |  | QLD-ET-WI-PMxxx-0000 | 4 | Log book
0000 (2) | … | FIRE SPRINKER SYSTEM | 136610.6841 | 18425.2912 |  | 118185.3929 |  | QLD-ET-WI-PMxxx-0000 | 1 | Log book
0001 | … | CHECK EYE WASH STATION | 3527.9116 | 3527.9116 |  |  |  | QLD-ET-WI-PMxxx-0001 | 1
0003 | … | PORTABLE FIRE EXTINGUISHER INSPECTION | 23883.5783 | 12817.1671 |  | 11066.4112 |  | QLD-ET-WI-PMxxx-0003 | 1
0004 | … | EMERGENCY LIGHTING MAINTENANCE | 23461.0528 | 7055.8231 | 16405.2297 |  |  | QLD-ET-WI-PMxxx-0004 | 1 | Log book
0005 | … | ENERGISED MAINTENANCE INSPECTION | 162448.0207 | 162448.0207 |  |  |  | QLD-ET-WI-PMxxx-0005 | 1 | Photographic + Direct Entry
0006 | … | UNINTERRUPTIBLE POWER SUPPLY | 30984.7076 | 23547.6702 | 7437.0374 |  |  | QLD-ET-WI-PMxxx-0006 | 1 | Log book
0010 (1) | … | YARD MAINTENANCE | 127979.818 | 34130.4932 |  | 93849.3247 |  | QLD-ET-WI-PMxxx-0010 | 1
0010 (2) | … | OIL FILLED CAPACITOR MAINTENANCE | 62940.6593 | 6545.241 |  | 56395.4184 |  | QLD-ET-WI-PMxxx-0010 | 2 | Log book + Photographs
0011 | … | INSPECT SPILL KITS | 14972.2618 | 12817.1671 |  | 2155.0947 |  | QLD-ET-WI-PMxxx-0011 | 1
0013 | … | FUNCTIONAL TEST OF HIGH VOLTAGE TEST EQUIPMENT | 4068.0376 | 4068.0376 |  |  |  | QLD-ET-WI-PMxxx-0013 | 1 | Log book
0014 | … | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | 12469.7874 | 6408.5835 |  | 6061.2038 |  | QLD-ET-WI-PMxxx-0014 | 1 | Log book
0016 | … | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | 17318.7504 | 6408.5835 |  | 10910.1669 |  | QLD-ET-WI-PMxxx-0016 | 1 | Log book
0017 | … | VEGETATION MANAGEMENT | 456452.4545 | 34130.4932 |  | 422321.9613 |  | QLD-ET-WI-PMxxx-0017 | 1 | Photographic + Log book
0019 | … | CABLE MARKER SIGN MAINTENANCE | 127331.5295 | 120769.4376 | 6562.0919 |  |  | QLD-ET-WI-PMxxx-0019 | 1 | Photographic + Log book
0022 | … | OUTDOOR POST TYPE CURRENT TRANSFORMER | 28260.5171 | 7627.7964 |  | 20200.1207 | 432.6 | QLD-ET-WI-PMxxx-0022 | 2 | Log book
0024 | … | CABLE SCREEN CURRENT TRANSFORMER | 11257.5466 | 6408.5835 |  | 4848.9631 |  | QLD-ET-WI-PMxxx-0024 | 1 | Log book
0026 | … | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE | 14086.1084 | 6408.5835 |  | 7677.5248 |  | QLD-ET-WI-PMxxx-0026 | 1 | Log book
0028 | … | POWER TRANSFORMER MAINTENANCE | 418441.0769 | 7488.8355 | 2734.2049 | 408218.0364 |  | QLD-ET-WI-PMxxx-0028 | 1 | Log book
0038 (1) | … | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | 33077.8803 | 6408.5835 |  | 26669.2968 |  | QLD-ET-WI-PMxxx-0038 | 1 | Log book
0038 (2) | … | AIR GAP SURGE LIMITER MAINTENANCE | 7620.8243 | 6408.5835 |  | 1212.2408 |  | QLD-ET-WI-PMxxx-0038 | 1 | Log book
0042 | … | AC FILTER RESISTOR MAINTENANCE | 28228.9173 | 6408.5835 |  | 21820.3338 |  | QLD-ET-WI-PMxxx-0042 | 1 | Log book
0050 (1) | … | VALVE COOLING SYSTEM MAINTENANCE | 105908.0855 | 7273.1031 | 57418.3038 | 41216.6786 |  | QLD-ET-WI-PMxxx-0050 | 3 | Log book
0050 (2) | … | NITROGEN BOTTLE REPLACEMENT | 79200.69 | 34130.4932 | 45070.1968 |  |  | QLD-ET-WI-PMxxx-0050 | 1 | Log book
0052 | … | VALVE COOLING SYSTEM PUMP MAINTENANCE | 25804.4358 | 6408.5835 |  | 19395.8522 |  | QLD-ET-WI-PMxxx-0052 | 1 | Log book
0054 | … | VALVE COOLING MCC THERMOGRAPHIC IMAGING | 34876.0211 | 7775.9911 |  | 16163.2102 | 10936.8198 | QLD-ET-WI-PMxxx-0054 | 1 | Photographic + Log book
0056 | … | AIR BLAST COOLER MAINTENANCE | 156637.5285 | 42190.319 | 48245.4158 | 66201.7937 |  | QLD-ET-WI-PMxxx-0056 | 1 | Log book
0060 | … | VALVE DEHUMIDIFIER MAINTENANCE | 32269.7198 | 6408.5835 |  | 25861.1363 |  | QLD-ET-WI-PMxxx-0060 | 1 | Log book
0062 | … | VALVE HUMIDITY CONTROL SYSTEM | 0 |  |  |  |  | QLD-ET-WI-PMxxx-0062 | 1 | Log book
0104 (1) | … | REACTOR MAINTENANCE | 193514.2563 | 37310.7745 | 65920 | 90283.4818 |  | QLD-ET-WI-PMxxx-0104 | 2
0104 (2) | … | PHASE REACTOR MAINTENANCE | 518341.4811 | 141907.2798 | 39700.6558 | 336733.5455 |  | QLD-ET-WI-PMxxx-0104 | 1 | Log book
0104 (3) | … | PHASE REACTOR FAN MAINTENANCE | 24467.6616 | 7721.5425 | 1749.8912 | 14996.228 |  | QLD-ET-WI-PMxxx-0104 | 2
0104 (4) | … | DC ZERO SEQUENCE SMOOTHING REACTOR MAINTENANCE | 7620.8243 | 6408.5835 |  | 1212.2408 |  | QLD-ET-WI-PMxxx-0104 | 1
0110 | … | IGBT VALVE MAINTENANCE | 61463.1282 | 21459.183 |  | 40003.9452 |  | QLD-ET-WI-PMxxx-0110 | 1 | Log book
0120 | … | DIRECT VOLTAGE DIVIDER MAINTENANCE | 15588.9654 | 10254.5149 |  | 5334.4505 |  | QLD-ET-WI-PMxxx-0120 | 2 | Log book
0124 | … | NITROGEN DISCHARGE UNIT MAINTENANCE | 17385.9676 | 7689.5191 |  | 9696.4485 |  | QLD-ET-WI-PMxxx-0124 | 2 | Log book
0126 | … | CONVERTER STATION THERMOGRAPHIC INSPECTION | 34876.0211 | 7775.9911 |  | 16163.2102 | 10936.8198 | QLD-ET-WI-PMxxx-0126 | 1 | Photographic
0128 | … | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | 881.9779 | 881.9779 |  |  |  | QLD-ET-WI-PMxxx-0128 | 1 | Log book
0140 | … | CIRCUIT BREAKER MAINTENANCE | 362559.4077 | 49217.9485 | 6180 | 307161.4591 |  | QLD-ET-WI-PMxxx-0140 | 3 | Photographic + Log book
0142 | … | INSULATING WALL BUSHING MAINTENANCE | 2734.7379 | 1280.9356 |  | 1453.8023 |  | QLD-ET-WI-PMxxx-0142 | 1 | Photographic + Log book
0150 | … | PLC FILTER TUNING UNIT MAINTENANCE | 2194.2493 | 1732.9993 |  | 461.25 |  | QLD-ET-WI-PMxxx-0150 | 1 | Log book
0160 (1) | … | DISCONNECTOR & EARTH SWITCH MAINTENANCE | 3299.8221 | 1312.9589 |  | 1986.8632 |  | QLD-ET-WI-PMxxx-0160 | 1 | Photographic + Log book
0160 (2) | … | MOTORISED OPERATING MECHANISM MAINTENANCE | 3299.8221 | 1312.9589 |  | 1986.8632 |  | QLD-ET-WI-PMxxx-0160 | 1 | Log book
0180 | … | MANUAL OPERATING MECHANISM MAINTENANCE | 0 |  |  |  |  | QLD-ET-WI-PMxxx-0180 | 1 | Log book
Prestart Inspection | … | PRESTART INSPECTIONS | 37302.4515 | 37302.4515
Cable Repairs | … | CABLE REPAIRS | 1845697.2099 | 609704.8203 | 31443.3568 | 1204549.0328
IGBT Repairs | … | IGBT VALVE REPAIRS | 85204.2332 | 6408.5835 |  | 78795.6497
Control System Repairs | … | CONTROL SYSTEM REPAIRS | 198269.8278 | 179130.3932 | 19139.4346
Building ac | … | BUILDING AIR-CONDITIONERS | 124862.913 | 41692.2572 |  | 83170.6559
Electricity Costs | … | ELECTRICITY COSTS | 3469970.3826 | 8204.4455 | 3461765.9371
Control Room Costs | … | CONTROL ROOM OPERATIONS | 1010323.477 | 8204.4455 | 1002119.0315
Remote Comms | … | REMOTE COMMUNICATIONS | 261643.5812 | 8204.4455 | 253439.1357
DBYD | … | DIAL BEFORE YOU DIG | 152932.9263 | 115200.8981 | 37732.0282
Site Security | … | SITE SECURITY | 287295.9696 | 8204.4455 | 279091.5241
Training Courses | … | TRAINING COURSES FOR CONTRACTORS | 97224.9419 | 16408.891 | 80816.0509
Onsite Test Equipment | … | ONSITE TEST EQUIPMENT MAINTENANCE | 35922.3252 | 17065.2466 |  | 18857.0785
Incidental Investigations | … | INCIDENTAL INVESTIGATIONS | 163248.4229 |  |  | 163248.4229
Travel | … | TRAVEL | 358816.8008 | 35552.5971 |  | 323264.2037
Other Items | … | OTHER COSTS | 183062.6221 | 42334.9387 |  | 140727.6833
Operations Manager | … | OPERATIONS MANAGER | 737397.8675 | 737397.8675
Senior Reliability Engineer | … | SENIOR RELIABILITY ENGINEER | 663288.3957 | 663288.3957
Reliability Engineer | … | RELIABILITY ENGINEER | 635353.6626 | 597557.1132 | 37796.5494
Works Planner | … | WORKS PLANNER | 513899.1174 | 513899.1174
Work Practices Specialist | … | WORK PRACTICES SPECIALIST | 513899.1174 | 513899.1174
Other Worksheets
Summary | … | SUMMARY
Asset Mgt Team | … | ASSET MGT TEAM
Summary of PMs | … | SUMMARY OF PMS
Modelling Assumptions | … | MODELLING ASSUMPTIONS
Blank | … | BLANK
DL OPEX Budget | … | DL OPEX BUDGET
Schematics | … | SCHEMATICS
Components in Schematic | … | COMPONENTS IN SCHEMATIC
Grouped Components | … | GROUPED COMPONENTS
ABB Maintenance | … | ABB MAINTENANCE
Byron Bay Trees | … | BYRON BAY TREES
Electricity Invoices | … | ELECTRICITY INVOICES
Maintenance Documents | … | MAINTENANCE DOCUMENTS
Chart Summary | …
DL PMs | …
OnSite Contractors | …

## Modelling Assumptions
MODELLING ASSUMPTIONS
Return to Index
Historical Costs calculated in the Reference Year
Reference Financial Year | 2014/15
Reference Year | 2014 | First year of the Financial Year 2014/15
All the following figures should be considered anecdotal
Charge Out Rates for APA Staff
Hourly rate for APA technicians including HCC | 100.251 | Calculated from the following figures
Hourly rate for APA O&M Supervisor including HCC | 126.9 | Calculated from the following figures
Hourly rate for APA Reliability Engineer including HCC | 126.9 | Calculated from the following figures
Hourly rate for APA Operations Manager including HCC | 153.549 | Calculated from the following figures
Hourly rate for Senior Reliability Engineer including HCC | 140.859 | Calculated from the following figures
Hourly rate for Works Planner including HCC | 109.134 | Calculated from the following figures
Hourly rate for Work Practices Specialist including HCC | 109.134 | Calculated from the following figures
Hourly rate for APA technicians | 79 | Average rate for the two APA technicians |  |  |  |  | Anecdotal data taken from email from regulatory manager 24/3/14
Hourly rate for APA O&M Supervisor | 100 | Rate for a leading hand |  |  |  |  | Anecdotal data taken from email from regulatory manager 24/3/14
Hourly rate for APA Reliability Engineer | 100 | Rate for an engineer |  |  |  |  | Anecdotal data taken from email from regulatory manager 24/3/14
Hourly rate for APA Operations Manager | 121 | Rate for APA Operations Manager |  |  |  |  | Anecdotal data taken from email from regulatory manager 24/3/14
Hourly rate for Senior Reliability Engineer | 111 | Assumed rate for the Senior Reliability Engineer |  |  |  |  | Assumed to fall between the Engineer and Operations Manager
Hourly rate for Works Planner | 86 | Assumed rate for the Works Planner |  |  |  |  | Assumed to be the rate of a senior technician
Hourly rate for Work Practices Specialist | 86 | Assumed rate for the Work Practices Specialist |  |  |  |  | Assumed to be the rate of a senior technician
Home Cost Centre Cost Allocation Percentage | 26.9% | [5 empty] | Anecdotal - Source draft CY14/FY15 budget
Rates of Inflation
The modelling has used the Reserve Bank of Australia (RBA) target range of 2 to 3%
For Labour rates the mid point has been selected
Exposure to overseas prices for most materials means the model has selected the upper end of the RBA's
Annual Increase in Contractor Labour Rates | 2.5% | Applied to all labour rates (explained in Appendix A of the report) | [5 empty] | Discussed with the regulatory manager
Annual Increase in cost of Materials | 3% | Applied to all materials (explained in Appendix A of the report) | [5 empty] | Discussed with the regulatory manager
MOMCSA
Management Operations, Maintenance and Commercial Services Agreement (the MOMCSA)
Agreed Margin from 10.1 (c) (i) | 10%
APA O&M Supervisor
Hours per maintenance item | 8.5833 | This time includes
Minutes
|  | Open and Read the preventative maintenance task from Maintenance Connection | [7 empty] | 10
|  | Plan the steps in the Work Order | [7 empty] | 30
|  | Identify and assess suitable contractors for the work | [7 empty] | 60
|  | Schedule the maintenance (ensure contractors are available during the planned outages) | [7 empty] | 120
|  | Raise the Purchase Order in the financial management system | [7 empty] | 20
|  | Locate the Work Instructions (stored separately from Maintenance Connection) | [7 empty] | 15
|  | Assemble and Send detailed work package to the contractors | [7 empty] | 30
|  | Onsite supervision of the work (especially during major scheduled outages) | [7 empty] | 90
There are two periods when APA schedule preventative maintenance
During these two periods it is usual for the O&M Supervisor to be onsite
Approximately 5% of the allocated time includes travel time
Complete the work order
|  |  | Attach maintenance results | [6 empty] | 20
|  |  | Update results fields | [6 empty] | 10
|  |  | Close work order | [6 empty] | 5
|  | Process contractor invoice including check the invoice is for an approved purchase order | [7 empty] | 30
|  | Prepare invoice for payment approval by the Operations Manager | [7 empty] | 10
|  | Close the Purchase Order and enter Invoice details into the systems | [7 empty] | 15
|  | Check the Maintenance Log updated | [7 empty] | 20
|  | Debrief with the contractor after work has been completed | [7 empty] | 30
It excludes photographic updating (this is added separately when for those items requiring a photographic record)
APA Onsite Technicians
Contractor Access to Site | 1 | There is a requirement to undertake an onsite safety briefing whenever contractors are given access to the site
While this briefing only takes 30 minutes (anecdotal) it occurs at both sites
Since maintenance work always occurs equally at both sites the model simply uses a value of 1 hour
APA Standard Week | 38 | hours
Working weeks per year | 46 | weeks (52 - 4 weeks annual leave - 10 days of public holidays)
Full time hours per year | 1748 | hours
Contractors
Byron Bay Trees | 87095.3143 | Total Per Annum in Reference Year (including any clearing for cable repairs)
Percentage of vegetation management in Yard | 10% | This percentage appears under Yard Maintenance the remainder in Vegetation Management (of the Cable Route)
Thearle/SAE | 75 | Anecdotal - this figure was chosen as a reasonable average Hourly Rate
Thearle base rate is $65 but most invoices show considerable amounts of overtime at $85 (and also must allow for travel).
Anecdotally SAE are quoted as $75 per hour (from O&M Supervisor)
Component Costs |  | Select if the component cost is capitalised (if TRUE then value is excluded from OPEX forecast)
Capitalise | TRUE | TRUE or FALSE | [6 empty] | TRUE
FALSE
Cost Per IGBT | 5000 | Anecdotal per IGBT
Cost Per Cable Joint | 14348 | Anecdotal per cable joint (two required per repair)
Cost of Cable | 168 | Anecdotal per metre
Cost per Oil Filled Capacitor | 6530.2 | Anecdotal average from a recent order
Values derived from above figures (do not edit)
Financial Year |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
First Year in the Financial Year |  |  | 2015 | 2016 | 2017 | 2018 | 2019
Adjustment factor Labour |  |  | 1.025 | 1.0506 | 1.0769 | 1.1038 | 1.1314
Adjustment factor materials |  |  | 1.03 | 1.0609 | 1.0927 | 1.1255 | 1.1593
MOMCSA Multiplier | 1.1

## 0000 (1)
Summary | FIRE DETECTION & ALARM SYSTEM
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 24489.1346 | 4606.9678 | 4855.4663 | 4840.1956 | 5101.2743 | 5085.2305
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 39395.131 | 7494.8 | 7682.17 | 7874.2242 | 8071.0799 | 8272.8569
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | not sighted
Fire Detection and Alarm System
| Sites | 2
Number of Components to be serviced |  | 2
Discussion
This worksheet calculates the additional hours (travel) required for the technician at one site to travel to the other site (because the other technician is unavailable)
This is only undertaken on this worksheet due to the requirement for monthly maintenance
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM001-0000 | Every 1 month(s) |  |  | 12 | 12 | 12 | 12 | 12
APA Costs
APA Maintenance Staff (Hrs) | 1.0769 | Hours per site per visit
APA Supervision (Hrs) | 0.5 | Hours per site (ensuring invoices correctly entered on system and log completed)
APA Material Costs | 0
APA Hours
Standard Time | 0.5 | hours to undertake onsite briefing
Additional time required when onsite technician must travel to the opposite site
Round trip from one site to other | 1.5 | hours
Trips per year (due to annual leave) | 1.8462 | 4 weeks annual leave means on average each local technician will be on leave for 1 of the monthly visits. The technician at the other site is then required to travel to give Hawkins access. Two technicians hence 12 x 2 x 4 / 52 trips
Trips per year (due to Cable Faults) | 2.7692 | When there is a cable fault one of the technicians is assigned full time to the repair. Assuming 12 cable faults per year and 1 week for each fault = 12 x 1 / 52 x 50% (because might be at other site)
Additional Hours (p.a.) | 6.9231 | Note this has only claimed the travel time - it is assumed that while the technician is at the other site they perform maintenance tasks
Total APA hours | 1.0769
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 304.6667 | Contracted rate per site
Contractor Materials | 0 | Invoices indicate there are material costs but have not been included
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs (Techs) | 107.9626 | 215.9252 | 13960.1796 | 2655.8803 | 2722.2773 | 2790.3343 | 2860.0926 | 2931.595
APA Staff Costs (O&M Sup) | 63.45 | 126.9 | 8204.4455 | 1560.87 | 1599.8918 | 1639.889 | 1680.8863 | 1722.9084
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 304.6667 | 609.3333 | 39395.131 | 7494.8 | 7682.17 | 7874.2242 | 8071.0799 | 8272.8569
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Discussion
Hawkins on Fire charge a fixed rate for all the required maintenance + Call out fee
This has been captured in monthly maintenance hence no additional costs are shown for less frequent maintenance
Maintenance Connection will still raise Work Orders for the less frequent maintenance hence a small allowance has been included to process these events
Annual Cost of Maintenance Contract
| 4960 | Per Annum (Anecdotal value from Operations Manager 7/5/14)
Call out fee
| 98 | per hour (anecdotal from operations manager 7/5/14)
| 196 | per month (Two sites must be visited)
| 2352 | Annual Call out fee
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM006-0000 | Every 6 month(s) |  |  | 2 | 2 | 2 | 2 | 2
APA Costs
APA Maintenance Staff (Hrs) | 0 | Hours per site (this work is captured in the monthly maintenance shown above)
APA Supervision (Hrs) | 0.5 | Hours per site (there is still a requirement to open and close multiple WOs generated by Maintenance Connection (as listed below))
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0 | This work is captured in the monthly maintenance
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 63.45 | 126.9 | 1367.4076 | 260.145 | 266.6486 | 273.3148 | 280.1477 | 287.1514
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0000 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0 | Hours per site (this work is captured in the monthly maintenance shown above)
APA Supervision (Hrs) | 0.5 | Hours per site (there is still a requirement to close the WOs)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0 | This work is captured in the monthly maintenance
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 63.45 | 126.9 | 683.7038 | 130.0725 | 133.3243 | 136.6574 | 140.0739 | 143.5757
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM024-0000 | Every 2 year(s) |  |  | 0 | 1 | 0 | 1 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0 | Hours per site
APA Supervision (Hrs) | 0.5 | Hours per site (there is still a requirement to close the WOs)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0 | This work is captured in the monthly maintenance
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 63.45 | 126.9 | 273.3982 | 0 | 133.3243 | 0 | 140.0739 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM001-0000 | Every 1 month(s)
QLD-ET-WI-PM001-0000 | FIRE DETECTION & ALARM SYSTEM - 1M | Bungalora System 1 - Fire System Equipment | Bungalora System 1 - Fire Alarm System
QLD-ET-WI-PM001-0000 | FIRE DETECTION & ALARM SYSTEM - 1M | Bungalora System 2 - Fire System Equipment | Bungalora System 2 - Fire Alarm System
QLD-ET-WI-PM001-0000 | FIRE DETECTION & ALARM SYSTEM - 1M | Bungalora System 3 - Fire System Equipment | Bungalora System 3 - Fire Alarm System
QLD-ET-WI-PM001-0000 | FIRE DETECTION & ALARM SYSTEM - 1M | Mullumbimby System 1 - Fire System Equipment | Mullumbimby System 1 - Fire Alarm System
QLD-ET-WI-PM001-0000 | FIRE DETECTION & ALARM SYSTEM - 1M | Mullumbimby System 2 - Fire System Equipment | Mullumbimby System 2 - Fire Alarm System
QLD-ET-WI-PM001-0000 | FIRE DETECTION & ALARM SYSTEM - 1M | Mullumbimby System 3 - Fire System Equipment | Mullumbimby System 3 - Fire Alarm System
QLD-ET-WI-PM006-0000 | Every 6 month(s)
QLD-ET-WI-PM006-0000 | FIRE DETECTION & ALARM SYSTEM - 6M | Bungalora System 1 - Fire System Equipment | Bungalora System 1 - Fire Alarm System
QLD-ET-WI-PM006-0000 | FIRE DETECTION & ALARM SYSTEM - 6M | Bungalora System 2 - Fire System Equipment | Bungalora System 2 - Fire Alarm System
QLD-ET-WI-PM006-0000 | FIRE DETECTION & ALARM SYSTEM - 6M | Bungalora System 3 - Fire System Equipment | Bungalora System 3 - Fire Alarm System
QLD-ET-WI-PM006-0000 | FIRE DETECTION & ALARM SYSTEM - 6M | Mullumbimby System 1 - Fire System Equipment | Mullumbimby System 1 - Fire Alarm System
QLD-ET-WI-PM006-0000 | FIRE DETECTION & ALARM SYSTEM - 6M | Mullumbimby System 2 - Fire System Equipment | Mullumbimby System 2 - Fire Alarm System
QLD-ET-WI-PM006-0000 | FIRE DETECTION & ALARM SYSTEM - 6M | Mullumbimby System 3 - Fire System Equipment | Mullumbimby System 3 - Fire Alarm System
QLD-ET-WI-PM012-0000 | Every 1 year(s)
QLD-ET-WI-PM012-0000 | FIRE DETECTION & ALARM SYSTEM - 1YR | Bungalora System 1 - Fire System Equipment | Bungalora System 1 - Fire Alarm System
QLD-ET-WI-PM012-0000 | FIRE DETECTION & ALARM SYSTEM - 1YR | Bungalora System 2 - Fire System Equipment | Bungalora System 2 - Fire Alarm System
QLD-ET-WI-PM012-0000 | FIRE DETECTION & ALARM SYSTEM - 1YR | Bungalora System 3 - Fire System Equipment | Bungalora System 3 - Fire Alarm System
QLD-ET-WI-PM012-0000 | FIRE DETECTION & ALARM SYSTEM - 1YR | Mullumbimby System 1 - Fire System Equipment | Mullumbimby System 1 - Fire Alarm System
QLD-ET-WI-PM012-0000 | FIRE DETECTION & ALARM SYSTEM - 1YR | Mullumbimby System 2 - Fire System Equipment | Mullumbimby System 2 - Fire Alarm System
QLD-ET-WI-PM012-0000 | FIRE DETECTION & ALARM SYSTEM - 1YR | Mullumbimby System 3 - Fire System Equipment | Mullumbimby System 3 - Fire Alarm System
QLD-ET-WI-PM024-0000 | Every 2 year(s)
QLD-ET-WI-PM024-0000 | FIRE DETECTION & ALARM SYSTEM - 2YR | Bungalora System 1 - Fire System Equipment | Bungalora System 1 - Fire Alarm System
QLD-ET-WI-PM024-0000 | FIRE DETECTION & ALARM SYSTEM - 2YR | Bungalora System 2 - Fire System Equipment | Bungalora System 2 - Fire Alarm System
QLD-ET-WI-PM024-0000 | FIRE DETECTION & ALARM SYSTEM - 2YR | Bungalora System 3 - Fire System Equipment | Bungalora System 3 - Fire Alarm System
QLD-ET-WI-PM024-0000 | FIRE DETECTION & ALARM SYSTEM - 2YR | Mullumbimby System 1 - Fire System Equipment | Mullumbimby System 1 - Fire Alarm System
QLD-ET-WI-PM024-0000 | FIRE DETECTION & ALARM SYSTEM - 2YR | Mullumbimby System 2 - Fire System Equipment | Mullumbimby System 2 - Fire Alarm System
QLD-ET-WI-PM024-0000 | FIRE DETECTION & ALARM SYSTEM - 2YR | Mullumbimby System 3 - Fire System Equipment | Mullumbimby System 3 - Fire Alarm System
Work Order # | FIRE DETECTION & ALARM SYSTEM - 1M
QLD-183917 | Hawkins On Fire | PM | 2013-12-09 10:18 | Done,
QLD-178321 | Hawkins On Fire | PM | 2013-10-17 17:43 | Hawkins on fire October invoice 107456 payed
QLD-174525 | Hawkins On Fire | PM | 2013-10-01 16:30 | Carried out by Hawkins
QLD-170624 | Hawkins On Fire | PM | 2013-09-16 17:27 | Complted during annual.
QLD-166838 | Hawkins On Fire | PM | 2013-07-19 16:07
QLD-162957 | Hawkins On Fire | PM | 2013-06-27 10:16
QLD-183918 | Hawkins On Fire | PM | 2013-12-09 10:18 | Done,
QLD-178324 | Hawkins On Fire | PM | 2013-10-17 17:43 | Hawkins on fire October invoice 107456 payed
QLD-174528 | Hawkins On Fire | PM | 2013-10-01 16:30 | Carried out by Hawkins
QLD-170626 | Hawkins On Fire | PM | 2013-09-16 17:27 | Complted during annual.
QLD-166841 | Hawkins On Fire | PM | 2013-07-19 16:07
QLD-162960 | Hawkins On Fire | PM | 2013-06-27 10:16
QLD-183919 | Hawkins On Fire | PM | 2013-12-09 10:18 | Done,
QLD-178325 | Hawkins On Fire | PM | 2013-10-17 17:43 | Hawkins on fire October invoice 107456 payed
QLD-174529 | Hawkins On Fire | PM | 2013-10-01 16:30 | Carried out by Hawkins
QLD-170625 | Hawkins On Fire | PM | 2013-09-16 17:27 | Complted during annual.
QLD-166842 | Hawkins On Fire | PM | 2013-07-19 16:07
QLD-162961 | Hawkins On Fire | PM | 2013-06-27 10:16
QLD-183920 | Hawkins On Fire | PM | 2013-12-09 10:18 | Done,
QLD-178326 | Hawkins On Fire | PM | 2013-10-17 17:43 | Hawkins on fire October invoice 107456 payed
QLD-174530 | Hawkins On Fire | PM | 2013-10-01 16:30 | Carried out by Hawkins
QLD-170627 | Hawkins On Fire | PM | 2013-09-16 17:27 | Complted during annual.
QLD-166843 | Hawkins On Fire | PM | 2013-07-19 16:07
QLD-162962 | Hawkins On Fire | PM | 2013-06-27 10:16
QLD-183921 | Hawkins On Fire | PM | 2013-12-09 10:18 | Done,
QLD-178327 | Hawkins On Fire | PM | 2013-10-17 17:43 | Hawkins on fire October invoice 107456 payed
QLD-174531 | Hawkins On Fire | PM | 2013-10-01 16:30 | Carried out by Hawkins
QLD-170629 | Hawkins On Fire | PM | 2013-09-16 17:27 | Complted during annual.
QLD-166844 | Hawkins On Fire | PM | 2013-07-19 16:07
QLD-162963 | Hawkins On Fire | PM | 2013-06-27 10:16
QLD-183922 | Hawkins On Fire | PM | 2013-12-09 10:18 | Done,
QLD-178328 | Hawkins On Fire | PM | 2013-10-17 17:43 | Hawkins on fire October invoice 107456 payed
QLD-174532 | Hawkins On Fire | PM | 2013-10-01 16:30 | Carried out by Hawkins
QLD-170631 | Hawkins On Fire | PM | 2013-09-16 17:27 | Complted during annual.
QLD-166845 | Hawkins On Fire | PM | 2013-07-19 16:07
QLD-162964 | Hawkins On Fire | PM | 2013-06-27 10:16
Work Order # | FIRE DETECTION & ALARM SYSTEM - 6M
QLD-166856 | Hawkins On Fire | PM | 2013-08-21 13:43
QLD-166857 | Hawkins On Fire | PM | 2013-08-21 13:43
QLD-166858 | Hawkins On Fire | PM | 2013-08-21 13:43
QLD-166859 | Hawkins On Fire | PM | 2013-08-21 13:43
QLD-166860 | Hawkins On Fire | PM | 2013-08-21 13:43
QLD-166861 | Hawkins On Fire | PM | 2013-08-21 13:43
Work Order # | FIRE DETECTION & ALARM SYSTEM - 1YR
QLD-164887 | Hawkins On Fire | PM | 2013-08-21 13:40
QLD-164888 | Hawkins On Fire | PM | 2013-08-21 13:40
QLD-164889 | Hawkins On Fire | PM | 2013-08-21 13:40
QLD-164890 | Hawkins On Fire | PM | 2013-08-21 13:40
QLD-164891 | Hawkins On Fire | PM | 2013-08-21 13:40
QLD-164892 | Hawkins On Fire | PM | 2013-08-21 13:40
GL Period Name | Project No | Task Num | Expenditure Type | Original Transaction Reference | Quantity | Cost Amount | PA Description | Vendor / Customer Name | MA Account | Task Name | Po Number | Receipt Comments
2012-11-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2530566 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #9221 - Approved by S. Coomber
2012-12-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2663124 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #95879 - Approved by S. Coomber
2013-02-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2832680 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #9828 - Approved by S. Coomber
2013-02-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2853064 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #8737 - Approved by S. Coomber
2013-02-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2853064 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #8853 - Approved by S. Coomber
2013-02-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2853064 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #9064 - Approved by S. Coomber
2013-02-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2853064 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #9221 - Approved by S. Coomber
2013-02-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2853064 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #9396 - Approved by S. Coomber
2013-02-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2884553 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #10071 - Approved by S. Coomber
2013-03-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2948842 | 824 | 824 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #8851 - Approved by S. Coomber
2013-05-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 3168661 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #103402 - Approved by S. Coomber
2013-06-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 3264219 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #103186 - Approved by S. Coomber
2013-06-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 3264219 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #10307 - Approved by S. Coomber
2013-06-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 3268374 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #103600 - Approved by S. Coomber
2013-07-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 3357512 | 596.94 | 596.94 | Standing Order for Essential Services Monthly Contracted Charge for 2013-14 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 293833 | Inv #103785 - Approved by S. Coomber
2013-08-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 3461865 | 596.94 | 596.94 | Standing Order for Essential Services Monthly Contracted Charge for 2013-14 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 293833 | Inv #106920 - Approved by S. Coomber
2013-09-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 3594102 | 596.94 | 596.94 | Standing Order for Essential Services Monthly Contracted Charge for 2013-14 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 293833 | Inv # 107286 26.09.13
2013-10-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 3676531 | 596.94 | 596.94 | Standing Order for Essential Services Monthly Contracted Charge for 2013-14 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 293833 | Inv #107456 - Approved by S. Coomber

## 0000 (2)
Summary | FIRE SPRINKER SYSTEM
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 18425.2912 | 3505.3538 | 3592.9877 | 3682.8124 | 3774.8827 | 3869.2547
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 118185.3929 | 22484.4 | 23046.51 | 23622.6727 | 24213.2396 | 24818.5706
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | future
Discussion
After the Mullumbimby fire it has been decided to install a fire suppression systems in the converter buildings
The first system is a sprinkler system
The aim is to extinguishing any fire before it can destroy the entire converter station (as occurred at Mullumbimby)
Drying components (even if they must be uninstalled and sent for professional treatment) will be much less expensive than replacement
The sprinkler system will consist of
Diesel pumps (two)
Fuel Storage
Water Tanks
Control System
Valves
Reticulation (pipework)
All these components will require specialist maintenance
The modelling has assumed that this will be contracted to a specialist fire company
Anecdotally the Operations Managers suggested that the cost of the maintenance will be "three times higher than maintenance of the current fire system"
The new sprinkler system is installed before July 2015
At this stage it is unclear if APA will also install a parallel Gas Suppression system - hence this option has not been costed
Fire Detection and Alarm System
| Buildings | 6
Number of Components to be serviced |  | 6
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM001-0000 | Every 1 month(s) |  |  | 12 | 12 | 12 | 12 | 12
APA Costs
APA Maintenance Staff (Hrs) | 0.26282 | Hours per building per visit (since occurs monthly have included estimated time for the technician to travel from the other site (refer tab 0000 (1)))
APA Supervision (Hrs) | 0.16667 | Hours per site (ensuring invoices correctly entered on system and log completed)
APA Material Costs | 0 | Nominal cost to purchase and replace diesel fuel for the two pumps assumed to be included in the contractor costs
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 304.6667 | Contracted rate per building
Contractor Materials | 0
Maintenance Contract | 304.6667 | Per Building Per Inspection (Anecdotal as recommended by Operations manager who indicated the "cost will be three times the cost of maintaining the current fire system")
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 47.498 | 284.9881 | 18425.2912 | 3505.3538 | 3592.9877 | 3682.8124 | 3774.8827 | 3869.2547
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 304.6667 | 1828 | 118185.3929 | 22484.4 | 23046.51 | 23622.6727 | 24213.2396 | 24818.5706
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 0001
Summary | CHECK EYE WASH STATION
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 3527.9116 | 671.1741 | 687.9535 | 705.1523 | 722.7811 | 740.8506
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Eye Stations
| Sites | 2
Number of Components to be serviced |  | 2
Discussion
Anecdotally : "Turn on the tap and ensure that water comes out"
Checking of the Eye Wash Station is a health and safety requirement so this worksheet includes APA staff time to ensure that the maintenance is done and LOGS updated
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM003-0001 | Every 3 month(s) |  |  | 4 | 4 | 4 | 4 | 4
APA Costs
APA Maintenance Staff (Hrs) | 0.5 | Hours per site (including the check and updating Log book)
APA Supervision (Hrs) | 0.25 | Hours per site (check log completed)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 81.8505 | 163.701 | 3527.9116 | 671.1741 | 687.9535 | 705.1523 | 722.7811 | 740.8506
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM003-0001 | Every 3 month(s)
QLD-ET-WI-PM003-0001 | CHECK EYE WASH STATION | Bungalora System 1 - Small Plant & Safety Equipment | Bungalora System 1 - Eye Wash Station
QLD-ET-WI-PM003-0001 | CHECK EYE WASH STATION | Mullumbimby System 1 - Small Plant & Safety Equipment | Mullumbimby System 1 - Eye Wash Station
Work Order # | CHECK EYE WASH STATION
QLD-185525 | COOMBER Stuart | PM | 2013-12-09 10:27 | Check by SC
QLD-171848 | COOMBER Stuart | PM | 2013-09-18 13:51 | tested, working sc
QLD-160542 | HARRIS James | PM | 2013-06-27 08:07
QLD-185526 | COOMBER Stuart | PM | 2013-12-09 10:27 | Check by SC
QLD-171849 | COOMBER Stuart | PM | 2013-10-18 11:45 | sc checked 16/10/13
QLD-160543 | HARRIS James | PM | 2013-06-27 08:07

## 0003
Summary | PORTABLE FIRE EXTINGUISHER INSPECTION
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 12817.1671 | 2438.4258 | 2499.3864 | 2561.8711 | 2625.9179 | 2691.5658
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 11066.4112 | 2105.35 | 2157.9837 | 2211.9333 | 2267.2317 | 2323.9125
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Portable Fire Extinguishers
| Sites | 2
Number of Components to be serviced |  | 2
Discussion
Maintenance of the fire extinguishers is contracted to Hawkins on Fire
The tag on each extinguisher indicates when it requires maintenance
The contractor exchanges extinguishers as required
The contract also covers testing of hose reels and hydrants
An additional charge is included to undertake hydrant flow tests
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM006-0003 | Every 6 month(s) |  |  | 2 | 2 | 2 | 2 | 2
APA Costs
APA Maintenance Staff (Hrs) | 0.5 | Hours per site (access)
APA Supervision (Hrs) | 4.2917 | Hours per site (ensuring invoices correctly entered on system and log completed)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 513.5 | Hawkins On Fire - Contracted rate per 6 months per site
Contractor Materials | 0
Annual Contractor Costs
Portable Fire Extinguishers | 1154 | Annual Contracted Fee (Anecdotal : From Operations Manager 7/5/14)
Hydrant Flow Tests | 900 | Annual Contracted Fee (Anecdotal : From Operations Manager 7/5/14)
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 594.738 | 1189.476 | 12817.1671 | 2438.4258 | 2499.3864 | 2561.8711 | 2625.9179 | 2691.5658
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 513.5 | 1027 | 11066.4112 | 2105.35 | 2157.9837 | 2211.9333 | 2267.2317 | 2323.9125
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM006-0003 | Every 6 month(s)
QLD-ET-WI-PM006-0003 | PORTABLE FIRE EXTINGUISHER INSPECTION | Bungalora System 1 - Fire System Equipment | Bungalora System 1 - Portable Fire Extinguisher
QLD-ET-WI-PM006-0003 | PORTABLE FIRE EXTINGUISHER INSPECTION | Bungalora System 2 - Fire System Equipment | Bungalora System 2 - Portable Fire Extinguisher
QLD-ET-WI-PM006-0003 | PORTABLE FIRE EXTINGUISHER INSPECTION | Bungalora System 3 - Fire System Equipment | Bungalora System 3 - Portable Fire Extinguisher
QLD-ET-WI-PM006-0003 | PORTABLE FIRE EXTINGUISHER INSPECTION | Mullumbimby System 1 - Fire System Equipment | Mullumbimby System 1 - Portable Fire Extinguisher
QLD-ET-WI-PM006-0003 | PORTABLE FIRE EXTINGUISHER INSPECTION | Mullumbimby System 2 - Fire System Equipment | Mullumbimby System 2 - Portable Fire Extinguisher
QLD-ET-WI-PM006-0003 | PORTABLE FIRE EXTINGUISHER INSPECTION | Mullumbimby System 3 - Fire System Equipment | Mullumbimby System 3 - Portable Fire Extinguisher
Work Order # | PORTABLE FIRE EXTINGUISHER INSPECTION
QLD-166862 | Hawkins On Fire | PM | 2013-08-21 13:43
QLD-166863 | Hawkins On Fire | PM | 2013-08-21 13:43
QLD-166864 | Hawkins On Fire | PM | 2013-08-21 13:43
QLD-166865 | Hawkins On Fire | PM | 2013-08-21 13:43
QLD-166866 | Hawkins On Fire | PM | 2013-08-21 13:43
QLD-166867 | Hawkins On Fire | PM | 2013-08-21 13:43
GL Period Name | Project No | Task Num | Expenditure Type | Original Transaction Reference | Quantity | Cost Amount | PA Description | Vendor / Customer Name | MA Account | Task Name | Po Number | Receipt Comments
2012-12-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2663124 | 132 | 132 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #9594 - Approved by S. Coomber
2013-02-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2853064 | 297 | 297 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #8874 - Approved by S. Coomber
2013-03-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2948842 | 434 | 434 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #8850 - Approved by S. Coomber
2013-03-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 2948842 | 824 | 824 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #8851 - Approved by S. Coomber
2013-06-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 3264219 | 824.5 | 824.5 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 272223 | Inv #103343 - Approved by S. Coomber
2013-09-01 | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | 3594102 | 322 | 322 | Standing Order for Essential Services Monthly Contracted Charge for 2013-14 FY | HAWKINS ON FIRE | Other Operating Costs | PLANT AND EQUIPMENT | 293833 | Inv # 107287 26.09.13

## 0004
Summary | EMERGENCY LIGHTING MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 7055.8231 | 1342.3482 | 1375.9069 | 1410.3046 | 1445.5622 | 1481.7012
APA Material Costs |  |  | 16405.2297 | 3090 | 3182.7 | 3278.181 | 3376.5264 | 3477.8222
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Emergency Lighting
| Buildings | 6
Number of Components to be serviced |  | 6
Discussion
Currently there is limited emergency lighting installed at the two sites
It will be upgraded in the near future
This modelling has assumed that the enhanced emergency lighting is installed before July 2015
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM006-0004 | Every 6 month(s) |  |  | 2 | 2 | 2 | 2 | 2
APA Costs
APA Maintenance Staff (Hrs) | 0.66667 | Hours per building
APA Supervision (Hrs) | 0.33333 | Hours per building (ensuring invoices correctly entered on system and log completed - contractor hours (not used) + additional time to order and invoice required batteries)
APA Material Costs | 250 | Battery replacement as needed
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0 | Hours per building
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 109.134 | 654.804 | 7055.8231 | 1342.3482 | 1375.9069 | 1410.3046 | 1445.5622 | 1481.7012
APA Material Costs | 250 | 1500 | 16405.2297 | 3090 | 3182.7 | 3278.181 | 3376.5264 | 3477.8222
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
APA Staff Hours
Testing | 15 | minutes
Replacement | 5 | minutes / light
Total Time | 0.66667 | hours (annual battery replacements / 2 since done every 6 months)
Material Costs
Assumption: Each light has its own battery (likely to avoid cable runs)
Internally lights required at 5 doors | 5
Externally lights required around perimeter | 20
Lifetime of each battery | 2.5 | years (2-3 years is reasonable given the harsh conditions)
Battery replacements per year | 10 | Should probably discount for the first year (given the batteries are new) but since this does not make a material difference have ignored
Cost of each battery | 50 | Commercial Grade Sealed Lead Acid Battery (7Ah)
Annual cost of batteries | 500
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM006-0004 | Every 6 month(s)
QLD-ET-WI-PM006-0004 | EMERGENCY LIGHTING MAINTENANCE | Bungalora | Bungalora - System 1
QLD-ET-WI-PM006-0004 | EMERGENCY LIGHTING MAINTENANCE | Bungalora | Bungalora - System 2
QLD-ET-WI-PM006-0004 | EMERGENCY LIGHTING MAINTENANCE | Bungalora | Bungalora - System 3
QLD-ET-WI-PM006-0004 | EMERGENCY LIGHTING MAINTENANCE | Mullumbimby | Mullumbimby - System 1
QLD-ET-WI-PM006-0004 | EMERGENCY LIGHTING MAINTENANCE | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM006-0004 | EMERGENCY LIGHTING MAINTENANCE | Mullumbimby | Mullumbimby - System 3
Work Order # | EMERGENCY LIGHTING MAINTENANCE
QLD-175944 | COOMBER Stuart | PM | 2013-09-19 09:56 | decommision

## 0005
Summary | ENERGISED MAINTENANCE INSPECTION
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 162448.0207 | 30905.226 | 31677.8566 | 32469.8031 | 33281.5481 | 34113.5868
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | DL-WI-17
Energised Maintenance
| Sites | 2
Number of Components to be serviced |  | 2
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM006-0005 | Every 1 month(s) |  |  | 12 | 12 | 12 | 12 | 12
APA Costs
APA Maintenance Staff (Hrs) | 10 | Hours per site (8 hours for the inspection and 2 hours for log book update + upload of photographs)
APA Supervision (Hrs) | 2 | Hours per site (raise and close work order, check log completed and catalogue photographs)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 1256.31 | 2512.62 | 162448.0207 | 30905.226 | 31677.8566 | 32469.8031 | 33281.5481 | 34113.5868
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM001-0005 | Every 1 month(s)
QLD-ET-WI-PM001-0005 | ENERGISED MAINTENANCE INSPECTION | Bungalora | Bungalora - System 1
QLD-ET-WI-PM001-0005 | ENERGISED MAINTENANCE INSPECTION | Bungalora | Bungalora - System 2
QLD-ET-WI-PM001-0005 | ENERGISED MAINTENANCE INSPECTION | Bungalora | Bungalora - System 3
QLD-ET-WI-PM001-0005 | ENERGISED MAINTENANCE INSPECTION | Mullumbimby | Mullumbimby - System 1
QLD-ET-WI-PM001-0005 | ENERGISED MAINTENANCE INSPECTION | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM001-0005 | ENERGISED MAINTENANCE INSPECTION | Mullumbimby | Mullumbimby - System 3
Work Order # | ENERGISED MAINTENANCE INSPECTION
QLD-188340 | COOMBER Stuart | PM | 2013-12-09 14:19 | system decommisioned
QLD-178332 | COOMBER Stuart | PM | 2013-10-18 11:43 | not needed as Directlink not operating due to reactor repair
QLD-174536 | COOMBER Stuart | PM | 2013-09-16 17:48 | Directlink off line this month fpr reactor repairs
QLD-170637 | COOMBER Stuart | PM | 2013-07-19 15:53 | Annual maintanance peroid.
QLD-166849 | EDWARDS2 Luke | PM | 2013-08-21 13:49 | Annual Maintenance period
QLD-162968 | EDWARDS2 Luke | PM | 2013-06-27 10:11
QLD-178333 | COOMBER Stuart | PM | 2013-10-18 11:43 | not needed as Directlink not operating due to reactor repair
QLD-174537 | COOMBER Stuart | PM | 2013-09-16 17:48 | Directlink off line this month fpr reactor repairs
QLD-170638 | COOMBER Stuart | PM | 2013-07-19 15:53 | Annual maintanance peroid.
QLD-166850 | EDWARDS2 Luke | PM | 2013-08-21 13:49 | Annual Maintenance period
QLD-162969 | EDWARDS2 Luke | PM | 2013-06-27 10:11
QLD-178337 | COOMBER Stuart | PM | 2013-10-18 11:43 | not needed as Directlink not operating due to reactor repair
QLD-174541 | COOMBER Stuart | PM | 2013-09-16 17:48 | Directlink off line this month fpr reactor repairs
QLD-170641 | COOMBER Stuart | PM | 2013-07-19 15:53 | Annual maintanance peroid.
QLD-166854 | EDWARDS2 Luke | PM | 2013-08-21 13:49 | Annual Maintenance period
QLD-162973 | EDWARDS2 Luke | PM | 2013-06-27 10:11
QLD-188342 | COOMBER Stuart | PM | 2013-12-09 14:19 | system decommisioned
QLD-178334 | COOMBER Stuart | PM | 2013-10-18 11:43 | not needed as Directlink not operating due to reactor repair
QLD-174538 | COOMBER Stuart | PM | 2013-09-16 17:48 | Directlink off line this month fpr reactor repairs
QLD-170635 | COOMBER Stuart | PM | 2013-07-19 15:53 | Annual maintanance peroid.
QLD-166851 | COOMBER Stuart | PM | 2013-07-08 13:18
QLD-162970 | HARRIS James | PM | 2013-07-18 15:48
QLD-178335 | COOMBER Stuart | PM | 2013-10-18 11:43 | not needed as Directlink not operating due to reactor repair
QLD-174539 | COOMBER Stuart | PM | 2013-09-16 17:48 | Directlink off line this month fpr reactor repairs
QLD-170636 | COOMBER Stuart | PM | 2013-07-19 15:53 | Annual maintanance peroid.
QLD-166852 | HARRIS James | PM | 2013-08-21 13:50 | Annual maintenance peroid.
QLD-162971 | HARRIS James | PM | 2013-07-18 15:48
QLD-178336 | COOMBER Stuart | PM | 2013-10-18 11:43 | not needed as Directlink not operating due to reactor repair
QLD-174540 | COOMBER Stuart | PM | 2013-09-16 17:48 | Directlink off line this month fpr reactor repairs
QLD-170639 | COOMBER Stuart | PM | 2013-07-19 15:53 | Annual maintanance peroid.
QLD-166853 | HARRIS James | PM | 2013-08-21 13:50 | Annual maintenance peroid.
QLD-162972 | HARRIS James | PM | 2013-07-18 15:48

## 0006
Summary | UNINTERRUPTIBLE POWER SUPPLY
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 23547.6702 | 4479.8703 | 4591.8671 | 4706.6638 | 4824.3304 | 4944.9386
APA Material Costs |  |  | 7437.0374 | 1400.8 | 1442.824 | 1486.1087 | 1530.692 | 1576.6127
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Uninterruptible Power Supplies
| DC disconnectors | 12
| Control System | 12
| Comms | 8
| OWS Computers | 2
Number of Components to be serviced |  | 34
Discussions
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM006-0006 | Every 6 month(s) |  |  | 2 | 2 | 2 | 2 | 2
APA Costs
APA Maintenance Staff (Hrs) | 0.56667 | Hours per UPS | Test pull the cord out of the back and test it survives, must be done sequentially
APA Supervision (Hrs) | 0.058824 | Hours per UPS (discounted time recognising no contractors involved but must still ensure invoices correctly entered on system and log completed)
APA Material Costs | 20 | per UPS
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 64.2736 | 2185.3026 | 23547.6702 | 4479.8703 | 4591.8671 | 4706.6638 | 4824.3304 | 4944.9386
APA Material Costs | 20 | 680 | 7437.0374 | 1400.8 | 1442.824 | 1486.1087 | 1530.692 | 1576.6127
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
APA Staff Hours
Testing | 15 | minutes (pull the cord out of the back and test it survives, must be done on each UPS separately and sequentially)
Replacement | 10 | minutes / UPS
Total Time | 0.56667 | hours (annual battery test and replacement)
Material Costs
Each UPS contains a battery
Lifetime of each battery | 2.5 | years (2-3 years is reasonable given commercial sealed lead acid battery and the harsh conditions)
Cost of each battery | 50
Average cost of batteries | 20 | Per UPS per year
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM006-0006 | Every 6 month(s)
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Bungalora System 1 - Station Service Power System | Bungalora System 1 - Uniterruptable DC and AC Supply A
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Bungalora System 1 - Station Service Power System | Bungalora System 1 - Uniterruptable DC and AC Supply B
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Bungalora System 2 - Station Service Power System | Bungalora System 2 - Uniterruptable DC and AC Supply A
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Bungalora System 2 - Station Service Power System | Bungalora System 2 - Uniterruptable DC and AC Supply B
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Bungalora System 3 - Station Service Power System | Bungalora System 3 - Uniterruptable DC and AC Supply A
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Bungalora System 3 - Station Service Power System | Bungalora System 3 - Uniterruptable DC and AC Supply B
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Mullumbimby System 1 - Station Service Power System | Mullumbimby System 1 - Uninterruptable DC and AC Supply A
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Mullumbimby System 1 - Station Service Power System | Mullumbimby System 1 - Uninterruptable DC and AC Supply B
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Mullumbimby System 2 - Station Service Power System | Mullumbimby System 2 - Uninterruptable DC and AC Supply A
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Mullumbimby System 2 - Station Service Power System | Mullumbimby System 2 - Uninterruptable DC and AC Supply B
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Mullumbimby System 3 - Station Service Power System | Mullumbimby System 3 - Uninterruptable DC and AC Supply A
QLD-ET-WI-PM006-0006 | UNINTERRUPTIBLE POWER SUPPLY | Mullumbimby System 3 - Station Service Power System | Mullumbimby System 3 - Uninterruptable DC and AC Supply B
Work Order # | UNINTERRUPTIBLE POWER SUPPLY
QLD-166868 | EDWARDS2 Luke | PM | 2013-09-18 14:15 | done during shutdown, , entered sc.
QLD-166869 | EDWARDS2 Luke | PM | 2013-09-18 14:15 | done during shutdown, , entered sc.
QLD-166870 | EDWARDS2 Luke | PM | 2013-09-18 14:15 | done during shutdown, , entered sc.
QLD-166871 | EDWARDS2 Luke | PM | 2013-09-18 14:15 | done during shutdown, , entered sc.
QLD-166872 | EDWARDS2 Luke | PM | 2013-09-18 14:15 | done during shutdown, , entered sc.
QLD-166873 | EDWARDS2 Luke | PM | 2013-09-18 14:15 | done during shutdown, , entered sc.
QLD-166874 | COOMBER Stuart | PM | 2013-09-18 13:10 | decommissioned
QLD-166875 | COOMBER Stuart | PM | 2013-09-18 13:10 | decommissioned
QLD-166878 | COOMBER Stuart | PM | 2013-10-01 15:46 | tested during annual shutdown , PCP A ups replaced.
QLD-166879 | COOMBER Stuart | PM | 2013-10-01 15:45 | Tested during annual maintenace, replaced PCP A UPS

## 0010 (1)
Summary | YARD MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 34130.4932 | 6493.2192 | 6655.5497 | 6821.9384 | 6992.4869 | 7167.2991
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 93849.3247 | 17854.5394 | 18300.9029 | 18758.4255 | 19227.3861 | 19708.0708
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Yard Maintenance
| Yards | 2
Number of Components to be serviced |  | 2
Discussion
Was unable to separate Yard Maintenance from Vegetation Management along the cable route
Have therefore assigned 10% of the total cost from Byron Bay Trees (the contractor) to Yard Maintenance
Refer to worksheet Modelling Assumptions to change the percentage
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM001-0010 | The last Fr of every 1 month(s) |  |  | 12 | 12 | 12 | 12 | 12
APA Costs
APA Maintenance Staff (Hrs) | 2 | Hours per yard per month (some supervision required)
APA Supervision (Hrs) | 0.5 | Hours per yard per month (ensuring invoices correctly entered on system and log completed)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) |  | Hours per yard per month
Contractor Hourly Rate |  | Contractor Byron Bay Trees
Contractor Labour | 725.7943 | This value comes from the Modelling Assumption worksheet
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 263.952 | 527.904 | 34130.4932 | 6493.2192 | 6655.5497 | 6821.9384 | 6992.4869 | 7167.2991
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 725.7943 | 1451.5886 | 93849.3247 | 17854.5394 | 18300.9029 | 18758.4255 | 19227.3861 | 19708.0708
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM001-0010 | The last Fr of every 1 month(s)
QLD-ET-WI-PM001-0010 | YARD MAINTENANCE | Bungalora | Bungalora - 110kV Overhead Bus
QLD-ET-WI-PM001-0010 | YARD MAINTENANCE | Mullumbimby | Mullumbimby - 132kV Overhead Bus
Work Order # | YARD MAINTENANCE
QLD-180915 | COOMBER Stuart | PM | 2013-10-17 17:53 | Done during extended Annual outage 2013
QLD-176791 | EDWARDS2 Luke | PM | 2013-09-16 17:38 | Both sites were accessed during the anual maintenace period , with weed control carried %0D%0Aout
QLD-173196 | EDWARDS2 Luke | PM | 2013-09-16 17:54 | done during annual maintence 2013
QLD-168780 | EDWARDS2 Luke | PM | 2013-08-21 15:12
QLD-165611 | COOMBER Stuart | PM | 2013-06-27 10:10
QLD-180916 | COOMBER Stuart | PM | 2013-10-17 17:53 | Done during extended Annual outage 2013
QLD-176792 | EDWARDS2 Luke | PM | 2013-09-16 17:38 | Both sites were accessed during the anual maintenace period , with weed control carried %0D%0Aout
QLD-173197 | EDWARDS2 Luke | PM | 2013-09-16 17:54 | done during annual maintence 2013
QLD-168781 | HARRIS James | PM | 2013-07-18 11:01 | Check and removed weeds from AC Yard
QLD-168781 | EDWARDS2 Luke | PM | 2013-07-18 11:01 | Check and removed weeds from AC Yard
QLD-165612 | COOMBER Stuart | PM | 2013-06-27 10:10

## 0010 (2)
Summary | OIL FILLED CAPACITOR MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6545.241 | 1219.2129 | 1249.6932 | 1417.593 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 56395.4184 | 6303.75 | 6461.3437 | 29883.7148 | 6788.4493 | 6958.1605
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-30 & DL-WI-38
AC Capacitor
| WT.C1 | 6
| WT.C2 | 6
| WA.Z1.C1 | 18
| WA.Z1.C2 | 18
| WA.Z1.Z11.C1 | 18
| WA.Z1.Z12.C1 | 18
DC Capacitor
| U.C1 | 6
| U.C2 | 6
| U.Vx.C1 | 18
| U.Vx.C2 | 18
| WPx.C1 | 12
Number of Components to be serviced |  | 144
Discussion
Note: That each capacitor is actually made up of banks of capacitors. The above figure is the number of BANKS of capacitors
Capacitors which are found to be leaking oil (annual inspection) or measured capacitance is down (three yearly inspection) are replaced
No figures were provided for the number of capacitors which are replaced
The cost of the capacitors would be CAPEX - however should have included contractor costs for the replacement
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0010 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.0069444 | Hours per capacitor (site access for contractor)
APA Supervision (Hrs) | 0.059606 | Hours per capacitor (engaging contractor, scheduling contractor, ensuring invoices correctly entered on system and log completed)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 0.56944 | Hours per capacitor
Contractor Hourly Rate | 75 | Thearle/SAE
Contractor Labour | 42.7083
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 8.2603 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 42.7083 | 6150 | 33134.5809 | 6303.75 | 6461.3437 | 6622.8773 | 6788.4493 | 6958.1605
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replacement Costs
Hours to replace each capacitor | 5 | hours (two staff for 2.5 hours)
Assumed failure rate | 0.5% | While 5 capacitors were purchased in 2013 the modelling assumes this failure rate
Total Number of Capacitors | 702
Average number replaced pa | 3.51 | This is figure is conservative (given 5 purchased in 12 months)
Total hours to replace failed capacitors | 10 | hours per year
Average hours to replace caps | 0.069444 | hours per year per capacitor
CAPITALISED COST OF CAPACITORS |  | Will only be included if Modelling Assumptions CAPITALISE = FALSE
Average cost (2013) | 6340 | Purchase of 5 capacitors was placed in August 2013 totalling $31700 (From Operation Manager 4/4/14)
Average cost in Reference Year (2014) | 6530.2
Average replacement cost | 159.1736 | Per "Capacitor shown on schematic" per year
Modelled replacement cost | 0 | If $0 then check CAPITALIZE on the Modelling Assumptions Sheet
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM036-0010 | Every 3 year(s) |  |  | 0 | 0 | 1 | 0 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0 | Hours per capacitor (no additional time for APA staff)
APA Supervision (Hrs) | 0.0069444 | Must still process the WO generated by Maintenance Connection (Time PER CAPACITOR)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 2 | Hours per capacitor (requires measurements to be made)
Contractor Hourly Rate | 75 | Thearle/SAE
Contractor Labour | 150
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 0.88125 | 126.9 | 136.6574 | 0 | 0 | 136.6574 | 0 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 150 | 21600 | 23260.8375 | 0 | 0 | 23260.8375 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM036-0010 | Every 3 year(s)
QLD-ET-WI-PM036-0010-BLA | OIL FILLED CAPACITOR MAINTENANCE - 3YR | Bungalora | Bungalora - 110kV Overhead Bus
QLD-ET-WI-PM036-0010-BLA1 | OIL FILLED CAPACITOR MAINTENANCE - 3YR | Bungalora | Bungalora - System 1
QLD-ET-WI-PM036-0010-BLA2 | OIL FILLED CAPACITOR MAINTENANCE - 3YR | Bungalora | Bungalora - System 2
QLD-ET-WI-PM036-0010-BLA3 | OIL FILLED CAPACITOR MAINTENANCE - 3YR | Bungalora | Bungalora - System 3
QLD-ET-WI-PM036-0010-MUL | OIL FILLED CAPACITOR MAINTENANCE - 3YR | Mullumbimby | Mullumbimby - 132kV Overhead Bus
QLD-ET-WI-PM036-0010-MUL1 | OIL FILLED CAPACITOR MAINTENANCE - 3YR | Mullumbimby | Mullumbimby - System 1
QLD-ET-WI-PM036-0010-MUL2 | OIL FILLED CAPACITOR MAINTENANCE - 3YR | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM036-0010-MUL3 | OIL FILLED CAPACITOR MAINTENANCE - 3YR | Mullumbimby | Mullumbimby - System 3

## 0011
Summary | INSPECT SPILL KITS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 12817.1671 | 2438.4258 | 2499.3864 | 2561.8711 | 2625.9179 | 2691.5658
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 2155.0947 | 410 | 420.25 | 430.7562 | 441.5252 | 452.5633
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Spill Kits
| Spill Kits | 2
Number of Components to be serviced |  | 2
Discussion
Anecdotally a contractor inspects the spill kits every 6 months
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM006-0011 | Every 6 month(s) |  |  | 2 | 2 | 2 | 2 | 2
APA Costs
APA Maintenance Staff (Hrs) | 0.5 | Hours per spill kit
APA Supervision (Hrs) | 4.2917 | Hours per spill kit
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 100 | Anecdotal figure suggested during discussions with O&M Supervisor
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 594.738 | 1189.476 | 12817.1671 | 2438.4258 | 2499.3864 | 2561.8711 | 2625.9179 | 2691.5658
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 100 | 200 | 2155.0947 | 410 | 420.25 | 430.7562 | 441.5252 | 452.5633
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM006-0011 | Every 6 month(s)
QLD-ET-WI-PM006-0011 | INSPECT SPILL KITS | Bungalora System 1 - Small Plant & Safety Equipment | Bungalora System 1 - Spill Kits
QLD-ET-WI-PM006-0011 | INSPECT SPILL KITS | Mullumbimby System 1 - Small Plant & Safety Equipment | Mullumbimby System 1 - Spill Kits
Work Order # | INSPECT SPILL KITS
QLD-171850 | EDWARDS2 Luke | PM | 2013-09-19 10:00 | checked by luke. 5.8.13
QLD-171851 | COOMBER Stuart | PM | 2013-10-18 11:45 | sc checked 16/10/13

## 0013
Summary | FUNCTIONAL TEST OF HIGH VOLTAGE TEST EQUIPMENT
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 4068.0376 | 773.9314 | 793.2797 | 813.1117 | 833.4394 | 854.2754
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Functional Test of High Voltage Test Equipment
| Per set of test equipment | 1 | only one set
Number of Components to be serviced |  | 1
Discussion
This is a functional test only - Calibration of the equipment is captured under Onsite Test Equipment
Thumper | Used to locate faults in the cable (after a cable fault)
Hi-Pot | Used to test the cable after a cable repair
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM006-0013 | Every 6 month(s) |  |  | 2 | 2 | 2 | 2 | 2
APA Costs
APA Maintenance Staff (Hrs) | 2.5 | Get the thumper and hi-pot test equipment out of storage and test they are working
APA Supervision (Hrs) | 1 | Hours per site (raise and close WO, check that log has been updated)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 377.5275 | 377.5275 | 4068.0376 | 773.9314 | 793.2797 | 813.1117 | 833.4394 | 854.2754
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM006-0013 | FUNCTIONAL TEST OF HIGH VOLTAGE TEST EQUIPMENT | DirectLink | DirectLink Easement

## 0014
Summary | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 6061.2038 | 1153.125 | 1181.9531 | 1211.502 | 1241.7895 | 1272.8342
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-31
Hall Effect Current Transformers
| WPx.T11 | 12
| WPx.T12 | 12
| WA.Z1.T1 | 18
| WA.Z1.T2 | 18
Number of Components to be serviced |  | 60
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0014 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.016667 | Hours per CT
APA Supervision (Hrs) | 0.14306 | Hours per CT
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 0.25 | Hours per CT
Contractor Hourly Rate | 75
Contractor Labour | 18.75
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 19.8246 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 18.75 | 1125 | 6061.2038 | 1153.125 | 1181.9531 | 1211.502 | 1241.7895 | 1272.8342
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0014-BLA1 | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | Bungalora
QLD-ET-WI-PM012-0014-BLA2 | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | Bungalora
QLD-ET-WI-PM012-0014-BLA3 | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | Bungalora
QLD-ET-WI-PM012-0014-MUL1 | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | Mullumbimby | Asset Name
QLD-ET-WI-PM012-0014-MUL2 | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | Mullumbimby | Bungalora - System 1
QLD-ET-WI-PM012-0014-MUL3 | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | Mullumbimby | Bungalora - System 2
Bungalora - System 3
Mullumbimby - System 1
Mullumbimby - System 2
Mullumbimby - System 3
Work Order # | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE
QLD-166905 | COOMBER Stuart | PM
QLD-166906 | MCALLISTER Jack (no PIO) | PM
QLD-166907 | EDWARDS2 Luke | PM
QLD-166908 | COOMBER Stuart | PM
QLD-166909 | Thearle Electrical | PM | 2013-07-19 13:51 | not in service
QLD-166910 | Thearle Electrical | PM | 2013-09-16 13:56 | Done, entered sc,
2013-09-04 13:42
|  |  | 2013-07-19 13:52 | not in service
|  |  | 2013-09-16 13:49 | done annaul maintenance
|  |  | 2013-09-16 13:49 | done annaul maintenance

## 0016
Summary | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 10910.1669 | 2075.625 | 2127.5156 | 2180.7035 | 2235.2211 | 2291.1016
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-28
Rogowski Current Transformers
| U.Vx.T1 | 18
| U.Vx.T2 | 18
| U.Vx.T3 | 18
Number of Components to be serviced |  | 54
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0016 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.018519 | Hours per CT
APA Supervision (Hrs) | 0.15895 | Hours per CT
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 0.5 | Hours per CT (this is half the value detailed on the ABB recommended maintenance)
Contractor Hourly Rate | 75 | Thearle/SAE
Contractor Labour | 37.5
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 22.0273 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 37.5 | 2025 | 10910.1669 | 2075.625 | 2127.5156 | 2180.7035 | 2235.2211 | 2291.1016
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0016 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | Bungalora - System 1 | Bungalora System 1 - Inverter / Rectifier Area
QLD-ET-WI-PM012-0016 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | Bungalora - System 2 | Bungalora System 2 - Inverter / Rectifier Area
QLD-ET-WI-PM012-0016 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | Bungalora - System 3 | Bungalora System 3 - Inverter / Rectifier Area
QLD-ET-WI-PM012-0016 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | Mullumbimby - System 1 | Mullumbimby System 1 - Inverter / Rectifier Area
QLD-ET-WI-PM012-0016 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | Mullumbimby - System 2 | Mullumbimby System 2 - Inverter / Rectifier Area
QLD-ET-WI-PM012-0016 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | Mullumbimby - System 3 | Mullumbimby System 3 - Inverter / Rectifier Area
Work Order # | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE
QLD-164876 | COOMBER Stuart | PM | 2013-09-04 13:33 | out of service
QLD-164879 | COOMBER Stuart | PM | 2013-09-18 13:00 | decommisioned
QLD-164880 | HARRIS James | PM | 2013-09-16 13:44 | Work complete during annual, enetred by sc
QLD-164881 | HARRIS James | PM | 2013-09-16 13:44 | Work complete during annual, enetred by sc

## 0017
Summary | VEGETATION MANAGEMENT
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 34130.4932 | 6493.2192 | 6655.5497 | 6821.9384 | 6992.4869 | 7167.2991
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 422321.9613 | 80345.4274 | 82354.0631 | 84412.9147 | 86523.2376 | 88686.3185
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | DL-OP-28
Vegetation Management
| Cable Route | 1 | Once per month
Number of Components to be serviced |  | 1
Discussion
Was unable to separate Vegetation Management from the Bryon Bay Tree company invoices
Have therefore assigned 90% of the total cost from Byron Bay Trees (the contractor) to Vegetation management along the cable route
Refer to sheet Modelling Assumptions to change the percentage
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM001-0017 | Every 1 month(s) |  |  | 12 | 12 | 12 | 12 | 12
APA Costs
APA Maintenance Staff (Hrs) | 4 | Hours per month (Technicians meet with contractor regularly to explain what is needed)
APA Supervision (Hrs) | 1 | Hours per month (entering invoices and cataloguing provided photographs)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate |  | Contractor Byron Bay Trees
Contractor Labour | 6532.1486 | This value comes from the Modelling Assumption worksheet
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 527.904 | 527.904 | 34130.4932 | 6493.2192 | 6655.5497 | 6821.9384 | 6992.4869 | 7167.2991
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 6532.1486 | 6532.1486 | 422321.9613 | 80345.4274 | 82354.0631 | 84412.9147 | 86523.2376 | 88686.3185
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM001-0017 | Every 1 month(s)
QLD-ET-WI-PM001-0017 | VEGETATION MANAGEMENT - 1M | DirectLink | DirectLink Easement
Work Order # | VEGETATION MANAGEMENT - 1M
QLD-190837 | EDWARDS2 Luke | PM | 2014-01-23 14:38 | byron bay trees complted on 7/1/14
QLD-186932 | EDWARDS2 Luke | PM | 2014-01-23 14:37 | byron bay tree servoce invoice 4355 paid
QLD-181577 | EDWARDS2 Luke | PM | 2013-12-09 16:07 | Luke sent emails to DBYD customers to liase regarding earthworks
QLD-177397 | EDWARDS2 Luke | PM | 2013-12-09 10:48 | Byron trees stokers siding, mclouds farm
QLD-173218 | COOMBER Stuart | PM | 2013-12-09 10:03
GL Period Name | Project No | Task Num | Expenditure Type | Original Transaction Reference | Quantity | Cost Amount | PA Description | Vendor / Customer Name | MA Account | Task Name | Po Number | Receipt Comments
2013-01-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 2754117 | 1134.55 | 1134.55 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 269473 | Inv #00002961 - Approved by S. Coomber
2013-02-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 2832680 | 3085.5 | 3085.5 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 269473 | Inv #00002980 - Approved by S. Coomber
2013-04-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 3001175 | 1200 | 1200 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 269473 | Inv # 00003020 25.04.13
2013-05-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 3130562 | 660 | 660 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 269473 | Byron Bay Tree Services & Landscapes P/L. Inv #00004016. 09.05.13.
2013-05-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 3168661 | 1440 | 1440 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 269473 | Inv #00004047 - Approved by S. Coomber
2013-05-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 3168661 | 1120 | 1120 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 269473 | Inv #00004044 - Approved by S. Coomber
2013-06-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 3244904 | 5754.25 | 5754.25 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 269473 | Inv #00004080 - Approved by S. Coomber
2013-06-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 3264219 | 2888 | 2888 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 269473 | Inv #00004091 - Approved by S. Coomber
2013-07-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 3335804 | 2024 | 2024 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Inv #00004121 - Approved by S. Coomber
2013-08-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 3465031 | 320 | 320 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Inv #00004185 - Approved by S. Coomber
2013-09-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 3598803 | 1160 | 1160 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Byron Bay Tree Services & Landscapes Pty Ltd. Inv No 00004219. 26.09.13
2013-10-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 3690557 | 5323.5 | 5323.5 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Inv #00004236 - Approved by S. Dodds
2013-11-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 4414726 | 15190.5 | 15190.5 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Byron Bay Tree Services & Landscapes P/L. Inv No 00004263. 27.11.13. Approved by Stuart Dodds
2013-12-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 5126743 | 440 | 440 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Byron Bay Tree Services & Landscapes P/L. Inv No 00004324. 28.11.13. Approved by Stuart Dodds.
2013-12-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 5701408 | 15190.5 | 15190.5 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Inv #00004263 - Approved by S. Coomber
2013-12-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 5701408 | 440 | 440 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Inv #00004324 - Approved by S. Coomber
2013-12-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 6163935 | 1684 | 1684 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Inv #00004361 - Approved by S. Dodds
2014-01-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 6350551 | 440 | 440 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Inv #00004385 - Approved by S. Dodds
2014-02-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 6379779 | 484 | 484 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Inv #00004407 - Approved by S. Dodds
2014-02-01 | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | 6379779 | 9596 | 9596 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | Contractors - O&M | EASEMENT | 293836 | Inv #00004370 - Approved by S. Dodds

## 0019
Summary | CABLE MARKER SIGN MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 120769.4376 | 22976.0064 | 23550.4066 | 24139.1667 | 24742.6459 | 25361.212
APA Material Costs |  |  | 6562.0919 | 1236 | 1273.08 | 1311.2724 | 1350.6106 | 1391.1289
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Cable Easement
| Cable Route | 1
Number of Components to be serviced |  | 1
Discussion
APA try to walk the full 56km of the cable route once a year
Each month the technicians pick a different section of the route
Due to the difficult and isolated terrain both technicians are required
In addition to replacing the Cable Markers this is used as a pre-inspection of areas requiring vegetation management
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM001-0019 | Every 1 month(s) |  |  | 12 | 12 | 12 | 12 | 12
APA Costs
APA Maintenance Staff (Hrs) | 18 | Hours per month (two technicians and updating vegetation contractor on areas requiring work)
APA Supervision (Hrs) | 0.5 | Hours per month
APA Material Costs | 100 | Cost of the signs per month (Suggested allowance from the Operations Manager)
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour
Contractor Materials
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 1867.968 | 1867.968 | 120769.4376 | 22976.0064 | 23550.4066 | 24139.1667 | 24742.6459 | 25361.212
APA Material Costs | 100 | 100 | 6562.0919 | 1236 | 1273.08 | 1311.2724 | 1350.6106 | 1391.1289
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM001-0019 | Every 1 month(s)
QLD-ET-WI-PM001-0019 | CABLE MARKER SIGN MAINTENANCE - 1M | DirectLink | DirectLink Easement
Work Order # | CABLE MARKER SIGN MAINTENANCE- 1M
QLD-181579 | EDWARDS2 Luke | PM | 2013-11-26 09:35 | stokers siding, sihn repair/replacement
QLD-177400 | EDWARDS2 Luke | PM | 2013-12-09 11:03 | Stokers siding
QLD-173220 | EDWARDS2 Luke | PM | 2013-12-09 10:04 | replced signs along rail track going into Muwulmbar

## 0022
Summary | OUTDOOR POST TYPE CURRENT TRANSFORMER
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 7627.7964 | 2438.4258 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 20200.1207 | 6457.5 | 3309.4687 | 3392.2055 | 3477.0106 | 3563.9359
Contractor Materials |  |  | 432.6 | 432.6 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-32 (1Yr)
OUTDOOR POST TYPE CURRENT TRANSFORMER
| WA.Z1.Z11.T1 | 18
| WA.Z1.Z12.T1 | 18
| U.T1 | 6
Number of Components to be serviced |  | 42
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0022 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.02381 | Hours per CT
APA Supervision (Hrs) | 0.20437 | Hours per CT
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 1 | Hours per CT (as per ABB recommended maintenance for WA.Z1.Z1x.T1)
Contractor Hourly Rate | 75 | Thearle/SAE
Contractor Labour | 75
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 28.3209 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 75 | 3150 | 16971.3707 | 3228.75 | 3309.4687 | 3392.2055 | 3477.0106 | 3563.9359
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM060-0022 | Every 5 year(s) |  |  | 1 | 0 | 0 | 0 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0.02381 | Hours per CT
APA Supervision (Hrs) | 0.20437 | Hours per CT
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 1 | Hours per CT (not shown on the ABB maintenance - however anecdotal discussions highlighted maintenance including application of grease)
Contractor Hourly Rate | 75 | Thearle/SAE
Contractor Labour | 75
Contractor Materials | 10 | Estimate as a nominal amount for grease per CT
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 28.3209 | 1189.476 | 1219.2129 | 1219.2129 | 0 | 0 | 0 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 75 | 3150 | 3228.75 | 3228.75 | 0 | 0 | 0 | 0
Contractor Materials | 10 | 420 | 432.6 | 432.6 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0022-BLA1 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | Bungalora | Asset Name
QLD-ET-WI-PM012-0022-BLA2 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | Bungalora | Bungalora - System 1
QLD-ET-WI-PM012-0022-BLA3 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | Bungalora | Bungalora - System 2
QLD-ET-WI-PM012-0022-MUL1 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | Mullumbimby | Bungalora - System 3
QLD-ET-WI-PM012-0022-MUL2 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | Mullumbimby | Mullumbimby - System 1
QLD-ET-WI-PM012-0022-MUL3 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | Mullumbimby | Mullumbimby - System 2
Mullumbimby - System 3
QLD-ET-WI-PM060-0022-BLA1 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | Bungalora
QLD-ET-WI-PM060-0022-BLA2 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | Bungalora | Bungalora - System 1
QLD-ET-WI-PM060-0022-BLA3 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | Bungalora | Bungalora - System 2
QLD-ET-WI-PM060-0022-MUL1 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | Mullumbimby | Bungalora - System 3
QLD-ET-WI-PM060-0022-MUL2 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | Mullumbimby | Mullumbimby - System 1
QLD-ET-WI-PM060-0022-MUL3 | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | Mullumbimby | Mullumbimby - System 2
Mullumbimby - System 3
Work Order # | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR
QLD-166911 | COOMBER Stuart | PM
QLD-166912 | EDWARDS2 Luke | PM | 2013-07-19 13:58 | done, entered sc.
QLD-166913 | Thearle Electrical | PM | 2013-09-18 14:09 | done entered sc
QLD-166914 | COOMBER Stuart | PM | 2013-09-16 14:00
QLD-166915 | Thearle Electrical | PM | 2013-07-19 13:58 | done entered sc
QLD-166916 | Thearle Electrical | PM | 2013-09-16 14:00 | done entered sc
2013-09-16 14:00

## 0024
Summary | CABLE SCREEN CURRENT TRANSFORMER
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 4848.9631 | 922.5 | 945.5625 | 969.2016 | 993.4316 | 1018.2674
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-33
Cable Screen Current Transformer
| R1.T11 | 6
| R1.T12 | 6
| R1.T21 | 6
| R1.T22 | 6
Number of Components to be serviced |  | 24
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0024 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.041667 | Hours per CT
APA Supervision (Hrs) | 0.35764 | Hours per CT
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 0.5 | Hours per CT (agrees with ABB recommended maintenance)
Contractor Hourly Rate | 75
Contractor Labour | 37.5
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 49.5615 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 37.5 | 900 | 4848.9631 | 922.5 | 945.5625 | 969.2016 | 993.4316 | 1018.2674
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location | Asset Name
QLD-ET-WI-PM012-0024-BLA1 | CABLE SCREEN CURRENT TRANSFORMER | Bungalora - System 1 | Bungalora System 1 - DC Filter Area
QLD-ET-WI-PM012-0024-BLA2 | CABLE SCREEN CURRENT TRANSFORMER | Bungalora - System 2 | Bungalora System 2 - DC Filter Area
QLD-ET-WI-PM012-0024-BLA3 | CABLE SCREEN CURRENT TRANSFORMER | Bungalora - System 3 | Bungalora System 3 - DC Filter Area
QLD-ET-WI-PM012-0024-MUL1 | CABLE SCREEN CURRENT TRANSFORMER | Mullumbimby - System 1 | Mullumbimby System 1 - DC Filter Area
QLD-ET-WI-PM012-0024-MUL2 | CABLE SCREEN CURRENT TRANSFORMER | Mullumbimby - System 2 | Mullumbimby System 2 - DC Filter Area
QLD-ET-WI-PM012-0024-MUL3 | CABLE SCREEN CURRENT TRANSFORMER | Mullumbimby - System 3 | Mullumbimby System 3 - DC Filter Area
Work Order # | CABLE SCREEN CURRENT TRANSFORMER
QLD-166917 | COOMBER Stuart | PM | 2013-07-19 14:09 | out of service
QLD-166918 | Thearle Electrical | PM | 2013-09-16 14:08 | done, entered sc
QLD-166919 | Thearle Electrical | PM | 2013-09-16 14:08 | done, entered sc
QLD-166920 | COOMBER Stuart | PM | 2013-07-19 14:09 | out of service
QLD-166921 | Thearle Electrical | PM | 2013-09-16 14:08 | done, entered sc
QLD-166922 | Thearle Electrical | PM | 2013-09-16 14:08 | done, entered sc

## 0026
Summary | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 7677.5248 | 1460.625 | 1497.1406 | 1534.5691 | 1572.9334 | 1612.2567
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-37
Capacitive Voltage Transformers
| WA.Z1.T11 | 18
| WT.T11 | 1 | Only shown on the single line diagram - Not shown in ABB schematic
Number of Components to be serviced |  | 19
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0026 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.052632 | Hours per VT
APA Supervision (Hrs) | 0.45175 | Hours per VT
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 1 | Hours per VT (from the ABB recommended maintenance)
Contractor Hourly Rate | 75
Contractor Labour | 75
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 62.604 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 75 | 1425 | 7677.5248 | 1460.625 | 1497.1406 | 1534.5691 | 1572.9334 | 1612.2567
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location | Asset Name
QLD-ET-WI-PM012-0026 | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | Bungalora System 1 - AC Filter Area | Bungalora System 1 - Capacitive Voltage Transformer WA.Z1.T11
QLD-ET-WI-PM012-0026 | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | Bungalora - 110kV Overhead Bus | Bungalora System 1 - Main Stn Incoming Capacitive Volt Transformer WT.T11
QLD-ET-WI-PM012-0026 | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | Bungalora System 2 - AC Filter Area | Bungalora System 2 - Capacitive Voltage Transformer WA.Z1.T11
QLD-ET-WI-PM012-0026 | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | Bungalora System 3 - AC Filter Area | Bungalora System 3 - Capacitive Voltage Transformer WA.Z1.T11
QLD-ET-WI-PM012-0026 | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | Mullumbimby System 1 - AC Filter Area | Mullumbimby System 1 - Capacitive Voltage Transformer WA.Z1.T11
QLD-ET-WI-PM012-0026 | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | Mullumbimby System 2 - AC Filter Area | Mullumbimby System 2 - Capacitive Voltage Transformer WA.Z1.T11
QLD-ET-WI-PM012-0026 | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | Mullumbimby System 3 - AC Filter Area | Mullumbimby System 3 - Capacitive Voltage Transformer WA.Z1.T11
Work Order # | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR
QLD-166929 | COOMBER Stuart | PM | 2013-07-19 15:34 | out of service
QLD-166928 | MCALLISTER Jack (no PIO) | PM | 2013-09-16 14:14 | Rust found WT T11 L1,L2,L3, arrange painter and cleaning.New work order opened, sc
QLD-166923 | MCALLISTER Jack (no PIO) | PM | 2013-09-16 14:14 | Rust found WT T11 L1,L2,L3, arrange painter and cleaning.New work order opened, sc
QLD-166924 | MCALLISTER Jack (no PIO) | PM | 2013-09-16 14:14 | Rust found WT T11 L1,L2,L3, arrange painter and cleaning.New work order opened, sc
QLD-166925 | COOMBER Stuart | PM | 2013-07-19 15:34 | out of service
QLD-166926 | HARRIS James | PM | 2013-09-16 14:48 | Done, enetered SC,
QLD-166927 | HARRIS James | PM | 2013-09-16 14:48 | Done, enetered SC,

## 0028
Summary | POWER TRANSFORMER MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 7488.8355 | 1424.7274 | 1460.3456 | 1496.8543 | 1534.2756 | 1572.6325
APA Material Costs |  |  | 2734.2049 | 515 | 530.45 | 546.3635 | 562.7544 | 579.637
Contractor Labour |  |  | 408218.0364 | 77662.2 | 79603.755 | 81593.8489 | 83633.6951 | 85724.5375
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | not sighted
Power Transformer
| WT2.T1 | 7 | Including Spare
Number of Components to be serviced |  | 7
Discussion
The Transformer OEM has been contracted to undertake this maintenance
The contract is reported as $32472 per year for each site
There are three transformers at each site
There is one spare transformer
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0028 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.42857 | Hours per transformer
APA Supervision (Hrs) | 1.2262 | Hours per transformer
APA Material Costs | 71.4286 | Oil sample checking now included in the Wilson contract was $1,000 p.a.
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 10824 | Anecdotal: The Operations Manager reported as $32472 per year for each site
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 198.5683 | 1389.978 | 7488.8355 | 1424.7274 | 1460.3456 | 1496.8543 | 1534.2756 | 1572.6325
APA Material Costs | 71.4286 | 500 | 2734.2049 | 515 | 530.45 | 546.3635 | 562.7544 | 579.637
Contractor Labour | 10824 | 75768 | 408218.0364 | 77662.2 | 79603.755 | 81593.8489 | 83633.6951 | 85724.5375
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contracted Cost of the Maintenance
Per Site | 32472 | Figure provided in email from Operations Manager 31/3/14
Spare Transformer | 10824 | Figure provided in email from Operations Manager 31/3/14
Total | 75768 | In 2014$
APA Oil Sample
APA staff | 2 | One APA technician for 2 hours at each site
Material Cost of the testing | 1000 | For all 7 samples
Discount | 50% | Additional testing is only done periodically
Scheduled Maintenance
PM ID | PM Name | Parent Location | Asset Name
QLD-ET-WI-PM012-0028-BLA1 | POWER TRANSFORMER MAINTENANCE | Bungalora - System 1 | Bungalora System 1 - AC Switchyard Area WT2
QLD-ET-WI-PM012-0028 | POWER TRANSFORMER MAINTENANCE | Bungalora System 2 - AC Switchyard Area WT2 | Bungalora System 2 - Power Transformer WT2.T1
QLD-ET-WI-PM012-0028 | POWER TRANSFORMER MAINTENANCE | Bungalora System 3 - AC Switchyard Area WT2 | Bungalora System 3 - Power Transformer WT2.T1
QLD-ET-WI-PM012-0028 | POWER TRANSFORMER MAINTENANCE | Mullumbimby System 1 - AC Switchyard Area WT2 | Mullumbimby System 1 - Power Transformer WT2.T1
QLD-ET-WI-PM012-0028 | POWER TRANSFORMER MAINTENANCE | Mullumbimby System 2 - AC Switchyard Area WT2 | Mullumbimby System 2 - Power Transformer WT2.T1
QLD-ET-WI-PM012-0028 | POWER TRANSFORMER MAINTENANCE | Mullumbimby System 3 - AC Switchyard Area WT2 | Mullumbimby System 3 - Power Transformer WT2.T1
Work Order # | POWER TRANSFORMER MAINTENANCE
QLD-166930 | EDWARDS2 Luke | PM | 2013-11-18 17:29 | Painted during this outage.Oil samples done.
QLD-166880 | COOMBER Stuart | PM | 2013-12-06 11:01 | Oils samples done, all good. Results on server
QLD-166881 | EDWARDS2 Luke | PM | 2013-11-18 17:21 | Painted during this outage.Oil samples done.
QLD-166882 | COOMBER Stuart | PM | 2013-12-06 11:01 | Oils samples done, all good. Results on server
QLD-166883 | COOMBER Stuart | PM | 2013-12-06 11:01 | Oils samples done, all good. Results on server
QLD-166884 | COOMBER Stuart | PM | 2013-12-06 11:01 | Oils samples done, all good. Results on server

## 0038 (1)
Summary | ZINC OXIDE SURGE ARRESTOR MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 26669.2968 | 5073.75 | 5200.5938 | 5330.6086 | 5463.8738 | 5600.4707
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-34
AC Surge Arrestor
| WT2.F1 | 18
| WT2.F2 | 6
| WA.Z1.F1 | 18
DC Surge Arrester
| WP1.F1 | 6
| WP2.F1 | 6
DC Cable Screen Arrestor
| R1.F1 | 6
| R1.F2 | 6
Number of Components to be serviced |  | 66
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0038 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.015152 | Hours per arrestor
APA Supervision (Hrs) | 0.13005 | Hours per arrestor
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 1 | Hours per arrestor (from ABB recommended maintenance)
Contractor Hourly Rate | 75 | Thearle/SAE
Contractor Labour | 75
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 18.0224 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 75 | 4950 | 26669.2968 | 5073.75 | 5200.5938 | 5330.6086 | 5463.8738 | 5600.4707
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location | Asset Name
QLD-ET-WI-PM012-0038-BLA1 | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | Bungalora | Bungalora - System 1
QLD-ET-WI-PM012-0038-BLA2 | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | Bungalora | Bungalora - System 2
QLD-ET-WI-PM012-0038-BLA3 | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | Bungalora | Bungalora - System 3
QLD-ET-WI-PM012-0038-MUL1 | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | Mullumbimby | Mullumbimby - System 1
QLD-ET-WI-PM012-0038-MUL2 | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM012-0038-MUL3 | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | Mullumbimby | Mullumbimby - System 3
Work Order # | ZINC OXIDE SURGE ARRESTOR MAINTENANCE
QLD-166931 | COOMBER Stuart | PM | 2013-07-19 15:46 | out of service
QLD-166932 | COOMBER Stuart | PM | 2013-09-18 14:43 | done, entered sc.
QLD-166933 | EDWARDS2 Luke | PM | 2013-09-16 17:43 | done
QLD-166934 | COOMBER Stuart | PM | 2013-07-19 15:46 | out of service
QLD-166935 | Thearle Electrical | PM | 2013-09-16 14:49 | Done sc
QLD-166936 | Thearle Electrical | PM | 2013-09-16 14:49 | Done sc

## 0038 (2)
Summary | AIR GAP SURGE LIMITER MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 1212.2408 | 230.625 | 236.3906 | 242.3004 | 248.3579 | 254.5668
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-34
DC Cable Screen Arrestor
| U.F11 | 6
Number of Components to be serviced |  | 6
Discussion
Inspection of the surge limiters
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
| Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.16667 | Hours per arrestor
APA Supervision (Hrs) | 1.4306 | Hours per arrestor
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 0.5 | Hours per arrestor (the ABB maintenance suggests that this will take 1 hour but have used the time suggested by APA staff)
Contractor Hourly Rate | 75 | Thearle/SAE
Contractor Labour | 37.5
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 198.246 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 37.5 | 225 | 1212.2408 | 230.625 | 236.3906 | 242.3004 | 248.3579 | 254.5668
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 0042
Summary | AC FILTER RESISTOR MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 21820.3338 | 4151.25 | 4255.0312 | 4361.407 | 4470.4422 | 4582.2033
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-35 (does not include WT1.R1)
AC Filter Resistor
| WT1.R1 | 18
| WA.Z1.Z11.R1 | 18
| WA.Z1.Z12.R1 | 18
Number of Components to be serviced |  | 54
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0042 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.018519 | Hours per filter resistor
APA Supervision (Hrs) | 0.15895 | Hours per filter resistor
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 1 | Hours per filter resistor
Contractor Hourly Rate | 75
Contractor Labour | 75
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 22.0273 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 75 | 4050 | 21820.3338 | 4151.25 | 4255.0312 | 4361.407 | 4470.4422 | 4582.2033
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0042-BLA1 | AC FILTER RESISTOR MAINTENANCE | Bungalora - System 1 | Bungalora System 1 - AC Filter Area
QLD-ET-WI-PM012-0042-BLA2 | AC FILTER RESISTOR MAINTENANCE | Bungalora - System 2 | Bungalora System 2 - AC Filter Area
QLD-ET-WI-PM012-0042-BLA3 | AC FILTER RESISTOR MAINTENANCE | Bungalora - System 3 | Bungalora System 3 - AC Filter Area
QLD-ET-WI-PM012-0042-MUL1 | AC FILTER RESISTOR MAINTENANCE | Mullumbimby - System 1 | Mullumbimby System 1 - AC Filter Area
QLD-ET-WI-PM012-0042-MUL2 | AC FILTER RESISTOR MAINTENANCE | Mullumbimby - System 2 | Mullumbimby System 2 - AC Filter Area
QLD-ET-WI-PM012-0042-MUL3 | AC FILTER RESISTOR MAINTENANCE | Mullumbimby - System 3 | Mullumbimby System 3 - AC Filter Area
Work Order # | AC FILTER RESISTOR MAINTENANCE
QLD-166885 | COOMBER Stuart | PM | 2013-09-18 13:21 | decommissioned
QLD-166937 | EDWARDS2 Luke | PM | 2013-09-16 17:46 | done
QLD-166938 | Thearle Electrical | PM | 2013-09-18 14:59 | done theirls, done, entered sc.
QLD-166939 | COOMBER Stuart | PM | 2013-07-19 15:51 | out of service
QLD-166940 | Thearle Electrical | PM | 2013-09-16 14:52 | Done eneterd sc
QLD-166941 | Thearle Electrical | PM | 2013-09-16 14:52 | Done eneterd sc

## 0050 (1)
Summary | VALVE COOLING SYSTEM MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 7273.1031 | 1582.1152 | 1249.6932 | 1525.5523 | 1312.9589 | 1602.7834
APA Material Costs |  |  | 57418.3038 | 10815 | 11139.45 | 11473.6335 | 11817.8425 | 12172.3778
Contractor Labour |  |  | 41216.6786 | 8148.75 | 7564.5 | 8561.2805 | 7947.4528 | 8994.6953
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Valve Cooling System Maintenance
| Sites | 2
Number of Components to be serviced |  | 2
Discussion
Valve operation, replacing deionising resin, removing and inspecting strainers, testing safety valves, transducer checks
Pump and motor alignment
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0050 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.5 | Hours per site per visit
APA Supervision (Hrs) | 4.2917 | Hours per site
APA Material Costs | 5250
Contractor Costs
Contractor Labour (Hrs) | 48 | Hours per site (Anecdotal: Operations Manager suggests 2 days per building with 3 buildings at each site)
Contractor Hourly Rate | 75
Contractor Labour | 3600 | Hours per site
Contractor Materials | 0
Materials
Deionising resin | 7000 | Source: OPEX Budget indicates 800 litres required per year
Pall Filter Cartridges | 3500 | Source: CY14/FY15 OPEX Budget
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 594.738 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 5250 | 10500 | 57418.3038 | 10815 | 11139.45 | 11473.6335 | 11817.8425 | 12172.3778
Contractor Labour | 3600 | 7200 | 38791.7044 | 7380 | 7564.5 | 7753.6125 | 7947.4528 | 8146.1391
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM024-0050 | Every 2 year(s) |  |  | 1 | 0 | 1 | 0 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.5 | Hours per site
APA Supervision (Hrs) | 0.5 | Hours per site (minor extra allowance over annual to process the WO created by Maintenance Connection)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 5 | Hours per site (taking times from ABB recommended maintenance of strainer and ion-exchange vessel)
Contractor Hourly Rate | 75
Contractor Labour | 375
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 113.5755 | 227.151 | 734.4471 | 232.8298 | 0 | 244.6168 | 0 | 257.0005
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 375 | 750 | 2424.9741 | 768.75 | 0 | 807.668 | 0 | 848.5562
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM060-0050 | Every 5 year(s) |  |  | 1 | 0 | 0 | 0 | 0
No maintenance has been costed for this PM - OEM instructions indicate 5 year maintenance not required
APA Costs
APA Maintenance Staff (Hrs) | 0 | Hours per site
APA Supervision (Hrs) | 0.5 | Hours per site (to close the WO generated by MC)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) |  | Hours per site
Contractor Hourly Rate
Contractor Labour | 0 | Included above
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 63.45 | 126.9 | 130.0725 | 130.0725 | 0 | 0 | 0 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0050 | Every 1 year(s)
QLD-ET-WI-PM012-0050 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | Bungalora - System 1 | Bungalora System 1 - Valve Cooling System
QLD-ET-WI-PM012-0050 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | Bungalora - System 2 | Bungalora System 2 - Valve Cooling System
QLD-ET-WI-PM012-0050 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | Bungalora - System 3 | Bungalora System 3 - Valve Cooling System
QLD-ET-WI-PM012-0050 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | Mullumbimby - System 1 | Mullumbimby System 1 - Valve Cooling System
QLD-ET-WI-PM012-0050 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | Mullumbimby - System 2 | Mullumbimby System 2 - Valve Cooling System
QLD-ET-WI-PM012-0050 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | Mullumbimby - System 3 | Mullumbimby System 3 - Valve Cooling System
QLD-ET-WI-PM024-0050 | Every 2 year(s)
QLD-ET-WI-PM024-0050 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | Bungalora - System 1 | Bungalora System 1 - Valve Cooling System
QLD-ET-WI-PM024-0050 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | Bungalora - System 2 | Bungalora System 2 - Valve Cooling System
QLD-ET-WI-PM024-0050 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | Bungalora - System 3 | Bungalora System 3 - Valve Cooling System
QLD-ET-WI-PM024-0050 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | Mullumbimby - System 1 | Mullumbimby System 1 - Valve Cooling System
QLD-ET-WI-PM024-0050 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | Mullumbimby - System 2 | Mullumbimby System 2 - Valve Cooling System
QLD-ET-WI-PM024-0050 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | Mullumbimby - System 3 | Mullumbimby System 3 - Valve Cooling System
QLD-ET-WI-PM060-0050 | Every 5 year(s)
QLD-ET-WI-PM060-0050-BLA1 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | Bungalora - System 1 | Bungalora System 1 - Valve Cooling System
QLD-ET-WI-PM060-0050-BLA2 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | Bungalora - System 2 | Bungalora System 2 - Valve Cooling System
QLD-ET-WI-PM060-0050-BLA3 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | Bungalora - System 3 | Bungalora System 3 - Valve Cooling System
QLD-ET-WI-PM060-0050-MUL1 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | Mullumbimby - System 1 | Mullumbimby System 1 - Valve Cooling System
QLD-ET-WI-PM060-0050-MUL2 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | Mullumbimby - System 2 | Mullumbimby System 2 - Valve Cooling System
QLD-ET-WI-PM060-0050-MUL3 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | Mullumbimby - System 3 | Mullumbimby System 3 - Valve Cooling System

## 0050 (2)
Summary | NITROGEN BOTTLE REPLACEMENT
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 34130.4932 | 6493.2192 | 6655.5497 | 6821.9384 | 6992.4869 | 7167.2991
APA Material Costs |  |  | 45070.1968 | 8489.1776 | 8743.8529 | 9006.1685 | 9276.3536 | 9554.6442
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Nitrogen bottle replacement
| Sites | 2 | Per Site
Number of Components to be serviced |  | 2
Discussion
The nitrogen bottle must be replaced regularly
Each converter building has 4 bottles (4 x 6 = 24 in total)
The bottle are used in pairs - so when changed 2 bottles are replaced
It takes an hour to replace the bottles (every 2 months per building)
Another hour has been allocated for the exchange of the bottles (every 2 months per site) and to update the log
The bottles remain the property of BOC with a monthly rental fee covering the hire of the bottle
Directlink must also purchase the nitrogen gas they use
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM001-0050 | Every 1 month(s) |  |  | 12 | 12 | 12 | 12 | 12
APA Costs
APA Maintenance Staff (Hrs) | 2 | Hours per site (contractor on site and to install the bottles)
APA Supervision (Hrs) | 0.5 | Hours per site (processing invoices)
APA Material Costs | 343.4133 | Material Cost per site per month
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0 | Hours per building
Contractor Materials | 0
Material Costs |  | Anecdotal Information from Operations Manager
Nitrogen Gas | 8241.92 | Total Cost p.a. (from Operations Manager 7/5/14)
Nitrogen Gas (refill) | 33.04 | Per bottle (From Operations Manager 7/5/14)
Bottles per year | 26 | From Operations Manager 7/5/14
Container service charge | 51.27 | per month (From Operations Manager 7/5/14)
Number of "containers" | 12 | (From Operations Manager 7/5/14)
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 263.952 | 527.904 | 34130.4932 | 6493.2192 | 6655.5497 | 6821.9384 | 6992.4869 | 7167.2991
APA Material Costs | 343.4133 | 686.8267 | 45070.1968 | 8489.1776 | 8743.8529 | 9006.1685 | 9276.3536 | 9554.6442
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 0052
Summary | VALVE COOLING SYSTEM PUMP MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 19395.8522 | 3690 | 3782.25 | 3876.8062 | 3973.7264 | 4073.0696
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Valve Cooling Pump Maintenance
| Pumps | 12
Number of Components to be serviced |  | 12 | Two pumps per building
Discussion
Major corrective maintenance has been undertaken recently
It is felt that this has addressed issues that were being experienced with these pumps (leaks)
Annual maintenance is therefore assumed to be an inspection, check of the oil and check the alignment
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0052 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.083333 | Hours per pump
APA Supervision (Hrs) | 0.71528 | Hours per pump
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 4 | Hours per pump (aligns with the ABB recommended time)
Contractor Hourly Rate | 75
Contractor Labour | 300
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 99.123 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 300 | 3600 | 19395.8522 | 3690 | 3782.25 | 3876.8062 | 3973.7264 | 4073.0696
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0052 | Every 1 year(s)
QLD-ET-WI-PM012-0052-BLA1 | VALVE COOLING SYSTEM PUMP MAINTENANCE | Bungalora - System 1 | Bungalora System 1 - Valve Cooling System
QLD-ET-WI-PM012-0052-BLA2 | VALVE COOLING SYSTEM PUMP MAINTENANCE | Bungalora - System 2 | Bungalora System 2 - Valve Cooling System
QLD-ET-WI-PM012-0052-BLA3 | VALVE COOLING SYSTEM PUMP MAINTENANCE | Bungalora - System 3 | Bungalora System 3 - Valve Cooling System
QLD-ET-WI-PM012-0052-MUL1 | VALVE COOLING SYSTEM PUMP MAINTENANCE | Mullumbimby - System 1 | Mullumbimby System 1 - Valve Cooling System
QLD-ET-WI-PM012-0052-MUL2 | VALVE COOLING SYSTEM PUMP MAINTENANCE | Mullumbimby - System 2 | Mullumbimby System 2 - Valve Cooling System
QLD-ET-WI-PM012-0052-MUL3 | VALVE COOLING SYSTEM PUMP MAINTENANCE | Mullumbimby - System 3 | Mullumbimby System 3 - Valve Cooling System
Work Order # | VALVE COOLING SYSTEM PUMP MAINTENANCE
QLD-166330 | EDWARDS2 Luke | PM | 2013-09-18 14:36 | All reactors checked. All phase reactors need further investigation, extended shutdown
QLD-166331 | HARRIS James | PM | 2013-08-22 14:48 | James harris insatlled and realigned pump and motor.%0D%0Atheirls changed bearings.
QLD-166332 | HARRIS James | PM | 2013-08-22 14:48 | James harris insatlled and realigned pump and motor.%0D%0Atheirls changed bearings.
QLD-166333 | COOMBER Stuart | PM | 2013-08-22 14:47 | out of service due to fire
QLD-166334 | HARRIS James | PM | 2013-08-22 14:48 | James harris insatlled and realigned pump and motor.%0D%0Atheirls changed bearings.
QLD-166335 | HARRIS James | PM | 2013-08-22 14:48 | James harris insatlled and realigned pump and motor.%0D%0Atheirls changed bearings.

## 0054
Summary | VALVE COOLING MCC THERMOGRAPHIC IMAGING
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 7775.9911 | 1479.3579 | 1516.3418 | 1554.2504 | 1593.1067 | 1632.9343
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 16163.2102 | 3075 | 3151.875 | 3230.6719 | 3311.4387 | 3394.2246
Contractor Materials |  |  | 10936.8198 | 2060 | 2121.8 | 2185.454 | 2251.0176 | 2318.5481
Scheduled Outage Required | No
Work Instruction | not sighted
Valve Cooling MCC Thermographic Imaging
| Sites | 2
Number of Components to be serviced |  | 2
Discussion
Using a thermographic camera take photographs of the various components looking for those which are running excessively hot
Those components which are running excessively hot are probably faulty (and require further maintenance)
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0054 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.5 | Hours per site
APA Supervision (Hrs) | 5.2917 | Hours per site (extra hour per site allocated for inspection of the photographs and storing)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 1500 | Thearle/SAE (Anecdotal: Works Scheduler stated it was a fixed price for the inspection and report)
Contractor Materials | 1000 | Anecdotal: Includes hire of the thermal imager (not possible to combine with 0126)
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 721.638 | 1443.276 | 7775.9911 | 1479.3579 | 1516.3418 | 1554.2504 | 1593.1067 | 1632.9343
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 1500 | 3000 | 16163.2102 | 3075 | 3151.875 | 3230.6719 | 3311.4387 | 3394.2246
Contractor Materials | 1000 | 2000 | 10936.8198 | 2060 | 2121.8 | 2185.454 | 2251.0176 | 2318.5481
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0054 | Every 1 year(s)
QLD-ET-WI-PM012-0054 | VALVE COOLING MCC THERMOGRAPHIC IMAGING | Bungalora System 1 - Station Service Power System | Bungalora System 1 - Valve Cooling Motor Control Centre | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0054 | VALVE COOLING MCC THERMOGRAPHIC IMAGING | Bungalora System 2 - Station Service Power System | Bungalora System 2 - Valve Cooling Motor Control Centre | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0054 | VALVE COOLING MCC THERMOGRAPHIC IMAGING | Bungalora System 3 - Station Service Power System | Bungalora System 3 - Valve Cooling Motor Control Centre | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0054 | VALVE COOLING MCC THERMOGRAPHIC IMAGING | Mullumbimby System 1 - Station Service Power System | Mullumbimby System 1 - Valve Cooling Motor Control Centre | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0054 | VALVE COOLING MCC THERMOGRAPHIC IMAGING | Mullumbimby System 2 - Station Service Power System | Mullumbimby System 2 - Valve Cooling Motor Control Centre | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0054 | VALVE COOLING MCC THERMOGRAPHIC IMAGING | Mullumbimby System 3 - Station Service Power System | Mullumbimby System 3 - Valve Cooling Motor Control Centre | 1 | 1 | 1 | 1
Work Order # | VALVE COOLING MCC THERMOGRAPHIC IMAGING
QLD-166315 | COOMBER Stuart | PM | 2013-08-22 14:51 | out of service

## 0056
Summary | AIR BLAST COOLER MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 42190.319 | 8514.1123 | 7477.2719 | 8945.1392 | 7855.8087 | 9397.9869
APA Material Costs |  |  | 48245.4158 | 15141 | 0 | 16063.0869 | 0 | 17041.3289
Contractor Labour |  |  | 66201.7937 | 20986.875 | 0 | 22049.3355 | 0 | 23165.5832
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Air Blast Cooler (Fan) Maintenance
| Fans | 210 | Each air blast cooler comprises 7 banks of 5 in each building
Number of Components to be serviced |  | 210
Discussion
3 monthly check fans for imbalance |  | Cleanliness - listening 1 minute per fan
Annual check of motor current and current imbalance |  | 10 minutes per motor
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM003-0056 | Every 3 months(s) | Check for imbalance |  | 4 | 4 | 4 | 4 | 4
APA Costs
APA Maintenance Staff (Hrs) | 0.016667 | Hours per fan (1 minute per fan motor)
APA Supervision (Hrs) | 0.0095238 | Hours per fan
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 2.8794 | 604.6785 | 13031.3943 | 2479.1819 | 2541.1614 | 2604.6904 | 2669.8077 | 2736.5529
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0056 | Every 1 year(s) | Check for current imbalance in the fan motors |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.17143 | Hours per fan (10 minutes per fan motor)
APA Supervision (Hrs) | 0.040873 | Hours per fan
APA Material Costs | 70 | From below assuming required replacements are undertaken annually
Contractor Costs
Contractor Labour (Hrs) | 0.8 | Hours per fan (to replace fans and motors)
Contractor Hourly Rate | 75 | Thearle/SAE
Contractor Labour | 60
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 22.3727 | 4698.261 | 25312.9933 | 4815.7175 | 4936.1105 | 5059.5132 | 5186.0011 | 5315.6511
APA Material Costs | 70 | 14700 | 48245.4158 | 15141 | 0 | 16063.0869 | 0 | 17041.3289
Contractor Labour | 60 | 12600 | 40739.5654 | 12915 | 0 | 13568.8219 | 0 | 14255.7435
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM024-0056 | Every 2 year(s) | Undertake Cleaning |  | 1 | 0 | 1 | 0 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.0047619 | Hours per fan
APA Supervision (Hrs) | 0.040873 | Hours per fan
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 0.5 | Hours per fan
Contractor Hourly Rate | 75
Contractor Labour | 37.5
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 5.6642 | 1189.476 | 3845.9314 | 1219.2129 | 0 | 1280.9356 | 0 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 37.5 | 7875 | 25462.2283 | 8071.875 | 0 | 8480.5137 | 0 | 8909.8397
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Material Costs
Anecdotal: Discussed with the Works Scheduler and the Operations Manager
Fan Motor replacement | 250
Fan Motor Lifetime | 5 | years
Annual material cost (Fan Motors) | 50
Time to replace (Fan Motors) | 2 | hours
Annual maintenance hours (Fan Motors) | 0.4 | hours / fan
Fan Blade replacement | 100
Fan Blade Lifetime | 5 | years
Annual material cost (Fan Blades) | 20 | per fan
Time to replace Fan Blade | 2 | hours
Annual maintenance hours (Fan Blades) | 0.4 | hours / fan
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM024-0056 | Every 2 year(s)
QLD-ET-WI-PM024-0056 | AIR BLAST COOLER MAINTENANCE | Bungalora System 1 - Valve Cooling System | Bungalora System 1 - Valve Cooling Water Cooling Tower
QLD-ET-WI-PM024-0056 | AIR BLAST COOLER MAINTENANCE | Bungalora System 2 - Valve Cooling System | Bungalora System 2 - Valve Cooling Water Cooling Tower
QLD-ET-WI-PM024-0056 | AIR BLAST COOLER MAINTENANCE | Bungalora System 3 - Valve Cooling System | Bungalora System 3 - Valve Cooling Water Cooling Tower
QLD-ET-WI-PM024-0056 | AIR BLAST COOLER MAINTENANCE | Mullumbimby System 1 - Valve Cooling System | Mullumbimby System 1 - Valve Cooling Water Cooling Tower
QLD-ET-WI-PM024-0056 | AIR BLAST COOLER MAINTENANCE | Mullumbimby System 2 - Valve Cooling System | Mullumbimby System 2 - Valve Cooling Water Cooling Tower
QLD-ET-WI-PM024-0056 | AIR BLAST COOLER MAINTENANCE | Mullumbimby System 3 - Valve Cooling System | Mullumbimby System 3 - Valve Cooling Water Cooling Tower
Work Order # | AIR BLAST COOLER MAINTENANCE
QLD-171841 | COOMBER Stuart | PM | 2013-12-09 09:54 | Notdone, system decommisioned
QLD-171842 | MCALLISTER Jack (no PIO) | PM | 2013-12-09 09:56 | All cooling fins cleaned. Selected motors/Fans changed
QLD-171843 | MCALLISTER Jack (no PIO) | PM | 2013-12-09 09:56 | All cooling fins cleaned. Selected motors/Fans changed
QLD-171844 | COOMBER Stuart | PM | 2013-09-19 10:02 | decommissioned
QLD-171845 | MCALLISTER Jack (no PIO) | PM | 2013-12-09 09:56 | All cooling fins cleaned. Selected motors/Fans changed
QLD-171846 | MCALLISTER Jack (no PIO) | PM | 2013-12-09 09:56 | All cooling fins cleaned. Selected motors/Fans changed

## 0060
Summary | VALVE DEHUMIDIFIER MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 25861.1363 | 4920 | 5043 | 5169.075 | 5298.3019 | 5430.7594
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | DL-WI-25
Valve Dehumidifier Maintenance
| Sites | 2
Number of Components to be serviced |  | 2
Discussion
ABB recommended inspection only checked that the fan motors where running
Testing revealed the dehumidifiers were non-operational so fans were only circulating air …
Non-operational status of the dehumidifiers was confirmed from testing by the OEM
APA have updated the maintenance procedure to include a functional test of the dehumidifiers
This enhanced maintenance is undertaken annually
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0060 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.5 | Hours per site
APA Supervision (Hrs) | 4.2917 | Hours per site
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 32 | Hours per site (Anecdotal: time suggested by the Operations Manager noting that there are three systems at each site)
Contractor Hourly Rate | 75 | Have used the same cost as Thearle/SAE despite invoices showing Munters costs are somewhat higher
Contractor Labour | 2400 | Munters (Onsite OPEX suggests that this might be slightly too high as Mullumbimby only is shown as $1540)
Contractor Materials | 0 | Invoices show that repairs are expensive so will accept slightly higher maintenance and $0 for materials
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 594.738 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 2400 | 4800 | 25861.1363 | 4920 | 5043 | 5169.075 | 5298.3019 | 5430.7594
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0060 | Every 1 year(s)
QLD-ET-WI-PM012-0060 | VALVE DEHUMIDIFIER MAINTENANCE | Bungalora - System 1 | Bungalora System 1 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0060 | VALVE DEHUMIDIFIER MAINTENANCE | Bungalora - System 2 | Bungalora System 2 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0060 | VALVE DEHUMIDIFIER MAINTENANCE | Bungalora - System 3 | Bungalora System 3 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0060 | VALVE DEHUMIDIFIER MAINTENANCE | Mullumbimby - System 1 | Mullumbimby System 1 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0060 | VALVE DEHUMIDIFIER MAINTENANCE | Mullumbimby - System 2 | Mullumbimby System 2 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0060 | VALVE DEHUMIDIFIER MAINTENANCE | Mullumbimby - System 3 | Mullumbimby System 3 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
Work Order # | VALVE DEHUMIDIFIER MAINTENANCE
QLD-166318 | COOMBER Stuart | PM | 2013-12-09 09:57 | System decommissioned. Munters looking after unit.
QLD-166319 | EDWARDS2 Luke | PM | 2013-12-09 13:59 | Units failed annual maintenance checks. Munters have pulled units out and %0D%0Ataken away for overhaul. New work order number 191697
QLD-166320 | EDWARDS2 Luke | PM | 2013-12-09 14:03 | Units failed annual maintenance checks.Munters have taken away for %0D%0Aoverhaul .New work order number 191694.
QLD-166321 | COOMBER Stuart | PM | 2013-08-22 14:50 | out of service
QLD-166322 | HARRIS James | PM | 2013-12-09 14:05 | Units failed annual maintenance checks.Munters have taken away for %0D%0Aoverhaul .New work order number 191700. reports on server
QLD-166323 | HARRIS James | PM | 2013-12-09 14:07 | Units failed annual maintenance checks.Munters have taken away for %0D%0Aoverhaul .New work order number 191696.
Task Num | Expenditure Type | Original Transaction Reference | Quantity | Cost Amount | PA Description | Vendor / Customer Name | MA Account | Task Name
560.01 PLANT AND EQUIP | R/M - PLANT / EQUIP | 6348904 | 8770.94 | 8770.94 | Testing and Repair of Dehumidifiers at Bungalora | MUNTERS PTY LTD | Repairs & Maint - Routine | PLANT AND EQUIPMENT
560.01 PLANT AND EQUIP | R/M - PLANT / EQUIP | 6348904 | 12693.06 | 12693.06 | Testing and Repair of Dehumidifiers at Mullumbimby | MUNTERS PTY LTD | Repairs & Maint - Routine | PLANT AND EQUIPMENT
560.01 PLANT AND EQUIP | R/M-NON-ROUTINE MAINTENANCE | 6302409 | 1540 | 1540 | Munters to carry out annual maintenace on Mullumbimby dehumindifiers, quote No.AUSASPARO3167-001 | MUNTERS PTY LTD | Repairs & Maint - Non - Routine | PLANT AND EQUIPMENT

## 0062
Summary | VALVE HUMIDITY CONTROL SYSTEM
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | DL-WI-25
Valve Humidifier Control System
| Sites | 2
Number of Components to be serviced |  | 2
Discussion
This maintenance is covered as a single item under 0060 (as outlined in discussions with the Works Scheduler)
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0062 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0 | Hours per site
APA Supervision (Hrs) | 0 | Hours per site
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0062 | Every 1 year(s)
QLD-ET-WI-PM012-0062 | VALVE HUMIDITY CONTROL SYSTEM | Bungalora - System 1 | Bungalora System 1 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0062 | VALVE HUMIDITY CONTROL SYSTEM | Bungalora - System 2 | Bungalora System 2 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0062 | VALVE HUMIDITY CONTROL SYSTEM | Bungalora - System 3 | Bungalora System 3 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0062 | VALVE HUMIDITY CONTROL SYSTEM | Mullumbimby - System 1 | Mullumbimby System 1 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0062 | VALVE HUMIDITY CONTROL SYSTEM | Mullumbimby - System 2 | Mullumbimby System 2 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
QLD-ET-WI-PM012-0062 | VALVE HUMIDITY CONTROL SYSTEM | Mullumbimby - System 3 | Mullumbimby System 3 - Heating Ventilating & Air Conditioning | 1 | 1 | 1 | 1 | 1
Work Order # | VALVE HUMIDITY CONTROL SYSTEM
QLD-166889 | COOMBER Stuart | PM | 2013-07-19 11:56 | no system 1 at Mullum
QLD-166891 | HARRIS James | PM | 2013-12-06 10:11 | Done, Munters carrying out a full overhaul of dehumnidifiers

## 0104 (1)
Summary | REACTOR MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 37310.7745 | 32121.4039 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 65920 | 65920 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 90283.4818 | 75068.4375 | 3664.0547 | 3755.6561 | 3849.5475 | 3945.7861
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-29
AC Reactor
| WT.L1 | 6
| WT.L2 | 6
| WT.L3 | 6
| WA.Z1.L1 | 18
| WA.Z1.Z11.L1 | 18
| WA.Z1.Z12.L1 | 18
| U.L1 | 3 | These 3 reactors are installed in the new Mullumbimby converter - the original phase reactors require special maintenance and are treated on sheet 0104 (2)
DC Reactor
| U.L2 | 6 | 9th harmonic reactor added during plant commissioning
| WP1.L1 | 6
| WP2.L1 | 6
Number of Components to be serviced |  | 93
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0104 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.010753 | Hours per reactor
APA Supervision (Hrs) | 0.092294 | Hours per reactor
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 0.5 | Hours per reactor since the WI requires them to be cleaned
Contractor Hourly Rate | 75
Contractor Labour | 37.5
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 12.7901 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 37.5 | 3487.5 | 18789.7318 | 3574.6875 | 3664.0547 | 3755.6561 | 3849.5475 | 3945.7861
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM180-0104 | Every 15 year(s) |  |  | 1 | 0 | 0 | 0 | 0
APA Costs
APA Maintenance Staff (Hrs) | 3 | Hours per reactor (this task will take several days - but safety briefings will be required each day + assistance)
APA Supervision (Hrs) | 0.18459 | Hours per reactor (due to the extent of the 15 yr maintenance have allowed extra time)
APA Material Costs | 688.172 | Average material cost per reactor
Contractor Costs
Contractor Labour (Hrs) | 10 | Hours per reactor
Contractor Hourly Rate | 75
Contractor Labour | 750
Contractor Materials | 0 | Sandpaper, cleaners, brushes, etc
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 324.1772 | 30148.479 | 30902.191 | 30902.191 | 0 | 0 | 0 | 0
APA Material Costs | 688.172 | 64000 | 65920 | 65920 | 0 | 0 | 0 | 0
Contractor Labour | 750 | 69750 | 71493.75 | 71493.75 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Material Costs for 15 year maintenance
All of the following figures were provided anecdotally by the Operations Manager
Reactor | diameter (m) | length (m) | Number | Reactor Surface Area
U.L2 | 1.035 | 1.53 | 6 | 59.6984
WP1.L1, WP2.L1 | 1.125 | 1.495 | 12 | 126.8104
Z11.L1 | 0.935 | 0.84 | 18 | 88.8266
Z12.L1 | 0.57 | 0.63 | 18 | 40.6133
Z1.L1 | 0.796 | 0.93 | 18 | 83.7237
WT.L1,2,3 | 1.155 | 1.355 | 18 | 177.0002
From the Material Data Sheet
Coverage | 6 | m2/kg
Cost | 16000 | $/tin | Anecdotal: Provided by Operations Manager
Tin Size | 25 | kg
Total Area to be painted | 576.6726 | m^2 (from above table)
kgs of paint | 96.1121
tins of paint | 4 | Whole Tins
Cost of Paint | 64000
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Bungalora | Bungalora
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Bungalora | Bungalora - System 2
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Bungalora | Bungalora - System 3
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Mullumbimby | Mullumbimby
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Mullumbimby | Mullumbimby - System 3
QLD-ET-WI-PM180-0104-BLA1 | REACTOR MAINTENANCE - 15YR | DirectLink | Bungalora - System 1
QLD-ET-WI-PM180-0104-BLA2 | REACTOR MAINTENANCE - 15YR | Bungalora | Bungalora - System 2
QLD-ET-WI-PM180-0104-BLA3 | REACTOR MAINTENANCE - 15YR | Bungalora | Bungalora - System 3
QLD-ET-WI-PM180-0104-MUL1 | REACTOR MAINTENANCE - 15YR | DirectLink | Mullumbimby - System 1
QLD-ET-WI-PM180-0104-MUL2 | REACTOR MAINTENANCE - 15YR | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM180-0104-MUL3 | REACTOR MAINTENANCE - 15YR | Mullumbimby | Mullumbimby - System 3
Work Order # | REACTOR MAINTENANCE - 1YR
QLD-164862 | COOMBER Stuart | PM | 2013-09-18 13:07 | decommissioned
QLD-164863 | EDWARDS2 Luke | PM | 2013-09-18 14:36 | All reactors checked. All phase reactors need further investigation, extended shutdown
QLD-164864 | EDWARDS2 Luke | PM | 2013-09-18 14:36 | All reactors checked. All phase reactors need further investigation, extended shutdown
QLD-164865 | COOMBER Stuart | PM | 2013-09-16 17:15 | out of service
QLD-164866 | EDWARDS2 Luke | PM | 2013-09-18 14:36 | All reactors checked. All phase reactors need further investigation, extended shutdown
QLD-164867 | EDWARDS2 Luke | PM | 2013-09-18 14:36 | All reactors checked. All phase reactors need further investigation, extended shutdown

## 0104 (2)
Summary | PHASE REACTOR MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 141907.2798 | 26997.4145 | 27672.3499 | 28364.1586 | 29073.2626 | 29800.0942
APA Material Costs |  |  | 39700.6558 | 7477.8 | 7702.134 | 7933.198 | 8171.194 | 8416.3298
Contractor Labour |  |  | 336733.5455 | 64062.5 | 65664.0625 | 67305.6641 | 68988.3057 | 70713.0133
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-46
AC Reactor (Phase Reactor)
| U.L1 | 15 | Assumption this maintenance only applies to the original phase reactors
Number of Components to be serviced |  | 15
Discussion
Air circulating through the ducting and reactor results in dust build up
Fibre glass ducting is showing signs of cracking so are applying grease to the surface each year (must first remove the old grease)
To clean the reactors a special machine grinds dry ice (CO2) and immediately uses it as the abrasive for blasting between the reactor coils (which also accumulate dust)
It is assumed that the new Mullumbimby phase reactor will also be treated each year
The new Mullumbimby station will have a different design of Phase Reactor which does not require the same level of maintenance
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0104 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 16.0667 | Hours per reactor (two people for a full 8 hour day - requires attention to detail)
APA Supervision (Hrs) | 1.1444 | Hours per reactor
APA Material Costs | 484 | Average cost per reactor
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 4166.6667 | Price per reactor for dry ice cleaning (Anecdotal: refer to discussion below)
Contractor Materials | 0 | Cost of dry ice assumed to be included in the contractor cost
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 1755.9294 | 26338.941 | 141907.2798 | 26997.4145 | 27672.3499 | 28364.1586 | 29073.2626 | 29800.0942
APA Material Costs | 484 | 7260 | 39700.6558 | 7477.8 | 7702.134 | 7933.198 | 8171.194 | 8416.3298
Contractor Labour | 4166.6667 | 62500 | 336733.5455 | 64062.5 | 65664.0625 | 67305.6641 | 68988.3057 | 70713.0133
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
APA Staff Hours
Technicians
Site Access for Contractors | 0.066667 | Security briefing
Application of grease | 16 | Requires close attention to detail - 2 staff for a full day each reactor
O&M Supervisor
Scheduling | 0.57222 | Raise and close work order, arranging specialist Dry Ice contract cleaner, sourcing dry ice, purchasing grease, etc
Additional due to critical nature | 0.57222 | High priority item: EXTRA attention to detail
Reliability Engineer |  | This is a placeholder and is not being used on this worksheet
Supervision during Dry Ice Cleaning | 8 | Work Instruction specifies that the reliability engineer must be present during dry ice cleaning (per building x 5)
Material Costs
Coating the fibre glass in an insulating grease
Additional control measure is to coat the fibre glassing in an insulating grease
Bugs get caught in this grease |  | Bugs per sq cm was 3 - 4 after only 4 months
Need to clean off grease before the new coat is reapplied
Dry Ice blasting of the phase reactor coil
Cost of initial dry ice cleaning | 25000 | Per Building (Anecdotal: Provided by Operations Manager)
Reduced time if cleaned annually | 50%
Price per building | 12500 | The original cost of applying the dry ice treatment was $25k per building. Annual cleaning will reduce the time (and cost)
Price per reactor | 4166.6667
Cost of the insulating grease
Price per tub | 440 | 22kg from Dow Corning (Anecdotal: Provided by Operations Manager)
Cost per reactor | 484 | 16.5 tubs used in the last maintenance cycle (Anecdotal: Operations Manager after discussion with onsite technicians)

## 0104 (3)
Summary | PHASE REACTOR FAN MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 7721.5425 | 1219.2129 | 1249.6932 | 1280.9356 | 2625.9179 | 1345.7829
APA Material Costs |  |  | 1749.8912 | 329.6 | 339.488 | 349.6726 | 360.1628 | 370.9677
Contractor Labour |  |  | 14996.228 | 1845 | 1891.125 | 1938.4031 | 7285.1651 | 2036.5348
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | not sighted
AC Reactor Cooling Fans
| Reactor Fans | 32 | 2 fans per reactor
Number of Components to be serviced |  | 32
Discussion
While the new Mullumbimby converter has different phase reactors there will still be a need to check the phase reactor fans
The 5 yearly maintenance of the Fans was last undertaken in 2013 - It will be due again in 2018
It is assumed that the new Mullumbimby fans will have their 5 year inspection brought into line with the other reactor fans
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0104 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.03125 | Hours per reactor fan
APA Supervision (Hrs) | 0.26823 | Hours per reactor fan
APA Material Costs | 10 | Lubricant
Contractor Costs
Contractor Labour (Hrs) | 0.75 | Hours per reactor (assumes that ABB recommended time is per PAIR of fans)
Contractor Hourly Rate | 75
Contractor Labour | 56.25 | Price per reactor
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 37.1711 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 10 | 320 | 1749.8912 | 329.6 | 339.488 | 349.6726 | 360.1628 | 370.9677
Contractor Labour | 56.25 | 1800 | 9697.9261 | 1845 | 1891.125 | 1938.4031 | 1986.8632 | 2036.5348
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | Contractor Rate | 85 | per hour | Cost | 16000 | $/tin | Quote not yet received (in email)
QLD-ET-WI-PM060-0104 | Every 5 year(s) |  |  | 0 | 0 | 0 | 1 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0.03125 | Hours per reactor fan
APA Supervision (Hrs) | 0.26823 | Hours per reactor fan
APA Material Costs | 0 | Average cost per reactor fan
Contractor Costs
Contractor Labour (Hrs) | 2 | Requires measurements and anecdotally is described as "difficult to access"
Contractor Hourly Rate | 75
Contractor Labour | 150 | Price per reactor fan
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 37.1711 | 1189.476 | 1312.9589 | 0 | 0 | 0 | 1312.9589 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 150 | 4800 | 5298.3019 | 0 | 0 | 0 | 5298.3019 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 0104 (4)
Summary | DC ZERO SEQUENCE SMOOTHING REACTOR MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 1212.2408 | 230.625 | 236.3906 | 242.3004 | 248.3579 | 254.5668
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-46
DC zero sequence smoothing reactor
| R1.L1 | 6
Number of Components to be serviced |  | 6
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0104 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.16667 | Hours per reactor
APA Supervision (Hrs) | 1.4306 | Hours per reactor
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 0.5 | Hours per reactor (WI requires them to be cleaned and this aligns with ABB's recommended maintenance)
Contractor Hourly Rate | 75
Contractor Labour | 37.5 | Price per reactor
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 198.246 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 37.5 | 225 | 1212.2408 | 230.625 | 236.3906 | 242.3004 | 248.3579 | 254.5668
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Bungalora | Bungalora
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Bungalora | Bungalora - System 2
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Bungalora | Bungalora - System 3
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Mullumbimby | Mullumbimby
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM012-0104 | REACTOR MAINTENANCE - 1YR | Mullumbimby | Mullumbimby - System 3

## 0110
Summary | IGBT VALVE MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 21459.183 | 4082.5422 | 4184.6058 | 4289.2209 | 4396.4514 | 4506.3627
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 40003.9452 | 7610.625 | 7800.8906 | 7995.9129 | 8195.8107 | 8400.706
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-26 | Defines all the required steps
IGBT Valves
| U.Vx.V1 | 18
| U.Vx.V2 | 18
Number of Components to be serviced |  | 36
Discussion
This is just the annual testing of the IGBT Values
The specialist test equipment must be set up and packed away after the testing
Before testing can commence the control system must be placed in the correct mode
The testing of the individual values is then undertaken
The valve positions which are faulty are recorded
Record keeping (locations of the faulty valves)
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0110 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
Visual Inspection of each of the IGBT Stacks
APA Costs
APA Maintenance Staff (Hrs) | 0.5 | Hours per IGBT valve (each valve contains 148 IGBTs)
APA Supervision (Hrs) | 0.47685 | Hours per IGBT valve (extra time allowed due to the number of failures and need to order replacements)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 2 | Hours per IGBT valve - As discussed with Work Scheduler (note the ABB maintenance suggests 3 staff for 3 hours)
Contractor Hourly Rate | 75
Contractor Labour | 150
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 110.638 | 3982.968 | 21459.183 | 4082.5422 | 4184.6058 | 4289.2209 | 4396.4514 | 4506.3627
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 150 | 5400 | 29093.7783 | 5535 | 5673.375 | 5815.2094 | 5960.5896 | 6109.6043
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reduced Light Test for all IGBT's
APA Costs
APA Maintenance Staff (Hrs) | 0 | Hours per IGBT valve (undertaken at same time as Visual Inspection so no extra time allocated)
APA Supervision (Hrs) | 0 | Hours per IGBT valve (undertaken at same time as Visual Inspection so no extra time allocated)
APA Material Costs | 0 | Average IGBT replacement cost per stack
Contractor Costs
Contractor Labour (Hrs) | 0.75 | Hours per IGBT valve (wheel test equipment up to each IGBT stack and test each IGBT individually)
Contractor Hourly Rate | 75 | Thearle/SAE
Contractor Labour | 56.25
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 56.25 | 2025 | 10910.1669 | 2075.625 | 2127.5156 | 2180.7035 | 2235.2211 | 2291.1016
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0110 | IGBT VALVE MAINTENANCE | Bungalora - System 1 | Bungalora System 1 - Inverter / Rectifier Area
QLD-ET-WI-PM012-0110 | IGBT VALVE MAINTENANCE | Bungalora - System 2 | Bungalora System 2 - Inverter / Rectifier Area
QLD-ET-WI-PM012-0110 | IGBT VALVE MAINTENANCE | Bungalora - System 3 | Bungalora System 3 - Inverter / Rectifier Area
QLD-ET-WI-PM012-0110 | IGBT VALVE MAINTENANCE | Mullumbimby - System 1 | Mullumbimby System 1 - Inverter / Rectifier Area
QLD-ET-WI-PM012-0110 | IGBT VALVE MAINTENANCE | Mullumbimby - System 2 | Mullumbimby System 2 - Inverter / Rectifier Area
QLD-ET-WI-PM012-0110 | IGBT VALVE MAINTENANCE | Mullumbimby - System 3 | Mullumbimby System 3 - Inverter / Rectifier Area
Work Order # | IGBT VALVE MAINTENANCE
QLD-166892 | COOMBER Stuart | PM | 2013-09-19 08:56 | decommissioned
QLD-166893 | Thearle Electrical | PM | 2013-12-09 09:51 | Done, spread sheet on server
QLD-166894 | Thearle Electrical | PM | 2013-12-09 09:50 | Done, spread sheet on server
QLD-166895 | COOMBER Stuart | PM | 2013-09-19 08:56 | decommissioned
QLD-166896 | Thearle Electrical | PM | 2013-12-06 10:51 | done, results on WO
QLD-166897 | Thearle Electrical | PM | 2013-12-06 10:43 | Done,

## 0120
Summary | DIRECT VOLTAGE DIVIDER MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 10254.5149 | 2438.4258 | 1249.6932 | 2561.8711 | 1312.9589 | 2691.5658
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 5334.4505 | 1383.75 | 472.7812 | 1453.8023 | 496.7158 | 1527.4011
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-36
DC Voltage Divider
| WPx.U1 | 12
Number of Components to be serviced |  | 12
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0120 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.083333 | Hours per voltage divider
APA Supervision (Hrs) | 0.71528 | Hours per voltage divider
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 0.5 | Hours per voltage divider (assumed to be inspection and halved the time recommended on the ABB maintenance schedule)
Contractor Hourly Rate | 75
Contractor Labour | 37.5
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 99.123 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 37.5 | 450 | 2424.4815 | 461.25 | 472.7812 | 484.6008 | 496.7158 | 509.1337
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM024-0120 | Every 2 year(s) |  |  | 1 | 0 | 1 | 0 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.083333 | Hours per voltage divider
APA Supervision (Hrs) | 0.71528 | Hours per voltage divider
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 1 | Hours per voltage divider (validated against ABB recommended maintenance)
Contractor Hourly Rate | 75
Contractor Labour | 75
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 99.123 | 1189.476 | 3845.9314 | 1219.2129 | 0 | 1280.9356 | 0 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 75 | 900 | 2909.969 | 922.5 | 0 | 969.2016 | 0 | 1018.2674
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0120-BLA1 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | Bungalora | Bungalora - System 1
QLD-ET-WI-PM012-0120-BLA2 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | Bungalora | Bungalora - System 2
QLD-ET-WI-PM012-0120-BLA3 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | Bungalora | Bungalora - System 3
QLD-ET-WI-PM012-0120-MUL1 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | Mullumbimby | Mullumbimby - System 1
QLD-ET-WI-PM012-0120-MUL2 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM012-0120-MUL3 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | Mullumbimby | Mullumbimby - System 3
QLD-ET-WI-PM024-0120-BLA1 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | Bungalora | Bungalora - System 1
QLD-ET-WI-PM024-0120-BLA2 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | Bungalora | Bungalora - System 2
QLD-ET-WI-PM024-0120-BLA3 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | Bungalora | Bungalora - System 3
QLD-ET-WI-PM024-0120-MUL1 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | Mullumbimby | Mullumbimby - System 1
QLD-ET-WI-PM024-0120-MUL2 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM024-0120-MUL3 | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | Mullumbimby | Mullumbimby - System 3
Work Order # | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR
QLD-166898 | COOMBER Stuart | PM | 2013-09-18 13:43 | decommissioned
QLD-166942 | EDWARDS2 Luke | PM | 2013-09-18 12:17 | done, entered sc
QLD-166943 | COOMBER Stuart | PM | 2013-09-18 14:50 | worked done by Luke and jack as per WO36.done, entered sc.
QLD-166943 | EDWARDS2 Luke | PM | 2013-09-18 14:50 | worked done by Luke and jack as per WO36.done, entered sc.
QLD-166944 | COOMBER Stuart | PM | 2013-09-18 13:28 | decommissioned
QLD-166945 | HARRIS James | PM | 2013-09-18 11:59 | done, entered sc
QLD-166946 | HARRIS James | PM | 2013-09-18 13:34 | done, entered sc
Work Order # | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR
QLD-171847 | COOMBER Stuart | PM | 2013-09-18 12:21 | decommissioned
QLD-171852 | EDWARDS2 Luke | PM | 2013-09-18 14:52 | work carried out by , luke and Jack.done, entered sc.
QLD-171853 | EDWARDS2 Luke | PM | 2013-09-18 14:53 | work done by LE and JMc.done, entered sc.
QLD-171854 | COOMBER Stuart | PM | 2013-09-18 12:19 | decommissioned
QLD-171855 | HARRIS James | PM | 2013-09-18 11:56 | done, checked sc
QLD-171856 | HARRIS James | PM | 2013-09-18 11:57 | done, sc

## 0124
Summary | NITROGEN DISCHARGE UNIT MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 7689.5191 | 1219.2129 | 1249.6932 | 2561.8711 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 9696.4485 | 1383.75 | 1418.3438 | 3876.8062 | 1490.1474 | 1527.4011
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | DL-WI-18
Nitrogen Discharge Unit
| Buildings | 6
Number of Components to be serviced |  | 6
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0124 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.16667 | Hours per building
APA Supervision (Hrs) | 1.4306 | Hours per building
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 3 | Hours per building (from the ABB recommended valve maintenance)
Contractor Hourly Rate | 75
Contractor Labour | 225
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 198.246 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 225 | 1350 | 7273.4446 | 1383.75 | 1418.3438 | 1453.8023 | 1490.1474 | 1527.4011
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM036-0124 | Every 3 year(s) |  |  | 0 | 0 | 1 | 0 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0.16667 | Hours per building
APA Supervision (Hrs) | 1.4306 | Hours per building
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 5 | Hours per building (Using the recommended hourly figure for ion-exchange maintenance from ABB)
Contractor Hourly Rate | 75
Contractor Labour | 375
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 198.246 | 1189.476 | 1280.9356 | 0 | 0 | 1280.9356 | 0 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 375 | 2250 | 2423.0039 | 0 | 0 | 2423.0039 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0124 | Every 1 year(s)
QLD-ET-WI-PM012-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | Bungalora System 1 - Valve Cooling System | Bungalora System 1 - Nitrogen Semi Automatic Discharge Unit
QLD-ET-WI-PM012-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | Bungalora System 2 - Valve Cooling System | Bungalora System 2 - Nitrogen Semi Automatic Discharge Unit
QLD-ET-WI-PM012-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | Bungalora System 3 - Valve Cooling System | Bungalora System 3 - Nitrogen Semi Automatic Discharge Unit
QLD-ET-WI-PM012-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | Mullumbimby System 1 - Valve Cooling System | Mullumbimby System 1 - Nitrogen Semi Automatic Discharge Unit
QLD-ET-WI-PM012-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | Mullumbimby System 2 - Valve Cooling System | Mullumbimby System 2 - Nitrogen Semi Automatic Discharge Unit
QLD-ET-WI-PM012-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | Mullumbimby System 3 - Valve Cooling System | Mullumbimby System 3 - Nitrogen Semi Automatic Discharge Unit
QLD-ET-WI-PM036-0124 | Every 3 year(s)
QLD-ET-WI-PM036-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | Bungalora System 1 - Valve Cooling System | Bungalora System 1 - Nitrogen Semi Automatic Discharge Unit
QLD-ET-WI-PM036-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | Bungalora System 2 - Valve Cooling System | Bungalora System 2 - Nitrogen Semi Automatic Discharge Unit
QLD-ET-WI-PM036-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | Bungalora System 3 - Valve Cooling System | Bungalora System 3 - Nitrogen Semi Automatic Discharge Unit
QLD-ET-WI-PM036-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | Mullumbimby System 1 - Valve Cooling System | Mullumbimby System 1 - Nitrogen Semi Automatic Discharge Unit
QLD-ET-WI-PM036-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | Mullumbimby System 2 - Valve Cooling System | Mullumbimby System 2 - Nitrogen Semi Automatic Discharge Unit
QLD-ET-WI-PM036-0124 | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | Mullumbimby System 3 - Valve Cooling System | Mullumbimby System 3 - Nitrogen Semi Automatic Discharge Unit

## 0126
Summary | CONVERTER STATION THERMOGRAPHIC INSPECTION
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 7775.9911 | 1479.3579 | 1516.3418 | 1554.2504 | 1593.1067 | 1632.9343
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 16163.2102 | 3075 | 3151.875 | 3230.6719 | 3311.4387 | 3394.2246
Contractor Materials |  |  | 10936.8198 | 2060 | 2121.8 | 2185.454 | 2251.0176 | 2318.5481
Scheduled Outage Required | No
Work Instruction | not sighted
Converter Station Thermographic Inspection
| Sites | 2
Number of Components to be serviced |  | 2
Discussion
Thermographic inspection of the Converter barn is not possible due to the installation of solid walls (and noise barriers)
A capital works program is being considered which will add windows to the converter barns
These windows will allow the scheduled maintenance to be undertaken
It is assumed that the windows will be installed before the annual inspection in 2015
Due to the number of components the thermal imaging equipment must be hired separately (cannot be combined with the Thermographic inspection listed in Worksheet 0054)
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PMxxx-0126 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.5 | Hours per site
APA Supervision (Hrs) | 5.2917 | Hours per site (extra hour per site allocated for inspection of the photographs and storing)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 1500 | Thearle/SAE fixed price - Includes writing the report and submitting all required photographic evidence
Contractor Materials | 1000 | Anecdotal : Discussed with Works Scheduler
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 721.638 | 1443.276 | 7775.9911 | 1479.3579 | 1516.3418 | 1554.2504 | 1593.1067 | 1632.9343
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 1500 | 3000 | 16163.2102 | 3075 | 3151.875 | 3230.6719 | 3311.4387 | 3394.2246
Contractor Materials | 1000 | 2000 | 10936.8198 | 2060 | 2121.8 | 2185.454 | 2251.0176 | 2318.5481
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0126 | Every 1 year(s)
QLD-ET-WI-PM012-0126 | CONVERTER STATION THERMOGRAPHIC INSPECTION | Bungalora | Bungalora - System 1
QLD-ET-WI-PM012-0126 | CONVERTER STATION THERMOGRAPHIC INSPECTION | Bungalora | Bungalora - System 2
QLD-ET-WI-PM012-0126 | CONVERTER STATION THERMOGRAPHIC INSPECTION | Bungalora | Bungalora - System 3
QLD-ET-WI-PM012-0126 | CONVERTER STATION THERMOGRAPHIC INSPECTION | Mullumbimby | Mullumbimby - System 1
QLD-ET-WI-PM012-0126 | CONVERTER STATION THERMOGRAPHIC INSPECTION | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM012-0126 | CONVERTER STATION THERMOGRAPHIC INSPECTION | Mullumbimby | Mullumbimby - System 3
Work Order # | CONVERTER STATION THERMOGRAPHIC INSPECTION
QLD-166899 | COOMBER Stuart | PM | 2013-09-18 14:14 | decommission ed
QLD-166902 | COOMBER Stuart | PM | 2013-09-18 14:14 | decommission ed

## 0128
Summary | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 881.9779 | 167.7935 | 171.9884 | 176.2881 | 180.6953 | 185.2127
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Valve Humidifier Control System
| Buildings | 6
Number of Components to be serviced |  | 6
Discussion
This is a very simple test - During the scheduled maintenance shut down, instead of using the control system to complete the shut down the emergency button is pressed
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0128 | Every 1 year(s) |  |  | 1 | 1 | 1 | 1 | 1
APA Costs
APA Maintenance Staff (Hrs) | 0.16667 | Hours per building
APA Supervision (Hrs) | 0.083333 | Hours per building (discounted due to simple nature of the test)
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 27.2835 | 163.701 | 881.9779 | 167.7935 | 171.9884 | 176.2881 | 180.6953 | 185.2127
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM012-0128 | Every 1 year(s)
QLD-ET-WI-PM012-0128 | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | Bungalora | Bungalora - System 1
QLD-ET-WI-PM012-0128 | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | Bungalora | Bungalora - System 2
QLD-ET-WI-PM012-0128 | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | Bungalora | Bungalora - System 3
QLD-ET-WI-PM012-0128 | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | Mullumbimby | Mullumbimby - System 1
QLD-ET-WI-PM012-0128 | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM012-0128 | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | Mullumbimby | Mullumbimby - System 3
Work Order # | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON
QLD-168084 | COOMBER Stuart | PM | 2013-09-16 17:23 | system decommissioned.
QLD-169333 | COOMBER Stuart | PM | 2013-09-16 17:22 | Pushed estop and CB opened.
QLD-168085 | COOMBER Stuart | PM | 2013-06-27 15:48 | No system 1 at Mullum.
QLD-169334 | COOMBER Stuart | PM | 2013-09-16 17:22 | Pushed estop and CB opened.

## 0140
Summary | CIRCUIT BREAKER MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 49217.9485 | 46624.054 | 0 | 1280.9356 | 1312.9589 | 0
APA Material Costs |  |  | 6180 | 6180 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 307161.4591 | 300775.5516 | 0 | 6299.8102 | 86.0974 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | Not sighted (OEM maintenance sheet)
AC Bypass breaker
| WT1.Q2 | 6
AC Circuit Breaker
| WT1.Q1 | 6
AC Disconnector
| WT.Q1 | 1
Number of Components to be serviced |  | 13
Discussion
Majority of this cost is the 15 year circuit breaker maintenance
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM006-0000 | Every 3 year(s) |  |  | 0 | 0 | 1 | 0 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0.076923 | Hours per circuit breaker
APA Supervision (Hrs) | 0.66026 | Hours per circuit breaker
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 6 | Hours per circuit breaker (from ABB recommended maintenance)
Contractor Hourly Rate | 75
Contractor Labour | 450
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 91.4982 | 1189.476 | 1280.9356 | 0 | 0 | 1280.9356 | 0 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 450 | 5850 | 6299.8102 | 0 | 0 | 6299.8102 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM012-0000 | Every 6 year(s) |  |  | 0 | 0 | 0 | 1 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0.076923 | Hours per circuit breaker
APA Supervision (Hrs) | 0.66026 | Hours per circuit breaker
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 6 | Hours per circuit breaker (from ABB recommended maintenance)
Contractor Hourly Rate | 1
Contractor Labour | 6
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 91.4982 | 1189.476 | 1312.9589 | 0 | 0 | 0 | 1312.9589 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 6 | 78 | 86.0974 | 0 | 0 | 0 | 86.0974 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM024-0000 | Every 15 year(s) |  |  | 1 | 0 | 0 | 0 | 0
APA Costs
APA Maintenance Staff (Hrs) | 33.2308 | Hours per circuit breaker (Contractor has specified that 2 APA staff must be available during the maintenance)
APA Supervision (Hrs) | 1.3205 | Hours per circuit breaker (increased due to the size of this job)
APA Material Costs | 461.5385 | Average equipment hire cost per circuit breaker
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 22572.274 | Average price per Circuit Breaker
Contractor Materials | 0
| Reference Year | Total in Reference Year (per maintenance cycle) | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 3498.9909 | 45486.882 | 46624.054 | 46624.054 | 0 | 0 | 0 | 0
APA Material Costs | 461.5385 | 6000 | 6180 | 6180 | 0 | 0 | 0 | 0
Contractor Labour | 22572.274 | 293439.5625 | 300775.5516 | 300775.5516 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Costs
The following anecdotal costs were initially developed by the Operations Manager
15 year maintenance of the circuit breakers has not been performed before and is not similar to any earlier work
APA Labour Costs |  | Contractor has requested that two APA staff are available throughout the maintenance
Time per mechanism | 8 | Estimated at 8 hours per mechanism
APA Staff | 2 | 2 APA staff
APA staff hours / mechanism | 16
Total APA staff hours | 432
APA Material Costs |  | Contractor requires hire of cherry pickers and cranes to be organised by APA
Total Material Costs | 6000
Contractor Labour Cost
| Number of Contacts | Number of Breaker Mechanisms | Number of Components | Cost
WT.Q1 | 3 | 3 | 1 | 29942.8125
WT1.Q1 | 3 | 3 | 6 | 179656.875
WT1.Q2 | 3 | 1 | 6 | 83839.875
Totals | 39 | 27 | 13 | 293439.5625
Cost of similar work (in 2012) | 9500 | Estimates based on Quote from ABB for a pole replacement in 2012
Cost Per Contact | 1996.1875 | 20% of original quote and adjusting 2012 to the Reference Year of 2014
Cost Per Mechanism | 7984.75 | 80% of original quote and adjusting 2012 to the Reference Year of 2014
Total Maintenance Cost (2014) | 293439.5625
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM036-0140 | Every 3 year(s)
QLD-ET-WI-PM036-0140-BLA1 | CIRCUIT BREAKER MAINTENANCE - 3YR | DirectLink | Bungalora System 3 - AC Switchyard Area WT1
QLD-ET-WI-PM036-0140-BLA2 | CIRCUIT BREAKER MAINTENANCE - 3YR | Bungalora - System 2 | Bungalora System 3 - AC Switchyard Area WT1
QLD-ET-WI-PM036-0140-BLA3 | CIRCUIT BREAKER MAINTENANCE - 3YR | Bungalora - System 3 | Bungalora System 3 - AC Switchyard Area WT1
QLD-ET-WI-PM036-0140-MUL1 | CIRCUIT BREAKER MAINTENANCE - 3YR | Mullumbimby - System 1 | Mullumbimby System 1 - AC Switchyard Area WT1
QLD-ET-WI-PM036-0140-MUL2 | CIRCUIT BREAKER MAINTENANCE - 3YR | Mullumbimby - System 2 | Mullumbimby System 1 - AC Switchyard Area WT1
QLD-ET-WI-PM036-0140-MUL3 | CIRCUIT BREAKER MAINTENANCE - 3YR | Mullumbimby - System 3 | Mullumbimby System 1 - AC Switchyard Area WT1
QLD-ET-WI-PM072-0140 | Every 6 year(s)
QLD-ET-WI-PM072-0140-BLA1 | CIRCUIT BREAKER MAINTENANCE - 6YR | Bungalora - System 1 | Mullumbimby System 2 - AC Switchyard Area WT1
QLD-ET-WI-PM072-0140-BLA2 | CIRCUIT BREAKER MAINTENANCE - 6YR | Bungalora - System 2 | Mullumbimby System 2 - AC Switchyard Area WT1
QLD-ET-WI-PM072-0140-BLA3 | CIRCUIT BREAKER MAINTENANCE - 6YR | Bungalora - System 3 | Mullumbimby System 2 - AC Switchyard Area WT1
QLD-ET-WI-PM072-0140-MUL1 | CIRCUIT BREAKER MAINTENANCE - 6YR | Mullumbimby - System 1 | Mullumbimby System 3 - AC Switchyard Area WT1
QLD-ET-WI-PM072-0140-MUL2 | CIRCUIT BREAKER MAINTENANCE - 6YR | Mullumbimby - System 2 | Mullumbimby System 3 - AC Switchyard Area WT1
QLD-ET-WI-PM072-0140-MUL3 | CIRCUIT BREAKER MAINTENANCE - 6YR | Mullumbimby - System 3 | Mullumbimby System 3 - AC Switchyard Area WT1
QLD-ET-WI-PM180-0140 | Every 15 year(s)
QLD-ET-WI-PM180-0140-BLA1 | CIRCUIT BREAKER MAINTENANCE - 15YR | DirectLink | Bungalora
QLD-ET-WI-PM180-0140-BLA2 | CIRCUIT BREAKER MAINTENANCE - 15YR | Bungalora - System 2 | Bungalora
QLD-ET-WI-PM180-0140-BLA3 | CIRCUIT BREAKER MAINTENANCE - 15YR | Bungalora - System 3 | Bungalora System 1 - AC Switchyard Area WT1
QLD-ET-WI-PM180-0140-MUL1 | CIRCUIT BREAKER MAINTENANCE - 15YR | Mullumbimby - System 1 | Bungalora System 2 - AC Switchyard Area WT1
QLD-ET-WI-PM180-0140-MUL2 | CIRCUIT BREAKER MAINTENANCE - 15YR | Mullumbimby - System 2 | Bungalora System 2 - AC Switchyard Area WT1
QLD-ET-WI-PM180-0140-MUL3 | CIRCUIT BREAKER MAINTENANCE - 15YR | Mullumbimby - System 3 | Bungalora System 2 - AC Switchyard Area WT1

## 0142
Summary | INSULATING WALL BUSHING MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 1280.9356 | 0 | 0 | 1280.9356 | 0 | 0
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 1453.8023 | 0 | 0 | 1453.8023 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | not sighted
Insulated Wall Bushing
| U.X1 | 18
Number of Components to be serviced |  | 18
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM036-0142 | Every 3 year(s) |  |  | 0 | 0 | 1 | 0 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0.055556 | Hours per wall bushing
APA Supervision (Hrs) | 0.47685 | Hours per wall bushing
APA Material Costs | 0 | Gas capture and replacement is reportedly not part of maintenance (is required for repairs)
Contractor Costs
Contractor Labour (Hrs) | 1 | Hours per wall bushing (from the ABB recommended maintenance)
Contractor Hourly Rate | 75
Contractor Labour | 75
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 66.082 | 1189.476 | 1280.9356 | 0 | 0 | 1280.9356 | 0 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 75 | 1350 | 1453.8023 | 0 | 0 | 1453.8023 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM036-0142 | Every 3 year(s)
QLD-ET-WI-PM036-0142 | INSULATING WALL BUSHING MAINTENANCE | Bungalora System 1 - Inverter / Rectifier Area | Bungalora System 1 - Wall Bushing
QLD-ET-WI-PM036-0142 | INSULATING WALL BUSHING MAINTENANCE | Bungalora System 2 - Inverter / Rectifier Area | Bungalora System 2 - Wall Bushing
QLD-ET-WI-PM036-0142 | INSULATING WALL BUSHING MAINTENANCE | Bungalora System 3 - Inverter / Rectifier Area | Bungalora System 3 - Wall Bushing
QLD-ET-WI-PM036-0142 | INSULATING WALL BUSHING MAINTENANCE | Mullumbimby System 1 - Inverter / Rectifier Area | Mullumbimby System 1 - Wall Bushing
QLD-ET-WI-PM036-0142 | INSULATING WALL BUSHING MAINTENANCE | Mullumbimby System 2 - Inverter / Rectifier Area | Mullumbimby System 2 - Wall Bushing
QLD-ET-WI-PM036-0142 | INSULATING WALL BUSHING MAINTENANCE | Mullumbimby System 3 - Inverter / Rectifier Area | Mullumbimby System 3 - Wall Bushing

## 0150
Summary | PLC FILTER TUNING UNIT MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 1732.9993 | 1732.9993 | 0 | 0 | 0 | 0
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 461.25 | 461.25 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | Not sighted (OEM maintenance sheet)
AC Tuning Circuit
| WT.Z1 | 12
Number of Components to be serviced |  | 12
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM060-0150 | Every 5 year(s) |  |  | 1 | 0 | 0 | 0 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0.5 | Hours per tuning cct
APA Supervision (Hrs) | 0.71528 | Hours per tuning cct
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 0.5 | From the ABB recommended maintenance
Contractor Hourly Rate | 75 | OEM instruction requires connection of a meter to make necessary measurements
Contractor Labour | 37.5
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 140.8942 | 1690.731 | 1732.9993 | 1732.9993 | 0 | 0 | 0 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 37.5 | 450 | 461.25 | 461.25 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM060-0150 | Every 5 year(s)
QLD-ET-WI-PM060-0150-BLA | PLC FILTER TURNING UNIT MAINTENANCE | Bungalora | Bungalora - 110kV Overhead Bus
QLD-ET-WI-PM060-0150-MUL | PLC FILTER TURNING UNIT MAINTENANCE | Mullumbimby | Mullumbimby - 132kV Overhead Bus

## 0160 (1)
Summary | DISCONNECTOR & EARTH SWITCH MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 1312.9589 | 0 | 0 | 0 | 1312.9589 | 0
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 1986.8632 | 0 | 0 | 0 | 1986.8632 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-45
DC Disconnector
| WP1.Q11 | 6
| WP2.Q11 | 6
DC Earth Switch
| WP1.Q21 | 6
| WP2.Q21 | 6
Number of Components to be serviced |  | 24
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM072-0160 | Every 6 year(s) |  |  | 0 | 0 | 0 | 1 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0.041667 | Hours per switch
APA Supervision (Hrs) | 0.35764 | Hours per switch
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 1 | Hours per switch (from the ABB recommended maintenance - however this suggests every 3 years)
Contractor Hourly Rate | 75
Contractor Labour | 75
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 49.5615 | 1189.476 | 1312.9589 | 0 | 0 | 0 | 1312.9589 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 75 | 1800 | 1986.8632 | 0 | 0 | 0 | 1986.8632 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM072-0160 | Every 6 year(s)
QLD-ET-WI-PM072-0160-BLA1 | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | Bungalora | Bungalora - System 1
QLD-ET-WI-PM072-0160-BLA2 | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | Bungalora | Bungalora - System 2
QLD-ET-WI-PM072-0160-BLA3 | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | Bungalora | Bungalora - System 3
QLD-ET-WI-PM072-0160-MUL1 | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | Mullumbimby | Mullumbimby - System 1
QLD-ET-WI-PM072-0160-MUL2 | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | Mullumbimby | Mullumbimby - System 2
QLD-ET-WI-PM072-0160-MUL3 | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | Mullumbimby | Mullumbimby - System 3

## 0160 (2)
Summary | MOTORISED OPERATING MECHANISM MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 1312.9589 | 0 | 0 | 0 | 1312.9589 | 0
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 1986.8632 | 0 | 0 | 0 | 1986.8632 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-45
DC Disconnector
| WP1.Q11 | 6
| WP2.Q11 | 6
DC Earth Switch
| WP1.Q21 | 6
| WP2.Q21 | 6
Number of Components to be serviced |  | 24
Discussion
This item only considers maintenance of the motors
This worksheet does not make a material contribution to the total O&M Direct Cost
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM072-0160 | Every 6 year(s) |  |  | 0 | 0 | 0 | 1 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0.041667 | Hours per switch
APA Supervision (Hrs) | 0.35764 | Hours per switch
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 1 | Hours per switch (from ABB recommended maintenance - although this suggests every 3 years)
Contractor Hourly Rate | 75
Contractor Labour | 75
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 49.5615 | 1189.476 | 1312.9589 | 0 | 0 | 0 | 1312.9589 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 75 | 1800 | 1986.8632 | 0 | 0 | 0 | 1986.8632 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 0180
Summary | MANUAL OPERATING MECHANISM MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction | DL-WI-45
AC Disconnector
| WT.Q11 | 1
| WT1.Q11 | 6
AC Earth Switch
| WA.Z1.Q21 | 18
Number of Components to be serviced |  | 25
Discussion
This maintenance is not scheduled during this AER period
It is included to avoid confusion with Work Instruction 45 which lists this maintenance
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
QLD-ET-WI-PM120-0180 | Every 10 year(s) |  |  | 0 | 0 | 0 | 0 | 0
APA Costs
APA Maintenance Staff (Hrs) | 0.04 | Hours per mechanism
APA Supervision (Hrs) | 0.34333 | Hours per mechanism
APA Material Costs | 0
Contractor Costs
Contractor Labour (Hrs) | 4 | Hours per mechanism (from the ABB recommended maintenance)
Contractor Hourly Rate | 75
Contractor Labour | 300
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 47.579 | 1189.476 | 0 | 0 | 0 | 0 | 0 | 0
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 300 | 7500 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Maintenance
PM ID | PM Name | Parent Location
QLD-ET-WI-PM120-0180 | Every 10 year(s) | Next Due: | 2020-10-01
Bungalora System 1 - Main Station Incoming AC Disconnector | QLD-ET-WI-PM120-0180 | HAND OPERATED DISCONNECTOR & EARTH SWITCH MAINT | Bungalora - 110kV Overhead Bus
Bungalora - System 1 | QLD-ET-WI-PM120-0180-BLA1 | HAND OPERATED DISCONNECTOR & EARTH SWITCH MAINT | Bungalora
Bungalora - System 2 | QLD-ET-WI-PM120-0180-BLA2 | HAND OPERATED DISCONNECTOR & EARTH SWTICH MAINT | Bungalora
Bungalora - System 3 | QLD-ET-WI-PM120-0180-BLA3 | HAND OPERATED DISCONNECTOR & EARTH SWITCH MAINT | Bungalora
Mullumbimby - System 1 | QLD-ET-WI-PM120-0180-MUL1 | HAND OPERATED DISCONNECTOR & EARTH SWITCH MAINT | Mullumbimby
Mullumbimby - System 2 | QLD-ET-WI-PM120-0180-MUL2 | HAND OPERATED DISCONNECTOR & EARTH SWITCH MAINT | Mullumbimby
Mullumbimby - System 3 | QLD-ET-WI-PM120-0180-MUL3 | HAND OPERATED DISCONNECTOR & EARTH SWTICH MAINT | Mullumbimby

## Prestart Inspection
Summary | PRESTART INSPECTIONS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 37302.4515 | 7096.6743 | 7274.0912 | 7455.9434 | 7642.342 | 7833.4006
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
After the Mullumbimby fire an inspection of the phase reactors has been added
The inspection looks for moisture on the phase reactors
The inspection is also required to check for vermin in and around the site
The inspection must check the phase reactors at BOTH ends of the link
This worksheet does not make a material contribution to the total O&M Direct Cost
Background to estimated number of inspections per year
One for each cable fault | 11.5 | Each cable fault can actually require more than one re-start
Two scheduled maintenance periods | 6 | All converter buildings must be inspected
Additional outages to undertake maintenance found during scheduled outage | 6
Two for IGBT replacement (not done during scheduled maintenance) | 2
Starts per year | 25.5 | Per PAIR of converter buildings (each end of the link being started must be inspected)
Times |  |  | Anecdotal values discussed with Operations Manager
Prestart inspection of each phase reactor | 10 | minutes | Per phase reactor
Inspection of the converter building for vermin etc | 15 | minutes | Per building
Travel to the other site (if other technician not available) | 90 | minutes | One round trip assumed to be required 25% of the time
Switching another 30 minutes per site | 30 | minutes | Original switching time (applied to each of the 2 systems)
Detailed inspection of the phase reactors in the new Mullumbimby station is not required however vermin inspection of the converter building will still be required
Average times (per start)
Inspection of phase reactors | 0.83333 | hours (required in 5 out of 6 buildings)
Vermin inspection | 0.5 | hours
Travel | 0.375 | hours
Switching | 1 | hours
Total APA Technician Time | 2.7083 | hours/prestart inspection
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 271.5131 | 6923.5847 | 37302.4515 | 7096.6743 | 7274.0912 | 7455.9434 | 7642.342 | 7833.4006
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Personnel taking the photographs need to allocate time to take and UPLOAD

## Cable Repairs
Summary | CABLE REPAIRS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 609704.8203 | 115994.4281 | 118894.2888 | 121866.6461 | 124913.3122 | 128036.145
APA Material Costs |  |  | 31443.3568 | 5922.5 | 6100.175 | 6283.1803 | 6471.6757 | 6665.8259
Contractor Labour |  |  | 1204549.0328 | 229161.6723 | 234890.7141 | 240762.982 | 246782.0565 | 252951.6079
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Repairs Per Year | 11.5
Data
Number of Cable Faults | 138 |  | Anecdotal: Provided by Reliability Engineer
Years | 12 |  | Deducting time that the cables have been non-operational
Average number of cable faults | 11.5 | Per Year
Discussion
Mullumbimby and Bungalora are connected by six HV DC cables
The cables are in pairs, with one pair connecting to one (of the three) converter station(s)
The cable easement is approximately 59km long
With six cables each 59km long indicates that Directlink contains 354km of HV DC cable
A cable fault in one cable will shut down the connected converter stations
The cables are laid side by side either in Galvanised Steel Trough (above ground) or buried (underground)
Roughly 50% of the cable is in GST with the remaining 50% buried underground
For safety reasons it is necessary to shut down the other converter stations
Modelling Assumption
Percentage of faults which are underground to in GST | 50% |  |  |  | Anecdotal - email from Operations Manager 7/5/14
APA staff time per fault | Source: Anecdotally discussed with the Works Scheduler
APA Staff Time
APA Staff Member on call including remote logon to verify | 0.5
Notification
Notify management that there is an issue | 1 |  |  |  | APA staff member on call is required to dial-in to validate the fault
Notify authorities that capability is reduced (1 system out) | 1
Notify APA staff and maintenance contractors | 1
Isolation
Switch out the system with the cable fault | 4
Locate the fault
Connect Thumper and create "hole" | 2 |  |  |  | The thumper deliberately enlarges the original fault to make it easier to find
APA personnel sent to approximate fault location (2 staff) | 8 |  |  |  | Average time, since could be located in remote parts of the cable route
Locate the actual fault location (2 staff) | 8 |  |  |  | Average time. If takes more than 4 hours then more staff are called into the search
Validate the fault location | 2 | 4 |  |  | Dig bore hole (adjusted for % underground)
Disconnect thumper from cable | 1
Coordinate Repairs |  |  |  |  | The start date of the repair is driven by the availability of required contractors
APA staff member assigned fulltime to manage the repair | 24 |  |  |  | Typically three days but can be longer
Expose the Cable
Find the fault in the cable | 2 |  |  |  | Even after thumping only a small hole less than 10mm in diameter
Remove the cover (only if in GST) | 1 | 2 |  |  | (adjusted for % underground)
Qualified supervisor of the excavator (only underground) | 2 | 4 |  |  | (adjusted for % underground)
Repair
Estimate length of cable to be replaced | 4 |  |  |  | Based on history of repairs in that area (more replaced if other joints are nearby)
Locate suitable length of cable | 2 |  |  |  | Several drums of different lengths so will pick most appropriate to cut required length off
Additional APA staff required during the repair | 8
Erect tent over the two joints (and removal) | 2
Test the repair
Use HI-POT to test the cable after the repair | 4
Reenergisation
Inspect the reactors to ensure dry before reenergisation | 2 |  |  |  | Pre-inspection of the three reactors before energisation (at both ends of the link)
Switch system back on (including notifying AEMO etc) | 4
Post Repair
Update the cable history to show latest repair | 2
APA Technical Staff hours | 85.5 | hours |  |  | Technician Hours
APA Supervisor Staff hours | 10 | hours |  |  | Updating fault location details, ordering replacement spares, paying invoices
Material Costs Per Fault
Discussion
The cable is cut in two places and the faulty section of cable is removed
As such each cable repair requires the installation of TWO cable joints
The cable must be bought in drums with ABB setting a large minimum order quantity
If the material costs are $0 then it is likely that Capitalise is set to TRUE on the Modelling Assumptions worksheet
APA material costs
Cable Joint | 0 |  |  |  | Two required for each repair
HVDC Cable | 0 | per metre
Typical length of repair | 100 | metres |  |  | Discussions indicate that 100m lengths are not uncommon
Barrier Tape / conduit | 10 | per metre |  |  | Only required for underground faults
Total material cost per repair | 500
Contractor Costs Per Fault
Discussion
Costs include the Specialist Cable Jointer, Electrical Contractor and Heavy lift contractor (to get the cable to the site and install)
No digging is required to access the cables when located in GST (above ground)
Digging is required when the cable is located underground (either in conduit or buried directly in the soil)
There are also concerns about public safety once the trench has been exposed
Security Fencing and security guards are required
Fault above ground | 9180.802 |  |  |  | Converted to reference year of 2014
Fault underground | 29701.3481 |  |  |  | Average of the two options shown below converted to reference year of 2014
| Per Repair in Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 9840.4605 | 113165.2958 | 609704.8203 | 115994.4281 | 118894.2888 | 121866.6461 | 124913.3122 | 128036.145
APA Material Costs | 500 | 5750 | 31443.3568 | 5922.5 | 6100.175 | 6283.1803 | 6471.6757 | 6665.8259
Contractor Labour | 19441.0751 | 223572.3632 | 1204549.0328 | 229161.6723 | 234890.7141 | 240762.982 | 246782.0565 | 252951.6079
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of Cable Repairs | Anecdotal: Analysis provided by the Operations Manager 7/5/14
The following costs are used in the modelling
Treated as anecdotal since invoices were not provided
Fault in Conduit
| Inv. No. |  | $
Civex | 11231 |  | 8182.5
Thearle | 52781 |  | 7704.15
NKT | 4616 |  | 4880
JD & LF Reeves | 1208 |  | 6902.5
27669.15
Fault Buried
| Inv. No. |  | $
Thearle | 47969 |  | 25404.7 | includes excavation costs
NKT | 4616 |  | 4880
30284.7
Fault in Transition / GST
| Inv. No. |  | $
Thearle | 46538 |  | 4076.88 |  | Jan 2013.
NKT | 4616 |  | 4880
8956.88

## IGBT Repairs
Summary | IGBT VALVE REPAIRS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 78795.6497 | 14990.625 | 15365.3906 | 15749.5254 | 16143.2635 | 16546.8451
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | Yes
Work Instruction |  | Defines all the required steps
IGBT Valves
| U.Vx.V1 | 18
| U.Vx.V2 | 18
Number of Components to be serviced |  | 36
Each "Valve" consists of 8 stacks of individual IGBTs
7 stacks of 20 IGBTs
1 stack of 8 IGBTs
Total IGBTs | 148
Modelling
Number of IGBT replacements | 39 | Per Year
Basis for figures
195 IGBTs Replaced over the last 5 years: |  | Source: Analysis from Noel Powell received 27/3/14
2009 | 35
2010 | 44
2011 | 38
2012 | 35
2013 | 43
Average failures per year | 39
Average Failure rate | 0.732%
Modelling Assumptions
Assumed number of unscheduled IGBT replacements | 2 | per year due to converter station trip when more than 4 IGBTs fail in a single valve
APA Costs
APA Maintenance Staff (Hrs) | 0.5 | Hours per unscheduled IGBT repair
APA Supervision (Hrs) | 4.2917 | Hours per unscheduled IGBT repair (raise wo, raise po, close wo, enter po on system + capturing details)
APA Material Costs | 0 | Average IGBT replacement cost per year
Contractor Costs
Contractor Labour (Hrs) | 5 | Hours for each IGBT (involves removal of water pipes, fibre optic, shields AND commissioning)
Contractor Hourly Rate | 75
Contractor Labour | 375
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 594.738 | 1189.476 | 6408.5835 | 1219.2129 | 1249.6932 | 1280.9356 | 1312.9589 | 1345.7829
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 375 | 14625 | 78795.6497 | 14990.625 | 15365.3906 | 15749.5254 | 16143.2635 | 16546.8451
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Material Costs
Modelled Cost per IGBT | 0 | If this value is $0 then check the Modelling Assumptions sheet for CAPITALISE
Annual Cost of replacement IGBTs | 0

## Control System Repairs
Summary | CONTROL SYSTEM REPAIRS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 179130.3932 | 34078.995 | 34930.9699 | 35804.2441 | 36699.3502 | 37616.834
APA Material Costs |  |  | 19139.4346 | 3605 | 3713.15 | 3824.5445 | 3939.2808 | 4057.4593
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted
Number of Control Systems |  | 10 | System A and System B for each of the 6 buildings
Incidents (alarms on the Alarm Screen) |  | 5 | Anecdotal: "Two repairs on each system per year" (verbal estimate provided by Operations Manager)
Number of repairs |  | 50 | per year
Discussion
Modelling has assumed that the new Mullumbimby converter will have a new control system
This new control system will not have as many faults as the existing controllers
APA Costs
APA Maintenance Staff (Hrs) | 6 | Average hours per repair (to identify the faulty card, rectify and test) - many faster, but some are MUCH longer…
APA Supervision (Hrs) | 0.5 | Order new cards and provide assistance during tricky diagnostics
APA Material Costs | 70 | Cards
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 0
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 664.956 | 33247.8 | 179130.3932 | 34078.995 | 34930.9699 | 35804.2441 | 36699.3502 | 37616.834
APA Material Costs | 70 | 3500 | 19139.4346 | 3605 | 3713.15 | 3824.5445 | 3939.2808 | 4057.4593
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fault Identification and Rectification
The operator notes that the Control system is not in the correct state
Identify the fault card
Sometimes a card reset will fix the problem
Card Replacements are more complex
Each card has unique data programmed into it (in EPROM) to identify its location
When replacing a card the correct software must be loaded and specific programming information identifying the location of the card
It is estimated that just reprogramming a card take around 2 hours
Cost of the replacement cards
Relay Cards | 700 | The most common failure
Power supply | 1000
CPU cards | 2000
PCI Cards | 14000
Assumed percentage of cards that are faulty and must be replaced | 10% | Sometimes reprogramming the cards is sufficient to fix the problem
Cost of cards | 700
Annual cost of card replacement | 3500
Discussion
The control system comprises three main parts
Personal computer running the operating system and all the interface cards
OEM designed interface cards plugged into the computer connected to external racks of equipment
OEM designed external racks of equipment are connected to the various CTs and VTs
Computer combines all the readings from the various Current Transformers and Voltage Transformers throughout each system
The PC is not an industrial design (it is standard commercial grade)
1990's designed computer based on Pentium computer chip with superseded PCI interface slots (for the OEM cards)
The computer is running a version of Microsoft Windows which is no longer supported (An embedded version of NT4)
A suitable computer motherboard is no longer available (even from industrial suppliers)
APA have located a number of spares from second hand shops which are then used as replacements
The PCI interface cards each contain a number of processors
These cards generate a large amount of heat
The PCI cards are plugged into the PC motherboard so the heat generated by the cards can not be isolated from the PC
It is not possible to replace one of the components without an upgrade to the whole system
OEM proprietary - PCI cards
MUST have air-conditioners to keep this working
MUST have UPS to ensure stable power supply
Even with these precautions there are a considerable number of repairs
OEM is able to support all but the computer motherboard

## Building ac
Summary | BUILDING AIR-CONDITIONERS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 41692.2572 | 7931.8211 | 8130.1166 | 8333.3695 | 8541.7037 | 8755.2463
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 83170.6559 | 15822.9562 | 16218.5301 | 16623.9934 | 17039.5932 | 17465.583
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | N/A
Discussion
The Air conditioners are used to protect the "fragile" Control Systems
Refer to Control System Repairs
Air Conditioner Maintenance
Number of maintenance contracts |  | 1 | Contracted Rate
Invoices
Nov 12 - Feb 14 | 20080.69
Average monthly cost in 2013$ | 1255.0431
Average monthly cost in 2014$ | 1286.4192
Number of Air-conditioners |  | 6 | per building
Buildings |  | 6
Total number of air-conditioners |  | 36
Alternate Maintenance Strategy
Rather than maintain a/c aim to replace (before they fail)
Lifetime of air-conditioners |  | 3 | Typically 2 to 3 years (domestic units not suited to running 24 x 7)
Cost of air-conditioners |  | 2500
Annual Cost to replace |  | 30000 | per year (i.e. much more expensive that current strategy so can not be recommended)
Modelling
APA Costs
APA Maintenance Staff (Hrs) | 12 | Hours per year - to let the contractor into the site each month
APA Supervision (Hrs) | 51.5 | Hours per year - To open and close WO and enter the monthly invoices onto the system
APA Material Costs | 0
Discount for O&M Supervisor time | 50% | since relationship with contractor is well established
Contractor Costs
Contractor Labour (Hrs)
Contractor Hourly Rate
Contractor Labour | 1286.4192 | per month | Source: Invoices
Contractor Materials | 0
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 7738.362 | 7738.362 | 41692.2572 | 7931.8211 | 8130.1166 | 8333.3695 | 8541.7037 | 8755.2463
APA Material Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour | 1286.4192 | 15437.0304 | 83170.6559 | 15822.9562 | 16218.5301 | 16623.9934 | 17039.5932 | 17465.583
Contractor Materials | Not Used | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Electricity Costs
Summary | ELECTRICITY COSTS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 8204.4455 | 1560.87 | 1599.8918 | 1639.889 | 1680.8863 | 1722.9084
APA Material Costs |  |  | 3461765.9371 | 634282.3329 | 668365.531 | 688416.4969 | 724483.5351 | 746218.0412
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
It is necessary to estimate the current cost of electricity for the Reference Year since the HVDC link has not been fully operational since August 2012
Mullumbimby Converter Fire occurred in August 2012
Directlink continued to operate (with two systems) until July 2013
It was turned off in August 2013 for repairs
It resumed operation with two converters in Jan 2014 (when another cable fault occurred)
Detailed Analysis (period of normal operation)
The following usage data comes from the 13 electricity invoices for Bungalora and Mullumbimby for the period immediately before the Mullumbimby fire
This period (July 2011 to July 2012) is considered to represent typical electricity use when three converter stations are available
Use in September and April would be expected to be lower due to Annual Maintenance
It was considered desirable to include a full 12 months of electricity use in this analysis
The choice was between July 2011 and July 2012
Both months show below average use however July 2011 does not reflect normal operation
July 2011 had multiple outages for cable faults and IGBT faults.
System 1 was offline for one day on 14/7/14 and then from 18/7/14 till early August.
System 2 was offline until 22/7/14, then again on 29/7/13 for one day.
System 3 was offline until 15/7/14 and then from 22/7/14 till early August.
For most of the month only one system was operational and therefore the analysis has used July 2012
Electricity Use and Demand (July 2011 to July 2012)
Mullumbimby
Date |  |  |  | 2011-07-01 | 2011-08-01 | 2011-09-01 | 2011-10-01 | 2011-11-01 | 2011-12-01 | 2012-01-01 | 2012-02-01 | 2012-03-01 | 2012-04-01 | 2012-05-01 | 2012-06-01 | 2012-07-01
Peak |  |  |  | 11831 | 19842 | 18694 | 23321 | 26738 | 21356 | 20106 | 22651 | 24466 | 14251 | 22859 | 19671 | 15164
Shoulder |  |  |  | 25586 | 40634 | 37513 | 47437 | 54005 | 43650 | 41382 | 46793 | 51780 | 29522 | 47771 | 40860 | 31865
Off Peak |  |  |  | 52222 | 77888 | 70658 | 104517 | 98233 | 96137 | 85035 | 84952 | 93851 | 82181 | 84019 | 84930 | 64022
Peak Demand |  |  |  | 207 | 287 | 287 | 337 | 388 | 339 | 392 | 378 | 390 | 260 | 312 | 272 | 216.3
Shoulder Demand |  |  |  | 234 | 331 | 307 | 364 | 497 | 351 | 403 | 409 | 422 | 286 | 323 | 311 | 244.8
Off Peak Demand |  |  |  | 235 | 335 | 323 | 369 | 471 | 373 | 366 | 376 | 420 | 284 | 330 | 309 | 243.2
Energy Charges |  |  |  | 5741.3168 | 8941.0349 | 8219.9332 | 11156.4731 | 11638.3679 | 10255.5915 | 9394.1715 | 10033.8987 | 11046.7346 | 7811.9055 | 10081.4454 | 9311.2486 | 7132.3002 | 33.79%
Network Charges (kWh) |  |  |  | 3243.2455 | 5058.3949 | 4652.5391 | 6295.4875 | 6591.4193 | 5786.9962 | 5307.645 | 5682.143 | 6254.9868 | 4388.1826 | 5712.0371 | 5259.3591 | 4030.9003
Network Charges (kW) |  |  |  | 7398.4761 | 10387.3488 | 9987.408 | 11744.8409 | 14845.2357 | 11594.0076 | 13140.3657 | 13054.9069 | 13579.1852 | 9136.2534 | 10624.4945 | 9775.0471 | 7727.1028
Other Charges |  |  |  | 932.5145 | 1439.4007 | 1319.7766 | 1823.3858 | 1861.8873 | 1676.3706 | 1524.2788 | 1606.1816 | 1769.5191 | 1310.2995 | 1608.8135 | 1513.2308 | 1155.2636
Access & Metering |  |  |  | 516.9937 | 516.9937 | 503.381 | 516.9937 | 503.381 | 516.9937 | 516.9937 | 489.7683 | 516.9937 | 503.381 | 516.9937 | 503.381 | 516.9937
Total |  |  |  | 17832.5466 | 26343.173 | 24683.0379 | 31537.181 | 35440.2912 | 29829.9596 | 29883.4547 | 30866.8985 | 33167.4194 | 23150.0219 | 28543.7842 | 26362.2666 | 20562.5606 | 340370.0487
Bungalora
Date |  |  |  | 2011-07-01 | 2011-08-01 | 2011-09-01 | 2011-10-01 | 2011-11-01 | 2011-12-01 | 2012-01-01 | 2012-02-01 | 2012-03-01 | 2012-04-01 | 2012-05-01 | 2012-06-01 | 2012-07-01
Peak |  |  |  | 11270 | 19622 | 18457 | 22891 | 26095 | 21180 | 19683 | 22284 | 23978 | 14220 | 22859 | 19591 | 15382.4
Shoulder |  |  |  | 24696 | 39878 | 36734 | 46216 | 52357 | 42917 | 40514 | 45705 | 50578 | 29387 | 47771 | 40621.76 | 32635.04
Off Peak |  |  |  | 51152 | 77538 | 70721 | 104215 | 97858 | 95322 | 85781 | 84587 | 93086 | 82162 | 84019 | 85065.84 | 64427.84
Peak Demand |  |  |  | 217 | 293 | 283 | 332 | 391 | 326 | 372 | 378 | 391 | 289 | 312 | 282 | 229.64
Shoulder Demand |  |  |  | 243 | 299 | 307 | 359 | 462 | 354 | 374 | 396 | 409 | 297 | 323 | 311 | 264.15
Off Peak Demand |  |  |  | 258 | 364 | 350 | 382 | 453 | 370 | 376 | 378 | 419 | 297 | 330 | 325 | 263.8
Energy Charges |  |  |  | 5825.5091 | 9252.3924 | 8517.0342 | 11515.6107 | 11961.6057 | 10608.0771 | 9759.3377 | 10354.3614 | 11372.3478 | 8157.6777 | 10547.1631 | 9721.8113 | 7567.5414 | 34.65%
Network Charges (kWh) |  |  |  | 3144.3791 | 5002.3079 | 4606.1908 | 6208.7812 | 6472.3431 | 5720.9845 | 5267.5101 | 5602.9456 | 6153.3914 | 4379.7848 | 5712.0371 | 5248.112 | 4089.1494
Network Charges (kW) |  |  |  | 7761.2416 | 10097.644 | 10019.879 | 11639.7265 | 14305.1449 | 11434.202 | 12441.7478 | 12867.327 | 13396.3058 | 9778.894 | 10624.4945 | 9979.2893 | 8286.4
Other Charges |  |  |  | 906.2886 | 1425.6063 | 1309.8625 | 1803.0688 | 1834.1529 | 1658.4359 | 1518.6091 | 1587.2481 | 1743.9797 | 1308.3749 | 1608.8135 | 1511.3333 | 1169.7682
Access & Metering |  |  |  | 611.9937 | 611.9937 | 598.381 | 611.9937 | 598.381 | 611.9937 | 611.9937 | 584.7683 | 611.9937 | 598.381 | 611.9937 | 598.381 | 611.9937
Total |  |  |  | 18249.412 | 26389.9443 | 25051.3476 | 31779.1809 | 35171.6277 | 30033.6931 | 29599.1984 | 30996.6504 | 33278.0184 | 24223.1124 | 29104.502 | 27058.9269 | 21724.8528 | 344411.0549
Assumed Cost of Electricity Reference Year 2014/15 | bar: 2011-07-01 to 2011-10-01
| Mullumbimby | Bungalora
Energy Charges | 2014/15 | 2014/15
Peak | 8.095 | 8.469 | c/kWh
Shoulder | 8.095 | 8.469 | c/kWh
Off Peak | 5.194 | 5.4339 | c/kWh
Network Charges
Peak | 4.7365 | 4.7365 | c/kWh
Shoulder | 4.7365 | 4.7365 | c/kWh
Off Peak | 2.8168 | 2.8168 | c/kWh
Peak Demand | 14.9551 | 14.9551 | $/kVA
Shoulder Demand | 14.9551 | 14.9551 | $/kVA
Off Peak Demand | 3.4182 | 3.4182 | $/kVA
Other Charges
ESC | 0.1473 | 0.1473 | c/kWh
LREC | 0.4812 | 0.4812 | c/kWh
SREC | 0.335 | 0.335 | c/kWh
AEMO Charge | 0.0378 | 0.0378 | c/kWh
AEMO Ancillary | 0.039 | 0.039 | c/kWh (Average value for most recent 12 months)
Access Charge | 13.6127 | 13.6127 | $ per day
VIP Metering | 95 | 190 | per calendar month
Estimated cost of electricity in Reference Year
Mullumbimby | 340370.0487
Bungalora | 344411.0549
Total | 684781.1036 |  | 13168.8674 | 2011-07-01: per week
APA supervisor hours
To enter the invoices into the system | 1 | hours per month
Contract to Procure Electricity for ALL APA assets | bar: 2011-07-01 to 2011-11-01
DJV are negotiating a lower rate for their energy use | bar: 2011-07-01 to 2011-11-01
Contract covers period July 14 to June 16 | 0% | SUGGESTED saving | bar: 2011-07-01 to 2011-11-01
Energy Charges as Percentage of total bill | 34.22% | Average of Mullumbimby and Bungalora | bar: 2011-07-01 to 2011-11-01
|  |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Cost without contract |  |  |  | 2011-07-01: 705324.5367; 2011-08-01: 726484.2728; 2011-09-01: 748278.801; 2011-10-01: 770727.165; 2011-11-01: 793848.98
Annual Saving with national procurement contract |  |  |  | 2011-07-01: 71042.2037; 2011-08-01: 58118.7418; 2011-09-01: 59862.3041; 2011-10-01: 46243.6299; 2011-11-01: 47630.9388
Final Cost with saving |  |  |  | 2011-07-01: 634282.3329; 2011-08-01: 668365.531; 2011-09-01: 688416.4969; 2011-10-01: 724483.5351; 2011-11-01: 746218.0412
Anecdotal information from Regulatory Manager 8/4/14 |  | Current | FY14/15 | 2011-07-01: FY15/16
Mullumbimby |  | 54477 | 39730 | 2011-07-01: 38443; 2011-08-01: Subject to new contract negotiation
Bungalora |  | 63908 | 46608 | 2011-07-01: 45098
Average Percentage Saving (on Energy Charges) |  |  | 27.07% | 2011-07-01: 29.43%; 2011-08-01: 23.38%; 2011-09-01: 23.38%; 2011-10-01: 17.53%; 2011-11-01: 17.53%
Average Total Saving (on total bill) |  |  |  | 2011-07-01: 10.07%; 2011-08-01: 8%; 2011-09-01: 8%; 2011-10-01: 6%; 2011-11-01: 6%; 2012-01-01: Using the Commercial Retail Margin from NERA Report for AEMC
Refer to Appendix A of the report for a discussion of these values
Other Calculations
Monthly Average Electricity Use (operational after fire) | Aug-12 to Jul-13
Mullumbimby | 106409.6667 | kWh / month
Bungalora | 113713.3375 | kWh / month
Difference | 6.423%
Assumptions
Have ignored the one month that the new converter at Mullumbimby is not fully operational
Reasoning
Mullumbimby is due to be fully operational in August 2015
Mullumbimby reduction due to loss of 1 converter | 6.423%
One month of lower use at Mullumbimby | 1.667%
Total "Saving" | 0.107% | Ignore likely to be undertaking commissioning tests
Mullumbimby
Directlink Site Electricity Review: Mullumbimby
(Amounts are Ex GST)
Supplier | Period | kWh | Amount
Country Energy | 2011-01-01 | 150197 | 25585.13
Country Energy | 2011-02-01 | 147077 | 24507.69
Country Energy | 2011-03-01 | 163412 | 27303.47
Country Energy | 2011-04-01 | 150718 | 21786.14
Country Energy | 2011-05-01 | 100767 | 17409.63
Country Energy | 2011-06-01 | 75883 | 11406.94
Country Energy | 2011-07-01 | 89639 | 15517.05
Country Energy | 2011-08-01 | 138364 | 22954.44
Country Energy | 2011-09-01 | 126865 | 21521.88
Country Energy | 2011-10-01 | 175275 | 27429.01
Country Energy | 2011-11-01 | 178976 | 30924.98
ERM Power Retail | 2011-12-01 | 161143 | 25100.8
ERM Power Retail | 2012-01-01 | 146523 | 25667.85
ERM Power Retail | 2012-02-01 | 154396 | 26420.44
ERM Power Retail | 2012-03-01 | 170097 | 28392.3
ERM Power Retail | 2012-04-01 | 125954 | 19799.15
ERM Power Retail | 2012-05-01 | 154649 | 24401.04
ERM Power Retail | 2012-06-01 | 145461 | 22503.93
Origin | 2012-07-01 | 111051 | 20886.91
Origin | 2012-08-01 | 84339 | 18188.88
Origin | 2012-09-01 | 93495 | 19640.66
Origin | 2012-10-01 | 132233 | 26852.07
Origin | 2012-11-01 | 95838 | 20915.9
Origin | 2012-12-01 | 143960 | 28823.85
Origin | 2013-01-01 | 141790 | 27746.89
Origin | 2013-02-01 | 101847 | 22676.06
Origin | 2013-03-01 | 81881 | 19597.06
Origin | 2013-04-01 | 79195 | 16498.67
Origin | 2013-05-01 | 110525 | 21660.24
Origin | 2013-06-01 | 105749 | 20141.51
Origin | 2013-07-01 | 106064 | 19620.51
Origin | 2013-08-01 | 68689 | 14873.3
Origin | 2013-09-01 | 39312 | 9788.32
Origin | 2013-10-01 | 36730 | 6747.25
Origin | 2013-11-01 | 32879 | 6353.52
Origin | 2013-12-01 | 29600 | 5642.51
Origin | 2014-01-01 | 41697 | 11976.15
Bungalora
Directlink Site Electricity Review: Bungalora
(Amounts are Ex GST)
Supplier | Period | kWh | Amount
Country Energy | 2011-01-01 | 150760 | 26243.97
Country Energy | 2011-02-01 | 146080 | 24693.02
Country Energy | 2011-03-01 | 161216 | 27129.13
Country Energy | 2011-04-01 | 147970 | 21866.2
Country Energy | 2011-05-01 | 100935 | 17609.64
Country Energy | 2011-06-01 | 75175 | 11775.38
Country Energy | 2011-07-01 | 87118 | 15897.91
Country Energy | 2011-08-01 | 137038 | 23090.57
Country Energy | 2011-09-01 | 125912 | 21918.5
Country Energy | 2011-10-01 | 173322 | 27751.76
Country Energy | 2011-11-01 | 176310 | 30802.94
ERM Power Retail | 2011-12-01 | 159419 | 25287.37
ERM Power Retail | 2012-01-01 | 145978 | 25421.69
ERM Power Retail | 2012-02-01 | 152576 | 26546.54
ERM Power Retail | 2012-03-01 | 167642 | 28512.72
ERM Power Retail | 2012-04-01 | 125769 | 20709.87
ERM Power Retail | 2012-05-01 | 152275 | 24619.47
ERM Power Retail | 2012-06-01 | 145278.6 | 23218.5
Origin | 2012-07-01 | 112445.28 | 22158.07
Origin | 2012-08-01 | 91229.28 | 19632.78
Origin | 2012-09-01 | 103629.12 | 21924.08
Origin | 2012-10-01 | 144200.32 | 31778.89
Origin | 2012-11-01 | 106856.16 | 23534.61
Origin | 2012-12-01 | 143365.44 | 29806.26
Origin | 2013-01-01 | 126525.6 | 29172.88
Origin | 2013-02-01 | 108739.52 | 24885.96
Origin | 2013-03-01 | 91026.88 | 22141.07
Origin | 2013-04-01 | 98363.65 | 20003.77
Origin | 2013-05-01 | 120968.12 | 24338.39
Origin | 2013-06-01 | 114233.47 | 22500.49
Origin | 2013-07-01 | 115422.49 | 21876.48
Origin | 2013-08-01 | 54767.37 | 12607.04
Origin | 2013-09-01 | 47638.55 | 9161.12
Origin | 2013-10-01 | 49757.38 | 10645.09
Origin | 2013-11-01 | 50107.83 | 13080.09
Origin | 2013-12-01 | 44654.42 | 8903.99
Origin | 2014-01-01 | 53737.75 | 13472.71
Origin | 2014-02-01 | 96311.26 | 21344.79

## Control Room Costs
Summary | CONTROL ROOM OPERATIONS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 8204.4455 | 1560.87 | 1599.8918 | 1639.889 | 1680.8863 | 1722.9084
APA Material Costs |  |  | 1002119.0315 | 190650 | 195416.25 | 200301.6562 | 205309.1977 | 210441.9276
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Cost of the control room (APA GasNet) | 186000 | p.a. |  | 190650 | 195416.25 | 200301.6562 | 205309.1977 | 210441.9276
APA GasNet remotely operate the Directlink asset
In 2008 the annual cost was | 140000 | in 2008 (agreement shown below)
Current cost (anecdotal) | 15500 | per month | From the CY14/FY15 OPEX Budget
APA supervisor hours
To enter the invoices into the system | 1 | hours per month
Discussion
Converting initial cost to the Reference Year of 2014 | 162357.0785 | Adjusting for inflation 2008 to 2014
Average annual rate of Inflation on Control Room Costs | 4.849%
Before using APA GasNet Directlink used to use Country Energy
2007-10-01 | 26660.12 | Comprising hourly rate of $5.42 for 4,918.84 hours
2007-11-01 | 18285.34 | Comprising hourly rate of $5.42 for 3,373.68 hours
2007-12-01 | 12912.1 | Comprising hourly rate of $5.42 for 2,382.31 hours
2008-01-01 | 19398.09 | Comprising hourly rate of $5.42 for 3,578.98 hours
Average | 19313.9125 | per month
Converting to Reference Year (Modelled inflation) | 22398.2172 |  | While the APA GasNet cost has increased ahead of inflation it is still lower than the cost of using Country Energy
Converting to Reference Year (APA GasNet inflation rate) | 25659.9123

## Remote Comms
Summary | REMOTE COMMUNICATIONS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 8204.4455 | 1560.87 | 1599.8918 | 1639.889 | 1680.8863 | 1722.9084
APA Material Costs |  |  | 253439.1357 | 48216 | 49421.4 | 50656.935 | 51923.3584 | 53221.4423
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Phone and data connection costs | 3920 | per month |  | Anecdotal: CY14/FY15 OPEX Budget combining phone and data charges
APA supervisor hours
To enter the invoices into the system | 1 | hour(s) per month

## DBYD
Summary | DIAL BEFORE YOU DIG
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 115200.8981 | 21916.6092 | 22464.5245 | 23026.1376 | 23601.791 | 24191.8358
APA Material Costs |  |  | 37732.0282 | 7107 | 7320.21 | 7539.8163 | 7766.0108 | 7998.9911
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Scheduled Outage Required | No
Work Instruction | not sighted | APA staff will attend the site with the person making the call to ensure they do not hit the HVDC cable
Number of requests (pa) |  | 265 | Per annum | Anecdotal value : The actual number of requests 1/3/13 to 1/3/14 provided by Operations Manager
Discussion
Dial Before You Dig is a national service which allows people intending to do earthworks to check that they are not going to encounter underground cables/pipes
Enquires made to Dial Before You Dig which may affect the HVDC cable are passed to APA for checking
If there is a chance that the earthworks will affect the cable APA staff must be in attendance during the earthworks (recent rule change)
APA Costs
| Reference Year | Total in Reference Year | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs | 21382.0578 | 21382.0578 | 115200.8981 | 21916.6092 | 22464.5245 | 23026.1376 | 23601.791 | 24191.8358
APA Material Costs | 6900 | 6900 | 37732.0282 | 7107 | 7320.21 | 7539.8163 | 7766.0108 | 7998.9911
Contractor Labour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Modelling
Not Affected | 152 |  | Actual breakdown of the requests from Operations Manager
Affected | 113
Percentage of Affected requiring a site visit | 20% |  | Estimated value from Operations Manager 20/3/14
Site visit is required if excavation is within 3 meters of the cable |  |  | Now requires APA to issue a permit and supervision of the actual digging
APA Technician Times | Anecdotal discussed with Operations Manager
Not Affected | 10 | minutes to check location on map and confirm OK
Affected - Phone Call to discuss details | 30 | minutes to check on map and call to discuss details
Affected - Phone call and site visit required | 360 | minutes including site visit, travel times, issue permit and supervise the dig
Total Time | 206.1333 | Hours per year
APA Supervisor Times
Not Affected | 0 | minutes to check location on map and confirm OK
Affected - Phone Call to discuss details | 0 | minutes to check on map and call to discuss details
Affected - Discuss site visit with supervisor | 15 | minutes
Total Time | 5.65 | Hours per year
Material Costs
DBYD Annual Fee | 500 | p.a. | From CY14/FY15 OPEX Budget
X-Info Landholder Database | 6400 | p.a. | From CY14/FY15 OPEX Budget
The X-info database should probably be shared with Cable Repairs but is included here

## Site Security
Summary | SITE SECURITY
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 8204.4455 | 1560.87 | 1599.8918 | 1639.889 | 1680.8863 | 1722.9084
APA Material Costs |  |  | 279091.5241 | 53096.2864 | 54423.6935 | 55784.2859 | 57178.893 | 58608.3653
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Security patrols at the two sites | 4316.7712 | per month |  | Average monthly cost of the invoices analysed below
Alarm System Monitoring | 200 |  |  | Monthly cost of alarm monitoring (anecdotal from the CY14/FY15 OPEX Budget)
APA supervisor hours
To enter the invoices into the system | 1 | hours per month
Discussion
Contractor
Sydney Night Patrol Security |  | Invoices shown below
| Date |  | Cost
| 2013-07-01 |  | 1661.89
| 2013-07-01 |  | 1703.44
| 2013-08-01 |  | 4950.4
| 2013-08-01 |  | 1703.44
| 2013-09-01 |  | 2748.2
| 2013-10-01 |  | 1703.44
| 2013-10-01 |  | 2366
| 2013-10-01 |  | 1703.44
| 2013-11-01 |  | 3858.4
| 2013-11-01 |  | 1703.44
| 2013-12-01 |  | 1703.44
| 2014-01-01 |  | 2857.4
| 2014-01-01 |  | 1703.44
| 2014-02-01 |  | 4167.8
| Total |  | 34534.17 | Total (for 8 months)
| Average |  | 4316.7712 | per month
Invoices show that the onsite guard has been removed after the security fencing was upgraded
The CY14/FY14 Opex Budget allocates | 3600 |  | Anecdotal explanation for using the average cost from invoices : "May not include patrols at Mullumbimby" (Operations Manager 7/5/14)

## Training Courses
Summary | TRAINING COURSES FOR CONTRACTORS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 16408.891 | 3121.74 | 3199.7835 | 3279.7781 | 3361.7725 | 3445.8169
APA Material Costs |  |  | 80816.0509 | 15375 | 15759.375 | 16153.3594 | 16557.1934 | 16971.1232
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
To address the unique nature of some of the maintenance requirements APA pay for contractors to receive specialist training
The rural nature of the two converter stations also means that APA need to maintain a strong relationship with their contractors
This does not include training courses that the Contractor should undertake themselves
Training courses (for staff and contractors)
Supervisor hours
Arranging training courses for staff | 8 | hrs/pa |  | 1040.58 | 1066.5945 | 1093.2594 | 1120.5908 | 1148.6056
Arranging training courses for contractors | 16 | hrs/pa |  | 2081.16 | 2133.189 | 2186.5187 | 2241.1817 | 2297.2112
Material Cost of the courses
Cost of the specialist training courses for contractors | 15000 | p.a. |  | 15375 | 15759.375 | 16153.3594 | 16557.1934 | 16971.1232 | Anecdotal: From CY14/FY15 OPEX Budget
Training Matrix
Directlink Training Matrix
Construction Industry Induction | Once | external
APA Induction | Once | internal
Directlink Induction | 18 months | internal
Confined Space Access | 2 years | external
Directlink High Voltage Switching Operator - Initial Course | 3 years | external
High Voltage Switching Operator - Practical Assessment | 3 years | external
Abridged Authorised Recipient Training | 3 years | external
APA Safety System Training | Once | internal
APA Permit Issue Officer Training PIO-B | 3 years | internal
Excavation Training PIO-E | 3 years | internal
Low Voltage Rescue Training | 1 year | internal
First Aid training | 1 year | internal
Resusitation Training | 1 year | internal
Working at Heights | 2 years | external
APA Oracle Finance System Training | Once | internal | N/A for external contractors
APA Maintenance Connection Training | Once | internal | N/A for external contractors
Electrical License Renewal | 5 years | external | N/A for external contractors
Mach2 Control System Training | Once | internal
Circuit Breaker Maintenance Training | Once | external
Elevated Work Platform | 3 years | external
Basic Rigging | 3 years | external
Forklift Training | 3 years | external
Underground Locator Training | 3 years | external

## Onsite Test Equipment
Summary | ONSITE TEST EQUIPMENT MAINTENANCE
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 17065.2466 | 3246.6096 | 3327.7748 | 3410.9692 | 3496.2434 | 3583.6495
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 18857.0785 | 3587.5 | 3677.1875 | 3769.1172 | 3863.3451 | 3959.9287
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
This worksheet does not make a material contribution to the total O&M Direct Cost
Calibration of Equipment
HI-POT, Thumper, 4 x Multi-meter, Low Resistance (micro-ohm meter for IGBT testing),
Labour 4 hours each quarter to bring contractors onsite
APA Technician Time | 16 | hrs p.a. |  | 1644.1164 | 1685.2193 | 1727.3498 | 1770.5335 | 1814.7969
APA Supervisor Time (Pay invoices etc) | 4 | hrs p.a. |  | 520.29 | 533.2972 | 546.6297 | 560.2954 | 574.3028
Contractor Labour Cost for testing | 1500 | p.a. |  | 1537.5 | 1575.9375 | 1615.3359 | 1655.7193 | 1697.1123 | Anecdotal: Discussions with O&M Supervisor
Safety equipment
Hot Sticks, Gloves, Earth Leads, etc
Test done every 6 months - TEX On SITE does this (look for invoices)
APA Technician Time | 8 | hrs p.a. |  | 822.0582 | 842.6097 | 863.6749 | 885.2668 | 907.3984
APA Supervisor Time (Pay invoices etc) | 2 | hrs p.a. |  | 260.145 | 266.6486 | 273.3148 | 280.1477 | 287.1514
Contractor Labour Cost for testing | 2000 | p.a. |  | 2050 | 2101.25 | 2153.7812 | 2207.6258 | 2262.8164 | From CY14/FY15 OPEX Budget

## Incidental Investigations
Summary | INCIDENTAL INVESTIGATIONS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 163248.4229 | 31057.5 | 31833.9375 | 32629.7859 | 33445.5306 | 34281.6689
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
APA Staff Hours
It is recognised that APA staff will be required to provide assistance to these consultants
The time is captured elsewhere in the model
Consultants and Technical Compliance
Contractor Labour Costs | 20300 | p.a. |  | 20807.5 | 21327.6875 | 21860.8797 | 22407.4017 | 22967.5867 | From CY14/FY15 OPEX Budget
Legal Fees
Contractor Labour Cost | 10000 | p.a. |  | 10250 | 10506.25 | 10768.9062 | 11038.1289 | 11314.0821 | From CY14/FY15 OPEX Budget

## Travel
Summary | TRAVEL
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 35552.5971 | 6763.77 | 6932.8642 | 7106.1859 | 7283.8405 | 7465.9365
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 323264.2037 | 61500 | 63037.5 | 64613.4375 | 66228.7734 | 67884.4928
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
Travel and accommodation to the two remote sites for APA staff
APA Staff Hours
Submitting claims for travel expenses | 1 | hour per week (allocated at the rate of the O&M Supervisor since they will have to be approved)
Travel
Contractor Labour Cost | 60000 | p.a. |  | 61500 | 63037.5 | 64613.4375 | 66228.7734 | 67884.4928 | From OPEX Budget

## Other Items
Summary | OTHER COSTS
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 42334.9387 | 8054.0892 | 8255.4414 | 8461.8275 | 8673.3732 | 8890.2075
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 140727.6833 | 26773 | 27442.325 | 28128.3831 | 28831.5927 | 29552.3825
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
An examination of the Corrective Maintenance tasks showed a considerable number of small "building maintenance related" items
An allowance has been included to undertake these minor maintenance tasks
Other costs at the two sites have been included in this worksheet with the costs taken from the CY14/FY15 OPEX budget
APA Staff Hours
Technician Hours spent on simple repairs | 2 | hours per month at each site (looking through the CMs)
Supervisor Hours spent on invoices for simple maintenance | 2 | hour per month (to raise and close WOs and to enter invoices into the financial system)
Vermin Control
Pest control at the two sites | 2000 | per quarter |  | 8200 | 8405 | 8615.125 | 8830.5031 | 9051.2657 | From OPEX Budget
Portaloo Hire (at Mullumbimby)
No onsite toilet | 400 | per month |  | 4920 | 5043 | 5169.075 | 5298.3019 | 5430.7594 | From OPEX Budget
Waste Removal
Monthly service fee | 110 | per month |  | 1353 | 1386.825 | 1421.4956 | 1457.033 | 1493.4588 | From OPEX Budget
General Consumables
Consumables used at the sites
Contractor Labour Cost | 1000 | per month |  | 12300 | 12607.5 | 12922.6875 | 13245.7547 | 13576.8986 | From OPEX Budget

## Operations Manager
Summary | OPERATIONS MANAGER
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 737397.8675 | 151910.6322 | 140995.7934 | 144520.6883 | 148133.7055 | 151837.0481
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
The Operations Manager is required to oversee Directlink, Murraylink and other APA activities
In 2015 they are going to be heavily involved with activities associated with the new Mullumbimby Converter Station
This will include observing acceptance testing of the new station
Refer to Appendix A of the report for a discussion of this role
Modelling Assumptions
Total percentage allocated to Directlink | 50%
During 2015/16 commissioning of the new Mullumbimby Converter station will be occurring
During the month of commissioning the majority of the Operations Manager's time will be spent on Directlink
Modelling estimates 8 weeks of 4 days spent on DL | 243.2 | Hours spend in the first two months of 2015/16 due to new Mullumbimby converter station
Normal allocation would be | 152 | Hours that would have been allocated using above percentage
Additional Hours in 2015/16 | 91.2
Modelling APA Staff Costs (Operations Manager) | Hours
Hours 2015/16 | 965.2
Hours 2016 to 2020 | 874

## Senior Reliability Engineer
Summary | SENIOR RELIABILITY ENGINEER
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 663288.3957 | 126188.5351 | 129343.2485 | 132576.8297 | 135891.2505 | 139288.5317
APA Material Costs |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
The review of Directlink operations found that there was a need for a Senior Reliability Engineer
Refer to Appendix A of the report for a discussion of this role
Modelling APA Staff Costs | Hours
Percentage allocated to Directlink | 50%
Hours | 874 | hours

## Reliability Engineer
Summary | RELIABILITY ENGINEER
Return to Index |  |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  |  | 597557.1132 | 113683.365 | 116525.4491 | 119438.5854 | 122424.55 | 125485.1637
APA Material Costs |  |  | 37796.5494 | 10300 | 10609 | 5463.635 | 5627.544 | 5796.3704
Contractor Labour |  |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
APA have purchased a Failure Reporting, Analysis, and Corrective Action System (FRACAS)
The FRACAS system provides basic analysis tools
APA are working to determine the data that needs to be captured and usefully analysed
Appropriate data will then need to be entered into the system
Once the data is entered the basic analysis tools can be used
The aim is to improve the efficiency of the maintenance
Examples
Cable Faults
There is heuristic evidence that the number of cable faults was increasing
The maintenance strategy (for cable repairs) was changed to replace larger sections of cable in areas with previous problems
Heuristically the changed strategy has stabilised the number of cable faults
If the data was available for analysis using FRACAS this result could be statistically verified
IGBT Failures
There is heuristic evidence that cable faults are causing IGBT failures
If the data was available for analysis using FRACAS this result could be statistically verified
If link between cable faults and IGBT was verified OEM now offers current limiting devices on the DC side which may reduce the number of IGBT faults
There is an initial set up phase for FRACAS
Determine data that should be captured in FRACAS
Enter data
Perform analysis to determine if entered data is sufficient
Design templates and reports
Propose modifications to maintenance strategy
Implement modified maintenance strategy
Test if the modified maintenance strategy is working
Ongoing use of the FRACAS system
Capturing required data
Regular analysis of data
Propose modifications to maintenance strategy
Implement modified maintenance strategy
Test if the modified maintenance strategy is working
Refer to Appendix A of the report for a discussion of this role
Modelling APA Staff Costs | Hours
Percentage allocated to Directlink | 50%
Average hours per annum | 874 | hours
Material Costs
Assumptions
During the initial design phase additional support will have to be obtained from the FRACAS system developer | 10000 | 2015/16 and 2016/17
Yearly ongoing maintenance of the package | 5000 | Thereafter

## Works Planner
Summary | WORKS PLANNER
Return to Index |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  | 513899.1174 | 97767.6939 | 100211.8862 | 102717.1834 | 105285.113 | 107917.2408
APA Material Costs |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
Refer to Appendix A of the report for a discussion of this role
Modelling APA Staff Costs | Hours
Percentage allocated to Directlink | 50%
Hour allocated to Directlink | 874

## Work Practices Specialist
Summary | WORK PRACTICES SPECIALIST
Return to Index |  | Total in AER Period | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
APA Staff Costs |  | 513899.1174 | 97767.6939 | 100211.8862 | 102717.1834 | 105285.113 | 107917.2408
APA Material Costs |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Labour |  | 0 | 0 | 0 | 0 | 0 | 0
Contractor Materials |  | 0 | 0 | 0 | 0 | 0 | 0
Discussion
Refer to Appendix A of the report for a discussion of this role
Modelling APA Staff Costs | Hours
Percentage allocated to Directlink | 50%
Hour allocated to Directlink | 874

## Blank
BLANK
Return to Index
|  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Checks
Number of cells |  | 64 | 64 | 64 | 64 | 64 | 64
|  | 64 | 64 | 64 | 64 | 64 | 64
|  | 64 | 64 | 64 | 64 | 64 | 64
|  | 64 | 64 | 64 | 64 | 64 | 64
Count Cells which are not blank |  | 64 | 64 | 64 | 64 | 64 | 64
|  | 64 | 64 | 64 | 64 | 64 | 64
|  | 64 | 64 | 64 | 64 | 64 | 64
|  | 64 | 64 | 64 | 64 | 64 | 64
SD: Training Matrix and costs
This is a dummy worksheet to mark the end of the items to be summed

## DL PMs
Asset Name | Parent Location | PM Name | PM ID | Frequency Desc | Last Generated Date | Next Scheduled Date | Asset No | Freq
Bungalora System 1 - Fire Alarm System | Bungalora System 1 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1M | QLD-ET-WI-PM001-0000 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0000 | 001
Bungalora System 1 - Fire Alarm System | Bungalora System 1 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 6M | QLD-ET-WI-PM006-0000 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0000 | 006
Bungalora System 1 - Fire Alarm System | Bungalora System 1 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1YR | QLD-ET-WI-PM012-0000 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0000 | 012
Bungalora System 1 - Fire Alarm System | Bungalora System 1 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 2YR | QLD-ET-WI-PM024-0000 | Every 2 year(s) | 27/07/2012 | 27/07/2014 | 0000 | 024
Bungalora System 2 - Fire Alarm System | Bungalora System 2 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1M | QLD-ET-WI-PM001-0000 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0000 | 001
Bungalora System 2 - Fire Alarm System | Bungalora System 2 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 6M | QLD-ET-WI-PM006-0000 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0000 | 006
Bungalora System 2 - Fire Alarm System | Bungalora System 2 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1YR | QLD-ET-WI-PM012-0000 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0000 | 012
Bungalora System 2 - Fire Alarm System | Bungalora System 2 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 2YR | QLD-ET-WI-PM024-0000 | Every 2 year(s) | 27/07/2012 | 27/07/2014 | 0000 | 024
Bungalora System 3 - Fire Alarm System | Bungalora System 3 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1M | QLD-ET-WI-PM001-0000 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0000 | 001
Bungalora System 3 - Fire Alarm System | Bungalora System 3 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 6M | QLD-ET-WI-PM006-0000 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0000 | 006
Bungalora System 3 - Fire Alarm System | Bungalora System 3 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1YR | QLD-ET-WI-PM012-0000 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0000 | 012
Bungalora System 3 - Fire Alarm System | Bungalora System 3 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 2YR | QLD-ET-WI-PM024-0000 | Every 2 year(s) | 27/07/2012 | 27/07/2014 | 0000 | 024
Mullumbimby System 1 - Fire Alarm System | Mullumbimby System 1 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1M | QLD-ET-WI-PM001-0000 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0000 | 001
Mullumbimby System 1 - Fire Alarm System | Mullumbimby System 1 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 6M | QLD-ET-WI-PM006-0000 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0000 | 006
Mullumbimby System 1 - Fire Alarm System | Mullumbimby System 1 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1YR | QLD-ET-WI-PM012-0000 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0000 | 012
Mullumbimby System 1 - Fire Alarm System | Mullumbimby System 1 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 2YR | QLD-ET-WI-PM024-0000 | Every 2 year(s) | 27/07/2012 | 27/07/2014 | 0000 | 024
Mullumbimby System 2 - Fire Alarm System | Mullumbimby System 2 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1M | QLD-ET-WI-PM001-0000 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0000 | 001
Mullumbimby System 2 - Fire Alarm System | Mullumbimby System 2 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 6M | QLD-ET-WI-PM006-0000 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0000 | 006
Mullumbimby System 2 - Fire Alarm System | Mullumbimby System 2 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1YR | QLD-ET-WI-PM012-0000 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0000 | 012
Mullumbimby System 2 - Fire Alarm System | Mullumbimby System 2 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 2YR | QLD-ET-WI-PM024-0000 | Every 2 year(s) | 27/07/2012 | 27/07/2014 | 0000 | 024
Mullumbimby System 3 - Fire Alarm System | Mullumbimby System 3 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1M | QLD-ET-WI-PM001-0000 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0000 | 001
Mullumbimby System 3 - Fire Alarm System | Mullumbimby System 3 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 6M | QLD-ET-WI-PM006-0000 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0000 | 006
Mullumbimby System 3 - Fire Alarm System | Mullumbimby System 3 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 1YR | QLD-ET-WI-PM012-0000 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0000 | 012
Mullumbimby System 3 - Fire Alarm System | Mullumbimby System 3 - Fire System Equipment | FIRE DETECTION & ALARM SYSTEM - 2YR | QLD-ET-WI-PM024-0000 | Every 2 year(s) | 27/07/2012 | 27/07/2014 | 0000 | 024
Bungalora System 1 - Eye Wash Station | Bungalora System 1 - Small Plant & Safety Equipment | CHECK EYE WASH STATION | QLD-ET-WI-PM003-0001 | Every 3 month(s) | 1/09/2013 | 1/12/2013 | 0001 | 003
Mullumbimby System 1 - Eye Wash Station | Mullumbimby System 1 - Small Plant & Safety Equipment | CHECK EYE WASH STATION | QLD-ET-WI-PM003-0001 | Every 3 month(s) | 1/09/2013 | 1/12/2013 | 0001 | 003
Bungalora System 1 - Portable Fire Extinguisher | Bungalora System 1 - Fire System Equipment | PORTABLE FIRE EXTINGUISHER INSPECTION | QLD-ET-WI-PM006-0003 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0003 | 006
Bungalora System 2 - Portable Fire Extinguisher | Bungalora System 2 - Fire System Equipment | PORTABLE FIRE EXTINGUISHER INSPECTION | QLD-ET-WI-PM006-0003 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0003 | 006
Bungalora System 3 - Portable Fire Extinguisher | Bungalora System 3 - Fire System Equipment | PORTABLE FIRE EXTINGUISHER INSPECTION | QLD-ET-WI-PM006-0003 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0003 | 006
Mullumbimby System 1 - Portable Fire Extinguisher | Mullumbimby System 1 - Fire System Equipment | PORTABLE FIRE EXTINGUISHER INSPECTION | QLD-ET-WI-PM006-0003 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0003 | 006
Mullumbimby System 2 - Portable Fire Extinguisher | Mullumbimby System 2 - Fire System Equipment | PORTABLE FIRE EXTINGUISHER INSPECTION | QLD-ET-WI-PM006-0003 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0003 | 006
Mullumbimby System 3 - Portable Fire Extinguisher | Mullumbimby System 3 - Fire System Equipment | PORTABLE FIRE EXTINGUISHER INSPECTION | QLD-ET-WI-PM006-0003 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0003 | 006
Bungalora - System 1 | Bungalora | EMERGENCY LIGHTING MAINTENANCE | QLD-ET-WI-PM006-0004 | Every 6 month(s) | 1/10/2013 | 1/04/2014 | 0004 | 006
Bungalora - System 2 | Bungalora | EMERGENCY LIGHTING MAINTENANCE | QLD-ET-WI-PM006-0004 | Every 6 month(s) | 1/10/2013 | 1/04/2014 | 0004 | 006
Bungalora - System 3 | Bungalora | EMERGENCY LIGHTING MAINTENANCE | QLD-ET-WI-PM006-0004 | Every 6 month(s) | 1/10/2013 | 1/04/2014 | 0004 | 006
Mullumbimby - System 1 | Mullumbimby | EMERGENCY LIGHTING MAINTENANCE | QLD-ET-WI-PM006-0004 | Every 6 month(s) | 1/10/2013 | 1/04/2014 | 0004 | 006
Mullumbimby - System 2 | Mullumbimby | EMERGENCY LIGHTING MAINTENANCE | QLD-ET-WI-PM006-0004 | Every 6 month(s) | 1/10/2013 | 1/04/2014 | 0004 | 006
Mullumbimby - System 3 | Mullumbimby | EMERGENCY LIGHTING MAINTENANCE | QLD-ET-WI-PM006-0004 | Every 6 month(s) | 1/10/2013 | 1/04/2014 | 0004 | 006
Bungalora - System 1 | Bungalora | ENERGISED MAINTENANCE INSPECTION | QLD-ET-WI-PM001-0005 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0005 | 001
Bungalora - System 2 | Bungalora | ENERGISED MAINTENANCE INSPECTION | QLD-ET-WI-PM001-0005 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0005 | 001
Bungalora - System 3 | Bungalora | ENERGISED MAINTENANCE INSPECTION | QLD-ET-WI-PM001-0005 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0005 | 001
Mullumbimby - System 1 | Mullumbimby | ENERGISED MAINTENANCE INSPECTION | QLD-ET-WI-PM001-0005 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0005 | 001
Mullumbimby - System 2 | Mullumbimby | ENERGISED MAINTENANCE INSPECTION | QLD-ET-WI-PM001-0005 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0005 | 001
Mullumbimby - System 3 | Mullumbimby | ENERGISED MAINTENANCE INSPECTION | QLD-ET-WI-PM001-0005 | Every 1 month(s) | 27/09/2013 | 27/10/2013 | 0005 | 001
Bungalora System 1 - Uniterruptable DC and AC Supply A | Bungalora System 1 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Bungalora System 1 - Uniterruptable DC and AC Supply B | Bungalora System 1 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Bungalora System 2 - Uniterruptable DC and AC Supply A | Bungalora System 2 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Bungalora System 2 - Uniterruptable DC and AC Supply B | Bungalora System 2 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Bungalora System 3 - Uniterruptable DC and AC Supply A | Bungalora System 3 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Bungalora System 3 - Uniterruptable DC and AC Supply B | Bungalora System 3 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Mullumbimby System 1 - Uninterruptable DC and AC Supply A | Mullumbimby System 1 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Mullumbimby System 1 - Uninterruptable DC and AC Supply B | Mullumbimby System 1 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Mullumbimby System 2 - Uninterruptable DC and AC Supply A | Mullumbimby System 2 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Mullumbimby System 2 - Uninterruptable DC and AC Supply B | Mullumbimby System 2 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Mullumbimby System 3 - Uninterruptable DC and AC Supply A | Mullumbimby System 3 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Mullumbimby System 3 - Uninterruptable DC and AC Supply B | Mullumbimby System 3 - Station Service Power System | UNINTERRUPTIBLE POWER SUPPLY | QLD-ET-WI-PM006-0006 | Every 6 month(s) | 27/07/2013 | 27/01/2014 | 0006 | 006
Bungalora - 110kV Overhead Bus | Bungalora | OIL FILLED CAPACITOR MAINTENANCE - 3YR | QLD-ET-WI-PM036-0010-BLA | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0010 | 036
Bungalora - 110kV Overhead Bus | Bungalora | YARD MAINTENANCE | QLD-ET-WI-PM001-0010 | The last Fr of every 1 month(s) | 27/09/2013 | 25/10/2013 | 0010 | 001
Bungalora - System 1 | Bungalora | OIL FILLED CAPACITOR MAINTENANCE - 3YR | QLD-ET-WI-PM036-0010-BLA1 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0010 | 036
Bungalora - System 2 | Bungalora | OIL FILLED CAPACITOR MAINTENANCE - 3YR | QLD-ET-WI-PM036-0010-BLA2 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0010 | 036
Bungalora - System 3 | Bungalora | OIL FILLED CAPACITOR MAINTENANCE - 3YR | QLD-ET-WI-PM036-0010-BLA3 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0010 | 036
Mullumbimby - 132kV Overhead Bus | Mullumbimby | OIL FILLED CAPACITOR MAINTENANCE - 3YR | QLD-ET-WI-PM036-0010-MUL | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0010 | 036
Mullumbimby - 132kV Overhead Bus | Mullumbimby | YARD MAINTENANCE | QLD-ET-WI-PM001-0010 | The last Fr of every 1 month(s) | 27/09/2013 | 25/10/2013 | 0010 | 001
Mullumbimby - System 1 | Mullumbimby | OIL FILLED CAPACITOR MAINTENANCE - 3YR | QLD-ET-WI-PM036-0010-MUL1 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0010 | 036
Mullumbimby - System 2 | Mullumbimby | OIL FILLED CAPACITOR MAINTENANCE - 3YR | QLD-ET-WI-PM036-0010-MUL2 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0010 | 036
Mullumbimby - System 3 | Mullumbimby | OIL FILLED CAPACITOR MAINTENANCE - 3YR | QLD-ET-WI-PM036-0010-MUL3 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0010 | 036
Bungalora System 1 - Spill Kits | Bungalora System 1 - Small Plant & Safety Equipment | INSPECT SPILL KITS | QLD-ET-WI-PM006-0011 | Every 6 month(s) | 1/09/2013 | 1/03/2014 | 0011 | 006
Mullumbimby System 1 - Spill Kits | Mullumbimby System 1 - Small Plant & Safety Equipment | INSPECT SPILL KITS | QLD-ET-WI-PM006-0011 | Every 6 month(s) | 1/09/2013 | 1/03/2014 | 0011 | 006
DirectLink Easement | DirectLink | FUNCTIONAL TEST OF HIGH VOLTAGE TEST EQUIPMENT | QLD-ET-WI-PM006-0013 | Every 6 month(s) | 26/08/2013 | 26/02/2014 | 0013 | 006
Bungalora - System 1 | Bungalora | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0014-BLA1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0014 | 012
Bungalora - System 2 | Bungalora | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0014-BLA2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0014 | 012
Bungalora - System 3 | Bungalora | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0014-BLA3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0014 | 012
Mullumbimby - System 1 | Mullumbimby | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0014-MUL1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0014 | 012
Mullumbimby - System 2 | Mullumbimby | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0014-MUL2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0014 | 012
Mullumbimby - System 3 | Mullumbimby | HALL EFFECT CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0014-MUL3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0014 | 012
Bungalora System 1 - Inverter / Rectifier Area | Bungalora - System 1 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0016 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0016 | 012
Bungalora System 2 - Inverter / Rectifier Area | Bungalora - System 2 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0016 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0016 | 012
Bungalora System 3 - Inverter / Rectifier Area | Bungalora - System 3 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0016 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0016 | 012
Mullumbimby System 1 - Inverter / Rectifier Area | Mullumbimby - System 1 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0016 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0016 | 012
Mullumbimby System 2 - Inverter / Rectifier Area | Mullumbimby - System 2 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0016 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0016 | 012
Mullumbimby System 3 - Inverter / Rectifier Area | Mullumbimby - System 3 | ROGOWSKI CURRENT TRANSDUCER MAINTENANCE | QLD-ET-WI-PM012-0016 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0016 | 012
DirectLink Easement | DirectLink | VEGETATION MANAGEMENT - 1M | QLD-ET-WI-PM001-0017 | Every 1 month(s) | 30/09/2013 | 30/10/2013 | 0017 | 001
DirectLink Easement | DirectLink | CABLE MARKER SIGN MAINTENANCE - 1M | QLD-ET-WI-PM001-0019 | Every 1 month(s) | 30/09/2013 | 30/10/2013 | 0019 | 001
Bungalora - System 1 | Bungalora | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | QLD-ET-WI-PM060-0022-BLA1 | Every 5 year(s) | 27/07/2010 | 27/07/2015 | 0022 | 060
Bungalora - System 1 | Bungalora | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | QLD-ET-WI-PM012-0022-BLA1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0022 | 012
Bungalora - System 2 | Bungalora | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | QLD-ET-WI-PM012-0022-BLA2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0022 | 012
Bungalora - System 2 | Bungalora | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | QLD-ET-WI-PM060-0022-BLA2 | Every 5 year(s) | 27/07/2010 | 27/07/2015 | 0022 | 060
Bungalora - System 3 | Bungalora | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | QLD-ET-WI-PM012-0022-BLA3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0022 | 012
Bungalora - System 3 | Bungalora | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | QLD-ET-WI-PM060-0022-BLA3 | Every 5 year(s) | 27/07/2010 | 27/07/2015 | 0022 | 060
Mullumbimby - System 1 | Mullumbimby | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | QLD-ET-WI-PM012-0022-MUL1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0022 | 012
Mullumbimby - System 1 | Mullumbimby | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | QLD-ET-WI-PM060-0022-MUL1 | Every 5 year(s) | 27/07/2010 | 27/07/2015 | 0022 | 060
Mullumbimby - System 2 | Mullumbimby | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | QLD-ET-WI-PM012-0022-MUL2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0022 | 012
Mullumbimby - System 2 | Mullumbimby | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | QLD-ET-WI-PM060-0022-MUL2 | Every 5 year(s) | 27/07/2010 | 27/07/2015 | 0022 | 060
Mullumbimby - System 3 | Mullumbimby | OUTDOOR POST TYPE CURRENT TRANSFORMER - 1YR | QLD-ET-WI-PM012-0022-MUL3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0022 | 012
Mullumbimby - System 3 | Mullumbimby | OUTDOOR POST TYPE CURRENT TRANSFORMER - 5YR | QLD-ET-WI-PM060-0022-MUL3 | Every 5 year(s) | 27/07/2010 | 27/07/2015 | 0022 | 060
Bungalora System 1 - DC Filter Area | Bungalora - System 1 | CABLE SCREEN CURRENT TRANSFORMER | QLD-ET-WI-PM012-0024-BLA1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0024 | 012
Bungalora System 2 - DC Filter Area | Bungalora - System 2 | CABLE SCREEN CURRENT TRANSFORMER | QLD-ET-WI-PM012-0024-BLA2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0024 | 012
Bungalora System 3 - DC Filter Area | Bungalora - System 3 | CABLE SCREEN CURRENT TRANSFORMER | QLD-ET-WI-PM012-0024-BLA3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0024 | 012
Mullumbimby System 1 - DC Filter Area | Mullumbimby - System 1 | CABLE SCREEN CURRENT TRANSFORMER | QLD-ET-WI-PM012-0024-MUL1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0024 | 012
Mullumbimby System 2 - DC Filter Area | Mullumbimby - System 2 | CABLE SCREEN CURRENT TRANSFORMER | QLD-ET-WI-PM012-0024-MUL2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0024 | 012
Mullumbimby System 3 - DC Filter Area | Mullumbimby - System 3 | CABLE SCREEN CURRENT TRANSFORMER | QLD-ET-WI-PM012-0024-MUL3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0024 | 012
Bungalora System 1 - Capacitive Voltage Transformer WA.Z1.T11 | Bungalora System 1 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0026 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0026 | 012
Bungalora System 1 - Capacitive Voltage Transformer WA.Z1.T11 | Bungalora System 1 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 10YR | QLD-ET-WI-PM120-0026 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0026 | 120
Bungalora System 1 - Main Stn Incoming Capacitive Volt Transformer WT.T11 | Bungalora - 110kV Overhead Bus | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0026 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0026 | 012
Bungalora System 1 - Main Stn Incoming Capacitive Volt Transformer WT.T11 | Bungalora - 110kV Overhead Bus | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 10YR | QLD-ET-WI-PM120-0026 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0026 | 120
Bungalora System 2 - Capacitive Voltage Transformer WA.Z1.T11 | Bungalora System 2 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0026 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0026 | 012
Bungalora System 2 - Capacitive Voltage Transformer WA.Z1.T11 | Bungalora System 2 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 10YR | QLD-ET-WI-PM120-0026 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0026 | 120
Bungalora System 3 - Capacitive Voltage Transformer WA.Z1.T11 | Bungalora System 3 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0026 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0026 | 012
Bungalora System 3 - Capacitive Voltage Transformer WA.Z1.T11 | Bungalora System 3 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 10YR | QLD-ET-WI-PM120-0026 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0026 | 120
Mullumbimby System 1 - Capacitive Voltage Transformer WA.Z1.T11 | Mullumbimby System 1 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0026 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0026 | 012
Mullumbimby System 1 - Capacitive Voltage Transformer WA.Z1.T11 | Mullumbimby System 1 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 10YR | QLD-ET-WI-PM120-0026 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0026 | 120
Mullumbimby System 2 - Capacitive Voltage Transformer WA.Z1.T11 | Mullumbimby System 2 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0026 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0026 | 012
Mullumbimby System 2 - Capacitive Voltage Transformer WA.Z1.T11 | Mullumbimby System 2 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 10YR | QLD-ET-WI-PM120-0026 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0026 | 120
Mullumbimby System 3 - Capacitive Voltage Transformer WA.Z1.T11 | Mullumbimby System 3 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0026 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0026 | 012
Mullumbimby System 3 - Capacitive Voltage Transformer WA.Z1.T11 | Mullumbimby System 3 - AC Filter Area | CAPACITIVE VOLTAGE TRANSFORMER MAINTENANCE - 10YR | QLD-ET-WI-PM120-0026 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0026 | 120
Bungalora System 1 - AC Switchyard Area WT2 | Bungalora - System 1 | POWER TRANSFORMER MAINTENANCE | QLD-ET-WI-PM012-0028-BLA1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0028 | 012
Bungalora System 2 - Power Transformer WT2.T1 | Bungalora System 2 - AC Switchyard Area WT2 | POWER TRANSFORMER MAINTENANCE | QLD-ET-WI-PM012-0028 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0028 | 012
Bungalora System 3 - Power Transformer WT2.T1 | Bungalora System 3 - AC Switchyard Area WT2 | POWER TRANSFORMER MAINTENANCE | QLD-ET-WI-PM012-0028 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0028 | 012
Mullumbimby System 1 - Power Transformer WT2.T1 | Mullumbimby System 1 - AC Switchyard Area WT2 | POWER TRANSFORMER MAINTENANCE | QLD-ET-WI-PM012-0028 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0028 | 012
Mullumbimby System 2 - Power Transformer WT2.T1 | Mullumbimby System 2 - AC Switchyard Area WT2 | POWER TRANSFORMER MAINTENANCE | QLD-ET-WI-PM012-0028 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0028 | 012
Mullumbimby System 3 - Power Transformer WT2.T1 | Mullumbimby System 3 - AC Switchyard Area WT2 | POWER TRANSFORMER MAINTENANCE | QLD-ET-WI-PM012-0028 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0028 | 012
Bungalora - System 1 | Bungalora | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | QLD-ET-WI-PM012-0038-BLA1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0038 | 012
Bungalora - System 2 | Bungalora | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | QLD-ET-WI-PM012-0038-BLA2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0038 | 012
Bungalora - System 3 | Bungalora | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | QLD-ET-WI-PM012-0038-BLA3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0038 | 012
Mullumbimby - System 1 | Mullumbimby | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | QLD-ET-WI-PM012-0038-MUL1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0038 | 012
Mullumbimby - System 2 | Mullumbimby | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | QLD-ET-WI-PM012-0038-MUL2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0038 | 012
Mullumbimby - System 3 | Mullumbimby | ZINC OXIDE SURGE ARRESTOR MAINTENANCE | QLD-ET-WI-PM012-0038-MUL3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0038 | 012
Bungalora System 1 - AC Filter Area | Bungalora - System 1 | AC FILTER RESISTOR MAINTENANCE | QLD-ET-WI-PM012-0042-BLA1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0042 | 012
Bungalora System 2 - AC Filter Area | Bungalora - System 2 | AC FILTER RESISTOR MAINTENANCE | QLD-ET-WI-PM012-0042-BLA2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0042 | 012
Bungalora System 3 - AC Filter Area | Bungalora - System 3 | AC FILTER RESISTOR MAINTENANCE | QLD-ET-WI-PM012-0042-BLA3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0042 | 012
Mullumbimby System 1 - AC Filter Area | Mullumbimby - System 1 | AC FILTER RESISTOR MAINTENANCE | QLD-ET-WI-PM012-0042-MUL1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0042 | 012
Mullumbimby System 2 - AC Filter Area | Mullumbimby - System 2 | AC FILTER RESISTOR MAINTENANCE | QLD-ET-WI-PM012-0042-MUL2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0042 | 012
Mullumbimby System 3 - AC Filter Area | Mullumbimby - System 3 | AC FILTER RESISTOR MAINTENANCE | QLD-ET-WI-PM012-0042-MUL3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0042 | 012
Bungalora System 1 - Valve Cooling System | Bungalora - System 1 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | QLD-ET-WI-PM012-0050 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0050 | 012
Bungalora System 1 - Valve Cooling System | Bungalora - System 1 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | QLD-ET-WI-PM024-0050 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0050 | 024
Bungalora System 1 - Valve Cooling System | Bungalora - System 1 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | QLD-ET-WI-PM060-0050-BLA1 | Every 5 year(s) | 1/10/2010 | 1/10/2015 | 0050 | 060
Bungalora System 2 - Valve Cooling System | Bungalora - System 2 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | QLD-ET-WI-PM012-0050 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0050 | 012
Bungalora System 2 - Valve Cooling System | Bungalora - System 2 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | QLD-ET-WI-PM024-0050 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0050 | 024
Bungalora System 2 - Valve Cooling System | Bungalora - System 2 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | QLD-ET-WI-PM060-0050-BLA2 | Every 5 year(s) | 1/10/2010 | 1/10/2015 | 0050 | 060
Bungalora System 3 - Valve Cooling System | Bungalora - System 3 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | QLD-ET-WI-PM012-0050 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0050 | 012
Bungalora System 3 - Valve Cooling System | Bungalora - System 3 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | QLD-ET-WI-PM024-0050 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0050 | 024
Bungalora System 3 - Valve Cooling System | Bungalora - System 3 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | QLD-ET-WI-PM060-0050-BLA3 | Every 5 year(s) | 1/10/2010 | 1/10/2015 | 0050 | 060
Mullumbimby System 1 - Valve Cooling System | Mullumbimby - System 1 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | QLD-ET-WI-PM012-0050 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0050 | 012
Mullumbimby System 1 - Valve Cooling System | Mullumbimby - System 1 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | QLD-ET-WI-PM024-0050 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0050 | 024
Mullumbimby System 1 - Valve Cooling System | Mullumbimby - System 1 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | QLD-ET-WI-PM060-0050-MUL1 | Every 5 year(s) | 1/10/2010 | 1/10/2015 | 0050 | 060
Mullumbimby System 2 - Valve Cooling System | Mullumbimby - System 2 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | QLD-ET-WI-PM012-0050 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0050 | 012
Mullumbimby System 2 - Valve Cooling System | Mullumbimby - System 2 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | QLD-ET-WI-PM024-0050 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0050 | 024
Mullumbimby System 2 - Valve Cooling System | Mullumbimby - System 2 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | QLD-ET-WI-PM060-0050-MUL2 | Every 5 year(s) | 1/10/2010 | 1/10/2015 | 0050 | 060
Mullumbimby System 3 - Valve Cooling System | Mullumbimby - System 3 | VALVE COOLING SYSTEM MAINTENANCE - 1YR | QLD-ET-WI-PM012-0050 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0050 | 012
Mullumbimby System 3 - Valve Cooling System | Mullumbimby - System 3 | VALVE COOLING SYSTEM MAINTENANCE - 2YR | QLD-ET-WI-PM024-0050 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0050 | 024
Mullumbimby System 3 - Valve Cooling System | Mullumbimby - System 3 | VALVE COOLING SYSTEM MAINTENANCE - 5YR | QLD-ET-WI-PM060-0050-MUL3 | Every 5 year(s) | 1/10/2010 | 1/10/2015 | 0050 | 060
Bungalora System 1 - Valve Cooling System | Bungalora - System 1 | VALVE COOLING SYSTEM PUMP MAINTENANCE | QLD-ET-WI-PM012-0052-BLA1 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0052 | 012
Bungalora System 2 - Valve Cooling System | Bungalora - System 2 | VALVE COOLING SYSTEM PUMP MAINTENANCE | QLD-ET-WI-PM012-0052-BLA2 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0052 | 012
Bungalora System 3 - Valve Cooling System | Bungalora - System 3 | VALVE COOLING SYSTEM PUMP MAINTENANCE | QLD-ET-WI-PM012-0052-BLA3 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0052 | 012
Mullumbimby System 1 - Valve Cooling System | Mullumbimby - System 1 | VALVE COOLING SYSTEM PUMP MAINTENANCE | QLD-ET-WI-PM012-0052-MUL1 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0052 | 012
Mullumbimby System 2 - Valve Cooling System | Mullumbimby - System 2 | VALVE COOLING SYSTEM PUMP MAINTENANCE | QLD-ET-WI-PM012-0052-MUL2 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0052 | 012
Mullumbimby System 3 - Valve Cooling System | Mullumbimby - System 3 | VALVE COOLING SYSTEM PUMP MAINTENANCE | QLD-ET-WI-PM012-0052-MUL3 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0052 | 012
Bungalora System 1 - Valve Cooling Motor Control Centre | Bungalora System 1 - Station Service Power System | VALVE COOLING MCC THERMOGRAPHIC IMAGING | QLD-ET-WI-PM012-0054 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0054 | 012
Bungalora System 2 - Valve Cooling Motor Control Centre | Bungalora System 2 - Station Service Power System | VALVE COOLING MCC THERMOGRAPHIC IMAGING | QLD-ET-WI-PM012-0054 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0054 | 012
Bungalora System 3 - Valve Cooling Motor Control Centre | Bungalora System 3 - Station Service Power System | VALVE COOLING MCC THERMOGRAPHIC IMAGING | QLD-ET-WI-PM012-0054 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0054 | 012
Mullumbimby System 1 - Valve Cooling Motor Control Centre | Mullumbimby System 1 - Station Service Power System | VALVE COOLING MCC THERMOGRAPHIC IMAGING | QLD-ET-WI-PM012-0054 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0054 | 012
Mullumbimby System 2 - Valve Cooling Motor Control Centre | Mullumbimby System 2 - Station Service Power System | VALVE COOLING MCC THERMOGRAPHIC IMAGING | QLD-ET-WI-PM012-0054 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0054 | 012
Mullumbimby System 3 - Valve Cooling Motor Control Centre | Mullumbimby System 3 - Station Service Power System | VALVE COOLING MCC THERMOGRAPHIC IMAGING | QLD-ET-WI-PM012-0054 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0054 | 012
Bungalora System 1 - Valve Cooling Water Cooling Tower | Bungalora System 1 - Valve Cooling System | AIR BLAST COOLER MAINTENANCE | QLD-ET-WI-PM024-0056 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0056 | 024
Bungalora System 2 - Valve Cooling Water Cooling Tower | Bungalora System 2 - Valve Cooling System | AIR BLAST COOLER MAINTENANCE | QLD-ET-WI-PM024-0056 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0056 | 024
Bungalora System 3 - Valve Cooling Water Cooling Tower | Bungalora System 3 - Valve Cooling System | AIR BLAST COOLER MAINTENANCE | QLD-ET-WI-PM024-0056 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0056 | 024
Mullumbimby System 1 - Valve Cooling Water Cooling Tower | Mullumbimby System 1 - Valve Cooling System | AIR BLAST COOLER MAINTENANCE | QLD-ET-WI-PM024-0056 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0056 | 024
Mullumbimby System 2 - Valve Cooling Water Cooling Tower | Mullumbimby System 2 - Valve Cooling System | AIR BLAST COOLER MAINTENANCE | QLD-ET-WI-PM024-0056 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0056 | 024
Mullumbimby System 3 - Valve Cooling Water Cooling Tower | Mullumbimby System 3 - Valve Cooling System | AIR BLAST COOLER MAINTENANCE | QLD-ET-WI-PM024-0056 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0056 | 024
Bungalora System 1 - Heating Ventilating & Air Conditioning | Bungalora - System 1 | VALVE DEHUMIDIFIER MAINTENANCE | QLD-ET-WI-PM012-0060 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0060 | 012
Bungalora System 2 - Heating Ventilating & Air Conditioning | Bungalora - System 2 | VALVE DEHUMIDIFIER MAINTENANCE | QLD-ET-WI-PM012-0060 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0060 | 012
Bungalora System 3 - Heating Ventilating & Air Conditioning | Bungalora - System 3 | VALVE DEHUMIDIFIER MAINTENANCE | QLD-ET-WI-PM012-0060 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0060 | 012
Mullumbimby System 1 - Heating Ventilating & Air Conditioning | Mullumbimby - System 1 | VALVE DEHUMIDIFIER MAINTENANCE | QLD-ET-WI-PM012-0060 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0060 | 012
Mullumbimby System 2 - Heating Ventilating & Air Conditioning | Mullumbimby - System 2 | VALVE DEHUMIDIFIER MAINTENANCE | QLD-ET-WI-PM012-0060 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0060 | 012
Mullumbimby System 3 - Heating Ventilating & Air Conditioning | Mullumbimby - System 3 | VALVE DEHUMIDIFIER MAINTENANCE | QLD-ET-WI-PM012-0060 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0060 | 012
Bungalora System 1 - Heating Ventilating & Air Conditioning | Bungalora - System 1 | VALVE HUMIDITY CONTROL SYSTEM | QLD-ET-WI-PM012-0062 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0062 | 012
Bungalora System 2 - Heating Ventilating & Air Conditioning | Bungalora - System 2 | VALVE HUMIDITY CONTROL SYSTEM | QLD-ET-WI-PM012-0062 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0062 | 012
Bungalora System 3 - Heating Ventilating & Air Conditioning | Bungalora - System 3 | VALVE HUMIDITY CONTROL SYSTEM | QLD-ET-WI-PM012-0062 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0062 | 012
Mullumbimby System 1 - Heating Ventilating & Air Conditioning | Mullumbimby - System 1 | VALVE HUMIDITY CONTROL SYSTEM | QLD-ET-WI-PM012-0062 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0062 | 012
Mullumbimby System 2 - Heating Ventilating & Air Conditioning | Mullumbimby - System 2 | VALVE HUMIDITY CONTROL SYSTEM | QLD-ET-WI-PM012-0062 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0062 | 012
Mullumbimby System 3 - Heating Ventilating & Air Conditioning | Mullumbimby - System 3 | VALVE HUMIDITY CONTROL SYSTEM | QLD-ET-WI-PM012-0062 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0062 | 012
Bungalora | DirectLink | REACTOR MAINTENANCE - 15YR | QLD-ET-WI-PM180-0104-BLA1 | Every 15 year(s) | 15/12/2000 | 15/12/2015 | 0104 | 180
Bungalora - System 1 | Bungalora | REACTOR MAINTENANCE - 1YR | QLD-ET-WI-PM012-0104 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0104 | 012
Bungalora - System 2 | Bungalora | REACTOR MAINTENANCE - 1YR | QLD-ET-WI-PM012-0104 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0104 | 012
Bungalora - System 2 | Bungalora | REACTOR MAINTENANCE - 15YR | QLD-ET-WI-PM180-0104-BLA2 | Every 15 year(s) | 15/12/2000 | 15/12/2015 | 0104 | 180
Bungalora - System 3 | Bungalora | REACTOR MAINTENANCE - 1YR | QLD-ET-WI-PM012-0104 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0104 | 012
Bungalora - System 3 | Bungalora | REACTOR MAINTENANCE - 15YR | QLD-ET-WI-PM180-0104-BLA3 | Every 15 year(s) | 15/12/2000 | 15/12/2015 | 0104 | 180
Mullumbimby | DirectLink | REACTOR MAINTENANCE - 15YR | QLD-ET-WI-PM180-0104-MUL1 | Every 15 year(s) | 15/12/2000 | 15/12/2015 | 0104 | 180
Mullumbimby - System 1 | Mullumbimby | REACTOR MAINTENANCE - 1YR | QLD-ET-WI-PM012-0104 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0104 | 012
Mullumbimby - System 2 | Mullumbimby | REACTOR MAINTENANCE - 1YR | QLD-ET-WI-PM012-0104 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0104 | 012
Mullumbimby - System 2 | Mullumbimby | REACTOR MAINTENANCE - 15YR | QLD-ET-WI-PM180-0104-MUL2 | Every 15 year(s) | 15/12/2000 | 15/12/2015 | 0104 | 180
Mullumbimby - System 3 | Mullumbimby | REACTOR MAINTENANCE - 1YR | QLD-ET-WI-PM012-0104 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0104 | 012
Mullumbimby - System 3 | Mullumbimby | REACTOR MAINTENANCE - 15YR | QLD-ET-WI-PM180-0104-MUL3 | Every 15 year(s) | 15/12/2000 | 15/12/2015 | 0104 | 180
Bungalora System 1 - Inverter / Rectifier Area | Bungalora - System 1 | IGBT VALVE MAINTENANCE | QLD-ET-WI-PM012-0110 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0110 | 012
Bungalora System 2 - Inverter / Rectifier Area | Bungalora - System 2 | IGBT VALVE MAINTENANCE | QLD-ET-WI-PM012-0110 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0110 | 012
Bungalora System 3 - Inverter / Rectifier Area | Bungalora - System 3 | IGBT VALVE MAINTENANCE | QLD-ET-WI-PM012-0110 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0110 | 012
Mullumbimby System 1 - Inverter / Rectifier Area | Mullumbimby - System 1 | IGBT VALVE MAINTENANCE | QLD-ET-WI-PM012-0110 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0110 | 012
Mullumbimby System 2 - Inverter / Rectifier Area | Mullumbimby - System 2 | IGBT VALVE MAINTENANCE | QLD-ET-WI-PM012-0110 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0110 | 012
Mullumbimby System 3 - Inverter / Rectifier Area | Mullumbimby - System 3 | IGBT VALVE MAINTENANCE | QLD-ET-WI-PM012-0110 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0110 | 012
Bungalora - System 1 | Bungalora | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0120-BLA1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0120 | 012
Bungalora - System 1 | Bungalora | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | QLD-ET-WI-PM024-0120-BLA1 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0120 | 024
Bungalora - System 2 | Bungalora | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0120-BLA2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0120 | 012
Bungalora - System 2 | Bungalora | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | QLD-ET-WI-PM024-0120-BLA2 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0120 | 024
Bungalora - System 3 | Bungalora | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0120-BLA3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0120 | 012
Bungalora - System 3 | Bungalora | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | QLD-ET-WI-PM024-0120-BLA3 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0120 | 024
Mullumbimby - System 1 | Mullumbimby | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0120-MUL1 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0120 | 012
Mullumbimby - System 1 | Mullumbimby | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | QLD-ET-WI-PM024-0120-MUL1 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0120 | 024
Mullumbimby - System 2 | Mullumbimby | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0120-MUL2 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0120 | 012
Mullumbimby - System 2 | Mullumbimby | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | QLD-ET-WI-PM024-0120-MUL2 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0120 | 024
Mullumbimby - System 3 | Mullumbimby | DIRECT VOLTAGE DIVIDER MAINTENANCE - 1YR | QLD-ET-WI-PM012-0120-MUL3 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0120 | 012
Mullumbimby - System 3 | Mullumbimby | DIRECT VOLTAGE DIVIDER MAINTENANCE - 2YR | QLD-ET-WI-PM024-0120-MUL3 | Every 2 year(s) | 1/09/2013 | 1/09/2015 | 0120 | 024
Bungalora System 1 - Nitrogen Semi Automatic Discharge Unit | Bungalora System 1 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | QLD-ET-WI-PM012-0124 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0124 | 012
Bungalora System 1 - Nitrogen Semi Automatic Discharge Unit | Bungalora System 1 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | QLD-ET-WI-PM036-0124 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0124 | 036
Bungalora System 2 - Nitrogen Semi Automatic Discharge Unit | Bungalora System 2 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | QLD-ET-WI-PM012-0124 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0124 | 012
Bungalora System 2 - Nitrogen Semi Automatic Discharge Unit | Bungalora System 2 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | QLD-ET-WI-PM036-0124 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0124 | 036
Bungalora System 3 - Nitrogen Semi Automatic Discharge Unit | Bungalora System 3 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | QLD-ET-WI-PM012-0124 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0124 | 012
Bungalora System 3 - Nitrogen Semi Automatic Discharge Unit | Bungalora System 3 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | QLD-ET-WI-PM036-0124 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0124 | 036
Mullumbimby System 1 - Nitrogen Semi Automatic Discharge Unit | Mullumbimby System 1 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | QLD-ET-WI-PM012-0124 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0124 | 012
Mullumbimby System 1 - Nitrogen Semi Automatic Discharge Unit | Mullumbimby System 1 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | QLD-ET-WI-PM036-0124 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0124 | 036
Mullumbimby System 2 - Nitrogen Semi Automatic Discharge Unit | Mullumbimby System 2 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | QLD-ET-WI-PM012-0124 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0124 | 012
Mullumbimby System 2 - Nitrogen Semi Automatic Discharge Unit | Mullumbimby System 2 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | QLD-ET-WI-PM036-0124 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0124 | 036
Mullumbimby System 3 - Nitrogen Semi Automatic Discharge Unit | Mullumbimby System 3 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 1YR | QLD-ET-WI-PM012-0124 | Every 1 year(s) | 21/07/2013 | 21/07/2014 | 0124 | 012
Mullumbimby System 3 - Nitrogen Semi Automatic Discharge Unit | Mullumbimby System 3 - Valve Cooling System | NITROGEN DISCHARGE UNIT MAINTENANCE - 3YR | QLD-ET-WI-PM036-0124 | Every 3 year(s) | 1/10/2011 | 1/10/2014 | 0124 | 036
Bungalora - System 1 | Bungalora | CONVERTER STATION THERMOGRAPHIC INSPECTION | QLD-ET-WI-PM012-0126 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0126 | 012
Bungalora - System 2 | Bungalora | CONVERTER STATION THERMOGRAPHIC INSPECTION | QLD-ET-WI-PM012-0126 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0126 | 012
Bungalora - System 3 | Bungalora | CONVERTER STATION THERMOGRAPHIC INSPECTION | QLD-ET-WI-PM012-0126 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0126 | 012
Mullumbimby - System 1 | Mullumbimby | CONVERTER STATION THERMOGRAPHIC INSPECTION | QLD-ET-WI-PM012-0126 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0126 | 012
Mullumbimby - System 2 | Mullumbimby | CONVERTER STATION THERMOGRAPHIC INSPECTION | QLD-ET-WI-PM012-0126 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0126 | 012
Mullumbimby - System 3 | Mullumbimby | CONVERTER STATION THERMOGRAPHIC INSPECTION | QLD-ET-WI-PM012-0126 | Every 1 year(s) | 27/07/2013 | 27/07/2014 | 0126 | 012
Bungalora - System 1 | Bungalora | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | QLD-ET-WI-PM012-0128 | Every 1 year(s) | 1/08/2013 | 1/08/2014 | 0128 | 012
Bungalora - System 2 | Bungalora | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | QLD-ET-WI-PM012-0128 | Every 1 year(s) | 6/08/2013 | 6/08/2014 | 0128 | 012
Bungalora - System 3 | Bungalora | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | QLD-ET-WI-PM012-0128 | Every 1 year(s) | 13/08/2013 | 13/08/2014 | 0128 | 012
Mullumbimby - System 1 | Mullumbimby | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | QLD-ET-WI-PM012-0128 | Every 1 year(s) | 1/08/2013 | 1/08/2014 | 0128 | 012
Mullumbimby - System 2 | Mullumbimby | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | QLD-ET-WI-PM012-0128 | Every 1 year(s) | 6/08/2013 | 6/08/2014 | 0128 | 012
Mullumbimby - System 3 | Mullumbimby | FUNCTIONAL TEST OF EMERGENCY STOP BUTTON | QLD-ET-WI-PM012-0128 | Every 1 year(s) | 13/08/2013 | 13/08/2014 | 0128 | 012
Bungalora | DirectLink | CIRCUIT BREAKER MAINTENANCE - 3YR | QLD-ET-WI-PM036-0140-BLA1 | Every 3 year(s) | 20/09/2011 | 20/09/2014 | 0140 | 036
Bungalora | DirectLink | CIRCUIT BREAKER MAINTENANCE - 15YR | QLD-ET-WI-PM180-0140-BLA1 | Every 15 year(s) | 1/10/2000 | 1/10/2015 | 0140 | 180
Bungalora | DirectLink | CIRCUIT BREAKER MAINTENANCE - 30YR | QLD-ET-WI-PM360-0140-BLA1 | Every 30 year(s) | 1/10/2000 | 1/10/2030 | 0140 | 360
Bungalora System 1 - AC Switchyard Area WT1 | Bungalora - System 1 | CIRCUIT BREAKER MAINTENANCE - 6YR | QLD-ET-WI-PM072-0140-BLA1 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0140 | 072
Bungalora System 2 - AC Switchyard Area WT1 | Bungalora - System 2 | CIRCUIT BREAKER MAINTENANCE - 3YR | QLD-ET-WI-PM036-0140-BLA2 | Every 3 year(s) | 20/09/2011 | 20/09/2014 | 0140 | 036
Bungalora System 2 - AC Switchyard Area WT1 | Bungalora - System 2 | CIRCUIT BREAKER MAINTENANCE - 6YR | QLD-ET-WI-PM072-0140-BLA2 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0140 | 072
Bungalora System 2 - AC Switchyard Area WT1 | Bungalora - System 2 | CIRCUIT BREAKER MAINTENANCE - 15YR | QLD-ET-WI-PM180-0140-BLA2 | Every 15 year(s) | 1/10/2000 | 1/10/2015 | 0140 | 180
Bungalora System 2 - AC Switchyard Area WT1 | Bungalora - System 2 | CIRCUIT BREAKER MAINTENANCE - 30YR | QLD-ET-WI-PM360-0140-BLA2 | Every 30 year(s) | 1/10/2000 | 1/10/2030 | 0140 | 360
Bungalora System 3 - AC Switchyard Area WT1 | Bungalora - System 3 | CIRCUIT BREAKER MAINTENANCE - 3YR | QLD-ET-WI-PM036-0140-BLA3 | Every 3 year(s) | 20/09/2011 | 20/09/2014 | 0140 | 036
Bungalora System 3 - AC Switchyard Area WT1 | Bungalora - System 3 | CIRCUIT BREAKER MAINTENANCE - 6YR | QLD-ET-WI-PM072-0140-BLA3 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0140 | 072
Bungalora System 3 - AC Switchyard Area WT1 | Bungalora - System 3 | CIRCUIT BREAKER MAINTENANCE - 15YR | QLD-ET-WI-PM180-0140-BLA3 | Every 15 year(s) | 1/10/2000 | 1/10/2015 | 0140 | 180
Bungalora System 3 - AC Switchyard Area WT1 | Bungalora - System 3 | CIRCUIT BREAKER MAINTENANCE - 30YR | QLD-ET-WI-PM360-0140-BLA3 | Every 30 year(s) | 1/10/2000 | 1/10/2030 | 0140 | 360
Mullumbimby System 1 - AC Switchyard Area WT1 | Mullumbimby - System 1 | CIRCUIT BREAKER MAINTENANCE - 3YR | QLD-ET-WI-PM036-0140-MUL1 | Every 3 year(s) | 20/09/2011 | 20/09/2014 | 0140 | 036
Mullumbimby System 1 - AC Switchyard Area WT1 | Mullumbimby - System 1 | CIRCUIT BREAKER MAINTENANCE - 6YR | QLD-ET-WI-PM072-0140-MUL1 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0140 | 072
Mullumbimby System 1 - AC Switchyard Area WT1 | Mullumbimby - System 1 | CIRCUIT BREAKER MAINTENANCE - 15YR | QLD-ET-WI-PM180-0140-MUL1 | Every 15 year(s) | 1/10/2000 | 1/10/2015 | 0140 | 180
Mullumbimby System 1 - AC Switchyard Area WT1 | Mullumbimby - System 1 | CIRCUIT BREAKER MAINTENANCE - 30YR | QLD-ET-WI-PM360-0140-MUL1 | Every 30 year(s) | 1/10/2000 | 1/10/2030 | 0140 | 360
Mullumbimby System 2 - AC Switchyard Area WT1 | Mullumbimby - System 2 | CIRCUIT BREAKER MAINTENANCE - 3YR | QLD-ET-WI-PM036-0140-MUL2 | Every 3 year(s) | 20/09/2011 | 20/09/2014 | 0140 | 036
Mullumbimby System 2 - AC Switchyard Area WT1 | Mullumbimby - System 2 | CIRCUIT BREAKER MAINTENANCE - 6YR | QLD-ET-WI-PM072-0140-MUL2 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0140 | 072
Mullumbimby System 2 - AC Switchyard Area WT1 | Mullumbimby - System 2 | CIRCUIT BREAKER MAINTENANCE - 15YR | QLD-ET-WI-PM180-0140-MUL2 | Every 15 year(s) | 1/10/2000 | 1/10/2015 | 0140 | 180
Mullumbimby System 2 - AC Switchyard Area WT1 | Mullumbimby - System 2 | CIRCUIT BREAKER MAINTENANCE - 30YR | QLD-ET-WI-PM360-0140-MUL2 | Every 30 year(s) | 1/10/2000 | 1/10/2030 | 0140 | 360
Mullumbimby System 3 - AC Switchyard Area WT1 | Mullumbimby - System 3 | CIRCUIT BREAKER MAINTENANCE - 6YR | QLD-ET-WI-PM072-0140-MUL3 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0140 | 072
Mullumbimby System 3 - AC Switchyard Area WT1 | Mullumbimby - System 3 | CIRCUIT BREAKER MAINTENANCE - 3YR | QLD-ET-WI-PM036-0140-MUL3 | Every 3 year(s) | 20/09/2011 | 20/09/2014 | 0140 | 036
Mullumbimby System 3 - AC Switchyard Area WT1 | Mullumbimby - System 3 | CIRCUIT BREAKER MAINTENANCE - 15YR | QLD-ET-WI-PM180-0140-MUL3 | Every 15 year(s) | 1/10/2000 | 1/10/2015 | 0140 | 180
Mullumbimby System 3 - AC Switchyard Area WT1 | Mullumbimby - System 3 | CIRCUIT BREAKER MAINTENANCE - 30YR | QLD-ET-WI-PM360-0140-MUL3 | Every 30 year(s) | 1/10/2000 | 1/10/2030 | 0140 | 360
Bungalora System 1 - Wall Bushing | Bungalora System 1 - Inverter / Rectifier Area | INSULATING WALL BUSHING MAINTENANCE | QLD-ET-WI-PM036-0142 | Every 3 year(s) | 19/09/2011 | 19/09/2014 | 0142 | 036
Bungalora System 2 - Wall Bushing | Bungalora System 2 - Inverter / Rectifier Area | INSULATING WALL BUSHING MAINTENANCE | QLD-ET-WI-PM036-0142 | Every 3 year(s) | 19/09/2011 | 19/09/2014 | 0142 | 036
Bungalora System 3 - Wall Bushing | Bungalora System 3 - Inverter / Rectifier Area | INSULATING WALL BUSHING MAINTENANCE | QLD-ET-WI-PM036-0142 | Every 3 year(s) | 19/09/2011 | 19/09/2014 | 0142 | 036
Mullumbimby System 1 - Wall Bushing | Mullumbimby System 1 - Inverter / Rectifier Area | INSULATING WALL BUSHING MAINTENANCE | QLD-ET-WI-PM036-0142 | Every 3 year(s) | 19/09/2011 | 19/09/2014 | 0142 | 036
Mullumbimby System 2 - Wall Bushing | Mullumbimby System 2 - Inverter / Rectifier Area | INSULATING WALL BUSHING MAINTENANCE | QLD-ET-WI-PM036-0142 | Every 3 year(s) | 19/09/2011 | 19/09/2014 | 0142 | 036
Mullumbimby System 3 - Wall Bushing | Mullumbimby System 3 - Inverter / Rectifier Area | INSULATING WALL BUSHING MAINTENANCE | QLD-ET-WI-PM036-0142 | Every 3 year(s) | 19/09/2011 | 19/09/2014 | 0142 | 036
Bungalora - 110kV Overhead Bus | Bungalora | PLC FILTER TURNING UNIT MAINTENANCE | QLD-ET-WI-PM060-0150-BLA | Every 5 year(s) | 1/10/2010 | 1/10/2015 | 0150 | 060
Mullumbimby - 132kV Overhead Bus | Mullumbimby | PLC FILTER TURNING UNIT MAINTENANCE | QLD-ET-WI-PM060-0150-MUL | Every 5 year(s) | 1/10/2010 | 1/10/2015 | 0150 | 060
Bungalora - System 1 | Bungalora | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | QLD-ET-WI-PM072-0160-BLA1 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0160 | 072
Bungalora - System 2 | Bungalora | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | QLD-ET-WI-PM072-0160-BLA2 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0160 | 072
Bungalora - System 3 | Bungalora | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | QLD-ET-WI-PM072-0160-BLA3 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0160 | 072
Mullumbimby - System 1 | Mullumbimby | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | QLD-ET-WI-PM072-0160-MUL1 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0160 | 072
Mullumbimby - System 2 | Mullumbimby | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | QLD-ET-WI-PM072-0160-MUL2 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0160 | 072
Mullumbimby - System 3 | Mullumbimby | MOTOR OPERATED DISCONN & EARTH SWITCH MAINTENANCE | QLD-ET-WI-PM072-0160-MUL3 | Every 6 year(s) | 1/10/2012 | 1/10/2018 | 0160 | 072
Bungalora - System 1 | Bungalora | HAND OPERATED DISCONNECTOR & EARTH SWITCH MAINT | QLD-ET-WI-PM120-0180-BLA1 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0180 | 120
Bungalora - System 2 | Bungalora | HAND OPERATED DISCONNECTOR & EARTH SWTICH MAINT | QLD-ET-WI-PM120-0180-BLA2 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0180 | 120
Bungalora - System 3 | Bungalora | HAND OPERATED DISCONNECTOR & EARTH SWITCH MAINT | QLD-ET-WI-PM120-0180-BLA3 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0180 | 120
Bungalora System 1 - Main Station Incoming AC Disconnector | Bungalora - 110kV Overhead Bus | HAND OPERATED DISCONNECTOR & EARTH SWITCH MAINT | QLD-ET-WI-PM120-0180 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0180 | 120
Mullumbimby - System 1 | Mullumbimby | HAND OPERATED DISCONNECTOR & EARTH SWITCH MAINT | QLD-ET-WI-PM120-0180-MUL1 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0180 | 120
Mullumbimby - System 2 | Mullumbimby | HAND OPERATED DISCONNECTOR & EARTH SWITCH MAINT | QLD-ET-WI-PM120-0180-MUL2 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0180 | 120
Mullumbimby - System 3 | Mullumbimby | HAND OPERATED DISCONNECTOR & EARTH SWTICH MAINT | QLD-ET-WI-PM120-0180-MUL3 | Every 10 year(s) | 1/10/2010 | 1/10/2020 | 0180 | 120
Bungalora
Bungalora - 110kV Overhead Bus
Bungalora - System 1
Bungalora - System 2
Bungalora - System 3
Bungalora System 1 - AC Filter Area
Bungalora System 1 - AC Switchyard Area WT1
Bungalora System 1 - AC Switchyard Area WT2
Bungalora System 1 - Capacitive Voltage Transformer WA.Z1.T11
Bungalora System 1 - DC Filter Area
Bungalora System 1 - Eye Wash Station
Bungalora System 1 - Fire Alarm System
Bungalora System 1 - Heating Ventilating & Air Conditioning
Bungalora System 1 - Inverter / Rectifier Area
Bungalora System 1 - Main Station Incoming AC Disconnector
Bungalora System 1 - Main Stn Incoming Capacitive Volt Transformer WT.T11
Bungalora System 1 - Nitrogen Semi Automatic Discharge Unit
Bungalora System 1 - Portable Fire Extinguisher
Bungalora System 1 - Spill Kits
Bungalora System 1 - Uniterruptable DC and AC Supply A
Bungalora System 1 - Uniterruptable DC and AC Supply B
Bungalora System 1 - Valve Cooling Motor Control Centre
Bungalora System 1 - Valve Cooling System
Bungalora System 1 - Valve Cooling Water Cooling Tower
Bungalora System 1 - Wall Bushing
Bungalora System 2 - AC Filter Area
Bungalora System 2 - AC Switchyard Area WT1
Bungalora System 2 - Capacitive Voltage Transformer WA.Z1.T11
Bungalora System 2 - DC Filter Area
Bungalora System 2 - Fire Alarm System
Bungalora System 2 - Heating Ventilating & Air Conditioning
Bungalora System 2 - Inverter / Rectifier Area
Bungalora System 2 - Nitrogen Semi Automatic Discharge Unit
Bungalora System 2 - Portable Fire Extinguisher
Bungalora System 2 - Power Transformer WT2.T1
Bungalora System 2 - Uniterruptable DC and AC Supply A
Bungalora System 2 - Uniterruptable DC and AC Supply B
Bungalora System 2 - Valve Cooling Motor Control Centre
Bungalora System 2 - Valve Cooling System
Bungalora System 2 - Valve Cooling Water Cooling Tower
Bungalora System 2 - Wall Bushing
Bungalora System 3 - AC Filter Area
Bungalora System 3 - AC Switchyard Area WT1
Bungalora System 3 - Capacitive Voltage Transformer WA.Z1.T11
Bungalora System 3 - DC Filter Area
Bungalora System 3 - Fire Alarm System
Bungalora System 3 - Heating Ventilating & Air Conditioning
Bungalora System 3 - Inverter / Rectifier Area
Bungalora System 3 - Nitrogen Semi Automatic Discharge Unit
Bungalora System 3 - Portable Fire Extinguisher
Bungalora System 3 - Power Transformer WT2.T1
Bungalora System 3 - Uniterruptable DC and AC Supply A
Bungalora System 3 - Uniterruptable DC and AC Supply B
Bungalora System 3 - Valve Cooling Motor Control Centre
Bungalora System 3 - Valve Cooling System
Bungalora System 3 - Valve Cooling Water Cooling Tower
Bungalora System 3 - Wall Bushing
DirectLink Easement
Mullumbimby
Mullumbimby - 132kV Overhead Bus
Mullumbimby - System 1
Mullumbimby - System 2
Mullumbimby - System 3
Mullumbimby System 1 - AC Filter Area
Mullumbimby System 1 - AC Switchyard Area WT1
Mullumbimby System 1 - Capacitive Voltage Transformer WA.Z1.T11
Mullumbimby System 1 - DC Filter Area
Mullumbimby System 1 - Eye Wash Station
Mullumbimby System 1 - Fire Alarm System
Mullumbimby System 1 - Heating Ventilating & Air Conditioning
Mullumbimby System 1 - Inverter / Rectifier Area
Mullumbimby System 1 - Nitrogen Semi Automatic Discharge Unit
Mullumbimby System 1 - Portable Fire Extinguisher
Mullumbimby System 1 - Power Transformer WT2.T1
Mullumbimby System 1 - Spill Kits
Mullumbimby System 1 - Uninterruptable DC and AC Supply A
Mullumbimby System 1 - Uninterruptable DC and AC Supply B
Mullumbimby System 1 - Valve Cooling Motor Control Centre
Mullumbimby System 1 - Valve Cooling System
Mullumbimby System 1 - Valve Cooling Water Cooling Tower
Mullumbimby System 1 - Wall Bushing
Mullumbimby System 2 - AC Filter Area
Mullumbimby System 2 - AC Switchyard Area WT1
Mullumbimby System 2 - Capacitive Voltage Transformer WA.Z1.T11
Mullumbimby System 2 - DC Filter Area
Mullumbimby System 2 - Fire Alarm System
Mullumbimby System 2 - Heating Ventilating & Air Conditioning
Mullumbimby System 2 - Inverter / Rectifier Area
Mullumbimby System 2 - Nitrogen Semi Automatic Discharge Unit
Mullumbimby System 2 - Portable Fire Extinguisher
Mullumbimby System 2 - Power Transformer WT2.T1
Mullumbimby System 2 - Uninterruptable DC and AC Supply A
Mullumbimby System 2 - Uninterruptable DC and AC Supply B
Mullumbimby System 2 - Valve Cooling Motor Control Centre
Mullumbimby System 2 - Valve Cooling System
Mullumbimby System 2 - Valve Cooling Water Cooling Tower
Mullumbimby System 2 - Wall Bushing
Mullumbimby System 3 - AC Filter Area
Mullumbimby System 3 - AC Switchyard Area WT1
Mullumbimby System 3 - Capacitive Voltage Transformer WA.Z1.T11
Mullumbimby System 3 - DC Filter Area
Mullumbimby System 3 - Fire Alarm System
Mullumbimby System 3 - Heating Ventilating & Air Conditioning
Mullumbimby System 3 - Inverter / Rectifier Area
Mullumbimby System 3 - Nitrogen Semi Automatic Discharge Unit
Mullumbimby System 3 - Portable Fire Extinguisher
Mullumbimby System 3 - Power Transformer WT2.T1
Mullumbimby System 3 - Uninterruptable DC and AC Supply A
Mullumbimby System 3 - Uninterruptable DC and AC Supply B
Mullumbimby System 3 - Valve Cooling Motor Control Centre
Mullumbimby System 3 - Valve Cooling System
Mullumbimby System 3 - Valve Cooling Water Cooling Tower
Mullumbimby System 3 - Wall Bushing

## OnSite Contractors
GL Period Name | Project Name | Project No | Task Num | Expenditure Type | Expenditure Organization | Original Transaction Reference | Quantity | Cost Amount | PA Description | Vendor / Customer Name | Employee Name | MA Account | Task Name | Po Number | Revenue Accrued Amount | Revenue Bill Amount | Receipt Comments | Work Type | Expenditure Item Date | Expenditure Item Id | Transaction Source | Current Project Org | Original Project Org | DR BSV | DR CC | DR Account | DR Activity | CR BSV | CR CC | CR Account | CR Activity
2011-01-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 709757 | 2610 | 2610 | SNP Security Inv No PN29304 - Security Officer - 13th December 2010 to 20th December 2010 | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 212036 |  |  | Inv # PN29304 06.01.2011 - ok to pay as per Stuart Dodds | GENERAL OPERATIONS | 2011-01-28 | 625255 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 693599 | 8800 | 8800 | Directlink's P1 & P2 Cable Fault Repair | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 211443 |  |  | Inv # 1734 17.01.2011 - Burringbah & Stokers Siding Repair - Travel, Accommodation & Labour 5th, 13th & 14th January 2011 - ok to pay as per Stuart Dodds | GENERAL OPERATIONS | 2011-01-20 | 611880 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 700890 | 2800 | 2800 | Security D/L HV Converter Station | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 211393 |  |  | Approved Stuart Dodds | GENERAL OPERATIONS | 2011-01-24 | 615328 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 751726 | 2610 | 2610 | Directlink HV Converter Station Security Officer January 2011 | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 213892 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-14 | 669146 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 751726 | 2800 | 2800 | Directlink HV Converter Station Security Officer January 10.01-17.01.2011 | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 213892 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-14 | 669147 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 751726 | 2862 | 2862 | Directlink HV Converter Station Security Officer January 03.01-09.01.2011 | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 213892 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-14 | 669148 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 774689 | 2862 | 2862 | Security DL Converter Station Terranora Rd, Bungalora | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 214693 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-24 | 698370 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 735698 | 1160.37 | 1160.37 | Testing of HV Sticks, gloves & modiewark | TEX ONSITE PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 213241 |  |  | testing done at Mullumbimby site 02/02/2011 | GENERAL OPERATIONS | 2011-02-07 | 653379 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 746266 | 1071.42 | 1071.42 | Annual Routine Test of HV Gloves, Sticks & Portable Earth at Directlink's Bungalora Station. | TEX ONSITE PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 213833 |  |  | test well done and completed at site on 8/2 | GENERAL OPERATIONS | 2011-02-11 | 666523 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 751726 | 2199 | 2199 | Directlink A3 Call-Out Fee Year 4 Dec 2010 Claim Ref: 3600S-VDJ0006/70012953 | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 213835 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-14 | 669134 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 751726 | 5910 | 5910 | Directlink A1 Fixed Fee Monthly Claim Year 4 Dec 2010 Claim Ref: 3600S-VDJ0006/70012952 | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 213835 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-14 | 669135 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 751726 | 2199 | 2199 | Directlink A3 Call-Out Fee Year 4 Jan 2011 Claim Ref: 3600S-VDJ0006/70012953 | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 213835 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-14 | 669136 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 751726 | 5910 | 5910 | Directlink A1 Fixed Fee Monthly Claim Year 4 Jan 2011 Claim Ref: 3600S-VDJ0006/70012952 | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 213835 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-14 | 669137 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 751726 | 30597.94 | 30597.94 | Directlink Unscheduled Works Dec 2010 Claim Ref: 3600S-VDJ006/70012953 | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 213837 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-14 | 669143 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 751726 | 27518.26 | 27518.26 | Directlink Unscheduled works Jan 2011 Claim Ref: 3600S-VDJ006/70012953 | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 213838 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-14 | 669144 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 769547 | 2400 | 2400 | Directlink's P1 Cable Fault Repair | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 214428 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-22 | 692421 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 774689 | 2199 | 2199 | DLink A3 Call-Out Fee Year 4 Feb 2011 Claim Ref: 3600S-VDJ006/70012953 | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 214694 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-24 | 698373 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 774689 | 5910 | 5910 | DLink A1 Fixed Fee Monthly Claim Year 4 Feb 2011 Claim Ref: 3600S-VDJ006/70012952 | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 214694 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-02-24 | 698374 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 812113 | 1107.93 | 1107.93 | Far North Coast Perm Patrol 09.01-08.02.11 DL HV Converter Station Bungalora | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | STATION SERVICES | 216471 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-11 | 741558 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 812113 | 2610 | 2610 | Security Officer 31.01.11-07.02.11 DL HV Converter Station Bungalora | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | STATION SERVICES | 216471 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-11 | 741559 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 806857 | 2610 | 2610 | Security 14.02-21.02.11 | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 216241 |  |  | Approved S Dodds | GENERAL OPERATIONS | 2011-03-09 | 735552 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 817573 | 2610 | 2610 | Directlink HV Converter Station Security Officer | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 216766 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-14 | 743199 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 835399 | 3190 | 3190 | Directlink HV Converter Station 28.02.11 - 07.03.11 | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 217597 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-22 | 767821 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 835399 | 2886 | 2886 | Directlink HV Converter Station 21.02.11 - 28.02.11 | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 217598 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-22 | 767822 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 835399 | 1107.93 | 1107.93 | Directlink HV Converter Station Security Patrol Services for the period 09.02.11 - 08.03.11 | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 217600 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-22 | 767824 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 843223 | 1107.93 | 1107.93 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-25 | 774899 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 843223 | 3190 | 3190 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-25 | 774900 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 849007 | 1107.93 | 1107.93 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Inv S336603 25.01.2011 - ok to pay as per Stuart Dodds | GENERAL OPERATIONS | 2011-03-28 | 777421 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 854520 | 3684 | 3684 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-30 | 788333 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 854520 | 3190 | 3190 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Doddds | GENERAL OPERATIONS | 2011-03-30 | 788334 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 854520 | 1107.93 | 1107.93 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-30 | 788335 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 817573 | 7481.4 | 7481.4 | Brushcutting, Digger Excavation Work, Arb Crew, Chipper Unit | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 216833 |  |  | Approved by S. Dodds. | GENERAL OPERATIONS | 2011-03-14 | 743204 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 817573 | 17240 | 17240 | Brushcutting Clearance Maint. Contract Work | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 216834 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-14 | 743205 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 790958 | 480 | 480 | Transporting Spare CB Pole's crate from Mansfield to Bungalora | COOLANGATTA CRANES | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 215516 |  |  | completed 14/2/2011 | GENERAL OPERATIONS | 2011-03-01 | 715504 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 817573 | 2199 | 2199 | Direct Link A3 Call Out-Fee | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 216759 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-14 | 743189 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 817573 | 5910 | 5910 | Direct Link A1 Fixed Fee | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 216759 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-14 | 743190 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 817573 | 240 | 240 | Certify & Test 3 backflow valves | PETER EDWARD KENNEDY | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 216767 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-14 | 743200 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 819562 | 630 | 630 | Removal & Installation of Faulty & Good CB Pole respectively at Bungalora Pole 3 Phase B | COOLANGATTA CRANES | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 215516 |  |  | well done | GENERAL OPERATIONS | 2011-03-15 | 749038 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 819562 | 1250 | 1250 | Transporting Faulty CB Pole's crate from Bungalora to ABB's Moorebank, Sydney Plant for check/repair. | COOLANGATTA CRANES | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 215516 |  |  | well done | GENERAL OPERATIONS | 2011-03-15 | 749043 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 832779 | 11817.6 | 11817.6 | Direct Link Unscheduled Works March 2011 Claim | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 217477 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-03-21 | 760854 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 842270 | 6256 | 6256 | Pole 2 KSB Pump 1 repair | KSB AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 217605 |  |  | installed at site 24/3 after repair at their workshop | GENERAL OPERATIONS | 2011-03-24 | 770785 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-04-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 881283 | 2939 | 2939 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-04-01 | 798088 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-04-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 911401 | 3190 | 3190 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-04-13 | 828961 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-04-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 911401 | 1107.93 | 1107.93 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-04-13 | 828962 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-04-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 914115 | 3190 | 3190 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-04-14 | 830110 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-04-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 943672 | 3190 | 3190 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-04-28 | 857214 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-04-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 956007 | 3245 | 3245 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-04-27 | 869080 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-04-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 943672 | 480 | 480 | Standing Order Vegetation Maintenance | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 218026 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-04-28 | 857217 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - GENERAL | APT MANAGEMENT SERVICES PTY LIMITED | 893988 | 480 | 480 | Delivery of spare CB mechanism from Mansfield to Mullumbimby | COOLANGATTA CRANES | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 219349 |  |  | job well done! | GENERAL OPERATIONS | 2011-04-06 | 811849 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572070 | 0
2011-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 943672 | 2199 | 2199 | Standing Order S/O Directlink Callout Fee | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 218017 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-04-28 | 857211 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 943672 | 8000 | 8000 | Cable Fault Repair | JUST JOINTERS PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 221083 |  |  | works completed 21/4 Thursday | GENERAL OPERATIONS | 2011-04-28 | 857433 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 946775 | 5125 | 5125 | Directlink's Mullumbimby System 1 Phase A Circuit Breaker Trip Latch Replacement, CB functional & Timing test | ABB AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 218036 |  |  | completed | GENERAL OPERATIONS | 2011-04-29 | 860587 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-05-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 1020754 | 3190 | 3190 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-05-31 | 949472 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-05-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 964634 | 3190 | 3190 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-05-05 | 878419 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-05-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 980934 | 1107.93 | 1107.93 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-05-12 | 895821 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-05-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 980934 | 3990 | 3990 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-05-12 | 895822 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-05-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 995023 | 3666 | 3666 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-05-18 | 911894 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-05-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1017878 | 2905 | 2905 | Standing Order Vegetation Maintenance | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 218026 |  |  | Approved by S. Coomber | GENERAL OPERATIONS | 2011-05-30 | 934282 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 965130 | 20976.77 | 20976.77 | Standing Order S/O Directlink Sch Mnt | TRANSFIELD SERVICES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 218308 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-05-05 | 879007 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 966148 | 23729.21 | 23729.21 | Standing Order S/O Directlink UnScheduled Mnt | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 218016 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-05-06 | 880933 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-06-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 1077400 | 456 | 456 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-06-22 | 1010772 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1024327 | 2199 | 2199 | Standing Order S/O Directlink Callout Fee | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 218017 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-06-01 | 953242 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1024327 | 20976.77 | 20976.77 | Standing Order S/O Directlink Sch Mnt | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 218308 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-06-01 | 953244 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1056455 | 3460 | 3460 | Directlink System 3 Cable Fault Repair | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 225756 |  |  | well done! | GENERAL OPERATIONS | 2011-06-14 | 988232 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1061910 | 3990 | 3990 | Mullumbimby noise monitoring | AIR NOISE ENVIRONMENT PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 222399 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-06-16 | 993755 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1098953 | 2199 | 2199 | Standing Order S/O Directlink Callout Fee | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 218017 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-06-30 | 1040870 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1098953 | 5910 | 5910 | Standing Order S/O Directlink Sch Mnt | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 218308 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-06-30 | 1040872 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-07-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 1115219 | 5136.02 | 5136.02 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019/L1 218019/L1 |  |  |  | GENERAL OPERATIONS | 2011-06-10 | 1070587 | AP VARIANCE | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-07-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 1150698 | 3567.2 | 3567.2 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Inv #: S350926A - Email approval by Stuart Dodds 20/07/11. | GENERAL OPERATIONS | 2011-07-20 | 1098645 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1130981 | 47469.52 | 47469.52 | Standing Order S/O Directlink Sch Mnt | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 218308 |  |  | Approved by Stuart Dodds 08/07/11. | GENERAL OPERATIONS | 2011-07-12 | 1081803 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1130981 | 9709 | 9709 | HV Circuit Breaker's Pole replacement works at Directlink Pole 3, B Phase. | ABB AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 219350 |  |  | completed | GENERAL OPERATIONS | 2011-07-12 | 1081804 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1139514 | 9600 | 9600 | Directlink HVDC Cable Jointing | THYRISTORS PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 229132 |  |  | completed 14 July 2011 | GENERAL OPERATIONS | 2011-07-15 | 1087380 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1148068 | 2309 | 2309 | Standing Order S/O Directlink Callout Fee | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 218017 |  |  | Approved by Stuart Dodds 13/07/11. | GENERAL OPERATIONS | 2011-07-19 | 1096304 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1148068 | 5780 | 5780 | Delivery and installation of Directlink Cable | CIVEX PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 228708 |  |  | completed 14/7 | GENERAL OPERATIONS | 2011-07-19 | 1096495 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1172929 | 21618.41 | 21618.41 | Standing Order S/O Directlink UnScheduled Mnt | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 218016 |  |  | Inv #: 90605327 - Approved by Stuart Dodds 14/07/11. | GENERAL OPERATIONS | 2011-07-29 | 1122448 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-08-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 1201881 | 4669.11 | 4669.11 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Inv #: S354029 - Email approval by Stuart Dodds 05/08/11. | GENERAL OPERATIONS | 2011-08-09 | 1159019 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-08-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 1237370 | 4669.11 | 4669.11 | SNP SECURITY - STANDING ORDER FOR FYE 2012 - SECURITY PATROLS FOR DIRECTLINK (30264 / 516.01) | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 231976 |  |  | Inv #: S356566 - Email approval by Stuart Dodds 16/08/11. | GENERAL OPERATIONS | 2011-08-24 | 1196142 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1210093 | 2309 | 2309 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - CALL OUT SCHEDULE FEE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 231985 |  |  | Inv #: 90606947 - Approved by Stuart Dodds 08/08/11. | GENERAL OPERATIONS | 2011-08-12 | 1165221 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1216028 | 10520 | 10520 | 150m Cable P1 Negative Fault Replacement | CIVEX PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 230658 |  |  | completed | GENERAL OPERATIONS | 2011-08-15 | 1167828 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1216028 | 4880 | 4880 | Cable Laying/Pulling of approximately 170m Directlink cable at Stokers Siding, NSW | CIVEX PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232014 |  |  | completed | GENERAL OPERATIONS | 2011-08-15 | 1167836 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1218603 | 23734.76 | 23734.76 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | Inv #: 90605332 - July 2011 - Approved by Stuart Dodds 13/07/11. | GENERAL OPERATIONS | 2011-08-16 | 1174955 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1218603 | 5890 | 5890 | Directlink Cable Faults Repair at Burringbar & Stoker Siding, NSW | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232730 |  |  | well done! | GENERAL OPERATIONS | 2011-08-16 | 1175146 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1237370 | 5910 | 5910 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | Inv #: 90606945 - Approved by Stuart Dodds 16/08/11. | GENERAL OPERATIONS | 2011-08-24 | 1196152 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1237370 | 8759.66 | 8759.66 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #: 90607078 - Approved by Stuart Dodds 16/08/11. | GENERAL OPERATIONS | 2011-08-24 | 1196156 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1237370 | 67210.94 | 67210.94 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #: 90606183 - Approved by Stuart Dodds 16/08/11. | GENERAL OPERATIONS | 2011-08-24 | 1196157 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 1289623 | 4860.54 | 4860.54 | SNP SECURITY - STANDING ORDER FOR FYE 2012 - SECURITY PATROLS FOR DIRECTLINK (30264 / 516.01) | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 231976 |  |  | Inv #: S360071 - Email approval by Stuart Dodds 08/09/11. | GENERAL OPERATIONS | 2011-09-14 | 1257665 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 1303673 | 988 | 988 | SNP SECURITY - STANDING ORDER FOR FYE 2012 - SECURITY PATROLS FOR DIRECTLINK (30264 / 516.01) | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 231976 |  |  | Inv #: PN32305 - Email approval by Stuart Dodds 20/09/11. | GENERAL OPERATIONS | 2011-09-20 | 1274583 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 1305094 | 5136.02 | 5136.02 | STANDING ORDER SECURITY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 218019 |  |  | Inv #: S350926 - Needed to receipt this invoice as AP had paid this invoice - although Stuart Dodds advised NOT to pay on this invoice due to a discrepancy over the amount. | GENERAL OPERATIONS | 2011-09-21 | 1277433 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 1308376 | 988 | 988 | SNP SECURITY - STANDING ORDER FOR FYE 2012 - SECURITY PATROLS FOR DIRECTLINK (30264 / 516.01) | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 231976 |  |  | Inv #: PN32453 - Email approval by Stuart Dodds 19/09/11. | GENERAL OPERATIONS | 2011-09-22 | 1277967 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1257517 | 5293.5 | 5293.5 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #: 00002346 - Approved by Stuart Dodds 26/08/11. | GENERAL OPERATIONS | 2011-09-01 | 1217419 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1257517 | 83073.22 | 83073.22 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #: 90607544 - Approved by Stuart Dodds 26/08/11. | GENERAL OPERATIONS | 2011-09-01 | 1217425 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1275036 | 2165 | 2165 | P3 HVDC Cable Fault Repair | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 234998 |  |  | the work completed 2/09/11 as planned | GENERAL OPERATIONS | 2011-09-08 | 1241821 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1291260 | 2309 | 2309 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - CALL OUT SCHEDULE FEE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 231985 |  |  | Inv #: 90608693 - Approved by Stuart Dodds 13/09/11. | GENERAL OPERATIONS | 2011-09-15 | 1260762 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1291260 | 5910 | 5910 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | Inv #: 90608690 - Approved by Stuart Dodds 13/09/11. | GENERAL OPERATIONS | 2011-09-15 | 1260763 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1309857 | 680.14 | 680.14 | ENERGY CRANE SERVICES - STANDING ORDER FOR FYE 2012 - CRANE TRUCK HIRE - DIRECTLINK (30264 / 560.01) | ENERGY CRANE SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 236199 |  |  | Inv #: 00011523 - Approved by Stuart Coomber 29/08/11. | GENERAL OPERATIONS | 2011-09-23 | 1282457 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1309857 | 760.5 | 760.5 | ENERGY CRANE SERVICES - STANDING ORDER FOR FYE 2012 - CRANE TRUCK HIRE - DIRECTLINK (30264 / 560.01) | ENERGY CRANE SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 236199 |  |  | Inv #: 00011581 - Approved by Stuart Coomber 29/08/11. | GENERAL OPERATIONS | 2011-09-23 | 1282458 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1309857 | 1297.28 | 1297.28 | ENERGY CRANE SERVICES - STANDING ORDER FOR FYE 2012 - CRANE TRUCK HIRE - DIRECTLINK (30264 / 560.01) | ENERGY CRANE SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 236199 |  |  | Inv #: 00011617 - Approved by Stuart Coomber 29/08/11. | GENERAL OPERATIONS | 2011-09-23 | 1282459 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1309857 | 1029.14 | 1029.14 | ENERGY CRANE SERVICES - STANDING ORDER FOR FYE 2012 - CRANE TRUCK HIRE - DIRECTLINK (30264 / 560.01) | ENERGY CRANE SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 236199 |  |  | Inv #: 00011624 - Approved by Stuart Coomber 29/08/11. | GENERAL OPERATIONS | 2011-09-23 | 1282460 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1309857 | 741.14 | 741.14 | ENERGY CRANE SERVICES - STANDING ORDER FOR FYE 2012 - CRANE TRUCK HIRE - DIRECTLINK (30264 / 560.01) | ENERGY CRANE SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 236199 |  |  | Inv #: 00011680 - Approved by Stuart Coomber 29/08/11. | GENERAL OPERATIONS | 2011-09-23 | 1282461 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1309857 | 1060.64 | 1060.64 | ENERGY CRANE SERVICES - STANDING ORDER FOR FYE 2012 - CRANE TRUCK HIRE - DIRECTLINK (30264 / 560.01) | ENERGY CRANE SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 236199 |  |  | Inv #: 00011691 - Approved by Stuart Coomber 06/09/11. | GENERAL OPERATIONS | 2011-09-23 | 1282462 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-10-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1375787 | 10520 | 10520 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 232079 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-10-19 | 1366885 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-10-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1392660 | 10520 | 10520 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #: 00002385 - Approved by Stuart Coomber 21/10/11. | GENERAL OPERATIONS | 2011-10-26 | 1386136 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-10-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1392660 | 7315 | 7315 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #: 00002431 - Approved by Stuart Coomber 21/10/11. | GENERAL OPERATIONS | 2011-10-26 | 1386137 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1333211 | 62493.27 | 62493.27 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #: 90609121 - Approved by Stuart Dodds 23/09/11. | GENERAL OPERATIONS | 2011-10-03 | 1309614 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1346537 | 7320 | 7320 | Directlink's P1 & P2 Cable Fault Repair Works | NKT CABLES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 237443 |  |  | cable fault repairs were all done/completed in 26/09/11 and 30/09/11 | GENERAL OPERATIONS | 2011-10-06 | 1329646 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1375787 | 2309 | 2309 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - CALL OUT SCHEDULE FEE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 231985 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-10-19 | 1366884 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1375787 | 5910 | 5910 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | Approved by S. Dodds | GENERAL OPERATIONS | 2011-10-19 | 1366888 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1404703 | 1995 | 1995 | Mullumbimby noise monitoring | AIR NOISE ENVIRONMENT PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 222399 |  |  |  | GENERAL OPERATIONS | 2011-10-31 | 1393109 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1413648 | 7557 | 7557 | ABB Circuit Breaker Type LTB 145 SN 8544366 Investigation and Repair | ABB AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 219907 |  |  | received/stored at Bungalora Store | GENERAL OPERATIONS | 2011-11-02 | 1408656 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1413648 | 1950 | 1950 | Check/arrangement of Directlink's HVDC cable drum in Bungalora Sta. | CIVEX PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 237582 |  |  | done 19/10/2011 | GENERAL OPERATIONS | 2011-11-02 | 1408860 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1417618 | 56993.59 | 56993.59 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #: 90610857 - Approved by Stuart Dodds 31/10/11. | GENERAL OPERATIONS | 2011-11-04 | 1419478 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1424430 | 860 | 860 | JD & LF REEVE - INV #: 1078 - INV DATE: 23/08/11 - EXCAVATOR HIRE AT TERRANORA RD, NORTH TUMBULGUM | JD & LF REEVE | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 239975 |  |  | Inv #: 1078 - Approved by Stuart Coomber. | GENERAL OPERATIONS | 2011-11-07 | 1421226 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1432881 | 41.91 | 41.91 | THEARLE ELECTRICAL - INV #: 40816 - INV DATE: 30/09/11 - SEND HIPTRONICS MACHINE TO MACEYS FOR REPAIRS (30264 / 560.01) | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 239961 |  |  | Inv #: 40816 - Approved by Stuart Dodds 31/10/11. | GENERAL OPERATIONS | 2011-11-10 | 1435556 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1450041 | 2309 | 2309 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - CALL OUT SCHEDULE FEE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 231985 |  |  | Inv #: 90612051 - Approved by Stuart Dodds 11/11/11. | GENERAL OPERATIONS | 2011-11-17 | 1459102 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1450041 | 5910 | 5910 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | Inv #: 90612048 - Approved by Stuart Dodds 11/11/11. | GENERAL OPERATIONS | 2011-11-17 | 1459104 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1452906 | 1235 | 1235 | 15T Franna Hire c/w Dogman for the CB Pole replacement at Bungalora Pole 2 Q2 Ph B. | NORTH EAST CRANES | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 241216 |  |  | completed as planned date 9/11 | GENERAL OPERATIONS | 2011-11-18 | 1461947 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1469642 | 9500 | 9500 | Replacement of Leaking SF6 Gas Circuit Breaker Pole at Bungalora Pole 2 Phase B | ABB AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 239148 |  |  | completed/tested 9/11/2011 | GENERAL OPERATIONS | 2011-11-25 | 1479691 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1497236 | 3895 | 3895 | AIR NOISE ENVIRONMENT PTY LTD - INV #: I-3276 - INV DATE: 29/09/11 - ENVIRONMENTAL MAISE MONITORING AT MULLUMBIMBY (30264 / 560.01) | AIR NOISE ENVIRONMENT PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 242477 |  |  | Inv #: I-3276 - Stuart Dodds approved payment of this invoice prior to going on leave 02/12/11. | GENERAL OPERATIONS | 2011-12-05 | 1511546 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1502113 | 3717.5 | 3717.5 | Directlink Bungalora Replacement of SEL 321-1 (protection relay on 110kV CB BLA9B1) motherboard. | ESSENTIAL ENERGY | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 233392 |  |  | completed | GENERAL OPERATIONS | 2011-12-06 | 1512245 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1529185 | 2309 | 2309 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - CALL OUT SCHEDULE FEE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 231985 |  |  | Inv #: 90614094 - Approved by Francisco Reyes 15/12/11. | GENERAL OPERATIONS | 2011-12-16 | 1551069 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1529185 | 5910 | 5910 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | Inv #: 90614093 - Approved by Francisco Reyes 15/12/11. | GENERAL OPERATIONS | 2011-12-16 | 1551070 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2011-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1549132 | 1440 | 1440 | Directlink System 3 Positive Cable Fault Repair at J/B 25/26 GST Transition | NKT CABLES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 244456 |  |  | completed as planned in 19 Dec 2011 | GENERAL OPERATIONS | 2011-12-22 | 1568941 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-01-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1610399 | 3844 | 3844 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 232079 |  |  | INV #00002502 - APPROVED BY S. COOMBER | GENERAL OPERATIONS | 2012-01-17 | 1616632 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1610399 | 2309 | 2309 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - CALL OUT SCHEDULE FEE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 231985 |  |  | INV #90615325 - APPROVED BY S. DODDS | GENERAL OPERATIONS | 2012-01-17 | 1616631 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1610399 | 5910 | 5910 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | INV #90615330 - APPROVED BY S. DODDS | GENERAL OPERATIONS | 2012-01-17 | 1616636 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1610399 | 14486.98 | 14486.98 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | INV #90615334 - APPROVED BY S. DODDS | GENERAL OPERATIONS | 2012-01-17 | 1616638 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1619447 | 4320 | 4320 | Directlink P2 Positive Cable Fault Repair | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 245947 |  |  | completed 16/01/2012 | GENERAL OPERATIONS | 2012-01-20 | 1623831 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-02-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1667902 | 660 | 660 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #00002472 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-02-07 | 1675552 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-02-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1689841 | 2118 | 2118 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #00002548 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-02-15 | 1698839 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-02-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1702116 | 480 | 480 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #00002518 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-02-20 | 1705151 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1653698 | 13674.79 | 13674.79 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #90615713 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-02-02 | 1659865 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1692705 | 1820.97 | 1820.97 | Routine testing of portable earths | TEX ONSITE PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 248071 |  |  | well done 13/2/2012 | GENERAL OPERATIONS | 2012-02-16 | 1700856 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1704449 | 2050 | 2050 | Noise Monitoring - Mullumbimby Converter Station | AIR NOISE ENVIRONMENT PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 248524 |  |  | Inv #I-3348 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-02-21 | 1715543 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1710356 | 6009 | 6009 | Investigation and repair of gas leak of 1xCB Pole type LTB 145D1/B at ABB's Moorebank, Sydney Warehouse | ABB AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 248235 |  |  | repaired at Moorebank, Sydney W/H and ready for delivery at site | GENERAL OPERATIONS | 2012-02-23 | 1720185 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1710356 | 3085 | 3085 | Directlink System 1 Cable Fault Repair | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 248373 |  |  | completed 13/02/2012 | GENERAL OPERATIONS | 2012-02-23 | 1720186 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-03-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1755063 | 480 | 480 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #00002576 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-03-09 | 1767063 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-03-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1761923 | 560 | 560 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #00002590 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-03-13 | 1775567 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1728731 | 26506.07 | 26506.07 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #90617538 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-03-01 | 1742797 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1728731 | 8651.36 | 8651.36 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #90617539 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-03-01 | 1742798 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1744678 | 3405 | 3405 | Directlink Pole 1 Positive Cable Repair | NKT CABLES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 249653 |  |  | completed 3/3/12 | GENERAL OPERATIONS | 2012-03-06 | 1750012 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1745277 | 390 | 390 | Unloading of CB delivery at site Bungalora | NORTH EAST CRANES | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 249654 |  |  | unloading works completed 1/3/12 | GENERAL OPERATIONS | 2012-03-06 | 1750309 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-04-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 1819297 | 6679.4 | 6679.4 | SNP SECURITY - STANDING ORDER FOR FYE 2012 - SECURITY PATROLS FOR DIRECTLINK (30264 / 516.01) | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 231976 |  |  | Inv #S375101 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-04-03 | 1842512 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2012-04-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1848032 | 680 | 680 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #00002623 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-04-13 | 1862538 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-04-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1860654 | 720 | 720 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #00002636 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-04-19 | 1885336 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1848032 | 2309 | 2309 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - CALL OUT SCHEDULE FEE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 231985 |  |  | Inv #90616902 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-04-13 | 1862536 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1848032 | 2309 | 2309 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - CALL OUT SCHEDULE FEE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 231985 |  |  | Inv #90619095 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-04-13 | 1862537 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1848032 | 5910 | 5910 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | Inv #90616906 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-04-13 | 1862539 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1848032 | 5910 | 5910 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | Inv #90619094 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-04-13 | 1862540 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1860654 | 2309 | 2309 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - CALL OUT SCHEDULE FEE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 231985 |  |  | Inv #90620750 - Approved By S. Dodds | GENERAL OPERATIONS | 2012-04-19 | 1885335 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1860654 | 21168.06 | 21168.06 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | Inv #90620752 - Approved By S. Dodds | GENERAL OPERATIONS | 2012-04-19 | 1885337 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-05-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1899818 | 680 | 680 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #00002623 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-05-01 | 1918836 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-05-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1906106 | 3640 | 3640 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #00002651 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-05-03 | 1926610 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-05-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1974454 | 1280 | 1280 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #00002672 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-05-25 | 1985752 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1906106 | 1910.5 | 1910.5 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #90621494 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-05-03 | 1926612 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1906106 | 60198.85 | 60198.85 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #90621492 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-05-03 | 1926613 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1967637 | 2309 | 2309 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - CALL OUT SCHEDULE FEE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 231985 |  |  | Inv #90622644 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-05-23 | 1979586 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 1967637 | 21168.06 | 21168.06 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | Inv #90622640 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-05-23 | 1979589 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | R/M - PLANT / EQUIP | APT MANAGEMENT SERVICES PTY LIMITED | 1906106 | 2880 | 2880 | Cable Repair Tuesday 17 April 2012 | NKT CABLES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Repairs & Maint - Routine | PLANT AND EQUIPMENT | 254333 |  |  | Inv #00002645 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-05-03 | 1926606 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 588530 | 0
2012-06-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2079840 | 1400 | 1400 | BYRON BAY TREE SERVICES & LANDSCAPES P/L - STANDING ORDER FOR FYE 2012 - VEGETATION MAINTENANCE (30264 / 554.01) | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 232079 |  |  | Inv #00002717 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-06-25 | 2082096 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2001553 | 2050 | 2050 | Noise Monitoring - Mullumbimby Converter Station | AIR NOISE ENVIRONMENT PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 248524 |  |  | Inv #I-3565 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-06-01 | 2016199 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2084236 | 1755 | 1755 | Tweed Heads & Mullumbimby Repair as per Invoice #00090834 | NEXT GEN FIBRE & DATA NETWORKS | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 259288 |  |  | Inv #00090834 - Approved by s. Coomber | GENERAL OPERATIONS | 2012-06-26 | 2096287 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2084236 | 4650 | 4650 | Tweed Heads Repair as per Invoice #00090952 | NEXT GEN FIBRE & DATA NETWORKS | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 259288 |  |  | Inv #00090952 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-06-26 | 2096288 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-07-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2182180 | 7000 | 7000 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 262022 |  |  | Inv #00002758 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-07-24 | 2196080 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2182180 | 2309 | 2309 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - CALL OUT SCHEDULE FEE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 231985 |  |  | Inv #90626145 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-07-24 | 2195937 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2182180 | 5910 | 5910 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - SCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232084 |  |  | Inv #90626144 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-07-24 | 2195938 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2182180 | 602.26 | 602.26 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43427 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-07-24 | 2196081 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2182180 | 370 | 370 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43507 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-07-24 | 2196082 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2182180 | 1617.26 | 1617.26 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43518 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-07-24 | 2196083 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2189271 | 1925 | 1925 | Relocate 3 reactor fan cabinets | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 245291 |  |  |  | GENERAL OPERATIONS | 2012-07-26 | 2198657 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | ELECTRICAL EQUIPMENT - PARTS | APT MANAGEMENT SERVICES PTY LIMITED | 2192871 | 10450 | 10450 | Directlink sys 2. CB LTB 145D1/B SPAR repacement.As per ABB quote 12Q1503924 | ABB AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Materials | PLANT AND EQUIPMENT | 258542 |  |  |  | GENERAL OPERATIONS | 2012-07-27 | 2201245 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 586640 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2272274 | 3760 | 3760 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 262022 |  |  | Inv #00002784 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-08-20 | 2275590 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2238000 | 1063.5 | 1063.5 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43071 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-09 | 2252990 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2238000 | 1790 | 1790 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43516 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-09 | 2252991 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2238000 | 3927.5 | 3927.5 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43764 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-09 | 2252992 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2238000 | 3068.75 | 3068.75 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43766 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-09 | 2252993 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2238000 | 3157.5 | 3157.5 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43767 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-09 | 2252994 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2238000 | 703.63 | 703.63 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43887 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-09 | 2252995 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2256979 | 4050.88 | 4050.88 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43888 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-14 | 2265285 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2264289 | 4750.88 | 4750.88 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43074 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-17 | 2273127 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2264289 | 325 | 325 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43167 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-17 | 2273128 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2264289 | 14804.47 | 14804.47 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43683 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-17 | 2273129 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2264289 | 3708.38 | 3708.38 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43889 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-17 | 2273130 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2264289 | 3120 | 3120 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #44006 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-17 | 2273131 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2264289 | 2165 | 2165 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #44007 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-17 | 2273132 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2272274 | 1468.63 | 1468.63 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #90628960 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-08-20 | 2275601 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2272274 | 33665.5 | 33665.5 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #90628949 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-08-20 | 2275602 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2272274 | 52019.28 | 52019.28 | TRANSFIELD SERVICES - STANDING ORDER FOR FYE 2012 - UNSCHEDULED MAINTENANCE - DIRECTLINK (30264 / 560.01) | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 232145 |  |  | Inv #90628951 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-08-20 | 2275603 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2300811 | 427.25 | 427.25 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv 44171 27.08.12 | GENERAL OPERATIONS | 2012-08-29 | 2310536 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2300811 | 1252.69 | 1252.69 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv 43983 13.08.12 | GENERAL OPERATIONS | 2012-08-29 | 2310537 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2300811 | 480 | 480 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv 44104 20.08.12 | GENERAL OPERATIONS | 2012-08-29 | 2310538 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | ELECTRICAL EQUIPMENT - CABLES | APT MANAGEMENT SERVICES PTY LIMITED | 2238000 | 3120 | 3120 | Cable Repairs Travel & Labour | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Materials | PLANT AND EQUIPMENT | 264122 |  |  | Inv #00002858 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-08-09 | 2253179 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 586620 | 0
2012-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | R/M - PLANT / EQUIP | APT MANAGEMENT SERVICES PTY LIMITED | 2299651 | 4300 | 4300 | Repairs to fibreglass reactor dome and tubes as quoted - Inv 00010326 08.08.12 | TWEED FIBREGLASS PRODUCTS | GHANAEENEJAD, Mr. REZA | Repairs & Maint - Routine | PLANT AND EQUIPMENT | 266087 |  |  | Inv 00010326 08.08.12 | GENERAL OPERATIONS | 2012-08-28 | 2305813 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 588530 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 2323981 | 15324.4 | 15324.4 | Standing Order for Security Patrols at Directlink for 2012-2013 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 262016 |  |  | Inv #S398322 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-09-04 | 2336176 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 2344002 | 764.4 | 764.4 | Standing Order for Security Patrols at Directlink for 2012-2013 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 262016 |  |  | Inv #S400187 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-09-11 | 2358209 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 630120 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2364842 | 5120 | 5120 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | EASEMENT | 262022 |  |  | Inv 00002818 13.09.12 | GENERAL OPERATIONS | 2012-09-17 | 2365095 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2344002 | 2320 | 2320 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43072 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-09-11 | 2358214 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2344002 | 1025 | 1025 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43768 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-09-11 | 2358215 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2344002 | 4270.38 | 4270.38 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43982 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-09-11 | 2358216 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2344002 | 3009.25 | 3009.25 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #43984 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-09-11 | 2358217 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2344002 | 3261.25 | 3261.25 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #44102 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-09-11 | 2358218 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2344002 | 19006.63 | 19006.63 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #44105 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-09-11 | 2358219 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2344002 | 256.14 | 256.14 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 262025 |  |  | Inv #44349 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-09-11 | 2358220 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 572010 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2378278 | 1785 | 1785 | Lindores Construction Logistics Pty Ltd. Inv 1607. 30.07.12.Hire of 25T crane and crew on site at Terrenora Road. | LINDORES CONSTRUCTION LOGISTICS PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 268386 |  |  | Lindores Construction Logistics. Inv 1607. 30.07.12. | GENERAL OPERATIONS | 2012-09-21 | 2381836 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | OTHER MATERIALS (NOT STORES) | APT MANAGEMENT SERVICES PTY LIMITED | 2364842 | 1250 | 1250 | Make & Test 5 new 18.9m Leads | NEXT GEN FIBRE & DATA NETWORKS | GHANAEENEJAD, Mr. REZA | Materials | PLANT AND EQUIPMENT | 267386 |  |  | Inv 00090995 31.07.12 | GENERAL OPERATIONS | 2012-09-17 | 2365360 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 586800 | 0
2012-10-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 2442046 | 3985.8 | 3985.8 | Standing Order for Security Patrols at Directlink for 2012-2013 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 269422 |  |  | Inv #S400795 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-10-10 | 2442941 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 630120 | 0
2012-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2456258 | 3935 | 3935 | Standing Order for Cable Fault Repairs for 2012 - 2013 FY | NKT CABLES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 270307 |  |  | Inv #00002969 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-10-15 | 2449287 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2530566 | 460 | 460 | Air Conditioning Maintenance for Mullumbimby | COOL-A-BAH COOLING SERVICES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | BUILDING & COMPOUNDS | 272226 |  |  | Inv #22001 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-07 | 2531988 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2530566 | 770 | 770 | Air Conditioning Maintenance for Mullumbimby | COOL-A-BAH COOLING SERVICES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | BUILDING & COMPOUNDS | 272226 |  |  | Inv #22046 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-07 | 2531989 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2587878 | 1727.27 | 1727.27 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora | COOL-A-BAH COOLING SERVICES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | BUILDING & COMPOUNDS | 273540 |  |  | Inv #22122 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-26 | 2572412 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2587878 | 1445 | 1445 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora | COOL-A-BAH COOLING SERVICES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | BUILDING & COMPOUNDS | 273540 |  |  | Inv #22045 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-11-26 | 2572413 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 2570027 | 4349.8 | 4349.8 | Standing Order for Security Patrols at Directlink for 2012-2013 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 269422 |  |  | Inv #S407191 - Approved by S. Dodds | GENERAL OPERATIONS | 2012-11-20 | 2563276 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 630120 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2587878 | 6320 | 6320 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | EASEMENT | 269473 |  |  | Inv #00002880 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-26 | 2572218 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2511647 | 2712.25 | 2712.25 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44904 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-02 | 2521806 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2511647 | 5136.61 | 5136.61 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #43263 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-02 | 2521807 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2511647 | 16782.69 | 16782.69 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #45163 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-02 | 2521808 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2511647 | 347.5 | 347.5 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #45185 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-02 | 2521809 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2511647 | 2960 | 2960 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #45365 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-02 | 2521810 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2511647 | 1398.25 | 1398.25 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #45366 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-02 | 2521811 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2530566 | 5965.06 | 5965.06 | Hire of Tiper Truck, Crane and Personnel | CIVEX PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 272224 |  |  | Inv #CIV11145 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-07 | 2531984 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2530566 | 1513 | 1513 | Labour and Materials for Reactor & Platform | ARGON ALUMINUM | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 272228 |  |  | Inv #00005919 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-07 | 2531991 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2530566 | 2332 | 2332 | Labour and Materials for Reactor & Platform | ARGON ALUMINUM | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 272228 |  |  | Inv #00005918 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-07 | 2531992 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2530566 | 1446 | 1446 | Labour and Materials for Reactor & Platform | ARGON ALUMINUM | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 272228 |  |  | Inv #00005917 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-07 | 2531993 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2530566 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | GHANAEENEJAD, Mr. REZA | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #9221 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-11-07 | 2531983 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2615955 | 1650 | 1650 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 269473 |  |  | Inv #00002908 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-05 | 2621431 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2663124 | 3480 | 3480 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 269473 |  |  | Inv #00002927 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-19 | 2661648 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 350 | 350 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #43517 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637803 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 792.5 | 792.5 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44419 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637805 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 778.63 | 778.63 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44420 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637806 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 960.88 | 960.88 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44421 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637807 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 275 | 275 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44422 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637808 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 3989 | 3989 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44423 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637809 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 1922.25 | 1922.25 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44424 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637810 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 455 | 455 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44425 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637812 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 2639.56 | 2639.56 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44426 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637813 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 8427.5 | 8427.5 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44427 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637814 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 2109.5 | 2109.5 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44429 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637816 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 427.25 | 427.25 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44430 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637817 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 1106.25 | 1106.25 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44977 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637818 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 4649.75 | 4649.75 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44978 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637819 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 785 | 785 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44979 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637820 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 7328.75 | 7328.75 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #45779 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637821 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 4958.88 | 4958.88 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #45786 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637822 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2637348 | 6240 | 6240 | Standing Order for Cable Fault Repairs for 2012 - 2013 FY | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 270307 |  |  | Inv #00003123 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-11 | 2637994 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2663124 | 132 | 132 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #9594 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-19 | 2661666 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2012-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2663124 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #95879 - Approved by S. Coomber | GENERAL OPERATIONS | 2012-12-19 | 2661667 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-01-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2754117 | 1134.55 | 1134.55 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | EASEMENT | 269473 |  |  | Inv #00002961 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-01-18 | 2719073 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2721586 | 3120 | 3120 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #44428 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-01-08 | 2701050 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2721586 | 5556.09 | 5556.09 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #45154 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-01-08 | 2701051 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | ELECTRICAL EQUIPMENT - PARTS | APT MANAGEMENT SERVICES PTY LIMITED | 2754117 | 10450 | 10450 | Directlink sys 2. CB LTB 145D1/B SPAR repacement.As per ABB quote 12Q1503924 | ABB AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Materials | PLANT AND EQUIPMENT | 258542 |  |  | Inv #1261910518 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-01-18 | 2719054 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204216 | 586640 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 2862154 | 5824 | 5824 | Standing Order for Security Patrols at Directlink for 2012-2013 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 269422 |  |  | Inv #S418387 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-02-20 | 2817589 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 630120 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2832680 | 3085.5 | 3085.5 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 269473 |  |  | Inv #00002980 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-12 | 2793739 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2832680 | 2775 | 2775 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #46279 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-12 | 2793729 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2832680 | 1804.5 | 1804.5 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #46532 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-12 | 2793730 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2832680 | 1800 | 1800 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #46533 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-12 | 2793731 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2832680 | 4076.88 | 4076.88 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #46538 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-12 | 2793732 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2832680 | 3200 | 3200 | Standing Order for Cable Fault Repairs for 2012 - 2013 FY | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 270307 |  |  | Inv #00003200 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-12 | 2793747 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2853064 | 11495.37 | 11495.37 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #46166 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-18 | 2808482 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2884553 | 3149.38 | 3149.38 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #46833 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-28 | 2842224 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | FREIGHT | APT MANAGEMENT SERVICES PTY LIMITED | 2862154 | 2529 | 2529 | Transportation of Reactor from Mansfield to Eagle Farm | NQ GROUP PTY LTD | GHANAEENEJAD, Mr. REZA | Materials | PLANT AND EQUIPMENT | 279847 |  |  | Inv #36692 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-20 | 2817947 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 586680 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | FREIGHT | APT MANAGEMENT SERVICES PTY LIMITED | 2862154 | 1742 | 1742 | Transportation of Reactor from Mansfield to Eagle Farm | NQ GROUP PTY LTD | GHANAEENEJAD, Mr. REZA | Materials | PLANT AND EQUIPMENT | 279847 |  |  | Inv #36691 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-20 | 2817948 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 586680 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2832680 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #9828 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-12 | 2793756 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2853064 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #8737 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-18 | 2808502 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2853064 | 297 | 297 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #8874 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-18 | 2808503 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2853064 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #8853 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-18 | 2808504 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2853064 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #9064 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-18 | 2808505 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2853064 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #9221 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-18 | 2808506 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2853064 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #9396 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-18 | 2808507 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2884553 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #10071 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-28 | 2842236 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | TRAINING | APT MANAGEMENT SERVICES PTY LIMITED | 2832680 | 9296.34 | 9296.34 | Directlink HV Training November 12, 2012 | TRANSFIELD SERVICES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Training | PLANT AND EQUIPMENT | 278461 |  |  | Inv #90638706 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-02-12 | 2793933 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 650040 | 0
2013-03-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2923814 | 1988 | 1988 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 273540 |  |  | Inv #22942 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-03-12 | 2877919 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-03-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 2923814 | 1661.89 | 1661.89 | Standing Order for Security Patrols at Mullumbimby | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | BUILDING & COMPOUNDS | 281320 |  |  | Inv #S419732 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-03-12 | 2878254 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 2923814 | 710 | 710 | Supply of Franna to Reposition Crate at Eagle Farm | NQ GROUP PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 280987 |  |  | Inv #36804 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-03-12 | 2878133 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2948842 | 4750 | 4750 | Standing Order for Cable Fault Repairs for 2012 - 2013 FY | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 270307 |  |  | Inv #0003301 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-03-20 | 2897575 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2948842 | 434 | 434 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #8850 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-03-20 | 2897582 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-03-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 2948842 | 824 | 824 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #8851 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-03-20 | 2897583 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2997386 | 1275 | 1275 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 273540 |  |  | Inv # 22985 21.03.13 | GENERAL OPERATIONS | 2013-04-04 | 2944223 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 2997386 | 357.83 | 357.83 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 273540 |  |  | Inv # 23230 21.03.13 | GENERAL OPERATIONS | 2013-04-04 | 2944238 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 2997386 | 1661.89 | 1661.89 | Standing Order for Security Patrols at Mullumbimby | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | BUILDING & COMPOUNDS | 281320 |  |  | Inv S422937 26.03.13 | GENERAL OPERATIONS | 2013-04-04 | 2944517 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3041339 | 5915 | 5915 | Standing Order for Security Patrols at Directlink for 2012-2013 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 269422 |  |  | Inv #S424277 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-04-18 | 2982391 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 630120 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3001175 | 1200 | 1200 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 269473 |  |  | Inv # 00003020 25.04.13 | GENERAL OPERATIONS | 2013-04-05 | 2951437 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3003477 | 7792.38 | 7792.38 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv # 47442 26.03.13 | GENERAL OPERATIONS | 2013-04-05 | 2946105 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3003477 | 480 | 480 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv # 47443 26.03.13 | GENERAL OPERATIONS | 2013-04-05 | 2946106 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3003477 | 7111.75 | 7111.75 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv # 47435 26.03.13 | GENERAL OPERATIONS | 2013-04-05 | 2946107 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3041339 | 3200 | 3200 | Standing Order for Cable Fault Repairs for 2012 - 2013 FY | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 270307 |  |  | Inv #00003200 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-04-18 | 2982395 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3059387 | 7340 | 7340 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #47025 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-04-24 | 3000219 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3059387 | 3850 | 3850 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #47704 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-04-24 | 3000220 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-04-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3077095 | 3440 | 3440 | Standing Order for Cable Fault Repairs for 2012 - 2013 FY | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 270307 |  |  | Inv #00003364 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-04-30 | 3020445 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3105255 | 935 | 935 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 273540 |  |  | Inv #22986 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-05-08 | 3055290 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3105255 | 1661.89 | 1661.89 | Standing Order for Security Patrols at Mullumbimby | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | BUILDING & COMPOUNDS | 281320 |  |  | Inv #S426518 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-05-08 | 3055477 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3168661 | 2112 | 2112 | Standing Order for Security Patrols at Directlink for 2012-2013 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 269422 |  |  | Inv #PN42039 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-05-29 | 3112893 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 630120 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3130562 | 660 | 660 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 269473 |  |  | Byron Bay Tree Services & Landscapes P/L. Inv #00004016. 09.05.13. | GENERAL OPERATIONS | 2013-05-16 | 3076475 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3168661 | 1440 | 1440 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 269473 |  |  | Inv #00004047 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-05-29 | 3112895 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3168661 | 1120 | 1120 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 269473 |  |  | Inv #00004044 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-05-29 | 3112896 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3168661 | 6179.75 | 6179.75 | Load Cable Drums onto flat bed and Transport to Site | CIVEX PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 288664 |  |  | Inv #00012952 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-05-29 | 3113287 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3168661 | 29530.25 | 29530.25 | Set Drums and remove cable. Re-roll cable onto new Drum | CIVEX PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 288664 |  |  | Inv #00012953 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-05-29 | 3113288 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3168661 | 214.5 | 214.5 | Equipment Hire as per Instructions from Noel Powell | CIVEX PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 288664 |  |  | Inv #00012954 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-05-29 | 3113289 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3101854 | 1107.75 | 1107.75 | Testing Costs for Bungalora | TEX ONSITE PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 280273 |  |  | Inv #00027731 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-05-07 | 3051965 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3101854 | 997.97 | 997.97 | Testing Costs for Mullumbimby | TEX ONSITE PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 280273 |  |  | Inv #00027731 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-05-07 | 3051966 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3119977 | 1941.13 | 1941.13 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #47970 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-05-13 | 3062563 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3119977 | 25404.7 | 25404.7 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #47969 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-05-13 | 3062564 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3130562 | 3311.88 | 3311.88 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Thearle Electrical. Inv #47543. 02.04.13. | GENERAL OPERATIONS | 2013-05-16 | 3076474 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3177757 | 3850 | 3850 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #48241 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-05-31 | 3122178 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3177757 | 3850 | 3850 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #47974 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-05-31 | 3122179 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3177757 | 3850 | 3850 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #47967 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-05-31 | 3122180 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | R/M - PLANT / EQUIP | APT MANAGEMENT SERVICES PTY LIMITED | 3081103 | 990 | 990 | Supply & Install 15 off Plates to System 1 Reactor | ARGON ALUMINUM | PROCUREMENT BUYER, Mr. | Repairs & Maint - Routine | PLANT AND EQUIPMENT | 286181 |  |  | Inv #00006644 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-05-01 | 3033535 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 588530 | 0
2013-05-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 3168661 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #103402 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-05-29 | 3112905 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-06-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3192297 | 1661.89 | 1661.89 | Standing Order for Security Patrols at Mullumbimby | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | BUILDING & COMPOUNDS | 281320 |  |  | Inv #S429522 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-06-05 | 3150057 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-06-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3198546 | 4240.6 | 4240.6 | Standing Order for Security Patrols at Directlink for 2012-2013 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 269422 |  |  | Inv #S428748 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-06-06 | 3151184 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 630120 | 0
2013-06-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3244904 | 5754.25 | 5754.25 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 269473 |  |  | Inv #00004080 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-06-21 | 3191470 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-06-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3264219 | 2888 | 2888 | Standing Order for Vegetation Maintenance for 2012-2013 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 269473 |  |  | Inv #00004091 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-06-27 | 3217296 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3237798 | 23850 | 23850 | Standing Order for Cable Fault Repairs for 2012 - 2013 FY | NKT CABLES AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 270307 |  |  | Inv #00003443 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-06-19 | 3186439 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 3264219 | 824.5 | 824.5 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #103343 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-06-27 | 3217343 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 3264219 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #103186 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-06-27 | 3217350 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 3264219 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #10307 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-06-27 | 3217352 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-06-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 3268374 | 584.49 | 584.49 | Standing Order for Essential Services Monthly Contracted Charge for 2012-13 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 272223 |  |  | Inv #103600 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-06-28 | 3221841 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 670160 | 0
2013-07-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3335804 | 1582 | 1582 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Inv #23745 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-07-17 | 3293123 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-07-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3364307 | 935 | 935 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Inv #23549 - Approved by N. Powell | GENERAL OPERATIONS | 2013-07-26 | 3317456 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-07-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3379919 | 1445 | 1445 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Inv #23548 - Approved by N. Powell | GENERAL OPERATIONS | 2013-07-31 | 3344278 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-07-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3309792 | 1661.89 | 1661.89 | Standing Order for Security Patrols at Mullumbimby | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | BUILDING & COMPOUNDS | 281320 |  |  | Inv #S432437 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-07-09 | 3274629 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-07-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3379919 | 1703.44 | 1703.44 | Standing Order for Security Patrols at Mullumbimby for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 293881 |  |  | Inv #S435299 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-07-31 | 3344280 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-07-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3335804 | 2024 | 2024 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 293836 |  |  | Inv #00004121 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-07-17 | 3293122 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3309792 | 3850 | 3850 | Standing Order for Unscheduled Maintenance at Directlink for 2012-2013 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 269424 |  |  | Inv #47818 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-07-09 | 3274615 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4020 | 204255 | 572010 | 0
2013-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | R/M - PLANT / EQUIP | APT MANAGEMENT SERVICES PTY LIMITED | 3339294 | 10741 | 10741 | Inspection / Repair of 1 x LTB Circuit Breaker Pole with SF6 Gas Leak as per Quotation #13Q1810269-Rev 1 | ABB AUSTRALIA PTY LTD | PROCUREMENT BUYER, Mr. | Repairs & Maint - Routine | PLANT AND EQUIPMENT | 279284 |  |  | Inv #1361905678 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-07-18 | 3295003 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 588530 | 0
2013-07-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 3357512 | 596.94 | 596.94 | Standing Order for Essential Services Monthly Contracted Charge for 2013-14 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 293833 |  |  | Inv #103785 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-07-24 | 3312318 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 670160 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3422831 | 1335 | 1335 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Inv #22119 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-08-12 | 3371681 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3432614 | 127.5 | 127.5 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Cool-A-Bah. Inv No 23893. 05.08.13. | GENERAL OPERATIONS | 2013-08-15 | 3384454 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3461865 | 938 | 938 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Inv #23780 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-08-22 | 3401318 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3461865 | 685 | 685 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Inv #23807 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-08-22 | 3401319 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3389348 | 4950.4 | 4950.4 | Standing Order for Security Patrols at Directlink for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | JONES, BRETT | Rent & Property Outgoings | STATION SERVICES | 293851 |  |  | Inv #S435508 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-08-02 | 3348700 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3502716 | 1703.44 | 1703.44 | Standing Order for Security Patrols at Mullumbimby for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 293881 |  |  | Inv #S438141 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-08-29 | 3423664 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3465031 | 320 | 320 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 293836 |  |  | Inv #00004185 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-08-23 | 3402738 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3403348 | 2132.15 | 2132.15 | Bungalora Testing | TEX ONSITE PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295539 |  |  | Inv #00030549 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-08-06 | 3365041 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3422831 | 3756 | 3756 | Large Transfer Plates as per Quotation #19142 | ARGON ALUMINUM | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 296444 |  |  | Inv #00007046 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-08-12 | 3371826 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3461865 | 3129.33 | 3129.33 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #49254 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-08-22 | 3401328 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3461865 | 7700 | 7700 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #49381 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-08-22 | 3401329 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3461865 | 1232.5 | 1232.5 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #49511 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-08-22 | 3401330 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3461865 | 780 | 780 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #49510 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-08-22 | 3401331 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-08-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 3461865 | 596.94 | 596.94 | Standing Order for Essential Services Monthly Contracted Charge for 2013-14 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 293833 |  |  | Inv #106920 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-08-22 | 3401317 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 670160 | 0
2013-09-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3519005 | 2748.2 | 2748.2 | Standing Order for Security Patrols at Directlink for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 293851 |  |  | Inv #S437343 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-09-03 | 3448848 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-09-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3598803 | 1160 | 1160 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | JONES, BRETT | Contractors - O&M | EASEMENT | 293836 |  |  | Byron Bay Tree Services & Landscapes Pty Ltd. Inv No 00004219. 26.09.13 | GENERAL OPERATIONS | 2013-09-27 | 3503612 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3590730 | 4840 | 4840 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Thearle Electrical. Inv No 50052. 19.09.13. Approved by Stuart Coomber | GENERAL OPERATIONS | 2013-09-25 | 3501350 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3590730 | 1874.5 | 1874.5 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Thearle Electrical Inv No 50094. 20.09.13. Approved by Stuart Coomber. | GENERAL OPERATIONS | 2013-09-25 | 3501351 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 3594102 | 596.94 | 596.94 | Standing Order for Essential Services Monthly Contracted Charge for 2013-14 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 293833 |  |  | Inv # 107286 26.09.13 | GENERAL OPERATIONS | 2013-09-26 | 3502838 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 670160 | 0
2013-09-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 3594102 | 322 | 322 | Standing Order for Essential Services Monthly Contracted Charge for 2013-14 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 293833 |  |  | Inv # 107287 26.09.13 | GENERAL OPERATIONS | 2013-09-26 | 3502839 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 670160 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3663913 | 109.09 | 109.09 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Inv #24225 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-10-17 | 3568532 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3612123 | 1703.44 | 1703.44 | Standing Order for Security Patrols at Mullumbimby for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | JONES, BRETT | Rent & Property Outgoings | STATION SERVICES | 293881 |  |  | Sydney Night Patrol and Inquiry Co Pty. Ltd. Inv No S440878. 26.09.13. Approved by Stuart Dodds | GENERAL OPERATIONS | 2013-10-01 | 3524974 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3641359 | 2366 | 2366 | Standing Order for Security Patrols at Directlink for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 293851 |  |  | Inv #S441890 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-10-10 | 3551811 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3713766 | 1703.44 | 1703.44 | Standing Order for Security Patrols at Mullumbimby for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 293881 |  |  | Approved by Stuart Dodds. SNP Security. Inv No S444598. 25.10.13. | GENERAL OPERATIONS | 2013-10-30 | 3610239 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3690557 | 5323.5 | 5323.5 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 293836 |  |  | Inv #00004236 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-10-25 | 3588354 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3614235 | 4008.27 | 4008.27 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Thearle Electrical. Inv No 50292. 01.10.13.Approved by Stuart Coomber | GENERAL OPERATIONS | 2013-10-02 | 3532852 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3614235 | 22368.67 | 22368.67 | Requested By: Noel Powell - ANI Painting - Inv # 00000184 TX Paining - 30264/560.01 | ANI PAINTING CONTRACTORS | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 300842 |  |  | Inv # 00000184 01.10.2013 | GENERAL OPERATIONS | 2013-10-02 | 3532856 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3625314 | 1152.12 | 1152.12 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | JONES, BRETT | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv # 50241 30.09.13 | GENERAL OPERATIONS | 2013-10-04 | 3541263 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3663913 | 5767.5 | 5767.5 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #49777 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-10-17 | 3568544 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3663913 | 5474 | 5474 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #49778 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-10-17 | 3568545 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3663913 | 3501.87 | 3501.87 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #50385 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-10-17 | 3568546 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3663913 | 11655.25 | 11655.25 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #49830 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-10-17 | 3568547 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3713766 | 8942.5 | 8942.5 | Tx Painting - Paints & Hardware | ANI PAINTING CONTRACTORS | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 303134 |  |  | ANI Painting Contractors Pty Ltd. Inv No 00000190. 17.10.13. Approved by Noel Powell. | GENERAL OPERATIONS | 2013-10-30 | 3610407 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-10-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | SAFETY EQUIPMENT | APT MANAGEMENT SERVICES PTY LIMITED | 3676531 | 596.94 | 596.94 | Standing Order for Essential Services Monthly Contracted Charge for 2013-14 FY | HAWKINS ON FIRE | PROCUREMENT BUYER, Mr. | Other Operating Costs | PLANT AND EQUIPMENT | 293833 |  |  | Inv #107456 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-10-21 | 3571606 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 670160 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 3840351 | 1020 | 1020 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Inv #24155 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-11-25 | 3684682 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 3822834 | 3858.4 | 3858.4 | Standing Order for Security Patrols at Directlink for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 293851 |  |  | Inv #S447067 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-11-22 | 3682423 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 4414726 | 1703.44 | 1703.44 | Standing Order for Security Patrols at Mullumbimby for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 293881 |  |  | SNP Security. Inv No S447890. 25.11.13.Approved by Stuart Dodds | GENERAL OPERATIONS | 2013-11-28 | 3705446 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 4414726 | 15190.5 | 15190.5 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | EASEMENT | 293836 |  |  | Byron Bay Tree Services & Landscapes P/L. Inv No 00004263. 27.11.13. Approved by Stuart Dodds | GENERAL OPERATIONS | 2013-11-28 | 3705444 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3721434 | 1940 | 1940 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #50534 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-11-01 | 3629796 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3721434 | 1757.5 | 1757.5 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #49831 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-11-01 | 3629797 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3721434 | 4291.27 | 4291.27 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #50535 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-11-01 | 3629798 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3721434 | 7260 | 7260 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #50596 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-11-01 | 3629799 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3721434 | 5561.5 | 5561.5 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #49782 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-11-01 | 3629800 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3721434 | 5220.75 | 5220.75 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #49779 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-11-01 | 3629801 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3773696 | 2997.5 | 2997.5 | Standing Order - SAE Group - Contractors O/M - Operation Labour - Financial Year 2013/14 | SAE GROUP PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 304524 |  |  | SAE. Inv No 7429 11.09.13. Approved by Noel Powell | GENERAL OPERATIONS | 2013-11-13 | 3659216 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3773696 | 2035 | 2035 | Standing Order - SAE Group - Contractors O/M - Operation Labour - Financial Year 2013/14 | SAE GROUP PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 304524 |  |  | SAE. Invoice No 7433. 16.09.13. Approved by Noel Powell | GENERAL OPERATIONS | 2013-11-13 | 3659217 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3773696 | 2120 | 2120 | Standing Order - SAE Group - Contractors O/M - Operation Labour - Financial Year 2013/14 | SAE GROUP PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 304524 |  |  | SAE. Inv 7434. 18.09.13. Approved by Noel Powell | GENERAL OPERATIONS | 2013-11-13 | 3659218 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3840351 | 1257.5 | 1257.5 | Standing Order - SAE Group - Contractors O/M - Operation Labour - Financial Year 2013/14 | SAE GROUP PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 304524 |  |  | Inv #7731 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-11-25 | 3684635 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-11-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 3840351 | 2279.83 | 2279.83 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #50924 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-11-25 | 3684684 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-12-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 6151002 | 1530 | 1530 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Inv #INV-0048 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-12-17 | 3781054 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2013-12-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 6151002 | 1703.44 | 1703.44 | Standing Order for Security Patrols at Mullumbimby for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 293881 |  |  | Inv #S450830 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-12-17 | 3781055 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2013-12-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 5126743 | 440 | 440 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | EASEMENT | 293836 |  |  | Byron Bay Tree Services & Landscapes P/L. Inv No 00004324. 28.11.13. Approved by Stuart Dodds. | GENERAL OPERATIONS | 2013-12-03 | 3728601 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-12-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 5701408 | 15190.5 | 15190.5 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 293836 |  |  | Inv #00004263 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-12-09 | 3745961 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-12-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 5701408 | 440 | 440 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 293836 |  |  | Inv #00004324 - Approved by S. Coomber | GENERAL OPERATIONS | 2013-12-09 | 3745962 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-12-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6163935 | 1684 | 1684 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 293836 |  |  | Inv #00004361 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-12-20 | 3791478 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2013-12-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 5701408 | 4713.75 | 4713.75 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #51052 - Approved by S. Dodds | GENERAL OPERATIONS | 2013-12-09 | 3745971 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 6348904 | 708 | 708 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Inv #INV-0054 - Approved by S. Dodds | GENERAL OPERATIONS | 2014-01-29 | 3872443 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 6302409 | 2857.4 | 2857.4 | Standing Order for Security Patrols at Directlink for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | PROCUREMENT BUYER, Mr. | Rent & Property Outgoings | STATION SERVICES | 293851 |  |  | Inv #S452442 - Approved by S. Dodds | GENERAL OPERATIONS | 2014-01-20 | 3854418 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 6345557 | 1703.44 | 1703.44 | Standing Order for Security Patrols at Mullumbimby for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 293881 |  |  | Inv #S454707 - Approved by S. Dodds | GENERAL OPERATIONS | 2014-01-28 | 3870462 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6350551 | 440 | 440 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 293836 |  |  | Inv #00004385 - Approved by S. Dodds | GENERAL OPERATIONS | 2014-01-30 | 3875982 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6335467 | 3800 | 3800 | Cable Fault Repair | NKT CABLES AUSTRALIA PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 309422 |  |  | Inv #00004579 - Approved by S. Coomber | GENERAL OPERATIONS | 2014-01-24 | 3861723 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6343289 | 466.13 | 466.13 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #51171 - Approved by S. Coomber | GENERAL OPERATIONS | 2014-01-28 | 3871210 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6343289 | 370 | 370 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #51479 - Approved by S. Coomber | GENERAL OPERATIONS | 2014-01-28 | 3871211 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6343289 | 433.63 | 433.63 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #51475- Approved by S. Coomber | GENERAL OPERATIONS | 2014-01-28 | 3871212 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6343289 | 401.13 | 401.13 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #51471 - Approved by S. Coomber | GENERAL OPERATIONS | 2014-01-28 | 3871213 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6343289 | 2582.88 | 2582.88 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #51172 - Approved by S. Coomber | GENERAL OPERATIONS | 2014-01-28 | 3871214 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6343289 | 4015.48 | 4015.48 | Standing Order for Unscheduled Maintenance at Directlink for 2013-2014 FY | THEARLE ELECTRICAL | PROCUREMENT BUYER, Mr. | Contractors - O&M | PLANT AND EQUIPMENT | 295182 |  |  | Inv #51170 - Approved by S. Coomber | GENERAL OPERATIONS | 2014-01-28 | 3871215 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | R/M - PLANT / EQUIP | APT MANAGEMENT SERVICES PTY LIMITED | 6348904 | 8770.94 | 8770.94 | Testing and Repair of Dehumidifiers at Bungalora | MUNTERS PTY LTD | GHANAEENEJAD, Mr. REZA | Repairs & Maint - Routine | PLANT AND EQUIPMENT | 309883 |  |  | Inv #CD2013004727 - Approved by S. Dodds | GENERAL OPERATIONS | 2014-01-29 | 3872541 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 588530 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | R/M - PLANT / EQUIP | APT MANAGEMENT SERVICES PTY LIMITED | 6348904 | 12693.06 | 12693.06 | Testing and Repair of Dehumidifiers at Mullumbimby | MUNTERS PTY LTD | GHANAEENEJAD, Mr. REZA | Repairs & Maint - Routine | PLANT AND EQUIPMENT | 309883 |  |  | Inv #CD2013004723 - Approved by S. Dodds | GENERAL OPERATIONS | 2014-01-29 | 3872542 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 588530 | 0
2014-01-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | R/M-NON-ROUTINE MAINTENANCE | APT MANAGEMENT SERVICES PTY LIMITED | 6302409 | 1540 | 1540 | Munters to carry out annual maintenace on Mullumbimby dehumindifiers, quote No.AUSASPARO3167-001 | MUNTERS PTY LTD | PROCUREMENT BUYER, Mr. | Repairs & Maint - Non - Routine | PLANT AND EQUIPMENT | 303290 |  |  | Inv #CD2013004510 - Approved by N. Powell | GENERAL OPERATIONS | 2014-01-20 | 3854450 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572245 | 0
2014-02-01 | AOE DL FIELD SERVICES | 30264 | 512.01 BUILDING/COMPOUNDS | CONTRACTED SERVICES | APT MANAGEMENT SERVICES PTY LIMITED | 6428530 | 708 | 708 | Standing Order for Air Conditioning Maintenance at Mullumbimby & Bungalora for 2013-2014 FY | COOL-A-BAH COOLING SERVICES PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | BUILDING & COMPOUNDS | 293837 |  |  | Inv #G1381 - Approved by S. Dodds | GENERAL OPERATIONS | 2014-02-21 | 3943528 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572210 | 0
2014-02-01 | AOE DL FIELD SERVICES | 30264 | 516.01 STATION SERVICES | SECURITY | APT MANAGEMENT SERVICES PTY LIMITED | 6428530 | 4167.8 | 4167.8 | Standing Order for Security Patrols at Directlink for 2013-2014 FY | SYDNEY NIGHT PATROL AND INQUIRY CO PTY LTD | GHANAEENEJAD, Mr. REZA | Rent & Property Outgoings | STATION SERVICES | 293851 |  |  | Inv #S456418 - Approved by S. Dodds | GENERAL OPERATIONS | 2014-02-21 | 3943529 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 630120 | 0
2014-02-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6379779 | 484 | 484 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 293836 |  |  | Inv #00004407 - Approved by S. Dodds | GENERAL OPERATIONS | 2014-02-07 | 3910281 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-02-01 | AOE DL FIELD SERVICES | 30264 | 554.01 EASEMENT | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6379779 | 9596 | 9596 | Standing Order for Vegetation Maintenance for 2013-2014 FY | BYRON BAY TREE SERVICES & LANDSCAPES PTY LTD | PROCUREMENT BUYER, Mr. | Contractors - O&M | EASEMENT | 293836 |  |  | Inv #00004370 - Approved by S. Dodds | GENERAL OPERATIONS | 2014-02-07 | 3910282 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6394729 | 1563.29 | 1563.29 | Test of HV Gloves, Stick & Portable Earth as per Job Number TEX641319 | TEX ONSITE PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 310677 |  |  | Tex Onsite. Inv No 00033598. 05.02.14 Approved by Stuart Dpdds | GENERAL OPERATIONS | 2014-02-11 | 3919385 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0
2014-02-01 | AOE DL FIELD SERVICES | 30264 | 560.01 PLANT AND EQUIP | CONTRACTORS - O/M | APT MANAGEMENT SERVICES PTY LIMITED | 6428530 | 810 | 810 | Standing Order - SAE Group - Contractors O/M - Operation Labour - Financial Year 2013/14 | SAE GROUP PTY LTD | GHANAEENEJAD, Mr. REZA | Contractors - O&M | PLANT AND EQUIPMENT | 304524 |  |  | Inv #8217 - Approved by S. Dodds | GENERAL OPERATIONS | 2014-02-21 | 3943497 | PO RECEIPT | APAO (EII) DIRECTLINK - FIELD SERVICES | APAO (EII) DIRECTLINK (OLD) | 4091 | 204411 | 572010 | 0

## DL OPEX Budget
DL OPEX BUDGET
Return to Index
EII Forecast
Opex Forecast
Actual Costs
Description | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 |  | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | Comments
Materials List
Pall Filter Cartridges | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 0 | 0 | 0 | 0 | 0 | 3500 | 0 | 0 | 0 | 0 | 0 | 0
Permusoft De-ionising Resin | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0 | 800 litres required
Nitrogen - BOC | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 250 | 0 | 0 | 250 | 750 | 0 | 0 | 250 | 0 | 0 | 250
General Consumables | 4400.84 | 5001.46 | 10031.97 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 28434.27 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Total Materials | 4400.84 | 5001.46 | 10031.97 | 1000 | 1000 | 1250 | 11500 | 1000 | 1250 | 1000 | 1000 | 1250 |  | 1000 | 1000 | 1250 | 1000 | 1000 | 1250
Contractors List
Maintenance Contractors | 37851.65 | 129331.06 | 33763.06 | 44000 | 44000 | 44000 | 60000 | 60000 | 44000 | 44000 | 44000 | 44000 | 628945.77 | 44000 | 44000 | 44000 | 44000 | 44000 | 44000
Control Room Contractor (Gasnet) | 14583 | 14583 | 14583 | 14583 | 14583 | 14583 | 15500 | 15500 | 15500 | 15500 | 15500 | 15500 | 180498 | 15500 | 15500 | 15500 | 15500 | 15500 | 15500
Cable Jointing Contractor | 3800 | 15000 | 4880 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 104680 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000
Country Energy - Bungalora | 8903.99 | 6472.71 | 12000 | 24000 | 24000 | 24000 | 27000 | 27000 | 27000 | 27000 | 27000 | 27000 | 261376.7 | 27000 | 27000 | 27000 | 27000 | 27000 | 27000
Country Energy - Mullumbimby | 5642.51 | 11976.15 | 12000 | 24000 | 24000 | 24000 | 27000 | 27000 | 27000 | 27000 | 27000 | 27000 | 263618.66 | 27000 | 27000 | 27000 | 27000 | 27000 | 27000
Country Energy - House Services | 581.14 | 2773.33 | 600 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 12954.47 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Cable Easement Maintenance | 0 | 14080 | 694 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 104774 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000
Hot Stick & earth Lead Testing | 0 | 1563.29 | 0 | 0 | 0 | 0 | 0 | 2400 | 0 | 0 | 0 | 0 | 3963.29 | 0 | 2400 | 0 | 0 | 0 | 0
Vermin Control | 0 | 0 | 0 | 2000 | 0 | 0 | 2000 | 0 | 0 | 2000 | 0 | 0 | 6000 | 2000 | 0 | 0 | 2000 | 0 | 0
Station Grounds Maintenance | 0 | 0 | 0 | 1000 | 1000 | 0 | 2000 | 2000 | 0 | 1000 | 0 | 1000 | 8000 | 0 | 2000 | 0 | 1000 | 0 | 1000
Bungalora Backflow Device Testing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | Annual Mtce
Telstra - WAN Data & Internet | 7703.14 | 678 | 7095.82 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 46976.96 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500
Landline & Mobile Comms | 271.88 | 53.63 | 487.02 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 4592.53 | 420 | 420 | 420 | 420 | 420 | 402
DBYD Charges | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0
X-Info Landholder Database | 0 | 0 | 6400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6400 | 0 | 0 | 6400 | 0 | 0 | 0
Richmond Waste Rubbish Collection Service | 79.65 | 260.01 | 63.72 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1393.38 | 110 | 110 | 110 | 110 | 110 | 110
Meter Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
Recipient Training | 0 | 0 | 1032 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 0 | 5000 | 16032 | 0 | 0 | 10000 | 0 | 0 | 5000
Portaloo Hire | 250 | 200 | 200 | 200 | 200 | 200 | 400 | 400 | 400 | 400 | 400 | 400 | 3650 | 400 | 400 | 400 | 400 | 400 | 400
Consultants & Regulatory Audits | 0 | 0 | 10300 | 0 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 20300 | 0 | 0 | 0 | 0 | 0 | 0
Security Patrols | 4560.84 | 5871.24 | 3000 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 45832.08 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
Security Alarm Monitoring | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 1200 | 200 | 200 | 200 | 200 | 200 | 200
Fire System Checks | 0 | 0 | 2266.32 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 7756.32 | 610 | 610 | 610 | 610 | 610 | 610
Platform Hire | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 0 | 0 | 0 | 0 | 0 | 5000 | 0 | 0 | 0 | 0 | 0 | 0
Legal Fees | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0
Software Licences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Contractors | 84227.8 | 202842.42 | 109364.94 | 138023 | 136023 | 135023 | 187840 | 162740 | 152340 | 145340 | 142640 | 148340 | 1744744.16 | 145340 | 146740 | 158740 | 145340 | 142340 | 148322
Travel | 762.53 | 2130.53 | 5073.36 | 4500 | 1500 | 3000 | 3000 | 6000 | 4500 | 3000 | 8490 | 4500 | 46456.42 | 4500 | 8490 | 7500 | 3000 | 3000 | 4500
Timesheet Allocations | 2014-01-01: 33111.22; 2014-02-01: 28909.8; 2014-03-01: 30000 | 92021.02
HCC Allocation | 16236.34 | 26498.1 | 15000 | 35000 | 35000 | 35000 | 56154.8767 | 54769.39 | 54773.89 | 53693.233 | 55486.8281 | 52563.0189 | 490175.6767 | 52258.3569 | 55128.109 | 55491.3281 | 54769.39 | 55711.8281 | 56208.7661
Total O&M | 138738.73 | 265382.31 | 169470.27 | 178523 | 173523 | 174273 | 258494.8767 | 224509.39 | 212863.89 | 203033.233 | 207616.8281 | 206653.0189 | 2413081.5467 | 203098.3569 | 211358.109 | 222981.3281 | 204109.39 | 202051.8281 | 210280.7661
OpEx O&M | 138738.73 | 265382.31 | 169470.27 | 178523 | 173523 | 174273 | 258494.8767 | 224509.39 | 212863.89 | 203033.233 | 207616.8281 | 206653.0189 | 2373397.2767 | 203098.3569 | 211358.109 | 222981.3281 | 204109.39 | 202051.8281 | 210280.7661

## Schematics
SCHEMATICS
Return to Index
End-to-End Line Diagram
This is the only diagram showing the difference between the two sites (WT area at Bungalora)
Bungalora
Mullumbimby

## Components in Schematic
COMPONENTS IN SCHEMATIC
Return to Index
Analysis of the Single Line Diagram
Total
.WT
| WT.L1 | 6 | AC Reactor | 3 separate reactors for each phase (L1, L2, L3) |  | DL-WI-29 |  | S1, S2
| WT.L2 | 6 | AC Reactor | 3 separate reactors for each phase (L1, L2, L3)
| WT.L3 | 6 | AC Reactor | 3 separate reactors for each phase (L1, L2, L3)
| WT.C1 | 6 | AC Capacitor
| WT.C2 | 6 | AC Capacitor
| WT.Z1 | 12 | AC Tuning Circuit
| WT.Q1 | 1 | AC Disconnector (Bungalora Only)
| WT.Q11 | 1 | AC Circuit Breaker (Bungalora Only)
.WT1 |  |  | P1, P2, P3 | Each is three phase |  | Monthly
| WT1.Q11 | 6 | AC Disconnector | 3 contacts, manual operation |  | DL-WI-17
| WT1.Q1 | 6 | AC Circuit Breaker | 3 contacts, 3 mechanisms |  |  |  | S1, S2
| WT1.Q2 | 6 | AC Bypass breaker | 3 contacts, 1 mechanism
| WT1.R1 | 18 | AC Resistor
.WT2 |  |  | P1, P2, P3
| WT2.F1 | 18 | AC Surge Arrestor
| WT2.F2 | 6 | AC Surge Arrestor
| WT2.T1 | 6 | Power Transformer
| ? | 12 | Current Transformers (integrated) |  | One on each phase
| ? | 6 | Cable End
.WA.Z1 |  |  | P1, P2, P3 |  |  |  |  | S1, S2
| WA.Z1.Q21 | 18 | AC Earth Switch?
| WA.Z1.F1 | 18 | AC Surge Arrestor
| WA.Z1.T11 | 18 | Capacitive Voltage Transformer
| WA.Z1.C1 | 18 | AC Capacitor
| WA.Z1.C2 | 18 | AC Capacitor
| WA.Z1.L1 | 18 | AC Reactor
| WA.Z1.T1 | 18 | Hall Effect Current Transformer
| WA.Z1.T2 | 18 | Hall Effect Current Transformer
.WA.Z1.Z11 | [6 empty] | S1, S2 | P1, P2, P3
| WA.Z1.Z11.C1 | 18 | AC Capacitor
| WA.Z1.Z11.R1 | 18 | AC Resistor
| WA.Z1.Z11.L1 | 18 | AC Reactor
| WA.Z1.Z11.T1 | 18 | Outdoor Post Type Current Transformer
.WA.Z1.Z12
| WA.Z1.Z12.C1 | 18 | AC Capacitor
| WA.Z1.Z12.R1 | 18 | AC Resistor
| WA.Z1.Z12.L1 | 18 | AC Reactor
| WA.Z1.Z12.T1 | 18 | Outdoor Post Type Current Transformer
.U |  |  | P1, P2, P3
| U.L1 | 18 | AC Reactor
| U.X1 | 18 | Insulated Wall Bushing
| U.C1 | 6 | DC Capacitor
| U.C2 | 6 | DC Capacitor
| U.L2 | 6 | DC Reactor
| U.T1 | 6 | Outdoor Post Type Current Transformer
| U.F11 | 6 | Air Gap Surge Limiter
.VA, .VB, .VC
| U.Vx.C1 | 18 | DC Capacitor
| U.Vx.C2 | 18 | DC Capacitor
| U.Vx.T1 | 18 | Rogowski Current Transformer
| U.Vx.T2 | 18 | Rogowski Current Transformer
| U.Vx.T3 | 18 | Rogowski Current Transformer
| U.Vx.V1 | 18 | IGBT Stack
| U.Vx.V2 | 18 | IGBT Stack
.WP1 and .WP2
| WPx.U1 | 12 | DC Voltage Divider
| WPx.L1 | 12 | DC Reactor
| WPx.C1 | 12 | DC Capacitor
| WPx.F1 | 12 | Arrester
| WPx.Q11 | 12 | DC Disconnector |  | M = Manual?
| WPx.Q21 | 12 | DC Earth Switch |  | M = Manual?
| WPx.T11 | 12 | Hall Effect Current Transducer |  | DL-WI-31
| WPx.T12 | 12 | Hall Effect Current Transducer |  | DL-WI-31
.R1
| R1.F1 | 6 | DC Cable Screen Arrestor
| R1.F2 | 6 | DC Cable Screen Arrestor
| R1.T11 | 6 | Cable Screen Current Transformer
| R1.T12 | 6 | Cable Screen Current Transformer
| R1.T21 | 6 | Cable Screen Current Transformer
| R1.T22 | 6 | Cable Screen Current Transformer
| R1.L1 | 6 | DC Zero sequence smoothing reactor |  | DL-WI-46
|  | 24 | Connections to cable screens

## Grouped Components
GROUPED COMPONENTS
Return to Index
Grouping the components from the Single Line Diagram
AC Bypass breaker |  | 6 | AC Capacitor |  | 84 |  | AC Resistor |  | 54 | AC Reactor |  | 90
| WT1.Q2 | 6 |  | WT.C1 | 6 |  |  | WT1.R1 | 18 |  | WT.L1 | 6
|  |  |  | WT.C2 | 6 |  |  | WA.Z1.Z11.R1 | 18 |  | WT.L2 | 6
AC Circuit Breaker |  | 7 |  | WA.Z1.C1 | 18 |  |  | WA.Z1.Z12.R1 | 18 |  | WT.L3 | 6
| WT1.Q1 | 6 |  | WA.Z1.C2 | 18 | [5 empty] | WA.Z1.L1 | 18
| WT.Q11 | 1 |  | WA.Z1.Z11.C1 | 18 | [5 empty] | WA.Z1.Z11.L1 | 18
|  |  |  | WA.Z1.Z12.C1 | 18 | [5 empty] | WA.Z1.Z12.L1 | 18
AC Disconnector |  | 7 | [8 empty] | U.L1 | 18
| WT1.Q11 | 6 | DC Capacitor |  | 60
| WT.Q1 | 1 |  | U.C1 | 6 |  |  |  |  | DC Reactor |  | 18
|  |  |  | U.C2 | 6 | [5 empty] | U.L2 | 6
AC Earth Switch |  | 18 |  | U.Vx.C1 | 18 | [5 empty] | WP1.L1 | 6
| WA.Z1.Q21 | 18 |  | U.Vx.C2 | 18 | [5 empty] | WP2.L1 | 6
|  |  |  | WPx.C1 | 12
DC Disconnector |  | 12 | [7 empty] | DC Zero sequence smoothing reactor
| WP1.Q11 | 6 | [8 empty] | R1.L1 | 6
| WP2.Q11 | 6 | Connections to Cable Screen
|  |  |  | ? | 24
DC Earth Switch |  | 12
| WP1.Q21 | 6
| WP2.Q21 | 6
Zinc Oxide Surge Arrestors
[7 empty] | AC Surge Arrestor |  | 42
Cable Screen Current Transformer |  | 24 | AC Tuning Circuit |  |  |  |  | WT2.F1 | 18 | Insulated Wall Bushing |  | 18
| R1.T11 | 6 |  | WT.Z1 | 12 |  |  | WT2.F2 | 6 |  | U.X1 | 18
| R1.T12 | 6 | [5 empty] | WA.Z1.F1 | 18
| R1.T21 | 6
| R1.T22 | 6 |  |  |  |  | DC Surge Arrester
|  |  | DC Voltage Divider |  | 12 |  |  | WP1.F1 | 6 | IGBT Stack |  | 36
Hall Effect Current Transducer |  | 60 |  | WPx.U1 | 12 |  |  | WP2.F1 | 6 |  | U.Vx.V1 | 18
| WPx.T11 | 12 | [8 empty] | U.Vx.V2 | 18
| WPx.T12 | 12 |  |  |  |  | DC Cable Screen Arrestor |  | 12
| WA.Z1.T1 | 18 | [5 empty] | R1.F1 | 6
| WA.Z1.T2 | 18 | [5 empty] | R1.F2 | 6
Capacitive Voltage Transformer
Outdoor Post Type Current Transformer |  | 42 |  | WA.Z1.T11 | 18
| WA.Z1.Z11.T1 | 18 |  | WT.T11 | 1 |  | Air Gap Surge Limiter
| WA.Z1.Z12.T1 | 18 | [5 empty] | U.F11 | 6
| U.T1 | 6 | Power Transformer |  | 6
|  |  |  | WT2.T1 | 7 | including Spare
Rogowski Current Transformer |  | 54 |  | ? | 12 | Integrated Current Transformer
| U.Vx.T1 | 18
| U.Vx.T2 | 18
| U.Vx.T3 | 18

## ABB Maintenance
ABB MAINTENANCE
Return to Index
Item | Description | TD | Time Between Maintenance (years) | Crew | Duration | Energised item/converter/system | Document | Remarks
P(1,2,3)-U VALVE ENCLOSURE
P(1,2,3)-U-V(A,B,C)-V(1,2) | IGBT valve stacks | TD-001 | 1 | PV,2PG | 9 | no/no/yes | 1JNL100033-472 Rev 00 | Electrical check Inspection
P(1,2,3)-U-L1 | Converter Reactors | TD-003 | 1-2 | PG | 1,5 | no/no/yes | 11.98 Rev 00 | Inspection Fans
P(1,2,3)-U-L2 | Filter Reactor | TD-024 | 1-2 | PE,PG | 1,5 | no/no/yes | MI-99.01.0163 | Inspection
P(1,2,3)-U-T1 | Filter CT | TD-076 | 1-2 | PE | ½ | no/no/yes |  | Inspection
P(1,2,3)-U-X1 | Wall Bushing (pole bus) | TD-009 | 1-2 | PE | 1 | no/no/yes | 2770 501E-8 | Inspection
P(1,2,3)-U-V(A,B,C)-C(1,2) | DC Capacitor | TD-014 | 1-2 | PE | 3 | no/no/yes | SECAP B-003/TD-HLA-011 | Inspection
|  |  |  | 3PE, 2PG | 3 | no/no/yes | SECAP B-003/TD-HLA-011 | Capacitance measurement
P(1,2,3)-U-C(1,2) | DC Capacitor | TD-014 | 1-2 | PE | 3 | no/no/yes | SECAP B-003/TD-HLA-011 | Inspection
|  |  | 3 | PE, 2PG | 3 | no/no/yes | SECAP B-003/TD-HLA-011 | Capacitance measurement
P(1,2,3)-U-V(A,B,C)-T(1,2,3) | Direct Current Measuring Device (Rogowski) | TD-074 | 1-2 | PE | 1 | no/no/yes | Power Electronic Measurements | Inspection
P(1,2,3)-WP POLE BUS
P(1,2,3)-WP(1,2)-L1 | DC Smoothing Reactor | TD-005 | 1-2 | PE, PG | 3 | no/no/yes | MI-99.01.0163 | Inspection
P(1,2,3)-WP(1,2)-C1 | DC Capacitor | TD-014 | 1-2 | PE | 3 | no/no/yes | SECAP B-003/TD-HLA-011 | Inspection
|  |  | 3 | PE, 2PG | 3 | no/no/yes | SECAP B-003/TD-HLA-011 | Capacitance measurement
P(1,2,3)-WP(1,2)-F1 | Arrester | TD-044 | 1-2 | PE | ½ | no/no/yes | XL 300 021-242 | Inspection
P(1,2,3)-WP(1,2)-Q11 | DC Disconnecter | TD-058 | 1-2 | PE | ¼ | no/no/yes |  | Inspection
|  |  | 3 | PB, PG | 1 | no/no/yes | 5275 826E-23 | Motor drive mechanism
|  |  | 5 | PB, PG | 2 | no/no/yes | 5309 868E-1 | Switch
P(1,2,3)-WP(1,2)-Q21 | DC Earthing Switch | TD-058 | 1-2 | PE | ¼ | no/no/yes |  | Inspection
|  |  | 3 | PB, PG | 1 | no/no/yes | 5275 826E-23 | Motor drive mechanism
|  |  | 5 | PB, PG | 2 | no/no/yes | 5309 868E-1 | Switch
P(1,2,3)-WP(1,2)-T(11,12) | DC Measuring Device | TD-074 | 1-2 | PE | 1 | no/no/yes | LB 2000-S/SP5 | Inspection
P(1,2,3)-WP(1,2)-U1 | Direct Voltage Divider | TD-075 | 1-2 | PE, PG | 1 | no/no/yes | F9837_1.DOC | Inspection
P(1,2,3)-R1
P(1,2,3)-R1-L1 | DC Zero Sequence Smoothing Reactor | TD-005 | 1-2 | PE | ½ | no/no/yes |  | Inspection
P(1,2,3)-R1-F(1,2) | Metallic Screen Arrester | TD-044 | 1-2 | PE | ½ | no/no/yes | HAAR 490 800 | Inspection
P(1,2,3)-R1-T(1,2) | DC Cable Screen Current Transformer | TD-076 | 1-2 | PE | ½ | no/no/yes |  | Inspection
P(1,2,3)-WA-Z1 AC FILTER BANK
P(1,2,3)-WA-Z1-Z11-C1 | AC Filter Capacitor | HP39 TD-011 | 1 | PE,PG | 3 | no/no/yes | SECAP B-003/TD-HLA-011 | Inspection
|  |  | 3 | PE,PG | 5 | no/no/yes | SECAP B-003/TD-HLA-011 | Capacitance measurement
P(1,2,3)-WA-Z1-Z12-C1 | AC Filter Capacitor | HP78 TD-011 | 1 | PE,PG | 3 | no/no/yes | SECAP B-003/TD-HLA-011 | Inspection
|  |  | 3 | PE,PG | 5 | no/no/yes | SECAP B-003/TD-HLA-011 | Capacitance measurement
P(1,2,3)-WA-Z1-C1 | AC PLC Noise Capacitor | TD-015 | 1-2 | PG | 1 | no/no/yes | 1HSE 96001-1E | Inspection
P(1,2,3)-WA-Z1-C2 | AC PLC Noise Capacitor | TD-015 | 1-2 | PG | 1 | no/no/yes | 1HSE 96001-1E | Inspection
P(1,2,3)-WA-Z1-Z11-L1 | AC Filter Reactor | HP39 TD-021 | 1-2 | PE,PG | 1 | no/no/yes | MI-99.01.0162 | Inspection
P(1,2,3)-WA-Z1-Z12-L1 | AC Filter Reactor HP78 | TD-021 | 1-2 | PE, PG | 1 | no/no/yes | MI-99.01.0162 | Inspection
P(1,2,3)-WA-Z1-L1 AC | PLC Noise Filter Reactor | TD-025 | 1-2 | PE, PG | 1 | no/no/yes | MI-99.01.0199 | Inspection
P(1,2,3)-WA-Z1-Z11-R1 | AC Filter Resistor | HP39 TD-031 | 2 | PG | 1 | no/no/yes | F9535_1.DOC | Inspection
P(1,2,3)-WA-Z1-Z12-R1 | AC Filter Resistor | HP78 TD-031 | 2 | PG | 1 | no/no/yes | F9535_1.DOC | Inspection
P(1,2,3)-WA-Z1-Z11-T1 | AC Filter Current Transformer | TD-072 | 1-2 | PE | 1 | no/no/yes | EKM Mm-0001.98 | Inspection
P(1,2,3)-WA-Z1-Z12-T1 | AC Filter Current Transformer | TD-072 | 1-2 | PE | 1 | no/no/yes | EKM Mm-0001.98 | Inspection
P(1,2,3)-WA-Z1-F1 | AC Filter Bus Arrester | TD-042 | 1-2 | PE | ½ | no/no/yes | XL 300 021-243 | Inspection
P(1,2,3)-WA-Z1-Q21 | AC Earthing Switch | TD-052 | 1-2 | PE | ½ | no/no/yes |  | Inspection
|  |  | 3 | PB, PG | 1 | no/no/yes | 5275 826E-24 | Manual drive mechanism
|  |  | 5 | PB, PG | 4 | no/no/yes | 5309 868E-2 | Switch
P(1,2,3)-WA-Z1-T(1,2) | AC Current Transformer (LEM) | TD-071 | 1-2 | PE | 1 | no/no/yes | LB 2000-S/SP5 | Inspection
P(1,2,3)-WA-Z1-T11 | Voltage Transformer | TD-077 | 1-2 | PE | 1 | no/no/yes | EKH WB-15.97 | Inspection
P(1,2,3)-WT(1,2) AC BUS
P(1,2,3)-WT2-T1 | Power Transformer | TD-002 | 1/12 | PE, PG | 2 | yes/yes/yes | 000 169 568 MI | Inspection (oil etc)
|  |  | 1/4 | PE, PG | 2 | yes/yes/yes | 000 169 568 MI | Inspection (oil etc)
|  |  | 1 | PE, PX | 5 | no/no/yes | 000 169 568 MI | Insulating oil
|  |  | 1 | PX, PE | 5 | no/no/yes | 000 169 568 MI | Bushings Insulation resistance measurements
|  |  | 1 | PX, PG | 10 | no/no/yes | 000 169 568 MI | Transformer overhaul
P(1,2,3)-WT2-F1 | AC Bus Arrester | TD-042 | 1-2 | PE,PG | 1 | no/no/yes | XL 300 021-242 | Inspection
P(1,2,3)-WT2-F2 | Power Transformer Neutral Arrester | TD-042 | 1-2 | PE,PG | 1 | no/no/yes | XL 300 021-242 | Inspection
P(1,2,3)-WT1-Q(1,2) | AC Circuit Breaker (3 ph) | TD-051 | 1-2(3) | PE, PG | 4 | no/no/yes | 1HSB425409-100en0 | Inspection
|  |  | ? | PB, PG | 6 | no/no/yes | 1HSB425409-100en0 | Greasing
|  |  | 6 (4) | PE, PG | 1 | yes/yes/yes | 1HSB425409-100en0 | Thermo vision measurements
|  |  | 15 (1) | 2PB, 3PG | 24 | no/no/yes | 1HSB425409-100en0 | Preventative maintenance
|  |  | 30 (2) | 2PB, 3PG | 24 | no/no/yes | 1HSB425409-100en0 | Overhaul
P(1,2,3)-WT1-Q11 | AC Disconnector (3 ph) | TD-052 | 1-2 | PE | ½ | no/no/yes | 5309 869E-1 | Inspection
|  |  | 3 | PB, PG | 1 | no/no/yes | 5309 869E-1 | Switch
|  |  | 5 | PB, PG | 4 | no/no/yes | 5275 826-24 en rev0 | Hand-operated device
WT PLC FILTER
WT-C(1,2) | AC PLC Noise Capacitor | TD-015 | 1-2 | PE,PG | 3 | no/no/no | SECAP B-003/TD-HLA-011 | Inspection
|  |  | 3 | PE,PG | 5 | no/no/no | SECAP B-003/TD-HLA-011 | Capacitance measurement
WT-L(1,2,3) | AC PLC Noise Filter Reactor | TD-025 | 1-2 | PE, PG | 1 | no/no/no | MI-99.01.0200 | Inspection
WT-Z(1,2) | AC PLC Filter Capacitor Tuning Unit | TD-091 | 1-2 | PE | ½ | no/no/no | HENF600012 | Inspection
VALVE COOLING SYSTEM |  | TD-302 |  |  |  | 8-5599-203 (Swede Water)
|  |  | 1/52 | PM | 1 | yes/yes/yes | 8-5599-203 | System check, Water leakage, Noise
|  |  | 1/12 | PM, PG | 2 | yes/yes/yes | Item 5 “Installation & Start up Manual” | Oxygen measurement
|  |  | 1/4 | PM, PG | 3 | yes/yes/yes | 8-1000-150/E | Main pumps
|  |  | 1/4 | PM, PG | 3 | yes/yes/yes | Item 2.4 & 2.5 “Operation Manual” | Expansion vessel (C1)
|  |  | 1/4 | PM, PG | 1 | yes/yes/yes | See “Cooler” | Air blast coolers
|  |  | 1 | PM, PG | 4 | yes/yes/yes | 8-1000-182/E | Pump motors, Bearings
|  |  | 1 | PM, PG | 3 | yes/yes/yes | 8-1000-104/E | Safety valve
|  |  | 1 | PM, PG | 4 | yes/yes/yes | 8-1000-087/E | Filter
|  |  | 3 | PM, PG | 5 | yes/yes/yes | 8-9900-002 | Ion-exchange vessel
|  |  | 3 | PM, PG | 5 | yes/yes/yes | 8-1000-016/E | Main strainer
|  |  | 1 | PM, PG | 5 | yes/yes/yes | 8-1000-208/E | Conductivity meter
FIRING PROTECTION SYSTEM |  |  | 1/12 | PE | 1 | yes/yes/yes | WFS-NTF-6B2202 | Power supply
|  |  | 1 | PE | 1 | yes/yes/yes |  | Air flow filter
|  |  | 1 | PE | 3 | yes/yes/yes |  | Piping cleaning
|  |  | 1 | PE | 3 | yes/yes/yes |  | Smoke test
AIR CONDITION UNITS |  |  | 1/12 | PE | 1 | yes/yes/yes |  | Inspection
DEHUMIDIFIERS |  |  | 1/12 | PE | 1 | yes/yes/yes |  | Inspection
UPS-SYSTEM |  |  | 1 | PE | 1 | yes/yes/yes |  | Inspection
CW FAN SILENCERS |  |  | 1 | PG | 3 | yes/yes/yes |  | Cleaning
CONVERTER STATION |  |  | 1/52 | PE | ½ | yes/yes/yes |  | General inspection of the whole station
Key
PC | Control Specialist | A PC is a specialist that has been trained by ABB (or ABB´s subsuppliers) to such a level of competence that the PC can, without any supervision or guidance, take charge of maintenance of the control equipment.
PB | Breaker Specialist | A PB is a specialist that has been trained by ABB (or ABB´s subsuppliers) to such a level of competence that the PB can, without any supervision or guidance, take charge of maintenance of breakers and disconnectors.
PX | Transformer Specialist | A PX is a specialist that has been trained by ABB (or ABB´s subsuppliers) to such a level of competence that the PX can, without any supervision or guidance, take charge of maintenance of power transformers.
PV | Valve Specialist | A PV is a specialist that has been trained by ABB (or ABB´s subsuppliers) to such a level of competence that the PV can, without any supervision or guidance, take charge of maintenance of the converter equipment
PM | Mechanic | A PM is a person who is able to perform advanced mechanical work with the guidance of drawings and written instructions.
PE | Electrician | A PE is a person who is able to perform advanced electrical work with the guidance of drawings and written instructions.
PG | Helper | A helper is a person who can perform work under the direct guidance of a mechanic, an electrician or a specialist.

## Byron Bay Trees
BYRON BAY TREES
Return to Index
Invoices for Bryon Bay Trees
Discussion
Vegetation Management and Yard Maintenance are both undertaken by Bryon Bay Trees
Vegetation Management occurs along the cable route - which follows a railway corridor
The railway line was closed in 2003 and Directlink is finding each year they need to do more vegetation management
The following analysis attempts to estimate what is required
Byron Bay Trees 2013 |  | hours | cost (including GST) | comments
4407 | 2014-02-06 | 5.5 | 532.4
4385 | 2014-01-30 | 5 | 484 | Bungalora station
4370 | 2014-01-30 | 124.5 | 10555.6 | Invoice shows incorrect rate for 4 man crew
4361 | 2013-12-19 | 20.5 | 1852.4
4355 | 2014-01-09 | 106 | 8727.4
4324 | 2013-11-28 | 5 | 484 | Bungalora station
4263 | 2013-11-27 | 196.75 | 16709.55
4236 | 2013-10-24 | 68.25 | 5855.85
4219 | 2013-09-26 | 14.5 | 1276 | Bungalora Station "No photos since Luke onsite"
4185 | 2013-08-22 | 4 | 352 | Bungalora Station
4121 | 2013-07-10 | 24 | 1883.2 | Excluding Chipper $343.2
4091 | 2013-06-13 | 32 | 2855.6 | Bungalora and Mullumbimby stations (excluding chipper hire)
4080 | 2013-06-06 | 44.75 | 6329.68
4047 | 2013-05-21 | 18 | 1584
4040 | 2013-05-21 | 14 | 1232
4016 | 2013-05-09 | 7.5 | 726 | Bungalora Station
3020 | 2013-03-26 | 19.5 | 1716 | Adjusting for 4 hours which was not charged
2980 | 2013-02-05 | 42.25 | 3394.05
12 months |  | 746.5 | 60015.7545 | Excluding GST
FY13/14 (7 months) |  |  | 49055.6 |  | (includes the chipper charge)
Projection FY13/14 |  |  | 84095.3143 | p.a. | For most of this period Directlink was not operational - hence does not include clearing required for cable faults
|  |  | 3000 | p.a. | Additional amount required for clearing for cable faults
Cost of Vegetation Management |  |  | 87095.3143 | p.a. | In reference year (2014)
Byron Bay Trees Aug 2011 - July 2012 |  |  | Including GST
2346 | 2011-08-18 |  | 5822.85
2385 | 2011-09-28 |  | 11572
2431 | 2011-10-18 |  | 8046.5 | Extra clearing due to line fault
2472 | 2011-12-08 |  | 726
2502 | 2011-12-15 |  | 4228.4
2518 | 2012-01-19 |  | 528 | Clearing for line fault
2548 | 2012-02-14 |  | 2329.8
2576 | 2012-03-06 |  | 528 | Clearing for line fault
2590 | 2012-03-13 |  | 616
2623 | 2012-04-12 |  | 748 | Includes clearing for a fault
2636 | 2012-04-19 |  | 792
2651 | 2012-05-01 |  | 4004
2672 | 2012-05-22 |  | 1408
2717 | 2012-06-19 |  | 1540
2758 | 2012-07-19 |  | 7700
12 months |  |  | 45990.5 | Excluding GST

## Electricity Invoices
ELECTRICITY INVOICES
Return to Index
Analysis of Electricity Use
Electricity use at the converter stations appears to depend on the number of converter stations which are in operation
Referring to the following figure:
Black Area: No converters operating
Purple Area: One converter operating
Red Area: Two converters operating
Green Area: Three converters operating
While the transition between none to one converters in operation and also from one to two converters is clear - the transition between two and three is unclear
Also the Peak demand using this 30 minute data is significantly lower than the peak demand shown on the electricity bills (15 minute interval data was not available)
Electricity Use and Demand
Mullumbimby
Date |  |  |  | 2011-07-01 | 2011-08-01 | 2011-09-01 | 2011-10-01 | 2011-11-01 | 2011-12-01 | 2012-01-01 | 2012-02-01 | 2012-03-01 | 2012-04-01 | 2012-05-01 | 2012-06-01
Peak |  |  |  | 11831 | 19842 | 18694 | 23321 | 26738 | 21356 | 20106 | 22651 | 24466 | 14251 | 22859 | 19671
Shoulder |  |  |  | 25586 | 40634 | 37513 | 47437 | 54005 | 43650 | 41382 | 46793 | 51780 | 29522 | 47771 | 40860
Off Peak |  |  |  | 52222 | 77888 | 70658 | 104517 | 98233 | 96137 | 85035 | 84952 | 93851 | 82181 | 84019 | 84930
Peak Demand |  |  |  | 207 | 287 | 287 | 337 | 388 | 339 | 392 | 378 | 390 | 260 | 312 | 272
Shoulder Demand |  |  |  | 234 | 331 | 307 | 364 | 497 | 351 | 403 | 409 | 422 | 286 | 323 | 311
Off Peak Demand |  |  |  | 235 | 335 | 323 | 369 | 471 | 373 | 366 | 376 | 420 | 284 | 330 | 309
Energy Charges |  |  |  | 5741.3168 | 8941.0349 | 8219.9332 | 11156.4731 | 11638.3679 | 10255.5915 | 9394.1715 | 10033.8987 | 11046.7346 | 7811.9055 | 10081.4454 | 9311.2486
Network Charges (kWh) |  |  |  | 3243.2455 | 5058.3949 | 4652.5391 | 6295.4875 | 6591.4193 | 5786.9962 | 5307.645 | 5682.143 | 6254.9868 | 4388.1826 | 5712.0371 | 5259.3591
Network Charges (kW) |  |  |  | 7398.4761 | 10387.3488 | 9987.408 | 11744.8409 | 14845.2357 | 11594.0076 | 13140.3657 | 13054.9069 | 13579.1852 | 9136.2534 | 10624.4945 | 9775.0471
Other Charges |  |  |  | 932.5145 | 1439.4007 | 1319.7766 | 1823.3858 | 1861.8873 | 1676.3706 | 1524.2788 | 1606.1816 | 1769.5191 | 1310.2995 | 1608.8135 | 1513.2308
Access & Metering |  |  |  | 516.9937 | 516.9937 | 503.381 | 516.9937 | 503.381 | 516.9937 | 516.9937 | 489.7683 | 516.9937 | 503.381 | 516.9937 | 503.381
Total |  |  |  | 17832.5466 | 26343.173 | 24683.0379 | 31537.181 | 35440.2912 | 29829.9596 | 29883.4547 | 30866.8985 | 33167.4194 | 23150.0219 | 28543.7842 | 26362.2666
Bungalora
Date |  |  |  | 2011-07-01 | 2011-08-01 | 2011-09-01 | 2011-10-01 | 2011-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01
Peak |  |  |  | 11270 | 19622 | 18457 | 22891 | 26095 | 21180 | 19683 | 22284 | 23978 | 14220 | 22859 | 19591
Shoulder |  |  |  | 24696 | 39878 | 36734 | 46216 | 52357 | 42917 | 40514 | 45705 | 50578 | 29387 | 47771 | 40621.76
Off Peak |  |  |  | 51152 | 77538 | 70721 | 104215 | 97858 | 95322 | 85781 | 84587 | 93086 | 82162 | 84019 | 85065.84
Peak Demand |  |  |  | 217 | 293 | 283 | 332 | 391 | 326 | 372 | 378 | 391 | 289 | 312 | 282
Shoulder Demand |  |  |  | 243 | 299 | 307 | 359 | 462 | 354 | 374 | 396 | 409 | 297 | 323 | 311
Off Peak Demand |  |  |  | 258 | 364 | 350 | 382 | 453 | 370 | 376 | 378 | 419 | 297 | 330 | 325
Energy Charges |  |  |  | 5825.5091 | 9252.3924 | 8517.0342 | 11515.6107 | 11961.6057 | 10608.0771 | 9759.3377 | 10354.3614 | 11372.3478 | 8157.6777 | 10547.1631 | 9721.8113
Network Charges (kWh) |  |  |  | 3144.3791 | 5002.3079 | 4606.1908 | 6208.7812 | 6472.3431 | 5720.9845 | 5267.5101 | 5602.9456 | 6153.3914 | 4379.7848 | 5712.0371 | 5248.112
Network Charges (kW) |  |  |  | 7761.2416 | 10097.644 | 10019.879 | 11639.7265 | 14305.1449 | 11434.202 | 12441.7478 | 12867.327 | 13396.3058 | 9778.894 | 10624.4945 | 9979.2893
Other Charges |  |  |  | 906.2886 | 1425.6063 | 1309.8625 | 1803.0688 | 1834.1529 | 1658.4359 | 1518.6091 | 1587.2481 | 1743.9797 | 1308.3749 | 1608.8135 | 1511.3333
Access & Metering |  |  |  | 611.9937 | 611.9937 | 598.381 | 611.9937 | 598.381 | 611.9937 | 611.9937 | 571.1556 | 611.9937 | 598.381 | 611.9937 | 598.381
Total |  |  |  | 18249.412 | 26389.9443 | 25051.3476 | 31779.1809 | 35171.6277 | 30033.6931 | 29599.1984 | 30983.0377 | 33278.0184 | 24223.1124 | 29104.502 | 27058.9269
Assumed Cost of Electricity | bar: 2011-07-01 to 2011-10-01
| Mullumbimby | Bungalora
Energy Charges | 2014 | 2014
Peak | 8.095 | 8.469 | c/kWh
Shoulder | 8.095 | 8.469 | c/kWh
Off Peak | 5.194 | 5.4339 | c/kWh
Network Charges
Peak | 4.7365 | 4.7365 | c/kWh
Shoulder | 4.7365 | 4.7365 | c/kWh
Off Peak | 2.8168 | 2.8168 | c/kWh
Peak Demand | 14.9551 | 14.9551 | $/kVA
Shoulder Demand | 14.9551 | 14.9551 | $/kVA
Off Peak Demand | 3.4182 | 3.4182 | $/kVA
Other Charges
ESC | 0.1473 | 0.1473 | c/kWh
LREC | 0.4812 | 0.4812 | c/kWh
SREC | 0.335 | 0.335 | c/kWh
AEMO Charge | 0.0378 | 0.0378 | c/kWh
AEMO Ancillary | 0.039 | 0.039 | c/kWh (Average value for most recent 12 months)
Access Charge | 13.6127 | 13.6127 | $ per day
VIP Metering | 95 | 190 | per calendar month
REDUCED OPERATIONS | bar: 2011-07-01 to 2011-10-01
Mullumbimby
Date | To Dec 2013 | From March 2013 | From Jan 2014 | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01
Peak | 7.7903 | 7.7903 | 8.095 | 15164 | 12383 | 12039 | 18632 | 13804 | 17682 | 18922 | 14852 | 10928 | 10696 | 16657 | 13936
Off Peak | 4.9473 | 4.9473 | 5.194 | 64022 | 45959 | 55520 | 73084 | 52552 | 86280 | 80219 | 56243 | 48422 | 46118 | 60387 | 63133
Shoulder | 7.7903 | 7.7903 | 8.095 | 31865 | 25997 | 25936 | 40517 | 29482 | 39998 | 42649 | 30752 | 22531 | 22381 | 33481 | 28680
Off Peak | 3.0003 | 3.0003 | 2.8168 | 64022 | 45959 | 55520 | 70215 | 52619 | 80013 | 74008 | 56268 | 45886 | 42224 | 60387 | 60898
Off Peak Demand | 3.4992 | 3.4992 | 3.4182 | 243.21 | 248.56 | 258.4 | 343.92 | 258.8 | 306.44 | 306.44 | 306.1 | 244.83 | 217.45 | 226.93 | 205.85
Peak | 5.0293 | 5.0293 | 4.7365 | 15164 | 12383 | 12039 | 19605 | 13830 | 20114 | 21384 | 15154 | 11864 | 12039 | 16657 | 14679
Shoulder | 5.0293 | 5.0293 | 4.7365 | 31865 | 25997 | 25936 | 42249 | 29376 | 43831 | 46406 | 30428 | 24065 | 25096 | 33481 | 30172
Peak Demand | 15.3097 | 15.3097 | 14.9551 | 216.33 | 220.91 | 222.5 | 279.61 | 256.01 | 363.63 | 265.6 | 290.83 | 265.6 | 216.93 | 239.24 | 201.38
Shoulder Demand | 15.3097 | 15.3097 | 14.9551 | 244.83 | 251.6 | 289.25 | 380.79 | 307.67 | 360.81 | 317.35 | 283.64 | 282.42 | 233.66 | 233.66 | 230.22
Access Charge | 13.9354 | 13.9354 | 13.6127 | 31 | 31 | 30 | 31 | 30 | 31 | 31 | 28 | 31 | 30 | 31 | 30
ESC | 0.1353 | 0.1869 | 0.1473 | 111051 | 84339 | 93495 | 132069 | 95825 | 143958 | 141798 | 101850 | 81815 | 79359 | 110525 | 105749
LREC | 0.4442 | 0.4766 | 0.4812 | 111051 | 84339 | 93495 | 132233 | 95838 | 143960 | 141790 | 101847 | 81881 | 79195 | 110525 | 105749
SREC | 0.5333 | 0.9479 | 0.335
AEMO Charge | 0.0434 | 0.0434 | 0.0378
AEMO Ancillary |  |  | 0.038667 | 0.0428 | 0.0121 | 0.0288 | 0.0313 | 0.0371 | 0.0629 | 0.03 | 0.0829 | 0.0357 | 0.038 | 0.0393 | 0.0231
VIP Metering | 95 | 95 | 95
Actual Bill |  |  |  | 22975.61 | 20007.77 | 21604.73 | 29537.29 | 23007.5 | 31706.25 | 30521.58 | 24943.67 | 21556.76 | 18148.56 | 23826.28 | 22155.67
Energy Charges |  |  |  | 6831.0606 | 5263.6467 | 5705.1074 | 8223.5693 | 5972.0144 | 8761.9755 | 8765.2402 | 6335.1984 | 5002.1381 | 4858.3933 | 6893.4267 | 6443.2932
Network Charges |  |  |  | 12629.3406 | 11844.8981 | 12732.6375 | 16963.452 | 13705.1139 | 18211.8672 | 16058.9064 | 14236.924 | 12862.4232 | 11211.838 | 12799.4096 | 11828.8529
Other |  |  |  | 1426.5015 | 1080.3325 | 1202.9158 | 1665.045 | 1238.6173 | 1850.0137 | 2483.8929 | 1864.8009 | 1479.075 | 1435.9195 | 1967.404 | 1869.3625
Total (exc GST) |  |  |  | 20886.9027 | 18188.8774 | 19640.6606 | 26852.0663 | 20915.7455 | 28823.8564 | 27308.0394 | 22436.9233 | 19343.6362 | 17506.1508 | 21660.2403 | 20141.5085
Total (2014) |  |  |  | 20563.1219 | 17920.0526 | 19307.7529 | 26422.445 | 20569.6827 | 28326.5576 | 26237.7614 | 21520.9291 | 18655.0608 | 16827.9978 | 20784.5782 | 19330.6984
Bungalora
Date |  |  |  | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01
Peak | 8.2724 | 8.2724 | 8.469 | 15382.4 | 13355.04 | 13314.24 | 20427.2 | 15380.96 | 18060.8 | 17058.4 | 15828 | 12085.92 | 13012.24 | 18519.46 | 14906.46
Off Peak | 5.2535 | 5.2535 | 5.4339 | 64427.84 | 49944.32 | 62116.48 | 80063.04 | 59385.44 | 87190.4 | 73536.16 | 59910.24 | 53918.4 | 58066.78 | 64497.78 | 68642.18
Shoulder | 8.2724 | 8.2724 | 8.469 | 32635.04 | 27929.92 | 28198.4 | 43710.08 | 32089.76 | 38114.24 | 35931.04 | 33001.28 | 25022.56 | 27284.63 | 37950.88 | 30684.83
Off Peak | 3.0003 | 3.0003 | 2.8168 | 64427.84 | 49944.32 | 62116.48 | 76963.52 | 59458.08 | 81487.84 | 69793.44 | 59962.24 | 51232 | 52963.58 | 64497.78 | 66186.33
Off Peak Demand | 3.4992 | 3.4992 | 3.4182 | 263.83 | 260.23 | 292.34 | 356.45 | 298.78 | 320.36 | 409.01 | 337.1 | 278.32 | 250.28 | 243.07 | 233.06
Peak | 5.0293 | 5.0293 | 4.7365 | 15382.4 | 13355.04 | 13314.24 | 21308.48 | 15266.24 | 19908.16 | 18824.96 | 16072 | 13053.12 | 14770.96 | 18519.46 | 15727.62
Shoulder | 5.0293 | 5.0293 | 4.7365 | 32635.04 | 27929.92 | 28198.4 | 45738.88 | 32129.44 | 41982.56 | 37972.96 | 32703.04 | 26687.84 | 30798.23 | 37950.88 | 32319.52
Peak Demand | 15.3097 | 15.3097 | 14.9551 | 229.64 | 218.87 | 258.54 | 290.83 | 276.07 | 355.76 | 361.54 | 307.9 | 289.55 | 244.85 | 263.87 | 219.74
Shoulder Demand | 15.3097 | 15.3097 | 14.9551 | 264.15 | 265.82 | 291.19 | 558.6 | 337.37 | 397.38 | 383.02 | 310.09 | 317.03 | 257.22 | 257.08 | 262.33
Access Charge | 13.9354 | 13.9354 | 13.6127 | 31 | 31 | 30 | 31 | 30 | 31 | 31 | 28 | 31 | 30 | 31 | 30
ESC | 0.1353 | 0.1869 | 0.1473 | 112445.28 | 91229.28 | 103629.12 | 144010.88 | 106853.76 | 143378.56 | 126591.36 | 108737.28 | 90972.96 | 98532.77 | 120968.12 | 114233.47
LREC | 0.4442 | 0.4766 | 0.4812 | 112445.28 | 91229.28 | 103629.12 | 144200.32 | 106856.16 | 143365.44 | 126525.6 | 108739.52 | 91026.88 | 98363.65 | 120968.12 | 114233.47
SREC | 0.5333 | 0.9479 | 0.335
AEMO Charge | 0.0434 | 0.0434 | 0.0378
AEMO Ancillary |  |  | 0.038667 | 0.0428 | 0.0121 | 0.0288 | 0.0313 | 0.0371 | 0.0629 | 0.03 | 0.0829 | 0.0357 | 0.038 | 0.0393 | 0.0231
VIP Metering | 95 | 95 | 95
Actual Bill |  |  |  | 24373.87 | 21596.05 | 24116.51 | 34956.78 | 25888.09 | 32786.9 | 32090.18 | 27374.57 | 24355.17 | 22004.16 | 26772.24 | 24750.55
Energy Charges |  |  |  | 7356.9113 | 6039.0819 | 6697.3809 | 9511.8042 | 7046.7819 | 9227.5717 | 8246.7206 | 7186.7378 | 5902.365 | 6384.0566 | 8059.8433 | 7377.6108
Network Charges |  |  |  | 13262.9377 | 12337.8766 | 13808.6955 | 20364.9551 | 15022.7271 | 18640.8982 | 18212.7458 | 15283.1032 | 14228.2584 | 12861.2604 | 14033.3259 | 13016.1559
Other |  |  |  | 1538.2189 | 1255.8317 | 1418.0051 | 1902.1225 | 1465.1113 | 1937.7858 | 2321.8262 | 2079.5625 | 1728.7086 | 1855.416 | 2239.3209 | 2106.7234
Total (exc GST) |  |  |  | 22158.0679 | 19632.7902 | 21924.0814 | 31778.8817 | 23534.6203 | 29806.2557 | 28781.2926 | 24549.4035 | 21859.332 | 21100.7329 | 24332.4901 | 22500.4901
Total (2014) |  |  |  | 21629.5805 | 19180.2656 | 21381.0983 | 31049.7885 | 22969.0728 | 29086.165 | 27536.3554 | 23382.0208 | 20924.6683 | 20105.9708 | 23174.6457 | 21429.3083
|  | 2014 |  | 2012-07-01: 2015; 2012-08-01: 2016; 2012-09-01: 2017; 2012-10-01: 2018; 2012-11-01: 2019
Mullumbimby |  | 0 |  | 2012-07-01: 0; 2012-08-01: 0; 2012-09-01: 0; 2012-10-01: 0; 2012-11-01: 0
Bungalora |  | 0 |  | 2012-07-01: 0; 2012-08-01: 0; 2012-09-01: 0; 2012-10-01: 0; 2012-11-01: 0
Total |  |  |  | 2012-07-01: 0; 2012-08-01: 0; 2012-09-01: 0; 2012-10-01: 0; 2012-11-01: 0; 2013-01-01: 0; 2013-02-01: -100%
Originally Claimed |  |  |  | 2012-07-01: 634282.3329; 2012-08-01: 668365.531; 2012-09-01: 688416.4969; 2012-10-01: 724483.5351; 2012-11-01: 746218.0412; 2013-01-01: 3461765.9371
kWh |  |  |  | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01
Mullumbimby |  |  |  | 111051 | 84339 | 93495 | 132233 | 95838 | 143960 | 141790 | 101847 | 81881 | 79195 | 110525 | 105749
Bungalora |  |  |  | 112445.28 | 91229.28 | 103629.12 | 144200.32 | 106856.16 | 143365.44 | 126525.6 | 108739.52 | 91026.88 | 98363.65 | 120968.12 | 114233.47

## Maintenance Documents
MAINTENANCE DOCUMENTS
Return to Index
APA GROUP
DIRECTLINK ANALYSIS
Directlink - GEIP Review of O&M Procedures
|  | Nil | 3 | 2013-10-16 | GIER - Recommendations | Y
|  | Nil | 3 | 2013-05-23 | Network Management Plan | Y | Issued
|  | Nil | 3 | 2013-11-01 | Forecast Methodology | Y | Issued
Documentation Procedures
|  | Doc ID | Rev | Date | Title | Provided Y/N | Status
1 |  | DL-DO-01 | 0 |  | Directlink Documentation Index | Y | Issued
2 |  | DL-DO-02 |  |  | Documentation Control | N | Not Issued
3 |  | DL-DO-03 | 0 |  | NSW Regulatory Compliance Plan | N | Not Issued
4 |  | DL-DO-04 | 1 | 2013-10-25 | Outage Recording Procedure | Y | Issued
5 |  | DL-DO-05 | 0 | 2013-06-12 | Operations Environmental Management plan | Y | Issued
6 |  | DL-DO-06 | 0 | 2013-12-16 | Asset Management Plan | Y | new
7 |  | DL-DO-08 | A | 2013-12-24 | Baseline Compliance Documentation | Y | new
Operating Procedures
|  | Doc ID | Rev | Date | Title | Provided Y/N | Status
8 |  | DL-OP-01 | A | 2007-10-29 | Overview of Directlink |  | Issued
9 |  | DL-OP-02 | 1 | 2013-09-16 | Using the Directlink local/Remote Operator Workstation |  | Issued
10 |  | DL-OP-03 | 0 | 2013-08-30 | External Control Schemes Functional Description |  | Issued
11 |  | DL-OP-04 | 0 |  | Control of Directlink Using the Operator Workstation | N | Issued
12 |  | DL-OP-05 | 2 | 2013-10-23 | Directlink Operations |  | Issued
13 |  | DL-OP-06 | 3 | 2008-04-10 | HV Switching Manual |  | Issued
14 |  | DL-OP-07 | 0 |  | Not Used |  | Not Used
15 |  | DL-OP-08 | 0 |  | Approved HV Equipment | N | Not Issued
16 |  | DL-OP-09 | 0 |  | Approved LV Equipment | N | Not Issued
17 |  | DL-OP-10 | 0 |  | Not Used |  | Not Used
18 |  | DL-OP-11 | 1 |  | Site Induction - Level 5 |  | Revoked
19 |  | DL-OP-12 | 1 |  | Site Induction - Level 4 |  | Revoked
20 |  | DL-OP-13 | 0 |  | Not Used |  | Not Used
21 |  | DL-OP-14 | 0 |  | Not Used |  | Not Used
22 |  | DL-OP-15 | 1 | 2013-09-20 | Permit to Work System |  | Issued
23 |  | DL-OP-16 | 0 |  | Co-ordination of Excavation Works Near DC Cable |  | Not Issued
24 |  | DL-OP-17 | 0 |  | Site Maintenance, Outages and Equipment Failures |  | Issued
25 |  | DL-OP-18 | 1 | 2013-09-16 | Guidelines for Encroachment |  | Rev 1 in Progress
26 |  | DL-OP-19 |  |  | Not Used |  | Not Issued
27 |  | DL-OP-20 | 0 |  | Guidelines For POC Response to Operational Events |  | Not Issued
28 |  | DL-OP-21 | 0 | 2013-08-20 | Black System Procedure |  | Issued
29 |  | DL-OP-22 | 0 |  | Remote Operations |  | Not Issued
30 |  | DL-OP-23 | 1 | 2013-09-16 | Emergency Response Plan |  | Issued
31 |  | DL-OP-24 | 0 | 2013-06-14 | HVDC Cable Repairs |  | new
32 |  | DL-OP-25 | 0 | 2013-06-14 | Analysis of Response of HVDC Assets to an Applicable Event (Network Event Response) |  | new
33 |  | DL-OP-26
34 |  | DL-OP-27 | 0 | 2013-12-23 | Protocol Revision of theMACH II Control & Protection System |  | new
35 |  | DL-OP-28 | 2 | 2014-02-19 | Vegetation Management |  | new
Work Instructions
|  | Doc ID | Rev | Date | Title | Provided Y/N | Status
36 |  | DL-WI-01 | 3 | 2013-09-05 | Tagout/Lockout Procedure |  | Issued
37 |  | DL-WI-02 | 1 | 2013-10-21 | Entry to Converter Building |  | Issued
38 |  | DL-WI-03 | 2 | 2013-10-21 | Preparation of Valve Enclosures for Access and for Energisation |  | Issued
39 |  | DL-WI-04 | 0 |  | Access to Sites |  | Issued
40 |  | DL-WI-05 | 0 | 2013-09-06 | Safe to Earth Procedure |  | Issued
41 |  | DL-WI-06 | 0 | 2013-09-06 | Application of Earths |  | Issued
42 |  | DL-WI-07 | 0 | 2013-09-06 | Discharging of Capacitor Banks |  | Issued
43 |  | DL-WI-08 | 1 | 2013-09-04 | HV Switching Sheets - Standard Wording |  | Issued
44 |  | DL-WI-09 | 1 | 2013-10-20 | Methods of High Voltage Isolation and Earthing |  | Issued
45 |  | DL-WI-10 | 0 |  | Not Used |  | Not Issued
46 |  | DL-WI-11 | 0 |  | Refilling Cooling System |  | Not Issued
47 |  | DL-WI-12 | 0 |  | Interrogation of Valve Data from IPM |  | Not Issued
48 |  | DL-WI-13 | 0 |  | IGBT Replacement |  | Not Issued
49 |  | DL-WI-14 | 0 |  | Not Used |  | Not Used
50 |  | DL-WI-15 | 0 |  | Basic Site Communications Troubleshooting |  | Not Issued
51 |  | DL-WI-16 | 0 |  | Outage and Failed Equipment Reporting
52 |  | DL-WI-17 | 2 | 2013-09-24 | Monthly Energised Maintenance Inspections |  | Issued
53 |  | DL-WI-18 | 1 | 2013-12-13 | Nitrogen Gas Facility |  | Issued
54 |  | DL-WI-19 | 0 |  | Not Used |  | Not Used
55 |  | DL-WI-20 | 0 |  | Not Used |  | Not Used
56 |  | DL-WI-21 | 0 |  | Not Used |  | Not Used
57 |  | DL-WI-22 | 0 | 2013-09-04 | Entry Into Confined Spaces and Poorly Ventilated Areas |  | Issued
58 |  | DL-WI-23 | 0 | 2013-09-04 | Resetting Automatic Shunt Valves |  | Issued
59 |  | DL-WI-24 | 0 |  | Not Used |  | Not Used
60 |  | DL-WI-25 | 0 | 2008-08-28 | Annual Valve Humidity Control System Maintenance |  | Issued
61 |  | DL-WI-26 | 1 | 2013-09-24 | Annual IGBT Valve Maintenance |  | Issued
62 |  | DL-WI-27 | 0 |  | Not Used |  | Not Used
63 |  | DL-WI-28 | 0 | 2008-08-28 | Annual Rogowski Current Transducer Maintenance |  | Issued
64 |  | DL-WI-29 | 2 | 2013-10-22 | Directlink Annual Reactor Maintenance |  | Issued
65 |  | DL-WI-30 | 1 | 2013-09-24 | Directlink Annual Capacitor Maintenance |  | Issued
66 |  | DL-WI-31 | 1 | 2013-09-24 | Directlink Annual Hall Effect Current Transducer Maintenance |  | Issued
67 |  | DL-WI-32 | 1 | 2013-09-04 | Directlink Annual Outdoor Post Type Current Transformer Maintenance |  | Issued
68 |  | DL-WI-33 | 1 | 2013-09-24 | Directlink Annual Cable Screen Current Transformer Maintenance |  | Issued
69 |  | DL-WI-34 | 1 | 2013-09-24 | Directlink Annual Surge Arrestor Maintenance |  | Issued
70 |  | DL-WI-35 | 1 | 2013-09-24 | Directlink Annual AC Filter Resistor Maintenance |  | Issued
71 |  | DL-WI-36 | 1 | 2013-09-24 | Directlink Annual & Two Year Direct Voltage Divider Maintenance |  | Issued
72 |  | DL-WI-37 | 1 | 2013-09-24 | Capacitive Voltage Transformer Maintenance |  | Issued
73 |  | DL-WI-38 | 1 | 2013-09-24 | Directlink Three Year Capacitor Maintenance |  | Issued
74 |  | DL-WI-40 | 0 |  | Hipotronics Cable Fault Locator Equipment |  | Issued
75 |  | DL-WI-41 | 0 |  | Hipotronics DC Insulation Test Set |  | Issued
76 |  | DL-WI-42 | 0 | 2010-03-23 | ABB Capacitance Bridge Type CB10 Test Set |  | new
77 |  | DL-WI-43 | 1 | 2013-09-24 | ABB Capacitance Bridge Type CB10 Test Set |  | Issued
78 |  | DL-WI-44 | 1 | 2013-10-23 | Converter Pre-energisation Inspection |  | Issued
79 |  | DL-WI-45 | 0 | 2013-11-21 | Disconnector & Earth SwitchMaintenance |  | Issued
80 |  | DL-WI-46 | 0 | 2014-01-31 | Annual Zero Sequence and Phase Reactor Maintenance |  | new
Safety Procedures
|  | Doc ID | Rev | Date | Title | Provided Y/N | Status
81 |  | DL-SP-01 | 3 | 2013-09-20 | Response to a Serious Electrical Accident |  | Issued
82 |  | DL-SP-02 | 1 | 2013-10-23 | Response to a Serious Electrical Accident - External |  | Issued
83 |  | DL-SP-03 | 0 |  | Job Safety Analysis - Handling of Gas Cylinders |  | Revoked
84 |  | DL-SP-04 | 1 | 2013-09-29 | Dangerous Goods Manifest - Mullumbimby (BUNGALORA) |  | Issued
85 |  | DL-SP-05 | 0 |  | Dangerous Goods Manifest - Bungalora |  | Not Issued
86 |  | DL-SP-06 | 0 |  | Directlink Safety Plan |  | Revoked
87 |  | DL-SP-07 | 0 |  | Directlink Safety Manual |  | Revoked
Operational Forms
|  | Doc ID | Rev | Date | Title |  | Status
88 |  | DL-OF-01 | 1 | 2013-09-16 | Work Site Safety Form |  | Issued
89 |  | DL-OF-02 | 1 | 2013-09-16 | Electrical Access/Test Permit |  | Issued
90 |  | DL-OF-03 | 0 |  | Electrical Access/Test Permit - Supplementary Page |  | Not Used
91 |  | DL-OF-04 (ML) | 1 | 2013-09-16 | Permit Application Form |  | Issued
92 |  | DL-OF-05 | 1 | 2013-09-16 | Authority to Work In The Vicinity Of Electrical or Mechanical Plant |  | Issued
93 |  | DL-OF-06 | 1 | 2013-09-16 | Clearance to Place Electrical Apparatus Into Service |  | Issued
94 |  | DL-OF-07 | 1 | 2013-09-16 | Statement of Condition of Apparatus/Plant |  | Issued
95 |  | DL-OF-08 | 1 | 2013-09-16 | Switching Sheet |  | Issued
96 |  | DL-OF-09 | 1 | 2013-09-16 | System Outage Request |  | Issued
97 |  | DL-OF-10 | 1 | 2013-09-16 | System Work Notification |  | Issued
98 |  | DL-OF-11 | 0 |  | Access Notification |  | Issued
99 |  | DL-OF-12 | 1 | 2013-09-16 | Work Permit |  | Issued
100 |  | DL-OF-13 | 1 | 2013-09-16 | Callout Log |  | Issued
101 |  | DL-OF-14 | 1 | 2013-09-16 | Consumables Log |  | Issued
102 |  | DL-OF-15 | 1 | 2013-09-16 | Maintenance Log |  | ?????
103 |  | DL-OF-16 | 1 | 2013-09-16 | Operations Log |  | Issued
104 |  | DL-OF-17 | 1 | 2013-09-16 | Outage Register |  | Issued
105 |  | DL-OF-18 | 1 | 2013-09-16 | Visitors Log |  | Issued
106 |  | DL-OF-19 | 1 | ??? | Hot Work Permit |  | ??
107 |  | DL-OF-20 | 0 |  | Not Used |  | Not Used
108 |  | DL-OF-21 (ML) | 1 | 2013-09-16 | Directlink Excavation Requirements |  | Issued
109 |  | DL-OF-22 | 2 | 2013-10-29 | Directlink Excavation Request |  | Issued
110 |  | DL-OF-23 | 0 |  | Accident / Incident Report Form |  | Revoked
111 |  | DL-OF-24 | 1 | 2013-09-16 | Confined Space Permit |  | Issued
112 |  | DL-OF-25 | 1 | 2013-09-16 | Safety Observation Report |  | Issued
113 |  | DL-OF-26 | 0 | 2013-09-06 | Directlink Phase Reactor Inspection Record Form |  | new
114 |  | DL-OF-27 | 0 | ?? | DC Cable Repair |  | new
115 |  | DL-OF-28 | 0 | ?? | Record of Temporary Change to MACH II Control System |  | new
116 |  | DL-OF-29 | 0 | 2013-12-16 | Valve Room Inspection Form |  | new
117 |  | DL-OF-30 | 0 | ?? | IGBT Replacement Form |  | new
118 |  | DL-OF-31 | 0 | ?? | PHASE REACTOR 5 YR FAN INSPECTION RECORD |  | new