## RIN template 4.2
REGULATORY REPORTING STATEMENT
Directlink Joint Venture
2015-16 to 2019-20
4.2 Service target performance incentive scheme (STPIS)
Table 4.2.1 Historical performance and proposed capes, collars and targets for the service component of the STPIS
Instructions
The TNSP is required to provide the performance actuals for the most recent five years, and the proposed caps, collars and targets for the forthcoming regulatory control period for the parameters under the service component of the STPIS in table 4.2.1 below.
Parameter | Performance actuals |  |  |  |  | Average of actual performance | Collar | Target | Cap | Weighting (% of MAR)
| 2008 | 2009 | 2010 | 2011 | 2012
Average circuit outage rate (per cent): | [9 empty] | 1
Circuit outage rate - fault | 800% | 466.7% | 666.7% | 833.3% | 666.7% | 686.7% | 815.9% | 686.7% | 557.4% | 1
Circuit outage rate – forced outage | 166.7% | 100% | 433.3% | 200% | 233.3% | 226.7% | 339% | 226.7% | 114.3% | 0
Proper operation of equipment (number of events): | [9 empty] | 0
Failure of protection system | 5 | 3 | 4 | 2 | 6 | 4 | 5.4142 | 4 | 2.5858 | 0
Material failure of SCADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Incorrect operational isolation of primary or secondary equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table 4.2.2 - Market impact component
Instructions
The TNSP is required to provide performance data in accordance with Appendix C of the STPIS for the preceding two calendar years in table 4.2.2 below. The TNSP is also required to provide relevant information in the MIC workbook attached to Appendix A of the Notice.
Year | Month | Market impact parameter count (DI) (without exclusions) | Market impact parameter count (DI) (with exclusions) | Market impact parameters (Hrs)
2013 | January |  |  | 0 |  | As the MIC has not historically applied to Directlink,
2013 | February |  |  | 0 |  | it has not gathered this information.
2013 | March |  |  | 0
2013 | April |  |  | 0
2013 | May |  |  | 0
2013 | June |  |  | 0
2013 | July |  |  | 0
2013 | August |  |  | 0
2013 | September |  |  | 0
2013 | October |  |  | 0
2013 | November |  |  | 0
2013 | December |  |  | 0
Total 2013 |  | 0 | 0 | 0
2014 | January |  |  | 0
2014 | February |  |  | 0
2014 | March |  |  | 0
2014 | April |  |  | 0
2014 | May |  |  | 0
2014 | June |  |  | 0
2014 | July |  |  | 0
2014 | August |  |  | 0
2014 | September |  |  | 0
2014 | October |  |  | 0
2014 | November |  |  | 0
2014 | December |  |  | 0
Total 2014 |  | 0 | 0 | 0
Calendar years 2008 to 2012 were chosen to avoid too much distortion caused by the complete Directlink outage in the second half of 2013.
Average Circuit Outage Rate – Fault (Target = 5 year average 2008 to 2012, Cap and Collar = ± 1 standard deviation)
The criteria used was to count events where the tripped any reason other than external network events.
Average Circuit Outage Rate – Forced (Target = 5 year average 2008 to 2012, Cap and Collar = ± 1 standard deviation)
The criteria used was to count events where the converter was tripped during maintenance, delayed from returning to service by a secondary fault, and where we needed to shutdown with less than 24 hours’ notice.
Failure of protection system (Target = 5 year average 2008 to 2012, Cap and Collar = ± 1 standard deviation).
The criteria used was to count events where the control & protection system caused a trip as a result of a fault or maintenance of the control & protection system. Events where the converter was offline for another reason and the control & protection system delayed restoration were not counted.
Material failure of the SCADA system (could not identify any events)
Incorrect operational isolation (could not identify any events)

## Outages
Direct Link Outages (Aug 2001- 2008) | [6 empty] | nr outages = | 33
Date | Outage Times |  | Outage Type | System | [5 empty] | System 1 outage hrs | System 2 outage hrs | System 3 outage hrs | Number of systems out |  | Equivalvent Outage Duration - Internal and External Events | Equivalvent Outage Duration - External Events Only | Equivalvent Outage Duration - Cable Faults Only | Equivalvent Outage Duration - Forced Outages Only | Equivalvent Outage Duration - Forced Outages Excluding Cable Faults | Equivalvent Outage Duration - Cable Faults Only
| From | To
2012-07-01 | 0:00 | to
2012-07-11 | to | 18:33 | forced | 3 | Both | Cable fault P2 (-ve) cable. | 258.55 |  | Cable Fault | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2012-07-11 | 7:02 | 15:33 | Scheduled | 1 | Both | Outage to repair System 3 cable fault | 8.5167 |  | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-07-11 | 7:03 | 15:35 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 8.5333 |  | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-07-11 | 15:33 | to
2012-08-14 | to | 8:33 | forced | 1 | BLA | Trip caused by flashover in phase reactor air ducting. | 809 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2012-07-11 | 15:35 | to
2012-07-14 | to | 15:25 | forced | 2 | MUL | Unable to return to service after cable fault repair due to control system fault. | 71.8333 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2012-07-17 | 7:02 | to
2012-07-18 | to | 19:50 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.8 |  | External | #VALUE! | #VALUE! | #VALUE!
2012-07-17 | 7:18 | to
2012-07-18 | to | 19:53 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.5833 |  | External | #VALUE! | #VALUE! | #VALUE!
2012-07-23 | 6:59 | to
2012-07-24 | to | 16:13 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.2333 |  | External | #VALUE! | #VALUE! | #VALUE!
2012-07-23 | 7:01 | to
2012-07-24 | to | 16:25 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.4 |  | External | #VALUE! | #VALUE! | #VALUE!
2012-08-14 | 8:33 | to
2013-06-01 | to | 0:00 | forced | 1 | MUL | Trip caused by fire in converter building. | 6975.45 |  | Fire | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2012-08-14 | 8:57 | to
2012-08-23 | to | 16:59 | forced | 2 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 224.0333 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2012-08-14 | 8:58 | to
2012-08-31 | to | 13:44 | forced | 3 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 412.7667 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2012-08-31 | 13:44 | to
2012-09-21 | to | 14:05 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 504.35 |  | Cable Fault | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2012-09-13 | 8:35 | 9:20 | forced | 2 | BLA | Trip cuased by valve control fault related to PCPB | 0.75 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2012-09-20 | 7:29 | to
2012-09-21 | to | 14:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault, return to service delayed by the need to inspect phase reactors for moisture. | 30.5167 |  | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-10-29 | 9:59 | to
2012-10-30 | to | 12:19 | forced | 3 | BLA | Trip cuased by fault with LEM power supply. Inspectgion found not problems. | 26.3333 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2012-11-12 | 5:23 | to
2012-11-23 | to | 15:35 | forced | 2 | MUL | Cable fault P2 (-ve) cable. | 274.2 |  | Cable Fault | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2012-11-18 | 17:50 | to
2012-11-27 | to | 14:57 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 213.1167 |  | Cable Fault | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2012-12-11 | 8:28 | 12:12 | forced | 2 | MUL | Fire protection system tripped the converter station | 3.7333 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2013-01-03 | 5:57 | to
2013-01-10 | to | 14:33 | forced | 2 | MUL | Cable fault P1 (+ve) cable. | 176.6 |  | Cable Fault | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2013-01-09 | 7:50 | 14:21 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 6.5167 |  | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-01-28 | 9:10 | to
2013-01-31 | to | 16:45 | forced | 3 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 79.5833 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2013-01-28 | 9:10 | to
2013-02-01 | to | 15:59 | forced | 2 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 102.8167 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2013-02-21 | 0:03 | 2:44 | forced | 3 | MUL | Trip caused by control system fault. | 2.6833 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2013-02-21 | 5:42 | to
2013-03-12 | to | 13:06 | forced | 3 | MUL | Cable fault P1 (+ve) cable. | 463.4 |  | Cable Fault | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2013-03-07 | 7:05 | 13:57 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 6.8667 |  | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-03-07 | 13:57 | to
2013-03-26 | to | 12:53 | forced | 2 | BLA | Return to service delayed by circuit breaker operating mechanism fault and IGBT failure | 454.9333 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2013-03-26 | 15:37 | to
2013-03-27 | to | 16:30 | forced | 2 | BLA | Trip caused by cooling water pump failure | 24.8833 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2013-04-03 | 13:53 | 14:58 | forced | 2 | BLA | Trip occurred during Control System Maintenance | 1.0833 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
[10 empty] | #VALUE! | #VALUE! | #VALUE!
2013-04-03 | 14:42 | 14:56 | forced | 3 | BLA | Trip occurred during Control System Maintenance | 0.23333 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2013-04-22 | 6:59 | 16:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 9.0167 |  | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-04-22 | 16:00 | to
2013-04-23 | to | 14:03 | forced | 2 | BLA | Return to service delayed by circuit breaker fault | 22.05 |  | Maintenance | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
2013-04-06 | 20:06 | to
2013-04-23 | to | 12:47 | forced | 3 | Both | Cable fault P12 (-ve) cable. | 400.6833 |  | Cable Fault | #VALUE! | #VALUE! | #VALUE! | [6 empty] | #VALUE!
[10 empty] | #VALUE! | #VALUE! | #VALUE! |  |  | 0 | 0 | 0 | 0 | #VALUE! | 0
[15 empty] | 8760 | 8760 | 8760 | 41 | 20 | 8760
[14 empty] | Availability | 100% | 100% | 100% | 0 | #VALUE! | 100%
[18 empty] | 0 | #VALUE!
0
8760
[14 empty] | Availability Excluding External Events | 100%
0
8760
[14 empty] | Availability Excluding External Events & Cable Faults | 100%
0
8760
[14 empty] | Availability Excluding External Events & Cable Faults & Fire | 100%

## Sheet1
Date | Outage Times |  | Outage Type | System |  |  |  |  | System 1 outage hrs | System 2 outage hrs | System 3 outage hrs | Number of systems out
| From | To
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-01-07 | 7:00 | 12:20 | forced | 2 | MUL | Computer failure at Mullumbimby | 5.3333 | Mach2 fault | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-01-01 | 0:00 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2007-02-08 | to | 18:00 | forced | 1 | BLA | Transformer differential trip, suspected loose core lamination. This portion of the outage is in 2007 | 930 | Transformer fault | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-03-17 | 8:28 | 16:31 | scheduled | 1 | MUL | Repairs to galvanised steel troughing | 8.05 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2007-03-17 | 8:59 | 16:32 | scheduled | 3 | MUL | Repairs to galvanised steel troughing | 7.55 | Maintenance | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-03-17 | 8:59 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2007-03-18 | to | 17:14 | forced | 2 | BLA | PCP mach2 computer failed during switching for planned repairs. | 32.25 | PCP failure | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-03-18 | 8:25 | 17:14 | scheduled | 1 | BLA | Repairs to galvanised steel troughing | 8.8167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2007-03-18 | 8:25 | 17:14 | scheduled | 3 | BLA | Repairs to galvanised steel troughing | 8.8167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-04-01 | 12:59 | 14:00 | forced | 1 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 | Other faults | #VALUE! | #VALUE! | #VALUE!
2007-04-01 | 12:59 | 14:00 | forced | 2 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 | Other faults | #VALUE! | #VALUE! | #VALUE!
2007-04-01 | 12:59 | 14:00 | forced | 3 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 | Other faults | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-04-09 | 13:29 | 16:35 | forced | 1 | MUL | Loss of pole 1, caused by 11kV fault. | 3.1 | External | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-04-16 | 9:30 | 11:00 | scheduled | 1 | Both | Single system outage for site visits | 1.5 | Maintenance | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-05-04 | 8:30 | 11:30 | scheduled | 1 | both | Single system outage for site visits | 3 | Maintenance | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-05-25 | 8:56 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2007-07-25 | to | 10:41 | forced | 3 | both | Cooling water leak in valve hall, phase reactor failure. | 1465.75 | Cooling system fault | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-05-25 | 10:51 | 14:36 | forced | 2 | both | Pole 2 tripped, no fault found, returned to service. | 3.75 | External | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-06-02 | 22:13 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2007-06-07 | to | 16:11 | forced | 2 | both | More than 5 IGBTs failed in a stack. | 113.9667 | More than 5 IGBTs failed | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-06-07 | 1:58 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2007-06-27 | to | 14:03 | forced | 1 | both | DC cable fault | 492.0833 | Other cable fault | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-06-16 | 12:14 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2007-06-18 | to | 9:56 | forced | 2 | both | A Powerlink fault at Mudgeeraba caused the loss of 110kV supplies to Terranora. | 45.7 | External | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-06-18 | 10:18 | 10:29 | forced | 2 | BLA | Power supply problem in PCPB Mach 2 | 0.18333 | Mach2 fault | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-06-29 | 5:55 | 5:58 | forced | 1 | MUL | Spurious trip, unknown cause | 0.05 | External | #VALUE! | #VALUE! | #VALUE!
2007-06-29 | 5:55 | 5:58 | forced | 2 | MUL | Spurious trip, unknown cause | 0.05 | External | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-07-09 | 16:21 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2007-07-10 | to | 11:50 | forced | 2 | BLA | Cooling equipment fault at Bungalora pole 2 | 19.4833 | Cooling system fault | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-07-18 | 8:32 | 13:05 | scheduled | 1 | BLA | Inspection of phase reactors at Bungalora | 4.55 | Maintenance | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-07-19 | 8:32 | 13:12 | forced | 2 | MUL | Spurious trip, unknown cause | 4.6667 | External | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-08-01 | 15:30 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2007-08-02 | to | 12:45 | forced | 3 | both | Pole 3 tripped, unknown cause. | 21.25 | External | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-09-04 | 7:01 | 20:02 | scheduled | 1 | both | Annual maintenance | 13.0167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-09-05 07:11 | 7:11 | 17:08 | scheduled | 2 | both | Annual maintenance | 9.95 | Maintenance | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-09-06 | 7:00 | 18:45 | scheduled | 3 | both | Annual maintenance | 11.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-10-05 | 12:17 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2007-11-15 | to | 14:30 | forced | 1 | BLA | Differential trip at Bungalora | 986.2167 | Unknown fault | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-10-26 | 22:30 | 23:21 | forced | 2 | Both | Fault on 132kV system | 0.85 | External | #VALUE! | #VALUE! | #VALUE!
2007-10-26 | 22:30 | 23:21 | forced | 3 | Both | Fault on 132kV system | 0.85 | External | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-11-05 | 11:00 | 13:10 | scheduled | 2 | Both | Systems 2 & 3 down for excavation on system 1 | 2.1667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2007-11-05 | 11:00 | 13:10 | scheduled | 3 | Both | Systems 2 & 3 down for excavation on system 1 | 2.1667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2007-11-27 | 7:15 | to
2007-11-27 | to | 17:00 | scheduled | 1 | both | Maintenance - Phase Reactors and IGBTs. Control system faults prevent return to service. | 9.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2007-11-27 | 17:00 | to
2007-12-19 | to | 17:00 | forced | 1 | MUL | Computer failure on pole 1 at Mullumbimby. | 528 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2007-11-28 | 7:15 | to
2007-11-28 | to | 17:00 | scheduled | 2 | both | Maintenance - Phase Reactors and IGBTs. Control system faults prevent return to service. | 9.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2007-11-28 | 17:00 | to
2007-12-20 | to | 18:05 | forced | 2 | both | Computer failure on pole 2 at Mullumbimby. | 529.0833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2007-11-29 | 8:08 | 15:14 | scheduled | 3 | both | Maintenance - Phase Reactors and IGBTs. | 7.1 | Maintenance | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-12-30 | 13:10 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2007-12-31 | to | 24:00 | forced | 2 | BLA | Auxiliary Power Failure caused control system problems | 34.8333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
[9 empty] | #VALUE! | #VALUE! | #VALUE!
2007-12-30 | 13:10 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2007-12-31 | to | 24:00 | forced | 3 | BLA | Auxiliary Power Failure caused control system problems | 34.8333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-01-01 | 0:00 | to
2008-01-02 | to | 16:50 | forced | 3 | BLA | Auxiliary Power Failure caused control system problems | 40.8331 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-01-01 | 0:00 | to
2008-01-02 | to | 20:09 | forced | 2 | BLA | Auxiliary Power Failure caused control system problems | 44.1497 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-02-02 | 22:11 | to
2008-02-03 | to | 10:48 | forced | 2 | MUL | Control System Faults | 12.6167 | Unknown fault
2008-02-13 | 8:30 | 17:00 | scheduled | 1 | both | Shutdown to investigate various faults | 8.5 | Maintenance
2008-02-19 | 6:00 | to | [6 empty] | #VALUE! | #VALUE! | #VALUE!
2008-02-21 | to | 0:27 | forced | 2 | both | Computer failure on pole 2 | 42.45 | PCP failure | #VALUE! | #VALUE! | #VALUE!
2008-02-20 | 7:00 | 11:00 | scheduled | 1 | both | Fire System Maintenance | 4 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-02-20 | 11:05 | 13:50 | scheduled | 3 | both | Fire System Maintenance | 2.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-02-27 | 8:00 | 10:35 | scheduled | 1 | BLA | Installation of power flow monitoring gear | 2.5833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-02-27 | 10:12 | 13:46 | scheduled | 2 | BLA | Installation of power flow monitoring gear | 3.5667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-02-27 | 11:00 | 15:34 | scheduled | 3 | BLA | Installation of power flow monitoring gear | 4.5667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-03-08 | 19:31 | to
2008-03-28 | to | 13:00 | forced | 2 | both | Cable fault | 473.4833 | Unknown fault | #VALUE! | #VALUE! | #VALUE!
2008-03-13 | 16:07 | to
2008-04-04 | to | 15:00 | forced | 1 | both | Cable fault | 526.8833 | Unknown fault | #VALUE! | #VALUE! | #VALUE!
2008-03-18 | 9:35 | 12:20 | scheduled | 3 | both | Outage to safely excavate sys1 cables for repair | 2.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-03-30 | 14:07 | 18:00 | forced | 3 | both | Unknown fault caused converter to trip | 3.8833 | External | #VALUE! | #VALUE! | #VALUE!
2008-04-09 | 7:25 | 15:35 | scheduled | 3 | both | Phase reactor inspections | 8.1667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-04-10 | 7:25 | 14:56 | scheduled | 2 | both | Phase reactor inspections | 7.5167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-04-11 | 7:08 | to
2008-04-24 | to | 17:32 | scheduled | 1 | both | Phase reactor inspections and Transformer swap out | 322.4 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-04-13 | 7:00 | 17:00 | scheduled | 2 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-04-13 | 7:00 | 17:00 | scheduled | 3 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-04-16 | 7:00 | 17:00 | scheduled | 2 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-04-16 | 7:00 | 17:00 | scheduled | 3 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-04-14 | 15:09 | to
2008-05-01 | to | 16:00 | forced | 2 | both | System 2 Cable fault | 408.85 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-12 | 8:00 | to
2008-05-15 | to | 18:45 | scheduled | 1 | both | Phase reactor repairs | 82.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-15 | 17:00 | 18:45 | scheduled | 2 | both | Communications Test | 1.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-15 | 17:00 | 18:45 | scheduled | 3 | both | Communications Test | 1.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-16 | 8:00 | to
2008-05-17 | to | 13:40 | scheduled | 3 | both | Phase reactor repairs | 29.6667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-18 | 8:00 | to
2008-05-19 | to | 14:11 | scheduled | 2 | both | Phase reactor repairs | 30.1833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-20 | 9:00 | 11:00 | scheduled | 1 | both | Comms cut over for trial operation | 2 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-20 | 9:00 | 11:00 | scheduled | 2 | both | Comms cut over for trial operation | 2 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-20 | 9:00 | 11:00 | scheduled | 3 | both | Comms cut over for trial operation | 2 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-20 | 17:00 | 17:30 | scheduled | 1 | both | Comms cut over after trial operation | 0.5 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-20 | 17:00 | 17:30 | scheduled | 2 | both | Comms cut over after trial operation | 0.5 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-20 | 17:00 | 17:30 | scheduled | 3 | both | Comms cut over after trial operation | 0.5 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-22 | 9:00 | 9:35 | scheduled | 1 | both | Comms cut over for trial operation | 0.58333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-22 | 9:00 | 9:35 | scheduled | 2 | both | Comms cut over for trial operation | 0.58333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-22 | 9:00 | 9:35 | scheduled | 3 | both | Comms cut over for trial operation | 0.58333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-22 | 16:00 | 16:20 | scheduled | 1 | both | Comms cut over after trial operation | 0.33333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-22 | 16:00 | 16:20 | scheduled | 2 | both | Comms cut over after trial operation | 0.33333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-22 | 16:00 | 16:20 | scheduled | 3 | both | Comms cut over after trial operation | 0.33333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-22 | 20:12 | to
2008-05-23 | to | 16:05 | forced | 3 | both | Reactor cooling fan fault. | 19.8833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-26 | 12:00 | 12:25 | scheduled | 1 | both | Final comms cut over. | 0.41667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-26 | 12:00 | 12:25 | scheduled | 2 | both | Final comms cut over. | 0.41667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-05-26 | 12:00 | 12:25 | scheduled | 3 | both | Final comms cut over. | 0.41667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-06-09 | 3:21 | to
2008-06-10 | to | 17:06 | forced | 3 | BLA | PCPA hard disk fault | 37.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-06-24 | 21:28 | 22:22 | forced | 1 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-06-24 | 21:28 | 22:22 | forced | 2 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-06-24 | 21:28 | 22:22 | forced | 3 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-06-25 | 5:30 | 18:55 | scheduled | 1 | MUL | Country Energy outage to connect CB 7H3 | 13.4167 | External | #VALUE! | #VALUE! | #VALUE!
2008-06-25 | 5:30 | 18:55 | scheduled | 2 | MUL | Country Energy outage to connect CB 7H3 | 13.4167 | External | #VALUE! | #VALUE! | #VALUE!
2008-06-25 | 5:30 | 18:55 | scheduled | 3 | MUL | Country Energy outage to connect CB 7H3 | 13.4167 | External | #VALUE! | #VALUE! | #VALUE!
2008-06-25 | 18:55 | 20:40 | forced | 1 | both | Comms fault from Dandenong to DL | 1.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-06-25 | 18:55 | 20:40 | forced | 2 | both | Comms fault from Dandenong to DL | 1.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-06-25 | 18:55 | 20:40 | forced | 3 | both | Comms fault from Dandenong to DL | 1.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-06-25 | 20:40 | to
2008-06-27 | to | 18:00 | forced | 1 | BLA | Faulty IGBTs | 45.3333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-06-27 | 22:47 | to
2008-07-09 | to | 15:43 | forced | 2 | both | Cable Fault | 280.9333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-06-29 | 3:30 | 8:00 | forced | 1 | MUL | TransGrid Tripping Scheme operation | 4.5 | External | #VALUE! | #VALUE! | #VALUE!
2008-06-29 | 3:30 | 8:00 | forced | 3 | MUL | TransGrid Tripping Scheme operation | 4.5 | External | #VALUE! | #VALUE! | #VALUE!
2008-06-29 | 8:00 | 10:27 | forced | 1 | MUL | Mach 2 faults after TransGrid Tripping Scheme operation | 2.4497 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-06-29 | 8:00 | 10:27 | forced | 3 | MUL | Mach 2 faults after TransGrid Tripping Scheme operation | 2.4497 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-07-11 | 7:00 | 18:43 | forced | 3 | BLA | Reactor Fan Trip | 11.7167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-07-12 | 8:25 | 16:15 | scheduled | 1 | BLA | Valve Cooling Water Leak Inspection | 7.8333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-07-14 | 11:03 | to
2008-08-04 | to | 14:54 | forced | 2 | both | Cable fault | 507.85 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-07-20 | 1:02 | 5:29 | scheduled | 1 | both | Country Energy outage | 4.45 | External | #VALUE! | #VALUE! | #VALUE!
2008-07-20 | 1:02 | 5:29 | scheduled | 3 | both | Country Energy outage | 4.45 | External | #VALUE! | #VALUE! | #VALUE!
2008-07-25 | 9:03 | 11:20 | scheduled | 1 | both | Outage to excavate Cables for repair to system 2 cable fault | 2.2833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-07-25 | 9:03 | 11:20 | scheduled | 3 | both | Outage to excavate Cables for repair to system 2 cable fault | 2.2833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-07-25 | 11:20 | to
2008-08-01 | to | 16:15 | forced | 3 |  | After outage to excavate cables for repair to system 2 cable fault, L2 phase of system 3 circuit breaker would not close. | 172.9167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-07-31 | 9:46 | 14:35 | scheduled | 1 | both | Outage to excavate Cables for repair to system 2 cable fault | 4.8167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-08-18 | 19:58 | to
2008-08-19 | to | 1:51 | forced | 1 | both | Abnormal frequency trip | 5.8833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-08-18 | 19:58 | to
2008-08-19 | to | 1:51 | forced | 2 | both | Abnormal frequency trip | 5.8833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-08-18 | 19:58 | to
2008-08-19 | to | 1:51 | forced | 3 | both | Abnormal frequency trip | 5.8833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2007-08-19 | 1:51 | 14:43 | forced | 3 | both | Abnormal frequency trip | 12.8667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-09-16 | 7:00 | to
2008-09-18 | to | 17:26 | scheduled | 2 | both | Annual Maintenance | 58.4333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-09-18 | 7:30 | to
2008-09-19 | to | 17:00 | scheduled | 3 | both | Annual Maintenance | 33.5 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-09-19 | 17:00 | to
2008-09-21 | to | 7:00 | forced | 3 | both | Mullumbimby sytem 3 control system fault | 38 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-09-21 | 7:00 | 16:00 | scheduled | 1 | both | Country energy requested outage for maintenance at Terranora | 9 | External | #VALUE! | #VALUE! | #VALUE!
2008-09-21 | 7:00 | 16:00 | scheduled | 2 | both | Country energy requested outage for maintenance at Terranora | 9 | External | #VALUE! | #VALUE! | #VALUE!
2008-09-21 | 7:00 | 16:00 | scheduled | 3 | both | Country energy requested outage for maintenance at Terranora | 9 | External | #VALUE! | #VALUE! | #VALUE!
2008-09-21 | 16:00 | to
2008-10-07 | to | 16:05 | forced | 3 | both | Mullumbimby sytem 3 control system fault | 384.0833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-09-20 | 7:00 | to
2008-09-21 | to | 7:00 | scheduled | 1 | both | Annual Maintenance | 24 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-09-21 | 16:00 | to
2008-09-25 | to | 15:55 | forced | 1 | both | Bungalora pre-insertion resistor overload trip - earths left on in the barn | 95.9167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-09-25 | 14:22 | 20:17 | forced | 2 | both | Mullumbimby reactor cooling fan trip | 5.9167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-10-01 | 18:17 | to
2008-11-14 | to | 19:11 | forced | 2 | both | Cable Fault P1 cable. | 1056.9 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-11-07 | 13:59 | to
2008-11-14 | to | 18:51 | forced | 1 | both | Cable Fault P1 cable. | 172.8667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-11-20 | 18:46 | 20:20 | forced | 1 | BLA | Auxiliary power failure | 1.5667 | External | #VALUE! | #VALUE! | #VALUE!
2008-11-20 | 18:46 | 20:20 | forced | 2 | BLA | Auxiliary power failure | 1.5667 | External | #VALUE! | #VALUE! | #VALUE!
2008-11-20 | 18:46 | 20:20 | forced | 3 | BLA | Auxiliary power failure | 1.5667 | External | #VALUE! | #VALUE! | #VALUE!
2008-11-24 | 7:02 | 15:02 | scheduled | 1 | both | Phase Reactor Inspections and cable clamp modifications | 8 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-11-25 | 6:54 | 15:36 | scheduled | 2 | both | Phase Reactor Inspections and cable clamp modifications | 8.7 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-11-26 | 7:05 | 14:45 | scheduled | 3 | both | Phase Reactor Inspections and cable clamp modifications | 7.6667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-11-27 | 7:10 | 13:14 | scheduled | 1 | both | Phase Reactor Inspections and cable clamp modifications | 6.0667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-12-08 | 1:18 | to
2008-12-16 | to | 13:12 | forced | 2 | both | Cable Fault P1 cable. | 203.9 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-12-15 | 8:10 | 10:25 | scheduled | 1 | both | Outage to locate Pole 1 cable fault | 2.25 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-12-15 | 8:17 | 10:28 | scheduled | 3 | both | Outage to locate Pole 1 cable fault | 2.1833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-12-19 | 23:06 | to
2008-12-31 | to | 9:42 | forced | 2 | both | Cable Fault P1 cable. | 274.6 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-12-30 | 7:47 | 9:22 | scheduled | 1 | both | Outage to locate Pole 1 cable fault | 1.5833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-12-30 | 7:41 | 9:24 | scheduled | 3 | both | Outage to locate Pole 1 cable fault | 1.7167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2008-12-31 | 11:13 | to
2008-12-31 | to | 24:00 | forced | 2 | both | Cable Fault P1 cable. | 12.7831 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-01-01 | 0:00 | to
2009-01-20 | to | 9:22 | forced | 2 | both | Cable Fault P1 cable. | 465.3667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-01-11 | 13:00 | to
2009-01-19 | to | 12:06 | forced | 1 | both | Cable Fault P1 cable. | 191.1 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-01-16 | 7:00 | 14:01 | scheduled | 3 | both | Outage to repair Pole 1 and Pole 2 cable faults | 7.0167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-02-09 | 21:00 | to
2009-02-18 | to | 10:53 | forced | 2 | both | Cable Fault P1 cable. | 205.8833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-02-10 | 7:26 | 12:01 | scheduled | 1 | both | Outage for Country Energy maintenance - 110kV bus at Terranora substation | 4.5833 | External | #VALUE! | #VALUE! | #VALUE!
2009-02-10 | 7:36 | 12:06 | scheduled | 3 | both | Outage for Country Energy maintenance - 110kV bus at Terranora substation | 4.5 | External | #VALUE! | #VALUE! | #VALUE!
2009-02-16 | 9:05 | 13:05 | scheduled | 1 | both | Outage to repair Pole 2 cable fault | 4 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-02-16 | 9:07 | 13:06 | scheduled | 3 | both | Outage to repair Pole 2 cable fault | 3.9833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-02-16 | 13:17 | 14:59 | scheduled | 1 | both | Outage to repair Pole 2 cable fault | 1.7 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-02-16 | 13:16 | 15:00 | scheduled | 3 | both | Outage to repair Pole 2 cable fault | 1.7333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-03-10 | 7:31 | 15:23 | scheduled | 3 | both | Outage for six month maintenance | 7.8667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-03-11 | 7:31 | 13:54 | scheduled | 2 | both | Outage for six month maintenance | 6.3833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-03-12 | 7:03 | to
2009-03-13 | to | 8:02 | scheduled | 1 | both | Outage for six month maintenance | 24.9833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-03-17 | 9:40 | to
2009-03-30 | to | 13:51 | forced | 3 | both | Cable Fault P1 & P2 cable. | 316.1833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-03-26 | 7:04 | 15:51 | scheculed | 1 | both | Outage to repair Pole 3 cable fault | 8.7833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-03-26 | 7:37 | 15:53 | scheculed | 2 | both | Outage to repair Pole 3 cable fault | 8.2667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-03-27 | 7:03 | 13:24 | scheculed | 1 | both | Outage to repair Pole 3 cable fault | 6.35 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-03-27 | 7:08 | 13:26 | scheculed | 2 | both | Outage to repair Pole 3 cable fault | 6.3 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-04-15 | 10:01 | 11:28 | scheculed | 1 | both | Outage for access valve enclosure lock change | 1.45 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-04-15 | 11:48 | 13:57 | scheculed | 2 | both | Outage for access valve enclosure lock change | 2.15 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-04-15 | 14:08 | 15:23 | scheculed | 3 | both | Outage for access valve enclosure lock change | 1.25 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-04-19 | 3:40 | 3:58 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.3 | External | #VALUE! | #VALUE! | #VALUE!
2009-04-19 | 3:40 | 3:58 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.3 | External | #VALUE! | #VALUE! | #VALUE!
2009-04-19 | 3:40 | 3:58 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.3 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-20 | 20:46 | 23:31 | forced | 1 | BLA | Auxilary power outage caused a reactor cooling fan changeover. Dampers did not open in time causing a trip. | 2.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-05-21 | 5:10 | 6:52 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Return delayed to investigate a CB Relay fault. | 1.7 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-21 | 5:10 | 5:24 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.23333 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-21 | 5:10 | 5:24 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.23333 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-22 | 4:32 | 4:38 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.1 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-22 | 4:32 | 4:39 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.11667 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-22 | 4:32 | 4:40 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.13333 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-22 | 7:59 | 8:59 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 1 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-22 | 7:59 | 9:03 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 1.0667 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-22 | 7:59 | 9:03 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 1.0667 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-22 | 15:18 | 16:34 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 1.2667 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-22 | 15:18 | 15:48 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.5 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-22 | 15:18 | 15:48 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.5 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-23 | 17:22 | to
2009-05-24 | to | 13:22 | forced | 3 | MUL | AC Filter capacitor protection trip. | 20 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-05-23 | 19:02 | 19:15 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.21667 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-23 | 19:02 | 19:14 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.2 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-23 | 19:34 | 19:40 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.1 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-23 | 19:34 | 19:41 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.11667 | External | #VALUE! | #VALUE! | #VALUE!
2009-05-26 | 18:02 | to
2009-06-06 | to | 13:08 | forced | 2 | Both | Cable fault P1 cable, Return to service delayed by too any Faulty IGBTs in B phase | 259.1 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-06-02 | 11:54 | 12:10 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.26667 | External | #VALUE! | #VALUE! | #VALUE!
2009-06-02 | 11:54 | 12:10 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.26667 | External | #VALUE! | #VALUE! | #VALUE!
2009-06-02 | 12:15 | 14:28 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 2.2167 | External | #VALUE! | #VALUE! | #VALUE!
2009-06-02 | 12:15 | 14:28 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 2.2167 | External | #VALUE! | #VALUE! | #VALUE!
2009-06-03 | 9:16 | 14:49 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 5.55 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-06-03 | 9:16 | 14:51 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.5833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-06-30 | 6:50 | to
2009-07-18 | to | 10:29 | forced | 2 | Both | Cable fault P1 cable, Return to service delayed by too any Faulty IGBTs in B phase | 435.65 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-07-14 | 9:04 | 14:19 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 5.25 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-07-14 | 9:13 | 14:21 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 5.1333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-07-15 | 8:36 | 10:24 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 1.8 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-07-15 | 8:38 | 10:21 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 1.7167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-07-16 | 9:12 | 17:32 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 8.3333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-07-16 | 9:02 | 17:29 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 8.45 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-07-16 | 17:29 | to
2009-07-21 | to | 17:38 | forced | 1 | Both | Unable to return to service. Too many faulty igbts. | 120.15 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-07-20 | 18:28 | to
2009-07-21 | to | 9:54 | forced | 2 | Both | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 15.4333 | External | #VALUE! | #VALUE! | #VALUE!
2009-07-20 | 18:28 | to
2009-07-21 | to | 9:56 | forced | 3 | Both | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 15.4667 | External | #VALUE! | #VALUE! | #VALUE!
2009-07-27 | 6:36 | to
2009-07-28 | to | 17:04 | Scheduled | 1 | Both | Shutdown for annual maintenance | 34.4667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-07-29 | 6:49 | to
2009-07-30 | to | 17:26 | Scheduled | 2 | Both | Shutdown for annual maintenance | 34.6167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-07-31 | 6:32 | to
2009-08-01 | to | 13:02 | Scheduled | 3 | Both | Shutdown for annual maintenance | 30.5 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-08-14 | 10:52 | 11:38 | forced | 1 | Both | Trip caused by flow protection. Standby pump did not start when pumps changed during while converter was running. | 0.76667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-08-25 | 13:27 | to
2009-08-29 | to | 14:54 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 97.45 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-08-27 | 8:14 | 16:47 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 8.55 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-08-27 | 8:07 | 16:49 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 8.7 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-08-27 | 17:11 | 21:20 | forced | 1 | MUL | Trip caused by Coutry Energy protection operation. Failed protection CT in Mullumbimby system 3 transformer | 4.15 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-08-27 | 17:11 | to
2009-09-04 | to | 17:04 | forced | 3 | MUL | Trip caused by Coutry Energy protection operation. Failed protection CT in Mullumbimby system 3 transformer | 191.8833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-09-04 | 7:22 | 16:49 | Scheduled | 1 | MUL | Outage for HV access to repair failed protection CT in Mullumbimby system 3 transformer | 9.45 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-09-04 | 7:23 | 16:50 | Scheduled | 2 | MUL | Outage for HV access to repair failed protection CT in Mullumbimby system 3 transformer | 9.45 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-09-29 | 7:04 | 17:14 | Scheduled | 1 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.1667 | External | #VALUE! | #VALUE! | #VALUE!
2009-09-29 | 7:07 | 17:39 | Scheduled | 2 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.5333 | External | #VALUE! | #VALUE! | #VALUE!
2009-09-29 | 7:09 | 17:18 | Scheduled | 3 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.15 | External | #VALUE! | #VALUE! | #VALUE!
2009-11-03 | 13:23 | 14:01 | forced | 3 | BLA | Trip by Flow Protection - Active CCP accidentally reset during maintenance | 0.63333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-11-04 | 2:42 | to
2009-11-13 | to | 10:18 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 223.6 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-11-10 | 17:50 | to
2009-11-10 | to | 18:44 | forced | 3 | Bla | Fault with 24V DC power supply | 0.9 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-11-11 | 10:11 | 16:08 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.95 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-11-11 | 10:16 | 16:06 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 5.8333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-11-19 | 1:51 | to
2009-11-28 | to | 9:57 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 224.1 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-11-20 | 2:17 | 2:55 | forced | 2 | MUL | Abnormal Frequency Trip. Country Energy System Problems. | 0.63333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-11-20 | 2:17 | 2:56 | forced | 3 | MUL | Abnormal Frequency Trip. Country Energy System Problems. | 0.65 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-11-26 | 9:06 | 14:59 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.8833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-11-26 | 9:15 | 14:57 | Scheduled | 2 | Both | Outage to enable access to repair the system 2 cable. | 5.7 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-11-27 | 10:28 | 11:03 | forced | 3 | MUL | Damper Resistor overload trip event on one PCP. Converter tripped while trying to clear the event. | 0.58333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-11-28 | 10:30 | to
2009-12-17 | to | 14:49 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 460.3167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-12-11 | 0:52 | 2:16 | forced | 1 | BLA | Operation of Powerlink intertrip scheme. | 1.4 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-12-11 | 0:52 | 2:17 | forced | 3 | BLA | Operation of Powerlink intertrip scheme. | 1.4167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-12-12 | 8:13 | 8:58 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-12-12 | 8:13 | 8:59 | forced | 3 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.76667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-12-15 | 7:02 | 17:07 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 10.0833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-12-15 | 7:20 | 17:04 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 9.7333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2009-12-17 | 22:14 | to
2009-12-31 | to | 24:00 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 337.7664 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-01-08 | 18:49 | 19:11 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.36667 | External | #VALUE! | #VALUE! | #VALUE!
2010-01-08 | 18:49 | 19:13 | forced | 3 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.4 | External | #VALUE! | #VALUE! | #VALUE!
2010-01-09 | 13:04 | to
2010-03-31 | to | 14:01 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 1944.95 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-01-12 | 7:16 | 16:16 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 9 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-01-13 | 13:37 | to
2010-01-21 | to | 9:56 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 188.3167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-01-01 | 0:00 | to
2010-01-14 | to | 9:14 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 321.2333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-01-15 | 7:23 | 8:05 | forced | 2 |  | Trip during control system maintenance | 0.7 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-01-19 | 7:03 | 14:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 7.15 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-01-20 | 21:01 | 21:34 | forced | 2 |  | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.55 | External | #VALUE! | #VALUE! | #VALUE!
2010-01-27 | 5:30 | to
2010-03-31 | to | 13:54 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 1520.4 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-03-27 | 6:04 | 17:35 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. | 11.5167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-03-28 | 6:04 | 15:41 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 9.6167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-03-31 | 23:18 | to
2010-04-17 | to | 9:26 | forced | 1 | Both | Cable fault P1 (+ve) cable. After cable repair, fault with DC voltage measuring delayed return to service. | 394.1333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-04-17 | 9:26 | to
2010-04-28 | to | 13:37 | forced | 1 | Both | Fault with DC voltage measuring delayed return to service after repair P1 (+ve) cable, | 268.1833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-04-09 | 17:48 | to
2010-04-20 | to | 13:44 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 259.9333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-04-14 | 7:04 | to
2010-04-15 | to | 15:51 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. Too many faulty igbts when energised from Mullumbimby. Igbts repaired the next day during system 2 cable fault repair. | 32.7833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-04-30 | 19:18 | to
2010-06-13 | to | 10:34 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 1047.2667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-05-05 | 11:00 | 13:14 | forced | 1 | BLA | Trip during fault finding of PCPB DC voltage measuring | 2.2333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-05-24 | 7:14 | to
2010-05-28 | to | 14:24 | Scheduled | 3 | Both | Outage to replace transformer CTs | 103.1667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-05-25 | 7:03 | 19:33 | Scheduled | 1 | Both | Outage to allow overhead crane access for replacing system 3 transformer CTs | 12.5 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-05-31 | 10:05 | 17:23 | Scheduled | 1 | Both | Outage to excavate the system 2 cable fault. | 7.3 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-05-31 | 10:10 | 17:26 | Scheduled | 3 | Both | Outage to excavate the system 2 cable fault under the river. | 7.2667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-05-31 | 17:26 | to
2010-06-08 | to | 13:18 | forced | 3 | Both | Outage to excavate the system 2 cable fault. Return to service delayed due to VCU Faults. | 187.8667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-06-01 | 13:43 | 14:33 | Scheduled | 1 | Both | Outage to cut system 2 cable during repair of fault under the river. | 0.83333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-06-03 | 6:55 | 17:48 | Scheduled | 1 | Both | Outage to joint system 2 cable during repair of fault under the river. | 10.8833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-06-04 | 7:00 | 16:15 | Scheduled | 1 | Both | Outage to joint system 2 cable during repair of fault under the river. | 9.25 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-06-10 | 2:02 | 16:02 | forced | 3 | BLA | Trip due to low water level. Pump leaking. | 14 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-07-06 | 1:03 | 16:18 | forced | 2 | MUL | UPS failure caused trip of converter | 15.25 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-07-15 | 22:07 | to
2010-07-26 | to | 8:19 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 250.2 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-07-22 | 6:03 | 17:22 | Scheduled | 1 | BLA | CE Requested Outage - Terranora Bus zone breakers | 11.3167 | External | #VALUE! | #VALUE! | #VALUE!
2010-07-22 | 6:06 | 17:23 | Scheduled | 3 | BLA | CE Requested Outage - Terranora Bus zone breakers | 11.2833 | External | #VALUE! | #VALUE! | #VALUE!
2010-07-22 | 17:22 | to
2010-07-26 | to | 7:00 | forced | 1 | MUL | Return to serivce delayed - Too many faulty IGBTs | 85.6333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-07-22 | 17:23 | to
2010-07-26 | to | 7:00 | forced | 3 | BLA | Return to serivce delayed - Too many faulty IGBTs | 85.6167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-07-26 | 7:00 | to
2010-07-28 | to | 14:39 | Scheduled | 3 | Both | Annual Maintenance | 55.65 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-07-26 | 7:00 | to
2010-07-29 | to | 15:18 | Scheduled | 1 | Both | Annual Maintenance | 80.3 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-07-28 | 15:02 | to
2010-07-29 | to | 14:44 | forced | 3 | BLA | Phase reactor partial discharge repair | 23.7 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-07-30 | 8:41 | to
2010-07-31 | to | 16:49 | Scheduled | 2 | Both | Annual Maintenance | 32.1333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-07-31 | 16:49 | to
2010-08-06 | to | 13:25 | forced | 2 | MUL | Return to serivce delayed - faulty control system components | 140.6 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-07-31 | 8:38 | 10:00 | Scheduled | 1 | MUL | CE Requested Outage - Lismore Tripping Scheme Work | 1.3667 | External | #VALUE! | #VALUE! | #VALUE!
2010-07-31 | 8:46 | 10:01 | Scheduled | 3 | MUL | CE Requested Outage - Lismore Tripping Scheme Work | 1.25 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-09 | 7:44 | 8:37 | forced | 1 | BLA | Auxiliary power failure | 0.88333 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-09 | 7:44 | 8:37 | forced | 2 | BLA | Auxiliary power failure | 0.88333 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-09 | 7:44 | 8:37 | forced | 3 | BLA | Auxiliary power failure | 0.88333 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-09 | 8:37 | to
2010-08-11 | to | 13:40 | forced | 1 | BLA | Restoration after auxiliary power failure | 53.05 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-08-09 | 8:37 | 15:58 | forced | 2 | BLA | Restoration after auxiliary power failure | 7.35 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-08-09 | 8:37 | 9:43 | forced | 3 | BLA | Restoration after auxiliary power failure | 1.1 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-08-10 | 12:04 | 18:39 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 6.5833 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-10 | 12:06 | 18:35 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 6.4833 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-11 | 6:04 | 13:42 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 7.6333 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-11 | 6:05 | 13:41 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 7.6 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-14 | 6:08 | 12:44 | Scheduled | 1 | BLA | County Energy Requested outage for work at Terranora | 6.6 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-14 | 6:10 | 12:45 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 6.5833 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-14 | 6:11 | 12:46 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 6.5833 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-15 | 6:03 | 11:50 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 5.7833 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-15 | 6:05 | 11:48 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 5.7167 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-15 | 6:06 | 11:46 | Scheduled | 1 | BLA | County Energy Requested outage for work at Terranora | 5.6667 | External | #VALUE! | #VALUE! | #VALUE!
2010-08-22 | 4:00 | 15:04 | forced | 2 | BLA | Reactor cooling fans tripped converter | 11.0667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-08-25 | 9:46 | 11:27 | forced | 2 | BLA | Trip caused by control system maintenance | 1.6833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-09-02 | 12:50 | 13:28 | Scheduled | 3 | BLA | Outage requested by Country Energy for protection testing | 0.63333 | External | #VALUE! | #VALUE! | #VALUE!
2010-09-02 | 12:51 | 13:28 | Scheduled | 2 | BLA | Outage requested by Country Energy for protection testing | 0.61667 | External | #VALUE! | #VALUE! | #VALUE!
2010-09-02 | 12:51 | 13:27 | Scheduled | 1 | BLA | Outage requested by Country Energy for protection testing | 0.6 | External | #VALUE! | #VALUE! | #VALUE!
2010-09-18 | 2:43 | to
2010-10-01 | to | 12:08 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 321.4167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-09-19 | 2:02 | to
2010-10-01 | to | 12:42 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 298.6667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-09-27 | 8:02 | 16:02 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. | 8 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-09-27 | 8:01 | 14:16 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 6.25 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-10-06 | 16:23 | to
2010-10-22 | to | 12:28 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 380.0833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-10-14 | 8:11 | 15:01 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable. | 6.8333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-10-14 | 8:11 | 15:03 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 6.8667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-10-17 | 10:06 | 14:02 | forced | 2 | MUL | Trip caused by fire protection system fault. | 3.9333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-10-29 | 9:38 | 11:08 | Scheduled | 1 | Both | Outage to repair GST damage. | 1.5 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-11-08 | 6:06 | 13:07 | Scheduled | 1 | MUL | Outage for CE Comms tower installation | 7.0167 | External | #VALUE! | #VALUE! | #VALUE!
2010-11-08 | 6:11 | 13:08 | Scheduled | 2 | MUL | Outage for CE Comms tower installation | 6.95 | External | #VALUE! | #VALUE! | #VALUE!
2010-11-08 | 6:34 | 13:09 | Scheduled | 3 | MUL | Outage for CE Comms tower installation | 6.5833 | External | #VALUE! | #VALUE! | #VALUE!
2010-11-09 | 6:04 | 13:19 | Scheduled | 1 | MUL | Outage for CE Comms tower installation | 7.25 | External | #VALUE! | #VALUE! | #VALUE!
2010-11-09 | 6:09 | 13:20 | Scheduled | 2 | MUL | Outage for CE Comms tower installation | 7.1833 | External | #VALUE! | #VALUE! | #VALUE!
2010-11-09 | 6:15 | 13:21 | Scheduled | 3 | MUL | Outage for CE Comms tower installation | 7.1 | External | #VALUE! | #VALUE! | #VALUE!
2010-11-14 | 1:21 | to
2010-11-20 | to | 8:14 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 150.8786 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-11-18 | 7:07 | 14:42 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable. | 7.5833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-11-18 | 7:10 | 14:42 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 7.5333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-11-23 | 7:02 | to
2010-11-24 | to | 15:30 | Scheduled | 1 | Both | IGBT/FO Test & Replacement | 32.4667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-11-24 | 15:30
2010-11-26 | to | 13:45 | forced | 1 | Both | IGBT Faults | 78.7167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-11-25 | 21:15 | to
2010-12-03 | to | 13:45 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 184.5 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-11-30 | 7:05 | 14:31 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 7.4333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-11-30 | 7:07 | 14:33 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 7.4333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-12-06 | 6:46 | to
2010-12-07 | to | 17:02 | Scheduled | 1 | Both | IGBT/FO Test & Investigation with ABB Mikael | 34.2667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-12-08 | 7:08 | to
2010-12-09 | to | 14:48 | Scheduled | 2 | Both | IGBT/FO Test & Investigation with ABB Mikael | 31.6667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-12-09 | 14:51 | to
2010-12-10 | to | 17:06 | Scheduled | 3 | Both | IGBT/FO Test & Investigation with ABB Mikael | 26.25 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-12-12 | 14:39 | to
2010-12-22 | to | 16:07 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 241.4667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-12-15 | 19:06 | to
2010-12-23 | to | 10:29 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 183.3833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-12-17 | 7:01 | 17:29 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 10.4667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-12-21 | 7:02 | 17:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 10.1667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-12-25 | 1:01 | 1:41 | forced | 1 | BLA | Auxiliary power failure - Rector cooling fans trip. | 0.66667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2010-12-27 | 13:03 | to
2011-01-01 | to | 0:00 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 106.95 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-01-01 | 0:00 | to
2011-01-07 | to | 9:07 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 153.1167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-01-05 | 7:01 | 14:15 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 7.2333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-01-05 | 7:04 | 14:17 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 7.2167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-01-07 | 6:36 | to
2011-01-17 | to | 9:35 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 242.9833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-01-10 | 15:21 | to
2011-01-18 | to | 11:39 | forced | 2 | Both | Cable fault P2 (-ve) cable. | 188.3 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-01-13 | 7:03 | 14:28 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 7.4167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-01-14 | 7:01 | 13:32 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable fault | 6.5167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-01-28 | 11:51 | to
2011-02-10 | to | 13:59 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 314.1333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-02-09 | 7:11 | 17:43 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 10.5333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-02-09 | 7:13 | 18:10 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 10.95 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-02-09 | 17:43 | to
2011-02-14 | to | 17:24 | forced | 3 | Both | Outage due to BLA System 3, B Phase CB Pole leaking insulating gas. | 119.6833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-02-14 | 7:03 | 16:10 | Scheduled | 1 | Both | Outage to enable access to the replacement of BLA System 3, B Phase CB Pole | 9.1167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-02-14 | 7:15 | 17:41 | Scheduled | 2 | Both | Outage to enable access to the replacement of BLA System 3, B Phase CB Pole | 10.4333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-02-14 | 17:41 | to
2011-02-18 | to | 11:31 | forced | 2 | MUL | Unable to return to service after planned outage. Too many faulty IGBTs | 89.8333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-02-15 | 7:13 | 7:42 | forced | 1 | MUL | Outage due to control system fault. | 0.48333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-02-21 | 17:15 | 18:31 | forced | 1 | BLA | Phase Reactor Cooling Fan L3 Trip | 1.2667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-03-13 | 12:24 | to
2011-03-28 | to | 13:23 | forced | 1 | MUL | Trip due to flash over in PLC filter yard. Return to service delayed due to to many faulty IGBTs | 360.9833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-03-13 | 12:24 | 19:31 | forced | 2 | MUL | Trip due to flash over in PLC filter yard. | 7.1167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-03-13 | 12:24 | 19:34 | forced | 3 | MUL | Trip due to flash over in PLC filter yard. | 7.1667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-04-01 | 6:18 | 13:48 | Scheduled | 1 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.5 | External | #VALUE! | #VALUE! | #VALUE!
2011-04-01 | 6:19 | 13:49 | Scheduled | 2 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.5 | External | #VALUE! | #VALUE! | #VALUE!
2011-04-01 | 6:21 | 13:49 | Scheduled | 3 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.4667 | External | #VALUE! | #VALUE! | #VALUE!
2011-04-01 | 13:49 | to
2011-04-08 | to | 12:55 | forced | 2 | Both | Faulty IGBTs prevented return to service after CE outage. | 167.1 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-04-18 | 16:05 | to
2011-04-23 | to | 13:09 | forced | 1 | Both | Cable Fault P1 (+ve) cable. | 117.0667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-04-21 | 7:01 | 15:26 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 8.4167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-04-21 | 7:02 | 15:28 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 8.4333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-05-08 | 16:23 | to
2011-06-11 | to | 16:25 | forced | 1 | Both | Outage caused by DC voltage imbalance. Return to service delayed by too many faulty IGBT optic fibres. | 816.0333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-05-14 | 11:26 | to
2011-05-30 | to | 11:26 | forced | 3 | Both | Cable Fault P1 (+ve) cable. Return to service after cable fault repair delayed by too many faulty IGBTs | 384 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-05-25 | 7:04 | 18:32 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault. | 11.4667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-05-25 | 18:32 | to
2011-07-22 | to | 10:15 | forced | 2 | Both | Unable to return to service after planned outage. Too many faulty IGBTs | 1383.7167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-06-10 | 2:56 | to
2011-07-15 | to | 10:18 | forced | 3 | Both | Cable Fault P1 (+ve) cable. | 847.3667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-07-14 | 6:11 | 20:25 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 14.2333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-07-15 | 10:30 | 11:09 | forced | 3 | BLA | Cooling system trip - high water temperature - proportional valve failed to operate. | 0.65 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-07-18 | 23:25 | to
2011-07-30 | to | 9:38 | forced | 1 | Both | Cable Fault P2 (-ve) cable. | 274.2167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-07-22 | 10:50 | to
2011-08-05 | to | 15:12 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 340.3667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-07-29 | 7:02 | 18:48 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 11.7667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-07-30 | 9:38 | to
2011-08-05 | to | 15:11 | forced | 1 | BLA | Unable to return to service after cable fault. Too many faulty IGBTs | 149.55 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-08-05 | 7:07 | 15:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 8.0833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-08-17 | 7:05 | 14:07 | Scheduled | 1 | Both | Outage for CE Comms tower work | 7.0333 | External | #VALUE! | #VALUE! | #VALUE!
2011-08-17 | 7:17 | 14:20 | Scheduled | 2 | Both | Outage for CE Comms tower work | 7.05 | External | #VALUE! | #VALUE! | #VALUE!
2011-08-17 | 7:24 | 14:18 | Scheduled | 3 | Both | Outage for CE Comms tower work | 6.9 | External | #VALUE! | #VALUE! | #VALUE!
2011-08-22 | 16:08 | to
2011-08-23 | to | 0:06 | forced | 3 | BLA | Rector Cooling fans faulty contactor | 7.9667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-08-22 | 16:08 | to
2011-08-23 | to | 9:50 | forced | 1 | BLA | Rector Cooling fans faulty contactor | 17.7 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-08-23 | 11:48 | 12:14 | forced | 2 | MUL | Trip cause during replacement of UPS fault indicating relay | 0.43333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-08-25 | 7:07 | to
2011-09-03 | to | 13:05 | forced | 3 | Both | Cable Fault P2 (-ve) cable. | 221.9667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-08-30 | 9:39 | 10:17 | forced | 2 | BLA | Valve control fault during maintenance work | 0.63333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-08-31 | 11:52 | 18:07 | Scheduled | 1 | Both | Outage for Coucil excavation of water pipe at Bungalora | 6.25 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-08-31 | 11:54 | 18:07 | Scheduled | 2 | Both | Outage for Coucil excavation of water pipe at Bungalora | 6.2167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-09-02 | 7:03 | 17:49 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 10.7667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-09-02 | 7:04 | 17:53 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 10.8167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-09-05 | 9:08 | 18:52 | forced | 3 | MUL | Rector Cooling fans faulty contactor | 9.7333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-09-12 | 9:30 | to
2011-09-26 | to | 16:14 | forced | 1 | Both | Cable Fault P1 (+ve) cable. | 342.7333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-09-24 | 8:33 | to
2011-09-30 | to | 17:57 | forced | 2 | Both | Cable Fault P1 (+ve) cable. | 153.4 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-09-26 | 7:07 | 15:59 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 8.8667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-09-30 | 7:05 | 17:10 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable fault | 10.0833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-09-30 | 7:12 | 17:13 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable fault | 10.0167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-11-03 | 7:18 | 13:22 | Scheduled | 2 | BLA | Outage to add SF6 Gas to bypass breaker | 6.0667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-11-08 | 7:43 | to
2011-11-09 | to | 16:07 | Scheduled | 1 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 32.4 | External | #VALUE! | #VALUE! | #VALUE!
2011-11-08 | 8:03 | to
2011-11-09 | to | 17:37 | Scheduled | 2 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 33.5667 | External | #VALUE! | #VALUE! | #VALUE!
2011-11-08 | 8:01 | to
2011-11-09 | to | 16:11 | Scheduled | 3 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 32.1667 | External | #VALUE! | #VALUE! | #VALUE!
2011-11-30 | 7:24 | 16:12 | Scheduled | 3 | Both | Outage to install sound prrofing on transformer | 8.8 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-12-06 | 9:55 | 10:37 | Scheduled | 2 | Both | Outage to add SF6 Gas to bypass breaker | 0.7 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-12-09 | 18:43 | to
2011-12-19 | to | 16:28 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 237.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-12-19 | 7:02 | 14:15 | Scheduled | 1 | Both | Outage to repair System 3 cable fault | 7.2167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-12-19 | 7:12 | 15:52 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 8.6667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2011-12-19 | 16:31 | to
2011-12-20 | to | 10:37 | forced | 3 | MUL | Reactor Cooling fans fault | 18.1 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-01-04 | 18:41 | 19:22 | forced | 1 | BLA | Reactor Cooling fans fault | 0.68333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-01-05 | 18:41 | to
2012-01-10 | to | 11:42 | forced | 1 | BLA | Reactor Cooling fans fault | 113.0167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-01-06 | 6:06 | 12:32 | Scheduled | 3 | MUL | Transformer Sound enclosure repairs | 6.4333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-01-06 | 12:32 | to
2012-01-10 | to | 16:46 | forced | 3 | MUL | Control system fault. | 100.2333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-01-10 | 21:57 | to
2012-01-16 | to | 16:48 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 138.85 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-01-16 | 8:03 | 14:37 | Scheduled | 1 | Both | Outage to repair System 2 cable fault | 6.5667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-01-16 | 8:03 | 14:38 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 6.5833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-01-16 | 16:48 | to
2012-01-23 | to | 12:04 | forced | 2 | MUL | Unable to return to service after cable fault. Too many faulty IGBTs | 163.2667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-01-25 | 5:57 | to
2012-02-03 | to | 16:59 | forced | 2 | MUL | Valve cooling control system fault | 227.0333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-02-04 | 1:11 | to
2012-02-13 | to | 16:32 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 231.35 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-02-13 | 7:05 | 16:30 | Scheduled | 2 | Both | Outage to repair System 1 cable fault | 9.4167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-02-13 | 7:08 | 16:29 | Scheduled | 3 | Both | Outage to repair System 1 cable fault | 9.35 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-02-16 | 11:01 | 11:42 | forced | 2 | MUL | Trip cuased by control system maintenance | 0.68333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-02-16 | 11:48 | 15:19 | forced | 2 | MUL | Trip cuased by control system maintenance | 3.5167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-02-20 | 7:44 | to
2012-02-21 | to | 13:04 | Scheduled | 2 | Both | Outage for IGBT replacement at Bungalora and & Transformer measurement at Mullumbimby | 29.3333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-02-28 | 20:58 | to
2012-03-09 | to | 11:43 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 230.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-03-02 | 9:15 | 9:44 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 0.48333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-03-03 | 7:11 | 15:00 | Scheduled | 3 | Both | Outage to repair System 1 cable fault | 7.8167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-03-03 | 7:14 | 15:00 | Scheduled | 2 | Both | Outage to repair System 1 cable fault | 7.7667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-03-29 | 11:14 | to
2012-03-30 | to | 7:00 | forced | 3 | BLA | Trip caused by control system fault. | 19.7667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-03-30 | 7:00 | to
2012-04-05 | to | 14:28 | Scheduled | 3 | MUL | Outage for Transformer sound enclosure. | 151.4667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-04-02 | 13:41 | to
2012-04-17 | to | 17:08 | forced | 2 | Both | Cable fault P2 (-ve) cable. | 363.45 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-04-17 | 17:08 | to
2012-05-11 | to | 14:12 | forced | 2 | Both | Return to service after cable fault delayed due to faulty IGBTs | 573.0667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-04-17 | 7:10 | 15:28 | Scheduled | 1 | Both | Outage to repair System 2 cable fault | 8.3 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-04-17 | 7:18 | 15:28 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 8.1667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-04-17 | 7:10 | to
2012-04-20 | to | 13:51 | Scheduled | 1 | MUL | Outage for Transformer sound enclosure. | 78.6833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-05-22 | 10:34 | 11:08 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 0.56667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-05-27 | 4:49 | to
2012-06-07 | to | 14:31 | forced | 3 | MUL | Trip caused by reactor cooling fan motor fault | 273.7 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-06-06 | 6:14 | 18:36 | Scheduled | 1 | MUL | Outage for Country Energy protection installation | 12.3667 | External | #VALUE! | #VALUE! | #VALUE!
2012-06-06 | 6:16 | 18:38 | Scheduled | 2 | MUL | Outage for Country Energy protection installation | 12.3667 | External | #VALUE! | #VALUE! | #VALUE!
2012-06-08 | 9:57 | 14:13 | forced | 2 | MUL | Trip caused by control system maintenance | 4.2667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-06-19 | 10:04 | 11:06 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 1.0333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-06-29 | 17:02 | to
2012-07-11 | to | 18:33 | forced | 3 | Both | Cable fault P2 (-ve) cable. | 289.5167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-07-11 | 7:02 | 15:33 | Scheduled | 1 | Both | Outage to repair System 3 cable fault | 8.5167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-07-11 | 7:03 | 15:35 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 8.5333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-07-11 | 15:33 | to
2012-08-14 | to | 8:33 | forced | 1 | BLA | Trip caused by flashover in phase reactor air ducting. | 809 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-07-11 | 15:35 | to
2012-07-14 | to | 15:25 | forced | 2 | MUL | Unable to return to service after cable fault repair due to control system fault. | 71.8333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-07-17 | 7:02 | to
2012-07-18 | to | 19:50 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.8 | External | #VALUE! | #VALUE! | #VALUE!
2012-07-17 | 7:18 | to
2012-07-18 | to | 19:53 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.5833 | External | #VALUE! | #VALUE! | #VALUE!
2012-07-23 | 6:59 | to
2012-07-24 | to | 16:13 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.2333 | External | #VALUE! | #VALUE! | #VALUE!
2012-07-23 | 7:01 | to
2012-07-24 | to | 16:25 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.4 | External | #VALUE! | #VALUE! | #VALUE!
2012-08-14 | 8:33 | to
2013-01-01 | to | 0:00 | forced | 1 | MUL | Trip caused by fire in converter building. | 3351.45 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-08-14 | 8:57 | to
2012-08-23 | to | 16:59 | forced | 2 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 224.0333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-08-14 | 8:58 | to
2012-08-31 | to | 13:44 | forced | 3 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 412.7667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-08-31 | 13:44 | to
2012-09-21 | to | 14:05 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 504.35 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-09-13 | 8:35 | 9:20 | forced | 2 | BLA | Trip cuased by valve control fault related to PCPB | 0.75 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-09-20 | 7:29 | to
2012-09-21 | to | 14:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault, return to service delayed by the need to inspect phase reactors for moisture. | 30.5167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-10-29 | 9:59 | to
2012-10-30 | to | 12:19 | forced | 3 | BLA | Trip cuased by fault with LEM power supply. Inspectgion found not problems. | 26.3333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-11-12 | 5:23 | to
2012-11-23 | to | 15:35 | forced | 2 | MUL | Cable fault P2 (-ve) cable. | 274.2 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-11-18 | 17:50 | to
2012-11-27 | to | 14:57 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 213.1167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2012-12-11 | 8:28 | 12:12 | forced | 2 | MUL | Fire protection system tripped the converter station | 3.7333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-01-01 | 0:00 | to
2014-01-01 | to | 0:00 | forced | 1 | MUL | Trip caused by fire in converter building. | 8760 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-01-03 | 5:57 | to
2013-01-10 | to | 14:33 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 176.6 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-01-09 | 7:50 | 14:21 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 6.5167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-01-28 | 9:10 | to
2013-01-31 | to | 16:45 | forced | 3 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 79.5833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-01-28 | 9:10 | to
2013-02-01 | to | 15:59 | forced | 2 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 102.8167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-02-21 | 0:03 | 2:44 | forced | 3 | MUL | Trip caused by control system fault. Auxiliary power disturbance caused both PCPs to fault. | 2.6833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-02-21 | 5:42 | to
2013-03-12 | to | 13:06 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 463.4 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-03-07 | 7:05 | 13:57 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 6.8667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-03-07 | 13:57 | to
2013-03-26 | to | 12:53 | forced | 2 | BLA | Return to service delayed by circuit breaker operating mechanism fault and IGBT failure | 454.9333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-03-26 | 15:37 | to
2013-03-27 | to | 16:30 | forced | 2 | BLA | Trip caused by cooling water pump failure | 24.8833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-04-03 | 13:53 | 14:58 | forced | 2 | BLA | Trip caused by cooling control system maintenance | 1.0833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-04-03 | 14:42 | 14:56 | forced | 3 | BLA | Trip caused by cooling control system maintenance | 0.23333 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-04-06 | 20:06 | to
2013-04-23 | to | 12:47 | forced | 3 | Both | Cable fault P2 (-ve) cable | 400.6833 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-04-22 | 6:59 | to
2013-04-22 | to | 16:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 9.0167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-04-22 | 16:00 | to
2013-04-23 | to | 14:03 | forced | 2 | Both | Return to service after cable repair outage delayed by valve control fault. | 22.05 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-07-29 | 10:00 | 13:38 | Scheduled | 2 | BLA | Outage to allow Essential Energy access at Terranora to position a crane. | 3.6333 | External | #VALUE! | #VALUE! | #VALUE!
2013-07-29 | 10:00 | 15:05 | Scheduled | 3 | BLA | Outage to allow Essential Energy access at Terranora to position a crane. | 5.0833 | External | #VALUE! | #VALUE! | #VALUE!
2013-07-29 | 13:38 | to
2013-08-06 | to | 18:00 | forced | 2 | BLA | Mullumbimby tripped because of too many faulty IGBTs. | 196.3667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-08-06 | 6:06 | to
2013-08-06 | to | 18:00 | Scheduled | 3 | BLA | Outage to de-energise the overhead buss to allow replacement of CT in the transformers of system 1 and system 2. | 11.9 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-08-06 | 18:00 | to
2014-01-01 | to | 0:00 | forced | 3 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 3534 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2013-08-06 | 18:00 | to
2014-01-01 | to | 0:00 | forced | 2 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 3534 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2014-01-01 | 0:00 | to
2015-01-01 | to | 0:00 | forced | 1 | MUL | Trip caused by fire in converter building. | 8760 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2014-01-01 | 0:00 | to
2014-01-21 | to | 17:07 | forced | 3 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 497.1167 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2014-01-01 | 0:00 | to
2014-02-11 | to | 12:10 | forced | 2 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 996.1667 | Maintenance | #VALUE! | #VALUE! | #VALUE!
2014-02-11 | 13:07 | to
2014-02-14 | to | 13:37 | forced | 2 | BLA | Trip caused by filter capacitor unbalanced protection. Return to service delayed by too many faulty IGBTs. | 72.5 | Maintenance
2014-02-14 | 14:34 | to
2014-02-28 | to | 13:05 | forced | 2 | Both | Cable fault P2 (-ve) cable | 334.5167 | Maintenance
2014-02-27 | 6:26 | 18:28 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 12.0333 | Maintenance
2014-03-01 | 8:28 | to
2014-03-21 | to | 17:33 | forced | 2 | Both | Cable fault P1 (+ve) cable | 489.0833 | Maintenance
2014-03-04 | 10:29 | to
2014-03-04 | to | 12:26 | forced | 3 | BLA | LEM Power supply intermittent fault caused operation of the over current protection | 1.95 | Maintenance
2014-03-12 | 6:05 | 14:58 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 8.8833 | Maintenance
2014-03-29 | 13:14 | to
2014-04-17 | to | 13:56 | forced | 3 | Both | Cable fault P1 (+ve) cable | 456.7 | Maintenance
2014-04-03 | 7:26 | 8:22 | forced | 2 | MUL | Fire system maintenance contrctor caused trip while doing maintenance | 0.93333 | Maintenance
2014-04-10 | 16:57 | 18:13 | forced | 2 | MUL | Fire system trip. No evidence of fire found. Suspect faulty fire system interface card. | 1.2667 | Maintenance
2014-04-11 | 8:06 | 14:16 | Scheduled | 2 | Both | Outage to excavate System 2 cable fault | 6.1667 | Maintenance
2014-04-16 | 7:28 | 17:33 | Scheduled | 2 | Both | Outage to excavate System 2 cable fault | 10.0833 | Maintenance
Note on A547: Continued from cable fault outage 17-Dec-09 22:14
Note on B840: Stuart Dodds: Zero dispatch received at 7:02. PCP problems. Converter blocked at 7:23
Note on C426: Stuart Dodds: Pole 1 Deblocked 14:29:00
Note on C428: Stuart Dodds: Pole 1 Deblocked 14:29:00
Note on G357: Outage extended to allow valve chamber to dry.

## Sheet2
2007-01-07 07:00 | 2007-01-07 12:20 | forced | 2 | MUL | Computer failure at Mullumbimby | 5.3333
2007-01-01 | 2007-02-08 18:00 | forced | 1 | BLA | Transformer differential trip, suspected loose core lamination. This portion of the outage is in 2007 | 930
2007-03-17 08:28 | 2007-03-17 16:31 | scheduled | 1 | MUL | Repairs to galvanised steel troughing | 8.05
2007-03-17 08:59 | 2007-03-17 16:32 | scheduled | 3 | MUL | Repairs to galvanised steel troughing | 7.55
2007-03-17 08:59 | 2007-03-18 17:14 | forced | 2 | BLA | PCP mach2 computer failed during switching for planned repairs. | 32.25
2007-03-18 08:25 | 2007-03-18 17:14 | scheduled | 1 | BLA | Repairs to galvanised steel troughing | 8.8167
2007-03-18 08:25 | 2007-03-18 17:14 | scheduled | 3 | BLA | Repairs to galvanised steel troughing | 8.8167
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 1 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 2 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 3 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167
2007-04-09 13:29 | 2007-04-09 16:35 | forced | 1 | MUL | Loss of pole 1, caused by 11kV fault. | 3.1
2007-04-16 09:30 | 2007-04-16 11:00 | scheduled | 1 | Both | Single system outage for site visits | 1.5
2007-05-04 08:30 | 2007-05-04 11:30 | scheduled | 1 | both | Single system outage for site visits | 3
2007-05-25 08:56 | 2007-07-25 10:41 | forced | 3 | both | Cooling water leak in valve hall, phase reactor failure. | 1465.75
2007-05-25 10:51 | 2007-05-25 14:36 | forced | 2 | both | Pole 2 tripped, no fault found, returned to service. | 3.75
2007-06-02 22:13 | 2007-06-07 16:11 | forced | 2 | both | More than 5 IGBTs failed in a stack. | 113.9667
2007-06-07 01:58 | 2007-06-27 14:03 | forced | 1 | both | DC cable fault | 492.0833
2007-06-16 12:14 | 2007-06-18 09:56 | forced | 2 | both | A Powerlink fault at Mudgeeraba caused the loss of 110kV supplies to Terranora. | 45.7
2007-06-18 10:18 | 2007-06-18 10:29 | forced | 2 | BLA | Power supply problem in PCPB Mach 2 | 0.18333
2007-06-29 05:55 | 2007-06-29 05:58 | forced | 1 | MUL | Spurious trip, unknown cause | 0.05
2007-06-29 05:55 | 2007-06-29 05:58 | forced | 2 | MUL | Spurious trip, unknown cause | 0.05
2007-07-09 16:21 | 2007-07-10 11:50 | forced | 2 | BLA | Cooling equipment fault at Bungalora pole 2 | 19.4833
2007-07-18 08:32 | 2007-07-18 13:05 | scheduled | 1 | BLA | Inspection of phase reactors at Bungalora | 4.55
2007-07-19 08:32 | 2007-07-19 13:12 | forced | 2 | MUL | Spurious trip, unknown cause | 4.6667
2007-08-01 15:30 | 2007-08-02 12:45 | forced | 3 | both | Pole 3 tripped, unknown cause. | 21.25
2007-09-04 07:01 | 2007-09-04 20:02 | scheduled | 1 | both | Annual maintenance | 13.0167
2007-09-05 14:22 | 2007-09-06 00:19 | scheduled | 2 | both | Annual maintenance | 9.95
2007-09-06 07:00 | 2007-09-06 18:45 | scheduled | 3 | both | Annual maintenance | 11.75
2007-10-05 12:17 | 2007-11-15 14:30 | forced | 1 | BLA | Differential trip at Bungalora | 986.2167
2007-10-26 22:30 | 2007-10-26 23:21 | forced | 2 | Both | Fault on 132kV system | 0.85
2007-10-26 22:30 | 2007-10-26 23:21 | forced | 3 | Both | Fault on 132kV system | 0.85
2007-11-05 11:00 | 2007-11-05 13:10 | scheduled | 2 | Both | Systems 2 & 3 down for excavation on system 1 | 2.1667
2007-11-05 11:00 | 2007-11-05 13:10 | scheduled | 3 | Both | Systems 2 & 3 down for excavation on system 1 | 2.1667
2007-11-27 07:15 | 2007-11-27 17:00 | scheduled | 1 | both | Maintenance - Phase Reactors and IGBTs. Control system faults prevent return to service. | 9.75
2007-11-27 17:00 | 2007-12-19 17:00 | forced | 1 | MUL | Computer failure on pole 1 at Mullumbimby. | 528
2007-11-28 07:15 | 2007-11-28 17:00 | scheduled | 2 | both | Maintenance - Phase Reactors and IGBTs. Control system faults prevent return to service. | 9.75
2007-11-28 17:00 | 2007-12-20 18:05 | forced | 2 | both | Computer failure on pole 2 at Mullumbimby. | 529.0833
2007-11-29 08:08 | 2007-11-29 15:14 | scheduled | 3 | both | Maintenance - Phase Reactors and IGBTs. | 7.1
2007-12-30 13:10 | 2008-01-01 | forced | 2 | BLA | Auxiliary Power Failure caused control system problems | 34.8333
2007-12-30 13:10 | 2008-01-01 | forced | 3 | BLA | Auxiliary Power Failure caused control system problems | 34.8333
2008-01-01 | 2008-01-02 16:50 | forced | 3 | BLA | Auxiliary Power Failure caused control system problems | 40.8331
2008-01-01 | 2008-01-02 20:09 | forced | 2 | BLA | Auxiliary Power Failure caused control system problems | 44.1497
2008-02-02 22:11 | 2008-02-03 10:48 | forced | 2 | MUL | Control System Faults | 12.6167
2008-02-13 08:30 | 2008-02-13 17:00 | scheduled | 1 | both | Shutdown to investigate various faults | 8.5
2008-02-19 06:00 | 2008-02-21 00:27 | forced | 2 | both | Computer failure on pole 2 | 42.45
2008-02-20 07:00 | 2008-02-20 11:00 | scheduled | 1 | both | Fire System Maintenance | 4
2008-02-20 11:05 | 2008-02-20 13:50 | scheduled | 3 | both | Fire System Maintenance | 2.75
2008-02-27 08:00 | 2008-02-27 10:35 | scheduled | 1 | BLA | Installation of power flow monitoring gear | 2.5833
2008-02-27 10:12 | 2008-02-27 13:46 | scheduled | 2 | BLA | Installation of power flow monitoring gear | 3.5667
2008-02-27 11:00 | 2008-02-27 15:34 | scheduled | 3 | BLA | Installation of power flow monitoring gear | 4.5667
2008-03-08 19:31 | 2008-03-28 13:00 | forced | 2 | both | Cable fault | 473.4833
2008-03-13 16:07 | 2008-04-04 15:00 | forced | 1 | both | Cable fault | 526.8833
2008-03-18 09:35 | 2008-03-18 12:20 | scheduled | 3 | both | Outage to safely excavate sys1 cables for repair | 2.75
2008-03-30 14:07 | 2008-03-30 18:00 | forced | 3 | both | Unknown fault caused converter to trip | 3.8833
2008-04-09 07:25 | 2008-04-09 15:35 | scheduled | 3 | both | Phase reactor inspections | 8.1667
2008-04-10 07:25 | 2008-04-10 14:56 | scheduled | 2 | both | Phase reactor inspections | 7.5167
2008-04-11 07:08 | 2008-04-24 17:32 | scheduled | 1 | both | Phase reactor inspections and Transformer swap out | 322.4
2008-04-13 07:00 | 2008-04-13 17:00 | scheduled | 2 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10
2008-04-13 07:00 | 2008-04-13 17:00 | scheduled | 3 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10
2008-04-16 07:00 | 2008-04-16 17:00 | scheduled | 2 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10
2008-04-16 07:00 | 2008-04-16 17:00 | scheduled | 3 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10
2008-04-14 15:09 | 2008-05-01 16:00 | forced | 2 | both | System 2 Cable fault | 408.85
2008-05-12 08:00 | 2008-05-15 18:45 | scheduled | 1 | both | Phase reactor repairs | 82.75
2008-05-15 17:00 | 2008-05-15 18:45 | scheduled | 2 | both | Communications Test | 1.75
2008-05-15 17:00 | 2008-05-15 18:45 | scheduled | 3 | both | Communications Test | 1.75
2008-05-16 08:00 | 2008-05-17 13:40 | scheduled | 3 | both | Phase reactor repairs | 29.6667
2008-05-18 08:00 | 2008-05-19 14:11 | scheduled | 2 | both | Phase reactor repairs | 30.1833
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 1 | both | Comms cut over for trial operation | 2
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 2 | both | Comms cut over for trial operation | 2
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 3 | both | Comms cut over for trial operation | 2
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 1 | both | Comms cut over after trial operation | 0.5
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 2 | both | Comms cut over after trial operation | 0.5
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 3 | both | Comms cut over after trial operation | 0.5
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 1 | both | Comms cut over for trial operation | 0.58333
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 2 | both | Comms cut over for trial operation | 0.58333
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 3 | both | Comms cut over for trial operation | 0.58333
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 1 | both | Comms cut over after trial operation | 0.33333
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 2 | both | Comms cut over after trial operation | 0.33333
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 3 | both | Comms cut over after trial operation | 0.33333
2008-05-22 20:12 | 2008-05-23 16:05 | forced | 3 | both | Reactor cooling fan fault. | 19.8833
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 1 | both | Final comms cut over. | 0.41667
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 2 | both | Final comms cut over. | 0.41667
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 3 | both | Final comms cut over. | 0.41667
2008-06-09 03:21 | 2008-06-10 17:06 | forced | 3 | BLA | PCPA hard disk fault | 37.75
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 1 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 2 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 3 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 1 | MUL | Country Energy outage to connect CB 7H3 | 13.4167
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 2 | MUL | Country Energy outage to connect CB 7H3 | 13.4167
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 3 | MUL | Country Energy outage to connect CB 7H3 | 13.4167
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 1 | both | Comms fault from Dandenong to DL | 1.75
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 2 | both | Comms fault from Dandenong to DL | 1.75
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 3 | both | Comms fault from Dandenong to DL | 1.75
2008-06-25 20:40 | 2008-06-27 18:00 | forced | 1 | BLA | Faulty IGBTs | 45.3333
2008-06-27 22:47 | 2008-07-09 15:43 | forced | 2 | both | Cable Fault | 280.9333
2008-06-29 03:30 | 2008-06-29 08:00 | forced | 1 | MUL | TransGrid Tripping Scheme operation | 4.5
2008-06-29 03:30 | 2008-06-29 08:00 | forced | 3 | MUL | TransGrid Tripping Scheme operation | 4.5
2008-06-29 08:00 | 2008-06-29 10:27 | forced | 1 | MUL | Mach 2 faults after TransGrid Tripping Scheme operation | 2.4497
2008-06-29 08:00 | 2008-06-29 10:27 | forced | 3 | MUL | Mach 2 faults after TransGrid Tripping Scheme operation | 2.4497
2008-07-11 07:00 | 2008-07-11 18:43 | forced | 3 | BLA | Reactor Fan Trip | 11.7167
2008-07-12 08:25 | 2008-07-12 16:15 | scheduled | 1 | BLA | Valve Cooling Water Leak Inspection | 7.8333
2008-07-14 11:03 | 2008-08-04 14:54 | forced | 2 | both | Cable fault | 507.85
2008-07-20 01:02 | 2008-07-20 05:29 | scheduled | 1 | both | Country Energy outage | 4.45
2008-07-20 01:02 | 2008-07-20 05:29 | scheduled | 3 | both | Country Energy outage | 4.45
2008-07-25 09:03 | 2008-07-25 11:20 | scheduled | 1 | both | Outage to excavate Cables for repair to system 2 cable fault | 2.2833
2008-07-25 09:03 | 2008-07-25 11:20 | scheduled | 3 | both | Outage to excavate Cables for repair to system 2 cable fault | 2.2833
2008-07-25 11:20 | 2008-08-01 16:15 | forced | 3 | 0 | After outage to excavate cables for repair to system 2 cable fault, L2 phase of system 3 circuit breaker would not close. | 172.9167
2008-07-31 09:46 | 2008-07-31 14:35 | scheduled | 1 | both | Outage to excavate Cables for repair to system 2 cable fault | 4.8167
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 1 | both | Abnormal frequency trip | 5.8833
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 2 | both | Abnormal frequency trip | 5.8833
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 3 | both | Abnormal frequency trip | 5.8833
2007-08-19 01:51 | 2007-08-19 14:43 | forced | 3 | both | Abnormal frequency trip | 12.8667
2008-09-16 07:00 | 2008-09-18 17:26 | scheduled | 2 | both | Annual Maintenance | 58.4333
2008-09-18 07:30 | 2008-09-19 17:00 | scheduled | 3 | both | Annual Maintenance | 33.5
2008-09-19 17:00 | 2008-09-21 07:00 | forced | 3 | both | Mullumbimby sytem 3 control system fault | 38
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 1 | both | Country energy requested outage for maintenance at Terranora | 9
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 2 | both | Country energy requested outage for maintenance at Terranora | 9
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 3 | both | Country energy requested outage for maintenance at Terranora | 9
2008-09-21 16:00 | 2008-10-07 16:05 | forced | 3 | both | Mullumbimby sytem 3 control system fault | 384.0833
2008-09-20 07:00 | 2008-09-21 07:00 | scheduled | 1 | both | Annual Maintenance | 24
2008-09-21 16:00 | 2008-09-25 15:55 | forced | 1 | both | Bungalora pre-insertion resistor overload trip - earths left on in the barn | 95.9167
2008-09-25 14:22 | 2008-09-25 20:17 | forced | 2 | both | Mullumbimby reactor cooling fan trip | 5.9167
2008-10-01 18:17 | 2008-11-14 19:11 | forced | 2 | both | Cable Fault P1 cable. | 1056.9
2008-11-07 13:59 | 2008-11-14 18:51 | forced | 1 | both | Cable Fault P1 cable. | 172.8667
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 1 | BLA | Auxiliary power failure | 1.5667
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 2 | BLA | Auxiliary power failure | 1.5667
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 3 | BLA | Auxiliary power failure | 1.5667
2008-11-24 07:02 | 2008-11-24 15:02 | scheduled | 1 | both | Phase Reactor Inspections and cable clamp modifications | 8
2008-11-25 06:54 | 2008-11-25 15:36 | scheduled | 2 | both | Phase Reactor Inspections and cable clamp modifications | 8.7
2008-11-26 07:05 | 2008-11-26 14:45 | scheduled | 3 | both | Phase Reactor Inspections and cable clamp modifications | 7.6667
2008-11-27 07:10 | 2008-11-27 13:14 | scheduled | 1 | both | Phase Reactor Inspections and cable clamp modifications | 6.0667
2008-12-08 01:18 | 2008-12-16 13:12 | forced | 2 | both | Cable Fault P1 cable. | 203.9
2008-12-15 08:10 | 2008-12-15 10:25 | scheduled | 1 | both | Outage to locate Pole 1 cable fault | 2.25
2008-12-15 08:17 | 2008-12-15 10:28 | scheduled | 3 | both | Outage to locate Pole 1 cable fault | 2.1833
2008-12-19 23:06 | 2008-12-31 09:42 | forced | 2 | both | Cable Fault P1 cable. | 274.6
2008-12-30 07:47 | 2008-12-30 09:22 | scheduled | 1 | both | Outage to locate Pole 1 cable fault | 1.5833
2008-12-30 07:41 | 2008-12-30 09:24 | scheduled | 3 | both | Outage to locate Pole 1 cable fault | 1.7167
2008-12-31 11:13 | 2009-01-01 | forced | 2 | both | Cable Fault P1 cable. | 12.7831
2009-01-01 | 2009-01-20 09:22 | forced | 2 | both | Cable Fault P1 cable. | 465.3667
2009-01-11 13:00 | 2009-01-19 12:06 | forced | 1 | both | Cable Fault P1 cable. | 191.1
2009-01-16 07:00 | 2009-01-16 14:01 | scheduled | 3 | both | Outage to repair Pole 1 and Pole 2 cable faults | 7.0167
2009-02-09 21:00 | 2009-02-18 10:53 | forced | 2 | both | Cable Fault P1 cable. | 205.8833
2009-02-10 07:26 | 2009-02-10 12:01 | scheduled | 1 | both | Outage for Country Energy maintenance - 110kV bus at Terranora substation | 4.5833
2009-02-10 07:36 | 2009-02-10 12:06 | scheduled | 3 | both | Outage for Country Energy maintenance - 110kV bus at Terranora substation | 4.5
2009-02-16 09:05 | 2009-02-16 13:05 | scheduled | 1 | both | Outage to repair Pole 2 cable fault | 4
2009-02-16 09:07 | 2009-02-16 13:06 | scheduled | 3 | both | Outage to repair Pole 2 cable fault | 3.9833
2009-02-16 13:17 | 2009-02-16 14:59 | scheduled | 1 | both | Outage to repair Pole 2 cable fault | 1.7
2009-02-16 13:16 | 2009-02-16 15:00 | scheduled | 3 | both | Outage to repair Pole 2 cable fault | 1.7333
2009-03-10 07:31 | 2009-03-10 15:23 | scheduled | 3 | both | Outage for six month maintenance | 7.8667
2009-03-11 07:31 | 2009-03-11 13:54 | scheduled | 2 | both | Outage for six month maintenance | 6.3833
2009-03-12 07:03 | 2009-03-13 08:02 | scheduled | 1 | both | Outage for six month maintenance | 24.9833
2009-03-17 09:40 | 2009-03-30 13:51 | forced | 3 | both | Cable Fault P1 & P2 cable. | 316.1833
2009-03-26 07:04 | 2009-03-26 15:51 | scheculed | 1 | both | Outage to repair Pole 3 cable fault | 8.7833
2009-03-26 07:37 | 2009-03-26 15:53 | scheculed | 2 | both | Outage to repair Pole 3 cable fault | 8.2667
2009-03-27 07:03 | 2009-03-27 13:24 | scheculed | 1 | both | Outage to repair Pole 3 cable fault | 6.35
2009-03-27 07:08 | 2009-03-27 13:26 | scheculed | 2 | both | Outage to repair Pole 3 cable fault | 6.3
2009-04-15 10:01 | 2009-04-15 11:28 | scheculed | 1 | both | Outage for access valve enclosure lock change | 1.45
2009-04-15 11:48 | 2009-04-15 13:57 | scheculed | 2 | both | Outage for access valve enclosure lock change | 2.15
2009-04-15 14:08 | 2009-04-15 15:23 | scheculed | 3 | both | Outage for access valve enclosure lock change | 1.25
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.3
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.3
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.3
2009-05-20 20:46 | 2009-05-20 23:31 | forced | 1 | BLA | Auxilary power outage caused a reactor cooling fan changeover. Dampers did not open in time causing a trip. | 2.75
2009-05-21 05:10 | 2009-05-21 06:52 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Return delayed to investigate a CB Relay fault. | 1.7
2009-05-21 05:10 | 2009-05-21 05:24 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.23333
2009-05-21 05:10 | 2009-05-21 05:24 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.23333
2009-05-22 04:32 | 2009-05-22 04:38 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.1
2009-05-22 04:32 | 2009-05-22 04:39 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.11667
2009-05-22 04:32 | 2009-05-22 04:40 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.13333
2009-05-22 07:59 | 2009-05-22 08:59 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 1
2009-05-22 07:59 | 2009-05-22 09:03 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 1.0667
2009-05-22 07:59 | 2009-05-22 09:03 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 1.0667
2009-05-22 15:18 | 2009-05-22 16:34 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 1.2667
2009-05-22 15:18 | 2009-05-22 15:48 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.5
2009-05-22 15:18 | 2009-05-22 15:48 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.5
2009-05-23 17:22 | 2009-05-24 13:22 | forced | 3 | MUL | AC Filter capacitor protection trip. | 20
2009-05-23 19:02 | 2009-05-23 19:15 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.21667
2009-05-23 19:02 | 2009-05-23 19:14 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.2
2009-05-23 19:34 | 2009-05-23 19:40 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.1
2009-05-23 19:34 | 2009-05-23 19:41 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.11667
2009-05-26 18:02 | 2009-06-06 13:08 | forced | 2 | Both | Cable fault P1 cable, Return to service delayed by too any Faulty IGBTs in B phase | 259.1
2009-06-02 11:54 | 2009-06-02 12:10 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.26667
2009-06-02 11:54 | 2009-06-02 12:10 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.26667
2009-06-02 12:15 | 2009-06-02 14:28 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 2.2167
2009-06-02 12:15 | 2009-06-02 14:28 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 2.2167
2009-06-03 09:16 | 2009-06-03 14:49 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 5.55
2009-06-03 09:16 | 2009-06-03 14:51 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.5833
2009-06-30 06:50 | 2009-07-18 10:29 | forced | 2 | Both | Cable fault P1 cable, Return to service delayed by too any Faulty IGBTs in B phase | 435.65
2009-07-14 09:04 | 2009-07-14 14:19 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 5.25
2009-07-14 09:13 | 2009-07-14 14:21 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 5.1333
2009-07-15 08:36 | 2009-07-15 10:24 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 1.8
2009-07-15 08:38 | 2009-07-15 10:21 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 1.7167
2009-07-16 09:12 | 2009-07-16 17:32 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 8.3333
2009-07-16 09:02 | 2009-07-16 17:29 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 8.45
2009-07-16 17:29 | 2009-07-21 17:38 | forced | 1 | Both | Unable to return to service. Too many faulty igbts. | 120.15
2009-07-20 18:28 | 2009-07-21 09:54 | forced | 2 | Both | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 15.4333
2009-07-20 18:28 | 2009-07-21 09:56 | forced | 3 | Both | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 15.4667
2009-07-27 06:36 | 2009-07-28 17:04 | Scheduled | 1 | Both | Shutdown for annual maintenance | 34.4667
2009-07-29 06:49 | 2009-07-30 17:26 | Scheduled | 2 | Both | Shutdown for annual maintenance | 34.6167
2009-07-31 06:32 | 2009-08-01 13:02 | Scheduled | 3 | Both | Shutdown for annual maintenance | 30.5
2009-08-14 10:52 | 2009-08-14 11:38 | forced | 1 | Both | Trip caused by flow protection. Standby pump did not start when pumps changed during while converter was running. | 0.76667
2009-08-25 13:27 | 2009-08-29 14:54 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 97.45
2009-08-27 08:14 | 2009-08-27 16:47 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 8.55
2009-08-27 08:07 | 2009-08-27 16:49 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 8.7
2009-08-27 17:11 | 2009-08-27 21:20 | forced | 1 | MUL | Trip caused by Coutry Energy protection operation. Failed protection CT in Mullumbimby system 3 transformer | 4.15
2009-08-27 17:11 | 2009-09-04 17:04 | forced | 3 | MUL | Trip caused by Coutry Energy protection operation. Failed protection CT in Mullumbimby system 3 transformer | 191.8833
2009-09-04 07:22 | 2009-09-04 16:49 | Scheduled | 1 | MUL | Outage for HV access to repair failed protection CT in Mullumbimby system 3 transformer | 9.45
2009-09-04 07:23 | 2009-09-04 16:50 | Scheduled | 2 | MUL | Outage for HV access to repair failed protection CT in Mullumbimby system 3 transformer | 9.45
2009-09-29 07:04 | 2009-09-29 17:14 | Scheduled | 1 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.1667
2009-09-29 07:07 | 2009-09-29 17:39 | Scheduled | 2 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.5333
2009-09-29 07:09 | 2009-09-29 17:18 | Scheduled | 3 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.15
2009-11-03 13:23 | 2009-11-03 14:01 | forced | 3 | BLA | Trip by Flow Protection - Active CCP accidentally reset during maintenance | 0.63333
2009-11-04 02:42 | 2009-11-13 10:18 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 223.6
2009-11-10 17:50 | 2009-11-10 18:44 | forced | 3 | Bla | Fault with 24V DC power supply | 0.9
2009-11-11 10:11 | 2009-11-11 16:08 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.95
2009-11-11 10:16 | 2009-11-11 16:06 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 5.8333
2009-11-19 01:51 | 2009-11-28 09:57 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 224.1
2009-11-20 02:17 | 2009-11-20 02:55 | forced | 2 | MUL | Abnormal Frequency Trip. Country Energy System Problems. | 0.63333
2009-11-20 02:17 | 2009-11-20 02:56 | forced | 3 | MUL | Abnormal Frequency Trip. Country Energy System Problems. | 0.65
2009-11-26 09:06 | 2009-11-26 14:59 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.8833
2009-11-26 09:15 | 2009-11-26 14:57 | Scheduled | 2 | Both | Outage to enable access to repair the system 2 cable. | 5.7
2009-11-27 10:28 | 2009-11-27 11:03 | forced | 3 | MUL | Damper Resistor overload trip event on one PCP. Converter tripped while trying to clear the event. | 0.58333
2009-11-28 10:30 | 2009-12-17 14:49 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 460.3167
2009-12-11 00:52 | 2009-12-11 02:16 | forced | 1 | BLA | Operation of Powerlink intertrip scheme. | 1.4
2009-12-11 00:52 | 2009-12-11 02:17 | forced | 3 | BLA | Operation of Powerlink intertrip scheme. | 1.4167
2009-12-12 08:13 | 2009-12-12 08:58 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.75
2009-12-12 08:13 | 2009-12-12 08:59 | forced | 3 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.76667
2009-12-15 07:02 | 2009-12-15 17:07 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 10.0833
2009-12-15 07:20 | 2009-12-15 17:04 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 9.7333
2009-12-17 22:14 | 2010-01-01 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 337.7664
2010-01-08 18:49 | 2010-01-08 19:11 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.36667
2010-01-08 18:49 | 2010-01-08 19:13 | forced | 3 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.4
2010-01-09 13:04 | 2010-03-31 14:01 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 1944.95
2010-01-12 07:16 | 2010-01-12 16:16 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 9
2010-01-13 13:37 | 2010-01-21 09:56 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 188.3167
2010-01-01 | 2010-01-14 09:14 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 321.2333
2010-01-15 07:23 | 2010-01-15 08:05 | forced | 2 | 0 | Trip during control system maintenance | 0.7
2010-01-19 07:03 | 2010-01-19 14:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 7.15
2010-01-20 21:01 | 2010-01-20 21:34 | forced | 2 | 0 | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.55
2010-01-27 05:30 | 2010-03-31 13:54 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 1520.4
2010-03-27 06:04 | 2010-03-27 17:35 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. | 11.5167
2010-03-28 06:04 | 2010-03-28 15:41 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 9.6167
2010-03-31 23:18 | 2010-04-17 09:26 | forced | 1 | Both | Cable fault P1 (+ve) cable. After cable repair, fault with DC voltage measuring delayed return to service. | 394.1333
2010-04-17 09:26 | 2010-04-28 13:37 | forced | 1 | Both | Fault with DC voltage measuring delayed return to service after repair P1 (+ve) cable, | 268.1833
2010-04-09 17:48 | 2010-04-20 13:44 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 259.9333
2010-04-14 07:04 | 2010-04-15 15:51 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. Too many faulty igbts when energised from Mullumbimby. Igbts repaired the next day during system 2 cable fault repair. | 32.7833
2010-04-30 19:18 | 2010-06-13 10:34 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 1047.2667
2010-05-05 11:00 | 2010-05-05 13:14 | forced | 1 | BLA | Trip during fault finding of PCPB DC voltage measuring | 2.2333
2010-05-24 07:14 | 2010-05-28 14:24 | Scheduled | 3 | Both | Outage to replace transformer CTs | 103.1667
2010-05-25 07:03 | 2010-05-25 19:33 | Scheduled | 1 | Both | Outage to allow overhead crane access for replacing system 3 transformer CTs | 12.5
2010-05-31 10:05 | 2010-05-31 17:23 | Scheduled | 1 | Both | Outage to excavate the system 2 cable fault. | 7.3
2010-05-31 10:10 | 2010-05-31 17:26 | Scheduled | 3 | Both | Outage to excavate the system 2 cable fault under the river. | 7.2667
2010-05-31 17:26 | 2010-06-08 13:18 | forced | 3 | Both | Outage to excavate the system 2 cable fault. Return to service delayed due to VCU Faults. | 187.8667
2010-06-01 13:43 | 2010-06-01 14:33 | Scheduled | 1 | Both | Outage to cut system 2 cable during repair of fault under the river. | 0.83333
2010-06-03 06:55 | 2010-06-03 17:48 | Scheduled | 1 | Both | Outage to joint system 2 cable during repair of fault under the river. | 10.8833
2010-06-04 07:00 | 2010-06-04 16:15 | Scheduled | 1 | Both | Outage to joint system 2 cable during repair of fault under the river. | 9.25
2010-06-10 02:02 | 2010-06-10 16:02 | forced | 3 | BLA | Trip due to low water level. Pump leaking. | 14
2010-07-06 01:03 | 2010-07-06 16:18 | forced | 2 | MUL | UPS failure caused trip of converter | 15.25
2010-07-15 22:07 | 2010-07-26 08:19 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 250.2
2010-07-22 06:03 | 2010-07-22 17:22 | Scheduled | 1 | BLA | CE Requested Outage - Terranora Bus zone breakers | 11.3167
2010-07-22 06:06 | 2010-07-22 17:23 | Scheduled | 3 | BLA | CE Requested Outage - Terranora Bus zone breakers | 11.2833
2010-07-22 17:22 | 2010-07-26 07:00 | forced | 1 | MUL | Return to serivce delayed - Too many faulty IGBTs | 85.6333
2010-07-22 17:23 | 2010-07-26 07:00 | forced | 3 | BLA | Return to serivce delayed - Too many faulty IGBTs | 85.6167
2010-07-26 07:00 | 2010-07-28 14:39 | Scheduled | 3 | Both | Annual Maintenance | 55.65
2010-07-26 07:00 | 2010-07-29 15:18 | Scheduled | 1 | Both | Annual Maintenance | 80.3
2010-07-28 15:02 | 2010-07-29 14:44 | forced | 3 | BLA | Phase reactor partial discharge repair | 23.7
2010-07-30 08:41 | 2010-07-31 16:49 | Scheduled | 2 | Both | Annual Maintenance | 32.1333
2010-07-31 16:49 | 2010-08-06 13:25 | forced | 2 | MUL | Return to serivce delayed - faulty control system components | 140.6
2010-07-31 08:38 | 2010-07-31 10:00 | Scheduled | 1 | MUL | CE Requested Outage - Lismore Tripping Scheme Work | 1.3667
2010-07-31 08:46 | 2010-07-31 10:01 | Scheduled | 3 | MUL | CE Requested Outage - Lismore Tripping Scheme Work | 1.25
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 1 | BLA | Auxiliary power failure | 0.88333
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 2 | BLA | Auxiliary power failure | 0.88333
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 3 | BLA | Auxiliary power failure | 0.88333
2010-08-09 08:37 | 2010-08-11 13:40 | forced | 1 | BLA | Restoration after auxiliary power failure | 53.05
2010-08-09 08:37 | 2010-08-09 15:58 | forced | 2 | BLA | Restoration after auxiliary power failure | 7.35
2010-08-09 08:37 | 2010-08-09 09:43 | forced | 3 | BLA | Restoration after auxiliary power failure | 1.1
2010-08-10 12:04 | 2010-08-10 18:39 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 6.5833
2010-08-10 12:06 | 2010-08-10 18:35 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 6.4833
2010-08-11 06:04 | 2010-08-11 13:42 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 7.6333
2010-08-11 06:05 | 2010-08-11 13:41 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 7.6
2010-08-14 06:08 | 2010-08-14 12:44 | Scheduled | 1 | BLA | County Energy Requested outage for work at Terranora | 6.6
2010-08-14 06:10 | 2010-08-14 12:45 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 6.5833
2010-08-14 06:11 | 2010-08-14 12:46 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 6.5833
2010-08-15 06:03 | 2010-08-15 11:50 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 5.7833
2010-08-15 06:05 | 2010-08-15 11:48 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 5.7167
2010-08-15 06:06 | 2010-08-15 11:46 | Scheduled | 1 | BLA | County Energy Requested outage for work at Terranora | 5.6667
2010-08-22 04:00 | 2010-08-22 15:04 | forced | 2 | BLA | Reactor cooling fans tripped converter | 11.0667
2010-08-25 09:46 | 2010-08-25 11:27 | forced | 2 | BLA | Trip caused by control system maintenance | 1.6833
2010-09-02 12:50 | 2010-09-02 13:28 | Scheduled | 3 | BLA | Outage requested by Country Energy for protection testing | 0.63333
2010-09-02 12:51 | 2010-09-02 13:28 | Scheduled | 2 | BLA | Outage requested by Country Energy for protection testing | 0.61667
2010-09-02 12:51 | 2010-09-02 13:27 | Scheduled | 1 | BLA | Outage requested by Country Energy for protection testing | 0.6
2010-09-18 02:43 | 2010-10-01 12:08 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 321.4167
2010-09-19 02:02 | 2010-10-01 12:42 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 298.6667
2010-09-27 08:02 | 2010-09-27 16:02 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. | 8
2010-09-27 08:01 | 2010-09-27 14:16 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 6.25
2010-10-06 16:23 | 2010-10-22 12:28 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 380.0833
2010-10-14 08:11 | 2010-10-14 15:01 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable. | 6.8333
2010-10-14 08:11 | 2010-10-14 15:03 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 6.8667
2010-10-17 10:06 | 2010-10-17 14:02 | forced | 2 | MUL | Trip caused by fire protection system fault. | 3.9333
2010-10-29 09:38 | 2010-10-29 11:08 | Scheduled | 1 | Both | Outage to repair GST damage. | 1.5
2010-11-08 06:06 | 2010-11-08 13:07 | Scheduled | 1 | MUL | Outage for CE Comms tower installation | 7.0167
2010-11-08 06:11 | 2010-11-08 13:08 | Scheduled | 2 | MUL | Outage for CE Comms tower installation | 6.95
2010-11-08 06:34 | 2010-11-08 13:09 | Scheduled | 3 | MUL | Outage for CE Comms tower installation | 6.5833
2010-11-09 06:04 | 2010-11-09 13:19 | Scheduled | 1 | MUL | Outage for CE Comms tower installation | 7.25
2010-11-09 06:09 | 2010-11-09 13:20 | Scheduled | 2 | MUL | Outage for CE Comms tower installation | 7.1833
2010-11-09 06:15 | 2010-11-09 13:21 | Scheduled | 3 | MUL | Outage for CE Comms tower installation | 7.1
2010-11-14 01:21 | 2010-11-20 08:14 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 150.8786
2010-11-18 07:07 | 2010-11-18 14:42 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable. | 7.5833
2010-11-18 07:10 | 2010-11-18 14:42 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 7.5333
2010-11-23 07:02 | 2010-11-24 15:30 | Scheduled | 1 | Both | IGBT/FO Test & Replacement | 32.4667
2010-11-24 15:30 | 2010-11-26 13:45 | forced | 1 | Both | IGBT Faults | 46.25
2010-11-25 21:15 | 2010-12-03 13:45 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 184.5
2010-11-30 07:05 | 2010-11-30 14:31 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 7.4333
2010-11-30 07:07 | 2010-11-30 14:33 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 7.4333
2010-12-06 06:46 | 2010-12-07 17:02 | Scheduled | 1 | Both | IGBT/FO Test & Investigation with ABB Mikael | 34.2667
2010-12-08 07:08 | 2010-12-09 14:48 | Scheduled | 2 | Both | IGBT/FO Test & Investigation with ABB Mikael | 31.6667
2010-12-09 14:51 | 2010-12-10 17:06 | Scheduled | 3 | Both | IGBT/FO Test & Investigation with ABB Mikael | 26.25
2010-12-12 14:39 | 2010-12-22 16:07 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 241.4667
2010-12-15 19:06 | 2010-12-23 10:29 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 183.3833
2010-12-17 07:01 | 2010-12-17 17:29 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 10.4667
2010-12-21 07:02 | 2010-12-21 17:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 10.1667
2010-12-25 01:01 | 2010-12-25 01:41 | forced | 1 | BLA | Auxiliary power failure - Rector cooling fans trip. | 0.66667
2010-12-27 13:03 | 2011-01-01 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 106.95
2011-01-01 | 2011-01-07 09:07 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 153.1167
2011-01-05 07:01 | 2011-01-05 14:15 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 7.2333
2011-01-05 07:04 | 2011-01-05 14:17 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 7.2167
2011-01-07 06:36 | 2011-01-17 09:35 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 242.9833
2011-01-10 15:21 | 2011-01-18 11:39 | forced | 2 | Both | Cable fault P2 (-ve) cable. | 188.3
2011-01-13 07:03 | 2011-01-13 14:28 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 7.4167
2011-01-14 07:01 | 2011-01-14 13:32 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable fault | 6.5167
2011-01-28 11:51 | 2011-02-10 13:59 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 314.1333
2011-02-09 07:11 | 2011-02-09 17:43 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 10.5333
2011-02-09 07:13 | 2011-02-09 18:10 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 10.95
2011-02-09 17:43 | 2011-02-14 17:24 | forced | 3 | Both | Outage due to BLA System 3, B Phase CB Pole leaking insulating gas. | 119.6833
2011-02-14 07:03 | 2011-02-14 16:10 | Scheduled | 1 | Both | Outage to enable access to the replacement of BLA System 3, B Phase CB Pole | 9.1167
2011-02-14 07:15 | 2011-02-14 17:41 | Scheduled | 2 | Both | Outage to enable access to the replacement of BLA System 3, B Phase CB Pole | 10.4333
2011-02-14 17:41 | 2011-02-18 11:31 | forced | 2 | MUL | Unable to return to service after planned outage. Too many faulty IGBTs | 89.8333
2011-02-15 07:13 | 2011-02-15 07:42 | forced | 1 | MUL | Outage due to control system fault. | 0.48333
2011-02-21 17:15 | 2011-02-21 18:31 | forced | 1 | BLA | Phase Reactor Cooling Fan L3 Trip | 1.2667
2011-03-13 12:24 | 2011-03-28 13:23 | forced | 1 | MUL | Trip due to flash over in PLC filter yard. Return to service delayed due to to many faulty IGBTs | 360.9833
2011-03-13 12:24 | 2011-03-13 19:31 | forced | 2 | MUL | Trip due to flash over in PLC filter yard. | 7.1167
2011-03-13 12:24 | 2011-03-13 19:34 | forced | 3 | MUL | Trip due to flash over in PLC filter yard. | 7.1667
2011-04-01 06:18 | 2011-04-01 13:48 | Scheduled | 1 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.5
2011-04-01 06:19 | 2011-04-01 13:49 | Scheduled | 2 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.5
2011-04-01 06:21 | 2011-04-01 13:49 | Scheduled | 3 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.4667
2011-04-01 13:49 | 2011-04-08 12:55 | forced | 2 | Both | Faulty IGBTs prevented return to service after CE outage. | 167.1
2011-04-18 16:05 | 2011-04-23 13:09 | forced | 1 | Both | Cable Fault P1 (+ve) cable. | 117.0667
2011-04-21 07:01 | 2011-04-21 15:26 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 8.4167
2011-04-21 07:02 | 2011-04-21 15:28 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 8.4333
2011-05-08 16:23 | 2011-06-11 16:25 | forced | 1 | Both | Outage caused by DC voltage imbalance. Return to service delayed by too many faulty IGBT optic fibres. | 816.0333
2011-05-14 11:26 | 2011-05-30 11:26 | forced | 3 | Both | Cable Fault P1 (+ve) cable. Return to service after cable fault repair delayed by too many faulty IGBTs | 384
2011-05-25 07:04 | 2011-05-25 18:32 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault. | 11.4667
2011-05-25 18:32 | 2011-07-22 10:15 | forced | 2 | Both | Unable to return to service after planned outage. Too many faulty IGBTs | 1383.7167
2011-06-10 02:56 | 2011-07-15 10:18 | forced | 3 | Both | Cable Fault P1 (+ve) cable. | 847.3667
2011-07-14 06:11 | 2011-07-14 20:25 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 14.2333
2011-07-15 10:30 | 2011-07-15 11:09 | forced | 3 | BLA | Cooling system trip - high water temperature - proportional valve failed to operate. | 0.65
2011-07-18 23:25 | 2011-07-30 09:38 | forced | 1 | Both | Cable Fault P2 (-ve) cable. | 274.2167
2011-07-22 10:50 | 2011-08-05 15:12 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 340.3667
2011-07-29 07:02 | 2011-07-29 18:48 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 11.7667
2011-07-30 09:38 | 2011-08-05 15:11 | forced | 1 | BLA | Unable to return to service after cable fault. Too many faulty IGBTs | 149.55
2011-08-05 07:07 | 2011-08-05 15:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 8.0833
2011-08-17 07:05 | 2011-08-17 14:07 | Scheduled | 1 | Both | Outage for CE Comms tower work | 7.0333
2011-08-17 07:17 | 2011-08-17 14:20 | Scheduled | 2 | Both | Outage for CE Comms tower work | 7.05
2011-08-17 07:24 | 2011-08-17 14:18 | Scheduled | 3 | Both | Outage for CE Comms tower work | 6.9
2011-08-22 16:08 | 2011-08-23 00:06 | forced | 3 | BLA | Rector Cooling fans faulty contactor | 7.9667
2011-08-22 16:08 | 2011-08-23 09:50 | forced | 1 | BLA | Rector Cooling fans faulty contactor | 17.7
2011-08-23 11:48 | 2011-08-23 12:14 | forced | 2 | MUL | Trip cause during replacement of UPS fault indicating relay | 0.43333
2011-08-25 07:07 | 2011-09-03 13:05 | forced | 3 | Both | Cable Fault P2 (-ve) cable. | 221.9667
2011-08-30 09:39 | 2011-08-30 10:17 | forced | 2 | BLA | Valve control fault during maintenance work | 0.63333
2011-08-31 11:52 | 2011-08-31 18:07 | Scheduled | 1 | Both | Outage for Coucil excavation of water pipe at Bungalora | 6.25
2011-08-31 11:54 | 2011-08-31 18:07 | Scheduled | 2 | Both | Outage for Coucil excavation of water pipe at Bungalora | 6.2167
2011-09-02 07:03 | 2011-09-02 17:49 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 10.7667
2011-09-02 07:04 | 2011-09-02 17:53 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 10.8167
2011-09-05 09:08 | 2011-09-05 18:52 | forced | 3 | MUL | Rector Cooling fans faulty contactor | 9.7333
2011-09-12 09:30 | 2011-09-26 16:14 | forced | 1 | Both | Cable Fault P1 (+ve) cable. | 342.7333
2011-09-24 08:33 | 2011-09-30 17:57 | forced | 2 | Both | Cable Fault P1 (+ve) cable. | 153.4
2011-09-26 07:07 | 2011-09-26 15:59 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 8.8667
2011-09-30 07:05 | 2011-09-30 17:10 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable fault | 10.0833
2011-09-30 07:12 | 2011-09-30 17:13 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable fault | 10.0167
2011-11-03 07:18 | 2011-11-03 13:22 | Scheduled | 2 | BLA | Outage to add SF6 Gas to bypass breaker | 6.0667
2011-11-08 07:43 | 2011-11-09 16:07 | Scheduled | 1 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 32.4
2011-11-08 08:03 | 2011-11-09 17:37 | Scheduled | 2 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 33.5667
2011-11-08 08:01 | 2011-11-09 16:11 | Scheduled | 3 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 32.1667
2011-11-30 07:24 | 2011-11-30 16:12 | Scheduled | 3 | Both | Outage to install sound prrofing on transformer | 8.8
2011-12-06 09:55 | 2011-12-06 10:37 | Scheduled | 2 | Both | Outage to add SF6 Gas to bypass breaker | 0.7
2011-12-09 18:43 | 2011-12-19 16:28 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 237.75
2011-12-19 07:02 | 2011-12-19 14:15 | Scheduled | 1 | Both | Outage to repair System 3 cable fault | 7.2167
2011-12-19 07:12 | 2011-12-19 15:52 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 8.6667
2011-12-19 16:31 | 2011-12-20 10:37 | forced | 3 | MUL | Reactor Cooling fans fault | 18.1
2012-01-04 18:41 | 2012-01-04 19:22 | forced | 1 | BLA | Reactor Cooling fans fault | 0.68333
2012-01-05 18:41 | 2012-01-10 11:42 | forced | 1 | BLA | Reactor Cooling fans fault | 113.0167
2012-01-06 06:06 | 2012-01-06 12:32 | Scheduled | 3 | MUL | Transformer Sound enclosure repairs | 6.4333
2012-01-06 12:32 | 2012-01-10 16:46 | forced | 3 | MUL | Control system fault. | 100.2333
2012-01-10 21:57 | 2012-01-16 16:48 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 138.85
2012-01-16 08:03 | 2012-01-16 14:37 | Scheduled | 1 | Both | Outage to repair System 2 cable fault | 6.5667
2012-01-16 08:03 | 2012-01-16 14:38 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 6.5833
2012-01-16 16:48 | 2012-01-23 12:04 | forced | 2 | MUL | Unable to return to service after cable fault. Too many faulty IGBTs | 163.2667
2012-01-25 05:57 | 2012-02-03 16:59 | forced | 2 | MUL | Valve cooling control system fault | 227.0333
2012-02-04 01:11 | 2012-02-13 16:32 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 231.35
2012-02-13 07:05 | 2012-02-13 16:30 | Scheduled | 2 | Both | Outage to repair System 1 cable fault | 9.4167
2012-02-13 07:08 | 2012-02-13 16:29 | Scheduled | 3 | Both | Outage to repair System 1 cable fault | 9.35
2012-02-16 11:01 | 2012-02-16 11:42 | forced | 2 | MUL | Trip cuased by control system maintenance | 0.68333
2012-02-16 11:48 | 2012-02-16 15:19 | forced | 2 | MUL | Trip cuased by control system maintenance | 3.5167
2012-02-20 07:44 | 2012-02-21 13:04 | Scheduled | 2 | Both | Outage for IGBT replacement at Bungalora and & Transformer measurement at Mullumbimby | 29.3333
2012-02-28 20:58 | 2012-03-09 11:43 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 230.75
2012-03-02 09:15 | 2012-03-02 09:44 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 0.48333
2012-03-03 07:11 | 2012-03-03 15:00 | Scheduled | 3 | Both | Outage to repair System 1 cable fault | 7.8167
2012-03-03 07:14 | 2012-03-03 15:00 | Scheduled | 2 | Both | Outage to repair System 1 cable fault | 7.7667
2012-03-29 11:14 | 2012-03-30 07:00 | forced | 3 | BLA | Trip caused by control system fault. | 19.7667
2012-03-30 07:00 | 2012-04-05 14:28 | Scheduled | 3 | MUL | Outage for Transformer sound enclosure. | 151.4667
2012-04-02 13:41 | 2012-04-17 17:08 | forced | 2 | Both | Cable fault P2 (-ve) cable. | 363.45
2012-04-17 17:08 | 2012-05-11 14:12 | forced | 2 | Both | Return to service after cable fault delayed due to faulty IGBTs | 573.0667
2012-04-17 07:10 | 2012-04-17 15:28 | Scheduled | 1 | Both | Outage to repair System 2 cable fault | 8.3
2012-04-17 07:18 | 2012-04-17 15:28 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 8.1667
2012-04-17 07:10 | 2012-04-20 13:51 | Scheduled | 1 | MUL | Outage for Transformer sound enclosure. | 78.6833
2012-05-22 10:34 | 2012-05-22 11:08 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 0.56667
2012-05-27 04:49 | 2012-06-07 14:31 | forced | 3 | MUL | Trip caused by reactor cooling fan motor fault | 273.7
2012-06-06 06:14 | 2012-06-06 18:36 | Scheduled | 1 | MUL | Outage for Country Energy protection installation | 12.3667
2012-06-06 06:16 | 2012-06-06 18:38 | Scheduled | 2 | MUL | Outage for Country Energy protection installation | 12.3667
2012-06-08 09:57 | 2012-06-08 14:13 | forced | 2 | MUL | Trip caused by control system maintenance | 4.2667
2012-06-19 10:04 | 2012-06-19 11:06 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 1.0333
2012-06-29 17:02 | 2012-07-11 18:33 | forced | 3 | Both | Cable fault P2 (-ve) cable. | 289.5167
2012-07-11 07:02 | 2012-07-11 15:33 | Scheduled | 1 | Both | Outage to repair System 3 cable fault | 8.5167
2012-07-11 07:03 | 2012-07-11 15:35 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 8.5333
2012-07-11 15:33 | 2012-08-14 08:33 | forced | 1 | BLA | Trip caused by flashover in phase reactor air ducting. | 809
2012-07-11 15:35 | 2012-07-14 15:25 | forced | 2 | MUL | Unable to return to service after cable fault repair due to control system fault. | 71.8333
2012-07-17 07:02 | 2012-07-18 19:50 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.8
2012-07-17 07:18 | 2012-07-18 19:53 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.5833
2012-07-23 06:59 | 2012-07-24 16:13 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.2333
2012-07-23 07:01 | 2012-07-24 16:25 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.4
2012-08-14 08:33 | 2013-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 3351.45
2012-08-14 08:57 | 2012-08-23 16:59 | forced | 2 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 224.0333
2012-08-14 08:58 | 2012-08-31 13:44 | forced | 3 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 412.7667
2012-08-31 13:44 | 2012-09-21 14:05 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 504.35
2012-09-13 08:35 | 2012-09-13 09:20 | forced | 2 | BLA | Trip cuased by valve control fault related to PCPB | 0.75
2012-09-20 07:29 | 2012-09-21 14:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault, return to service delayed by the need to inspect phase reactors for moisture. | 30.5167
2012-10-29 09:59 | 2012-10-30 12:19 | forced | 3 | BLA | Trip cuased by fault with LEM power supply. Inspectgion found not problems. | 26.3333
2012-11-12 05:23 | 2012-11-23 15:35 | forced | 2 | MUL | Cable fault P2 (-ve) cable. | 274.2
2012-11-18 17:50 | 2012-11-27 14:57 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 213.1167
2012-12-11 08:28 | 2012-12-11 12:12 | forced | 2 | MUL | Fire protection system tripped the converter station | 3.7333
2013-01-01 | 2014-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 8760
2013-01-03 05:57 | 2013-01-10 14:33 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 176.6
2013-01-09 07:50 | 2013-01-09 14:21 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 6.5167
2013-01-28 09:10 | 2013-01-31 16:45 | forced | 3 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 79.5833
2013-01-28 09:10 | 2013-02-01 15:59 | forced | 2 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 102.8167
2013-02-21 00:03 | 2013-02-21 02:44 | forced | 3 | MUL | Trip caused by control system fault. Auxiliary power disturbance caused both PCPs to fault. | 2.6833
2013-02-21 05:42 | 2013-03-12 13:06 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 463.4
2013-03-07 07:05 | 2013-03-07 13:57 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 6.8667
2013-03-07 13:57 | 2013-03-26 12:53 | forced | 2 | BLA | Return to service delayed by circuit breaker operating mechanism fault and IGBT failure | 454.9333
2013-03-26 15:37 | 2013-03-27 16:30 | forced | 2 | BLA | Trip caused by cooling water pump failure | 24.8833
2013-04-03 13:53 | 2013-04-03 14:58 | forced | 2 | BLA | Trip caused by cooling control system maintenance | 1.0833
2013-04-03 14:42 | 2013-04-03 14:56 | forced | 3 | BLA | Trip caused by cooling control system maintenance | 0.23333
2013-04-06 20:06 | 2013-04-23 12:47 | forced | 3 | Both | Cable fault P2 (-ve) cable | 400.6833
2013-04-22 06:59 | 2013-04-22 16:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 9.0167
2013-04-22 16:00 | 2013-04-23 14:03 | forced | 2 | Both | Return to service after cable repair outage delayed by valve control fault. | 22.05
2013-07-29 10:00 | 2013-07-29 13:38 | Scheduled | 2 | BLA | Outage to allow Essential Energy access at Terranora to position a crane. | 3.6333
2013-07-29 10:00 | 2013-07-29 15:05 | Scheduled | 3 | BLA | Outage to allow Essential Energy access at Terranora to position a crane. | 5.0833
2013-07-29 13:38 | 2013-08-06 18:00 | forced | 2 | BLA | Mullumbimby tripped because of too many faulty IGBTs. | 196.3667
2013-08-06 06:06 | 2013-08-06 18:00 | Scheduled | 3 | BLA | Outage to de-energise the overhead buss to allow replacement of CT in the transformers of system 1 and system 2. | 11.9
2013-08-06 18:00 | 2014-01-01 | forced | 3 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 3534
2013-08-06 18:00 | 2014-01-01 | forced | 2 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 3534
2014-01-01 | 2015-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 8760
2014-01-01 | 2014-01-21 17:07 | forced | 3 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 497.1167
2014-01-01 | 2014-02-11 12:10 | forced | 2 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 996.1667
2014-02-11 13:07 | 2014-02-14 13:37 | forced | 2 | BLA | Trip caused by filter capacitor unbalanced protection. Return to service delayed by too many faulty IGBTs. | 72.5
2014-02-14 14:34 | 2014-02-28 13:05 | forced | 2 | Both | Cable fault P2 (-ve) cable | 334.5167
2014-02-27 06:26 | 2014-02-27 18:28 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 12.0333
2014-03-01 08:28 | 2014-03-21 17:33 | forced | 2 | Both | Cable fault P1 (+ve) cable | 489.0833
2014-03-04 10:29 | 2014-03-04 12:26 | forced | 3 | BLA | LEM Power supply intermittent fault caused operation of the over current protection | 1.95
2014-03-12 06:05 | 2014-03-12 14:58 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 8.8833
2014-03-29 13:14 | 2014-04-17 13:56 | forced | 3 | Both | Cable fault P1 (+ve) cable | 456.7
2014-04-03 07:26 | 2014-04-03 08:22 | forced | 2 | MUL | Fire system maintenance contrctor caused trip while doing maintenance | 0.93333
2014-04-10 16:57 | 2014-04-10 18:13 | forced | 2 | MUL | Fire system trip. No evidence of fire found. Suspect faulty fire system interface card. | 1.2667
2014-04-11 08:06 | 2014-04-11 14:16 | Scheduled | 2 | Both | Outage to excavate System 2 cable fault | 6.1667
2014-04-16 07:28 | 2014-04-16 17:33 | Scheduled | 2 | Both | Outage to excavate System 2 cable fault | 10.0833

## Sheet3
Outage Start | Outage Finish |  | System | Converter | Description | Duration |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014
2007-01-01 | 2007-02-08 18:00 | forced | 1 | BLA | Transformer differential trip, suspected loose core lamination. This portion of the outage is in 2007 | 930 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-01-07 07:00 | 2007-01-07 12:20 | forced | 2 | MUL | Computer failure at Mullumbimby | 5.3333 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-03-17 08:59 | 2007-03-18 17:14 | forced | 2 | BLA | PCP mach2 computer failed during switching for planned repairs. | 32.25 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 1 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 2 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 3 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-09 13:29 | 2007-04-09 16:35 | forced | 1 | MUL | Loss of pole 1, caused by 11kV fault. | 3.1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-05-25 08:56 | 2007-07-25 10:41 | forced | 3 | both | Cooling water leak in valve hall, phase reactor failure. | 1465.75 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-05-25 10:51 | 2007-05-25 14:36 | forced | 2 | both | Pole 2 tripped, no fault found, returned to service. | 3.75 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-02 22:13 | 2007-06-07 16:11 | forced | 2 | both | More than 5 IGBTs failed in a stack. | 113.9667 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-07 01:58 | 2007-06-27 14:03 | forced | 1 | both | DC cable fault | 492.0833 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-16 12:14 | 2007-06-18 09:56 | forced | 2 | both | A Powerlink fault at Mudgeeraba caused the loss of 110kV supplies to Terranora. | 45.7 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-18 10:18 | 2007-06-18 10:29 | forced | 2 | BLA | Power supply problem in PCPB Mach 2 | 0.18333 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-29 05:55 | 2007-06-29 05:58 | forced | 1 | MUL | Spurious trip, unknown cause | 0.05 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-29 05:55 | 2007-06-29 05:58 | forced | 2 | MUL | Spurious trip, unknown cause | 0.05 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-07-09 16:21 | 2007-07-10 11:50 | forced | 2 | BLA | Cooling equipment fault at Bungalora pole 2 | 19.4833 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-07-19 08:32 | 2007-07-19 13:12 | forced | 2 | MUL | Spurious trip, unknown cause | 4.6667 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-08-01 15:30 | 2007-08-02 12:45 | forced | 3 | both | Pole 3 tripped, unknown cause. | 21.25 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-08-19 01:51 | 2007-08-19 14:43 | forced | 3 | both | Abnormal frequency trip | 12.8667 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-10-05 12:17 | 2007-11-15 14:30 | forced | 1 | BLA | Differential trip at Bungalora | 986.2167 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-10-26 22:30 | 2007-10-26 23:21 | forced | 2 | Both | Fault on 132kV system | 0.85 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-10-26 22:30 | 2007-10-26 23:21 | forced | 3 | Both | Fault on 132kV system | 0.85 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-27 17:00 | 2007-12-19 17:00 | forced | 1 | MUL | Computer failure on pole 1 at Mullumbimby. | 528 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-28 17:00 | 2007-12-20 18:05 | forced | 2 | both | Computer failure on pole 2 at Mullumbimby. | 529.0833 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-12-30 13:10 | 2008-01-01 | forced | 2 | BLA | Auxiliary Power Failure caused control system problems | 34.8333 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-12-30 13:10 | 2008-01-01 | forced | 3 | BLA | Auxiliary Power Failure caused control system problems | 34.8333 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-01-01 | 2008-01-02 20:09 | forced | 2 | BLA | Auxiliary Power Failure caused control system problems | 44.1497 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-01-01 | 2008-01-02 16:50 | forced | 3 | BLA | Auxiliary Power Failure caused control system problems | 40.8331 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-02 22:11 | 2008-02-03 10:48 | forced | 2 | MUL | Control System Faults | 12.6167 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-19 06:00 | 2008-02-21 00:27 | forced | 2 | both | Computer failure on pole 2 | 42.45 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-03-08 19:31 | 2008-03-28 13:00 | forced | 2 | both | Cable fault | 473.4833 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-03-13 16:07 | 2008-04-04 15:00 | forced | 1 | both | Cable fault | 526.8833 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-03-30 14:07 | 2008-03-30 18:00 | forced | 3 | both | Unknown fault caused converter to trip | 3.8833 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-14 15:09 | 2008-05-01 16:00 | forced | 2 | both | System 2 Cable fault | 408.85 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 20:12 | 2008-05-23 16:05 | forced | 3 | both | Reactor cooling fan fault. | 19.8833 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-09 03:21 | 2008-06-10 17:06 | forced | 3 | BLA | PCPA hard disk fault | 37.75 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 1 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 2 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 3 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 1 | both | Comms fault from Dandenong to DL | 1.75 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 2 | both | Comms fault from Dandenong to DL | 1.75 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 3 | both | Comms fault from Dandenong to DL | 1.75 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 20:40 | 2008-06-27 18:00 | forced | 1 | BLA | Faulty IGBTs | 45.3333 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-27 22:47 | 2008-07-09 15:43 | forced | 2 | both | Cable Fault | 280.9333 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 03:30 | 2008-06-29 08:00 | forced | 1 | MUL | TransGrid Tripping Scheme operation | 4.5 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 03:30 | 2008-06-29 08:00 | forced | 3 | MUL | TransGrid Tripping Scheme operation | 4.5 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 08:00 | 2008-06-29 10:27 | forced | 1 | MUL | Mach 2 faults after TransGrid Tripping Scheme operation | 2.4497 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 08:00 | 2008-06-29 10:27 | forced | 3 | MUL | Mach 2 faults after TransGrid Tripping Scheme operation | 2.4497 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-11 07:00 | 2008-07-11 18:43 | forced | 3 | BLA | Reactor Fan Trip | 11.7167 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-14 11:03 | 2008-08-04 14:54 | forced | 2 | both | Cable fault | 507.85 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-25 11:20 | 2008-08-01 16:15 | forced | 3 | 0 | After outage to excavate cables for repair to system 2 cable fault, L2 phase of system 3 circuit breaker would not close. | 172.9167 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 1 | both | Abnormal frequency trip | 5.8833 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 2 | both | Abnormal frequency trip | 5.8833 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 3 | both | Abnormal frequency trip | 5.8833 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-19 17:00 | 2008-09-21 07:00 | forced | 3 | both | Mullumbimby sytem 3 control system fault | 38 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 16:00 | 2008-09-25 15:55 | forced | 1 | both | Bungalora pre-insertion resistor overload trip - earths left on in the barn | 95.9167 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 16:00 | 2008-10-07 16:05 | forced | 3 | both | Mullumbimby sytem 3 control system fault | 384.0833 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-25 14:22 | 2008-09-25 20:17 | forced | 2 | both | Mullumbimby reactor cooling fan trip | 5.9167 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-10-01 18:17 | 2008-11-14 19:11 | forced | 2 | both | Cable Fault P1 cable. | 1056.9 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-07 13:59 | 2008-11-14 18:51 | forced | 1 | both | Cable Fault P1 cable. | 172.8667 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 1 | BLA | Auxiliary power failure | 1.5667 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 2 | BLA | Auxiliary power failure | 1.5667 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 3 | BLA | Auxiliary power failure | 1.5667 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-08 01:18 | 2008-12-16 13:12 | forced | 2 | both | Cable Fault P1 cable. | 203.9 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-19 23:06 | 2008-12-31 09:42 | forced | 2 | both | Cable Fault P1 cable. | 274.6 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-31 11:13 | 2009-01-01 | forced | 2 | both | Cable Fault P1 cable. | 12.7831 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2009-01-01 | 2009-01-20 09:22 | forced | 2 | both | Cable Fault P1 cable. | 465.3667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-01-11 13:00 | 2009-01-19 12:06 | forced | 1 | both | Cable Fault P1 cable. | 191.1 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-02-09 21:00 | 2009-02-18 10:53 | forced | 2 | both | Cable Fault P1 cable. | 205.8833 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-03-17 09:40 | 2009-03-30 13:51 | forced | 3 | both | Cable Fault P1 & P2 cable. | 316.1833 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.3 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.3 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.3 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-20 20:46 | 2009-05-20 23:31 | forced | 1 | BLA | Auxilary power outage caused a reactor cooling fan changeover. Dampers did not open in time causing a trip. | 2.75 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-21 05:10 | 2009-05-21 06:52 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Return delayed to investigate a CB Relay fault. | 1.7 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-21 05:10 | 2009-05-21 05:24 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.23333 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-21 05:10 | 2009-05-21 05:24 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.23333 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-22 04:32 | 2009-05-22 04:38 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.1 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-22 04:32 | 2009-05-22 04:39 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.11667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-22 04:32 | 2009-05-22 04:40 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.13333 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-22 07:59 | 2009-05-22 08:59 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 1 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-22 07:59 | 2009-05-22 09:03 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 1.0667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-22 07:59 | 2009-05-22 09:03 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 1.0667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-22 15:18 | 2009-05-22 16:34 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 1.2667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-22 15:18 | 2009-05-22 15:48 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.5 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-22 15:18 | 2009-05-22 15:48 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.5 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-23 17:22 | 2009-05-24 13:22 | forced | 3 | MUL | AC Filter capacitor protection trip. | 20 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:02 | 2009-05-23 19:15 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.21667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:02 | 2009-05-23 19:14 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.2 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:34 | 2009-05-23 19:40 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.1 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:34 | 2009-05-23 19:41 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.11667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-05-26 18:02 | 2009-06-06 13:08 | forced | 2 | Both | Cable fault P1 cable, Return to service delayed by too any Faulty IGBTs in B phase | 259.1 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-06-02 11:54 | 2009-06-02 12:10 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.26667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-06-02 11:54 | 2009-06-02 12:10 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.26667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-06-02 12:15 | 2009-06-02 14:28 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 2.2167 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-06-02 12:15 | 2009-06-02 14:28 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 2.2167 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-06-30 06:50 | 2009-07-18 10:29 | forced | 2 | Both | Cable fault P1 cable, Return to service delayed by too any Faulty IGBTs in B phase | 435.65 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-07-16 17:29 | 2009-07-21 17:38 | forced | 1 | Both | Unable to return to service. Too many faulty igbts. | 120.15 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-07-20 18:28 | 2009-07-21 09:54 | forced | 2 | Both | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 15.4333 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-07-20 18:28 | 2009-07-21 09:56 | forced | 3 | Both | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 15.4667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-08-14 10:52 | 2009-08-14 11:38 | forced | 1 | Both | Trip caused by flow protection. Standby pump did not start when pumps changed during while converter was running. | 0.76667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-08-25 13:27 | 2009-08-29 14:54 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 97.45 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-08-27 17:11 | 2009-08-27 21:20 | forced | 1 | MUL | Trip caused by Coutry Energy protection operation. Failed protection CT in Mullumbimby system 3 transformer | 4.15 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-08-27 17:11 | 2009-09-04 17:04 | forced | 3 | MUL | Trip caused by Coutry Energy protection operation. Failed protection CT in Mullumbimby system 3 transformer | 191.8833 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-11-03 13:23 | 2009-11-03 14:01 | forced | 3 | BLA | Trip by Flow Protection - Active CCP accidentally reset during maintenance | 0.63333 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-11-04 02:42 | 2009-11-13 10:18 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 223.6 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-11-10 17:50 | 2009-11-10 18:44 | forced | 3 | Bla | Fault with 24V DC power supply | 0.9 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-11-19 01:51 | 2009-11-28 09:57 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 224.1 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-11-20 02:17 | 2009-11-20 02:55 | forced | 2 | MUL | Abnormal Frequency Trip. Country Energy System Problems. | 0.63333 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-11-20 02:17 | 2009-11-20 02:56 | forced | 3 | MUL | Abnormal Frequency Trip. Country Energy System Problems. | 0.65 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-11-27 10:28 | 2009-11-27 11:03 | forced | 3 | MUL | Damper Resistor overload trip event on one PCP. Converter tripped while trying to clear the event. | 0.58333 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-11-28 10:30 | 2009-12-17 14:49 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 460.3167 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-12-11 00:52 | 2009-12-11 02:16 | forced | 1 | BLA | Operation of Powerlink intertrip scheme. | 1.4 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-12-11 00:52 | 2009-12-11 02:17 | forced | 3 | BLA | Operation of Powerlink intertrip scheme. | 1.4167 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-12-12 08:13 | 2009-12-12 08:58 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.75 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-12-12 08:13 | 2009-12-12 08:59 | forced | 3 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.76667 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-12-17 22:14 | 2010-01-01 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 337.7664 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2010-01-01 | 2010-01-14 09:14 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 321.2333 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-01-08 18:49 | 2010-01-08 19:11 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.36667 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-01-08 18:49 | 2010-01-08 19:13 | forced | 3 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.4 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-01-09 13:04 | 2010-03-31 14:01 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 1944.95 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-01-13 13:37 | 2010-01-21 09:56 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 188.3167 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-01-15 07:23 | 2010-01-15 08:05 | forced | 2 | 0 | Trip during control system maintenance | 0.7 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-01-20 21:01 | 2010-01-20 21:34 | forced | 2 | 0 | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.55 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-01-27 05:30 | 2010-03-31 13:54 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 1520.4 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-03-31 23:18 | 2010-04-17 09:26 | forced | 1 | Both | Cable fault P1 (+ve) cable. After cable repair, fault with DC voltage measuring delayed return to service. | 394.1333 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-04-09 17:48 | 2010-04-20 13:44 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 259.9333 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-04-17 09:26 | 2010-04-28 13:37 | forced | 1 | Both | Fault with DC voltage measuring delayed return to service after repair P1 (+ve) cable, | 268.1833 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-04-30 19:18 | 2010-06-13 10:34 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 1047.2667 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-05-05 11:00 | 2010-05-05 13:14 | forced | 1 | BLA | Trip during fault finding of PCPB DC voltage measuring | 2.2333 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-05-31 17:26 | 2010-06-08 13:18 | forced | 3 | Both | Outage to excavate the system 2 cable fault. Return to service delayed due to VCU Faults. | 187.8667 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-06-10 02:02 | 2010-06-10 16:02 | forced | 3 | BLA | Trip due to low water level. Pump leaking. | 14 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-07-06 01:03 | 2010-07-06 16:18 | forced | 2 | MUL | UPS failure caused trip of converter | 15.25 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-07-15 22:07 | 2010-07-26 08:19 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 250.2 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-07-22 17:22 | 2010-07-26 07:00 | forced | 1 | MUL | Return to serivce delayed - Too many faulty IGBTs | 85.6333 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-07-22 17:23 | 2010-07-26 07:00 | forced | 3 | BLA | Return to serivce delayed - Too many faulty IGBTs | 85.6167 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-07-28 15:02 | 2010-07-29 14:44 | forced | 3 | BLA | Phase reactor partial discharge repair | 23.7 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-07-31 16:49 | 2010-08-06 13:25 | forced | 2 | MUL | Return to serivce delayed - faulty control system components | 140.6 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 1 | BLA | Auxiliary power failure | 0.88333 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 2 | BLA | Auxiliary power failure | 0.88333 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 3 | BLA | Auxiliary power failure | 0.88333 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-09 08:37 | 2010-08-11 13:40 | forced | 1 | BLA | Restoration after auxiliary power failure | 53.05 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-09 08:37 | 2010-08-09 15:58 | forced | 2 | BLA | Restoration after auxiliary power failure | 7.35 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-09 08:37 | 2010-08-09 09:43 | forced | 3 | BLA | Restoration after auxiliary power failure | 1.1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-22 04:00 | 2010-08-22 15:04 | forced | 2 | BLA | Reactor cooling fans tripped converter | 11.0667 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-25 09:46 | 2010-08-25 11:27 | forced | 2 | BLA | Trip caused by control system maintenance | 1.6833 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-09-18 02:43 | 2010-10-01 12:08 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 321.4167 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-09-19 02:02 | 2010-10-01 12:42 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 298.6667 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-10-06 16:23 | 2010-10-22 12:28 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 380.0833 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-10-17 10:06 | 2010-10-17 14:02 | forced | 2 | MUL | Trip caused by fire protection system fault. | 3.9333 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-11-14 01:21 | 2010-11-20 08:14 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 150.8786 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-11-24 15:30 | 2010-11-26 13:45 | forced | 1 | Both | IGBT Faults | 46.25 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-11-25 21:15 | 2010-12-03 13:45 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 184.5 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-12-12 14:39 | 2010-12-22 16:07 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 241.4667 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-12-15 19:06 | 2010-12-23 10:29 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 183.3833 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-12-25 01:01 | 2010-12-25 01:41 | forced | 1 | BLA | Auxiliary power failure - Rector cooling fans trip. | 0.66667 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-12-27 13:03 | 2011-01-01 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 106.95 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2011-01-01 | 2011-01-07 09:07 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 153.1167 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-01-07 06:36 | 2011-01-17 09:35 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 242.9833 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-01-10 15:21 | 2011-01-18 11:39 | forced | 2 | Both | Cable fault P2 (-ve) cable. | 188.3 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-01-28 11:51 | 2011-02-10 13:59 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 314.1333 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-02-09 17:43 | 2011-02-14 17:24 | forced | 3 | Both | Outage due to BLA System 3, B Phase CB Pole leaking insulating gas. | 119.6833 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-02-14 17:41 | 2011-02-18 11:31 | forced | 2 | MUL | Unable to return to service after planned outage. Too many faulty IGBTs | 89.8333 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-02-15 07:13 | 2011-02-15 07:42 | forced | 1 | MUL | Outage due to control system fault. | 0.48333 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-02-21 17:15 | 2011-02-21 18:31 | forced | 1 | BLA | Phase Reactor Cooling Fan L3 Trip | 1.2667 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-03-13 12:24 | 2011-03-28 13:23 | forced | 1 | MUL | Trip due to flash over in PLC filter yard. Return to service delayed due to to many faulty IGBTs | 360.9833 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-03-13 12:24 | 2011-03-13 19:31 | forced | 2 | MUL | Trip due to flash over in PLC filter yard. | 7.1167 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-03-13 12:24 | 2011-03-13 19:34 | forced | 3 | MUL | Trip due to flash over in PLC filter yard. | 7.1667 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-04-01 13:49 | 2011-04-08 12:55 | forced | 2 | Both | Faulty IGBTs prevented return to service after CE outage. | 167.1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-04-18 16:05 | 2011-04-23 13:09 | forced | 1 | Both | Cable Fault P1 (+ve) cable. | 117.0667 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-05-08 16:23 | 2011-06-11 16:25 | forced | 1 | Both | Outage caused by DC voltage imbalance. Return to service delayed by too many faulty IGBT optic fibres. | 816.0333 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-05-14 11:26 | 2011-05-30 11:26 | forced | 3 | Both | Cable Fault P1 (+ve) cable. Return to service after cable fault repair delayed by too many faulty IGBTs | 384 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-05-25 18:32 | 2011-07-22 10:15 | forced | 2 | Both | Unable to return to service after planned outage. Too many faulty IGBTs | 1383.7167 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-06-10 02:56 | 2011-07-15 10:18 | forced | 3 | Both | Cable Fault P1 (+ve) cable. | 847.3667 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-07-15 10:30 | 2011-07-15 11:09 | forced | 3 | BLA | Cooling system trip - high water temperature - proportional valve failed to operate. | 0.65 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-07-18 23:25 | 2011-07-30 09:38 | forced | 1 | Both | Cable Fault P2 (-ve) cable. | 274.2167 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-07-22 10:50 | 2011-08-05 15:12 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 340.3667 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-07-30 09:38 | 2011-08-05 15:11 | forced | 1 | BLA | Unable to return to service after cable fault. Too many faulty IGBTs | 149.55 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-08-22 16:08 | 2011-08-23 09:50 | forced | 1 | BLA | Rector Cooling fans faulty contactor | 17.7 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-08-22 16:08 | 2011-08-23 00:06 | forced | 3 | BLA | Rector Cooling fans faulty contactor | 7.9667 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-08-23 11:48 | 2011-08-23 12:14 | forced | 2 | MUL | Trip cause during replacement of UPS fault indicating relay | 0.43333 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-08-25 07:07 | 2011-09-03 13:05 | forced | 3 | Both | Cable Fault P2 (-ve) cable. | 221.9667 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-08-30 09:39 | 2011-08-30 10:17 | forced | 2 | BLA | Valve control fault during maintenance work | 0.63333 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-09-05 09:08 | 2011-09-05 18:52 | forced | 3 | MUL | Rector Cooling fans faulty contactor | 9.7333 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-09-12 09:30 | 2011-09-26 16:14 | forced | 1 | Both | Cable Fault P1 (+ve) cable. | 342.7333 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-09-24 08:33 | 2011-09-30 17:57 | forced | 2 | Both | Cable Fault P1 (+ve) cable. | 153.4 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-12-09 18:43 | 2011-12-19 16:28 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 237.75 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-12-19 16:31 | 2011-12-20 10:37 | forced | 3 | MUL | Reactor Cooling fans fault | 18.1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2012-01-04 18:41 | 2012-01-04 19:22 | forced | 1 | BLA | Reactor Cooling fans fault | 0.68333 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-01-05 18:41 | 2012-01-10 11:42 | forced | 1 | BLA | Reactor Cooling fans fault | 113.0167 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-01-06 12:32 | 2012-01-10 16:46 | forced | 3 | MUL | Control system fault. | 100.2333 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-01-10 21:57 | 2012-01-16 16:48 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 138.85 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-01-16 16:48 | 2012-01-23 12:04 | forced | 2 | MUL | Unable to return to service after cable fault. Too many faulty IGBTs | 163.2667 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-01-25 05:57 | 2012-02-03 16:59 | forced | 2 | MUL | Valve cooling control system fault | 227.0333 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-02-04 01:11 | 2012-02-13 16:32 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 231.35 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-02-16 11:01 | 2012-02-16 11:42 | forced | 2 | MUL | Trip cuased by control system maintenance | 0.68333 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-02-16 11:48 | 2012-02-16 15:19 | forced | 2 | MUL | Trip cuased by control system maintenance | 3.5167 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-02-28 20:58 | 2012-03-09 11:43 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 230.75 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-03-29 11:14 | 2012-03-30 07:00 | forced | 3 | BLA | Trip caused by control system fault. | 19.7667 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-04-02 13:41 | 2012-04-17 17:08 | forced | 2 | Both | Cable fault P2 (-ve) cable. | 363.45 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-04-17 17:08 | 2012-05-11 14:12 | forced | 2 | Both | Return to service after cable fault delayed due to faulty IGBTs | 573.0667 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-05-27 04:49 | 2012-06-07 14:31 | forced | 3 | MUL | Trip caused by reactor cooling fan motor fault | 273.7 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-06-08 09:57 | 2012-06-08 14:13 | forced | 2 | MUL | Trip caused by control system maintenance | 4.2667 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-06-29 17:02 | 2012-07-11 18:33 | forced | 3 | Both | Cable fault P2 (-ve) cable. | 289.5167 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-07-11 15:33 | 2012-08-14 08:33 | forced | 1 | BLA | Trip caused by flashover in phase reactor air ducting. | 809 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-07-11 15:35 | 2012-07-14 15:25 | forced | 2 | MUL | Unable to return to service after cable fault repair due to control system fault. | 71.8333 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-08-14 08:33 | 2013-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 3351.45 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-08-14 08:57 | 2012-08-23 16:59 | forced | 2 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 224.0333 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-08-14 08:58 | 2012-08-31 13:44 | forced | 3 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 412.7667 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-08-31 13:44 | 2012-09-21 14:05 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 504.35 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-09-13 08:35 | 2012-09-13 09:20 | forced | 2 | BLA | Trip cuased by valve control fault related to PCPB | 0.75 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-10-29 09:59 | 2012-10-30 12:19 | forced | 3 | BLA | Trip cuased by fault with LEM power supply. Inspectgion found not problems. | 26.3333 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-11-12 05:23 | 2012-11-23 15:35 | forced | 2 | MUL | Cable fault P2 (-ve) cable. | 274.2 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-11-18 17:50 | 2012-11-27 14:57 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 213.1167 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-12-11 08:28 | 2012-12-11 12:12 | forced | 2 | MUL | Fire protection system tripped the converter station | 3.7333 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2013-01-01 | 2014-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 8760 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-01-03 05:57 | 2013-01-10 14:33 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 176.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-01-28 09:10 | 2013-02-01 15:59 | forced | 2 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 102.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-01-28 09:10 | 2013-01-31 16:45 | forced | 3 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 79.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-02-21 00:03 | 2013-02-21 02:44 | forced | 3 | MUL | Trip caused by control system fault. Auxiliary power disturbance caused both PCPs to fault. | 2.6833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-02-21 05:42 | 2013-03-12 13:06 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 463.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-03-07 13:57 | 2013-03-26 12:53 | forced | 2 | BLA | Return to service delayed by circuit breaker operating mechanism fault and IGBT failure | 454.9333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-03-26 15:37 | 2013-03-27 16:30 | forced | 2 | BLA | Trip caused by cooling water pump failure | 24.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-04-03 13:53 | 2013-04-03 14:58 | forced | 2 | BLA | Trip caused by cooling control system maintenance | 1.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-04-03 14:42 | 2013-04-03 14:56 | forced | 3 | BLA | Trip caused by cooling control system maintenance | 0.23333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-04-06 20:06 | 2013-04-23 12:47 | forced | 3 | Both | Cable fault P2 (-ve) cable | 400.6833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-04-22 16:00 | 2013-04-23 14:03 | forced | 2 | Both | Return to service after cable repair outage delayed by valve control fault. | 22.05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-07-29 13:38 | 2013-08-06 18:00 | forced | 2 | BLA | Mullumbimby tripped because of too many faulty IGBTs. | 196.3667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-08-06 18:00 | 2014-01-01 | forced | 2 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 3534 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-08-06 18:00 | 2014-01-01 | forced | 3 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 3534 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2014-01-01 | 2015-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 8760 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-01-01 | 2014-02-11 12:10 | forced | 2 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 996.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-01-01 | 2014-01-21 17:07 | forced | 3 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 497.1167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-02-11 13:07 | 2014-02-14 13:37 | forced | 2 | BLA | Trip caused by filter capacitor unbalanced protection. Return to service delayed by too many faulty IGBTs. | 72.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-02-14 14:34 | 2014-02-28 13:05 | forced | 2 | Both | Cable fault P2 (-ve) cable | 334.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-03-01 08:28 | 2014-03-21 17:33 | forced | 2 | Both | Cable fault P1 (+ve) cable | 489.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-03-04 10:29 | 2014-03-04 12:26 | forced | 3 | BLA | LEM Power supply intermittent fault caused operation of the over current protection | 1.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-03-29 13:14 | 2014-04-17 13:56 | forced | 3 | Both | Cable fault P1 (+ve) cable | 456.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-04-03 07:26 | 2014-04-03 08:22 | forced | 2 | MUL | Fire system maintenance contrctor caused trip while doing maintenance | 0.93333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-04-10 16:57 | 2014-04-10 18:13 | forced | 2 | MUL | Fire system trip. No evidence of fire found. Suspect faulty fire system interface card. | 1.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
[16 empty] | Average | SD | CAP | COLLAR
[7 empty] | Year Totals | 26 | 40 | 51 | 40 | 31 | 27 | 15 | 10 | 37.8 | 8.3283 | 29.4717 | 46.1283
[8 empty] | 866.7% | 1333% | 1700% | 1333% | 1033% | 900% | 500% | 333.3% | 1260% |  | 982.4% | 1538%
2009-03-26 07:04 | 2009-03-26 15:51 | scheculed | 1 | both | Outage to repair Pole 3 cable fault | 8.7833
2009-03-26 07:37 | 2009-03-26 15:53 | scheculed | 2 | both | Outage to repair Pole 3 cable fault | 8.2667
2009-03-27 07:03 | 2009-03-27 13:24 | scheculed | 1 | both | Outage to repair Pole 3 cable fault | 6.35
2009-03-27 07:08 | 2009-03-27 13:26 | scheculed | 2 | both | Outage to repair Pole 3 cable fault | 6.3
2009-04-15 10:01 | 2009-04-15 11:28 | scheculed | 1 | both | Outage for access valve enclosure lock change | 1.45
2009-04-15 11:48 | 2009-04-15 13:57 | scheculed | 2 | both | Outage for access valve enclosure lock change | 2.15
2009-04-15 14:08 | 2009-04-15 15:23 | scheculed | 3 | both | Outage for access valve enclosure lock change | 1.25
2007-03-17 08:28 | 2007-03-17 16:31 | scheduled | 1 | MUL | Repairs to galvanised steel troughing | 8.05
2007-03-17 08:59 | 2007-03-17 16:32 | scheduled | 3 | MUL | Repairs to galvanised steel troughing | 7.55
2007-03-18 08:25 | 2007-03-18 17:14 | scheduled | 1 | BLA | Repairs to galvanised steel troughing | 8.8167
2007-03-18 08:25 | 2007-03-18 17:14 | scheduled | 3 | BLA | Repairs to galvanised steel troughing | 8.8167
2007-04-16 09:30 | 2007-04-16 11:00 | scheduled | 1 | Both | Single system outage for site visits | 1.5
2007-05-04 08:30 | 2007-05-04 11:30 | scheduled | 1 | both | Single system outage for site visits | 3
2007-07-18 08:32 | 2007-07-18 13:05 | scheduled | 1 | BLA | Inspection of phase reactors at Bungalora | 4.55
2007-09-04 07:01 | 2007-09-04 20:02 | scheduled | 1 | both | Annual maintenance | 13.0167
2007-09-05 14:22 | 2007-09-06 00:19 | scheduled | 2 | both | Annual maintenance | 9.95
2007-09-06 07:00 | 2007-09-06 18:45 | scheduled | 3 | both | Annual maintenance | 11.75
2007-11-05 11:00 | 2007-11-05 13:10 | scheduled | 2 | Both | Systems 2 & 3 down for excavation on system 1 | 2.1667
2007-11-05 11:00 | 2007-11-05 13:10 | scheduled | 3 | Both | Systems 2 & 3 down for excavation on system 1 | 2.1667
2007-11-27 07:15 | 2007-11-27 17:00 | scheduled | 1 | both | Maintenance - Phase Reactors and IGBTs. Control system faults prevent return to service. | 9.75
2007-11-28 07:15 | 2007-11-28 17:00 | scheduled | 2 | both | Maintenance - Phase Reactors and IGBTs. Control system faults prevent return to service. | 9.75
2007-11-29 08:08 | 2007-11-29 15:14 | scheduled | 3 | both | Maintenance - Phase Reactors and IGBTs. | 7.1
2008-02-13 08:30 | 2008-02-13 17:00 | scheduled | 1 | both | Shutdown to investigate various faults | 8.5 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-20 07:00 | 2008-02-20 11:00 | scheduled | 1 | both | Fire System Maintenance | 4
2008-02-20 11:05 | 2008-02-20 13:50 | scheduled | 3 | both | Fire System Maintenance | 2.75
2008-02-27 08:00 | 2008-02-27 10:35 | scheduled | 1 | BLA | Installation of power flow monitoring gear | 2.5833
2008-02-27 10:12 | 2008-02-27 13:46 | scheduled | 2 | BLA | Installation of power flow monitoring gear | 3.5667
2008-02-27 11:00 | 2008-02-27 15:34 | scheduled | 3 | BLA | Installation of power flow monitoring gear | 4.5667
2008-03-18 09:35 | 2008-03-18 12:20 | scheduled | 3 | both | Outage to safely excavate sys1 cables for repair | 2.75 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-09 07:25 | 2008-04-09 15:35 | scheduled | 3 | both | Phase reactor inspections | 8.1667
2008-04-10 07:25 | 2008-04-10 14:56 | scheduled | 2 | both | Phase reactor inspections | 7.5167
2008-04-11 07:08 | 2008-04-24 17:32 | scheduled | 1 | both | Phase reactor inspections and Transformer swap out | 322.4
2008-04-13 07:00 | 2008-04-13 17:00 | scheduled | 2 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10
2008-04-13 07:00 | 2008-04-13 17:00 | scheduled | 3 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10
2008-04-16 07:00 | 2008-04-16 17:00 | scheduled | 2 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10
2008-04-16 07:00 | 2008-04-16 17:00 | scheduled | 3 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10
2008-05-12 08:00 | 2008-05-15 18:45 | scheduled | 1 | both | Phase reactor repairs | 82.75 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-15 17:00 | 2008-05-15 18:45 | scheduled | 2 | both | Communications Test | 1.75
2008-05-15 17:00 | 2008-05-15 18:45 | scheduled | 3 | both | Communications Test | 1.75
2008-05-16 08:00 | 2008-05-17 13:40 | scheduled | 3 | both | Phase reactor repairs | 29.6667
2008-05-18 08:00 | 2008-05-19 14:11 | scheduled | 2 | both | Phase reactor repairs | 30.1833
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 1 | both | Comms cut over for trial operation | 2
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 2 | both | Comms cut over for trial operation | 2
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 3 | both | Comms cut over for trial operation | 2
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 1 | both | Comms cut over after trial operation | 0.5
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 2 | both | Comms cut over after trial operation | 0.5
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 3 | both | Comms cut over after trial operation | 0.5
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 1 | both | Comms cut over for trial operation | 0.58333
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 2 | both | Comms cut over for trial operation | 0.58333
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 3 | both | Comms cut over for trial operation | 0.58333
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 1 | both | Comms cut over after trial operation | 0.33333
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 2 | both | Comms cut over after trial operation | 0.33333
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 3 | both | Comms cut over after trial operation | 0.33333
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 1 | both | Final comms cut over. | 0.41667
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 2 | both | Final comms cut over. | 0.41667
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 3 | both | Final comms cut over. | 0.41667
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 1 | MUL | Country Energy outage to connect CB 7H3 | 13.4167
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 2 | MUL | Country Energy outage to connect CB 7H3 | 13.4167
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 3 | MUL | Country Energy outage to connect CB 7H3 | 13.4167
2008-07-12 08:25 | 2008-07-12 16:15 | scheduled | 1 | BLA | Valve Cooling Water Leak Inspection | 7.8333
2008-07-20 01:02 | 2008-07-20 05:29 | scheduled | 1 | both | Country Energy outage | 4.45
2008-07-20 01:02 | 2008-07-20 05:29 | scheduled | 3 | both | Country Energy outage | 4.45
2008-07-25 09:03 | 2008-07-25 11:20 | scheduled | 1 | both | Outage to excavate Cables for repair to system 2 cable fault | 2.2833
2008-07-25 09:03 | 2008-07-25 11:20 | scheduled | 3 | both | Outage to excavate Cables for repair to system 2 cable fault | 2.2833
2008-07-31 09:46 | 2008-07-31 14:35 | scheduled | 1 | both | Outage to excavate Cables for repair to system 2 cable fault | 4.8167
2008-09-16 07:00 | 2008-09-18 17:26 | scheduled | 2 | both | Annual Maintenance | 58.4333
2008-09-18 07:30 | 2008-09-19 17:00 | scheduled | 3 | both | Annual Maintenance | 33.5
2008-09-20 07:00 | 2008-09-21 07:00 | scheduled | 1 | both | Annual Maintenance | 24
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 1 | both | Country energy requested outage for maintenance at Terranora | 9
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 2 | both | Country energy requested outage for maintenance at Terranora | 9
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 3 | both | Country energy requested outage for maintenance at Terranora | 9
2008-11-24 07:02 | 2008-11-24 15:02 | scheduled | 1 | both | Phase Reactor Inspections and cable clamp modifications | 8
2008-11-25 06:54 | 2008-11-25 15:36 | scheduled | 2 | both | Phase Reactor Inspections and cable clamp modifications | 8.7
2008-11-26 07:05 | 2008-11-26 14:45 | scheduled | 3 | both | Phase Reactor Inspections and cable clamp modifications | 7.6667
2008-11-27 07:10 | 2008-11-27 13:14 | scheduled | 1 | both | Phase Reactor Inspections and cable clamp modifications | 6.0667
2008-12-15 08:10 | 2008-12-15 10:25 | scheduled | 1 | both | Outage to locate Pole 1 cable fault | 2.25
2008-12-15 08:17 | 2008-12-15 10:28 | scheduled | 3 | both | Outage to locate Pole 1 cable fault | 2.1833
2008-12-30 07:41 | 2008-12-30 09:24 | scheduled | 3 | both | Outage to locate Pole 1 cable fault | 1.7167
2008-12-30 07:47 | 2008-12-30 09:22 | scheduled | 1 | both | Outage to locate Pole 1 cable fault | 1.5833
2009-01-16 07:00 | 2009-01-16 14:01 | scheduled | 3 | both | Outage to repair Pole 1 and Pole 2 cable faults | 7.0167
2009-02-10 07:26 | 2009-02-10 12:01 | scheduled | 1 | both | Outage for Country Energy maintenance - 110kV bus at Terranora substation | 4.5833
2009-02-10 07:36 | 2009-02-10 12:06 | scheduled | 3 | both | Outage for Country Energy maintenance - 110kV bus at Terranora substation | 4.5
2009-02-16 09:05 | 2009-02-16 13:05 | scheduled | 1 | both | Outage to repair Pole 2 cable fault | 4
2009-02-16 09:07 | 2009-02-16 13:06 | scheduled | 3 | both | Outage to repair Pole 2 cable fault | 3.9833
2009-02-16 13:16 | 2009-02-16 15:00 | scheduled | 3 | both | Outage to repair Pole 2 cable fault | 1.7333
2009-02-16 13:17 | 2009-02-16 14:59 | scheduled | 1 | both | Outage to repair Pole 2 cable fault | 1.7
2009-03-10 07:31 | 2009-03-10 15:23 | scheduled | 3 | both | Outage for six month maintenance | 7.8667
2009-03-11 07:31 | 2009-03-11 13:54 | scheduled | 2 | both | Outage for six month maintenance | 6.3833
2009-03-12 07:03 | 2009-03-13 08:02 | scheduled | 1 | both | Outage for six month maintenance | 24.9833
2009-06-03 09:16 | 2009-06-03 14:49 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 5.55
2009-06-03 09:16 | 2009-06-03 14:51 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.5833
2009-07-14 09:04 | 2009-07-14 14:19 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 5.25
2009-07-14 09:13 | 2009-07-14 14:21 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 5.1333
2009-07-15 08:36 | 2009-07-15 10:24 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 1.8
2009-07-15 08:38 | 2009-07-15 10:21 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 1.7167
2009-07-16 09:02 | 2009-07-16 17:29 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 8.45
2009-07-16 09:12 | 2009-07-16 17:32 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 8.3333
2009-07-27 06:36 | 2009-07-28 17:04 | Scheduled | 1 | Both | Shutdown for annual maintenance | 34.4667
2009-07-29 06:49 | 2009-07-30 17:26 | Scheduled | 2 | Both | Shutdown for annual maintenance | 34.6167
2009-07-31 06:32 | 2009-08-01 13:02 | Scheduled | 3 | Both | Shutdown for annual maintenance | 30.5
2009-08-27 08:07 | 2009-08-27 16:49 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 8.7
2009-08-27 08:14 | 2009-08-27 16:47 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 8.55
2009-09-04 07:22 | 2009-09-04 16:49 | Scheduled | 1 | MUL | Outage for HV access to repair failed protection CT in Mullumbimby system 3 transformer | 9.45
2009-09-04 07:23 | 2009-09-04 16:50 | Scheduled | 2 | MUL | Outage for HV access to repair failed protection CT in Mullumbimby system 3 transformer | 9.45
2009-09-29 07:04 | 2009-09-29 17:14 | Scheduled | 1 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.1667
2009-09-29 07:07 | 2009-09-29 17:39 | Scheduled | 2 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.5333
2009-09-29 07:09 | 2009-09-29 17:18 | Scheduled | 3 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.15
2009-11-11 10:11 | 2009-11-11 16:08 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.95
2009-11-11 10:16 | 2009-11-11 16:06 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 5.8333
2009-11-26 09:06 | 2009-11-26 14:59 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.8833
2009-11-26 09:15 | 2009-11-26 14:57 | Scheduled | 2 | Both | Outage to enable access to repair the system 2 cable. | 5.7
2009-12-15 07:02 | 2009-12-15 17:07 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 10.0833
2009-12-15 07:20 | 2009-12-15 17:04 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 9.7333
2010-01-12 07:16 | 2010-01-12 16:16 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 9
2010-01-19 07:03 | 2010-01-19 14:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 7.15
2010-03-27 06:04 | 2010-03-27 17:35 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. | 11.5167
2010-03-28 06:04 | 2010-03-28 15:41 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 9.6167
2010-04-14 07:04 | 2010-04-15 15:51 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. Too many faulty igbts when energised from Mullumbimby. Igbts repaired the next day during system 2 cable fault repair. | 32.7833 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-05-24 07:14 | 2010-05-28 14:24 | Scheduled | 3 | Both | Outage to replace transformer CTs | 103.1667
2010-05-25 07:03 | 2010-05-25 19:33 | Scheduled | 1 | Both | Outage to allow overhead crane access for replacing system 3 transformer CTs | 12.5
2010-05-31 10:05 | 2010-05-31 17:23 | Scheduled | 1 | Both | Outage to excavate the system 2 cable fault. | 7.3
2010-05-31 10:10 | 2010-05-31 17:26 | Scheduled | 3 | Both | Outage to excavate the system 2 cable fault under the river. | 7.2667
2010-06-01 13:43 | 2010-06-01 14:33 | Scheduled | 1 | Both | Outage to cut system 2 cable during repair of fault under the river. | 0.83333
2010-06-03 06:55 | 2010-06-03 17:48 | Scheduled | 1 | Both | Outage to joint system 2 cable during repair of fault under the river. | 10.8833
2010-06-04 07:00 | 2010-06-04 16:15 | Scheduled | 1 | Both | Outage to joint system 2 cable during repair of fault under the river. | 9.25
2010-07-22 06:03 | 2010-07-22 17:22 | Scheduled | 1 | BLA | CE Requested Outage - Terranora Bus zone breakers | 11.3167
2010-07-22 06:06 | 2010-07-22 17:23 | Scheduled | 3 | BLA | CE Requested Outage - Terranora Bus zone breakers | 11.2833
2010-07-26 07:00 | 2010-07-28 14:39 | Scheduled | 3 | Both | Annual Maintenance | 55.65
2010-07-26 07:00 | 2010-07-29 15:18 | Scheduled | 1 | Both | Annual Maintenance | 80.3
2010-07-30 08:41 | 2010-07-31 16:49 | Scheduled | 2 | Both | Annual Maintenance | 32.1333
2010-07-31 08:38 | 2010-07-31 10:00 | Scheduled | 1 | MUL | CE Requested Outage - Lismore Tripping Scheme Work | 1.3667
2010-07-31 08:46 | 2010-07-31 10:01 | Scheduled | 3 | MUL | CE Requested Outage - Lismore Tripping Scheme Work | 1.25
2010-08-10 12:04 | 2010-08-10 18:39 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 6.5833
2010-08-10 12:06 | 2010-08-10 18:35 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 6.4833
2010-08-11 06:04 | 2010-08-11 13:42 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 7.6333
2010-08-11 06:05 | 2010-08-11 13:41 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 7.6
2010-08-14 06:08 | 2010-08-14 12:44 | Scheduled | 1 | BLA | County Energy Requested outage for work at Terranora | 6.6
2010-08-14 06:10 | 2010-08-14 12:45 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 6.5833
2010-08-14 06:11 | 2010-08-14 12:46 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 6.5833
2010-08-15 06:03 | 2010-08-15 11:50 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 5.7833
2010-08-15 06:05 | 2010-08-15 11:48 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 5.7167
2010-08-15 06:06 | 2010-08-15 11:46 | Scheduled | 1 | BLA | County Energy Requested outage for work at Terranora | 5.6667
2010-09-02 12:50 | 2010-09-02 13:28 | Scheduled | 3 | BLA | Outage requested by Country Energy for protection testing | 0.63333
2010-09-02 12:51 | 2010-09-02 13:28 | Scheduled | 2 | BLA | Outage requested by Country Energy for protection testing | 0.61667
2010-09-02 12:51 | 2010-09-02 13:27 | Scheduled | 1 | BLA | Outage requested by Country Energy for protection testing | 0.6
2010-09-27 08:01 | 2010-09-27 14:16 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 6.25
2010-09-27 08:02 | 2010-09-27 16:02 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. | 8
2010-10-14 08:11 | 2010-10-14 15:01 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable. | 6.8333
2010-10-14 08:11 | 2010-10-14 15:03 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 6.8667
2010-10-29 09:38 | 2010-10-29 11:08 | Scheduled | 1 | Both | Outage to repair GST damage. | 1.5
2010-11-08 06:06 | 2010-11-08 13:07 | Scheduled | 1 | MUL | Outage for CE Comms tower installation | 7.0167
2010-11-08 06:11 | 2010-11-08 13:08 | Scheduled | 2 | MUL | Outage for CE Comms tower installation | 6.95
2010-11-08 06:34 | 2010-11-08 13:09 | Scheduled | 3 | MUL | Outage for CE Comms tower installation | 6.5833
2010-11-09 06:04 | 2010-11-09 13:19 | Scheduled | 1 | MUL | Outage for CE Comms tower installation | 7.25
2010-11-09 06:09 | 2010-11-09 13:20 | Scheduled | 2 | MUL | Outage for CE Comms tower installation | 7.1833
2010-11-09 06:15 | 2010-11-09 13:21 | Scheduled | 3 | MUL | Outage for CE Comms tower installation | 7.1
2010-11-18 07:07 | 2010-11-18 14:42 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable. | 7.5833
2010-11-18 07:10 | 2010-11-18 14:42 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 7.5333
2010-11-23 07:02 | 2010-11-24 15:30 | Scheduled | 1 | Both | IGBT/FO Test & Replacement | 32.4667
2010-11-30 07:05 | 2010-11-30 14:31 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 7.4333
2010-11-30 07:07 | 2010-11-30 14:33 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 7.4333
2010-12-06 06:46 | 2010-12-07 17:02 | Scheduled | 1 | Both | IGBT/FO Test & Investigation with ABB Mikael | 34.2667
2010-12-08 07:08 | 2010-12-09 14:48 | Scheduled | 2 | Both | IGBT/FO Test & Investigation with ABB Mikael | 31.6667
2010-12-09 14:51 | 2010-12-10 17:06 | Scheduled | 3 | Both | IGBT/FO Test & Investigation with ABB Mikael | 26.25
2010-12-17 07:01 | 2010-12-17 17:29 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 10.4667
2010-12-21 07:02 | 2010-12-21 17:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 10.1667
2011-01-05 07:01 | 2011-01-05 14:15 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 7.2333
2011-01-05 07:04 | 2011-01-05 14:17 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 7.2167
2011-01-13 07:03 | 2011-01-13 14:28 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 7.4167
2011-01-14 07:01 | 2011-01-14 13:32 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable fault | 6.5167
2011-02-09 07:11 | 2011-02-09 17:43 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 10.5333
2011-02-09 07:13 | 2011-02-09 18:10 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 10.95
2011-02-14 07:03 | 2011-02-14 16:10 | Scheduled | 1 | Both | Outage to enable access to the replacement of BLA System 3, B Phase CB Pole | 9.1167
2011-02-14 07:15 | 2011-02-14 17:41 | Scheduled | 2 | Both | Outage to enable access to the replacement of BLA System 3, B Phase CB Pole | 10.4333
2011-04-01 06:18 | 2011-04-01 13:48 | Scheduled | 1 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.5
2011-04-01 06:19 | 2011-04-01 13:49 | Scheduled | 2 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.5
2011-04-01 06:21 | 2011-04-01 13:49 | Scheduled | 3 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.4667
2011-04-21 07:01 | 2011-04-21 15:26 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 8.4167
2011-04-21 07:02 | 2011-04-21 15:28 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 8.4333
2011-05-25 07:04 | 2011-05-25 18:32 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault. | 11.4667
2011-07-14 06:11 | 2011-07-14 20:25 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 14.2333
2011-07-29 07:02 | 2011-07-29 18:48 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 11.7667
2011-08-05 07:07 | 2011-08-05 15:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 8.0833
2011-08-17 07:05 | 2011-08-17 14:07 | Scheduled | 1 | Both | Outage for CE Comms tower work | 7.0333
2011-08-17 07:17 | 2011-08-17 14:20 | Scheduled | 2 | Both | Outage for CE Comms tower work | 7.05
2011-08-17 07:24 | 2011-08-17 14:18 | Scheduled | 3 | Both | Outage for CE Comms tower work | 6.9
2011-08-31 11:52 | 2011-08-31 18:07 | Scheduled | 1 | Both | Outage for Coucil excavation of water pipe at Bungalora | 6.25 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-08-31 11:54 | 2011-08-31 18:07 | Scheduled | 2 | Both | Outage for Coucil excavation of water pipe at Bungalora | 6.2167 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-09-02 07:03 | 2011-09-02 17:49 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 10.7667
2011-09-02 07:04 | 2011-09-02 17:53 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 10.8167
2011-09-26 07:07 | 2011-09-26 15:59 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 8.8667
2011-09-30 07:05 | 2011-09-30 17:10 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable fault | 10.0833
2011-09-30 07:12 | 2011-09-30 17:13 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable fault | 10.0167
2011-11-03 07:18 | 2011-11-03 13:22 | Scheduled | 2 | BLA | Outage to add SF6 Gas to bypass breaker | 6.0667 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-11-08 07:43 | 2011-11-09 16:07 | Scheduled | 1 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 32.4
2011-11-08 08:01 | 2011-11-09 16:11 | Scheduled | 3 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 32.1667
2011-11-08 08:03 | 2011-11-09 17:37 | Scheduled | 2 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 33.5667
2011-11-30 07:24 | 2011-11-30 16:12 | Scheduled | 3 | Both | Outage to install sound prrofing on transformer | 8.8
2011-12-06 09:55 | 2011-12-06 10:37 | Scheduled | 2 | Both | Outage to add SF6 Gas to bypass breaker | 0.7 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-12-19 07:02 | 2011-12-19 14:15 | Scheduled | 1 | Both | Outage to repair System 3 cable fault | 7.2167
2011-12-19 07:12 | 2011-12-19 15:52 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 8.6667
2012-01-06 06:06 | 2012-01-06 12:32 | Scheduled | 3 | MUL | Transformer Sound enclosure repairs | 6.4333
2012-01-16 08:03 | 2012-01-16 14:37 | Scheduled | 1 | Both | Outage to repair System 2 cable fault | 6.5667
2012-01-16 08:03 | 2012-01-16 14:38 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 6.5833
2012-02-13 07:05 | 2012-02-13 16:30 | Scheduled | 2 | Both | Outage to repair System 1 cable fault | 9.4167
2012-02-13 07:08 | 2012-02-13 16:29 | Scheduled | 3 | Both | Outage to repair System 1 cable fault | 9.35
2012-02-20 07:44 | 2012-02-21 13:04 | Scheduled | 2 | Both | Outage for IGBT replacement at Bungalora and & Transformer measurement at Mullumbimby | 29.3333 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-03-02 09:15 | 2012-03-02 09:44 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 0.48333 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-03-03 07:11 | 2012-03-03 15:00 | Scheduled | 3 | Both | Outage to repair System 1 cable fault | 7.8167
2012-03-03 07:14 | 2012-03-03 15:00 | Scheduled | 2 | Both | Outage to repair System 1 cable fault | 7.7667
2012-03-30 07:00 | 2012-04-05 14:28 | Scheduled | 3 | MUL | Outage for Transformer sound enclosure. | 151.4667
2012-04-17 07:10 | 2012-04-17 15:28 | Scheduled | 1 | Both | Outage to repair System 2 cable fault | 8.3
2012-04-17 07:10 | 2012-04-20 13:51 | Scheduled | 1 | MUL | Outage for Transformer sound enclosure. | 78.6833
2012-04-17 07:18 | 2012-04-17 15:28 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 8.1667
2012-05-22 10:34 | 2012-05-22 11:08 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 0.56667 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-06-06 06:14 | 2012-06-06 18:36 | Scheduled | 1 | MUL | Outage for Country Energy protection installation | 12.3667
2012-06-06 06:16 | 2012-06-06 18:38 | Scheduled | 2 | MUL | Outage for Country Energy protection installation | 12.3667
2012-06-19 10:04 | 2012-06-19 11:06 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 1.0333 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-07-11 07:02 | 2012-07-11 15:33 | Scheduled | 1 | Both | Outage to repair System 3 cable fault | 8.5167
2012-07-11 07:03 | 2012-07-11 15:35 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 8.5333
2012-07-17 07:02 | 2012-07-18 19:50 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.8
2012-07-17 07:18 | 2012-07-18 19:53 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.5833
2012-07-23 06:59 | 2012-07-24 16:13 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.2333
2012-07-23 07:01 | 2012-07-24 16:25 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.4
2012-09-20 07:29 | 2012-09-21 14:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault, return to service delayed by the need to inspect phase reactors for moisture. | 30.5167
2013-01-09 07:50 | 2013-01-09 14:21 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 6.5167
2013-03-07 07:05 | 2013-03-07 13:57 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 6.8667
2013-04-22 06:59 | 2013-04-22 16:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 9.0167
2013-07-29 10:00 | 2013-07-29 13:38 | Scheduled | 2 | BLA | Outage to allow Essential Energy access at Terranora to position a crane. | 3.6333
2013-07-29 10:00 | 2013-07-29 15:05 | Scheduled | 3 | BLA | Outage to allow Essential Energy access at Terranora to position a crane. | 5.0833
2013-08-06 06:06 | 2013-08-06 18:00 | Scheduled | 3 | BLA | Outage to de-energise the overhead buss to allow replacement of CT in the transformers of system 1 and system 2. | 11.9
2014-02-27 06:26 | 2014-02-27 18:28 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 12.0333
2014-03-12 06:05 | 2014-03-12 14:58 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 8.8833
2014-04-11 08:06 | 2014-04-11 14:16 | Scheduled | 2 | Both | Outage to excavate System 2 cable fault | 6.1667
2014-04-16 07:28 | 2014-04-16 17:33 | Scheduled | 2 | Both | Outage to excavate System 2 cable fault | 10.0833

## Avg Cct Outage Rate
Outage Start | Outage Finish |  | System | Converter | Description | Duration | Fault | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | [5 empty] | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014
2007-01-01 | 2007-02-08 18:00 | forced | 1 | BLA | Transformer differential trip, suspected loose core lamination. This portion of the outage is in 2007 | 930 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-01-07 07:00 | 2007-01-07 12:20 | forced | 2 | MUL | Computer failure at Mullumbimby | 5.3333 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-03-17 08:28 | 2007-03-17 16:31 | scheduled | 1 | MUL | Repairs to galvanised steel troughing | 8.05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-03-17 08:59 | 2007-03-18 17:14 | forced | 2 | BLA | PCP mach2 computer failed during switching for planned repairs. | 32.25 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-03-17 08:59 | 2007-03-17 16:32 | scheduled | 3 | MUL | Repairs to galvanised steel troughing | 7.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-03-18 08:25 | 2007-03-18 17:14 | scheduled | 1 | BLA | Repairs to galvanised steel troughing | 8.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-03-18 08:25 | 2007-03-18 17:14 | scheduled | 3 | BLA | Repairs to galvanised steel troughing | 8.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 1 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 2 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 3 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-09 13:29 | 2007-04-09 16:35 | forced | 1 | MUL | Loss of pole 1, caused by 11kV fault. | 3.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-16 09:30 | 2007-04-16 11:00 | scheduled | 1 | Both | Single system outage for site visits | 1.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-05-04 08:30 | 2007-05-04 11:30 | scheduled | 1 | both | Single system outage for site visits | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-05-25 08:56 | 2007-07-25 10:41 | forced | 3 | both | Cooling water leak in valve hall, phase reactor failure. | 1465.75 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-05-25 10:51 | 2007-05-25 14:36 | forced | 2 | both | Pole 2 tripped, no fault found, returned to service. | 3.75 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-02 22:13 | 2007-06-07 16:11 | forced | 2 | both | More than 5 IGBTs failed in a stack. | 113.9667 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-07 01:58 | 2007-06-27 14:03 | forced | 1 | both | DC cable fault | 492.0833 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-16 12:14 | 2007-06-18 09:56 | forced | 2 | both | A Powerlink fault at Mudgeeraba caused the loss of 110kV supplies to Terranora. | 45.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-18 10:18 | 2007-06-18 10:29 | forced | 2 | BLA | Power supply problem in PCPB Mach 2 | 0.18333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-29 05:55 | 2007-06-29 05:58 | forced | 1 | MUL | Spurious trip, unknown cause | 0.05 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-29 05:55 | 2007-06-29 05:58 | forced | 2 | MUL | Spurious trip, unknown cause | 0.05 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-07-09 16:21 | 2007-07-10 11:50 | forced | 2 | BLA | Cooling equipment fault at Bungalora pole 2 | 19.4833 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-07-18 08:32 | 2007-07-18 13:05 | scheduled | 1 | BLA | Inspection of phase reactors at Bungalora | 4.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-07-19 08:32 | 2007-07-19 13:12 | forced | 2 | MUL | Spurious trip, unknown cause | 4.6667 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-08-01 15:30 | 2007-08-02 12:45 | forced | 3 | both | Pole 3 tripped, unknown cause. | 21.25 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-08-19 01:51 | 2007-08-19 14:43 | forced | 3 | both | Abnormal frequency trip | 12.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-09-04 07:01 | 2007-09-04 20:02 | scheduled | 1 | both | Annual maintenance | 13.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-09-05 14:22 | 2007-09-06 00:19 | scheduled | 2 | both | Annual maintenance | 9.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-09-06 07:00 | 2007-09-06 18:45 | scheduled | 3 | both | Annual maintenance | 11.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-10-05 12:17 | 2007-11-15 14:30 | forced | 1 | BLA | Differential trip at Bungalora | 986.2167 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-10-26 22:30 | 2007-10-26 23:21 | forced | 2 | Both | Fault on 132kV system | 0.85 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-10-26 22:30 | 2007-10-26 23:21 | forced | 3 | Both | Fault on 132kV system | 0.85 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-05 11:00 | 2007-11-05 13:10 | scheduled | 2 | Both | Systems 2 & 3 down for excavation on system 1 | 2.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-05 11:00 | 2007-11-05 13:10 | scheduled | 3 | Both | Systems 2 & 3 down for excavation on system 1 | 2.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-27 07:15 | 2007-11-27 17:00 | scheduled | 1 | both | Maintenance - Phase Reactors and IGBTs. Control system faults prevent return to service. | 9.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-27 17:00 | 2007-12-19 17:00 | forced | 1 | MUL | Computer failure on pole 1 at Mullumbimby. | 528 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-28 07:15 | 2007-11-28 17:00 | scheduled | 2 | both | Maintenance - Phase Reactors and IGBTs. Control system faults prevent return to service. | 9.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-28 17:00 | 2007-12-20 18:05 | forced | 2 | both | Computer failure on pole 2 at Mullumbimby. | 529.0833 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-29 08:08 | 2007-11-29 15:14 | scheduled | 3 | both | Maintenance - Phase Reactors and IGBTs. | 7.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-12-30 13:10 | 2008-01-01 | forced | 2 | BLA | Auxiliary Power Failure caused control system problems | 34.8333 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-12-30 13:10 | 2008-01-01 | forced | 3 | BLA | Auxiliary Power Failure caused control system problems | 34.8333 | A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-01-01 | 2008-01-02 20:09 | forced | 2 | BLA | Auxiliary Power Failure caused control system problems | 44.1497 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-01-01 | 2008-01-02 16:50 | forced | 3 | BLA | Auxiliary Power Failure caused control system problems | 40.8331 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-02 22:11 | 2008-02-03 10:48 | forced | 2 | MUL | Control System Faults | 12.6167 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-13 08:30 | 2008-02-13 17:00 | scheduled | 1 | both | Shutdown to investigate various faults | 8.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-19 06:00 | 2008-02-21 00:27 | forced | 2 | both | Computer failure on pole 2 | 42.45 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-20 07:00 | 2008-02-20 11:00 | scheduled | 1 | both | Fire System Maintenance | 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-20 11:05 | 2008-02-20 13:50 | scheduled | 3 | both | Fire System Maintenance | 2.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-27 08:00 | 2008-02-27 10:35 | scheduled | 1 | BLA | Installation of power flow monitoring gear | 2.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-27 10:12 | 2008-02-27 13:46 | scheduled | 2 | BLA | Installation of power flow monitoring gear | 3.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-27 11:00 | 2008-02-27 15:34 | scheduled | 3 | BLA | Installation of power flow monitoring gear | 4.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-03-08 19:31 | 2008-03-28 13:00 | forced | 2 | both | Cable fault | 473.4833 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-03-13 16:07 | 2008-04-04 15:00 | forced | 1 | both | Cable fault | 526.8833 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-03-18 09:35 | 2008-03-18 12:20 | scheduled | 3 | both | Outage to safely excavate sys1 cables for repair | 2.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-03-30 14:07 | 2008-03-30 18:00 | forced | 3 | both | Unknown fault caused converter to trip | 3.8833 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-09 07:25 | 2008-04-09 15:35 | scheduled | 3 | both | Phase reactor inspections | 8.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-10 07:25 | 2008-04-10 14:56 | scheduled | 2 | both | Phase reactor inspections | 7.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-11 07:08 | 2008-04-24 17:32 | scheduled | 1 | both | Phase reactor inspections and Transformer swap out | 322.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-13 07:00 | 2008-04-13 17:00 | scheduled | 2 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-13 07:00 | 2008-04-13 17:00 | scheduled | 3 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-14 15:09 | 2008-05-01 16:00 | forced | 2 | both | System 2 Cable fault | 408.85 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-16 07:00 | 2008-04-16 17:00 | scheduled | 2 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-16 07:00 | 2008-04-16 17:00 | scheduled | 3 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-12 08:00 | 2008-05-15 18:45 | scheduled | 1 | both | Phase reactor repairs | 82.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-15 17:00 | 2008-05-15 18:45 | scheduled | 2 | both | Communications Test | 1.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-15 17:00 | 2008-05-15 18:45 | scheduled | 3 | both | Communications Test | 1.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-16 08:00 | 2008-05-17 13:40 | scheduled | 3 | both | Phase reactor repairs | 29.6667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-18 08:00 | 2008-05-19 14:11 | scheduled | 2 | both | Phase reactor repairs | 30.1833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 1 | both | Comms cut over for trial operation | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 2 | both | Comms cut over for trial operation | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 3 | both | Comms cut over for trial operation | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 1 | both | Comms cut over after trial operation | 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 2 | both | Comms cut over after trial operation | 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 3 | both | Comms cut over after trial operation | 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 1 | both | Comms cut over for trial operation | 0.58333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 2 | both | Comms cut over for trial operation | 0.58333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 3 | both | Comms cut over for trial operation | 0.58333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 1 | both | Comms cut over after trial operation | 0.33333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 2 | both | Comms cut over after trial operation | 0.33333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 3 | both | Comms cut over after trial operation | 0.33333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 20:12 | 2008-05-23 16:05 | forced | 3 | both | Reactor cooling fan fault. | 19.8833 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 1 | both | Final comms cut over. | 0.41667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 2 | both | Final comms cut over. | 0.41667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 3 | both | Final comms cut over. | 0.41667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-09 03:21 | 2008-06-10 17:06 | forced | 3 | BLA | PCPA hard disk fault | 37.75 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 1 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 2 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 3 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 1 | MUL | Country Energy outage to connect CB 7H3 | 13.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 2 | MUL | Country Energy outage to connect CB 7H3 | 13.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 3 | MUL | Country Energy outage to connect CB 7H3 | 13.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 1 | both | Comms fault from Dandenong to DL | 1.75 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 2 | both | Comms fault from Dandenong to DL | 1.75 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 3 | both | Comms fault from Dandenong to DL | 1.75 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 20:40 | 2008-06-27 18:00 | forced | 1 | BLA | Faulty IGBTs | 45.3333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-27 22:47 | 2008-07-09 15:43 | forced | 2 | both | Cable Fault | 280.9333 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 03:30 | 2008-06-29 08:00 | forced | 1 | MUL | TransGrid Tripping Scheme operation | 4.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 03:30 | 2008-06-29 08:00 | forced | 3 | MUL | TransGrid Tripping Scheme operation | 4.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 08:00 | 2008-06-29 10:27 | forced | 1 | MUL | Mach 2 faults after TransGrid Tripping Scheme operation | 2.4497 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 08:00 | 2008-06-29 10:27 | forced | 3 | MUL | Mach 2 faults after TransGrid Tripping Scheme operation | 2.4497 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-11 07:00 | 2008-07-11 18:43 | forced | 3 | BLA | Reactor Fan Trip | 11.7167 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-12 08:25 | 2008-07-12 16:15 | scheduled | 1 | BLA | Valve Cooling Water Leak Inspection | 7.8333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-14 11:03 | 2008-08-04 14:54 | forced | 2 | both | Cable fault | 507.85 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-20 01:02 | 2008-07-20 05:29 | scheduled | 1 | both | Country Energy outage | 4.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-20 01:02 | 2008-07-20 05:29 | scheduled | 3 | both | Country Energy outage | 4.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-25 09:03 | 2008-07-25 11:20 | scheduled | 1 | both | Outage to excavate Cables for repair to system 2 cable fault | 2.2833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-25 09:03 | 2008-07-25 11:20 | scheduled | 3 | both | Outage to excavate Cables for repair to system 2 cable fault | 2.2833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-25 11:20 | 2008-08-01 16:15 | forced | 3 | 0 | After outage to excavate cables for repair to system 2 cable fault, L2 phase of system 3 circuit breaker would not close. | 172.9167 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-31 09:46 | 2008-07-31 14:35 | scheduled | 1 | both | Outage to excavate Cables for repair to system 2 cable fault | 4.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 1 | both | Abnormal frequency trip | 5.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 2 | both | Abnormal frequency trip | 5.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 3 | both | Abnormal frequency trip | 5.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-16 07:00 | 2008-09-18 17:26 | scheduled | 2 | both | Annual Maintenance | 58.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-18 07:30 | 2008-09-19 17:00 | scheduled | 3 | both | Annual Maintenance | 33.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-19 17:00 | 2008-09-21 07:00 | forced | 3 | both | Mullumbimby sytem 3 control system fault | 38 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-20 07:00 | 2008-09-21 07:00 | scheduled | 1 | both | Annual Maintenance | 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 1 | both | Country energy requested outage for maintenance at Terranora | 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 2 | both | Country energy requested outage for maintenance at Terranora | 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 3 | both | Country energy requested outage for maintenance at Terranora | 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 16:00 | 2008-09-25 15:55 | forced | 1 | both | Bungalora pre-insertion resistor overload trip - earths left on in the barn | 95.9167 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 16:00 | 2008-10-07 16:05 | forced | 3 | both | Mullumbimby sytem 3 control system fault | 384.0833 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-25 14:22 | 2008-09-25 20:17 | forced | 2 | both | Mullumbimby reactor cooling fan trip | 5.9167 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-10-01 18:17 | 2008-11-14 19:11 | forced | 2 | both | Cable Fault P1 cable. | 1056.9 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-07 13:59 | 2008-11-14 18:51 | forced | 1 | both | Cable Fault P1 cable. | 172.8667 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 1 | BLA | Auxiliary power failure | 1.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 2 | BLA | Auxiliary power failure | 1.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 3 | BLA | Auxiliary power failure | 1.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-24 07:02 | 2008-11-24 15:02 | scheduled | 1 | both | Phase Reactor Inspections and cable clamp modifications | 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-25 06:54 | 2008-11-25 15:36 | scheduled | 2 | both | Phase Reactor Inspections and cable clamp modifications | 8.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-26 07:05 | 2008-11-26 14:45 | scheduled | 3 | both | Phase Reactor Inspections and cable clamp modifications | 7.6667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-27 07:10 | 2008-11-27 13:14 | scheduled | 1 | both | Phase Reactor Inspections and cable clamp modifications | 6.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-08 01:18 | 2008-12-16 13:12 | forced | 2 | both | Cable Fault P1 cable. | 203.9 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-15 08:10 | 2008-12-15 10:25 | scheduled | 1 | both | Outage to locate Pole 1 cable fault | 2.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-15 08:17 | 2008-12-15 10:28 | scheduled | 3 | both | Outage to locate Pole 1 cable fault | 2.1833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-19 23:06 | 2008-12-31 09:42 | forced | 2 | both | Cable Fault P1 cable. | 274.6 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-30 07:41 | 2008-12-30 09:24 | scheduled | 3 | both | Outage to locate Pole 1 cable fault | 1.7167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-30 07:47 | 2008-12-30 09:22 | scheduled | 1 | both | Outage to locate Pole 1 cable fault | 1.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-31 11:13 | 2009-01-01 | forced | 2 | both | Cable Fault P1 cable. | 12.7831 | A | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-01-01 | 2009-01-20 09:22 | forced | 2 | both | Cable Fault P1 cable. | 465.3667 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-01-11 13:00 | 2009-01-19 12:06 | forced | 1 | both | Cable Fault P1 cable. | 191.1 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-01-16 07:00 | 2009-01-16 14:01 | scheduled | 3 | both | Outage to repair Pole 1 and Pole 2 cable faults | 7.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-09 21:00 | 2009-02-18 10:53 | forced | 2 | both | Cable Fault P1 cable. | 205.8833 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-10 07:26 | 2009-02-10 12:01 | scheduled | 1 | both | Outage for Country Energy maintenance - 110kV bus at Terranora substation | 4.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-10 07:36 | 2009-02-10 12:06 | scheduled | 3 | both | Outage for Country Energy maintenance - 110kV bus at Terranora substation | 4.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-16 09:05 | 2009-02-16 13:05 | scheduled | 1 | both | Outage to repair Pole 2 cable fault | 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-16 09:07 | 2009-02-16 13:06 | scheduled | 3 | both | Outage to repair Pole 2 cable fault | 3.9833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-16 13:16 | 2009-02-16 15:00 | scheduled | 3 | both | Outage to repair Pole 2 cable fault | 1.7333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-16 13:17 | 2009-02-16 14:59 | scheduled | 1 | both | Outage to repair Pole 2 cable fault | 1.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-10 07:31 | 2009-03-10 15:23 | scheduled | 3 | both | Outage for six month maintenance | 7.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-11 07:31 | 2009-03-11 13:54 | scheduled | 2 | both | Outage for six month maintenance | 6.3833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-12 07:03 | 2009-03-13 08:02 | scheduled | 1 | both | Outage for six month maintenance | 24.9833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-17 09:40 | 2009-03-30 13:51 | forced | 3 | both | Cable Fault P1 & P2 cable. | 316.1833 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-26 07:04 | 2009-03-26 15:51 | scheculed | 1 | both | Outage to repair Pole 3 cable fault | 8.7833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-26 07:37 | 2009-03-26 15:53 | scheculed | 2 | both | Outage to repair Pole 3 cable fault | 8.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-27 07:03 | 2009-03-27 13:24 | scheculed | 1 | both | Outage to repair Pole 3 cable fault | 6.35 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-27 07:08 | 2009-03-27 13:26 | scheculed | 2 | both | Outage to repair Pole 3 cable fault | 6.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-15 10:01 | 2009-04-15 11:28 | scheculed | 1 | both | Outage for access valve enclosure lock change | 1.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-15 11:48 | 2009-04-15 13:57 | scheculed | 2 | both | Outage for access valve enclosure lock change | 2.15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-15 14:08 | 2009-04-15 15:23 | scheculed | 3 | both | Outage for access valve enclosure lock change | 1.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-20 20:46 | 2009-05-20 23:31 | forced | 1 | BLA | Auxilary power outage caused a reactor cooling fan changeover. Dampers did not open in time causing a trip. | 2.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-21 05:10 | 2009-05-21 06:52 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Return delayed to investigate a CB Relay fault. | 1.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-21 05:10 | 2009-05-21 05:24 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.23333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-21 05:10 | 2009-05-21 05:24 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.23333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 04:32 | 2009-05-22 04:38 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 04:32 | 2009-05-22 04:39 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.11667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 04:32 | 2009-05-22 04:40 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.13333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 07:59 | 2009-05-22 08:59 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 07:59 | 2009-05-22 09:03 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 1.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 07:59 | 2009-05-22 09:03 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 1.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 15:18 | 2009-05-22 16:34 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 1.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 15:18 | 2009-05-22 15:48 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 15:18 | 2009-05-22 15:48 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-23 17:22 | 2009-05-24 13:22 | forced | 3 | MUL | AC Filter capacitor protection trip. | 20 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:02 | 2009-05-23 19:15 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.21667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:02 | 2009-05-23 19:14 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:34 | 2009-05-23 19:40 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:34 | 2009-05-23 19:41 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.11667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-26 18:02 | 2009-06-06 13:08 | forced | 2 | Both | Cable fault P1 cable, Return to service delayed by too any Faulty IGBTs in B phase | 259.1 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-02 11:54 | 2009-06-02 12:10 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.26667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-02 11:54 | 2009-06-02 12:10 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.26667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-02 12:15 | 2009-06-02 14:28 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 2.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-02 12:15 | 2009-06-02 14:28 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 2.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-03 09:16 | 2009-06-03 14:49 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 5.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-03 09:16 | 2009-06-03 14:51 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-30 06:50 | 2009-07-18 10:29 | forced | 2 | Both | Cable fault P1 cable, Return to service delayed by too any Faulty IGBTs in B phase | 435.65 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-14 09:04 | 2009-07-14 14:19 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 5.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-14 09:13 | 2009-07-14 14:21 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 5.1333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-15 08:36 | 2009-07-15 10:24 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 1.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-15 08:38 | 2009-07-15 10:21 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 1.7167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-16 09:02 | 2009-07-16 17:29 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 8.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-16 09:12 | 2009-07-16 17:32 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 8.3333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-16 17:29 | 2009-07-21 17:38 | forced | 1 | Both | Unable to return to service. Too many faulty igbts. | 120.15 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-07-20 18:28 | 2009-07-21 09:54 | forced | 2 | Both | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 15.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-20 18:28 | 2009-07-21 09:56 | forced | 3 | Both | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 15.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-27 06:36 | 2009-07-28 17:04 | Scheduled | 1 | Both | Shutdown for annual maintenance | 34.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-29 06:49 | 2009-07-30 17:26 | Scheduled | 2 | Both | Shutdown for annual maintenance | 34.6167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-31 06:32 | 2009-08-01 13:02 | Scheduled | 3 | Both | Shutdown for annual maintenance | 30.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-14 10:52 | 2009-08-14 11:38 | forced | 1 | Both | Trip caused by flow protection. Standby pump did not start when pumps changed during while converter was running. | 0.76667 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-25 13:27 | 2009-08-29 14:54 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 97.45 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-27 08:07 | 2009-08-27 16:49 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 8.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-27 08:14 | 2009-08-27 16:47 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 8.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-27 17:11 | 2009-08-27 21:20 | forced | 1 | MUL | Trip caused by Coutry Energy protection operation. Failed protection CT in Mullumbimby system 3 transformer | 4.15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-27 17:11 | 2009-09-04 17:04 | forced | 3 | MUL | Trip caused by Coutry Energy protection operation. Failed protection CT in Mullumbimby system 3 transformer | 191.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-09-04 07:22 | 2009-09-04 16:49 | Scheduled | 1 | MUL | Outage for HV access to repair failed protection CT in Mullumbimby system 3 transformer | 9.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-09-04 07:23 | 2009-09-04 16:50 | Scheduled | 2 | MUL | Outage for HV access to repair failed protection CT in Mullumbimby system 3 transformer | 9.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-09-29 07:04 | 2009-09-29 17:14 | Scheduled | 1 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-09-29 07:07 | 2009-09-29 17:39 | Scheduled | 2 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.5333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-09-29 07:09 | 2009-09-29 17:18 | Scheduled | 3 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-03 13:23 | 2009-11-03 14:01 | forced | 3 | BLA | Trip by Flow Protection - Active CCP accidentally reset during maintenance | 0.63333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-11-04 02:42 | 2009-11-13 10:18 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 223.6 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-10 17:50 | 2009-11-10 18:44 | forced | 3 | Bla | Fault with 24V DC power supply | 0.9 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-11 10:11 | 2009-11-11 16:08 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-11 10:16 | 2009-11-11 16:06 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 5.8333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-19 01:51 | 2009-11-28 09:57 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 224.1 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-20 02:17 | 2009-11-20 02:55 | forced | 2 | MUL | Abnormal Frequency Trip. Country Energy System Problems. | 0.63333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-20 02:17 | 2009-11-20 02:56 | forced | 3 | MUL | Abnormal Frequency Trip. Country Energy System Problems. | 0.65 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-26 09:06 | 2009-11-26 14:59 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-26 09:15 | 2009-11-26 14:57 | Scheduled | 2 | Both | Outage to enable access to repair the system 2 cable. | 5.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-27 10:28 | 2009-11-27 11:03 | forced | 3 | MUL | Damper Resistor overload trip event on one PCP. Converter tripped while trying to clear the event. | 0.58333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2009-11-28 10:30 | 2009-12-17 14:49 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 460.3167 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-11 00:52 | 2009-12-11 02:16 | forced | 1 | BLA | Operation of Powerlink intertrip scheme. | 1.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-11 00:52 | 2009-12-11 02:17 | forced | 3 | BLA | Operation of Powerlink intertrip scheme. | 1.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-12 08:13 | 2009-12-12 08:58 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-12 08:13 | 2009-12-12 08:59 | forced | 3 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.76667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-15 07:02 | 2009-12-15 17:07 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 10.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-15 07:20 | 2009-12-15 17:04 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 9.7333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-17 22:14 | 2010-01-01 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 337.7664 | A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-01 | 2010-01-14 09:14 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 321.2333 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-08 18:49 | 2010-01-08 19:11 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.36667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-08 18:49 | 2010-01-08 19:13 | forced | 3 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-09 13:04 | 2010-03-31 14:01 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 1944.95 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-12 07:16 | 2010-01-12 16:16 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-13 13:37 | 2010-01-21 09:56 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 188.3167 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-15 07:23 | 2010-01-15 08:05 | forced | 2 | 0 | Trip during control system maintenance | 0.7 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-01-19 07:03 | 2010-01-19 14:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 7.15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-20 21:01 | 2010-01-20 21:34 | forced | 2 | 0 | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-27 05:30 | 2010-03-31 13:54 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 1520.4 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-03-27 06:04 | 2010-03-27 17:35 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. | 11.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-03-28 06:04 | 2010-03-28 15:41 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 9.6167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-03-31 23:18 | 2010-04-17 09:26 | forced | 1 | Both | Cable fault P1 (+ve) cable. After cable repair, fault with DC voltage measuring delayed return to service. | 394.1333 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-04-09 17:48 | 2010-04-20 13:44 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 259.9333 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-04-14 07:04 | 2010-04-15 15:51 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. Too many faulty igbts when energised from Mullumbimby. Igbts repaired the next day during system 2 cable fault repair. | 32.7833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-04-17 09:26 | 2010-04-28 13:37 | forced | 1 | Both | Fault with DC voltage measuring delayed return to service after repair P1 (+ve) cable, | 268.1833 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-04-30 19:18 | 2010-06-13 10:34 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 1047.2667 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-05-05 11:00 | 2010-05-05 13:14 | forced | 1 | BLA | Trip during fault finding of PCPB DC voltage measuring | 2.2333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-05-24 07:14 | 2010-05-28 14:24 | Scheduled | 3 | Both | Outage to replace transformer CTs | 103.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-05-25 07:03 | 2010-05-25 19:33 | Scheduled | 1 | Both | Outage to allow overhead crane access for replacing system 3 transformer CTs | 12.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-05-31 10:05 | 2010-05-31 17:23 | Scheduled | 1 | Both | Outage to excavate the system 2 cable fault. | 7.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-05-31 10:10 | 2010-05-31 17:26 | Scheduled | 3 | Both | Outage to excavate the system 2 cable fault under the river. | 7.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-05-31 17:26 | 2010-06-08 13:18 | forced | 3 | Both | Outage to excavate the system 2 cable fault. Return to service delayed due to VCU Faults. | 187.8667 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-06-01 13:43 | 2010-06-01 14:33 | Scheduled | 1 | Both | Outage to cut system 2 cable during repair of fault under the river. | 0.83333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-06-03 06:55 | 2010-06-03 17:48 | Scheduled | 1 | Both | Outage to joint system 2 cable during repair of fault under the river. | 10.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-06-04 07:00 | 2010-06-04 16:15 | Scheduled | 1 | Both | Outage to joint system 2 cable during repair of fault under the river. | 9.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-06-10 02:02 | 2010-06-10 16:02 | forced | 3 | BLA | Trip due to low water level. Pump leaking. | 14 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-06 01:03 | 2010-07-06 16:18 | forced | 2 | MUL | UPS failure caused trip of converter | 15.25 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-15 22:07 | 2010-07-26 08:19 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 250.2 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-22 06:03 | 2010-07-22 17:22 | Scheduled | 1 | BLA | CE Requested Outage - Terranora Bus zone breakers | 11.3167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-22 06:06 | 2010-07-22 17:23 | Scheduled | 3 | BLA | CE Requested Outage - Terranora Bus zone breakers | 11.2833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-22 17:22 | 2010-07-26 07:00 | forced | 1 | MUL | Return to serivce delayed - Too many faulty IGBTs | 85.6333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-07-22 17:23 | 2010-07-26 07:00 | forced | 3 | BLA | Return to serivce delayed - Too many faulty IGBTs | 85.6167 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-07-26 07:00 | 2010-07-28 14:39 | Scheduled | 3 | Both | Annual Maintenance | 55.65 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-26 07:00 | 2010-07-29 15:18 | Scheduled | 1 | Both | Annual Maintenance | 80.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-28 15:02 | 2010-07-29 14:44 | forced | 3 | BLA | Phase reactor partial discharge repair | 23.7 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-07-30 08:41 | 2010-07-31 16:49 | Scheduled | 2 | Both | Annual Maintenance | 32.1333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-31 08:38 | 2010-07-31 10:00 | Scheduled | 1 | MUL | CE Requested Outage - Lismore Tripping Scheme Work | 1.3667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-31 08:46 | 2010-07-31 10:01 | Scheduled | 3 | MUL | CE Requested Outage - Lismore Tripping Scheme Work | 1.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-31 16:49 | 2010-08-06 13:25 | forced | 2 | MUL | Return to serivce delayed - faulty control system components | 140.6 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 1 | BLA | Auxiliary power failure | 0.88333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 2 | BLA | Auxiliary power failure | 0.88333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 3 | BLA | Auxiliary power failure | 0.88333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-09 08:37 | 2010-08-11 13:40 | forced | 1 | BLA | Restoration after auxiliary power failure | 53.05 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-09 08:37 | 2010-08-09 15:58 | forced | 2 | BLA | Restoration after auxiliary power failure | 7.35 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-09 08:37 | 2010-08-09 09:43 | forced | 3 | BLA | Restoration after auxiliary power failure | 1.1 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-08-10 12:04 | 2010-08-10 18:39 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 6.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-10 12:06 | 2010-08-10 18:35 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 6.4833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-11 06:04 | 2010-08-11 13:42 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 7.6333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-11 06:05 | 2010-08-11 13:41 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 7.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-14 06:08 | 2010-08-14 12:44 | Scheduled | 1 | BLA | County Energy Requested outage for work at Terranora | 6.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-14 06:10 | 2010-08-14 12:45 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 6.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-14 06:11 | 2010-08-14 12:46 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 6.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-15 06:03 | 2010-08-15 11:50 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 5.7833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-15 06:05 | 2010-08-15 11:48 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 5.7167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-15 06:06 | 2010-08-15 11:46 | Scheduled | 1 | BLA | County Energy Requested outage for work at Terranora | 5.6667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-22 04:00 | 2010-08-22 15:04 | forced | 2 | BLA | Reactor cooling fans tripped converter | 11.0667 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-25 09:46 | 2010-08-25 11:27 | forced | 2 | BLA | Trip caused by control system maintenance | 1.6833 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-09-02 12:50 | 2010-09-02 13:28 | Scheduled | 3 | BLA | Outage requested by Country Energy for protection testing | 0.63333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-02 12:51 | 2010-09-02 13:28 | Scheduled | 2 | BLA | Outage requested by Country Energy for protection testing | 0.61667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-02 12:51 | 2010-09-02 13:27 | Scheduled | 1 | BLA | Outage requested by Country Energy for protection testing | 0.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-18 02:43 | 2010-10-01 12:08 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 321.4167 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-19 02:02 | 2010-10-01 12:42 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 298.6667 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-27 08:01 | 2010-09-27 14:16 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 6.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-27 08:02 | 2010-09-27 16:02 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. | 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-10-06 16:23 | 2010-10-22 12:28 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 380.0833 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-10-14 08:11 | 2010-10-14 15:01 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable. | 6.8333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-10-14 08:11 | 2010-10-14 15:03 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 6.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-10-17 10:06 | 2010-10-17 14:02 | forced | 2 | MUL | Trip caused by fire protection system fault. | 3.9333 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-10-29 09:38 | 2010-10-29 11:08 | Scheduled | 1 | Both | Outage to repair GST damage. | 1.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-08 06:06 | 2010-11-08 13:07 | Scheduled | 1 | MUL | Outage for CE Comms tower installation | 7.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-08 06:11 | 2010-11-08 13:08 | Scheduled | 2 | MUL | Outage for CE Comms tower installation | 6.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-08 06:34 | 2010-11-08 13:09 | Scheduled | 3 | MUL | Outage for CE Comms tower installation | 6.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-09 06:04 | 2010-11-09 13:19 | Scheduled | 1 | MUL | Outage for CE Comms tower installation | 7.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-09 06:09 | 2010-11-09 13:20 | Scheduled | 2 | MUL | Outage for CE Comms tower installation | 7.1833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-09 06:15 | 2010-11-09 13:21 | Scheduled | 3 | MUL | Outage for CE Comms tower installation | 7.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-14 01:21 | 2010-11-20 08:14 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 150.8786 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-18 07:07 | 2010-11-18 14:42 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable. | 7.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-18 07:10 | 2010-11-18 14:42 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 7.5333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-23 07:02 | 2010-11-24 15:30 | Scheduled | 1 | Both | IGBT/FO Test & Replacement | 32.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-24 15:30 | 2010-11-26 13:45 | forced | 1 | Both | IGBT Faults | 46.25 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2010-11-25 21:15 | 2010-12-03 13:45 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 184.5 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-30 07:05 | 2010-11-30 14:31 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 7.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-30 07:07 | 2010-11-30 14:33 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 7.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-06 06:46 | 2010-12-07 17:02 | Scheduled | 1 | Both | IGBT/FO Test & Investigation with ABB Mikael | 34.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-08 07:08 | 2010-12-09 14:48 | Scheduled | 2 | Both | IGBT/FO Test & Investigation with ABB Mikael | 31.6667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-09 14:51 | 2010-12-10 17:06 | Scheduled | 3 | Both | IGBT/FO Test & Investigation with ABB Mikael | 26.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-12 14:39 | 2010-12-22 16:07 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 241.4667 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-15 19:06 | 2010-12-23 10:29 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 183.3833 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-17 07:01 | 2010-12-17 17:29 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 10.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-21 07:02 | 2010-12-21 17:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 10.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-25 01:01 | 2010-12-25 01:41 | forced | 1 | BLA | Auxiliary power failure - Rector cooling fans trip. | 0.66667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-27 13:03 | 2011-01-01 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 106.95 | A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-01 | 2011-01-07 09:07 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 153.1167 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-05 07:01 | 2011-01-05 14:15 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 7.2333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-05 07:04 | 2011-01-05 14:17 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 7.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-07 06:36 | 2011-01-17 09:35 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 242.9833 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-10 15:21 | 2011-01-18 11:39 | forced | 2 | Both | Cable fault P2 (-ve) cable. | 188.3 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-13 07:03 | 2011-01-13 14:28 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 7.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-14 07:01 | 2011-01-14 13:32 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable fault | 6.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-28 11:51 | 2011-02-10 13:59 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 314.1333 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-09 07:11 | 2011-02-09 17:43 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 10.5333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-09 07:13 | 2011-02-09 18:10 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 10.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-09 17:43 | 2011-02-14 17:24 | forced | 3 | Both | Outage due to BLA System 3, B Phase CB Pole leaking insulating gas. | 119.6833 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-02-14 07:03 | 2011-02-14 16:10 | Scheduled | 1 | Both | Outage to enable access to the replacement of BLA System 3, B Phase CB Pole | 9.1167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-14 07:15 | 2011-02-14 17:41 | Scheduled | 2 | Both | Outage to enable access to the replacement of BLA System 3, B Phase CB Pole | 10.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-14 17:41 | 2011-02-18 11:31 | forced | 2 | MUL | Unable to return to service after planned outage. Too many faulty IGBTs | 89.8333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-02-15 07:13 | 2011-02-15 07:42 | forced | 1 | MUL | Outage due to control system fault. | 0.48333 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-21 17:15 | 2011-02-21 18:31 | forced | 1 | BLA | Phase Reactor Cooling Fan L3 Trip | 1.2667 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-03-13 12:24 | 2011-03-28 13:23 | forced | 1 | MUL | Trip due to flash over in PLC filter yard. Return to service delayed due to to many faulty IGBTs | 360.9833 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-03-13 12:24 | 2011-03-13 19:31 | forced | 2 | MUL | Trip due to flash over in PLC filter yard. | 7.1167 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-03-13 12:24 | 2011-03-13 19:34 | forced | 3 | MUL | Trip due to flash over in PLC filter yard. | 7.1667 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-01 06:18 | 2011-04-01 13:48 | Scheduled | 1 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-01 06:19 | 2011-04-01 13:49 | Scheduled | 2 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-01 06:21 | 2011-04-01 13:49 | Scheduled | 3 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-01 13:49 | 2011-04-08 12:55 | forced | 2 | Both | Faulty IGBTs prevented return to service after CE outage. | 167.1 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-04-18 16:05 | 2011-04-23 13:09 | forced | 1 | Both | Cable Fault P1 (+ve) cable. | 117.0667 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-21 07:01 | 2011-04-21 15:26 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 8.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-21 07:02 | 2011-04-21 15:28 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 8.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-05-08 16:23 | 2011-06-11 16:25 | forced | 1 | Both | Outage caused by DC voltage imbalance. Return to service delayed by too many faulty IGBT optic fibres. | 816.0333 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-05-14 11:26 | 2011-05-30 11:26 | forced | 3 | Both | Cable Fault P1 (+ve) cable. Return to service after cable fault repair delayed by too many faulty IGBTs | 384 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-05-25 07:04 | 2011-05-25 18:32 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault. | 11.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-05-25 18:32 | 2011-07-22 10:15 | forced | 2 | Both | Unable to return to service after planned outage. Too many faulty IGBTs | 1383.7167 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-06-10 02:56 | 2011-07-15 10:18 | forced | 3 | Both | Cable Fault P1 (+ve) cable. | 847.3667 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-14 06:11 | 2011-07-14 20:25 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 14.2333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-15 10:30 | 2011-07-15 11:09 | forced | 3 | BLA | Cooling system trip - high water temperature - proportional valve failed to operate. | 0.65 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-18 23:25 | 2011-07-30 09:38 | forced | 1 | Both | Cable Fault P2 (-ve) cable. | 274.2167 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-22 10:50 | 2011-08-05 15:12 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 340.3667 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-29 07:02 | 2011-07-29 18:48 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 11.7667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-30 09:38 | 2011-08-05 15:11 | forced | 1 | BLA | Unable to return to service after cable fault. Too many faulty IGBTs | 149.55 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-08-05 07:07 | 2011-08-05 15:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 8.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-17 07:05 | 2011-08-17 14:07 | Scheduled | 1 | Both | Outage for CE Comms tower work | 7.0333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-17 07:17 | 2011-08-17 14:20 | Scheduled | 2 | Both | Outage for CE Comms tower work | 7.05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-17 07:24 | 2011-08-17 14:18 | Scheduled | 3 | Both | Outage for CE Comms tower work | 6.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-22 16:08 | 2011-08-23 09:50 | forced | 1 | BLA | Rector Cooling fans faulty contactor | 17.7 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-22 16:08 | 2011-08-23 00:06 | forced | 3 | BLA | Rector Cooling fans faulty contactor | 7.9667 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-23 11:48 | 2011-08-23 12:14 | forced | 2 | MUL | Trip cause during replacement of UPS fault indicating relay | 0.43333 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-25 07:07 | 2011-09-03 13:05 | forced | 3 | Both | Cable Fault P2 (-ve) cable. | 221.9667 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-30 09:39 | 2011-08-30 10:17 | forced | 2 | BLA | Valve control fault during maintenance work | 0.63333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2011-08-31 11:52 | 2011-08-31 18:07 | Scheduled | 1 | Both | Outage for Coucil excavation of water pipe at Bungalora | 6.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-31 11:54 | 2011-08-31 18:07 | Scheduled | 2 | Both | Outage for Coucil excavation of water pipe at Bungalora | 6.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-02 07:03 | 2011-09-02 17:49 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 10.7667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-02 07:04 | 2011-09-02 17:53 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 10.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-05 09:08 | 2011-09-05 18:52 | forced | 3 | MUL | Rector Cooling fans faulty contactor | 9.7333 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-12 09:30 | 2011-09-26 16:14 | forced | 1 | Both | Cable Fault P1 (+ve) cable. | 342.7333 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-24 08:33 | 2011-09-30 17:57 | forced | 2 | Both | Cable Fault P1 (+ve) cable. | 153.4 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-26 07:07 | 2011-09-26 15:59 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 8.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-30 07:05 | 2011-09-30 17:10 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable fault | 10.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-30 07:12 | 2011-09-30 17:13 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable fault | 10.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-11-03 07:18 | 2011-11-03 13:22 | Scheduled | 2 | BLA | Outage to add SF6 Gas to bypass breaker | 6.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-11-08 07:43 | 2011-11-09 16:07 | Scheduled | 1 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 32.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-11-08 08:01 | 2011-11-09 16:11 | Scheduled | 3 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 32.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-11-08 08:03 | 2011-11-09 17:37 | Scheduled | 2 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 33.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-11-30 07:24 | 2011-11-30 16:12 | Scheduled | 3 | Both | Outage to install sound prrofing on transformer | 8.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-12-06 09:55 | 2011-12-06 10:37 | Scheduled | 2 | Both | Outage to add SF6 Gas to bypass breaker | 0.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-12-09 18:43 | 2011-12-19 16:28 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 237.75 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-12-19 07:02 | 2011-12-19 14:15 | Scheduled | 1 | Both | Outage to repair System 3 cable fault | 7.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-12-19 07:12 | 2011-12-19 15:52 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 8.6667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-12-19 16:31 | 2011-12-20 10:37 | forced | 3 | MUL | Reactor Cooling fans fault | 18.1 | A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-04 18:41 | 2012-01-04 19:22 | forced | 1 | BLA | Reactor Cooling fans fault | 0.68333 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-05 18:41 | 2012-01-10 11:42 | forced | 1 | BLA | Reactor Cooling fans fault | 113.0167 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-06 06:06 | 2012-01-06 12:32 | Scheduled | 3 | MUL | Transformer Sound enclosure repairs | 6.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-06 12:32 | 2012-01-10 16:46 | forced | 3 | MUL | Control system fault. | 100.2333 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-10 21:57 | 2012-01-16 16:48 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 138.85 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-16 08:03 | 2012-01-16 14:37 | Scheduled | 1 | Both | Outage to repair System 2 cable fault | 6.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-16 08:03 | 2012-01-16 14:38 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 6.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-16 16:48 | 2012-01-23 12:04 | forced | 2 | MUL | Unable to return to service after cable fault. Too many faulty IGBTs | 163.2667 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-01-25 05:57 | 2012-02-03 16:59 | forced | 2 | MUL | Valve cooling control system fault | 227.0333 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-04 01:11 | 2012-02-13 16:32 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 231.35 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-13 07:05 | 2012-02-13 16:30 | Scheduled | 2 | Both | Outage to repair System 1 cable fault | 9.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-13 07:08 | 2012-02-13 16:29 | Scheduled | 3 | Both | Outage to repair System 1 cable fault | 9.35 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-16 11:01 | 2012-02-16 11:42 | forced | 2 | MUL | Trip cuased by control system maintenance | 0.68333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-02-16 11:48 | 2012-02-16 15:19 | forced | 2 | MUL | Trip cuased by control system maintenance | 3.5167 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-02-20 07:44 | 2012-02-21 13:04 | Scheduled | 2 | Both | Outage for IGBT replacement at Bungalora and & Transformer measurement at Mullumbimby | 29.3333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-28 20:58 | 2012-03-09 11:43 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 230.75 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-03-02 09:15 | 2012-03-02 09:44 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 0.48333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-03-03 07:11 | 2012-03-03 15:00 | Scheduled | 3 | Both | Outage to repair System 1 cable fault | 7.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-03-03 07:14 | 2012-03-03 15:00 | Scheduled | 2 | Both | Outage to repair System 1 cable fault | 7.7667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-03-29 11:14 | 2012-03-30 07:00 | forced | 3 | BLA | Trip caused by control system fault. | 19.7667 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-03-30 07:00 | 2012-04-05 14:28 | Scheduled | 3 | MUL | Outage for Transformer sound enclosure. | 151.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-04-02 13:41 | 2012-04-17 17:08 | forced | 2 | Both | Cable fault P2 (-ve) cable. | 363.45 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-04-17 07:10 | 2012-04-17 15:28 | Scheduled | 1 | Both | Outage to repair System 2 cable fault | 8.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-04-17 07:10 | 2012-04-20 13:51 | Scheduled | 1 | MUL | Outage for Transformer sound enclosure. | 78.6833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-04-17 07:18 | 2012-04-17 15:28 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 8.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-04-17 17:08 | 2012-05-11 14:12 | forced | 2 | Both | Return to service after cable fault delayed due to faulty IGBTs | 573.0667 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-05-22 10:34 | 2012-05-22 11:08 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 0.56667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-05-27 04:49 | 2012-06-07 14:31 | forced | 3 | MUL | Trip caused by reactor cooling fan motor fault | 273.7 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-06-06 06:14 | 2012-06-06 18:36 | Scheduled | 1 | MUL | Outage for Country Energy protection installation | 12.3667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-06-06 06:16 | 2012-06-06 18:38 | Scheduled | 2 | MUL | Outage for Country Energy protection installation | 12.3667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-06-08 09:57 | 2012-06-08 14:13 | forced | 2 | MUL | Trip caused by control system maintenance | 4.2667 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-06-19 10:04 | 2012-06-19 11:06 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 1.0333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-06-29 17:02 | 2012-07-11 18:33 | forced | 3 | Both | Cable fault P2 (-ve) cable. | 289.5167 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-11 07:02 | 2012-07-11 15:33 | Scheduled | 1 | Both | Outage to repair System 3 cable fault | 8.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-11 07:03 | 2012-07-11 15:35 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 8.5333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-11 15:33 | 2012-08-14 08:33 | forced | 1 | BLA | Trip caused by flashover in phase reactor air ducting. | 809 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-11 15:35 | 2012-07-14 15:25 | forced | 2 | MUL | Unable to return to service after cable fault repair due to control system fault. | 71.8333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-07-17 07:02 | 2012-07-18 19:50 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-17 07:18 | 2012-07-18 19:53 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-23 06:59 | 2012-07-24 16:13 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.2333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-23 07:01 | 2012-07-24 16:25 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-08-14 08:33 | 2013-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 3351.45 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-08-14 08:57 | 2012-08-23 16:59 | forced | 2 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 224.0333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-08-14 08:58 | 2012-08-31 13:44 | forced | 3 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 412.7667 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2012-08-31 13:44 | 2012-09-21 14:05 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 504.35 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-09-13 08:35 | 2012-09-13 09:20 | forced | 2 | BLA | Trip cuased by valve control fault related to PCPB | 0.75 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-09-20 07:29 | 2012-09-21 14:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault, return to service delayed by the need to inspect phase reactors for moisture. | 30.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-10-29 09:59 | 2012-10-30 12:19 | forced | 3 | BLA | Trip cuased by fault with LEM power supply. Inspectgion found not problems. | 26.3333 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-11-12 05:23 | 2012-11-23 15:35 | forced | 2 | MUL | Cable fault P2 (-ve) cable. | 274.2 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-11-18 17:50 | 2012-11-27 14:57 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 213.1167 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-12-11 08:28 | 2012-12-11 12:12 | forced | 2 | MUL | Fire protection system tripped the converter station | 3.7333 | A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-01-01 | 2014-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 8760 | A | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-01-03 05:57 | 2013-01-10 14:33 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 176.6 | A | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-01-09 07:50 | 2013-01-09 14:21 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 6.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-01-28 09:10 | 2013-02-01 15:59 | forced | 2 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 102.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-01-28 09:10 | 2013-01-31 16:45 | forced | 3 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 79.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-02-21 00:03 | 2013-02-21 02:44 | forced | 3 | MUL | Trip caused by control system fault. Auxiliary power disturbance caused both PCPs to fault. | 2.6833 | A | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-02-21 05:42 | 2013-03-12 13:06 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 463.4 | A | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-03-07 07:05 | 2013-03-07 13:57 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 6.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-03-07 13:57 | 2013-03-26 12:53 | forced | 2 | BLA | Return to service delayed by circuit breaker operating mechanism fault and IGBT failure | 454.9333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-03-26 15:37 | 2013-03-27 16:30 | forced | 2 | BLA | Trip caused by cooling water pump failure | 24.8833 | A | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-04-03 13:53 | 2013-04-03 14:58 | forced | 2 | BLA | Trip caused by cooling control system maintenance | 1.0833 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-04-03 14:42 | 2013-04-03 14:56 | forced | 3 | BLA | Trip caused by cooling control system maintenance | 0.23333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-04-06 20:06 | 2013-04-23 12:47 | forced | 3 | Both | Cable fault P2 (-ve) cable | 400.6833 | A | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-04-22 06:59 | 2013-04-22 16:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 9.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-04-22 16:00 | 2013-04-23 14:03 | forced | 2 | Both | Return to service after cable repair outage delayed by valve control fault. | 22.05 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-07-29 10:00 | 2013-07-29 13:38 | Scheduled | 2 | BLA | Outage to allow Essential Energy access at Terranora to position a crane. | 3.6333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-07-29 10:00 | 2013-07-29 15:05 | Scheduled | 3 | BLA | Outage to allow Essential Energy access at Terranora to position a crane. | 5.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-07-29 13:38 | 2013-08-06 18:00 | forced | 2 | BLA | Return to service delayed because of too many faulty IGBTs, after Outage to allow Essential Energy access at Terranora to position a crane. | 196.3667 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-08-06 06:06 | 2013-08-06 18:00 | Scheduled | 3 | BLA | Outage to de-energise the overhead buss to allow replacement of CT in the transformers of system 1 and system 2. | 11.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-08-06 18:00 | 2014-01-01 | forced | 2 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 3534 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2013-08-06 18:00 | 2014-01-01 | forced | 3 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 3534 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2014-01-01 | 2015-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 8760 | A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-01-01 | 2014-02-11 12:10 | forced | 2 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 996.1667 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-01-01 | 2014-01-21 17:07 | forced | 3 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 497.1167 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-02-11 13:07 | 2014-02-14 13:37 | forced | 2 | BLA | Trip caused by filter capacitor unbalanced protection. Return to service delayed by too many faulty IGBTs. | 72.5 | A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-02-14 14:34 | 2014-02-28 13:05 | forced | 2 | Both | Cable fault P2 (-ve) cable | 334.5167 | A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-02-27 06:26 | 2014-02-27 18:28 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 12.0333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-03-01 08:28 | 2014-03-21 17:33 | forced | 2 | Both | Cable fault P1 (+ve) cable | 489.0833 | A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-03-04 10:29 | 2014-03-04 12:26 | forced | 3 | BLA | LEM Power supply intermittent fault caused operation of the over current protection | 1.95 | A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-03-12 06:05 | 2014-03-12 14:58 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 8.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-03-29 13:14 | 2014-04-17 13:56 | forced | 3 | Both | Cable fault P1 (+ve) cable | 456.7 | A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-04-03 07:26 | 2014-04-03 08:22 | forced | 2 | MUL | Fire system maintenance contrctor caused trip while doing maintenance | 0.93333 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2014-04-10 16:57 | 2014-04-10 18:13 | forced | 2 | MUL | Fire system trip. No evidence of fire found. Suspect faulty fire system interface card. | 1.2667 | A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-04-11 08:06 | 2014-04-11 14:16 | Scheduled | 2 | Both | Outage to excavate System 2 cable fault | 6.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 SD = 68% |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-04-16 07:28 | 2014-04-16 17:33 | Scheduled | 2 | Both | Outage to excavate System 2 cable fault | 10.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | Average | SD | CAP | COLLAR | [9 empty] | Average | SD | CAP | COLLAR
[7 empty] | Year Totals | 16 | 24 | 14 | 20 | 25 | 20 | 6 | 7 | 20.6 | 3.8781 | 16.7219 | 24.4781 | Year Totals | 5 | 5 | 3 | 13 | 6 | 7 | 7 | 3 | 6.8 | 3.3705 | 3.4295 | 10.1705
[8 empty] | 533.3% | 800% | 466.7% | 666.7% | 833.3% | 666.7% | 200% | 233.3% | 686.7% |  | 557.4% | 815.9% |  | 166.7% | 166.7% | 100% | 433.3% | 200% | 233.3% | 233.3% | 100% | 226.7% |  | 114.3% | 339%
[8 empty] | Fault Outage | [12 empty] | Forced Outage

## Proper Op of Equip
Outage Start | Outage Finish |  | System | Converter | Description | Duration | Fault | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | [5 empty] | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014
2007-01-01 | 2007-02-08 18:00 | forced | 1 | BLA | Transformer differential trip, suspected loose core lamination. This portion of the outage is in 2007 | 930 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-01-07 07:00 | 2007-01-07 12:20 | forced | 2 | MUL | Computer failure at Mullumbimby | 5.3333 | P | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-03-17 08:28 | 2007-03-17 16:31 | scheduled | 1 | MUL | Repairs to galvanised steel troughing | 8.05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-03-17 08:59 | 2007-03-18 17:14 | forced | 2 | BLA | PCP mach2 computer failed during switching for planned repairs. | 32.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-03-17 08:59 | 2007-03-17 16:32 | scheduled | 3 | MUL | Repairs to galvanised steel troughing | 7.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-03-18 08:25 | 2007-03-18 17:14 | scheduled | 1 | BLA | Repairs to galvanised steel troughing | 8.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-03-18 08:25 | 2007-03-18 17:14 | scheduled | 3 | BLA | Repairs to galvanised steel troughing | 8.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 1 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 2 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-01 12:59 | 2007-04-01 14:00 | forced | 3 | BLA | Earth fault in AC filter yard B phase, due to a weed coming into contact with a reactor. | 1.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-09 13:29 | 2007-04-09 16:35 | forced | 1 | MUL | Loss of pole 1, caused by 11kV fault. | 3.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-04-16 09:30 | 2007-04-16 11:00 | scheduled | 1 | Both | Single system outage for site visits | 1.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-05-04 08:30 | 2007-05-04 11:30 | scheduled | 1 | both | Single system outage for site visits | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-05-25 08:56 | 2007-07-25 10:41 | forced | 3 | both | Cooling water leak in valve hall, phase reactor failure. | 1465.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-05-25 10:51 | 2007-05-25 14:36 | forced | 2 | both | Pole 2 tripped, no fault found, returned to service. | 3.75 | P | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-02 22:13 | 2007-06-07 16:11 | forced | 2 | both | More than 5 IGBTs failed in a stack. | 113.9667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-07 01:58 | 2007-06-27 14:03 | forced | 1 | both | DC cable fault | 492.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-16 12:14 | 2007-06-18 09:56 | forced | 2 | both | A Powerlink fault at Mudgeeraba caused the loss of 110kV supplies to Terranora. | 45.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-18 10:18 | 2007-06-18 10:29 | forced | 2 | BLA | Power supply problem in PCPB Mach 2 | 0.18333 | P | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-29 05:55 | 2007-06-29 05:58 | forced | 1 | MUL | Spurious trip, unknown cause | 0.05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-06-29 05:55 | 2007-06-29 05:58 | forced | 2 | MUL | Spurious trip, unknown cause | 0.05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-07-09 16:21 | 2007-07-10 11:50 | forced | 2 | BLA | Cooling equipment fault at Bungalora pole 2 | 19.4833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-07-18 08:32 | 2007-07-18 13:05 | scheduled | 1 | BLA | Inspection of phase reactors at Bungalora | 4.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-07-19 08:32 | 2007-07-19 13:12 | forced | 2 | MUL | Spurious trip, unknown cause | 4.6667 | P | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-08-01 15:30 | 2007-08-02 12:45 | forced | 3 | both | Pole 3 tripped, unknown cause. | 21.25 | P | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-08-19 01:51 | 2007-08-19 14:43 | forced | 3 | both | Abnormal frequency trip | 12.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-09-04 07:01 | 2007-09-04 20:02 | scheduled | 1 | both | Annual maintenance | 13.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-09-05 14:22 | 2007-09-06 00:19 | scheduled | 2 | both | Annual maintenance | 9.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-09-06 07:00 | 2007-09-06 18:45 | scheduled | 3 | both | Annual maintenance | 11.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-10-05 12:17 | 2007-11-15 14:30 | forced | 1 | BLA | Differential trip at Bungalora | 986.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-10-26 22:30 | 2007-10-26 23:21 | forced | 2 | Both | Fault on 132kV system | 0.85 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-10-26 22:30 | 2007-10-26 23:21 | forced | 3 | Both | Fault on 132kV system | 0.85 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-05 11:00 | 2007-11-05 13:10 | scheduled | 2 | Both | Systems 2 & 3 down for excavation on system 1 | 2.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-05 11:00 | 2007-11-05 13:10 | scheduled | 3 | Both | Systems 2 & 3 down for excavation on system 1 | 2.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-27 07:15 | 2007-11-27 17:00 | scheduled | 1 | both | Maintenance - Phase Reactors and IGBTs. Control system faults prevent return to service. | 9.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-27 17:00 | 2007-12-19 17:00 | forced | 1 | MUL | Computer failure on pole 1 at Mullumbimby. | 528 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-28 07:15 | 2007-11-28 17:00 | scheduled | 2 | both | Maintenance - Phase Reactors and IGBTs. Control system faults prevent return to service. | 9.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-28 17:00 | 2007-12-20 18:05 | forced | 2 | both | Computer failure on pole 2 at Mullumbimby. | 529.0833 | P | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-11-29 08:08 | 2007-11-29 15:14 | scheduled | 3 | both | Maintenance - Phase Reactors and IGBTs. | 7.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-12-30 13:10 | 2008-01-01 | forced | 2 | BLA | Auxiliary Power Failure caused control system problems | 34.8333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007-12-30 13:10 | 2008-01-01 | forced | 3 | BLA | Auxiliary Power Failure caused control system problems | 34.8333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-01-01 | 2008-01-02 20:09 | forced | 2 | BLA | Auxiliary Power Failure caused control system problems | 44.1497 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-01-01 | 2008-01-02 16:50 | forced | 3 | BLA | Auxiliary Power Failure caused control system problems | 40.8331 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-02 22:11 | 2008-02-03 10:48 | forced | 2 | MUL | Control System Faults | 12.6167 | P | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-13 08:30 | 2008-02-13 17:00 | scheduled | 1 | both | Shutdown to investigate various faults | 8.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-19 06:00 | 2008-02-21 00:27 | forced | 2 | both | Computer failure on pole 2 | 42.45 | P | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-20 07:00 | 2008-02-20 11:00 | scheduled | 1 | both | Fire System Maintenance | 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-20 11:05 | 2008-02-20 13:50 | scheduled | 3 | both | Fire System Maintenance | 2.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-27 08:00 | 2008-02-27 10:35 | scheduled | 1 | BLA | Installation of power flow monitoring gear | 2.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-27 10:12 | 2008-02-27 13:46 | scheduled | 2 | BLA | Installation of power flow monitoring gear | 3.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-02-27 11:00 | 2008-02-27 15:34 | scheduled | 3 | BLA | Installation of power flow monitoring gear | 4.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-03-08 19:31 | 2008-03-28 13:00 | forced | 2 | both | Cable fault | 473.4833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-03-13 16:07 | 2008-04-04 15:00 | forced | 1 | both | Cable fault | 526.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-03-18 09:35 | 2008-03-18 12:20 | scheduled | 3 | both | Outage to safely excavate sys1 cables for repair | 2.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-03-30 14:07 | 2008-03-30 18:00 | forced | 3 | both | Unknown fault caused converter to trip | 3.8833 | P | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-09 07:25 | 2008-04-09 15:35 | scheduled | 3 | both | Phase reactor inspections | 8.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-10 07:25 | 2008-04-10 14:56 | scheduled | 2 | both | Phase reactor inspections | 7.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-11 07:08 | 2008-04-24 17:32 | scheduled | 1 | both | Phase reactor inspections and Transformer swap out | 322.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-13 07:00 | 2008-04-13 17:00 | scheduled | 2 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-13 07:00 | 2008-04-13 17:00 | scheduled | 3 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-14 15:09 | 2008-05-01 16:00 | forced | 2 | both | System 2 Cable fault | 408.85 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-16 07:00 | 2008-04-16 17:00 | scheduled | 2 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-04-16 07:00 | 2008-04-16 17:00 | scheduled | 3 | both | De-energise 110kV O/H bus at Bungalora for safe access with a crane to system1 transformer. | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-12 08:00 | 2008-05-15 18:45 | scheduled | 1 | both | Phase reactor repairs | 82.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-15 17:00 | 2008-05-15 18:45 | scheduled | 2 | both | Communications Test | 1.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-15 17:00 | 2008-05-15 18:45 | scheduled | 3 | both | Communications Test | 1.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-16 08:00 | 2008-05-17 13:40 | scheduled | 3 | both | Phase reactor repairs | 29.6667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-18 08:00 | 2008-05-19 14:11 | scheduled | 2 | both | Phase reactor repairs | 30.1833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 1 | both | Comms cut over for trial operation | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 2 | both | Comms cut over for trial operation | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 09:00 | 2008-05-20 11:00 | scheduled | 3 | both | Comms cut over for trial operation | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 1 | both | Comms cut over after trial operation | 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 2 | both | Comms cut over after trial operation | 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-20 17:00 | 2008-05-20 17:30 | scheduled | 3 | both | Comms cut over after trial operation | 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 1 | both | Comms cut over for trial operation | 0.58333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 2 | both | Comms cut over for trial operation | 0.58333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 09:00 | 2008-05-22 09:35 | scheduled | 3 | both | Comms cut over for trial operation | 0.58333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 1 | both | Comms cut over after trial operation | 0.33333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 2 | both | Comms cut over after trial operation | 0.33333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 16:00 | 2008-05-22 16:20 | scheduled | 3 | both | Comms cut over after trial operation | 0.33333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-22 20:12 | 2008-05-23 16:05 | forced | 3 | both | Reactor cooling fan fault. | 19.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 1 | both | Final comms cut over. | 0.41667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 2 | both | Final comms cut over. | 0.41667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-05-26 12:00 | 2008-05-26 12:25 | scheduled | 3 | both | Final comms cut over. | 0.41667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-09 03:21 | 2008-06-10 17:06 | forced | 3 | BLA | PCPA hard disk fault | 37.75 | P | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 1 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 2 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-24 21:28 | 2008-06-24 22:22 | forced | 3 | BLA | Communications Fault - Telstra optic fibre fault at Kempsey | 0.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 1 | MUL | Country Energy outage to connect CB 7H3 | 13.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 2 | MUL | Country Energy outage to connect CB 7H3 | 13.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 05:30 | 2008-06-25 18:55 | scheduled | 3 | MUL | Country Energy outage to connect CB 7H3 | 13.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 1 | both | Comms fault from Dandenong to DL | 1.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 2 | both | Comms fault from Dandenong to DL | 1.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 18:55 | 2008-06-25 20:40 | forced | 3 | both | Comms fault from Dandenong to DL | 1.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-25 20:40 | 2008-06-27 18:00 | forced | 1 | BLA | Faulty IGBTs | 45.3333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-27 22:47 | 2008-07-09 15:43 | forced | 2 | both | Cable Fault | 280.9333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 03:30 | 2008-06-29 08:00 | forced | 1 | MUL | TransGrid Tripping Scheme operation | 4.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 03:30 | 2008-06-29 08:00 | forced | 3 | MUL | TransGrid Tripping Scheme operation | 4.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 08:00 | 2008-06-29 10:27 | forced | 1 | MUL | Mach 2 faults after TransGrid Tripping Scheme operation | 2.4497 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-06-29 08:00 | 2008-06-29 10:27 | forced | 3 | MUL | Mach 2 faults after TransGrid Tripping Scheme operation | 2.4497 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-11 07:00 | 2008-07-11 18:43 | forced | 3 | BLA | Reactor Fan Trip | 11.7167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-12 08:25 | 2008-07-12 16:15 | scheduled | 1 | BLA | Valve Cooling Water Leak Inspection | 7.8333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-14 11:03 | 2008-08-04 14:54 | forced | 2 | both | Cable fault | 507.85 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-20 01:02 | 2008-07-20 05:29 | scheduled | 1 | both | Country Energy outage | 4.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-20 01:02 | 2008-07-20 05:29 | scheduled | 3 | both | Country Energy outage | 4.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-25 09:03 | 2008-07-25 11:20 | scheduled | 1 | both | Outage to excavate Cables for repair to system 2 cable fault | 2.2833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-25 09:03 | 2008-07-25 11:20 | scheduled | 3 | both | Outage to excavate Cables for repair to system 2 cable fault | 2.2833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-25 11:20 | 2008-08-01 16:15 | forced | 3 | 0 | After outage to excavate cables for repair to system 2 cable fault, L2 phase of system 3 circuit breaker would not close. | 172.9167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-07-31 09:46 | 2008-07-31 14:35 | scheduled | 1 | both | Outage to excavate Cables for repair to system 2 cable fault | 4.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 1 | both | Abnormal frequency trip | 5.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 2 | both | Abnormal frequency trip | 5.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-08-18 19:58 | 2008-08-19 01:51 | forced | 3 | both | Abnormal frequency trip | 5.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-16 07:00 | 2008-09-18 17:26 | scheduled | 2 | both | Annual Maintenance | 58.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-18 07:30 | 2008-09-19 17:00 | scheduled | 3 | both | Annual Maintenance | 33.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-19 17:00 | 2008-09-21 07:00 | forced | 3 | both | Mullumbimby sytem 3 control system fault | 38 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-20 07:00 | 2008-09-21 07:00 | scheduled | 1 | both | Annual Maintenance | 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 1 | both | Country energy requested outage for maintenance at Terranora | 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 2 | both | Country energy requested outage for maintenance at Terranora | 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 07:00 | 2008-09-21 16:00 | scheduled | 3 | both | Country energy requested outage for maintenance at Terranora | 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 16:00 | 2008-09-25 15:55 | forced | 1 | both | Bungalora pre-insertion resistor overload trip - earths left on in the barn | 95.9167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-21 16:00 | 2008-10-07 16:05 | forced | 3 | both | Mullumbimby sytem 3 control system fault | 384.0833 | P | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-09-25 14:22 | 2008-09-25 20:17 | forced | 2 | both | Mullumbimby reactor cooling fan trip | 5.9167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-10-01 18:17 | 2008-11-14 19:11 | forced | 2 | both | Cable Fault P1 cable. | 1056.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-07 13:59 | 2008-11-14 18:51 | forced | 1 | both | Cable Fault P1 cable. | 172.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 1 | BLA | Auxiliary power failure | 1.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 2 | BLA | Auxiliary power failure | 1.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-20 18:46 | 2008-11-20 20:20 | forced | 3 | BLA | Auxiliary power failure | 1.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-24 07:02 | 2008-11-24 15:02 | scheduled | 1 | both | Phase Reactor Inspections and cable clamp modifications | 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-25 06:54 | 2008-11-25 15:36 | scheduled | 2 | both | Phase Reactor Inspections and cable clamp modifications | 8.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-26 07:05 | 2008-11-26 14:45 | scheduled | 3 | both | Phase Reactor Inspections and cable clamp modifications | 7.6667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-11-27 07:10 | 2008-11-27 13:14 | scheduled | 1 | both | Phase Reactor Inspections and cable clamp modifications | 6.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-08 01:18 | 2008-12-16 13:12 | forced | 2 | both | Cable Fault P1 cable. | 203.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-15 08:10 | 2008-12-15 10:25 | scheduled | 1 | both | Outage to locate Pole 1 cable fault | 2.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-15 08:17 | 2008-12-15 10:28 | scheduled | 3 | both | Outage to locate Pole 1 cable fault | 2.1833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-19 23:06 | 2008-12-31 09:42 | forced | 2 | both | Cable Fault P1 cable. | 274.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-30 07:41 | 2008-12-30 09:24 | scheduled | 3 | both | Outage to locate Pole 1 cable fault | 1.7167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-30 07:47 | 2008-12-30 09:22 | scheduled | 1 | both | Outage to locate Pole 1 cable fault | 1.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008-12-31 11:13 | 2009-01-01 | forced | 2 | both | Cable Fault P1 cable. | 12.7831 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-01-01 | 2009-01-20 09:22 | forced | 2 | both | Cable Fault P1 cable. | 465.3667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-01-11 13:00 | 2009-01-19 12:06 | forced | 1 | both | Cable Fault P1 cable. | 191.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-01-16 07:00 | 2009-01-16 14:01 | scheduled | 3 | both | Outage to repair Pole 1 and Pole 2 cable faults | 7.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-09 21:00 | 2009-02-18 10:53 | forced | 2 | both | Cable Fault P1 cable. | 205.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-10 07:26 | 2009-02-10 12:01 | scheduled | 1 | both | Outage for Country Energy maintenance - 110kV bus at Terranora substation | 4.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-10 07:36 | 2009-02-10 12:06 | scheduled | 3 | both | Outage for Country Energy maintenance - 110kV bus at Terranora substation | 4.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-16 09:05 | 2009-02-16 13:05 | scheduled | 1 | both | Outage to repair Pole 2 cable fault | 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-16 09:07 | 2009-02-16 13:06 | scheduled | 3 | both | Outage to repair Pole 2 cable fault | 3.9833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-16 13:16 | 2009-02-16 15:00 | scheduled | 3 | both | Outage to repair Pole 2 cable fault | 1.7333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-02-16 13:17 | 2009-02-16 14:59 | scheduled | 1 | both | Outage to repair Pole 2 cable fault | 1.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-10 07:31 | 2009-03-10 15:23 | scheduled | 3 | both | Outage for six month maintenance | 7.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-11 07:31 | 2009-03-11 13:54 | scheduled | 2 | both | Outage for six month maintenance | 6.3833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-12 07:03 | 2009-03-13 08:02 | scheduled | 1 | both | Outage for six month maintenance | 24.9833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-17 09:40 | 2009-03-30 13:51 | forced | 3 | both | Cable Fault P1 & P2 cable. | 316.1833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-26 07:04 | 2009-03-26 15:51 | scheculed | 1 | both | Outage to repair Pole 3 cable fault | 8.7833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-26 07:37 | 2009-03-26 15:53 | scheculed | 2 | both | Outage to repair Pole 3 cable fault | 8.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-27 07:03 | 2009-03-27 13:24 | scheculed | 1 | both | Outage to repair Pole 3 cable fault | 6.35 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-03-27 07:08 | 2009-03-27 13:26 | scheculed | 2 | both | Outage to repair Pole 3 cable fault | 6.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-15 10:01 | 2009-04-15 11:28 | scheculed | 1 | both | Outage for access valve enclosure lock change | 1.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-15 11:48 | 2009-04-15 13:57 | scheculed | 2 | both | Outage for access valve enclosure lock change | 2.15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-15 14:08 | 2009-04-15 15:23 | scheculed | 3 | both | Outage for access valve enclosure lock change | 1.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-04-19 03:40 | 2009-04-19 03:58 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-20 20:46 | 2009-05-20 23:31 | forced | 1 | BLA | Auxilary power outage caused a reactor cooling fan changeover. Dampers did not open in time causing a trip. | 2.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-21 05:10 | 2009-05-21 06:52 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Return delayed to investigate a CB Relay fault. | 1.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-21 05:10 | 2009-05-21 05:24 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.23333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-21 05:10 | 2009-05-21 05:24 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.23333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 04:32 | 2009-05-22 04:38 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 04:32 | 2009-05-22 04:39 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.11667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 04:32 | 2009-05-22 04:40 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.13333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 07:59 | 2009-05-22 08:59 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 07:59 | 2009-05-22 09:03 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 1.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 07:59 | 2009-05-22 09:03 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 1.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 15:18 | 2009-05-22 16:34 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 1.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 15:18 | 2009-05-22 15:48 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-22 15:18 | 2009-05-22 15:48 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-23 17:22 | 2009-05-24 13:22 | forced | 3 | MUL | AC Filter capacitor protection trip. | 20 | P | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:02 | 2009-05-23 19:15 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.21667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:02 | 2009-05-23 19:14 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:34 | 2009-05-23 19:40 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-23 19:34 | 2009-05-23 19:41 | forced | 2 | MUL | Inter tripping scheme tripped all three poles | 0.11667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-05-26 18:02 | 2009-06-06 13:08 | forced | 2 | Both | Cable fault P1 cable, Return to service delayed by too any Faulty IGBTs in B phase | 259.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-02 11:54 | 2009-06-02 12:10 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 0.26667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-02 11:54 | 2009-06-02 12:10 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 0.26667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-02 12:15 | 2009-06-02 14:28 | forced | 1 | MUL | Inter tripping scheme tripped all three poles | 2.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-02 12:15 | 2009-06-02 14:28 | forced | 3 | MUL | Inter tripping scheme tripped all three poles | 2.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-03 09:16 | 2009-06-03 14:49 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 5.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-03 09:16 | 2009-06-03 14:51 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-06-30 06:50 | 2009-07-18 10:29 | forced | 2 | Both | Cable fault P1 cable, Return to service delayed by too any Faulty IGBTs in B phase | 435.65 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-14 09:04 | 2009-07-14 14:19 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 5.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-14 09:13 | 2009-07-14 14:21 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 5.1333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-15 08:36 | 2009-07-15 10:24 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 1.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-15 08:38 | 2009-07-15 10:21 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. Repair abandoned. Insufficient instruction for joint kit. | 1.7167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-16 09:02 | 2009-07-16 17:29 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 8.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-16 09:12 | 2009-07-16 17:32 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 8.3333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-16 17:29 | 2009-07-21 17:38 | forced | 1 | Both | Unable to return to service. Too many faulty igbts. | 120.15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-20 18:28 | 2009-07-21 09:54 | forced | 2 | Both | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 15.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-20 18:28 | 2009-07-21 09:56 | forced | 3 | Both | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 15.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-27 06:36 | 2009-07-28 17:04 | Scheduled | 1 | Both | Shutdown for annual maintenance | 34.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-29 06:49 | 2009-07-30 17:26 | Scheduled | 2 | Both | Shutdown for annual maintenance | 34.6167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-07-31 06:32 | 2009-08-01 13:02 | Scheduled | 3 | Both | Shutdown for annual maintenance | 30.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-14 10:52 | 2009-08-14 11:38 | forced | 1 | Both | Trip caused by flow protection. Standby pump did not start when pumps changed during while converter was running. | 0.76667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-25 13:27 | 2009-08-29 14:54 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 97.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-27 08:07 | 2009-08-27 16:49 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 8.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-27 08:14 | 2009-08-27 16:47 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 8.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-27 17:11 | 2009-08-27 21:20 | forced | 1 | MUL | Trip caused by Coutry Energy protection operation. Failed protection CT in Mullumbimby system 3 transformer | 4.15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-08-27 17:11 | 2009-09-04 17:04 | forced | 3 | MUL | Trip caused by Coutry Energy protection operation. Failed protection CT in Mullumbimby system 3 transformer | 191.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-09-04 07:22 | 2009-09-04 16:49 | Scheduled | 1 | MUL | Outage for HV access to repair failed protection CT in Mullumbimby system 3 transformer | 9.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-09-04 07:23 | 2009-09-04 16:50 | Scheduled | 2 | MUL | Outage for HV access to repair failed protection CT in Mullumbimby system 3 transformer | 9.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-09-29 07:04 | 2009-09-29 17:14 | Scheduled | 1 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-09-29 07:07 | 2009-09-29 17:39 | Scheduled | 2 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.5333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-09-29 07:09 | 2009-09-29 17:18 | Scheduled | 3 | MUL | Country Energy required 132kV bus de-energised for inspections of CB in their substation | 10.15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-03 13:23 | 2009-11-03 14:01 | forced | 3 | BLA | Trip by Flow Protection - Active CCP accidentally reset during maintenance | 0.63333 | P | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-04 02:42 | 2009-11-13 10:18 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 223.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-10 17:50 | 2009-11-10 18:44 | forced | 3 | Bla | Fault with 24V DC power supply | 0.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-11 10:11 | 2009-11-11 16:08 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-11 10:16 | 2009-11-11 16:06 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 5.8333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-19 01:51 | 2009-11-28 09:57 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 224.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-20 02:17 | 2009-11-20 02:55 | forced | 2 | MUL | Abnormal Frequency Trip. Country Energy System Problems. | 0.63333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-20 02:17 | 2009-11-20 02:56 | forced | 3 | MUL | Abnormal Frequency Trip. Country Energy System Problems. | 0.65 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-26 09:06 | 2009-11-26 14:59 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 5.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-26 09:15 | 2009-11-26 14:57 | Scheduled | 2 | Both | Outage to enable access to repair the system 2 cable. | 5.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-27 10:28 | 2009-11-27 11:03 | forced | 3 | MUL | Damper Resistor overload trip event on one PCP. Converter tripped while trying to clear the event. | 0.58333 | P | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-11-28 10:30 | 2009-12-17 14:49 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 460.3167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-11 00:52 | 2009-12-11 02:16 | forced | 1 | BLA | Operation of Powerlink intertrip scheme. | 1.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-11 00:52 | 2009-12-11 02:17 | forced | 3 | BLA | Operation of Powerlink intertrip scheme. | 1.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-12 08:13 | 2009-12-12 08:58 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-12 08:13 | 2009-12-12 08:59 | forced | 3 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.76667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-15 07:02 | 2009-12-15 17:07 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 10.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-15 07:20 | 2009-12-15 17:04 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 9.7333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009-12-17 22:14 | 2010-01-01 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 337.7664 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-01 | 2010-01-14 09:14 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 321.2333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-08 18:49 | 2010-01-08 19:11 | forced | 1 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.36667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-08 18:49 | 2010-01-08 19:13 | forced | 3 | MUL | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-09 13:04 | 2010-03-31 14:01 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 1944.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-12 07:16 | 2010-01-12 16:16 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-13 13:37 | 2010-01-21 09:56 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 188.3167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-15 07:23 | 2010-01-15 08:05 | forced | 2 | 0 | Trip during control system maintenance | 0.7 | P | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-19 07:03 | 2010-01-19 14:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 7.15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-20 21:01 | 2010-01-20 21:34 | forced | 2 | 0 | Inter tripping scheme tripped all three poles. Faulty Communications line between Mullumbimby and Lismore. | 0.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-01-27 05:30 | 2010-03-31 13:54 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 1520.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-03-27 06:04 | 2010-03-27 17:35 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. | 11.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-03-28 06:04 | 2010-03-28 15:41 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 9.6167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-03-31 23:18 | 2010-04-17 09:26 | forced | 1 | Both | Cable fault P1 (+ve) cable. After cable repair, fault with DC voltage measuring delayed return to service. | 394.1333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-04-09 17:48 | 2010-04-20 13:44 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 259.9333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-04-14 07:04 | 2010-04-15 15:51 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. Too many faulty igbts when energised from Mullumbimby. Igbts repaired the next day during system 2 cable fault repair. | 32.7833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-04-17 09:26 | 2010-04-28 13:37 | forced | 1 | Both | Fault with DC voltage measuring delayed return to service after repair P1 (+ve) cable, | 268.1833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-04-30 19:18 | 2010-06-13 10:34 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 1047.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-05-05 11:00 | 2010-05-05 13:14 | forced | 1 | BLA | Trip during fault finding of PCPB DC voltage measuring | 2.2333 | P | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-05-24 07:14 | 2010-05-28 14:24 | Scheduled | 3 | Both | Outage to replace transformer CTs | 103.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-05-25 07:03 | 2010-05-25 19:33 | Scheduled | 1 | Both | Outage to allow overhead crane access for replacing system 3 transformer CTs | 12.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-05-31 10:05 | 2010-05-31 17:23 | Scheduled | 1 | Both | Outage to excavate the system 2 cable fault. | 7.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-05-31 10:10 | 2010-05-31 17:26 | Scheduled | 3 | Both | Outage to excavate the system 2 cable fault under the river. | 7.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-05-31 17:26 | 2010-06-08 13:18 | forced | 3 | Both | Outage to excavate the system 2 cable fault. Return to service delayed due to VCU Faults. | 187.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-06-01 13:43 | 2010-06-01 14:33 | Scheduled | 1 | Both | Outage to cut system 2 cable during repair of fault under the river. | 0.83333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-06-03 06:55 | 2010-06-03 17:48 | Scheduled | 1 | Both | Outage to joint system 2 cable during repair of fault under the river. | 10.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-06-04 07:00 | 2010-06-04 16:15 | Scheduled | 1 | Both | Outage to joint system 2 cable during repair of fault under the river. | 9.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-06-10 02:02 | 2010-06-10 16:02 | forced | 3 | BLA | Trip due to low water level. Pump leaking. | 14 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-06 01:03 | 2010-07-06 16:18 | forced | 2 | MUL | UPS failure caused trip of converter | 15.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-15 22:07 | 2010-07-26 08:19 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 250.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-22 06:03 | 2010-07-22 17:22 | Scheduled | 1 | BLA | CE Requested Outage - Terranora Bus zone breakers | 11.3167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-22 06:06 | 2010-07-22 17:23 | Scheduled | 3 | BLA | CE Requested Outage - Terranora Bus zone breakers | 11.2833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-22 17:22 | 2010-07-26 07:00 | forced | 1 | MUL | Return to serivce delayed - Too many faulty IGBTs | 85.6333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-22 17:23 | 2010-07-26 07:00 | forced | 3 | BLA | Return to serivce delayed - Too many faulty IGBTs | 85.6167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-26 07:00 | 2010-07-28 14:39 | Scheduled | 3 | Both | Annual Maintenance | 55.65 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-26 07:00 | 2010-07-29 15:18 | Scheduled | 1 | Both | Annual Maintenance | 80.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-28 15:02 | 2010-07-29 14:44 | forced | 3 | BLA | Phase reactor partial discharge repair | 23.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-30 08:41 | 2010-07-31 16:49 | Scheduled | 2 | Both | Annual Maintenance | 32.1333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-31 08:38 | 2010-07-31 10:00 | Scheduled | 1 | MUL | CE Requested Outage - Lismore Tripping Scheme Work | 1.3667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-31 08:46 | 2010-07-31 10:01 | Scheduled | 3 | MUL | CE Requested Outage - Lismore Tripping Scheme Work | 1.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-07-31 16:49 | 2010-08-06 13:25 | forced | 2 | MUL | Return to serivce delayed - faulty control system components | 140.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 1 | BLA | Auxiliary power failure | 0.88333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 2 | BLA | Auxiliary power failure | 0.88333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-09 07:44 | 2010-08-09 08:37 | forced | 3 | BLA | Auxiliary power failure | 0.88333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-09 08:37 | 2010-08-11 13:40 | forced | 1 | BLA | Restoration after auxiliary power failure | 53.05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-09 08:37 | 2010-08-09 15:58 | forced | 2 | BLA | Restoration after auxiliary power failure | 7.35 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-09 08:37 | 2010-08-09 09:43 | forced | 3 | BLA | Restoration after auxiliary power failure | 1.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-10 12:04 | 2010-08-10 18:39 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 6.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-10 12:06 | 2010-08-10 18:35 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 6.4833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-11 06:04 | 2010-08-11 13:42 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 7.6333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-11 06:05 | 2010-08-11 13:41 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 7.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-14 06:08 | 2010-08-14 12:44 | Scheduled | 1 | BLA | County Energy Requested outage for work at Terranora | 6.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-14 06:10 | 2010-08-14 12:45 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 6.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-14 06:11 | 2010-08-14 12:46 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 6.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-15 06:03 | 2010-08-15 11:50 | Scheduled | 3 | BLA | County Energy Requested outage for work at Terranora | 5.7833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-15 06:05 | 2010-08-15 11:48 | Scheduled | 2 | BLA | County Energy Requested outage for work at Terranora | 5.7167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-15 06:06 | 2010-08-15 11:46 | Scheduled | 1 | BLA | County Energy Requested outage for work at Terranora | 5.6667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-22 04:00 | 2010-08-22 15:04 | forced | 2 | BLA | Reactor cooling fans tripped converter | 11.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-08-25 09:46 | 2010-08-25 11:27 | forced | 2 | BLA | Trip caused by control system maintenance | 1.6833 | P | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-02 12:50 | 2010-09-02 13:28 | Scheduled | 3 | BLA | Outage requested by Country Energy for protection testing | 0.63333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-02 12:51 | 2010-09-02 13:28 | Scheduled | 2 | BLA | Outage requested by Country Energy for protection testing | 0.61667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-02 12:51 | 2010-09-02 13:27 | Scheduled | 1 | BLA | Outage requested by Country Energy for protection testing | 0.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-18 02:43 | 2010-10-01 12:08 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 321.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-19 02:02 | 2010-10-01 12:42 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 298.6667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-27 08:01 | 2010-09-27 14:16 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 6.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-09-27 08:02 | 2010-09-27 16:02 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable. | 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-10-06 16:23 | 2010-10-22 12:28 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 380.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-10-14 08:11 | 2010-10-14 15:01 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable. | 6.8333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-10-14 08:11 | 2010-10-14 15:03 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 6.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-10-17 10:06 | 2010-10-17 14:02 | forced | 2 | MUL | Trip caused by fire protection system fault. | 3.9333 | P | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-10-29 09:38 | 2010-10-29 11:08 | Scheduled | 1 | Both | Outage to repair GST damage. | 1.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-08 06:06 | 2010-11-08 13:07 | Scheduled | 1 | MUL | Outage for CE Comms tower installation | 7.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-08 06:11 | 2010-11-08 13:08 | Scheduled | 2 | MUL | Outage for CE Comms tower installation | 6.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-08 06:34 | 2010-11-08 13:09 | Scheduled | 3 | MUL | Outage for CE Comms tower installation | 6.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-09 06:04 | 2010-11-09 13:19 | Scheduled | 1 | MUL | Outage for CE Comms tower installation | 7.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-09 06:09 | 2010-11-09 13:20 | Scheduled | 2 | MUL | Outage for CE Comms tower installation | 7.1833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-09 06:15 | 2010-11-09 13:21 | Scheduled | 3 | MUL | Outage for CE Comms tower installation | 7.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-14 01:21 | 2010-11-20 08:14 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 150.8786 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-18 07:07 | 2010-11-18 14:42 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable. | 7.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-18 07:10 | 2010-11-18 14:42 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable. | 7.5333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-23 07:02 | 2010-11-24 15:30 | Scheduled | 1 | Both | IGBT/FO Test & Replacement | 32.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-24 15:30 | 2010-11-26 13:45 | forced | 1 | Both | IGBT Faults | 46.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-25 21:15 | 2010-12-03 13:45 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 184.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-30 07:05 | 2010-11-30 14:31 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable. | 7.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-11-30 07:07 | 2010-11-30 14:33 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable. | 7.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-06 06:46 | 2010-12-07 17:02 | Scheduled | 1 | Both | IGBT/FO Test & Investigation with ABB Mikael | 34.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-08 07:08 | 2010-12-09 14:48 | Scheduled | 2 | Both | IGBT/FO Test & Investigation with ABB Mikael | 31.6667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-09 14:51 | 2010-12-10 17:06 | Scheduled | 3 | Both | IGBT/FO Test & Investigation with ABB Mikael | 26.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-12 14:39 | 2010-12-22 16:07 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 241.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-15 19:06 | 2010-12-23 10:29 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 183.3833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-17 07:01 | 2010-12-17 17:29 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 10.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-21 07:02 | 2010-12-21 17:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 10.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-25 01:01 | 2010-12-25 01:41 | forced | 1 | BLA | Auxiliary power failure - Rector cooling fans trip. | 0.66667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010-12-27 13:03 | 2011-01-01 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 106.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-01 | 2011-01-07 09:07 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 153.1167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-05 07:01 | 2011-01-05 14:15 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 7.2333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-05 07:04 | 2011-01-05 14:17 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 7.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-07 06:36 | 2011-01-17 09:35 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 242.9833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-10 15:21 | 2011-01-18 11:39 | forced | 2 | Both | Cable fault P2 (-ve) cable. | 188.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-13 07:03 | 2011-01-13 14:28 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 7.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-14 07:01 | 2011-01-14 13:32 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable fault | 6.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-01-28 11:51 | 2011-02-10 13:59 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 314.1333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-09 07:11 | 2011-02-09 17:43 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 10.5333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-09 07:13 | 2011-02-09 18:10 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 10.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-09 17:43 | 2011-02-14 17:24 | forced | 3 | Both | Outage due to BLA System 3, B Phase CB Pole leaking insulating gas. | 119.6833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-14 07:03 | 2011-02-14 16:10 | Scheduled | 1 | Both | Outage to enable access to the replacement of BLA System 3, B Phase CB Pole | 9.1167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-14 07:15 | 2011-02-14 17:41 | Scheduled | 2 | Both | Outage to enable access to the replacement of BLA System 3, B Phase CB Pole | 10.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-14 17:41 | 2011-02-18 11:31 | forced | 2 | MUL | Unable to return to service after planned outage. Too many faulty IGBTs | 89.8333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-15 07:13 | 2011-02-15 07:42 | forced | 1 | MUL | Outage due to control system fault. | 0.48333 | P | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-02-21 17:15 | 2011-02-21 18:31 | forced | 1 | BLA | Phase Reactor Cooling Fan L3 Trip | 1.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-03-13 12:24 | 2011-03-28 13:23 | forced | 1 | MUL | Trip due to flash over in PLC filter yard. Return to service delayed due to to many faulty IGBTs | 360.9833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-03-13 12:24 | 2011-03-13 19:31 | forced | 2 | MUL | Trip due to flash over in PLC filter yard. | 7.1167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-03-13 12:24 | 2011-03-13 19:34 | forced | 3 | MUL | Trip due to flash over in PLC filter yard. | 7.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-01 06:18 | 2011-04-01 13:48 | Scheduled | 1 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-01 06:19 | 2011-04-01 13:49 | Scheduled | 2 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-01 06:21 | 2011-04-01 13:49 | Scheduled | 3 | BLA | Outage Requested by Country Energy for Work at Terranora | 7.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-01 13:49 | 2011-04-08 12:55 | forced | 2 | Both | Faulty IGBTs prevented return to service after CE outage. | 167.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-18 16:05 | 2011-04-23 13:09 | forced | 1 | Both | Cable Fault P1 (+ve) cable. | 117.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-21 07:01 | 2011-04-21 15:26 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 8.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-04-21 07:02 | 2011-04-21 15:28 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 8.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-05-08 16:23 | 2011-06-11 16:25 | forced | 1 | Both | Outage caused by DC voltage imbalance. Return to service delayed by too many faulty IGBT optic fibres. | 816.0333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-05-14 11:26 | 2011-05-30 11:26 | forced | 3 | Both | Cable Fault P1 (+ve) cable. Return to service after cable fault repair delayed by too many faulty IGBTs | 384 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-05-25 07:04 | 2011-05-25 18:32 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault. | 11.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-05-25 18:32 | 2011-07-22 10:15 | forced | 2 | Both | Unable to return to service after planned outage. Too many faulty IGBTs | 1383.7167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-06-10 02:56 | 2011-07-15 10:18 | forced | 3 | Both | Cable Fault P1 (+ve) cable. | 847.3667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-14 06:11 | 2011-07-14 20:25 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 14.2333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-15 10:30 | 2011-07-15 11:09 | forced | 3 | BLA | Cooling system trip - high water temperature - proportional valve failed to operate. | 0.65 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-18 23:25 | 2011-07-30 09:38 | forced | 1 | Both | Cable Fault P2 (-ve) cable. | 274.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-22 10:50 | 2011-08-05 15:12 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 340.3667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-29 07:02 | 2011-07-29 18:48 | Scheduled | 2 | Both | Outage to enable access to repair the system 1 cable fault | 11.7667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-07-30 09:38 | 2011-08-05 15:11 | forced | 1 | BLA | Unable to return to service after cable fault. Too many faulty IGBTs | 149.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-05 07:07 | 2011-08-05 15:12 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 8.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-17 07:05 | 2011-08-17 14:07 | Scheduled | 1 | Both | Outage for CE Comms tower work | 7.0333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-17 07:17 | 2011-08-17 14:20 | Scheduled | 2 | Both | Outage for CE Comms tower work | 7.05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-17 07:24 | 2011-08-17 14:18 | Scheduled | 3 | Both | Outage for CE Comms tower work | 6.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-22 16:08 | 2011-08-23 09:50 | forced | 1 | BLA | Rector Cooling fans faulty contactor | 17.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-22 16:08 | 2011-08-23 00:06 | forced | 3 | BLA | Rector Cooling fans faulty contactor | 7.9667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-23 11:48 | 2011-08-23 12:14 | forced | 2 | MUL | Trip cause during replacement of UPS fault indicating relay | 0.43333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-25 07:07 | 2011-09-03 13:05 | forced | 3 | Both | Cable Fault P2 (-ve) cable. | 221.9667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-30 09:39 | 2011-08-30 10:17 | forced | 2 | BLA | Valve control fault during maintenance work | 0.63333 | P | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-31 11:52 | 2011-08-31 18:07 | Scheduled | 1 | Both | Outage for Coucil excavation of water pipe at Bungalora | 6.25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-08-31 11:54 | 2011-08-31 18:07 | Scheduled | 2 | Both | Outage for Coucil excavation of water pipe at Bungalora | 6.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-02 07:03 | 2011-09-02 17:49 | Scheduled | 1 | Both | Outage to enable access to repair the system 3 cable fault | 10.7667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-02 07:04 | 2011-09-02 17:53 | Scheduled | 2 | Both | Outage to enable access to repair the system 3 cable fault | 10.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-05 09:08 | 2011-09-05 18:52 | forced | 3 | MUL | Rector Cooling fans faulty contactor | 9.7333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-12 09:30 | 2011-09-26 16:14 | forced | 1 | Both | Cable Fault P1 (+ve) cable. | 342.7333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-24 08:33 | 2011-09-30 17:57 | forced | 2 | Both | Cable Fault P1 (+ve) cable. | 153.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-26 07:07 | 2011-09-26 15:59 | Scheduled | 3 | Both | Outage to enable access to repair the system 1 cable fault | 8.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-30 07:05 | 2011-09-30 17:10 | Scheduled | 1 | Both | Outage to enable access to repair the system 2 cable fault | 10.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-09-30 07:12 | 2011-09-30 17:13 | Scheduled | 3 | Both | Outage to enable access to repair the system 2 cable fault | 10.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-11-03 07:18 | 2011-11-03 13:22 | Scheduled | 2 | BLA | Outage to add SF6 Gas to bypass breaker | 6.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-11-08 07:43 | 2011-11-09 16:07 | Scheduled | 1 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 32.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-11-08 08:01 | 2011-11-09 16:11 | Scheduled | 3 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 32.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-11-08 08:03 | 2011-11-09 17:37 | Scheduled | 2 | Both | Essential Energy requested outage for TNA-BLA line protection work. | 33.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-11-30 07:24 | 2011-11-30 16:12 | Scheduled | 3 | Both | Outage to install sound prrofing on transformer | 8.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-12-06 09:55 | 2011-12-06 10:37 | Scheduled | 2 | Both | Outage to add SF6 Gas to bypass breaker | 0.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-12-09 18:43 | 2011-12-19 16:28 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 237.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-12-19 07:02 | 2011-12-19 14:15 | Scheduled | 1 | Both | Outage to repair System 3 cable fault | 7.2167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-12-19 07:12 | 2011-12-19 15:52 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 8.6667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011-12-19 16:31 | 2011-12-20 10:37 | forced | 3 | MUL | Reactor Cooling fans fault | 18.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-04 18:41 | 2012-01-04 19:22 | forced | 1 | BLA | Reactor Cooling fans fault | 0.68333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-05 18:41 | 2012-01-10 11:42 | forced | 1 | BLA | Reactor Cooling fans fault | 113.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-06 06:06 | 2012-01-06 12:32 | Scheduled | 3 | MUL | Transformer Sound enclosure repairs | 6.4333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-06 12:32 | 2012-01-10 16:46 | forced | 3 | MUL | Control system fault. | 100.2333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-10 21:57 | 2012-01-16 16:48 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 138.85 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-16 08:03 | 2012-01-16 14:37 | Scheduled | 1 | Both | Outage to repair System 2 cable fault | 6.5667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-16 08:03 | 2012-01-16 14:38 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 6.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-16 16:48 | 2012-01-23 12:04 | forced | 2 | MUL | Unable to return to service after cable fault. Too many faulty IGBTs | 163.2667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-01-25 05:57 | 2012-02-03 16:59 | forced | 2 | MUL | Valve cooling control system fault | 227.0333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-04 01:11 | 2012-02-13 16:32 | forced | 1 | Both | Cable fault P2 (-ve) cable. | 231.35 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-13 07:05 | 2012-02-13 16:30 | Scheduled | 2 | Both | Outage to repair System 1 cable fault | 9.4167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-13 07:08 | 2012-02-13 16:29 | Scheduled | 3 | Both | Outage to repair System 1 cable fault | 9.35 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-16 11:01 | 2012-02-16 11:42 | forced | 2 | MUL | Trip cuased by control system maintenance | 0.68333 | P | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-16 11:48 | 2012-02-16 15:19 | forced | 2 | MUL | Trip cuased by control system maintenance | 3.5167 | P | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-20 07:44 | 2012-02-21 13:04 | Scheduled | 2 | Both | Outage for IGBT replacement at Bungalora and & Transformer measurement at Mullumbimby | 29.3333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-02-28 20:58 | 2012-03-09 11:43 | forced | 1 | Both | Cable fault P1 (+ve) cable. | 230.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-03-02 09:15 | 2012-03-02 09:44 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 0.48333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-03-03 07:11 | 2012-03-03 15:00 | Scheduled | 3 | Both | Outage to repair System 1 cable fault | 7.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-03-03 07:14 | 2012-03-03 15:00 | Scheduled | 2 | Both | Outage to repair System 1 cable fault | 7.7667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-03-29 11:14 | 2012-03-30 07:00 | forced | 3 | BLA | Trip caused by control system fault. | 19.7667 | P | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-03-30 07:00 | 2012-04-05 14:28 | Scheduled | 3 | MUL | Outage for Transformer sound enclosure. | 151.4667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-04-02 13:41 | 2012-04-17 17:08 | forced | 2 | Both | Cable fault P2 (-ve) cable. | 363.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-04-17 07:10 | 2012-04-17 15:28 | Scheduled | 1 | Both | Outage to repair System 2 cable fault | 8.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-04-17 07:10 | 2012-04-20 13:51 | Scheduled | 1 | MUL | Outage for Transformer sound enclosure. | 78.6833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-04-17 07:18 | 2012-04-17 15:28 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 8.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-04-17 17:08 | 2012-05-11 14:12 | forced | 2 | Both | Return to service after cable fault delayed due to faulty IGBTs | 573.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-05-22 10:34 | 2012-05-22 11:08 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 0.56667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-05-27 04:49 | 2012-06-07 14:31 | forced | 3 | MUL | Trip caused by reactor cooling fan motor fault | 273.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-06-06 06:14 | 2012-06-06 18:36 | Scheduled | 1 | MUL | Outage for Country Energy protection installation | 12.3667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-06-06 06:16 | 2012-06-06 18:38 | Scheduled | 2 | MUL | Outage for Country Energy protection installation | 12.3667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-06-08 09:57 | 2012-06-08 14:13 | forced | 2 | MUL | Trip caused by control system maintenance | 4.2667 | P | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-06-19 10:04 | 2012-06-19 11:06 | Scheduled | 2 | BLA | Outage to add insulating gas to circuit breaker | 1.0333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-06-29 17:02 | 2012-07-11 18:33 | forced | 3 | Both | Cable fault P2 (-ve) cable. | 289.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-11 07:02 | 2012-07-11 15:33 | Scheduled | 1 | Both | Outage to repair System 3 cable fault | 8.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-11 07:03 | 2012-07-11 15:35 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 8.5333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-11 15:33 | 2012-08-14 08:33 | forced | 1 | BLA | Trip caused by flashover in phase reactor air ducting. | 809 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-11 15:35 | 2012-07-14 15:25 | forced | 2 | MUL | Unable to return to service after cable fault repair due to control system fault. | 71.8333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-17 07:02 | 2012-07-18 19:50 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-17 07:18 | 2012-07-18 19:53 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 36.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-23 06:59 | 2012-07-24 16:13 | Scheduled | 2 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.2333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-07-23 07:01 | 2012-07-24 16:25 | Scheduled | 3 | MUL | Outage for Essential Energy protection work at Mullumbimby | 33.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-08-14 08:33 | 2013-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 3351.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-08-14 08:57 | 2012-08-23 16:59 | forced | 2 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 224.0333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-08-14 08:58 | 2012-08-31 13:44 | forced | 3 | MUL | Outage to allow de-energisation for fire fighting. Prolonged by comms outage. | 412.7667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-08-31 13:44 | 2012-09-21 14:05 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 504.35 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-09-13 08:35 | 2012-09-13 09:20 | forced | 2 | BLA | Trip cuased by valve control fault related to PCPB | 0.75 | P | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-09-20 07:29 | 2012-09-21 14:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault, return to service delayed by the need to inspect phase reactors for moisture. | 30.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-10-29 09:59 | 2012-10-30 12:19 | forced | 3 | BLA | Trip cuased by fault with LEM power supply. Inspectgion found not problems. | 26.3333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-11-12 05:23 | 2012-11-23 15:35 | forced | 2 | MUL | Cable fault P2 (-ve) cable. | 274.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-11-18 17:50 | 2012-11-27 14:57 | forced | 3 | MUL | Cable fault P2 (-ve) cable. | 213.1167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012-12-11 08:28 | 2012-12-11 12:12 | forced | 2 | MUL | Fire protection system tripped the converter station | 3.7333 | P | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-01-01 | 2014-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 8760 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-01-03 05:57 | 2013-01-10 14:33 | forced | 2 | Both | Cable fault P1 (+ve) cable. | 176.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-01-09 07:50 | 2013-01-09 14:21 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 6.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-01-28 09:10 | 2013-02-01 15:59 | forced | 2 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 102.8167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-01-28 09:10 | 2013-01-31 16:45 | forced | 3 | BLA | Trip caused by Flow protection. Auxiliary power lost. | 79.5833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-02-21 00:03 | 2013-02-21 02:44 | forced | 3 | MUL | Trip caused by control system fault. Auxiliary power disturbance caused both PCPs to fault. | 2.6833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-02-21 05:42 | 2013-03-12 13:06 | forced | 3 | Both | Cable fault P1 (+ve) cable. | 463.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-03-07 07:05 | 2013-03-07 13:57 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 6.8667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-03-07 13:57 | 2013-03-26 12:53 | forced | 2 | BLA | Return to service delayed by circuit breaker operating mechanism fault and IGBT failure | 454.9333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-03-26 15:37 | 2013-03-27 16:30 | forced | 2 | BLA | Trip caused by cooling water pump failure | 24.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-04-03 13:53 | 2013-04-03 14:58 | forced | 2 | BLA | Trip caused by cooling control system maintenance | 1.0833 | P | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-04-03 14:42 | 2013-04-03 14:56 | forced | 3 | BLA | Trip caused by cooling control system maintenance | 0.23333 | P | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-04-06 20:06 | 2013-04-23 12:47 | forced | 3 | Both | Cable fault P2 (-ve) cable | 400.6833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-04-22 06:59 | 2013-04-22 16:00 | Scheduled | 2 | Both | Outage to repair System 3 cable fault | 9.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-04-22 16:00 | 2013-04-23 14:03 | forced | 2 | Both | Return to service after cable repair outage delayed by valve control fault. | 22.05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-07-29 10:00 | 2013-07-29 13:38 | Scheduled | 2 | BLA | Outage to allow Essential Energy access at Terranora to position a crane. | 3.6333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-07-29 10:00 | 2013-07-29 15:05 | Scheduled | 3 | BLA | Outage to allow Essential Energy access at Terranora to position a crane. | 5.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-07-29 13:38 | 2013-08-06 18:00 | forced | 2 | BLA | Return to service delayed because of too many faulty IGBTs, after Outage to allow Essential Energy access at Terranora to position a crane. | 196.3667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-08-06 06:06 | 2013-08-06 18:00 | Scheduled | 3 | BLA | Outage to de-energise the overhead buss to allow replacement of CT in the transformers of system 1 and system 2. | 11.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-08-06 18:00 | 2014-01-01 | forced | 2 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 3534 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-08-06 18:00 | 2014-01-01 | forced | 3 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 3534 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-01-01 | 2015-01-01 | forced | 1 | MUL | Trip caused by fire in converter building. | 8760 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-01-01 | 2014-02-11 12:10 | forced | 2 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 996.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-01-01 | 2014-01-21 17:07 | forced | 3 | BLA | Return to service delayed by damage to the reactor cooling fibreglass | 497.1167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-02-11 13:07 | 2014-02-14 13:37 | forced | 2 | BLA | Trip caused by filter capacitor unbalanced protection. Return to service delayed by too many faulty IGBTs. | 72.5 | P | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-02-14 14:34 | 2014-02-28 13:05 | forced | 2 | Both | Cable fault P2 (-ve) cable | 334.5167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-02-27 06:26 | 2014-02-27 18:28 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 12.0333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-03-01 08:28 | 2014-03-21 17:33 | forced | 2 | Both | Cable fault P1 (+ve) cable | 489.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-03-04 10:29 | 2014-03-04 12:26 | forced | 3 | BLA | LEM Power supply intermittent fault caused operation of the over current protection | 1.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-03-12 06:05 | 2014-03-12 14:58 | Scheduled | 3 | Both | Outage to repair System 2 cable fault | 8.8833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-03-29 13:14 | 2014-04-17 13:56 | forced | 3 | Both | Cable fault P1 (+ve) cable | 456.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-04-03 07:26 | 2014-04-03 08:22 | forced | 2 | MUL | Fire system trip. No evidence of fire found. Suspect faulty fire system interface card. | 0.93333 | P | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-04-10 16:57 | 2014-04-10 18:13 | forced | 2 | MUL | Fire system trip. No evidence of fire found. Suspect faulty fire system interface card. | 1.2667 | P | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-04-11 08:06 | 2014-04-11 14:16 | Scheduled | 2 | Both | Outage to excavate System 2 cable fault | 6.1667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-04-16 07:28 | 2014-04-16 17:33 | Scheduled | 2 | Both | Outage to excavate System 2 cable fault | 10.0833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | Average | SD | CAP | COLLAR | [9 empty] | Average | SD | CAP | COLLAR
[7 empty] | Year Totals | 6 | 5 | 3 | 4 | 2 | 6 | 2 | 3 | 4 | 1.4142 | 2.5858 | 5.4142 | Year Totals | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | Proper Operation of Equipment | [12 empty] | Forced Outage