East Australian Pipeline Limited REPORT OPTIMISED DESIGN AND COST ESTIMATE EAPL PIPELINE NETWORK 1 DOCUMENT NO: 042-R01 Prepared by Venton & Associates Pty. Ltd. 98 Cliff Avenue Northbridge NSW 2063 TEL: +61 2 9958 2600 FAX: +61 2 9967 0401 June 20, 1999

TABLE OF CONTENTS

SECTION	PAGE

1.	summary	1

1.1	general	1

1.2	System design	1

1.3	Capital cost Estimate	1

2.	study basis	3

2.1	Pipeline Network	3

2.2	Load Basis	4

2.2.1	Pipeline Load Growth Projection	4

2.2.2	Load Profiles	4

2.2.3	Small Loads	4

2.2.4	Gas Flow – Moomba to Wilton	5

2.2.5	Net Gas Flow at Culcairn	5

2.3	Gas composition	6

3.	pipeline hydraulic design	8

3.1	General	8

3.2	Modelling assumptions	8

3.3	Pipeline operating pressure	9

3.4	Steady state calculations	10

3.5	Dalton – Canberra PIPELINE	12

3.6	unsteady state calculations	12

3.6.1	General	12

3.6.2	Calculation Results	14

3.6.3	Pipeline Compression	14

3.7	young compression	17

3.8	pipeline configuration	17

4.	Capital Cost Estimates	18

4.1	Estimate BAsis	18

4.2	Assumptions	18

4.3	Estimate Exclusions	19

4.4	Project approvals / land acquisition costs	19

4.5	Linepipe costs	19

4.6	Estimated Cost	19

4.7	Pipeline development cost	20

4.8	Cost reduction for  DN 300 pipeline to culcairn	21

4.9	Potential saving - Dalton – Canberra pipeline	21

4.10	Impact of australian dollar variability	21

4.11	Operating Costs – Fuel gas consumption	22

ATTACHMENTS

Attachment 1	HYDRAULIC MODEL OUTPUT

Attachment 2	PIPELINE CONFIGURATION

Attachment 3	ESTIMATE DETAIL SUMMARY

Attachment 4	SYSTEM LOAD PROFILES

# summary

## general

This report presents the results of a study undertaken by Venton and Associates Pty. Ltd. (VAPL). For East Australian Pipeline Limited (EAPL) to determine the current cost of the existing pipeline network developed today using current technology and standards.

The proposed design is considered to be an “Optimised” design, and the capital cost estimates presented are considered to represent the present day cost of the Optimised design.  The estimate accuracy is  20%.

The study considers pipelines developed to match a current projection of the load growth in the pipeline.

The study assumes that the NSW load growth is essentially within the Sydney – Newcastle - Wollongong regions, and it considers interstate gas market and supply opportunities.

EAPL provided estimates of the pipeline loads between 2000 and 2014 and details of the load profiles applying to the major loads along the pipeline.  EAPL also provided details of the existing pipeline routes, the route elevation, location of offtake points, and certain information on construction features along the pipeline routes for use in capital cost estimating.

VAPL developed designs for the pipeline network based on a network having the capacity to deliver the 2014 load using incremental compression.  Hydraulic modelling used the SIROGAS unsteady state pipeline model for network performance modelling for the initial study.  A simple steady state model was also used to establish the probable pipeline diameters and compression requirements.

## System design

The optimised pipeline network is based on a transmission pipeline between Moomba and Young operating a Class 900 pressure of 15.3 MPa.  The balance of the pipeline network operates at a Class 600 pressure of 10.2 MPa, maximum.  The selected pipeline diameters and their associated operating pressures are summarised in Table 1-1.

Table 1-1 Pipeline Network Diameters and Pressures

| Pipeline | Diameter and Pressure |
| --- | --- |
| Moomba to Young | DN 600, Class 900 |
| Young to Wilton | DN 600, Class 600 |
| Dalton to Canberra | DN 300, Class 600 |
| Northern Laterals | DN 150, Class 600 (all lines) |
| Young – Culcairn | DN 350, Class 600 |
| Burnt Creek to Griffith | DN 150, Class 600 |

The pipeline requires an initial compressor station at Moomba to raise the current Moomba supply pressure from approximately 6.0 MPa to the required inlet pressure of 15.3 MPa.

Incremental compression is required progressively along the pipeline as the load grows with time.  One intermediate compressor station is required in year 2000.  Because the load falls between after 2000, the intermediate compressor station is not required again until about 2008.  In year 2014, the pipeline has 5 intermediate compressor stations.

## Capital cost Estimate

The estimated capital costs of the pipeline networks are summarised in Table 1-2.

Table 1-2 Estimated Capital Cost of Optimised Network (Year 2000 Basis)

| Pipeline | Estimated Cost ($A’000s) |
| --- | --- |
| Moomba to Young | 698,665 |
| Young to Wilton | 194,403 |
| Young to Culcairn | 64,677 |
| Dalton to Canberra | 18,974 |
| Young to Lithgow | 51,051 |
| Junee to Griffith | 30,446 |
| Estimated Cost | 1,058,216 |

The estimated cost to develop the pipeline to year 2014 and a net present cost for the full development of the pipeline is presented in Table 1-3.

Table 1-3 Net Present Cost of Pipeline Developed to 2014

|  | Estimated Cost ($A’000s) |
| --- | --- |
| Estimated Cost of Incremental Compression | 167,100 |
| Net Present Cost of Incremental Compression Escalation = 1.5% Discount Rate = 8.5% | 96,725 |
| Initial Cost | 1,058,116 |
| Net Present Project Cost | 1,154,841 |

Some further optimisation of the system is possible.  For example,

- With more analysis it might be possible to deliver the performance required in year 2000 without an intermediate compressor station, thus delaying the cost of this facility for 8 years.

- In year 2014, additional compression is required to maintain the flow to Culcairn during minimum pressure periods at Young.  The conceptual design provides this by installing a single 2.5 MW unit in the Young Laterals station, maintaining a 10 MPa supply to the Culcairn lateral and freeing the Young - Wilton compressor from this demand.  Locating this unit at Bomen or Uranquinty may provide a better solution from and operating standpoint, but the installation date is well in the future, and the impact of this cost on net present cost is minimal.

- Reducing the diameter of the Dalton – Canberra pipeline from DN 300 to DN 250, and by closely matching the diameter of the Northern and Junee-Griffith laterals to the nominal flows.

- A mix of pipeline diameters in the Northern Laterals pipeline.

However the study considers that while these refinements will result in small capital cost savings, they may increase the operating complexity of the pipeline network, and result in increased operating costs, or future incremental capital.  Consequently the refinements are discounted by the study.

It should be noted that the capital cost estimates are based on currency exchange rates that were considered reasonable at the time of the study, and on imported line pipe costs current at the time of the estimate.  Both the Australian dollar and the international line pipe market are volatile, and any comparative use of the estimate should ensure that adjustments are made to ensure that the estimate basis is common.

# study basis

## Pipeline Network

The pipeline network modelled in this study is illustrated in the following map.  The network consists of a trunk pipeline from Moomba to Wilton, with lateral pipelines serving Orange-Bathurst-Lithgow, Canberra, Junee-Griffith and an interconnection pipeline with Victoria between Young and Culcairn, illustrated in the following figure.

## Load Basis

### Pipeline Load Growth Projection

This analysis is based on an assessment of the energy that will be transported by the pipeline network between 2000 and 2014. The assessment was developed by EAPL, having regard to the growth of the New South Wales market published in the Fourth Gas Supply and Demand Study published by the Australian Gas Association in 1997, projected on a base of known loads in the pipeline network in 1998.  The assessment also included an analysis of development opportunities and the impact of competing pipelines.

Base and High load cases were developed by EAPL and provided as an input to this study in late 1998.

The Base case load case was revised in March 1999 as a result of a revised assessment of the market following the decision by the Eastern Gas Pipeline project to complete a pipeline from Victoria to Sydney in mid 2000.   At this time EAPL considered the High case unrealistic and discarded it from further consideration.

The nominated loads are the Maximum Demand Quantity (MDQ) from all shippers.  The MDQ’s for the major demands are modified by the application of a load profile including a load factor.

Shortly before this report was finalised EAPL advised that the forecast loads for the Canberra, Bomen, Griffith and Northern Laterals loads between 2000 and 2005 had been reduced from those used in this study.  Since the reduction was small, and there was no change to the overall demand forecast in this period the potential impact on completed hydraulic designs was small, it was decided to ignore the revision.

### Load Profiles

The design philosophy used by EAPL in ensuring the existing system has adequate capacity to deliver the winter peak demand is adopted for this study.  The philosophy is:

- The historical demand profile for a seven (7) day peak period is applied to the average daily load for the flow case.

- The pipeline capacity is modelled for three continuous weeks at this load and load profile to establish stable performance.

- To be an acceptable design the pressures in the pipeline network must exceed the minimum design or contract pressure at all points throughout the network.

The hydraulic design is based on the projected load and load profiles for major centres (Sydney, Canberra, Junee-Griffith and the Bathurst/Lithgow area.

The profiles adopted are presented in Attachment 4.

The peak day flow was determined from historic data supplied by EAPL, and calculated from the average daily load for the year under consideration.  The first day in the weekly cycle is Saturday.

Each of the minor loads is assumed to be constant at the average value calculated from the average daily load.  This simplifying assumption is reasonable because each of the loads is small relative to the total load in the transmission pipeline network.

### Small Loads

Pipeline capacity modelling assumes that the current load at minor demand points is maintained constant throughout the life of the study period.  This is a slightly conservative assumption, forcing the entire load growth to the major loads – however since the loads are small relative to the major demands, and the growth in the smaller, rural centres is typically less than 1%, the conservatism introduced by this assumption is small.

### Gas Flow – Moomba to Wilton

Figure 2-1 illustrates the assessed gas flow (expressed in energy units) between Moomba and Young required to satisfy the New South Wales (NSW) and Victorian projected market between 1999 and 2014.

Figure 2-1   Gas Flow from Moomba

### Net Gas Flow at Culcairn

Figure 2-2 shows the projected capacity required at Culcairn for gas transported between NSW and Victoria through the recently constructed Interconnect Pipeline.

The net flow at Culcairn is the sum of the contracted supply of Victorian sourced gas to NSW, and of Moomba sourced gas into Victoria.  A negative value indicates that the net flow direction is from NSW to Victoria.

The net flow into NSW is modest, as a result of the modest growth in the NSW market, coupled with an assumed capacity of the existing Moomba gas supply to satisfy a significant proportion of the growth.  Toward the end of the study period, the net flow direction reverses.

Figure 2-2 Gas Flows through Culcairn to and from NSW

## Gas composition

The study assumes a gas composition for supplies from both Moomba and Victoria that is similar to the composition currently supplied from Moomba.  Table 2-4 presents the composition used to calculate gas properties in the pipeline hydraulic design.

Table 2-4 Assumed Gas Composition

| Gas Component | Concentration (Mole %) |
| --- | --- |
| C1 | 83.67 |
| C2 | 9.62 |
| C3 | 0.46 |
| IC4 | 0.05 |
| NC4 | 0.03 |
| IC5 | 0.07 |
| NC5 | 0.03 |
| C6+ | 0.32 |
| N2 | 2.86 |
| CO2 | 2.99 |

The gross heating value (GHV) for gas with this composition is 39.03 MJ/m3.  However to maintain consistency with calculations undertaken by EAPL, the market loads were converted to volumetric flow using a GHV of 38.5 MJ/m3.  This assumption is slightly conservative, resulting in slightly higher volumetric flows than would be calculated if the GHV calculated from the gas composition was used.  (Note the assumed GHV correctly describes the average heating value of gas from Victoria).

This assumption has no significant impact on the outcome of hydraulic design and pipeline capacity determination.

# pipeline hydraulic design

## General

Pipeline hydraulic design is the process to determine the size, operating pressure and configuration of intermediate compressor facilities along the pipeline route.

The pipeline hydraulic design used:

- A steady state – linear pipeline model for to make an initial selection of the pipe diameters and operating pressures.

The steady state model determines the pipeline diameter that will continuously deliver the nominated MDQ flows between the assumed inlet and outlet pressures.  The steady state model may over or under-predict the diameter required to deliver the unsteady state flows, depending on the duration of the peak load, and the linepack that is available for drawdown in the period that the outflow is higher than the pipeline inflow.

Steady state modelling is typically used for pipeline diameter selection unless there is specific information available on the load profile.

- An unsteady state model to assess the capacity of the pipeline system to deliver the flow required for a peak load week, using load profiles established from historic data from the existing system for each major load.  The unsteady state model used was the FLOWTRAN/SIROGAS model supplied by William J Turner Pty Ltd.  This product has been used by EAPL for pipeline system modelling for some years. (Note that revised calculations in March 1999 were checked using the Stoner and Gregg Engineering software).

Because unsteady state computer programs accurately model a real pipeline, permitting the supply and delivery flows and pressures to vary with time, they are appropriate for design of pipeline systems where there is sound knowledge of the profile of the major loads.  This is the case for the EAPL system.

## Modelling assumptions

Each hydraulic model requires a number of assumptions that reflect the design basis and the design assumptions.  The key assumptions are addressed in this section:

| Item | Assumption |
| --- | --- |
| Ground Temperature | 21 C |
| Maximum Pipeline Inlet Temperature | 60 C |
| Pipeline Roughness | 0.007 mm (Burnished steel typically 0.0076 mm – 0.0127 mm) (Epoxy – Acrylic Lining typically 0.0051 – 0.0076 mm |
| Supply Pressure (Moomba) | 6.0 MPa |
| Supply Pressure (Wodonga) | 10.2 MPa |
| Delivery Pressure (Wilton) | 3.8 MPa, (Minimum) |
| Delivery Pressure (Canberra) | 1.2 MPa (Minimum) |
| Delivery Pressure (Griffith) | 1.75 MPa (Minimum) |
| Delivery Pressure (Lithgow) | 1.75 MPa (Minimum) |
| Pipe Steel Grades | API 5L Grade X70 and X80 (large diameter pipes) |
| Pipeline Maximum Operating Pressures | 10.2 and 15.3 MPa (Class 600 and Class 900) |

The design roughness is typical of steel pipe that has been burnished smooth by regular pigging to remove latent scale, rust or other surface contamination, or is a conservative value for pipe that is internally lined with an epoxy coating.

Typical roughness values for pipe steel following construction and hydrostatic testing are about 0.025 mm.  Thus the assumed value is appropriate either for lined pipe, or for a pipeline that has undergone a regime of wire brush pigging during its operation to progressively improve its surface quality.

The pressure supplied by Santos at Moomba is understood to normally be higher than the assumed pressure.  This conservative assumption increases the required compressor power and fuel at Moomba but does not change the equipment selection.

The design assumes that the maximum compressor ratio used on the pipelines is 1.5, and the maximum station power is 9.0 MW (except in the case of the initial compressor station at Moomba).

A 9 MW station can be supplied as:

- A single Solar Mars unit (9 MW @ 35C)

- Two Solar Taurus T70 (11.6 MW @ 35C)

- Three Solar Taurus T60 units (12.8 MW @ 35C)

Multiple smaller unit installations provide additional power, and offer increased reliability at reduced cost, because the loss of pipeline capacity resulting from loss of one unit may be offset by the reserve power available at the downstream compressor station.

## Pipeline operating pressure

Maximum allowable operating pressures (MAOP) of Australian gas pipelines have progressively increased from 7 MPa used for the design of the Moomba to Wilton Pipeline, to 10.2 MPa currently used for most new pipelines, and 15.3 MPa, used for some long transmission pipelines.

Gas pipelines operate more efficiently as their operating pressure increases.  This is because friction loss increases with the square of the flowing velocity, and the actual volume of gas reduces in proportion to the flowing pressure.  Consequently a modest increase in flowing pressure makes a significant impact on the pressure losses in the pipeline.

Thus, increased operating pressure can enable the pipeline diameter to be reduced, lowering its cost.

Factors that limit the benefit of high-pressure pipelines are:

- The increased cost of compression to deliver the gas at the higher pressure and,

- The cost, and energy loss (inefficiency) that results from having to reduce the pressure from transmission level to the pressure required by the end user.

An inspection of the EAPL pipeline network suggests that it is practical to construct the pipeline between Moomba and Young as a Class 900 pipeline, with a MAOP of 15.3 MPa.  Downstream of Young there is no benefit in operating the pipeline at this pressure because the relatively short distance in a properly sized pipeline would result in the delivery pressure at Wilton being significantly higher than that required.

Consequently the hydraulic design has adopted:

- A MAOP of 15.3 MPa for the Moomba to Young section of the pipeline.

- A MAOP of 10.2 MPa for all other pipelines.

These pressures are equal to the class limit for flanges that satisfy the requirements of ANSI Class 900 and Class 600 respectively.  They currently require the designer to purchase flanges satisfying alternative compliance codes to permit this pressure at the design temperature.   The Australian Industry is currently considering an anomaly between various pressure vessel codes, and it is probable that if these pipelines were constructed today, the industry would approve their construction without derating at the pipeline design temperature.

## Steady state calculations

Steady State calculations were made using the flows through the pipelines in year 2014 to establish the nominal diameter and compression configuration for each line, to minimise the effort required to achieve an optimum.  The steady state program used includes an option to allocate compressor stations of known power at optimum locations.

The results of these calculations are summarised in Table 3-5 and Table 3-6.

Table 3-5 shows that the DN 650 pipeline and the DN 600 pipelines are both candidates for the Base load.  Because the initial cost of the DN 650 pipeline will be higher than the DN 600, and the number of compressor stations are similar, it is probable that a net present cost analysis would result in the DN 600 alternative offering a lower cost basis.

Table 3-5  Pipeline Configurations - Steady State - 2014 Flow

| Pipeline | Pressure In/Out (MPa) | Nominal Diameter (mm) | No. Compressor Stations | Operating Power (kW) |
| --- | --- | --- | --- | --- |
| Moomba – Young (Flow, 2014) | 15.3 / 10.2 | DN 650 | 2 | 16,000 |
|  | 15.3 / 10.2 | DN 600 | 5 | 25,850 |
|  | 15.3 / 10.2 | DN 500 | 10 | 90,710 |

Because the load growth does not occur until 2009, an economic optimum solution might be to install a DN 500 or DN550 pipeline and be prepared to loop the pipeline to deliver the flows required between 2010 and 2014.  At 2009, for example, a DN500 pipeline would require 5 compressor stations and 24,200 kW.

The DN 500 option was discarded by a preliminary inspection of the probable incremental looping costs, while the DN550 option was discarded because it is an uncommon diameter and it will still require significant compression or looping to deliver the 2014 load.

Consequently the study considers that the smallest reasonable diameter between Moomba and Young is DN 600.

Table 3-6 shows that a DN 550 pipeline is required between Young and Wilton to deliver the load without intermediate compression.

Because DN 550 is an unusual diameter, because the delivery pressure is close to the nominal minimum pressure at Wilton, and because supply security is important to the Sydney market, the study has selected a DN 600 pipe as the optimum diameter.

It is probable that under unsteady state conditions, the pipe diameter could be reduced by one size (50 mm nominal), to make a greater use of the linepack in this section, but considering the size of the Sydney load, diameter constraint near the delivery point of an unsteady state load is undesirable.

Table 3-6 Pipeline Configurations - Steady State - 2014 Flow

| Pipeline | Nominal Diameter (mm) | Pressure In (MPa) | Pressure Out (MPa) | No. Compressor Stations |
| --- | --- | --- | --- | --- |
| Young – Wilton (Flow, 2014) | DN 650 | 10.2 | 8.5 | - |
|  | DN 600 | 10.2 | 7.6 | - |
|  | DN 550 | 10.2 | 5.5 | - |
|  | DN 500 | 10.2 | - | - |

Table 3-7 shows the steady state performance of pipelines transporting gas flows along the pipeline between Young and Culcairn, assuming the inlet pressure at Culcairn is 10.2 MPa.  This is not a correct assumption for the pipeline in its current configuration because compression is planned to be supplied at the NSW- Victoria border, and at Uranquinty.

In the absence of detailed knowledge of the gas pipeline network in Victoria, this study has assumed that the compressor station locations currently adopted are appropriate to the optimised design.

Table 3-7 Pipeline Configuration - Maximum Net Flow

| Pipeline | Nominal Diameter (mm) | Pressure In (MPa) | Pressure Out (MPa) | No. Compressor Stations |
| --- | --- | --- | --- | --- |
| Young to Culcairn (Flow in 2000) (25 TJ/d Delivered) | DN 350 | 10.2 | 10.0 | - |
|  | DN 300 | 10.2 | 9.9 | - |
| Young – Culcairn (Flow in 2014) (93TJ/d Delivered) | DN 400 | 10.2 | 8.9 | - |
|  | DN 350 | 10.2 | 6.9 |  |
|  | DN 300 | 10.2 | >7 | 1 |
| Culcairn – Young (Flow in 2005) (18 TJ/d Delivered) | DN 350 | 10.2 | 10.1 | - |
|  | DN 300 | 10.2 | 9.9 | - |

The steady state analysis suggests that the pipeline diameter should be either DN 300 or DN 350.

The study adopted a DN 350 pipeline for the Young to Culcairn pipeline because:

- The pipeline provides a link between the Moomba gas reserves and the Melbourne market, and between the Victorian reserves and the Sydney market.  The capacity of a DN 300 pipeline is too small to be reasonably considered as a means of linking the markets.

A reasonable minimum pipeline diameter to link the two largest markets and supplies on the east coast is probably DN 400 or DN 450.  However these could not be justified using the load projections.

- The projected flows through the pipeline between 2001 and 2012 are such that a DN 250 or a DN 200 pipeline could service them.  A pipeline of this diameter between these markets would require tariffs that could not stimulate any growth in capacity (and probably should not be built).

- The incremental cost between a DN 300 and DN 350 pipeline is not great.

- A DN 350 pipeline could probably be justified through a combination of being a minimum strategic diameter to provide useful gas flows between the states (for an event such as the 1998 supply interruption at Esso’s Longford facility).  It has sufficient capacity to offer competitive tariffs if its capacity was utilised.  This would challenge the owning company’s marketing department to aggressively market the capacity and have a reasonable chance of securing sufficient to utilise a reasonable proportion of the capacity earlier than the current projection.

The selected diameter does not offer an optimised design for the identified Interconnect loads.  However it is considered to offer the minimum reasonable diameter that would be constructed on the basis of the market opportunities for interstate gas trading.

## Dalton – Canberra PIPELINE

The Canberra load has large daily swings and the capacity is sensitive to the Young delivery pressure.

The current diameter is DN 250, and satisfying the Canberra capacity through this pipeline often determines the operating pressure in the Young to Wilton pipeline, leading to inefficient pipeline operation.  While this problem will reduce with the optimised, higher pressure design, it may under some conditions impose a constraint on the Young – Wilton pipeline operation.

Because the pipeline is only 58 km long and the incremental cost of a larger diameter is small, a DN 300 diameter pipeline is selected as providing an optimum design considering both the capital cost and operating flexibility requirements of this pipeline.

## unsteady state calculations

### General

The unsteady state performance of the pipeline network was predicted to determine the pipeline development required to achieve capacity by progressive installation of compressor stations and compressor plant.

The initial installation is required to satisfy the year 2000 load.  This design is satisfactory for the projected loads until 2009, when equipment is installed that has capacity to satisfy the 2012 load.  In 2012 the system capacity is further enhanced to provide the capacity to deliver the 2014 load.

The analysis assumes that the pipeline is developed using compressor stations installed at the locations in Table 3-8.

Table 3-8  Compressor Station Locations

| Pipeline | Compressor Site | Kilometre Post | Separation (km) |
| --- | --- | --- | --- |
| Moomba to Wilton | Moomba | 0 |  |
|  | Binerah Downs | 170 | 170 |
|  | Questa Park | 380 | 210 |
|  | Bulla Park | 579 | 199 |
|  | Pine Ridge | 777 | 198 |
|  | Marsden | 942 | 165 |
|  | Young | 1034 | 92 |
| Northern Laterals (Bathurst-Lithgow) | Young | 0.1 | 0.1 |
| Culcairn - Young | Uranquinty | 60 | 124 |
|  | Young (suction) | 218 | 158 |
| Young – Culcairn | Young (discharge) | 0 | 0 |
|  | Uranquinty | 158 | 158 |

Notes:

- The sites selected as compressor station sites on the Moomba to Wilton pipeline are sites that exist on the current pipeline.  A consequence of this assumption is that the spacing between compressor stations varies, and this results in a less than optimal performance from compressor stations.  If a more detailed analysis of the pipeline shows that the compressor stations can be spaced at approximately equal separations then improved performance can be expected, and the design nominated is conservative.

- The current pipeline design includes a small compressor installed at Young to reinforce the supply to the northern laterals pipeline (Bathurst – Lithgow).  This study assumes that this compressor unit is required during the development of the network, because conditions will occur where a higher pressure is required to deliver gas flows on the Northern Lateral than on the Young – Wilton pipeline.  In this situation it is more efficient to operate a small compressor to supply the lateral than to over-compress the Young - Sydney pipeline.

- Because the net gas flow in the Young – Culcairn pipeline is both to and from Victoria, this pipeline will be configured to deliver gas from the discharge of the Young compressor station when the flow direction is towards Victoria, and to receive gas into the suction of the Young compressor when the net flow direction is north.

The unsteady state SIROGAS calculation commences with a steady state calculation that fills the pipeline to a pressure profile that satisfies steady state deliveries nominated in the data file.  The unsteady state calculation commences from this starting condition, with the load and load profiles nominated for each of the fixed and profiled loads respectively. For this study, the calculation is run over a three week period.  If the steady state flows nominated for the system are close to the unsteady state conditions, the pressure profile in the network should repeat through the three week cycle with little change.  If the flows used to determine the initial steady state pipeline pressure profile differ from the unsteady state conditions, then the pressure profile will reduce or increase with time (as linepack is drawn from, or added to the pipeline).

A run was judged to be successful if the minimum pressure at the endpoints of each pipeline was higher than the nominated minimum value.

The unsteady state calculation procedure for the revised loads in March 1999 commenced with a steady state solution for the pipeline operating at average flows.  The unsteady state solution then commences from the steady state condition and applies a time varying profile to each of the major outflows.  Some additional computation was necessary to ensure that the revised analysis produced results similar to those produced by Sirogas.

Each of the unsteady state models computes the hydraulic power required to compress the gas between the suction and discharged pressures, and then computes the engine power and fuel consumption using correlations that are determined by the design engineer.  Typically the values are determined for:

- The heat rate – power curves for the selected engine published by the manufacturer assuming operation at or near best efficiency point.

- An expected compressor efficiency, typically in the range of 70-85%, (the low efficiency applies to the smaller units while the higher efficiency applies to the larger efficiency running near best efficiency.

Correlation coefficients are then used to calculate the power and fuel consumption.

The analyses performed for this study used performance data for Solar T60 and Mars units in the compressor models, but no attempt was made to refine the correlation coefficients to reflect the performance of the machines at part load, and no attempt was made to apply de-rated engine performance to specific installations.  The number of machines required to deliver the required power is based on inspection of the calculated power and then applying judgement.

Consequently the computed power and consumed fuel must be considered as reasonable estimates, and not as absolute values.

### Calculation Results

The calculations confirmed that the basic pipeline configuration is:

Moomba to Young		DN 600, Class 900

Young to Wilton		DN 600, Class 600

Dalton to Canberra		DN 300, Class 600

Northern Laterals		DN 150, Class 600 (all lines)

Young – Culcairn		DN 350, Class 600

Burnt Creek to Griffith	DN 150, Class 600

The output from each of the calculations is shown graphically as plots of pressure at nominated locations and flow, in Attachment 1 to this report.

Further refinement could:

- Change the Northern Lateral from all DN 150 pipe to a combination of DN 200, 150 and 100 pipe.  The effect of this would be to reduce the pressure gradient between Young and about Orange and increase the pressure gradient in the laterals to Oberon, Orange Meter station and Lithgow.  It is not considered that this change would have a material effect on the capital cost of the pipeline at this level of cost estimate.

- Reduce the diameter of the Dalton to Canberra pipeline from DN 300 to DN 250, the size currently adopted in the network design.  The cost impact of this change is included in the estimate section of this report.

- Reduce the diameter of the Young – Culcairn pipeline from DN 350 to DN 300.  This would be associated with increased compression in 2013

### Pipeline Compression

Compression is required on the pipeline initially and then incrementally to match the pipeline capacity with the forecast load growth.

#### Moomba Inlet Compression

Table 3-9 illustrates the compression required for the new pipeline at Moomba, assuming that the gas production facilities continue to deliver gas at 6.0 MPa. For the purposes of this study, the Moomba compressor station is assumed powered with Solar Mars 100 units that will deliver 9 MW when operated at site conditions at a design ambient temperature of 35 C.  At times when the ambient temperature is less than 35 C the delivered power is more than 9 MW.

Table 3-9 Moomba Compression to Raise pressure from 6.0 MPa to 15.3 MPa

| Year | Required Power | Compressor Units |
| --- | --- | --- |
| 2000 | 14,500 | 2 x Solar Mars 100 9 MW @ 40C |
| 2004 | <13,000 |  |
| 2006 |  |  |
| 2007 |  |  |
| 2009 | 15,100 | Add 1 standby |
| 2011 |  |  |
| 2012 | 18,400 |  |
| 2013 |  |  |
| 2014 | 22,200 | Add 1 Standby |

The compressor installation schedule initially provides two units at the compressor station, supplying 100% redundancy, since the high pressure design adopted requires the initial supply to be delivered at the design inlet pressure.

As the required power increases, units are added progressively to maintain a reasonable level of redundancy.  In general, the new compression is installed in the year prior to the year nominated as it being required.

#### Pipeline Compression

Table 3-10 illustrates the calculated power demand at each of the compressor station sites required in the development of the pipeline.  The power is reported as maximum, average and minimum kW demand during the period of the simulation.  An optimum configuration will minimise the variation between maximum and minimum power demand, and it is apparent from the table that some further refinement may offer a more uniform application of the power.

Table 3-10  Pipeline Compression

|  | Binerah | Questa Pk | Bulla Pk | Pine Ridge | Young | Young Laterals |
| --- | --- | --- | --- | --- | --- | --- |
| - Max. Average Min. | - | 3,950 3,500 3,150 | - | - | - | 340 260 170 |
| 2004 | - | - | - | - | - |  |
| 2009 Max. Average Min. | - | 5,100 4,600 3,700 | - | - | - | 160 230 120 |
| 2012 Max. Average Min. | - | 7,150 6,750 4,350 | - | 7,000 4,850 1,650 | 5,650 2,860 0 | 350 180 0 |
| 2014 Max. Average Min. | 9,000 8,500 5,300 | 9,300 8,500 4,900 | 9000 7,700 4,000 | 9,000 6,400 2,600 | 6,000 4,100 0 | 2,300 1,460 0 |

Table 3-11  Pipeline Compressor Installation Schedule

|  | Binerah | Questa | Bulla Pk | Pine Ridge | Young | Young |
| --- | --- | --- | --- | --- | --- | --- |
| 2000 |  | 1 x T60 |  |  |  | 2 x 400 kW |
| 2009 |  |  |  |  |  |  |
| 2012 |  | Add 1 x T60 |  | 2 x T60 | 2 x T60 |  |
| 2014 | 2 x Mars 100 | Add 1 x T60 | 2 x T70 |  |  | 1 X C40 |

Table 3-11 presents a probable installation schedule for pipeline compressor stations based on Solar T60 compressor units.  The installation schedule is based on providing sufficient power at the compressor station site by the time that it is required, and providing adequate redundancy, recognising the maturity and proven reliability of the units.

#### Pipeline Compression at Young for Northern Laterals Pipeline

A compressor is installed in 2000 at Young to maintain a nominal pressure of 10 MPa at the inlet to this pipeline.   This machine allows the Northern Laterals pipeline to be optimally sized for a known inlet pressure, and allows the high capacity Young to Wilton pipeline to be operated at a pressure that is optimised for the load in that pipeline, thus contributing to efficient pipeline operation.

This compressor is installed as a component of the initial pipeline construction. Two 400 kW units (duty / standby) are installed for continuous operation because there is no main pipeline compression at Young.

#### Pipeline Compression for the Young to Culcairn Pipeline

Intermediate compression is not considered necessary on the Culcairn to Young pipeline under normal conditions, provided the delivery pressure from either Barnawatha (net flow from Victoria to NSW) or from Young (net flow south from NSW to Victoria) is higher than 9 MPa.

The design assumes that in an optimised development, a compressor station is located at Barnawatha to deliver gas from Victoria into NSW, or to receive gas from NSW and boost the pressure from NSW to that required for delivery into Victoria, depending on the net flow direction.  (This might not be the case for 2014 loads, when it might be more efficient to boost the pressure at Culcairn).

The design assumes that when the flow direction is north, flow is received into the suction of the Young compressor station, and when the flow is south, it is delivered from the discharge (or suction) of the Young compressor station, depending on the pressure required in the system.

Calculations performed for the pipeline between Barnawatha and Young for the peak flow years at Culcairn are shown in Table 3-12.  From inspection of the output of the unsteady state calculations, the pressures at Young are typically lower than the values tabulated when flow is north, and when the flow is south, the Young compressor can be operated to deliver the pressure required, even though this may be somewhat inefficient.

It is necessary to maintain an inlet pressure of 10 MPa to deliver the 2014 flow.  The study assumes that this is provided by installing an additional compressor on the Northern Laterals offtake.  This allows the Young – Wilton pipeline to continue to operate independently of the lateral pipelines.  This may or may not be an optimum design – however because the capital expenditure is some 13 years into the future the present day impact of the net present cost is small, and does not justify further refinement.

Table 3-12  Pressures in Culcairn to Young Pipeline

| Year | Culcairn Flow | Diameter | Pressure (MPa) |  |  |
| --- | --- | --- | --- | --- | --- |
|  | (scm/h) | (mm nominal) | Barnawatha | Bomen | Young |
| 2000 (Unsteady State) | 27,010 | DN 350 | 7.0-8.9 (at Culcairn) |  | 7.3 –9.0 |
| 2014 (Unsteady State) | -100,640 | DN 350 | 7.0-7.6 (at Culcairn) | 8.3-8.8 | 10.2 |

Note : Negative flow represents flow from NSW into Victoria.

Inspection of the output from steady state calculations suggests that it may be practical to install smaller  diameters and still not provide intermediate compression.  However considerable flexibility is lost, and the larger diameter is considered to represent a more flexible design at minimum cost penalty.

## young compression

The design provides an intermediate compressor at Questa Park and does not provide a compressor at Young.  It could be argued that this limits the operational flexibility of the pipeline because the remoteness of the second compressor from the Sydney market will impose a time constant on the system that restricts its ability to respond to the variation in Sydney and Canberra market loads.

This may introduce inefficient operation, resulting in some operational pressure regulation at Young between the ANSI Class 900 and ANSI Class 600 pipeline sections, rather than using pressure regulation for occasional overpresure regulation.

The conceptual design assumes that with experience in load profiles, and with on-line predictive modelling capability in the control room, it will be practical to operate the Questa Park compressor to maintain adequate pressure at the inlet to the Young facility without having to resort to active pressure regulation at Young.

## pipeline configuration

A significant proportion of the cost of a pipeline system is associated with the pipeline facilities (isolation valves and scraper stations.

Since the construction of the existing pipelines, there have been changes in design codes, and development of internal inspection equipment that permit the spacing between these facilities to be increased.

The optimised design recognises the cost benefit of both these developments.

The pipeline configuration used in the cost estimates is tabulated in Attachment 2.  The Moomba to Young pipeline is divided into six scraper sections each approximately 170 km long.  The scraper sections are located at sites nominated as future compressor stations.

Each scraper section has two intermediate isolating valves, locating valves at a spacing of approximately 60 km.

Between Young and Wilton there are two scraper sections (Young – Goulburn and Goulburn – Wilton).  This pipeline contains 9 intermediate isolating valves.

The Young – Culcairn pipeline is divided into two scraper sections, nominally Young-Uranquinty and Uranquinty – Wodonga (Barnawatha).  The pipeline and pipeline facilities between Culcairn and Barnawatha are assumed to be provided by Transmission Pipelines Australia.

The NSW laterals pipeline includes 8 intermediate isolation valves.

The pipelines are provided with cathodic protection systems for control of external corrosion.

The pipeline network is provided with a communications system assumed to be provided by a combination of leased communication lines and leased communication capacity from satellite services.

# Capital Cost Estimates

## Estimate BAsis

The cost estimates are developed from a database of strongly supported as-built cost data and project cost estimates for pipelines in arid and coastal regions of Australia.

The estimates incorporate allowance for the features that currently exist along the pipelines, and advised by EAPL.

All costs are in First Quarter 1999 dollars with no allowance for escalation.  The estimate includes allowance for financing the project with the interest cost calculated over a funds drawdown period.

Costs are based on the nominal quantities identified on the detailed worksheets, and in particular, on the actual lengths of the existing pipeline routes.

Allowance is made for notional quantities of rock trench, padding and other physical constraints of the pipeline route provided by EAPL.  In some cases accurate lengths of these features were not available from EAPL, and the quantities allowed are based on judgement using experience and some knowledge of the routes by the author.  The accuracy of the estimates is considered to be 20%.  The accuracy of the construction cost portion of the estimate is influenced by the assumptions made in relation to the ground conditions.

## Assumptions

A number of assumptions were made in developing the estimate.  The extent to which these assumptions influence the overall cost of constructing the pipelines through undisturbed country is unknown.  The assumptions are:

- All felled trees and vegetation are stockpiled and respread on the right of way, or burned after completion.  No allowance is made for chipping and/or mulching of felled trees.

- The estimate assumes that mobilisation costs are spread over more than one construction spread.  For example, the equipment used for Dalton to Canberra will also be employed on at least one other section.  Accordingly, mobilisation and demobilisation costs are spread across each of the pipeline projects.

- Currency conversion:	1 AUD = 0.64 USD.

- Interest on finance raised for construction of the project is assumed to be 8.5%.  The interest charged is calculated using this rate, assuming 100% debt for the estimated cost applied for a 24 month project construction period, and assuming that through management of the finance drawdown, only 40% of the calculated interest is paid.

Escalation between the time of the estimate and the completion of construction is assumed to average 1.5% per annum.  The project estimate is escalated at this rate for a 24 month period, assuming that progressive drawdown of the capital will result in only 60% of the calculated value being applied to the project.

- Owner’s costs are assumed to be 2% of the capital cost of the project.

- Engineering, procurement and project management costs are assumed to be 7.5% of the estimated capital cost of the project.

- A contingency of 10% is applied to the estimated cost, including Owners, EPCM and Interest charges.

- An allowance is made for Capitalised spares at a rate of 1.5% of the capital cost.

## Estimate Exclusions

The estimate makes no allowance for:

- Cost of feasibility studies

- Import Duties

## Project approvals / land acquisition costs

A reasonable estimate of the cost of obtaining approval for this project is included in the detailed estimate, having regard to the increasing cost of this activity in pipeline development projects.

The estimate takes note of the recent change to energy transportation pipelines that identify them as “Permitted Future Acts” under the Native Title Legislation.  This simplifies the approval process, and requires identified Native Title Claimants to be compensated in the same manner as other affected landholders.

The amounts allowed in the estimates for the project approvals represent a reasonable cost for the activities.  If this project was developed as a greenfields project it is possible that the project management would have some difficulty in managing the work within the estimated amounts.  This is because the project profile would be such that it would attract a great deal of attention from Government and Landowner / Landholder / Land Claimant Groups that could increase the estimated cost significantly.

However there is a significant allowance for Contingency (omissions) in the capital cost estimate that should accommodate omissions in this area.

## Linepipe costs

Line pipe costs make up a significant proportion of the estimate.

BHP Oil and Gas Pipe provided a budget quotation for the DN 450 and smaller line pipe.   Accordingly the estimate is based on an average cost for this pipe of $A 1150 / tonne delivered Port Kembla, in both API 5L Grade X70 and API 5L Grade X80.  Budget quotations received for similar pipe in October were $A 1100 / tonne for API 5L X80 and $A 1063 / tonne for API 5L grade X 70.

This tonnage rate was applied to larger diameter pipelines.

It must be appreciated that line pipe is offered on a world price basis.  At times when the world market is flat, as is the present situation, line pipe cost is relatively low.  In December 1997 typical prices for similar material was around $A 1400 / tonne.

A variation of this amount between the time of this estimate and construction of the pipeline would add approximately $A 65 million to the cost of the pipe.

## Estimated Cost

A summary of the estimated capital cost of the pipelines proposed in this study is presented in Table 4-13.  A detailed estimate summary is presented in Attachment 3.

Table 4-13  Estimated Cost of Optimised Pipelines

| Pipeline | Estimated Cost ($A’000s) |
| --- | --- |
| Moomba to Young | 698,665 |
| Young to Wilton | 194,403 |
| Young to Culcairn | 64,677 |
| Dalton to Canberra | 18,974 |
| Young to Lithgow | 51,051 |
| Junee to Griffith | 30,446 |
| Estimated Cost | 1,058,216 |

## Pipeline development cost

The pipeline system requires incremental development through the addition of compressor stations as the pipeline load increases and the supply pattern changes.  The incremental compressor station cost for the trunk pipeline is presented in Table 4-14.

The incremental development of the pipeline has assumed that development is staged. The development costs provide for installation of incremental compression in the years prior to that when the full power is required, ensuring that spare capacity is available as the demand increases.  For example, the pipeline is constructed in 1999 with capacity for loads to approximately 2004.  Prior to 2004, additional compression is installed to provide power to 2006.  In 2006 additional power is installed to deliver flows to 2009, and in 2009 additional power is installed to achieve the 2011 load, and so on.

The actual expenditure dates presented in Table 4-14 represent a reasonable judgement of the probable expenditure, because the hydraulic analysis was not undertaken on a year by year basis.  Furthermore, it is probable that the expenditure for each stage would be undertaken over a two year period.

The incremental compressor station costs used in the above calculation are:

- Moomba Inlet - Cost per additional Solar Mars 100 unit, complete per installation is approx $17.5M, and approximately $31.1 M for a two unit station.

- Moomba - Wilton Intermediate Stations - Two Taurus 60 installation is $23.0M, and $10.0M per additional unit.

Table 4-14  Future Development Costs and Net Present Cost

| Pipeline | Estimated Cost ($A’000s) |
| --- | --- |
| 2001 | 0 |
| 2002 | 0 |
| 2003 | 0 |
| 2004 | 0 |
| 2005 | 0 |
| 2006 | 0 |
| 2007 | 0 |
| 2008 | 0 |
| 2009 | 73,500 |
| 2010 | 0 |
| 2011 | 0 |
| 2012 | 93,600 |
| 2013 | 0 |
| 2014 | 0 |
| Estimated Cost | 167,100 |
| Net Present Cost Escalation = 1.5% Discount Rate = 8.5% | 96,725 |
| Initial Cost | 1,058,116 |
| Net Present Project Cost | 1,154,841 |

## Cost reduction for  DN 300 pipeline to culcairn

The Young to Culcairn pipeline was selected as DN 350, because this was considered as the smallest diameter that could reasonably be justified to link the NSW and Victorian markets and gas supplies.

The cost penalty of this decision is estimated to be approximately $6.0 million in initial capital cost, although there is a cost penalty in 2012 in the order of $15 M  to construct an intermediate compressor station.  At a discount rate of 8.5%, the net present cost of the future compressor station is about $5.6 M.  This is close to the initial cost, and suggests that the selected diameter does not significantly depart from an optimum solution.

## Potential saving - Dalton – Canberra pipeline

The proposed Dalton to Canberra pipeline size is DN 300.  The Canberra load is highly variable, and a larger than necessary pipeline was selected to provide a more constant delivery pressure to Canberra.

It is possible to deliver the volume required through a DN 250 pipeline.  If this was adopted, the capital cost of the pipeline would reduce by approximately $2.4 M.

## Impact of australian dollar variability

This cost estimate is presented in Australian dollars, with US dollar components converted to Australian Dollars at the assumed rate of 1.00 AUD = 0.64 USD.

The Australian dollar is currently quite volatile, and consequently any change in the relativity will have a significant impact on the estimated cost presented in this analysis.

By way of example, a change in the exchange rate from 1.00 AUD = 0.64 USD to 1.0 AUD = 0.60 USD (a change of 6.7%) will result in the estimated costs increasing by between 2.5 and 3.0%.

## Operating Costs – Fuel gas consumption

Fuel gas consumed by the operating compressors is calculated by the unsteady state model.  As discussed earlier in this report, the fuel gas calculation makes assumptions about the engine and compressor efficiency, and also assumes them to be constant irrespective of the unit load.  Consequently the calculated fuel gas demand is a reasonable estimate of the usage.

The calculated values also apply to the times of the year when the pipeline is operating at the maximum load condition addressed in the model.

The annual fuel cost should be estimated using the values tabulated in Table 4-15, and modified using an experienced base factor that relates the annual usage to the peak usage.

Table 4-15  Estimated Fuel Demand

| Year | Average Fuel Demand for One (1) Week Operation at Peak Load (sm3/h) |
| --- | --- |
| 2000 | 6,100 |
| 2004 |  |
| 2007 |  |
| 2009 | 6,475 |
| 2011 |  |
| 2012 | 11,770 |
| 2013 |  |
| 2014 | 19,442 |

The demand for the years for which calculations were not made is roughly proportional to the total system throughput in that year.

ATTACHMENT 1

HYDRAULIC MODEL OUTPUT

(not available with electronic version of the report)

ATTACHMENT 2

PIPELINE CONFIGURATION

(Deleted – confidential)

ATTACHMENT 3

ESTIMATE DETAIL SUMMARY

| Owners Project Costs | 2.0% |
| --- | --- |
| EPCM | 7.5% |
| Financing Costs | 6.8% |
| Escalation | 1.8% |
| Contingency | 10.0% |
| Capitalised Spares | 1.5% |
| Financing Cost Basis |  |
| Project Duration | 24 |
| Interest During Construction | 8.5% |
| Drawdown Factor | 0.4 |
| Escalation Basis |  |
| Project Duration | 24 |
| Escalation During Construction | 1.5% |
| Drawdown Factor | 0.6 |

| EAPL OPTIMISED SYSTEM DESIGN |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CAPITAL COST ESTIMATES |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | MOOMBA TO YOUNG |  |  |  |  | YOUNG TO WILTON |  |  |  | YOUNG TO CULCAIRN |  |  |  | DALTON TO CANBERRA |  |  |  | YOUNG TO LITHGOW |  |  |  | JUNEE TO GRIFFITH |  |  |  |
| LINEPIPE DIA. | DN 600 |  |  |  |  | DN 600 |  |  |  | DN 350 |  |  |  | DN 300 |  |  |  | DN 150 |  |  |  | DN 150 |  |  |  |
| WALL THICKNESS (mm) | 11.8 |  |  |  | 9 |  |  | 5.3 |  |  | 78% 4.8 / 22% 7.1 |  |  |  | 4.8 |  |  | 4.8 |  |  |
| PIPE SPEC | API 5L X80 |  |  |  |  | API 5L X70 |  |  |  | API 5L X70 |  |  |  | API 5L X70 |  |  |  | API 5L X42 |  |  |  | API 5L X42 |  |  |  |
| CONSTRUCTION (m/day) | 2100 |  |  |  | 2100 |  |  | 3500 |  |  | 3600 |  |  | 3400 |  |  | 3700 |  |  |
| ROUTE LENGTH (km) | 1034 |  |  |  | 265 |  |  | 218 |  |  | 58 |  |  | 270 |  |  | 179 |  |  |
|  | QTY | $'000 |  |  | QTY | $'000 |  | QTY | $'000 |  | QTY | $'000 |  | QTY | $'000 |  | QTY | $'000 |  |
| LINEPIPE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| LINEPIPE (EX BHP) F.I.S. SITE |  |  |  |  |  |  |  | 218 km | 11396 |  | 58 km | 2601 |  | 279 km | 5301 |  | 179 km | 3401 |  |
| LINEPIPE C.I.F. WOLLONGONG (EX JAPAN) | 1034 km | 206800 |  |  | 265 km | 40423 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FREIGHT WOLLONGONG TO SITE | 182 kt | 6915 |  |  | 35.6 kt | 1347 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| YELLOWJACKET COATING (1000um) |  |  |  |  |  |  |  |  | 218 km | 4113 |  | 58 km | 936 |  | 279 km | 2340 |  | 179 km | 1502 |  |
| FBE COATING (400um) | 1034 km | 35748 |  |  | 265 km | 9162 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| sub total |  | 249463 |  |  |  | 50932 |  |  | 15509 |  |  | 3537 |  |  | 7641 |  |  | 4903 |  |
| SURVEY & EASEMENT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ROUTE SURVEY | 1034 km | 775 |  |  | 265 km | 292 |  | 218 km | 165 |  | 58 km | 45 |  | 279 km | 376 |  | 179 km | 224 |  |
| GEOTECHNICAL INVESTIGATION | 1034 km | 517 |  |  | 265 km | 193 |  | 218 km | 100 |  | 58 km | 50 |  | 279 km | 185 |  | 179 km | 100 |  |
| EASEMENT DOCUMENT SUBMISSION | ITEM | 1015 |  |  | ITEM | 960 |  | ITEM | 845 |  | ITEM | 320 |  | ITEM | 815 |  | ITEM | 540 |  |
| LANDOWNER CONTACT / NEGOTIATIONS | 1034 km | 1300 |  |  | 265 km | 1000 |  | 218 km | 800 |  | 58 km | 150 |  | 279 km | 800 |  | 179 km | 800 |  |
| LAND VALUATIONS | 1034 km | 715 |  |  | 265 km | 500 |  | 218 km | 400 |  | 58 km | 75 |  | 279 km | 300 |  | 179 km | 300 |  |
| EASEMENT LODGEMENT/REGISTRATION | ITEM | 780 |  |  | ITEM | 690 |  | ITEM | 635 |  | ITEM | 350 |  | ITEM | 570 |  | ITEM | 395 |  |
| CLAIMS / DAMAGES & ACQUISITION | 1034 km | 1860 |  |  | 265 km | 1645 |  | 218 km | 1390 |  | 58 km | 395 |  | 279 km | 1295 |  | 179 km | 810 |  |
| sub total |  | 6962 |  |  |  | 5280 |  |  | 4335 |  |  | 1385 |  |  | 4341 |  |  | 3169 |  |
| ENVIRONMENT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| BIOLOGICAL SURVEYS | 1034 km | 1160 |  |  | 265 km | 625 |  | 218 km | 680 |  | 58 km | 110 |  | 279 km | 810 |  | 179 km | 410 |  |
| CULTURAL SURVEYS / NATIVE TITLE | 1034 km | 4630 |  |  | 265 km | 2270 |  | 218 km | 1500 |  | 58 km | 400 |  | 279 km | 2000 |  | 179 km | 1200 |  |
| CONSTRUCTION MONITORING / AUDITS | 1034 km | 1710 |  |  | 265 km | 475 |  | 218 km | 240 |  | 58 km | 75 |  | 279 km | 400 |  | 179 km | 200 |  |
| sub total |  | 7500 |  |  |  | 3370 |  |  | 2420 |  |  | 585 |  |  | 3210 |  |  | 1810 |  |
| PIPELINE CONSTRUCTION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MOBILISATION & DEMOBILISATION | ITEM | 9900 |  |  | ITEM | 5550 |  | ITEM | 2900 |  | ITEM | 750 |  | ITEM | 1300 |  | ITEM | 1300 |  |
| CLEAR & GRADE R.O.W. | 1034 km | 2245 |  |  | 265 km | 672 |  | 218 km | 392 |  | 58 km | 79 |  | 279 km | 561 |  | 179 km | 305 |  |
| STRINGING | 182 kt | 31857 |  |  | 35.6 kt | 4910 |  | 9.98 kt | 1478 |  | 2.45 kt | 338 |  | 5.45 kt | 805 |  | 3.5 kt | 417 |  |
| DITCHING - EASY | 740 km | 8600 |  |  | 170 km | 2081 |  | 183 km | 854 |  | 41 km | 165 |  | 112 km | 299 |  | 126 km | 321 |  |
| DITCHING - RIP & EXCAVATE | 164 km | 6177 |  |  | 30 km | 1246 |  | 27 km | 657 |  | 13 km | 169 |  | 140 km | 1056 |  | 49 km | 334 |  |
| DITCHING - DRILL & BLAST / ROCKSAW | 130 km | 18498 |  |  | 65 km | 9434 |  | 8 km | 603 |  | 4 km | 272 |  | 27 km | 979 |  | 4 km | 126 |  |
| BENDING | 1034 km | 2419 |  |  | 265 km | 618 |  | 218 km | 421 |  | 58 km | 94 |  | 279 km | 238 |  | 179 km | 143 |  |
| WELDING | 1034 km | 24183 |  |  | 265 km | 6404 |  | 218 km | 2893 |  | 58 km | 678 |  | 279 km | 1495 |  | 179 km | 902 |  |
| FIELD JOINTS | 1034 km | 8344 |  |  | 265 km | 2138 |  | 218 km | 1009 |  | 58 km | 237 |  | 279 km | 526 |  | 179 km | 332 |  |
| RADIOGRAPHY | 1034 km | 8056 |  |  | 265 km | 1997 |  | 218 km | 823 |  | 58 km | 213 |  | 279 km | 431 |  | 179 km | 278 |  |
| LOWER IN | 1034 km | 9864 |  |  | 265 km | 2433 |  | 218 km | 939 |  | 58 km | 206 |  | 279 km | 453 |  | 179 km | 263 |  |
| TRENCH BREAKERS | 50 No | 34 |  |  | 200 No | 140 |  |  |  |  | 30 No | 16 |  | 650 No | 194 |  |  |  |  |
| WEIGHT COATING / SET - ON WEIGHTS | 20 km | 1565 |  |  | 30 km | 2598 |  | 5 km | 186 |  |  |  |  |  |  |  | 15 km | 238 |  |
| BEDDING & BACKFILL | 1034 km | 10672 |  |  | 265 km | 2871 |  | 218 km | 1474 |  | 58 km | 339 |  | 279 km | 764 |  | 179 km | 423 |  |
| E/O FOR PADDING | 680 km | 29986 |  |  | 198 km | 9439 |  | 98 km | 3589 |  | 47 km | 1389 |  | 184 km | 2217 |  | 126 km | 1484 |  |
| RIVER & CREEK CROSSINGS (DREDGED) | 470 m | 373 |  |  | 4800 m | 4070 |  | 770 m | 445 |  | 180 m | 94 |  | 1630 m | 465 |  | 900 m | 256 |  |
| HORIZONTAL DIRECTIONAL DRILLING | 580 m | 694 |  |  | 7400 m | 8428 |  | 100 m | 185 |  |  |  |  | 2350 m | 914 |  | 900 m | 320 |  |
| ROAD & RAIL CROSSINGS | 20 No | 780 |  |  | 39 No | 1598 |  | 25 No | 404 |  | 5 No | 90 |  | 31 No | 286 |  | 20 No | 202 |  |
| TIE INS | 1034 km | 6514 |  |  | 265 km | 1667 |  | 218 km | 865 |  | 58 km | 183 |  | 279 km | 384 |  | 179 km | 225 |  |
| HYDRO TESTING | 1034 km | 7030 |  |  | 265 km | 1801 |  | 218 km | 984 |  | 58 km | 205 |  | 279 km | 479 |  | 179 km | 315 |  |
| DEWATERING & DRYING | 1034 km | 7026 |  |  | 265 km | 1783 |  | 218 km | 766 |  | 58 km | 212 |  | 279 km | 530 |  | 179 km | 335 |  |
| GROUND & AERIAL MARKERS | 1034 km | 1442 |  |  | 265 km | 369 |  | 218 km | 304 |  | 58 km | 81 |  | 279 km | 613 |  | 179 km | 250 |  |
| RESTORATION INCL FENCES & GATES | 1034 km | 3560 |  |  | 265 km | 716 |  | 218 km | 680 |  | 58 km | 166 |  | 279 km | 290 |  | 179 km | 384 |  |
| CATHODIC PROTECTION | 1034 km | 1438 |  |  | 265 km | 398 |  | 218 km | 345 |  | 58 km | 100 |  | 279 km | 545 |  | 179 km | 190 |  |
| SURVEY & AS BUILTS | 1034 km | 2028 |  |  | 265 km | 660 |  | 218 km | 480 |  | 58 km | 130 |  | 279 km | 590 |  | 179 km | 345 |  |
| PRECOMMISSIONING | ITEM | 800 |  |  | ITEM | 380 |  | ITEM | 225 |  | ITEM | 125 |  | ITEM | 250 |  | ITEM | 160 |  |
| sub total |  | 204085 |  |  |  | 74401 |  |  | 23901 |  |  | 6331 |  |  | 16664 |  |  | 9848 |  |
| STATIONS & FACILITIES |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SCRAPER LAUNCHER OR RECEIVER | 1 No | 678 |  |  | 2 No | 1356 |  | 2 No | 662 |  | 2 No | 596 |  | 6 No | 828 |  | 2 No | 276 |  |
| COMBINED LAUNCHER / RECEIVER | 6 No | 6642 |  |  | 1 No | 1107 |  |  |  |  |  |  |  | 1 No | 226 |  |  |  |  |
| MAIN LINE VALVE STATIONS | 11 No | 6688 |  |  | 9 No | 5472 |  | 8 No | 1948 |  | 3 No | 654 |  | 14 No | 1638 |  | 8 No | 936 |  |
| INLET COMPRESSION STN (2 X MARS 100) | ITEM | 31100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| BOOSTER COMPRESSION | ITEM | 10000 |  |  |  |  |  |  |  |  |  |  |  |  | 1500 |  |  |  |  |
| OFFTAKE - PRESS REG & METER (DN50) |  |  |  |  |  |  |  |  |  | 1 No | 103 |  |  |  |  |  |  |  |  |  |  |
| OFFTAKE - PRESS REG & METER (DN100) |  |  |  |  |  |  |  |  |  | 1 No | 339 |  |  |  |  |  |  |  | 7 No | 2632 |  |
| OFFTAKE - PRESS REG & METER (DN150) | 1 No | 580 |  |  |  |  |  | 2 No | 1022 |  |  |  |  | 6 No | 3480 |  |  |  |  |
| PRESS REG, HEATER & METER (DN100) |  |  |  |  |  | 5 No | 2183 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| PRESS REG, HEATER & METER (DN300) |  |  |  |  |  |  |  |  |  |  |  | 1 No | 1575 |  |  |  |  |  |  |  |
| PRESS REG, HEATER & METER (DN750) |  |  |  |  |  | 1 No | 5014 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COMMUNICATIONS & SCADA | ITEM | 6800 |  |  | ITEM | 1850 |  | ITEM | 580 |  | ITEM | 225 |  | ITEM | 530 |  | ITEM | 325 |  |
| MAINTENANCE BASES | 1 No | 4120 |  |  | 1 No | 1650 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| YOUNG OPERATIONS CENTRE W. EQUIPMENT | ITEM | 1000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CORPORATE OFFICE FITOUT & EQUIPMENT | ITEM | 1500 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| sub total |  | 69108 |  |  |  | 18632 |  |  | 4654 |  |  | 3050 |  |  | 8202 |  |  | 4169 |  |
| Direct Project Costs |  | 537118 |  |  |  | 152615 |  |  | 50819 |  |  | 14888 |  |  | 40058 |  |  | 23899 |  |
| CAPITALISED SPARES 1.5% |  | 1037 |  |  |  | 279 |  |  | 70 |  |  | 46 |  |  | 123 |  |  | 63 |  |
| OWNERS PROJECT COSTS 2% |  | 10742 |  |  |  | 3052 |  |  | 1016 |  |  | 298 |  |  | 801 |  |  | 478 |  |
| EPCM 7.5% |  | 40284 |  |  |  | 11446 |  |  | 3811 |  |  | 1117 |  |  | 3004 |  |  | 1792 |  |
| ESCALATION COST 1.8% |  | 10605 |  |  |  | 3013 |  |  | 1003 |  |  | 294 |  |  | 792 |  |  | 472 |  |
| PROJECT FINANCING COST 6.8% |  | 40064 |  |  |  | 11364 |  |  | 3784 |  |  | 1109 |  |  | 2983 |  |  | 1780 |  |
| CONTINGENCY 10% |  | 58814 |  |  |  | 12534 |  |  | 4174 |  |  | 1223 |  |  | 3290 |  |  | 1963 |  |
| TOTALS $'000 | 698,665 |  |  | 194,303 |  |  |  | 64,677 |  |  | 18,974 |  |  | 51,051 |  |  | 30,446 |  |  |
| Estimated Project Cost ($'000s) | $1,058,116 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| EAPL OPTIMISED SYSTEM DESIGN |  |
| --- | --- |
| CAPITAL COST ESTIMATE - MOOMBA INLET COMPRESSION STATION |  |
| ITEM | A$'M |
| CIVILS / CONCRETE / STRUCTURAL STEEL / BUILDINGS | 2.18 |
| 2 No MARS 100 COMP UNITS | 17.90 |
| METERING SKIDS | 0.90 |
| GAS AFTER COOLING | 1.20 |
| 600 KW GENERATOR | 0.54 |
| OTHER EQUIPMENT | 0.36 |
| DESIGN ALLOWANCES | 0.79 |
| THIRD PARTY INSPECTION, VENDOR REP | 0.34 |
| PIPING & VALVES | 3.44 |
| ELECTRICAL | 1.48 |
| CONTROL SYSTEMS | 0.36 |
| INSTRUMENTATION | 1.35 |
| PAINT & INSULATION | 0.26 |
| TOTAL | 31.10 |

| NOTE : COSTS EXCLUDE OWNERS COSTS, EPCM & CONTINGENCIES. |  |
| --- | --- |

| Unit Price | 4,000 | USD | 01/11/1998 | With Enclosure |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Current Exchange Rate | 0.64 |  |  |  |  |  |  |  |
| Unit cost | 6,250 | AUD |  |  |  |  |  |  |
| Freight & Insurance | 150 |  |  |  |  |  |  |  |
| Current cost to site | 6,400 |  |  |  |  |  |  |  |
| Rated Power | 4742 |  | Size Factor | 0.66 |  |  |  |  |
| Base Power | 3132 |  |  |  |  |  |  |  |
| T60 Size | Size Factor |  |  | 1.31489861 |  |  |  |  |  |
|  | Quantity |  |  |  | Extra Unit |  | Single Unit |  |  |
| Development |  |  |  |  |  |  |  |  |
| Land | 1 | 80 | 80 |  |  |  |  |  |
| Landscaping | 1 | 50 | 50 |  |  |  |  |  |
| Subtotal |  |  | 130 |  |  |  |  | 130 |
| Materials |  | Unit Cost |  |  |  |  |  |  |
| Compressor Unit | 2 | 6,400 | 12800 |  | 6400 | 1 | 6,400 | 6,400 |
| Valve Control Skid | 1 | 300 | 394 |  | 394 | 1 | 300 | 300 |
| Fuel Skid | 1 | 100 | 131 |  | 131 | 1 | 100 | 100 |
| Inlet Filters | 2 | 75 | 197 |  | 0 | 2 | 75 | 150 |
| Station Piping / Valves | 1 | 800 | 1052 |  | 460 | 1 | 800 | 800 |
| Cooler | 2 | 130 | 342 |  | 171 | 1 | 130 | 130 |
| Buildings | 2 | 150 | 394 |  | 197 | 1 | 150 | 150 |
| Control System | 1 | 150 | 197 |  | 197 | 1 | 150 | 150 |
| Power Generation | 2 | 85 | 224 |  | 112 | 2 | 85 | 170 |
| Electrical/MCC/Cables | 1 | 200 | 263 |  | 131 | 1 | 200 | 200 |
| Field Instrumentation | 1 | 150 | 197 |  | 131 | 1 | 150 | 150 |
| Spares | 1 | 300 | 394 |  | 131 | 1 | 300 | 300 |
| Transport | 1 | 80 | 105 |  | 53 | 1 | 80 | 80 |
| Subtotal |  |  | 16692 |  | 8510 |  |  | 9080 |
| Installation |  |  |  |  |  |  |  |  |
| Site Clear & Grade, Fencing | 1 | 150 | 197 |  | 66 | 1 | 150 | 150 |
| Foundations | 1 | 200 | 263 |  | 197 | 1 | 200 | 200 |
| Equipment Installation | 1 | 300 | 394 |  | 394 | 1 | 300 | 300 |
| E & I Installation | 1 | 400 | 526 |  | 263 | 1 | 400 | 400 |
| Piping Installation | 1 | 400 | 526 |  | 329 | 1 | 400 | 400 |
| Subtotal |  |  | 1907 |  | 1249 |  |  | 1450 |
| EPCM | 12% |  | 2231 |  | 1171 |  |  | 1263 |
| Contingency | 10% |  | 2095 |  | 1093 |  |  | 1192 |
| Total |  |  | 23055 |  | 12024 |  |  | 13115 |

| Installation Schedule |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Discount Rate |  |  | 0.085 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Excalatioon Rate |  |  | 0.015 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Required at Date |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Base Case | 2001 | 2002 |  | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | Total |
| Moomba |  |  |  |  |  |  |  |  |  |  |  |  | 17500 |  | 17500 |  |
| Binerah |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 31100 |  |
| Questa |  |  |  |  |  |  |  |  |  |  |  |  | 10000 |  | 10000 |  |
| Bulla |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25000 |  |
| Pine |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Marsden |  |  |  |  |  |  |  |  |  |  |  |  | 23000 |  |  |  |
| Young |  |  |  |  |  |  |  |  |  |  |  |  | 23000 |  | 10000 |  |
|  |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73500 | 0 | 93600 | 167100 |
| Installed At Date |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Base Case | 2001 | 2002 |  | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 |  |
| Moomba |  |  |  |  |  |  |  |  |  | 17500 |  |  | 17500 |  |  |  |
| Binerah |  |  |  |  |  |  |  |  |  |  |  |  | 31100 |  |  |  |
| Questa |  |  |  |  |  |  |  |  |  | 10000 |  |  | 10000 |  |  |  |
| Bulla |  |  |  |  |  |  |  |  |  |  |  |  | 25000 |  |  |  |
| Pine |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Marsden |  |  |  |  |  |  |  |  |  | 23000 |  |  |  |  |  |  |
| Young |  |  |  |  |  |  |  |  |  | 23000 |  |  | 10000 |  |  |  |
|  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 73500 | 0 | 0 | 93600 | 0 | 0 | 167100 |
|  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 84039 | 0 | 0 | 111909 | 0 | 0 |  |
| Net Present Cost | $96,725.50 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

ATTACHMENT 4

SYSTEM LOAD PROFILES

(Deleted – confidential)